## Introduction
Cost-Effectiveness of ASHRAE Standard 90.1-2022 Compared to ASHRAE Standard 90.1-2019
The report providing documentation for this spreadsheet can be found at:
https://www.energycodes.gov/national-and-state-analysis
This workbook accompanies the report National Cost-Effectiveness of ANSI/ASHRAE/IES Standard 90.1-2022 available at the same location as this spreadsheet at the URL shown at the right. The report provides the full description of this project and the cost estimate methodology as well as additional details on the cost estimate items.
Pacific Northwest National Laboratory (PNNL) conducted this study in support of the U.S. Department of Energy (DOE) Building Energy Codes Program (BECP). BECP was founded in 1993 in response to the Energy Policy Act of 1992, which mandated that DOE participate in the development process for national model codes and that DOE help states adopt and implement progressive energy codes. DOE has supported the development and implementation of more stringent building energy codes since the 1970s, but the BECP was the first DOE program assigned with specific mandates in regard to energy codes.
Building energy codes set baseline minimum requirements for energy-efficient design and construction for new and renovated buildings, and impact energy use and emissions for the life of the buildings. Energy codes are part of the greater collection of regulations that govern the design, construction, and operation of buildings for the health and life safety of occupants. Improving these regulations generates consistent and long-lasting energy savings.
For this project, BECP directed PNNL to analyze the cost-effectiveness of the changes in Standard 90.1 from 90.1-2019 to 90.1-2022 (ANSI/ASHRAE/IESNA 2019, ANSI/ASHRAE/IESNA 2022) applied in the United States. The first task was to define the building elements that need to change for compliance with these two standards. The second task was to develop costs for the required changes in buildings. The third task was to analyze the cost-effectiveness of the changes. This workbook includes the descriptions of the cost items and the cost estimates.
Changes to Standard 90.1-2019 were implemented through addenda, and Standard 90.1-2022 is simply Standard 90.1-2019 with all approved addenda. Previous work by PNNL assessed the energy savings due to the addenda. The addenda are the cost estimate items in most cases and are listed with brief descriptions in the cost spreadsheets.
A suite of prototype building models were used to quantify the energy impacts of the addenda. The development of the prototype models and the energy savings analysis are documented in the quantitative analysis report completed as part of the DOE determination process. For this cost effectiveness project, PNNL used six prototype buildings and five climate locations. For comparison, the quantitative analysis used 16 prototypes and 17 climate locations. Cost estimate and cost effectiveness results are developed for all 30 combinations of the selected six prototypes and five climate locations:
Selected Prototypes Selected Climate Locations
Small Office 2A Tampa, FL
Large Office 3A Atlanta, GA
Standalone Retail 3B El Paso, TX
Primary School 4A New York, NY
Small Hotel 5A Buffalo, NY
Mid-rise Apartment
This cost estimate spreadsheet is organized in sections, some with multiple worksheets, with each section or sub-section highlighted with a different colored tab:
1) Introduction (white)
2) HVAC (blue)
3) Lighting (red)
4) Envelope (orange)
5) Cost Estimate Summaries (olive)
Within the cost estimate sections, there are several types of cost worksheets. Component costs (labeled with “comp” in the worksheet name) are the individual cost items not assigned to the particular prototype, such as the cost for a 33 W linear LED lamp and fixture. Prototype costs (labeled with “proto” in the worksheet name) are the assignment of component costs to the applicable prototypes and climate zones. For HVAC costs, there is one cost worksheet for each prototype. The Interior Lighting LPD section includes an additional worksheet that assigns costs by lighting space types and these are then assigned to the prototypes. The Envelope worksheet combines component and prototype costs. Summary results for new construction, maintenance and replacement over 40 years are shown for each prototype and climate zone in the Summary worksheets.
There is also a Cost Estimate Summary sheet. It has costs with replacements for 29 years with the residual value of items with useful lives that extend beyond 30 years shown in year 30. It also shows a scenario that extends the replacements for 39 years and includes residual values in year 40. Residual values are discussed in Section 5.1.1 of the main report.
The cost estimates include material, labor, construction equipment, incremental commissioning and maintenance where significant, and overhead and profit (OH&P). These costs were estimated for both the initial project, and for replacement, which required defining the useful life of the cost items before replacement.
A variety of sources were used to produce the cost estimate and are identified in the various worksheets. For mechanical costs, two consulting firms were used for prior versions of this study, Faithful+Gould a cost estimating firm, and Solarc a mechanical, electrical and plumbing engineering consulting firm. For lighting costs and a couple of mechanical items, PNNL in house expertise was applied supported by online resources. Any older costs were adjusted for inflation.
Several general parameters apply to all of the cost estimates as shown in the worksheet General Cost Parameters. These items include overhead and profit, identified separately for first cost, and for replacement costs. Also included is a general method for adjusting labor costs for replacement. Finally, costs for small tools, and general construction equipment are included.

## MechFormulaDoc (hidden)
Generally, data is found from 5 climate zones, based on capacity [col I & J from HVAC_Data]
and then interpolated from standard costs [HVAC Costs Comp] to find relevant cost for prototype
Example from small office
The following is done for each of up to 5 climte zones
Cell K 13 as an example
|  | Formula: | =IF(CZ_1=0,0,IF(OR(INDIRECT("$"&K$4&ROW(K13))>=MAX(INDIRECT($C13&K$5)),(INDIRECT("$"&K$4&ROW(K13))<MIN(INDIRECT($C13&K$5)))),"OUT OF RANGE",INDEX(INDIRECT($C13&K$6),MATCH(INDIRECT("$"&K$4&ROW(K13)),INDIRECT($C13&K$5),1),K$7)+(INDEX(INDIRECT($C13&K$6),MATCH(INDIRECT("$"&K$4&ROW(K13)),INDIRECT($C13&K$5),1)+1,K$7)-INDEX(INDIRECT($C13&K$6),MATCH(INDIRECT("$"&K$4&ROW(K13)),INDIRECT($C13&K$5),1),K$7))*(INDIRECT("$"&K$4&ROW(K13))-INDEX(INDIRECT($C13&K$5),MATCH(INDIRECT("$"&K$4&ROW(K13)),INDIRECT($C13&K$5),1)))/(INDEX(INDIRECT($C13&K$5),MATCH(INDIRECT("$"&K$4&ROW(K13)),INDIRECT($C13&K$5),1)+1)-INDEX(INDIRECT($C13&K$5),MATCH(INDIRECT("$"&K$4&ROW(K13)),INDIRECT($C13&K$5),1)))))
0 if current CZ inactive |  | Breakdown: | =IF(CZ_1=0,0,
Test for interpolation out of range |  |  | ,IF(OR(INDIRECT("$"&K$4&ROW(K13))>=MAX(INDIRECT($C13&K$5)),(INDIRECT("$"&K$4&ROW(K13))<MIN(INDIRECT($C13&K$5)))),"OUT OF RANGE", | compare current row, col I (ref from row4) to interpolation range, a named range formed from col C and row 5 "Heat_Pump_2007Par"
|  |  | INDEX(INDIRECT($C13&K$6), MATCH(INDIRECT("$"&K$4&ROW(K13)), INDIRECT($C13&K$5),1),K$7) +(INDEX(INDIRECT($C13&K$6), MATCH(INDIRECT("$"&K$4&ROW(K13)), INDIRECT($C13&K$5),1)+1,K$7) -INDEX(INDIRECT($C13&K$6), MATCH(INDIRECT("$"&K$4&ROW(K13)), INDIRECT($C13&K$5),1),K$7)) *(INDIRECT("$"&K$4&ROW(K13)) -INDEX(INDIRECT($C13&K$5), MATCH(INDIRECT("$"&K$4&ROW(K13)), INDIRECT($C13&K$5),1))) /(INDEX(INDIRECT($C13&K$5), MATCH(INDIRECT("$"&K$4&ROW(K13)), INDIRECT($C13&K$5),1)+1) -INDEX(INDIRECT($C13&K$5), MATCH(INDIRECT("$"&K$4&ROW(K13)), INDIRECT($C13&K$5),1))))) | this is an interpolation formula, given the size parameters in column "I" will look up the cost on HVAC comp using the KEY_2007_Par & KEY_2007Costs names on [HVAC Costs Comp], where KEY is the technology word in col C As long as the formula is relatively copied, it will work, if things are properly named on [HVAC Costs Comp] Name setup required for formula to reference: Key Equip Type name part in Col C System name/parameter in Col G Ref column for case size parameter in row 4 parameter name part in row 5 cost name part in row 6 Col A needs an x for items to be counted in summaries below Spot checking is best performed by manually reproducing the interpolation
Note:
Cost cells referred to in HVAC Costs Comp have the form:
XXX_2007_Costs
where:
|  |  | XXX | is the equipment type, and
|  |  | _2007_Costs | is a range that includes cost information for the base case that can be looked up
|  |  | XXX_2007_par | refers to the parameters related to the cost rows
The above are referenced for interpolation; Par = x; Costs = y
For now - leaving 2007 as reference to base and 2010 as reference to target; as changing all those names is problematic. These are internal name references; and the reference rows will be hidden in the public copy.

## HVAC Methodology
90.1 Cost Effectiveness - HVAC Cost Methodology
Mid Rise Apartment Split system cost vs. capacity
The regressions for bare costs + 10% (subcontractor cost level) are:
|  |  | material | labor
|  | C | 2690.6 | 2202.7
|  | x | -208.45 | -73.657
|  | x^2 | 17.693 | 6.1014
The costs above, developed in 2012, are updated with labor and
material inflation multipliers applied at the prototype cost level.
There are 6 addenda to 90.1-2019 with analyzed energy savings that affected the HVAC requirements in chapter 6 of 90.1.
Explanation of how these addenda are applied to the cost estimates is provided in the cost descriptions in the mechanical component and prototype worksheets and are not covered in this methodology narrative.
Note that the Mid-rise Apartment prototype has less extensive incremental mechanical costs and a simplified method is used to determine those costs based on simulated equipment capacities. Detail is shown at right.
The topic that is highlighted here is the costs developed to address changes in HVAC system and plant capacity between the 90.1-2019 and 90.1-2022 prototype models. The changes are due to changes in cooling and heating loads primarily because of changes in the interior lighting power allowance.
The HVAC capacity changes are a large part of the mechanical cost estimates. The costs were estimated for a range of equipment sizes corresponding to the models. The cost estimate sheet is laid out with 90.1-2019 and 90.1-2022 descriptions together for ease of comparison, followed by the related costs in adjacent sections. The costs in these two parts are the same when estimated as components with the exception of the ductwork and piping costs. Ductwork and piping cost results are presented in the HVAC cost component worksheet and the same costs are presented in the prototype specific cost worksheets. For the other capacity related inputs, the component costs are mapped to the prototype model information in the prototype worksheets.
The capacity related costs are organized with other related addenda in two sections, the upper portion for HVAC system related costs such as packaged variable air volume rooftop units and ductwork, and HVAC plant related costs such as chillers and piping.
In general, two manufacturers' equipment selections are included along with an average of the prototype costs, which is what is used for the cost estimate. The RS Means 2023 labor estimate is used for all cases. The material costs are usually similar to the costs used for the estimate except the material costs for air handling units (AHUs), both variable air volume and constant air volume units. The RS Means AHU equipment costs are substantially higher but it is not known what these costs include. Review of the air handler unit costs by Faithful+Gould, the primary mechanical cost estimator, with the suppliers who provided these costs, determined that the costs fit the equipment descriptions provided by PNNL including costs for the cabinet, fan, and cooling and heating coils. The lower costs from the consultant and suppliers is used. Note that where material costs were developed in prior years, they have been updated to 2023 using inflation factors specific to the equipment type that are based on a comparison of material costs in the RS Means 2012, 2014, and 2023 cost handbooks.
The costs are assigned to the prototypes using formulas that extract the corresponding component costs to the model capacity inputs and outputs as appropriate. A few cost items are simply pasted into the component costs such as the ductwork and piping costs, which were developed specifically for a given prototype and climate. The formulas are complex and include interpolation between the component cost values for selected capacities. The formulas are converted to values in this version of the spreadsheet. This method is believed to provide representative costs for the category of buildings for each prototype, at least those with some similarity in building size, shape and HVAC system type, rather than just the specific inputs and output capacities of these prototype models.
Generally, there was a decrease in costs due to a decrease in capacity and airflow for mechanical equipment, thus offsetting increased costs from addenda that added costs.
Piping and Ductwork Costs
Piping and ductwork costs (and some controls costs) were developed by Solarc, an integrated architectural, mechanical, electrical and plumbing design consultant, who specialize in green buildings. This effort includes developing schematic level single line representative layout of the ductwork and piping for each prototype. Detailed costs for these at the level of duct and pipe size and length, and all fittings were developed based on the component by component costs from RS Means 2012. In some cases, the multiple costs are used to develop regressions for material and labor costs as a function of unit capacity or transfer fluid flow. Where these costs were developed in 2012, they have been updated to 2023 using inflation factors specific to the equipment type that are based on a comparison of material costs in the RS Means 2012 and 2023 cost handbooks. Acquiring these costs from individual suppliers was cost prohibitive for the project budget and would diverge greatly between suppliers according to Solarc. Solarc identified that for some prototypes and climates, the differences in capacity were so close that there were very limited cost differences and separate costs were not developed. This is why some of these costs are identical to each other between climate zones for a given prototype.
An incremental cost was determined for changes in required apartment system capacity. Individual unit capacities from the prototype model were evaluated for a cost for both the baseline and target runs. The difference represented the cost change. Individual unit costs were based on data from RS Means Mechanical Cost Data, 2012 for split -system air cooled air conditioners with a DX evaporator cooling coil in a heating and cooling unit with ducted supply air. (Means D3050 165). Data from several typical applications were tabulated to arrive at material and labor costs in terms of $ per ton of cooling. Outliers were removed and a curve fit developed.

## HVAC Costs Comp
[16 empty] | 90.1 Cost Effectiveness - HVAC Costs by Component |  |  |  |  | Hide | [10 empty] | Find Rows
Incremental Costs for verification only
[16 empty] | Hide rows colored orange | Range name extensions | _2007Par | _2007Costs | _2010Par | _2010Costs | [13 empty] | 3 | [6 empty] | 10 | [31 empty] | incremental costs are captured in total cost calculations
Not used - retain to avoid disrupting other | [15 empty] | Item and Addenda | Base Code | [5 empty] | Target Code | [10 empty] | Base Code - costs (no costs if just an added item in Target Code ) | [19 empty] | Target Code - costs with added or changed code provisions (or see description if costs are just tied to change in capacity). | [19 empty] | Incremental Costs
cell references | [28 empty] | Other Parameters |  |  |  |  | New Constrution | [7 empty] | Maintenance | Replacement | [10 empty] | New Construction | [8 empty] | Maintenance | Replacement
[17 empty] | Description | Source of Information | Manufacturer | Model and Series | Series | 90.1-2019 Cost Parameter | Description | Source of Information (RS Means Mechanical Cost Data 2014 used for labor unless stated) | Manufacturer | Model and Series | Not Used | 90.1-2022 Cost Parameter | Appropriate Other Parameters |  |  |  | 2012 to 2023 Material inflation adjustment | Material Subtotal | Labor Crew Type | Labor ($/Hr) | Labor (Hours) | Labor Subtotal | Construction Equipment | Cost Adjustments (OH&P, G-C, GC, infl., contingency etc.) | Total | Annual | Replacement Life (years) | Not Used | Material Subtotal | Labor Crew Type | Labor ($/Hr) | Labor (Hours) | Labor Subtotal | Construction Equipment | Cost Adjustments (OH&P, G-C, GC, contingency etc.) | Total | Not Used | Material Subtotal | Labor Crew Type | Labor ($/Hr) | Labor (Hours) | Labor Subtotal | Construction Equipment | Cost Adjustments (OH&P, G-C, GC, cont'gcy., infl. etc.) |  | Total Cost | Annual | Replacement Life (years) | Not Used | Material Subtotal | Labor Crew Type | Labor ($/Hr) | Labor (Hours) | Labor Subtotal | Construction Equipment | Cost Adjustments (OH&P, G-C, GC, contingency etc.) | Total Cost | New Construction 2019 minus 2016
[16 empty] | HVAC System Costs Associated with Capacity Changes | Costs used to account for changes in system capacity due to other changes in 90.1, primarily lighting. Costs are base costs for system that meets 90.1 standard requirements before application of addenda. This cost is without an economizer or ERV as they are not always required. Systems have DDC control. These costs are current or have been adjusted for inflation to current prices. | Costs developed in 2012 are updated with inflation factors based on Means to bring them forward. |  |  |  |  | Costs shown are the same for base code and target code. Difference in cost for capacity between base and target models is without any of the addenda changes. Difference in cost by capacity will be calculated in final summary sheet based on the base and target capacity for a particular system in a prototype and climate zone.
[16 empty] | VAV Air Handling Units | VAV air handling units with chilled and hot water coils, built-up, or rooftop as available, based on supply airflow. This equipment meets the general requirements of the base code that do not change in the target code and are commonly available in the market. VFD used to provide variable airflow. This cost is without an economizer or ERV as they are not always required. Coils selected in mid-range of coil sizes for unit sized based on supply airflow. | Equipment information below. Labor hours from RS Means 2023 Mechanical Cost Data. Packaged, Outdoor Type, Central-Station AHU, 23 74 13.10 |  |  |  | Supply Airflow, cfm | Same as for base code for same size units. |  |  |  |  | Supply Airflow, cfm |  |  |  |  | Inflation from 2012 to 2023
[17 empty] | Manufacturer 1 | Faithful+Gould - Carrier | Carrier | 39 M |  | 16000 | [5 empty] | 16000 |  |  |  |  | 1.242 | 20250 | Q-6 | 67.72 | 64.5518 | 4371.4479 |  | 21728.8451 | 46350.2929 |  | 15 |  | 20250 | Q-6 | 67.72 | 106.5105 | 7212.889 |  | 29149.1983 | 56612.0874 |  | 20250 | Q-6 | 67.72 | 64.5518 | 4371.4479 |  | 21728.8451 |  | 46350.2929 |  | 15 |  | 20250 | Q-6 | 67.72 | 106.5105 | 7212.889 |  | 29149.1983 | 56612.0874 | 0
[18 empty] | Airtech Thermex | Carrier | 39 M |  | 20000 | [5 empty] | 20000 |  |  |  |  | 1.242 | 21600 | Q-6 | 67.72 | 82.759 | 5604.4395 |  | 24086.5013 | 51290.9407 |  | 15 |  | 21600 | Q-6 | 67.72 | 136.5523 | 9247.3251 |  | 32786.5357 | 63633.8608 |  | 21600 | Q-6 | 67.72 | 82.759 | 5604.4395 |  | 24086.5013 |  | 51290.9407 |  | 15 |  | 21600 | Q-6 | 67.72 | 136.5523 | 9247.3251 |  | 32786.5357 | 63633.8608 | 0
[18 empty] | Airtech Thermex, Minneapolis MN | Carrier | 39 M |  | 25000 | [5 empty] | 25000 |  |  |  |  | 1.242 | 27000 | Q-6 | 67.72 | 101.3795 | 6865.4197 |  | 29972.8331 | 63838.2529 |  | 15 |  | 27000 | Q-6 | 67.72 | 167.2762 | 11327.9426 |  | 40731.0485 | 79058.9911 |  | 27000 | Q-6 | 67.72 | 101.3795 | 6865.4197 |  | 29972.8331 |  | 63838.2529 |  | 15 |  | 27000 | Q-6 | 67.72 | 167.2762 | 11327.9426 |  | 40731.0485 | 79058.9911 | 0
[19 empty] | Carrier | 39 M |  | 30000 | [5 empty] | 30000 |  |  |  |  | 1.242 | 32400 | Q-6 | 67.72 | 120 | 8126.4 |  | 35859.165 | 76385.565 |  | 15 |  | 32400 | Q-6 | 67.72 | 198 | 13408.56 |  | 48675.5613 | 94484.1213 |  | 32400 | Q-6 | 67.72 | 120 | 8126.4 |  | 35859.165 |  | 76385.565 |  | 15 |  | 32400 | Q-6 | 67.72 | 198 | 13408.56 |  | 48675.5613 | 94484.1213 | 0
[19 empty] | Carrier | 39 M |  | 40000 | [5 empty] | 40000 |  |  |  |  | 1.242 | 40500 | Q-6 | 67.72 | 157.241 | 10648.3605 |  | 45297.3934 | 96445.754 |  | 15 |  | 40500 | Q-6 | 67.72 | 259.4477 | 17569.7949 |  | 61726.708 | 119796.5029 |  | 40500 | Q-6 | 67.72 | 157.241 | 10648.3605 |  | 45297.3934 |  | 96445.754 |  | 15 |  | 40500 | Q-6 | 67.72 | 259.4477 | 17569.7949 |  | 61726.708 | 119796.5029 | 0
[19 empty] | extrapolated |  |  | 50000 | [5 empty] | 50000 |  |  |  |  | 1.242 | 48600 | Q-6 | 67.72 | 194.482 | 13170.321 |  | 54735.6219 | 116505.9429 |  | 15 |  | 48600 | Q-6 | 67.72 | 320.8953 | 21731.0297 |  | 74777.8548 | 145108.8845 |  | 48600 | Q-6 | 67.72 | 194.482 | 13170.321 |  | 54735.6219 |  | 116505.9429 |  | 15 |  | 48600 | Q-6 | 67.72 | 320.8953 | 21731.0297 |  | 74777.8548 | 145108.8845 | 0
[17 empty] | Manufacturer 2 | Faithful+Gould - Trane price estimates for range of sizes | Trane | Performance Climate Changer |  | 16000 | [5 empty] | 16000 | 562.5 | 40 |  |  | 1.242 | 22500 | Q-6 | 67.72 | 64.5518 | 4371.4479 |  | 23674.2078 | 50545.6557 |  | 15 |  | 22500 | Q-6 | 67.72 | 106.5105 | 7212.889 |  | 31514.0973 | 61226.9864 |  | 22500 | Q-6 | 67.72 | 64.5518 | 4371.4479 |  | 23674.2078 |  | 50545.6557 |  | 15 |  | 22500 | Q-6 | 67.72 | 106.5105 | 7212.889 |  | 31514.0973 | 61226.9864 | 0
[18 empty] | Minneapolis MN | Trane | Performance Climate Changer |  | 20000 | [5 empty] | 20000 | 480 | 50 |  |  | 1.242 | 24000 | Q-6 | 67.72 | 82.759 | 5604.4395 |  | 26161.5548 | 55765.9943 |  | 15 |  | 24000 | Q-6 | 67.72 | 136.5523 | 9247.3251 |  | 35309.0946 | 68556.4198 |  | 24000 | Q-6 | 67.72 | 82.759 | 5604.4395 |  | 26161.5548 |  | 55765.9943 |  | 15 |  | 24000 | Q-6 | 67.72 | 136.5523 | 9247.3251 |  | 35309.0946 | 68556.4198 | 0
[19 empty] | Trane | Performance Climate Changer |  | 25000 | [5 empty] | 25000 | 480 | 62.5 |  |  | 1.242 | 30000 | Q-6 | 67.72 | 101.3795 | 6865.4197 |  | 32566.6501 | 69432.0698 |  | 15 |  | 30000 | Q-6 | 67.72 | 167.2762 | 11327.9426 |  | 43884.2472 | 85212.1897 |  | 30000 | Q-6 | 67.72 | 101.3795 | 6865.4197 |  | 32566.6501 |  | 69432.0698 |  | 15 |  | 30000 | Q-6 | 67.72 | 167.2762 | 11327.9426 |  | 43884.2472 | 85212.1897 | 0
[19 empty] | Trane | Performance Climate Changer |  | 30000 | [5 empty] | 30000 | 480 | 65 |  |  | 1.242 | 31200 | Q-6 | 67.72 | 120 | 8126.4 |  | 34821.6382 | 74148.0382 |  | 15 |  | 31200 | Q-6 | 67.72 | 198 | 13408.56 |  | 47414.2818 | 92022.8418 |  | 31200 | Q-6 | 67.72 | 120 | 8126.4 |  | 34821.6382 |  | 74148.0382 |  | 15 |  | 31200 | Q-6 | 67.72 | 198 | 13408.56 |  | 47414.2818 | 92022.8418 | 0
[19 empty] | Trane | Performance Climate Changer |  | 40000 | [5 empty] | 40000 | 450 | 97.5 |  |  | 1.242 | 43875 | Q-6 | 67.72 | 157.241 | 10648.3605 |  | 48215.4375 | 102738.798 |  | 15 |  | 43875 | Q-6 | 67.72 | 259.4477 | 17569.7949 |  | 65274.0565 | 126718.8514 |  | 43875 | Q-6 | 67.72 | 157.241 | 10648.3605 |  | 48215.4375 |  | 102738.798 |  | 15 |  | 43875 | Q-6 | 67.72 | 259.4477 | 17569.7949 |  | 65274.0565 | 126718.8514 | 0
[19 empty] | extrapolated |  |  | 50000 | [5 empty] | 50000 | 450 | 105 |  |  | 1.242 | 56550 | Q-6 | 67.72 | 194.482 | 13170.321 |  | 61609.2369 | 131329.5579 |  | 15 |  | 56550 | Q-6 | 67.72 | 320.8953 | 21731.0297 |  | 83133.8313 | 161414.861 |  | 56550 | Q-6 | 67.72 | 194.482 | 13170.321 |  | 61609.2369 |  | 131329.5579 |  | 15 |  | 56550 | Q-6 | 67.72 | 320.8953 | 21731.0297 |  | 83133.8313 | 161414.861 | 0
[16 empty] | VAV_AHU | Average of two manufacturers | [15 empty] | 1.242 | [6 empty] | 0 | [10 empty] | 0 | [8 empty] | 0
[18 empty] | Faithful+Gould |  |  |  | 16000 | [5 empty] | 16000 |  |  |  |  | 1.242 | 21375 | Q-6 | 67.72 | 64.5518 | 4371.4479 |  | 22701.5264 | 48447.9743 |  | 15 |  | 21375 | Q-6 | 67.72 | 106.5105 | 7212.889 |  | 30331.6478 | 58919.5369 |  | 21375 | Q-6 | 67.72 | 64.5518 | 4371.4479 |  | 22701.5264 |  | 48447.9743 |  | 15 |  | 21375 | Q-6 | 67.72 | 106.5105 | 7212.889 |  | 30331.6478 | 58919.5369 | 0
[16 empty] | used for load changes | [5 empty] | 20000 | [5 empty] | 20000 |  |  |  |  | 1.242 | 22800 | Q-6 | 67.72 | 82.759 | 5604.4395 |  | 25124.0281 | 53528.4675 |  | 15 |  | 22800 | Q-6 | 67.72 | 136.5523 | 9247.3251 |  | 34047.8152 | 66095.1403 |  | 22800 | Q7 | 67.72 | 82.759 | 5604.4395 |  | 25124.0281 |  | 53528.4675 |  | 15 |  | 22800 | Q-6 | 67.72 | 136.5523 | 9247.3251 |  | 34047.8152 | 66095.1403 | 0
[22 empty] | 25000 | [5 empty] | 25000 |  |  |  |  | 1.242 | 28500 | Q-6 | 67.72 | 101.3795 | 6865.4197 |  | 31269.7416 | 66635.1614 |  | 15 |  | 28500 | Q-6 | 67.72 | 167.2762 | 11327.9426 |  | 42307.6478 | 82135.5904 |  | 28500 | Q7 | 67.72 | 101.3795 | 6865.4197 |  | 31269.7416 |  | 66635.1614 |  | 15 |  | 28500 | Q-6 | 67.72 | 167.2762 | 11327.9426 |  | 42307.6478 | 82135.5904 | 0
[22 empty] | 30000 | [5 empty] | 30000 |  |  |  |  | 1.242 | 31800 | Q-6 | 67.72 | 120 | 8126.4 |  | 35340.4016 | 75266.8016 |  | 15 |  | 31800 | Q-6 | 67.72 | 198 | 13408.56 |  | 48044.9215 | 93253.4815 |  | 31800 | Q7 | 67.72 | 120 | 8126.4 |  | 35340.4016 |  | 75266.8016 |  | 15 |  | 31800 | Q-6 | 67.72 | 198 | 13408.56 |  | 48044.9215 | 93253.4815 | 0
[22 empty] | 40000 | [5 empty] | 40000 |  |  |  |  | 1.242 | 42187.5 | Q-6 | 67.72 | 157.241 | 10648.3605 |  | 46756.4155 | 99592.276 |  | 15 |  | 42187.5 | Q-6 | 67.72 | 259.4477 | 17569.7949 |  | 63500.3823 | 123257.6771 |  | 42187.5 | Q7 | 67.72 | 157.241 | 10648.3605 |  | 46756.4155 |  | 99592.276 |  | 15 |  | 42187.5 | Q-6 | 67.72 | 259.4477 | 17569.7949 |  | 63500.3823 | 123257.6771 | 0
[22 empty] | 50000 | [5 empty] | 50000 |  |  |  |  | 1.242 | 52575 | Q-6 | 67.72 | 194.482 | 13170.321 |  | 58172.4294 | 123917.7504 |  | 15 |  | 52575 | Q-6 | 67.72 | 320.8953 | 21731.0297 |  | 78955.843 | 153261.8728 |  | 52575 | Q7 | 67.72 | 194.482 | 13170.321 |  | 58172.4294 |  | 123917.7504 |  | 15 |  | 52575 | Q-6 | 67.72 | 320.8953 | 21731.0297 |  | 78955.843 | 153261.8728 | 0
1.242
[16 empty] | CAV Air Handling Units | CAV air handling units with chilled and hot water coils, built-up, or rooftop as available based on supply airflow. This equipment meets the general requirements of the base code that do not change in the target code and are commonly available in the market. This cost is without an economizer or ERV as they are not always required. Coils selected in mid-range of coil sizes for unit sized based on supply airflow. Duct work, diffusers etc. not included. | Equipment information below. Labor hours from RS Means 2023 Mechanical Cost Data. Packaged, Outdoor Type, Central-Station AHU, 23 74 13.10 31XX |  |  |  | Supply Airflow, cfm | Same as for base code for same size units. |  |  |  |  | Supply Airflow, cfm |  |  |  |  | Inflation from 2012 to 2023
[17 empty] | Manufacturer 1 | Faithful+Gould | Carrier | 39 L |  | 400 | [5 empty] | 1650 |  |  |  |  | 1.239 | 3060 | Q6 | 67.72 | 23.2547 | 1574.8105 |  | 4152.3721 | 8787.1827 |  | 15 |  | 3060 | Q6 | 67.72 | 38.3703 | 2598.4374 |  | 6034.5011 | 11692.9385 |  | 3060 | Q6 | 67.72 | 23.2547 | 1574.8105 |  | 4152.3721 |  | 8787.1827 |  | 15 |  | 3060 | Q6 | 67.72 | 38.3703 | 2598.4374 |  | 6034.5011 | 11692.9385 | 0
[18 empty] | Airtech Thermex |  | 39 L |  | 2000 | [5 empty] | 2000 |  |  |  |  | 1.239 | 9000 | Q6 | 67.72 | 24 | 1625.28 |  | 9310.1043 | 19935.3843 |  | 15 |  | 9000 | Q6 | 67.72 | 39.6 | 2681.712 |  | 12339.2107 | 24020.9227 |  | 9000 | Q6 | 67.72 | 24 | 1625.28 |  | 9310.1043 |  | 19935.3843 |  | 15 |  | 9000 | Q6 | 67.72 | 39.6 | 2681.712 |  | 12339.2107 | 24020.9227 | 0
[18 empty] | Minneapolis MN |  | 39 L |  | 4000 | [5 empty] | 4000 |  |  |  |  | 1.239 | 10350 | Q6 | 67.72 | 28.2587 | 1913.6769 |  | 10749.6855 | 23013.3624 |  | 15 |  | 10350 | Q6 | 67.72 | 46.6268 | 3157.5669 |  | 14270.3455 | 27777.9124 |  | 10350 | Q6 | 67.72 | 28.2587 | 1913.6769 |  | 10749.6855 |  | 23013.3624 |  | 15 |  | 10350 | Q6 | 67.72 | 46.6268 | 3157.5669 |  | 14270.3455 | 27777.9124 | 0
[18 empty] | Carrier |  | 39 L |  | 8000 | [5 empty] | 8000 |  |  |  |  | 1.239 | 13050 | Q6 | 67.72 | 39.8476 | 2698.4795 |  | 13829.6778 | 29578.1572 |  | 15 |  | 13050 | Q6 | 67.72 | 65.7485 | 4452.4911 |  | 18506.8642 | 36009.3554 |  | 13050 | Q6 | 67.72 | 39.8476 | 2698.4795 |  | 13829.6778 |  | 29578.1572 |  | 15 |  | 13050 | Q6 | 67.72 | 65.7485 | 4452.4911 |  | 18506.8642 | 36009.3554 | 0
[20 empty] | 39 M |  | 16000 | [5 empty] | 16000 |  |  |  |  | 1.239 | 18900 | Q6 | 67.72 | 62.8296 | 4254.8205 |  | 20363.9018 | 43518.7223 |  | 15 |  | 18900 | Q6 | 67.72 | 103.6688 | 7020.4538 |  | 27426.7874 | 53347.2412 |  | 18900 | Q6 | 67.72 | 62.8296 | 4254.8205 |  | 20363.9018 |  | 43518.7223 |  | 15 |  | 18900 | Q6 | 67.72 | 103.6688 | 7020.4538 |  | 27426.7874 | 53347.2412 | 0
[20 empty] | 39 M |  | 20000 | [5 empty] | 20000 |  |  |  |  | 1.239 | 20700 | Q6 | 67.72 | 80 | 5417.6 |  | 23034.7346 | 49152.3346 |  | 15 |  | 20700 | Q6 | 67.72 | 132 | 8939.04 |  | 31401.8613 | 61040.9013 |  | 20700 | Q6 | 67.72 | 80 | 5417.6 |  | 23034.7346 |  | 49152.3346 |  | 15 |  | 20700 | Q6 | 67.72 | 132 | 8939.04 |  | 31401.8613 | 61040.9013 | 0
[17 empty] | Manufacturer 2 | Faithful+Gould | Trane | Performance |  | 1650 | [5 empty] | 1650 |  | 1650 |  |  | 1.239 | 3400 | Q6 | 67.72 | 23.2547 | 1574.8105 |  | 4444.8067 | 9419.6173 |  | 15 |  | 3400 | Q6 | 67.72 | 38.3703 | 2598.4374 |  | 6390.1792 | 12388.6165 |  | 3400 | Q6 | 67.72 | 23.2547 | 1574.8105 |  | 4444.8067 |  | 9419.6173 |  | 15 |  | 3400 | Q6 | 67.72 | 38.3703 | 2598.4374 |  | 6390.1792 | 12388.6165 | 0
[18 empty] | Trane Corp. |  | Performance |  | 2000 | [5 empty] | 2000 |  | 0 |  |  | 1.239 | 10000 | Q6 | 67.72 | 24 | 1625.28 |  | 10170.2061 | 21795.4861 |  | 15 |  | 10000 | Q6 | 67.72 | 39.6 | 2681.712 |  | 13385.3227 | 26067.0347 |  | 10000 | Q6 | 67.72 | 24 | 1625.28 |  | 10170.2061 |  | 21795.4861 |  | 15 |  | 10000 | Q6 | 67.72 | 39.6 | 2681.712 |  | 13385.3227 | 26067.0347 | 0
[18 empty] | Minneapolis MN |  | Performance |  | 4000 | [5 empty] | 4000 |  | 0 |  |  | 1.239 | 11500 | Q6 | 67.72 | 28.2587 | 1913.6769 |  | 11738.8026 | 25152.4795 |  | 15 |  | 11500 | Q6 | 67.72 | 46.6268 | 3157.5669 |  | 15473.3742 | 30130.9411 |  | 11500 | Q6 | 67.72 | 28.2587 | 1913.6769 |  | 11738.8026 |  | 25152.4795 |  | 15 |  | 11500 | Q6 | 67.72 | 46.6268 | 3157.5669 |  | 15473.3742 | 30130.9411 | 0
[22 empty] | 8000 | [5 empty] | 8000 |  | 0 |  |  | 1.239 | 14500 | Q6 | 67.72 | 39.8476 | 2698.4795 |  | 15076.8253 | 32275.3048 |  | 15 |  | 14500 | Q6 | 67.72 | 65.7485 | 4452.4911 |  | 20023.7266 | 38976.2177 |  | 14500 | Q6 | 67.72 | 39.8476 | 2698.4795 |  | 15076.8253 |  | 32275.3048 |  | 15 |  | 14500 | Q6 | 67.72 | 65.7485 | 4452.4911 |  | 20023.7266 | 38976.2177 | 0
[20 empty] | Performance |  | 16000 | [5 empty] | 16000 |  | 0 |  |  | 1.239 | 21000 | Q6 | 67.72 | 62.8296 | 4254.8205 |  | 22170.1155 | 47424.936 |  | 15 |  | 21000 | Q6 | 67.72 | 103.6688 | 7020.4538 |  | 29623.6225 | 57644.0763 |  | 21000 | Q6 | 67.72 | 62.8296 | 4254.8205 |  | 22170.1155 |  | 47424.936 |  | 15 |  | 21000 | Q6 | 67.72 | 103.6688 | 7020.4538 |  | 29623.6225 | 57644.0763 | 0
[20 empty] | Performance |  | 20000 | [5 empty] | 20000 |  | 20000 |  |  | 1.239 | 20700 | Q6 | 67.72 | 80 | 5417.6 |  | 23034.7346 | 49152.3346 |  | 15 |  | 20700 | Q6 | 67.72 | 132 | 8939.04 |  | 31401.8613 | 61040.9013 |  | 20700 | Q6 | 67.72 | 80 | 5417.6 |  | 23034.7346 |  | 49152.3346 |  | 15 |  | 20700 | Q6 | 67.72 | 132 | 8939.04 |  | 31401.8613 | 61040.9013 | 0
[16 empty] | CAV_AHU | Average of two manufacturers | [15 empty] | 1.239 | [6 empty] | 0 | [10 empty] | 0 | [8 empty] | 0
[22 empty] | 400 | [5 empty] | 1650 |  |  |  |  | 1.239 | 3230 | Q6 | 67.72 | 23.2547 | 1574.8105 |  | 4298.5894 | 9103.4 |  | 15 |  | 3230 | Q6 | 67.72 | 38.3703 | 2598.4374 |  | 6212.3401 | 12040.7775 |  | 3230 | Q6 | 67.72 | 23.2547 | 1574.8105 |  | 4298.5894 |  | 9103.4 | 0 | 15 |  | 3230 | Q6 | 67.72 | 38.3703 | 2598.4374 |  | 6212.3401 | 12040.7775 | 0
[16 empty] | used for load changes | [5 empty] | 2000 | [5 empty] | 2000 |  |  |  |  | 1.239 | 9500 | Q6 | 67.72 | 24 | 1625.28 |  | 9740.1552 | 20865.4352 |  | 15 |  | 9500 | Q6 | 67.72 | 39.6 | 2681.712 |  | 12862.2667 | 25043.9787 |  | 9500 | Q6 | 67.72 | 24 | 1625.28 |  | 9740.1552 |  | 20865.4352 | 0 | 15 |  | 9500 | Q6 | 67.72 | 39.6 | 2681.712 |  | 12862.2667 | 25043.9787 | 0
[22 empty] | 4000 | [5 empty] | 4000 |  |  |  |  | 1.239 | 10925 | Q6 | 67.72 | 28.2587 | 1913.6769 |  | 11244.244 | 24082.9209 |  | 15 |  | 10925 | Q6 | 67.72 | 46.6268 | 3157.5669 |  | 14871.8599 | 28954.4268 |  | 10925 | Q6 | 67.72 | 28.2587 | 1913.6769 |  | 11244.244 |  | 24082.9209 | 0 | 15 |  | 10925 | Q6 | 67.72 | 46.6268 | 3157.5669 |  | 14871.8599 | 28954.4268 | 0
[22 empty] | 8000 | [5 empty] | 8000 |  |  |  |  | 1.239 | 13775 | Q6 | 67.72 | 39.8476 | 2698.4795 |  | 14453.2516 | 30926.731 |  | 15 |  | 13775 | Q6 | 67.72 | 65.7485 | 4452.4911 |  | 19265.2954 | 37492.7865 |  | 13775 | Q6 | 67.72 | 39.8476 | 2698.4795 |  | 14453.2516 |  | 30926.731 | 0 | 15 |  | 13775 | Q6 | 67.72 | 65.7485 | 4452.4911 |  | 19265.2954 | 37492.7865 | 0
[22 empty] | 12000 | [5 empty] | 12000 |  |  |  |  | 1.239 | 16625 | Q6 | 67.72 | 51.1072 | 3460.9796 |  | 17640.7263 | 37726.7059 |  | 15 |  | 16625 | Q6 | 67.72 | 84.3269 | 5710.6163 |  | 23618.6044 | 45954.2207 |  | 16625 | Q6 | 67.72 | 51.1072 | 3460.9796 |  | 17640.7263 |  | 37726.7059 | 0 | 15 |  | 16625 | Q6 | 67.72 | 84.3269 | 5710.6163 |  | 23618.6044 | 45954.2207 | 0
[22 empty] | 16000 | [5 empty] | 16000 |  |  |  |  | 1.239 | 19950 | Q6 | 67.72 | 62.8296 | 4254.8205 |  | 21267.0086 | 45471.8292 |  | 15 |  | 19950 | Q6 | 67.72 | 103.6688 | 7020.4538 |  | 28525.2049 | 55495.6588 |  | 19950 | Q6 | 67.72 | 62.8296 | 4254.8205 |  | 21267.0086 |  | 45471.8292 | 0 | 15 |  | 19950 | Q6 | 67.72 | 103.6688 | 7020.4538 |  | 28525.2049 | 55495.6588 | 0
[22 empty] | 20000 | [5 empty] | 20000 |  |  |  |  | 1.239 | 20700 | Q6 | 67.72 | 80 | 5417.6 |  | 23034.7346 | 49152.3346 |  | 15 |  | 20700 | Q6 | 67.72 | 132 | 8939.04 |  | 31401.8613 | 61040.9013 |  | 20700 | Q6 | 67.72 | 80 | 5417.6 |  | 23034.7346 |  | 49152.3346 | 0 | 15 |  | 20700 | Q6 | 67.72 | 132 | 8939.04 |  | 31401.8613 | 61040.9013 | 0
[16 empty] | Packaged VAV DX Rooftoop Unit | Packaged VAV rooftop system with gas furnace. This equipment meets the general requirements of the base code that do not change in the target code and are commonly available in the market. This cost is without an economizer or ERV as they are not always required. | Equipment information below. Labor hours from RS Means 2023 Mechanical Cost Data. Single zone, electric cool, gas heat, VAV, 23 74 33.10 41XX |  |  |  | Cooling Capacity, Tons | Same as for base code for same size units. |  |  |  |  | Cooling Capacity, Tons |  |  |  |  | Inflation from 2012 to 2023 | [32 empty] | 0
[17 empty] | Manufacturer 1 | Faithful+Gould | Carrier | 48 A |  | 20 | [5 empty] | 20 |  |  |  |  | 1.147 | 19800 | Q6 | 67.72 | 56.5667 | 3830.6979 |  | 17993.7531 | 41624.451 |  | 15 |  | 19800 | Q6 | 67.72 | 93.3351 | 6320.6515 |  | 24596.9764 | 50717.6279 |  | 19800 | Q6 | 67.72 | 56.5667 | 3830.6979 |  | 17993.7531 |  | 41624.451 | 0 | 15 |  | 19800 | Q6 | 67.72 | 93.3351 | 6320.6515 |  | 24596.9764 | 50717.6279 | 0
[18 empty] | Airtech Thermex |  | 48 A |  | 25 | [5 empty] | 25 |  |  |  |  | 1.147 | 23400 | Q7 | 69.05 | 66.116 | 4565.3098 |  | 21302.1503 | 49267.4601 |  | 15 |  | 23400 | Q7 | 69.05 | 109.0914 | 7532.7612 |  | 29137.7419 | 60070.5031 |  | 23400 | Q7 | 69.05 | 66.116 | 4565.3098 |  | 21302.1503 |  | 49267.4601 | 0 | 15 |  | 23400 | Q7 | 69.05 | 109.0914 | 7532.7612 |  | 29137.7419 | 60070.5031 | 0
[18 empty] | Minneapolis MN |  | 48 A |  | 30 | [5 empty] | 30 |  |  |  |  | 1.147 | 23850 | Q7 | 69.05 | 78.744 | 5437.2732 |  | 22468.9128 | 51756.186 |  | 15 |  | 23850 | Q7 | 69.05 | 129.9276 | 8971.5008 |  | 31108.9596 | 63930.4604 |  | 23850 | Q7 | 69.05 | 78.744 | 5437.2732 |  | 22468.9128 |  | 51756.186 | 0 | 15 |  | 23850 | Q7 | 69.05 | 129.9276 | 8971.5008 |  | 31108.9596 | 63930.4604 | 0
[18 empty] | Carrier |  | 48 A |  | 40 | [5 empty] | 40 |  |  |  |  | 1.147 | 31950 | Q7 | 69.05 | 104 | 7181.2 |  | 30000.7142 | 69131.9142 |  | 15 |  | 31950 | Q7 | 69.05 | 171.6 | 11848.98 |  | 41489.4991 | 85288.4791 |  | 31950 | Q7 | 69.05 | 104 | 7181.2 |  | 30000.7142 |  | 69131.9142 | 0 | 15 |  | 31950 | Q7 | 69.05 | 171.6 | 11848.98 |  | 41489.4991 | 85288.4791 | 0
[17 empty] | Manufacturer 2 | Faithful+Gould | Trane | YCD |  | 20 | [5 empty] | 20 |  |  |  |  | 1.147 | 19500 | Q6 | 67.72 | 56.5667 | 3830.6979 |  | 17777.1583 | 41107.8561 |  | 15 |  | 19500 | Q6 | 67.72 | 93.3351 | 6320.6515 |  | 24328.7221 | 50149.3736 |  | 19500 | Q6 | 67.72 | 56.5667 | 3830.6979 |  | 17777.1583 |  | 41107.8561 | 0 | 15 |  | 19500 | Q6 | 67.72 | 93.3351 | 6320.6515 |  | 24328.7221 | 50149.3736 | 0
[18 empty] | Trane Corp. |  | YCD |  | 25 | [5 empty] | 25 |  |  |  |  | 1.147 | 23125 | Q7 | 69.05 | 66.116 | 4565.3098 |  | 21103.605 | 48793.9148 |  | 15 |  | 23125 | Q7 | 69.05 | 109.0914 | 7532.7612 |  | 28891.8421 | 59549.6033 |  | 23125 | Q7 | 69.05 | 66.116 | 4565.3098 |  | 21103.605 |  | 48793.9148 | 0 | 15 |  | 23125 | Q7 | 69.05 | 109.0914 | 7532.7612 |  | 28891.8421 | 59549.6033 | 0
[18 empty] | Minneapolis MN |  | YCD |  | 30 | [5 empty] | 30 |  |  |  |  | 1.147 | 30000 | Q7 | 69.05 | 78.744 | 5437.2732 |  | 26909.1073 | 62346.3805 |  | 15 |  | 30000 | Q7 | 69.05 | 129.9276 | 8971.5008 |  | 36608.1735 | 75579.6743 |  | 30000 | Q7 | 69.05 | 78.744 | 5437.2732 |  | 26909.1073 |  | 62346.3805 | 0 | 15 |  | 30000 | Q7 | 69.05 | 129.9276 | 8971.5008 |  | 36608.1735 | 75579.6743 | 0
[18 empty] | Trane |  | YCD |  | 40 | [5 empty] | 40 |  |  |  |  | 1.147 | 39000 | Q7 | 69.05 | 104 | 7181.2 |  | 35090.6932 | 81271.8932 |  | 15 |  | 39000 | Q7 | 69.05 | 171.6 | 11848.98 |  | 47793.4761 | 98642.4561 |  | 39000 | Q7 | 69.05 | 104 | 7181.2 |  | 35090.6932 |  | 81271.8932 | 0 | 15 |  | 39000 | Q7 | 69.05 | 171.6 | 11848.98 |  | 47793.4761 | 98642.4561 | 0
[16 empty] | VAV_DX | Average of two manufacturers | [15 empty] | 1.147 | [6 empty] | 0 |  |  |  |  | 0 | [5 empty] | 0 | [8 empty] | 0
[18 empty] | 15 ton unit prorated from 20 ton per Means 23 74 33.10 |  |  |  | 15 | [5 empty] | 15 |  |  |  |  | 1.147 | 14478.9474 | Q6 | 67.72 | 48.0159 | 3251.6389 |  | 13592.9699 | 31323.5562 |  | 15 |  | 14478.9474 | Q6 | 67.72 | 79.2263 | 5365.2042 |  | 18797.1489 | 38641.3004 |  | 14478.9474 | Q6 | 67.72 | 48.0159 | 3251.6389 |  | 13592.9699 |  | 31323.5562 | 0 | 15 |  | 14478.9474 | Q6 | 67.72 | 79.2263 | 5365.2042 |  | 18797.1489 | 38641.3004 | 0
[16 empty] | used for load changes | [5 empty] | 20 | [5 empty] | 20 |  |  |  |  | 1.147 | 19650 | Q6 | 67.72 | 56.5667 | 3830.6979 |  | 17885.4557 | 41366.1536 |  | 15 |  | 19650 | Q6 | 67.72 | 93.3351 | 6320.6515 |  | 24462.8492 | 50433.5008 |  | 19650 | Q6 | 67.72 | 56.5667 | 3830.6979 |  | 17885.4557 |  | 41366.1536 | 0 | 15 |  | 19650 | Q6 | 67.72 | 93.3351 | 6320.6515 |  | 24462.8492 | 50433.5008 | 0
[22 empty] | 25 | [5 empty] | 25 |  |  |  |  | 1.147 | 23262.5 | Q7 | 69.05 | 66.116 | 4565.3098 |  | 21202.8777 | 49030.6875 |  | 15 |  | 23262.5 | Q7 | 69.05 | 109.0914 | 7532.7612 |  | 29014.792 | 59810.0532 |  | 23262.5 | Q7 | 69.05 | 66.116 | 4565.3098 |  | 21202.8777 |  | 49030.6875 | 0 | 15 |  | 23262.5 | Q7 | 69.05 | 109.0914 | 7532.7612 |  | 29014.792 | 59810.0532 | 0
[22 empty] | 30 | [5 empty] | 30 |  |  |  |  | 1.147 | 26925 | Q7 | 69.05 | 78.744 | 5437.2732 |  | 24689.01 | 57051.2832 |  | 15 |  | 26925 | Q7 | 69.05 | 129.9276 | 8971.5008 |  | 33858.5666 | 69755.0674 |  | 26925 | Q7 | 69.05 | 78.744 | 5437.2732 |  | 24689.01 |  | 57051.2832 | 0 | 15 |  | 26925 | Q7 | 69.05 | 129.9276 | 8971.5008 |  | 33858.5666 | 69755.0674 | 0
[22 empty] | 40 | [5 empty] | 40 |  |  |  |  | 1.147 | 35475 | Q7 | 69.05 | 104 | 7181.2 |  | 32545.7037 | 75201.9037 |  | 15 |  | 35475 | Q7 | 69.05 | 171.6 | 11848.98 |  | 44641.4876 | 91965.4676 |  | 35475 | Q7 | 69.05 | 104 | 7181.2 |  | 32545.7037 |  | 75201.9037 | 0 | 15 |  | 35475 | Q7 | 69.05 | 171.6 | 11848.98 |  | 44641.4876 | 91965.4676 | 0
[16 empty] | Packaged CAV DX Rooftop Unit | Packaged CAV rooftop system with gas furnace. This equipment meets the general requirements of the base code that do not change in the target code and are commonly available in the market. This cost is without an economizer or ERV as they are not always required. | Equipment information below. Labor hours from RS Means 2023 Mechanical Cost Data. Outdoor-Air-Units Roof Top Air Conditioners, single zone, electric cool, gas heat, RS Means 23 74 33.10 11XX |  |  |  | Cooling Capacity, Tons | Same as for base code for same size units. |  |  |  |  | Cooling Capacity, Tons |  |  |  |  | Inflation from 2012 to 2023 | [19 empty] | Material adjustment for inflation | [12 empty] | 0
[17 empty] | Manufacturer 1 | Faithful+Gould | Carrier | 48 ES |  | 2 |  |  |  | 1 |  | 2 |  |  |  |  | 0.793 | 2250 | Q5 | 65.3 | 19.311 | 1261.0083 |  | 1646.1701 | 5157.1784 |  | 15 |  | 2250 | Q5 | 65.3 | 31.8632 | 2080.6637 |  | 2965.3555 | 7296.0192 |  | 2250 | Q5 | 65.3 | 19.311 | 1261.0083 |  | 1646.1701 |  | 5157.1784 | 0 | 15 |  | 2250 | Q5 | 65.3 | 31.8632 | 2080.6637 |  | 2965.3555 | 7296.0192 | 0
[17 empty] | No Increased efficiency from 2013 to 2016 | Airtech Thermex | Carrier | 48 ES |  | 2.5 | Means standard vs. Green book values for these units |  |  | 1 |  | 2.5 |  |  |  |  | 0.793 | 2700 | Q5 | 65.3 | 21.084 | 1376.7852 |  | 1843.6876 | 5920.4728 |  | 15 |  | 2700 | Q5 | 65.3 | 34.7886 | 2271.6956 |  | 3312.9712 | 8284.6668 |  | 2700 | Q5 | 65.3 | 21.084 | 1376.7852 |  | 1843.6876 |  | 5920.4728 | 0 | 15 |  | 2700 | Q5 | 65.3 | 34.7886 | 2271.6956 |  | 3312.9712 | 8284.6668 | 0
[18 empty] | Minneapolis MN | Carrier | 48 HC |  | 3 | Green book indicates SEER 14 |  |  | 1 |  | 3 |  |  |  |  | 0.793 | 2925 | Q5 | 65.3 | 22.857 | 1492.5621 |  | 1998.337 | 6415.8991 |  | 15 |  | 2925 | Q5 | 65.3 | 37.7141 | 2462.7275 |  | 3590.9319 | 8978.6594 |  | 2925 | Q5 | 65.3 | 22.857 | 1492.5621 |  | 1998.337 |  | 6415.8991 | 0 | 15 |  | 2925 | Q5 | 65.3 | 37.7141 | 2462.7275 |  | 3590.9319 | 8978.6594 | 0
[18 empty] | Carrier | Carrier | 48 HC |  | 4 | 23 74 33.10 Roof Top Air conditioners |  |  | 1 |  | 4 |  |  |  |  | 0.793 | 3600 | Q5 | 65.3 | 26.403 | 1724.1159 |  | 2350.5039 | 7674.6198 |  | 15 |  | 3600 | Q5 | 65.3 | 43.565 | 2844.7912 |  | 4216.5084 | 10661.2996 |  | 3600 | Q5 | 65.3 | 26.403 | 1724.1159 |  | 2350.5039 |  | 7674.6198 | 0 | 15 |  | 3600 | Q5 | 65.3 | 43.565 | 2844.7912 |  | 4216.5084 | 10661.2996 | 0
[19 empty] | Carrier | 48 HC | 60 | 5 |  |  |  | 1 |  | 5 |  |  |  |  | 0.793 | 4050 | Q5 | 65.3 | 28.521 | 1862.4213 |  | 2569.7724 | 8482.1937 |  | 15 |  | 4050 | Q5 | 65.3 | 47.0596 | 3072.9951 |  | 4604.6574 | 11727.6525 |  | 4050 | Q5 | 65.3 | 28.521 | 1862.4213 |  | 2569.7724 |  | 8482.1937 | 0 | 15 |  | 4050 | Q5 | 65.3 | 47.0596 | 3072.9951 |  | 4604.6574 | 11727.6525 | 0
[19 empty] | Carrier | 48 HC | 72 | 6 | [5 empty] | 6 |  |  |  |  | 0.793 | 4500 | Q5 | 65.3 | 30.769 | 2009.2157 |  | 2797.237 | 9306.4527 |  | 15 |  | 4500 | Q5 | 65.3 | 50.7689 | 3315.2059 |  | 5008.0798 | 12823.2857 |  | 4500 | Q5 | 65.3 | 30.769 | 2009.2157 |  | 2797.237 |  | 9306.4527 | 0 | 15 |  | 4500 | Q5 | 65.3 | 50.7689 | 3315.2059 |  | 5008.0798 | 12823.2857 | 0
[19 empty] | Carrier | 48 HC |  | 7.5 | [5 empty] | 7.5 |  |  |  |  | 0.793 | 5850 | Q5 | 65.3 | 32.258 | 2106.4474 |  | 3148.3221 | 11104.7695 |  | 15 |  | 5850 | Q5 | 65.3 | 53.2257 | 3475.6382 |  | 5600.9489 | 14926.5871 |  | 5850 | Q5 | 65.3 | 32.258 | 2106.4474 |  | 3148.3221 |  | 11104.7695 | 0 | 15 |  | 5850 | Q5 | 65.3 | 53.2257 | 3475.6382 |  | 5600.9489 | 14926.5871 | 0
[19 empty] | prorated |  |  | 8.5 | [5 empty] | 8.5 |  |  |  |  | 0.793 | 6390 | Q5 | 65.3 | 33.7476 | 2203.7183 |  | 3345.1195 | 11938.8378 |  | 15 |  | 6390 | Q5 | 65.3 | 55.6835 | 3636.1352 |  | 5943.1306 | 15969.2658 |  | 6390 | Q5 | 65.3 | 33.7476 | 2203.7183 |  | 3345.1195 |  | 11938.8378 | 0 | 15 |  | 6390 | Q5 | 65.3 | 55.6835 | 3636.1352 |  | 5943.1306 | 15969.2658 | 0
[19 empty] | Carrier | 48 HC |  | 10 | [5 empty] | 10 |  |  |  |  | 0.793 | 7200 | Q6 | 67.72 | 35.982 | 2436.701 |  | 3724.387 | 13361.088 |  | 15 |  | 7200 | Q6 | 67.72 | 59.3703 | 4020.5567 |  | 6613.071 | 17833.6278 |  | 7200 | Q6 | 67.72 | 35.982 | 2436.701 |  | 3724.387 |  | 13361.088 | 0 | 15 |  | 7200 | Q6 | 67.72 | 59.3703 | 4020.5567 |  | 6613.071 | 17833.6278 | 0
[19 empty] | Carrier | 48 HC |  | 12.5 | [5 empty] | 12.5 |  |  |  |  | 0.793 | 9000 | Q6 | 67.72 | 37.975 | 2571.667 |  | 4197.6403 | 15769.3073 |  | 15 |  | 9000 | Q6 | 67.72 | 62.6587 | 4243.2505 |  | 7413.1416 | 20656.3922 |  | 9000 | Q6 | 67.72 | 37.975 | 2571.667 |  | 4197.6403 |  | 15769.3073 | 0 | 15 |  | 9000 | Q6 | 67.72 | 62.6587 | 4243.2505 |  | 7413.1416 | 20656.3922 | 0
[19 empty] | Carrier | 48 HC |  | 15 | [5 empty] | 15 |  |  |  |  | 0.793 | 9675 | Q6 | 67.72 | 43.032 | 2914.127 |  | 4656.8859 | 17246.0129 |  | 15 |  | 9675 | Q6 | 67.72 | 71.0028 | 4808.3096 |  | 8238.2605 | 22721.5702 |  | 9675 | Q6 | 67.72 | 43.032 | 2914.127 |  | 4656.8859 |  | 17246.0129 | 0 | 15 |  | 9675 | Q6 | 67.72 | 71.0028 | 4808.3096 |  | 8238.2605 | 22721.5702 | 0
[19 empty] | Carrier | 48 HC |  | 17.5 | [5 empty] | 17.5 |  |  |  |  | 0.793 | 11250 | Q6 | 67.72 | 45.889 | 3107.6031 |  | 5143.7619 | 19501.365 |  | 15 |  | 11250 | Q6 | 67.72 | 75.7168 | 5127.5451 |  | 9073.9474 | 25451.4925 |  | 11250 | Q6 | 67.72 | 45.889 | 3107.6031 |  | 5143.7619 |  | 19501.365 | 0 | 15 |  | 11250 | Q6 | 67.72 | 75.7168 | 5127.5451 |  | 9073.9474 | 25451.4925 | 0
[19 empty] | Carrier | 48 HC |  | 20 | [5 empty] | 20 |  |  |  |  | 0.793 | 12375 | Q7 | 69.05 | 47.976 | 3312.7428 |  | 5556.1627 | 21243.9055 |  | 15 |  | 12375 | Q7 | 69.05 | 79.1604 | 5466.0256 |  | 9791.3097 | 27632.3353 |  | 12375 | Q7 | 69.05 | 47.976 | 3312.7428 |  | 5556.1627 |  | 21243.9055 | 0 | 15 |  | 12375 | Q7 | 69.05 | 79.1604 | 5466.0256 |  | 9791.3097 | 27632.3353 | 0
[17 empty] | Manufacturer 2 | Faithful+Gould | Trane | 4TCC |  | 2 | [5 empty] | 2 |  |  |  |  | 0.793 | 2500 | Q5 | 65.3 | 19.311 | 1261.0083 |  | 1693.8014 | 5454.8097 |  | 15 |  | 2500 | Q5 | 65.3 | 31.8632 | 2080.6637 |  | 3042.7499 | 7623.4136 |  | 2500 | Q5 | 65.3 | 19.311 | 1261.0083 |  | 1693.8014 |  | 5454.8097 | 0 | 15 |  | 2500 | Q5 | 65.3 | 31.8632 | 2080.6637 |  | 3042.7499 | 7623.4136 | 0
[18 empty] | Trane Corp. | Trane | 4TCC |  | 2.5 | [5 empty] | 2.5 |  |  |  |  | 0.793 | 3000 | Q5 | 65.3 | 21.084 | 1376.7852 |  | 1900.8452 | 6277.6304 |  | 15 |  | 3000 | Q5 | 65.3 | 34.7886 | 2271.6956 |  | 3405.8445 | 8677.5401 |  | 3000 | Q5 | 65.3 | 21.084 | 1376.7852 |  | 1900.8452 |  | 6277.6304 | 0 | 15 |  | 3000 | Q5 | 65.3 | 34.7886 | 2271.6956 |  | 3405.8445 | 8677.5401 | 0
[18 empty] | Minneapolis MN | Trane | 4TCC |  | 3 | [5 empty] | 3 |  |  |  |  | 0.793 | 3250 | Q5 | 65.3 | 22.857 | 1492.5621 |  | 2060.2577 | 6802.8198 |  | 15 |  | 3250 | Q5 | 65.3 | 37.7141 | 2462.7275 |  | 3691.5447 | 9404.2722 |  | 3250 | Q5 | 65.3 | 22.857 | 1492.5621 |  | 2060.2577 |  | 6802.8198 | 0 | 15 |  | 3250 | Q5 | 65.3 | 37.7141 | 2462.7275 |  | 3691.5447 | 9404.2722 | 0
[18 empty] | Trane | Trane | YSC |  | 4 | [5 empty] | 4 |  |  |  |  | 0.793 | 4000 | Q5 | 65.3 | 26.403 | 1724.1159 |  | 2426.714 | 8150.8299 |  | 15 |  | 4000 | Q5 | 65.3 | 43.565 | 2844.7912 |  | 4340.3395 | 11185.1307 |  | 4000 | Q5 | 65.3 | 26.403 | 1724.1159 |  | 2426.714 |  | 8150.8299 | 0 | 15 |  | 4000 | Q5 | 65.3 | 43.565 | 2844.7912 |  | 4340.3395 | 11185.1307 | 0
[19 empty] | Trane | YSC |  | 5 | [5 empty] | 5 |  |  |  |  | 0.793 | 4500 | Q5 | 65.3 | 28.521 | 1862.4213 |  | 2655.5088 | 9017.9301 |  | 15 |  | 4500 | Q5 | 65.3 | 47.0596 | 3072.9951 |  | 4743.9674 | 12316.9625 |  | 4500 | Q5 | 65.3 | 28.521 | 1862.4213 |  | 2655.5088 |  | 9017.9301 | 0 | 15 |  | 4500 | Q5 | 65.3 | 47.0596 | 3072.9951 |  | 4743.9674 | 12316.9625 | 0
[19 empty] | Trane | YSC |  | 6 | [5 empty] | 6 |  |  |  |  | 0.793 | 5000 | Q5 | 65.3 | 30.769 | 2009.2157 |  | 2892.4996 | 9901.7153 |  | 15 |  | 5000 | Q5 | 65.3 | 50.7689 | 3315.2059 |  | 5162.8686 | 13478.0745 |  | 5000 | Q5 | 65.3 | 30.769 | 2009.2157 |  | 2892.4996 |  | 9901.7153 | 0 | 15 |  | 5000 | Q5 | 65.3 | 50.7689 | 3315.2059 |  | 5162.8686 | 13478.0745 | 0
[19 empty] | Trane | YSC |  | 7.5 | [5 empty] | 7.5 |  |  |  |  | 0.793 | 6500 | Q5 | 65.3 | 32.258 | 2106.4474 |  | 3272.1634 | 11878.6108 |  | 15 |  | 6500 | Q5 | 65.3 | 53.2257 | 3475.6382 |  | 5802.1744 | 15777.8126 |  | 6500 | Q5 | 65.3 | 32.258 | 2106.4474 |  | 3272.1634 |  | 11878.6108 | 0 | 15 |  | 6500 | Q5 | 65.3 | 53.2257 | 3475.6382 |  | 5802.1744 | 15777.8126 | 0
[19 empty] | prorated |  |  | 8.5 | [5 empty] | 8.5 |  |  |  |  | 0.793 | 7366.6667 | Q5 | 65.3 | 33.7476 | 2203.7183 |  | 3531.1991 | 13101.5841 |  | 15 |  | 7366.6667 | Q5 | 65.3 | 55.6835 | 3636.1352 |  | 6245.4848 | 17248.2867 |  | 7366.6667 | Q5 | 65.3 | 33.7476 | 2203.7183 |  | 3531.1991 |  | 13101.5841 | 0 | 15 |  | 7366.6667 | Q5 | 65.3 | 55.6835 | 3636.1352 |  | 6245.4848 | 17248.2867 | 0
[19 empty] | Trane | YSC |  | 10 | [5 empty] | 10 |  |  |  |  | 0.793 | 8000 | Q6 | 67.72 | 35.982 | 2436.701 |  | 3876.8071 | 14313.5082 |  | 15 |  | 8000 | Q6 | 67.72 | 59.3703 | 4020.5567 |  | 6860.7332 | 18881.2899 |  | 8000 | Q6 | 67.72 | 35.982 | 2436.701 |  | 3876.8071 |  | 14313.5082 | 0 | 15 |  | 8000 | Q6 | 67.72 | 59.3703 | 4020.5567 |  | 6860.7332 | 18881.2899 | 0
[19 empty] | Trane | YSC |  | 12.5 | [5 empty] | 12.5 |  |  |  |  | 0.793 | 10000 | Q6 | 67.72 | 37.975 | 2571.667 |  | 4388.1655 | 16959.8325 |  | 15 |  | 10000 | Q6 | 67.72 | 62.6587 | 4243.2505 |  | 7722.7193 | 21965.9699 |  | 10000 | Q6 | 67.72 | 37.975 | 2571.667 |  | 4388.1655 |  | 16959.8325 | 0 | 15 |  | 10000 | Q6 | 67.72 | 62.6587 | 4243.2505 |  | 7722.7193 | 21965.9699 | 0
[19 empty] | Trane | YSC |  | 15 | [5 empty] | 15 |  |  |  |  | 0.793 | 10750 | Q6 | 67.72 | 43.032 | 2914.127 |  | 4861.7005 | 18525.8275 |  | 15 |  | 10750 | Q6 | 67.72 | 71.0028 | 4808.3096 |  | 8571.0566 | 24129.3662 |  | 10750 | Q6 | 67.72 | 43.032 | 2914.127 |  | 4861.7005 |  | 18525.8275 | 0 | 15 |  | 10750 | Q6 | 67.72 | 71.0028 | 4808.3096 |  | 8571.0566 | 24129.3662 | 0
[19 empty] | Trane | YSC |  | 17.5 | [5 empty] | 17.5 |  |  |  |  | 0.793 | 12500 | Q6 | 67.72 | 45.889 | 3107.6031 |  | 5381.9184 | 20989.5214 |  | 15 |  | 12500 | Q6 | 67.72 | 75.7168 | 5127.5451 |  | 9460.9196 | 27088.4647 |  | 12500 | Q6 | 67.72 | 45.889 | 3107.6031 |  | 5381.9184 |  | 20989.5214 | 0 | 15 |  | 12500 | Q6 | 67.72 | 75.7168 | 5127.5451 |  | 9460.9196 | 27088.4647 | 0
[19 empty] | Trane | YSC |  | 20 | [5 empty] | 20 |  |  |  |  | 0.793 | 13750 | Q7 | 69.05 | 47.976 | 3312.7428 |  | 5818.1348 | 22880.8776 |  | 15 |  | 13750 | Q7 | 69.05 | 79.1604 | 5466.0256 |  | 10216.979 | 29433.0046 |  | 13750 | Q7 | 69.05 | 47.976 | 3312.7428 |  | 5818.1348 |  | 22880.8776 | 0 | 15 |  | 13750 | Q7 | 69.05 | 79.1604 | 5466.0256 |  | 10216.979 | 29433.0046 | 0
[16 empty] | CAV_DX | Average of two manufacturers
[22 empty] | 1.5 | [5 empty] | 1.5 |  |  |  |  | 0.793 | 1900 | Q5 | 65.3 | 17.538 | 1145.2314 |  | 1467.705 | 4512.9364 |  | 15 |  | 1900 | Q5 | 65.3 | 28.9377 | 1889.6318 |  | 2648.6975 | 6438.3293 |  | 1900 | Q5 | 65.3 | 17.538 | 1145.2314 |  | 1467.705 |  | 4512.9364 | 0 | 15 |  | 1900 | Q5 | 65.3 | 28.9377 | 1889.6318 |  | 2648.6975 | 6438.3293 | 0
[16 empty] | used for load changes | [5 empty] | 2 | [5 empty] | 2 |  |  |  |  | 0.793 | 2375 | Q5 | 65.3 | 19.311 | 1261.0083 |  | 1669.9857 | 5305.994 |  | 15 |  | 2375 | Q5 | 65.3 | 31.8632 | 2080.6637 |  | 3004.0527 | 7459.7164 |  | 2375 | Q5 | 65.3 | 19.311 | 1261.0083 |  | 1669.9857 |  | 5305.994 | 0 | 15 |  | 2375 | Q5 | 65.3 | 31.8632 | 2080.6637 |  | 3004.0527 | 7459.7164 | 0
[17 empty] | Material costs shown from 2012 survey are adjusted for inflation to 2023 |  |  |  |  | 2.5 | [5 empty] | 2.5 |  |  |  |  | 0.793 | 2850 | Q5 | 65.3 | 21.084 | 1376.7852 |  | 1872.2664 | 6099.0516 |  | 15 |  | 2850 | Q5 | 65.3 | 34.7886 | 2271.6956 |  | 3359.4079 | 8481.1034 |  | 2850 | Q5 | 65.3 | 21.084 | 1376.7852 |  | 1872.2664 |  | 6099.0516 | 0 | 15 |  | 2850 | Q5 | 65.3 | 34.7886 | 2271.6956 |  | 3359.4079 | 8481.1034 | 0
[17 empty] | Adjustment included in cost adjustments column and based on |  |  |  |  | 3 | [5 empty] | 3 |  |  |  |  | 0.793 | 3087.5 | Q5 | 65.3 | 22.857 | 1492.5621 |  | 2029.2973 | 6609.3594 |  | 15 |  | 3087.5 | Q5 | 65.3 | 37.7141 | 2462.7275 |  | 3641.2383 | 9191.4658 |  | 3087.5 | Q5 | 65.3 | 22.857 | 1492.5621 |  | 2029.2973 |  | 6609.3594 | 0 | 15 |  | 3087.5 | Q5 | 65.3 | 37.7141 | 2462.7275 |  | 3641.2383 | 9191.4658 | 0
[17 empty] | Difference in Means 2012 and 2023 for similar equipment |  |  |  |  | 4 | [5 empty] | 4 |  |  |  |  | 0.793 | 3800 | Q5 | 65.3 | 26.403 | 1724.1159 |  | 2388.6089 | 7912.7248 |  | 15 |  | 3800 | Q5 | 65.3 | 43.565 | 2844.7912 |  | 4278.4239 | 10923.2152 |  | 3800 | Q5 | 65.3 | 26.403 | 1724.1159 |  | 2388.6089 |  | 7912.7248 | 0 | 15 |  | 3800 | Q5 | 65.3 | 43.565 | 2844.7912 |  | 4278.4239 | 10923.2152 | 0
[22 empty] | 5 | [5 empty] | 5 |  |  |  |  | 0.793 | 4275 | Q5 | 65.3 | 28.521 | 1862.4213 |  | 2612.6406 | 8750.0619 |  | 15 |  | 4275 | Q5 | 65.3 | 47.0596 | 3072.9951 |  | 4674.3124 | 12022.3075 |  | 4275 | Q5 | 65.3 | 28.521 | 1862.4213 |  | 2612.6406 |  | 8750.0619 | 0 | 15 |  | 4275 | Q5 | 65.3 | 47.0596 | 3072.9951 |  | 4674.3124 | 12022.3075 | 0
[22 empty] | 6 | [5 empty] | 6 |  |  |  |  | 0.793 | 4750 | Q5 | 65.3 | 30.769 | 2009.2157 |  | 2844.8683 | 9604.084 |  | 15 |  | 4750 | Q5 | 65.3 | 50.7689 | 3315.2059 |  | 5085.4742 | 13150.6801 |  | 4750 | Q5 | 65.3 | 30.769 | 2009.2157 |  | 2844.8683 |  | 9604.084 | 0 | 15 |  | 4750 | Q5 | 65.3 | 50.7689 | 3315.2059 |  | 5085.4742 | 13150.6801 | 0
[17 empty] | 2-ton minimum |  |  |  |  | 7.5 | [5 empty] | 7.5 |  |  |  |  | 0.793 | 6175 | Q5 | 65.3 | 32.258 | 2106.4474 |  | 3210.2427 | 11491.6901 |  | 15 |  | 6175 | Q5 | 65.3 | 53.2257 | 3475.6382 |  | 5701.5617 | 15352.1999 |  | 6175 | Q5 | 65.3 | 32.258 | 2106.4474 |  | 3210.2427 |  | 11491.6901 | 0 | 15 |  | 6175 | Q5 | 65.3 | 53.2257 | 3475.6382 |  | 5701.5617 | 15352.1999 | 0
[22 empty] | 8.5 | [5 empty] | 8.5 |  |  |  |  | 0.793 | 6878.3333 | Q5 | 65.3 | 33.7476 | 2203.7183 |  | 3438.1593 | 12520.2109 |  | 15 |  | 6878.3333 | Q5 | 65.3 | 55.6835 | 3636.1352 |  | 6094.3077 | 16608.7762 |  | 6878.3333 | Q5 | 65.3 | 33.7476 | 2203.7183 |  | 3438.1593 |  | 12520.2109 | 0 | 15 |  | 6878.3333 | Q5 | 65.3 | 55.6835 | 3636.1352 |  | 6094.3077 | 16608.7762 | 0
[22 empty] | 10 | [5 empty] | 10 |  |  |  |  | 0.793 | 7600 | Q6 | 67.72 | 35.982 | 2436.701 |  | 3800.5971 | 13837.2981 |  | 15 |  | 7600 | Q6 | 67.72 | 59.3703 | 4020.5567 |  | 6736.9021 | 18357.4588 |  | 7600 | Q6 | 67.72 | 35.982 | 2436.701 |  | 3800.5971 |  | 13837.2981 | 0 | 15 |  | 7600 | Q6 | 67.72 | 59.3703 | 4020.5567 |  | 6736.9021 | 18357.4588 | 0
[22 empty] | 12.5 | [5 empty] | 12.5 |  |  |  |  | 0.793 | 9500 | Q6 | 67.72 | 37.975 | 2571.667 |  | 4292.9029 | 16364.5699 |  | 15 |  | 9500 | Q6 | 67.72 | 62.6587 | 4243.2505 |  | 7567.9305 | 21311.181 |  | 9500 | Q6 | 67.72 | 37.975 | 2571.667 |  | 4292.9029 |  | 16364.5699 | 0 | 15 |  | 9500 | Q6 | 67.72 | 62.6587 | 4243.2505 |  | 7567.9305 | 21311.181 | 0
[22 empty] | 15 | [5 empty] | 15 |  |  |  |  | 0.793 | 10212.5 | Q6 | 67.72 | 43.032 | 2914.127 |  | 4759.2932 | 17885.9202 |  | 15 |  | 10212.5 | Q6 | 67.72 | 71.0028 | 4808.3096 |  | 8404.6586 | 23425.4682 |  | 10212.5 | Q6 | 67.72 | 43.032 | 2914.127 |  | 4759.2932 |  | 17885.9202 | 0 | 15 |  | 10212.5 | Q6 | 67.72 | 71.0028 | 4808.3096 |  | 8404.6586 | 23425.4682 | 0
[22 empty] | 17.5 | [5 empty] | 17.5 |  |  |  |  | 0.793 | 11875 | Q6 | 67.72 | 45.889 | 3107.6031 |  | 5262.8401 | 20245.4432 |  | 15 |  | 11875 | Q6 | 67.72 | 75.7168 | 5127.5451 |  | 9267.4335 | 26269.9786 |  | 11875 | Q6 | 67.72 | 45.889 | 3107.6031 |  | 5262.8401 |  | 20245.4432 | 0 | 15 |  | 11875 | Q6 | 67.72 | 75.7168 | 5127.5451 |  | 9267.4335 | 26269.9786 | 0
[22 empty] | 20 | [5 empty] | 20 |  |  |  |  | 0.793 | 13062.5 | Q7 | 69.05 | 47.976 | 3312.7428 |  | 5687.1487 | 22062.3915 |  | 15 |  | 13062.5 | Q7 | 69.05 | 79.1604 | 5466.0256 |  | 10004.1444 | 28532.67 |  | 13062.5 | Q7 | 69.05 | 47.976 | 3312.7428 |  | 5687.1487 |  | 22062.3915 | 0 | 15 |  | 13062.5 | Q7 | 69.05 | 79.1604 | 5466.0256 |  | 10004.1444 | 28532.67 | 0
[17 empty] | extrapolated - some values in models exceed 20 tons. RS Means shows cost/ton within +/1 5% of the average from 17.5 to 30 tons |  |  |  |  | 30 | [5 empty] | 30 |  |  |  |  | 0.793 | 17812.5 | Q7 | 69.05 | 56.324 | 3889.1722 |  | 7148.679 | 28850.3512 |  | 15 |  | 17812.5 | Q7 | 69.05 | 92.9346 | 6417.1341 |  | 12511.75 | 36741.3841 |  | 17812.5 | Q7 | 69.05 | 56.324 | 3889.1722 |  | 7148.679 |  | 28850.3512 | 0 | 15 |  | 17812.5 | Q7 | 69.05 | 92.9346 | 6417.1341 |  | 12511.75 | 36741.3841 | 0
[16 empty] | Packaged Heat Pump adjusted for load changes | Packaged heat pump with gas backup. This equipment meets the general requirements of the base code that do not change in the target code and are commonly available in the market. This cost is without an economizer or ERV as they are not always required. | Equipment information below. Labor from RS Means 2023 Mechanical Cost Data. Air-Source Heat Pumps, single zone, electric cool, gas heat, RS Means 23 81 43.10 10XX |  |  |  | Cooling Capacity, Tons | Same as for base code for same size units. | [9 empty] | Inflation from 2012 to 2023 | [19 empty] | Material adjustment for inflation
1.217
[17 empty] | Manufacturer 1 | Faithful+Gould | Carrier | 50PSH |  | 1.5 | [5 empty] | 1.5 |  |  |  |  | 1.217 | 1800 | Q5 | 65.3 | 6.67 | 435.551 |  | 1909.2513 | 4144.8023 |  | 15 |  | 1800 | Q5 | 65.3 | 11.0055 | 718.6591 |  | 2601.2484 | 5119.9075 |  | 1800 | Q5 | 65.3 | 6.67 | 435.551 |  | 1909.2513 |  | 4144.8023 | 0 | 15 |  | 1800 | Q5 | 65.3 | 11.0055 | 718.6591 |  | 2601.2484 | 5119.9075 | 0
[18 empty] | Airtech Thermex | Carrier | 50PSH |  | 2 | [5 empty] | 2 |  |  |  |  | 1.217 | 2250 | Q5 | 65.3 | 8 | 522.4 |  | 2365.2859 | 5137.6859 |  | 15 |  | 2250 | Q5 | 65.3 | 13.2 | 861.96 |  | 3211.9084 | 6323.8684 |  | 2250 | Q5 | 65.3 | 8 | 522.4 |  | 2365.2859 |  | 5137.6859 | 0 | 15 |  | 2250 | Q5 | 65.3 | 13.2 | 861.96 |  | 3211.9084 | 6323.8684 | 0
[18 empty] | Minneapolis MN | Carrier | 50PSH |  | 2.5 | [5 empty] | 2.5 |  |  |  |  | 1.217 | 2475 | Q5 | 65.3 | 10 | 653 |  | 2677.4702 | 5805.4702 |  | 15 |  | 2475 | Q5 | 65.3 | 16.5 | 1077.45 |  | 3674.0845 | 7226.5345 |  | 2475 | Q5 | 65.3 | 10 | 653 |  | 2677.4702 |  | 5805.4702 | 0 | 15 |  | 2475 | Q5 | 65.3 | 16.5 | 1077.45 |  | 3674.0845 | 7226.5345 | 0
[18 empty] | Carrier | Carrier | 50PSH |  | 3 |  |  |  | 1 |  | 3 |  |  |  |  | 1.217 | 2700 | Q5 | 65.3 | 13.33 | 870.449 |  | 3073.5061 | 6643.9551 |  | 15 |  | 2700 | Q5 | 65.3 | 21.9945 | 1436.2408 |  | 4292.5193 | 8428.7602 |  | 2700 | Q5 | 65.3 | 13.33 | 870.449 |  | 3073.5061 |  | 6643.9551 | 0 | 15 |  | 2700 | Q5 | 65.3 | 21.9945 | 1436.2408 |  | 4292.5193 | 8428.7602 | 0
[18 empty] | Carrier | Carrier | 50PSH |  | 4 |  |  |  | 1 |  | 4 |  |  |  |  | 1.217 | 2925 | Q5 | 65.3 | 20 | 1306 |  | 3680.1168 | 7911.1168 |  | 15 |  | 2925 | Q5 | 65.3 | 33 | 2154.9 |  | 5303.3631 | 10383.2631 |  | 2925 | Q5 | 65.3 | 20 | 1306 |  | 3680.1168 |  | 7911.1168 | 0 | 15 |  | 2925 | Q5 | 65.3 | 33 | 2154.9 |  | 5303.3631 | 10383.2631 | 0
[18 empty] | Carrier | Carrier | 50PSH |  | 5 |  |  |  | 1 |  | 5 |  |  |  |  | 1.217 | 3060 | Q5 | 65.3 | 32 | 2089.6 |  | 4548.3281 | 9697.9281 |  | 15 |  | 3060 | Q5 | 65.3 | 52.8 | 3447.84 |  | 6849.5363 | 13357.3763 |  | 3060 | Q5 | 65.3 | 32 | 2089.6 |  | 4548.3281 |  | 9697.9281 | 0 | 15 |  | 3060 | Q5 | 65.3 | 52.8 | 3447.84 |  | 6849.5363 | 13357.3763 | 0
[17 empty] | Manufacturer 2 | Faithful+Gould | [21 empty] | 0
[18 empty] | Trane Corp. | Trane | 4TCC |  | 1.5 | [5 empty] | 1.5 |  |  |  |  | 1.217 | 2025 | Q5 | 65.3 | 6.67 | 435.551 |  | 2095.3428 | 4555.8938 |  | 15 |  | 2025 | Q5 | 65.3 | 11.0055 | 718.6591 |  | 2828.449 | 5572.1082 |  | 2025 | Q5 | 65.3 | 6.67 | 435.551 |  | 2095.3428 |  | 4555.8938 | 0 | 15 |  | 2025 | Q5 | 65.3 | 11.0055 | 718.6591 |  | 2828.449 | 5572.1082 | 0
[18 empty] | Minneapolis MN | Trane | 4TCC |  | 2 | [5 empty] | 2 |  |  |  |  | 1.217 | 2700 | Q5 | 65.3 | 8 | 522.4 |  | 2737.4689 | 5959.8689 |  | 15 |  | 2700 | Q5 | 65.3 | 13.2 | 861.96 |  | 3666.3097 | 7228.2697 |  | 2700 | Q5 | 65.3 | 8 | 522.4 |  | 2737.4689 |  | 5959.8689 | 0 | 15 |  | 2700 | Q5 | 65.3 | 13.2 | 861.96 |  | 3666.3097 | 7228.2697 | 0
[18 empty] | Trane | Trane | 4TCC |  | 2.5 | [5 empty] | 2.5 |  |  |  |  | 1.217 | 3225 | Q5 | 65.3 | 10 | 653 |  | 3297.7752 | 7175.7752 |  | 15 |  | 3225 | Q5 | 65.3 | 16.5 | 1077.45 |  | 4431.42 | 8733.87 |  | 3225 | Q5 | 65.3 | 10 | 653 |  | 3297.7752 |  | 7175.7752 | 0 | 15 |  | 3225 | Q5 | 65.3 | 16.5 | 1077.45 |  | 4431.42 | 8733.87 | 0
[22 empty] | 3 | [5 empty] | 3
[22 empty] | 4 | [5 empty] | 4
[22 empty] | 5 | [5 empty] | 5
[16 empty] | Heat_Pump | Average of two manufacturers
[22 empty] | 1.5 |  |  |  | 1 |  | 1.5 |  |  |  |  | 1.217 | 1912.5 | Q5 | 65.3 | 6.67 | 435.551 |  | 2002.297 | 4350.348 |  | 15 |  | 1912.5 | Q5 | 65.3 | 11.0055 | 718.6591 |  | 2714.8487 | 5346.0079 | 1.217 | 1912.5 | Q5 | 65.3 | 6.67 | 435.551 |  | 2002.297 |  | 4350.348 | 0 | 15 |  | 1912.5 | Q5 | 65.3 | 11.0055 | 718.6591 |  | 2714.8487 | 5346.0079 | 0
[17 empty] | Material costs shown from 2012 survey are adjusted for inflation to 2023 |  |  |  |  | 2 |  |  |  | 1 |  | 2 |  |  |  |  | 1.217 | 2475 | Q5 | 65.3 | 8 | 522.4 |  | 2551.3774 | 5548.7774 |  | 15 |  | 2475 | Q5 | 65.3 | 13.2 | 861.96 |  | 3439.109 | 6776.069 | 1.217 | 2475 | Q5 | 65.3 | 8 | 522.4 |  | 2551.3774 |  | 5548.7774 | 0 | 15 |  | 2475 | Q5 | 65.3 | 13.2 | 861.96 |  | 3439.109 | 6776.069 | 0
[17 empty] | Adjustment included in cost adjustments column and based on |  |  |  |  | 2.5 |  |  |  | 1 |  | 2.5 |  |  |  |  | 1.217 | 2850 | Q5 | 65.3 | 10 | 653 |  | 2987.6227 | 6490.6227 |  | 15 |  | 2850 | Q5 | 65.3 | 16.5 | 1077.45 |  | 4052.7523 | 7980.2023 | 1.217 | 2850 | Q5 | 65.3 | 10 | 653 |  | 2987.6227 |  | 6490.6227 | 0 | 15 |  | 2850 | Q5 | 65.3 | 16.5 | 1077.45 |  | 4052.7523 | 7980.2023 | 0
[17 empty] | Difference in Means 2012 and 2023 for similar equipment |  |  |  |  | 3 |  |  |  | 1 |  | 3 |  |  |  |  | 1.217 | 2700 | Q5 | 65.3 | 13.33 | 870.449 |  | 3073.5061 | 6643.9551 |  | 15 |  | 2700 | Q5 | 65.3 | 21.9945 | 1436.2408 |  | 4292.5193 | 8428.7602 | 1.217 | 2700 | Q5 | 65.3 | 13.33 | 870.449 |  | 3073.5061 |  | 6643.9551 | 0 | 15 |  | 2700 | Q5 | 65.3 | 21.9945 | 1436.2408 |  | 4292.5193 | 8428.7602 | 0
[22 empty] | 4 |  |  |  | 1 |  | 4 |  |  |  |  | 1.217 | 2925 | Q5 | 65.3 | 20 | 1306 |  | 3680.1168 | 7911.1168 |  | 15 |  | 2925 | Q5 | 65.3 | 33 | 2154.9 |  | 5303.3631 | 10383.2631 | 1.217 | 2925 | Q5 | 65.3 | 20 | 1306 |  | 3680.1168 |  | 7911.1168 | 0 | 15 |  | 2925 | Q5 | 65.3 | 33 | 2154.9 |  | 5303.3631 | 10383.2631 | 0
[22 empty] | 5 |  |  |  | 1 |  | 5 |  |  |  |  | 1.217 | 3060 | Q5 | 65.3 | 32 | 2089.6 |  | 4548.3281 | 9697.9281 |  | 15 |  | 3060 | Q5 | 65.3 | 52.8 | 3447.84 |  | 6849.5363 | 13357.3763 | 1.217 | 3060 | Q5 | 65.3 | 32 | 2089.6 |  | 4548.3281 |  | 9697.9281 | 0 | 15 |  | 3060 | Q5 | 65.3 | 52.8 | 3447.84 |  | 6849.5363 | 13357.3763 | 0
[17 empty] | Split system DX with gas furnace for mid-rise apartment Costs and regression developed in 2012 are updated on apartment prototype sheet with inflation factors based on Means to bring them forward to 2023. | Data shown used to create these: | Curve Fits
[16 empty] | Split-System_W_Furnace |  |  | Material
[18 empty] | All climate zones | y = 17.693x2 - 208.45x + 2690.6
[16 empty] | used for load changes |  |  | R² = 0.9455
Labor
[18 empty] | All climate zones | y = 6.1014x2 - 73.657x + 2202.7
[19 empty] | R² = 0.9001 | [13 empty] | 2023 costs
90.1-2016 bo | [15 empty] | Furnace_eff | 90.1-2016 bo Non-weatherized gas furnace < 225 kBtuh, 78% AFUE, 100 kBtuh | Material costs are from the appliance standard rulemaking. Originally in 2012$ but converted to 2023$. Labor from RS Means 2023 Mechanical Cost Data. Gas-fired furnace, Gas, AGA certified, upflow, direct drive models. RS Means 23 54 16.13 |  |  |  | 100000 | Same as base code but with 81% AFUE | Same as base code 3.4% higher material cost than base code |  |  |  | 100000 |  |  |  |  | 1 | 2638.35 | Q9 | 63.13 | 5 | 315.65 |  | 1627.3421 | 4581.3421 | 0 | 15 |  | 2638.35 | Q9 | 63.13 | 8.25 | 520.8225 |  | 2286.5968 | 5445.7693 |  | 2738.35 | Q9 | 63.13 | 5 | 315.65 |  | 1677.4714 |  | 4731.4714 | 0 | 15 |  | 2738.35 | Q9 | 63.13 | 8.25 | 520.8225 |  | 2351.739 | 5610.9115 | 150.1293
[16 empty] | Furnace_eff_apt | 90.1-2016 bo Non-weatherized gas furnace < 225 kBtuh, 78% AFUE, 4 kBtuh | Material costs are from the appliance standard rulemaking. Originally in 2012$ but converted to 2023$. Labor from RS Means 2023 Mechanical Cost Data. Gas-fired furnace, Gas, AGA certified, upflow, direct drive models. RS Means 23 54 16.13 |  |  |  | 4000 | Same as base code but with 81% AFUE | Same as base code 3.4% higher material cost than base code |  |  |  | 4000 |  |  |  |  | 1 | 642 | Q9 | 63.13 | 5 | 315.65 |  | 626.5863 | 1584.2363 | 0 | 15 |  | 642 | Q9 | 63.13 | 8.25 | 520.8225 |  | 986.1303 | 2148.9528 |  | 666 | Q9 | 63.13 | 5 | 315.65 |  | 638.6173 |  | 1620.2673 | 0 | 15 |  | 666 | Q9 | 63.13 | 8.25 | 520.8225 |  | 1001.7645 | 2188.587 | 36.031
|  |  |  | X | X | X | X | X | X | [6 empty] | Duct Work and Zone Air Distribution changes due to HVAC Load Changes | Estimated cost of air delivery duct work and zone components such as terminal units and diffusers for the 6 prototype buildings. Mid-rise apartment common area systems are very small and have negligible differences between cases. Values are ordered from smallest to largest total airflow. The base code and target code estimates are both used for interpolation as the sizing is based on the total airflow, and there are no other differences in duct system costs between the two codes. There are no incremental differences between the two codes except based on changes in load and airflow, so the numbers are relevant, with a cost multiplier based on inflation from 2012 to current prices. Duct costs were developed for a range of climate zones. A curve fit formula was developed with the built-in curve fit function in Excel. Material and labor functions were developed and are shown below with the R2 values. Total costs are computed for each city location with each prototype cost worksheet using the same cost factors - total values shown here are just for these specific airflows. and the total cost is associated with total airflow for purposes of assigning OH&P and other factors. | Solarc one-line diagram and component cost estimate using model HVAC outputs for selected climate zones from PNNL. Costs developed in 2012 are updated with inflation factors based on Means to bring them forward to current costs. |  |  |  | Airflow, cfm | Costs shown are duplicates of the base code costs, adjusted for total airflow. Addendum AU adds deducts from allowed static pressure for systems without central heating and cooling coils. This affects VAV systems in the Primary school and Large office for this CE analysis. Cost impact is evaluated as follows: When units do not have preheat or central heating coils, the fan design static pressure is reduced by 0.3 inches to calculate savings. For those units without preheat coils, it is assumed that ductwork is upsized, resulting in more sheet metal and more labor. Based on an analysis of ductwork sizing for multiple sizes of round ductwork, about 15% of the ductwork needs to be upsized to the next standard size to provide a 0.3" reduction in total system static pressure, resulting in an overall ductwork cost increase of 2.75%. The cost adders are calculated on the HVAC building tabs for units without preheat coils. In the simulation, a preheat coil is used in zones where the mixed air temperature will be less than 55F at design outside air conditions. | Solarc one-line diagram and component cost estimate using model HVAC outputs from PNNL. |  |  |  | Airflow, cfm |  |  |  | 2012 to 2023 Labor inflation adjustment, applied after regression results developed in 2012 | 2012 to 2023 Material inflation adjustment, applied after regression results developed in 2012 | [17 empty] | Inflation cost adjustments not included for air distribution below because they are transferred to where the regressions are applied on prototype sheets
[17 empty] | Small Office | Data shown used to create these: | Curve Fits |  |  |  | Small Office | Data shown used to create these: | Curve Fits | [6 empty] | inf_lab_DUCT | inf_mat_DUCT
[17 empty] | 3C San Francisco 90.1-2010 |  | Material |  |  | 2958.124 | 3C San Francisco 90.1-2010 |  | Material |  |  | 2958.124 |  |  |  | 1.344 | 1.537 | 5319.4866 | Q-10 | 65.47 | 297.2153 | 19458.6832 |  | 25742.2849 | 50520.4547 |  | 30 |  | 5319.4866 | Q-10 | 65.47 | 490.4052 | 32106.8272 |  | 38475.286 | 75901.5999 |  | 5319.4866 | Q-10 | 65.47 | 297.2153 | 19458.6832 |  | 25742.2849 |  | 50520.4547 | 0 | 30 |  | 5319.4866 | Q-10 | 65.47 | 490.4052 | 32106.8272 |  | 43192.6794 | 80618.9933 | 0
[17 empty] | 3C San Francisco 90.1-2007 | All climate zones | y = 0.2902x + 4511.3 |  |  | 3055.598 | 3C San Francisco 90.1-2007 | All climate zones | y = 0.2902x + 4511.3 |  |  | 3055.598 |  |  |  | 1.344 | 1.537 | 5325.0322 | Q-10 | 65.47 | 297.7901 | 19496.3148 |  | 25785.8685 | 50607.2155 |  | 30 |  | 5325.0322 | Q-10 | 65.47 | 491.3536 | 32168.9194 |  | 38546.6053 | 76040.5569 |  | 5325.0322 | Q-10 | 65.47 | 297.7901 | 19496.3148 |  | 25785.8685 |  | 50607.2155 | 0 | 30 |  | 5325.0322 | Q-10 | 65.47 | 491.3536 | 32168.9194 |  | 43268.9166 | 80762.8682 | 0
[17 empty] | 7 Duluth 90.1-2010 |  | R² = 0.8963 |  |  | 3318.354 | 7 Duluth 90.1-2010 |  | R² = 0.8963 |  |  | 3318.354 |  |  |  | 1.344 | 1.537 | 5455.4328 | Q-10 | 65.47 | 312.2062 | 20440.1399 |  | 26867.6175 | 52763.1902 |  | 30 |  | 5455.4328 | Q-10 | 65.47 | 515.1402 | 33726.2309 |  | 40329.681 | 79511.3447 |  | 5455.4328 | Q-10 | 65.47 | 312.2062 | 20440.1399 |  | 26867.6175 |  | 52763.1902 | 0 | 30 |  | 5455.4328 | Q-10 | 65.47 | 515.1402 | 33726.2309 |  | 45167.6333 | 84349.297 | 0
[17 empty] | 8 Fairbanks 90.1-2010 |  | Labor |  |  | 3369.21 | 8 Fairbanks 90.1-2010 |  | Labor |  |  | 3369.21 |  |  |  | 1.344 | 1.537 | 5524.2951 | Q-10 | 65.47 | 317.2964 | 20773.3924 |  | 27279.4054 | 53577.0929 |  | 30 |  | 5524.2951 | Q-10 | 65.47 | 523.539 | 34276.0975 |  | 40974.1272 | 80774.5198 |  | 5524.2951 | Q-10 | 65.47 | 317.2964 | 20773.3924 |  | 27279.4054 |  | 53577.0929 | 0 | 30 |  | 5524.2951 | Q-10 | 65.47 | 523.539 | 34276.0975 |  | 45873.1475 | 85673.5401 | 0
[17 empty] | 5A Chicago 90.1-2010 | All climate zones | y = 1.5764x + 9922.5 |  |  | 3426.423 | 5A Chicago 90.1-2010 | All climate zones | y = 1.5764x + 9922.5 |  |  | 3426.423 |  |  |  | 1.344 | 1.537 | 5560.5069 | Q-10 | 65.47 | 315.3198 | 20643.9897 |  | 27201.815 | 53406.3115 |  | 30 |  | 5560.5069 | Q-10 | 65.47 | 520.2777 | 34062.583 |  | 40764.8949 | 80387.9848 |  | 5560.5069 | Q-10 | 65.47 | 315.3198 | 20643.9897 |  | 27201.815 |  | 53406.3115 | 0 | 30 |  | 5560.5069 | Q-10 | 65.47 | 520.2777 | 34062.583 |  | 45696.0284 | 85319.1183 | 0
[17 empty] | 7 Duluth 90.1-2007 |  | R² = 0.9473 |  |  | 3437.018 | 7 Duluth 90.1-2007 |  | R² = 0.9473 |  |  | 3437.018 |  |  |  | 1.344 | 1.537 | 5573.041 | Q-10 | 65.47 | 319.3544 | 20908.1313 |  | 27473.2286 | 53954.4009 |  | 30 |  | 5573.041 | Q-10 | 65.47 | 526.9347 | 34498.4166 |  | 41248.3034 | 81319.7609 |  | 5573.041 | Q-10 | 65.47 | 319.3544 | 20908.1313 |  | 27473.2286 |  | 53954.4009 | 0 | 30 |  | 5573.041 | Q-10 | 65.47 | 526.9347 | 34498.4166 |  | 46190.5522 | 86262.0098 | 0
[17 empty] | 8 Fairbanks 90.1-2007 |  |  |  |  | 3500.588 | 8 Fairbanks 90.1-2007 |  |  |  |  | 3500.588 |  |  |  | 1.344 | 1.537 | 5533.0058 | Q-10 | 65.47 | 318.1283 | 20827.861 |  | 27343.3832 | 53704.25 |  | 30 |  | 5533.0058 | Q-10 | 65.47 | 524.9117 | 34365.9706 |  | 41077.8013 | 80976.7777 |  | 5533.0058 | Q-10 | 65.47 | 318.1283 | 20827.861 |  | 27343.3832 |  | 53704.25 | 0 | 30 |  | 5533.0058 | Q-10 | 65.47 | 524.9117 | 34365.9706 |  | 45984.5464 | 85883.5229 | 0
[17 empty] | 5A Chicago 90.1-2007 |  |  |  |  | 3538.73 | 5A Chicago 90.1-2007 |  |  |  |  | 3538.73 |  |  |  | 1.344 | 1.537 | 5528.4947 | Q-10 | 65.47 | 316.1077 | 20695.5731 |  | 27209.7627 | 53433.8306 |  | 30 |  | 5528.4947 | Q-10 | 65.47 | 521.5778 | 34147.6957 |  | 40836.8505 | 80513.0409 |  | 5528.4947 | Q-10 | 65.47 | 316.1077 | 20695.5731 |  | 27209.7627 |  | 53433.8306 | 0 | 30 |  | 5528.4947 | Q-10 | 65.47 | 521.5778 | 34147.6957 |  | 45739.5951 | 85415.7855 | 0
[17 empty] | 2A Houston 90.1-2010 |  |  |  |  | 3788.772 | 2A Houston 90.1-2010 |  |  |  |  | 3788.772 |  |  |  | 1.344 | 1.537 | 5663.377 | Q-10 | 65.47 | 328.2 | 21487.2513 |  | 28150.4753 | 55301.1036 |  | 30 |  | 5663.377 | Q-10 | 65.47 | 541.5299 | 35453.9646 |  | 42349.1027 | 83466.4443 |  | 5663.377 | Q-10 | 65.47 | 328.2 | 21487.2513 |  | 28150.4753 |  | 55301.1036 | 0 | 30 |  | 5663.377 | Q-10 | 65.47 | 541.5299 | 35453.9646 |  | 47371.4628 | 88488.8044 | 0
[17 empty] | 2A Houston 90.1-2007 |  |  |  |  | 3873.532 | 2A Houston 90.1-2007 |  |  |  |  | 3873.532 |  |  |  | 1.344 | 1.537 | 5677.3444 | Q-10 | 65.47 | 329.2156 | 21553.7467 |  | 28232.938 | 55464.0291 |  | 30 |  | 5677.3444 | Q-10 | 65.47 | 543.2058 | 35563.6821 |  | 42477.84 | 83718.8664 |  | 5677.3444 | Q-10 | 65.47 | 329.2156 | 21553.7467 |  | 28232.938 |  | 55464.0291 | 0 | 30 |  | 5677.3444 | Q-10 | 65.47 | 543.2058 | 35563.6821 |  | 47512.5865 | 88753.613 | 0
[17 empty] | 3B El Paso 90.1-2010 |  |  |  |  | 4026.1 | 3B El Paso 90.1-2010 |  |  |  |  | 4026.1 |  |  |  | 1.344 | 1.537 | 5667.0382 | Q-10 | 65.47 | 334.7161 | 21913.8629 |  | 28567.1506 | 56148.0517 |  | 30 |  | 5667.0382 | Q-10 | 65.47 | 552.2816 | 36157.8738 |  | 43119.0472 | 84943.9591 |  | 5667.0382 | Q-10 | 65.47 | 334.7161 | 21913.8629 |  | 28567.1506 |  | 56148.0517 | 0 | 30 |  | 5667.0382 | Q-10 | 65.47 | 552.2816 | 36157.8738 |  | 48144.654 | 89969.566 | 0
[17 empty] | 3B El Paso 90.1-2007 |  |  |  |  | 4138.407 | 3B El Paso 90.1-2007 |  |  |  |  | 4138.407 |  |  |  | 1.344 | 1.537 | 5693.3871 | Q-10 | 65.47 | 341.6567 | 22368.2611 |  | 29040.3174 | 57101.9655 |  | 30 |  | 5693.3871 | Q-10 | 65.47 | 563.7335 | 36907.6308 |  | 43953.7644 | 86554.7822 |  | 5693.3871 | Q-10 | 65.47 | 341.6567 | 22368.2611 |  | 29040.3174 |  | 57101.9655 | 0 | 30 |  | 5693.3871 | Q-10 | 65.47 | 563.7335 | 36907.6308 |  | 49002.7378 | 91603.7556 | 0
[17 empty] | 2B Phoenix 90.1-2010 |  |  |  |  | 4651.205 | 2B Phoenix 90.1-2010 |  |  |  |  | 4651.205 |  |  |  | 1.344 | 1.537 | 5891.0895 | Q-10 | 65.47 | 358.483 | 23469.8843 |  | 30362.4149 | 59723.3887 |  | 30 |  | 5891.0895 | Q-10 | 65.47 | 591.497 | 38725.3091 |  | 46064.5923 | 90680.991 |  | 5891.0895 | Q-10 | 65.47 | 358.483 | 23469.8843 |  | 30362.4149 |  | 59723.3887 | 0 | 30 |  | 5891.0895 | Q-10 | 65.47 | 591.497 | 38725.3091 |  | 51288.8909 | 95905.2896 | 0
[17 empty] | 2B Phoenix 90.1-2007 |  |  |  |  | 4771.988 | 2B Phoenix 90.1-2007 |  |  |  |  | 4771.988 |  |  |  | 1.344 | 1.537 | 5933.2863 | Q-10 | 65.47 | 362.1621 | 23710.7502 |  | 30650.1397 | 60294.1762 |  | 30 |  | 5933.2863 | Q-10 | 65.47 | 597.5674 | 39122.7378 |  | 46525.446 | 91581.4701 |  | 5933.2863 | Q-10 | 65.47 | 362.1621 | 23710.7502 |  | 30650.1397 |  | 60294.1762 | 0 | 30 |  | 5933.2863 | Q-10 | 65.47 | 597.5674 | 39122.7378 |  | 51787.1653 | 96843.1894 | 0
[17 empty] | Large Office | Data shown used to create these: | Curve Fits |  |  |  | Large Office | Data shown used to create these: | Curve Fits | [17 empty] | 30 | [16 empty] | 0 |  |  |  | 30
[17 empty] | 3C San Francisco 90.1-2010 |  | Material |  |  | 230185 | 3C San Francisco 90.1-2010 |  | Material |  |  | 230185 |  |  |  | 1.344 | 1.537 | 663915.5344 | Q-10 | 65.47 | 48101.7068 | 3149218.7424 |  | 3908593.8577 | 7721728.1344 |  | 30 |  | 663915.5344 | Q-10 | 65.47 | 79367.8162 | 5196210.9249 |  | 6098562.3399 | 11958688.7992 |  | 663915.5344 | Q-10 | 65.47 | 48101.7068 | 3149218.7424 |  | 3908593.8577 |  | 7721728.1344 | 0 | 30 |  | 663915.5344 | Q-10 | 65.47 | 79367.8162 | 5196210.9249 |  | 6687331.7029 | 12547458.1621 | 0
[17 empty] | 3C San Francisco 90.1-2007 | All climate zones | y = 0.7091x + 503192 |  |  | 245425 | 3C San Francisco 90.1-2007 | All climate zones | y = 0.7091x + 503192 |  |  | 245425 |  |  |  | 1.344 | 1.537 | 675326.6127 | Q-10 | 65.47 | 49125.1967 | 3216226.6286 |  | 3988209.0048 | 7879762.2461 |  | 30 |  | 675326.6127 | Q-10 | 65.47 | 81056.5746 | 5306773.9372 |  | 6226556.3305 | 12208656.8804 |  | 675326.6127 | Q-10 | 65.47 | 49125.1967 | 3216226.6286 |  | 3988209.0048 |  | 7879762.2461 | 0 | 30 |  | 675326.6127 | Q-10 | 65.47 | 81056.5746 | 5306773.9372 |  | 6825445.1935 | 12807545.7435 | 0
[17 empty] | 7 Duluth 90.1-2010 |  | R² = 0.8176 |  |  | 253877 | 7 Duluth 90.1-2010 |  | R² = 0.8176 |  |  | 253877 |  |  |  | 1.344 | 1.537 | 689128.217 | Q-10 | 65.47 | 50442.5718 | 3302475.1771 |  | 4089526.362 | 8081129.7561 |  | 30 |  | 689128.217 | Q-10 | 65.47 | 83230.2435 | 5449084.0421 |  | 6390725.3541 | 12528937.6132 |  | 689128.217 | Q-10 | 65.47 | 50442.5718 | 3302475.1771 |  | 4089526.362 |  | 8081129.7561 | 0 | 30 |  | 689128.217 | Q-10 | 65.47 | 83230.2435 | 5449084.0421 |  | 7001853.6683 | 13140065.9275 | 0
[17 empty] | 8 Fairbanks 90.1-2010 |  | Labor |  |  | 254832 | 8 Fairbanks 90.1-2010 |  | Labor |  |  | 254832 |  |  |  | 1.344 | 1.537 | 685966.793 | Q-10 | 65.47 | 50314.7022 | 3294103.5536 |  | 4077310.1391 | 8057380.4857 |  | 30 |  | 685966.793 | Q-10 | 65.47 | 83019.2586 | 5435270.8635 |  | 6373603.7111 | 12494841.3675 |  | 685966.793 | Q-10 | 65.47 | 50314.7022 | 3294103.5536 |  | 4077310.1391 |  | 8057380.4857 | 0 | 30 |  | 685966.793 | Q-10 | 65.47 | 83019.2586 | 5435270.8635 |  | 6981928.4313 | 13103166.0878 | 0
[17 empty] | 5A Chicago 90.1-2010 | All climate zones | y = 3.2521x + 2E+06 |  |  | 256016 | 5A Chicago 90.1-2010 | All climate zones | y = 3.2521x + 2E+06 |  |  | 256016 |  |  |  | 1.344 | 1.537 | 675696.0406 | Q-10 | 65.47 | 49513.8753 | 3241673.4187 |  | 4013260.5975 | 7930630.0568 |  | 30 |  | 675696.0406 | Q-10 | 65.47 | 81697.8943 | 5348761.1409 |  | 6272580.8386 | 12297038.0201 |  | 675696.0406 | Q-10 | 65.47 | 49513.8753 | 3241673.4187 |  | 4013260.5975 |  | 7930630.0568 | 0 | 30 |  | 675696.0406 | Q-10 | 65.47 | 81697.8943 | 5348761.1409 |  | 6871797.3153 | 12896254.4969 | 0
[17 empty] | 2A Houston 90.1-2010 |  | R² = 0.8751 |  |  | 258539 | 2A Houston 90.1-2010 |  | R² = 0.8751 |  |  | 258539 |  |  |  | 1.344 | 1.537 | 679011.6898 | Q-10 | 65.47 | 49650.0737 | 3250590.3257 |  | 4026204.9325 | 7955806.948 |  | 30 |  | 679011.6898 | Q-10 | 65.47 | 81922.6216 | 5363474.0374 |  | 6290784.0211 | 12333269.7483 |  | 679011.6898 | Q-10 | 65.47 | 49650.0737 | 3250590.3257 |  | 4026204.9325 |  | 7955806.948 | 0 | 30 |  | 679011.6898 | Q-10 | 65.47 | 81922.6216 | 5363474.0374 |  | 6892940.8609 | 12935426.5881 | 0
[17 empty] | 7 Duluth 90.1-2007 |  |  |  |  | 259259 | 7 Duluth 90.1-2007 |  |  |  |  | 259259 |  |  |  | 1.344 | 1.537 | 698774.9563 | Q-10 | 65.47 | 51261.6796 | 3356102.1665 |  | 4153915.5633 | 8208792.6861 |  | 30 |  | 698774.9563 | Q-10 | 65.47 | 84581.7714 | 5537568.5747 |  | 6493495.111 | 12729838.642 |  | 698774.9563 | Q-10 | 65.47 | 51261.6796 | 3356102.1665 |  | 4153915.5633 |  | 8208792.6861 | 0 | 30 |  | 698774.9563 | Q-10 | 65.47 | 84581.7714 | 5537568.5747 |  | 7113178.2854 | 13349521.8164 | 0
[17 empty] | 8 Fairbanks 90.1-2007 |  |  |  |  | 271190 | 8 Fairbanks 90.1-2007 |  |  |  |  | 271190 |  |  |  | 1.344 | 1.537 | 702825.2456 | Q-10 | 65.47 | 51278.4716 | 3357201.536 |  | 4160272.692 | 8220299.4736 |  | 30 |  | 702825.2456 | Q-10 | 65.47 | 84609.4781 | 5539382.5343 |  | 6498111.544 | 12740319.3239 |  | 702825.2456 | Q-10 | 65.47 | 51278.4716 | 3357201.536 |  | 4160272.692 |  | 8220299.4736 | 0 | 30 |  | 702825.2456 | Q-10 | 65.47 | 84609.4781 | 5539382.5343 |  | 7121386.5702 | 13363594.3501 | 0
[17 empty] | 5A Chicago 90.1-2007 |  |  |  |  | 271316 | 5A Chicago 90.1-2007 |  |  |  |  | 271316 |  |  |  | 1.344 | 1.537 | 697784.9223 | Q-10 | 65.47 | 51200.781 | 3352115.1308 |  | 4148771.6716 | 8198671.7247 |  | 30 |  | 697784.9223 | Q-10 | 65.47 | 84481.2886 | 5530989.9658 |  | 6485676.708 | 12714451.5961 |  | 697784.9223 | Q-10 | 65.47 | 51200.781 | 3352115.1308 |  | 4148771.6716 |  | 8198671.7247 | 0 | 30 |  | 697784.9223 | Q-10 | 65.47 | 84481.2886 | 5530989.9658 |  | 7104481.9067 | 13333256.7948 | 0
[17 empty] | 2A Houston 90.1-2007 |  |  |  |  | 271572 | 2A Houston 90.1-2007 |  |  |  |  | 271572 |  |  |  | 1.344 | 1.537 | 699129.7767 | Q-10 | 65.47 | 51290.041 | 3357958.984 |  | 4156172.2213 | 8213260.982 |  | 30 |  | 699129.7767 | Q-10 | 65.47 | 84628.5676 | 5540632.3235 |  | 6497067.0341 | 12736829.1343 |  | 699129.7767 | Q-10 | 65.47 | 51290.041 | 3357958.984 |  | 4156172.2213 |  | 8213260.982 | 0 | 30 |  | 699129.7767 | Q-10 | 65.47 | 84628.5676 | 5540632.3235 |  | 7117064.868 | 13356826.9683 | 0
[17 empty] | 3B El Paso 90.1-2010 |  |  |  |  | 281318 | 3B El Paso 90.1-2010 |  |  |  |  | 281318 |  |  |  | 1.344 | 1.537 | 690016.8724 | Q-10 | 65.47 | 50859.3711 | 3329763.0255 |  | 4117034.3576 | 8136814.2554 |  | 30 |  | 690016.8724 | Q-10 | 65.47 | 83917.9623 | 5494108.992 |  | 6440400.5298 | 12624526.3942 |  | 690016.8724 | Q-10 | 65.47 | 50859.3711 | 3329763.0255 |  | 4117034.3576 |  | 8136814.2554 | 0 | 30 |  | 690016.8724 | Q-10 | 65.47 | 83917.9623 | 5494108.992 |  | 7052316.9158 | 13236442.7802 | 0
[17 empty] | 2B Phoenix 90.1-2010 |  |  |  |  | 285937 | 2B Phoenix 90.1-2010 |  |  |  |  | 285937 |  |  |  | 1.344 | 1.537 | 707455.8883 | Q-10 | 65.47 | 52420.6289 | 3431978.5758 |  | 4238523.532 | 8377957.9961 |  | 30 |  | 707455.8883 | Q-10 | 65.47 | 86494.0377 | 5662764.6501 |  | 6635666.867 | 13005887.4054 |  | 707455.8883 | Q-10 | 65.47 | 52420.6289 | 3431978.5758 |  | 4238523.532 |  | 8377957.9961 | 0 | 30 |  | 707455.8883 | Q-10 | 65.47 | 86494.0377 | 5662764.6501 |  | 7263048.4105 | 13633268.9489 | 0
[17 empty] | 3B El Paso 90.1-2007 |  |  |  |  | 298776 | 3B El Paso 90.1-2007 |  |  |  |  | 298776 |  |  |  | 1.344 | 1.537 | 711463.6654 | Q-10 | 65.47 | 52571.3975 | 3441849.3946 |  | 4253293.8057 | 8406606.8657 |  | 30 |  | 711463.6654 | Q-10 | 65.47 | 86742.8059 | 5679051.5011 |  | 6656037.1948 | 13046552.3613 |  | 711463.6654 | Q-10 | 65.47 | 52571.3975 | 3441849.3946 |  | 4253293.8057 |  | 8406606.8657 | 0 | 30 |  | 711463.6654 | Q-10 | 65.47 | 86742.8059 | 5679051.5011 |  | 7286972.8897 | 13677488.0562 | 0
[17 empty] | 2B Phoenix 90.1-2007 |  |  |  |  | 300964 | 2B Phoenix 90.1-2007 |  |  |  |  | 300964 |  |  |  | 1.344 | 1.537 | 719825.4451 | Q-10 | 65.47 | 53326.1176 | 3491260.9202 |  | 4311932.9592 | 8523019.3245 |  | 30 |  | 719825.4451 | Q-10 | 65.47 | 87988.0941 | 5760580.5183 |  | 6750385.4398 | 13230791.4032 |  | 719825.4451 | Q-10 | 65.47 | 53326.1176 | 3491260.9202 |  | 4311932.9592 |  | 8523019.3245 | 0 | 30 |  | 719825.4451 | Q-10 | 65.47 | 87988.0941 | 5760580.5183 |  | 7388736.4751 | 13869142.4385 | 0
[17 empty] | Stand-Alone Retail | Data shown used to create these: | Curve Fits |  |  |  | Stand-Alone Retail | Data shown used to create these: | Curve Fits | [17 empty] | 30 | [16 empty] | 0 |  |  |  | 30
[17 empty] | 3C San Francisco 90.1-2010 |  | Material |  |  | 17869.527 | 3C San Francisco 90.1-2010 |  | Material |  |  | 17869.527 |  |  |  | 1.344 | 1.537 | 24053.6174 | Q-10 | 65.47 | 1808.0927 | 118375.8266 |  | 145740.2329 | 288169.6769 |  | 30 |  | 24053.6174 | Q-10 | 65.47 | 2983.3529 | 195320.1138 |  | 228650.7973 | 448024.5285 |  | 24053.6174 | Q-10 | 65.47 | 1808.0927 | 118375.8266 |  | 145740.2329 |  | 288169.6769 | 0 | 30 |  | 24053.6174 | Q-10 | 65.47 | 2983.3529 | 195320.1138 |  | 249981.8737 | 469355.6049 | 0
[17 empty] | 3C San Francisco 90.1-2007 | All climate zones | y = 1.6479x + 55981 |  |  | 18594.225 | 3C San Francisco 90.1-2007 | All climate zones | y = 1.6479x + 55981 |  |  | 18594.225 |  |  |  | 1.344 | 1.537 | 23027.9819 | Q-10 | 65.47 | 1725.7147 | 112982.5432 |  | 139192.0774 | 275202.6025 |  | 30 |  | 23027.9819 | Q-10 | 65.47 | 2847.4293 | 186421.1963 |  | 218279.0824 | 427728.2606 |  | 23027.9819 | Q-10 | 65.47 | 1725.7147 | 112982.5432 |  | 139192.0774 |  | 275202.6025 | 0 | 30 |  | 23027.9819 | Q-10 | 65.47 | 2847.4293 | 186421.1963 |  | 238700.6113 | 448149.7895 | 0
[17 empty] | 2A Houston 90.1-2010 |  | R² = 0.653 |  |  | 19912.243 | 2A Houston 90.1-2010 |  | R² = 0.653 |  |  | 19912.243 |  |  |  | 1.344 | 1.537 | 24479.6468 | Q-10 | 65.47 | 1853.3094 | 121336.1655 |  | 149155.4325 | 294971.2448 |  | 30 |  | 24479.6468 | Q-10 | 65.47 | 3057.9605 | 200204.673 |  | 234254.5628 | 458938.8826 |  | 24479.6468 | Q-10 | 65.47 | 1853.3094 | 121336.1655 |  | 149155.4325 |  | 294971.2448 | 0 | 30 |  | 24479.6468 | Q-10 | 65.47 | 3057.9605 | 200204.673 |  | 255963.4479 | 480647.7677 | 0
[17 empty] | 8 Fairbanks 90.1-2010 |  | Labor |  |  | 20075.406 | 8 Fairbanks 90.1-2010 |  | Labor |  |  | 20075.406 |  |  |  | 1.344 | 1.537 | 24838.5194 | Q-10 | 65.47 | 1857.7226 | 121625.1014 |  | 149903.618 | 296367.2389 |  | 30 |  | 24838.5194 | Q-10 | 65.47 | 3065.2424 | 200681.4173 |  | 235008.1938 | 460528.1306 |  | 24838.5194 | Q-10 | 65.47 | 1857.7226 | 121625.1014 |  | 149903.618 |  | 296367.2389 | 0 | 30 |  | 24838.5194 | Q-10 | 65.47 | 3065.2424 | 200681.4173 |  | 257035.3321 | 482555.2688 | 0
[17 empty] | 7 Duluth 90.1-2010 | All climate zones | y = 0.2548x + 18981 |  |  | 20187.713 | 7 Duluth 90.1-2010 | All climate zones | y = 0.2548x + 18981 |  |  | 20187.713 |  |  |  | 1.344 | 1.537 | 24860.9491 | Q-10 | 65.47 | 1865.1998 | 122114.631 |  | 150405.5794 | 297381.1595 |  | 30 |  | 24860.9491 | Q-10 | 65.47 | 3077.5797 | 201489.1411 |  | 235903.5664 | 462253.6566 |  | 24860.9491 | Q-10 | 65.47 | 1865.1998 | 122114.631 |  | 150405.5794 |  | 297381.1595 | 0 | 30 |  | 24860.9491 | Q-10 | 65.47 | 3077.5797 | 201489.1411 |  | 257950.5956 | 484300.6858 | 0
[17 empty] | 8 Fairbanks 90.1-2007 |  | R² = 0.4026 |  |  | 20344.519 | 8 Fairbanks 90.1-2007 |  | R² = 0.4026 |  |  | 20344.519 |  |  |  | 1.344 | 1.537 | 23693.168 | Q-10 | 65.47 | 1764.6613 | 115532.3735 |  | 142523.6302 | 281749.1717 |  | 30 |  | 23693.168 | Q-10 | 65.47 | 2911.6911 | 190628.4163 |  | 223300.053 | 437621.6373 |  | 23693.168 | Q-10 | 65.47 | 1764.6613 | 115532.3735 |  | 142523.6302 |  | 281749.1717 | 0 | 30 |  | 23693.168 | Q-10 | 65.47 | 2911.6911 | 190628.4163 |  | 244311.4779 | 458633.0622 | 0
[17 empty] | 7 Duluth 90.1-2007 |  |  |  |  | 20594.561 | 7 Duluth 90.1-2007 |  |  |  |  | 20594.561 |  |  |  | 1.344 | 1.537 | 23714.1003 | Q-10 | 65.47 | 1786.22 | 116943.8253 |  | 143913.7386 | 284571.6642 |  | 30 |  | 23714.1003 | Q-10 | 65.47 | 2947.263 | 192957.3117 |  | 225853.1722 | 442524.5842 |  | 23714.1003 | Q-10 | 65.47 | 1786.22 | 116943.8253 |  | 143913.7386 |  | 284571.6642 | 0 | 30 |  | 23714.1003 | Q-10 | 65.47 | 2947.263 | 192957.3117 |  | 246883.1602 | 463554.5722 | 0
[17 empty] | 5A Chicago 90.1-2007 |  |  |  |  | 21058.622 | 5A Chicago 90.1-2007 |  |  |  |  | 21058.622 |  |  |  | 1.344 | 1.537 | 23474.7283 | Q-10 | 65.47 | 1834.799 | 120124.2926 |  | 146671.4659 | 290270.4868 |  | 30 |  | 23474.7283 | Q-10 | 65.47 | 3027.4184 | 198205.0827 |  | 231419.5355 | 453099.3465 |  | 23474.7283 | Q-10 | 65.47 | 1834.799 | 120124.2926 |  | 146671.4659 |  | 290270.4868 | 0 | 30 |  | 23474.7283 | Q-10 | 65.47 | 3027.4184 | 198205.0827 |  | 252237.2451 | 473917.0562 | 0
[17 empty] | 5A Chicago 90.1-2010 |  |  |  |  | 21062.86 | 5A Chicago 90.1-2010 |  |  |  |  | 21062.86 |  |  |  | 1.344 | 1.537 | 24612.6341 | Q-10 | 65.47 | 1928.187 | 126238.402 |  | 154062.3622 | 304913.3982 |  | 30 |  | 24612.6341 | Q-10 | 65.47 | 3181.5085 | 208293.3633 |  | 243161.2956 | 476067.293 |  | 24612.6341 | Q-10 | 65.47 | 1928.187 | 126238.402 |  | 154062.3622 |  | 304913.3982 | 0 | 30 |  | 24612.6341 | Q-10 | 65.47 | 3181.5085 | 208293.3633 |  | 264988.1157 | 497894.113 | 0
[17 empty] | 2A Houston 90.1-2007 |  |  |  |  | 21287.474 | 2A Houston 90.1-2007 |  |  |  |  | 21287.474 |  |  |  | 1.344 | 1.537 | 23595.4942 | Q-10 | 65.47 | 1845.4964 | 120824.6493 |  | 147505.5517 | 291925.6953 |  | 30 |  | 23595.4942 | Q-10 | 65.47 | 3045.0691 | 199360.6714 |  | 232758.2867 | 455714.4523 |  | 23595.4942 | Q-10 | 65.47 | 1845.4964 | 120824.6493 |  | 147505.5517 |  | 291925.6953 | 0 | 30 |  | 23595.4942 | Q-10 | 65.47 | 3045.0691 | 199360.6714 |  | 253683.0932 | 476639.2588 | 0
[17 empty] | 3B El Paso 90.1-2010 |  |  |  |  | 23285.691 | 3B El Paso 90.1-2010 |  |  |  |  | 23285.691 |  |  |  | 1.344 | 1.537 | 25234.9412 | Q-10 | 65.47 | 1986.5171 | 130057.2774 |  | 158563.0991 | 313855.3177 |  | 30 |  | 25234.9412 | Q-10 | 65.47 | 3277.7533 | 214594.5077 |  | 250437.5994 | 490267.0483 |  | 25234.9412 | Q-10 | 65.47 | 1986.5171 | 130057.2774 |  | 158563.0991 |  | 313855.3177 | 0 | 30 |  | 25234.9412 | Q-10 | 65.47 | 3277.7533 | 214594.5077 |  | 272816.2899 | 512645.7388 | 0
[17 empty] | 2B Phoenix 90.1-2010 |  |  |  |  | 23677.706 | 2B Phoenix 90.1-2010 |  |  |  |  | 23677.706 |  |  |  | 1.344 | 1.537 | 25849.2066 | Q-10 | 65.47 | 2007.8867 | 131456.3433 |  | 160717.0244 | 318022.5743 |  | 30 |  | 25849.2066 | Q-10 | 65.47 | 3313.0131 | 216902.9664 |  | 253354.9441 | 496107.1171 |  | 25849.2066 | Q-10 | 65.47 | 2007.8867 | 131456.3433 |  | 160717.0244 |  | 318022.5743 | 0 | 30 |  | 25849.2066 | Q-10 | 65.47 | 3313.0131 | 216902.9664 |  | 276278.3736 | 519030.5466 | 0
[17 empty] | 3B El Paso 90.1-2007 |  |  |  |  | 24031.579 | 3B El Paso 90.1-2007 |  |  |  |  | 24031.579 |  |  |  | 1.344 | 1.537 | 24888.2633 | Q-10 | 65.47 | 1940.6309 | 127053.1027 |  | 155209.3276 | 307150.6936 |  | 30 |  | 24888.2633 | Q-10 | 65.47 | 3202.0409 | 209637.6195 |  | 244806.6558 | 479332.5386 |  | 24888.2633 | Q-10 | 65.47 | 1940.6309 | 127053.1027 |  | 155209.3276 |  | 307150.6936 | 0 | 30 |  | 24888.2633 | Q-10 | 65.47 | 3202.0409 | 209637.6195 |  | 266877.9076 | 501403.7904 | 0
[17 empty] | 2B Phoenix 90.1-2007 |  |  |  |  | 24279.502 | 2B Phoenix 90.1-2007 |  |  |  |  | 24279.502 |  |  |  | 1.344 | 1.537 | 24907.6016 | Q-10 | 65.47 | 1929.756 | 126341.1256 |  | 154547.2067 | 305795.9338 |  | 30 |  | 24907.6016 | Q-10 | 65.47 | 3184.0974 | 208462.8572 |  | 243538.2642 | 476908.7229 |  | 24907.6016 | Q-10 | 65.47 | 1929.756 | 126341.1256 |  | 154547.2067 |  | 305795.9338 | 0 | 30 |  | 24907.6016 | Q-10 | 65.47 | 3184.0974 | 208462.8572 |  | 265626.6654 | 498997.1241 | 0
[17 empty] | Primary School | Data shown used to create these: | Curve Fits |  |  |  | Primary School | Data shown used to create these: | Curve Fits | [17 empty] | 30 | [16 empty] | 0 |  |  |  | 30
[17 empty] | 3C San Francisco 90.1-2010 |  | Material |  |  | 35054.617 | 3C San Francisco 90.1-2010 |  | Material |  |  | 35054.617 |  |  |  | 1.344 | 1.537 | 53620.9438 | Q-10 | 65.47 | 3151.3531 | 206319.0884 |  | 269307.2928 | 529247.325 |  | 30 |  | 53620.9438 | Q-10 | 65.47 | 5199.7326 | 340426.4959 |  | 406139.0881 | 800186.5278 |  | 53620.9438 | Q-10 | 65.47 | 3151.3531 | 206319.0884 |  | 269307.2928 |  | 529247.325 | 0 | 30 |  | 53620.9438 | Q-10 | 65.47 | 5199.7326 | 340426.4959 |  | 453690.8734 | 847738.3131 | 0
[17 empty] | 5A Chicago 90.1-2010 | All climate zones | y = 0.7194x + 28317 |  |  | 37404.588 | 5A Chicago 90.1-2010 | All climate zones | y = 0.7194x + 28317 |  |  | 37404.588 |  |  |  | 1.344 | 1.537 | 54570.3589 | Q-10 | 65.47 | 3264.1396 | 213703.2171 |  | 277677.9284 | 545951.5044 |  | 30 |  | 54570.3589 | Q-10 | 65.47 | 5385.8303 | 352610.3083 |  | 420043.0795 | 827223.7466 |  | 54570.3589 | Q-10 | 65.47 | 3264.1396 | 213703.2171 |  | 277677.9284 |  | 545951.5044 | 0 | 30 |  | 54570.3589 | Q-10 | 65.47 | 5385.8303 | 352610.3083 |  | 468436.819 | 875617.4861 | 0
[17 empty] | 2A Houston 90.1-2010 |  | R² = 0.8831 |  |  | 37580.465 | 2A Houston 90.1-2010 |  | R² = 0.8831 |  |  | 37580.465 |  |  |  | 1.344 | 1.537 | 55188.5807 | Q-10 | 65.47 | 3292.9523 | 215589.5883 |  | 280307.5141 | 551085.6832 |  | 30 |  | 55188.5807 | Q-10 | 65.47 | 5433.3713 | 355722.8207 |  | 423839.7611 | 834751.1625 |  | 55188.5807 | Q-10 | 65.47 | 3292.9523 | 215589.5883 |  | 280307.5141 |  | 551085.6832 | 0 | 30 |  | 55188.5807 | Q-10 | 65.47 | 5433.3713 | 355722.8207 |  | 472781.7482 | 883693.1496 | 0
[17 empty] | 3B El Paso 90.1-2010 |  | Labor |  |  | 38726.844 | 3B El Paso 90.1-2010 |  | Labor |  |  | 38726.844 |  |  |  | 1.344 | 1.537 | 55188.6914 | Q-10 | 65.47 | 3317.2194 | 217178.3545 |  | 281841.5935 | 554208.6393 |  | 30 |  | 55188.6914 | Q-10 | 65.47 | 5473.412 | 358344.2849 |  | 426698.3407 | 840231.317 |  | 55188.6914 | Q-10 | 65.47 | 3317.2194 | 217178.3545 |  | 281841.5935 |  | 554208.6393 | 0 | 30 |  | 55188.6914 | Q-10 | 65.47 | 5473.412 | 358344.2849 |  | 475640.4259 | 889173.4022 | 0
[17 empty] | 8 Fairbanks 90.1-2010 | All climate zones | y = 2.3902x + 122683 |  |  | 41513.329 | 8 Fairbanks 90.1-2010 | All climate zones | y = 2.3902x + 122683 |  |  | 41513.329 |  |  |  | 1.344 | 1.537 | 63139.493 | Q-10 | 65.47 | 3377.1365 | 221101.1294 |  | 296024.5556 | 580265.1779 |  | 30 |  | 63139.493 | Q-10 | 65.47 | 5572.2753 | 364816.8634 |  | 438935.5233 | 866891.8798 |  | 63139.493 | Q-10 | 65.47 | 3377.1365 | 221101.1294 |  | 296024.5556 |  | 580265.1779 | 0 | 30 |  | 63139.493 | Q-10 | 65.47 | 5572.2753 | 364816.8634 |  | 494928.488 | 922884.8444 | 0
[17 empty] | 5A Chicago 90.1-2007 |  | R² = 0.9806 |  |  | 42066.388 | 5A Chicago 90.1-2007 |  | R² = 0.9806 |  |  | 42066.388 |  |  |  | 1.344 | 1.537 | 58574.8997 | Q-10 | 65.47 | 3357.668 | 219826.5244 |  | 288825.7933 | 567227.2174 |  | 30 |  | 58574.8997 | Q-10 | 65.47 | 5540.1522 | 362713.7653 |  | 433668.7778 | 854957.4429 |  | 58574.8997 | Q-10 | 65.47 | 3357.668 | 219826.5244 |  | 288825.7933 |  | 567227.2174 | 0 | 30 |  | 58574.8997 | Q-10 | 65.47 | 5540.1522 | 362713.7653 |  | 485613.7988 | 906902.4639 | 0
[17 empty] | 7 Duluth 90.1-2010 |  |  |  |  | 42464.76 | 7 Duluth 90.1-2010 |  |  |  |  | 42464.76 |  |  |  | 1.344 | 1.537 | 56869.5314 | Q-10 | 65.47 | 3429.1281 | 224505.019 |  | 291113.0767 | 572487.6271 |  | 30 |  | 56869.5314 | Q-10 | 65.47 | 5658.0614 | 370433.2814 |  | 440975.4088 | 868278.2215 |  | 56869.5314 | Q-10 | 65.47 | 3429.1281 | 224505.019 |  | 291113.0767 |  | 572487.6271 | 0 | 30 |  | 56869.5314 | Q-10 | 65.47 | 5658.0614 | 370433.2814 |  | 491408.0859 | 918710.8986 | 0
[17 empty] | 3C San Francisco 90.1-2007 |  |  |  |  | 43291.17 | 3C San Francisco 90.1-2007 |  |  |  |  | 43291.17 |  |  |  | 1.344 | 1.537 | 59289.5655 | Q-10 | 65.47 | 3409.9773 | 223251.2135 |  | 293066.7057 | 575607.4847 |  | 30 |  | 59289.5655 | Q-10 | 65.47 | 5626.4625 | 368364.5022 |  | 440296.026 | 867950.0937 |  | 59289.5655 | Q-10 | 65.47 | 3409.9773 | 223251.2135 |  | 293066.7057 |  | 575607.4847 | 0 | 30 |  | 59289.5655 | Q-10 | 65.47 | 5626.4625 | 368364.5022 |  | 492874.8224 | 920528.8902 | 0
[17 empty] | 2A Houston 90.1-2007 |  |  |  |  | 44649.449 | 2A Houston 90.1-2007 |  |  |  |  | 44649.449 |  |  |  | 1.344 | 1.537 | 60114.8423 | Q-10 | 65.47 | 3508.1462 | 229678.3293 |  | 300351.0476 | 590144.2192 |  | 30 |  | 60114.8423 | Q-10 | 65.47 | 5788.4412 | 378969.2434 |  | 452397.2938 | 891481.3795 |  | 60114.8423 | Q-10 | 65.47 | 3508.1462 | 229678.3293 |  | 300351.0476 |  | 590144.2192 | 0 | 30 |  | 60114.8423 | Q-10 | 65.47 | 5788.4412 | 378969.2434 |  | 505707.9569 | 944792.0426 | 0
[17 empty] | 3B El Paso 90.1-2007 |  |  |  |  | 46596.81 | 3B El Paso 90.1-2007 |  |  |  |  | 46596.81 |  |  |  | 1.344 | 1.537 | 61199.8034 | Q-10 | 65.47 | 3570.1778 | 233739.5417 |  | 305690.6721 | 600630.0173 |  | 30 |  | 61199.8034 | Q-10 | 65.47 | 5890.7934 | 385670.2438 |  | 460410.9932 | 907281.0405 |  | 61199.8034 | Q-10 | 65.47 | 3570.1778 | 233739.5417 |  | 305690.6721 |  | 600630.0173 | 0 | 30 |  | 61199.8034 | Q-10 | 65.47 | 5890.7934 | 385670.2438 |  | 514683.8147 | 961553.862 | 0
[17 empty] | 8 Fairbanks 90.1-2007 |  |  |  |  | 47094.775 | 8 Fairbanks 90.1-2007 |  |  |  |  | 47094.775 |  |  |  | 1.344 | 1.537 | 62766.6473 | Q-10 | 65.47 | 3563.6439 | 233311.7644 |  | 307326.2862 | 603404.6979 |  | 30 |  | 62766.6473 | Q-10 | 65.47 | 5880.0124 | 384964.4112 |  | 460662.013 | 908393.0715 |  | 62766.6473 | Q-10 | 65.47 | 3563.6439 | 233311.7644 |  | 307326.2862 |  | 603404.6979 | 0 | 30 |  | 62766.6473 | Q-10 | 65.47 | 5880.0124 | 384964.4112 |  | 516324.3331 | 964055.3916 | 0
[17 empty] | 7 Duluth 90.1-2007 |  |  |  |  | 48137.323 | 7 Duluth 90.1-2007 |  |  |  |  | 48137.323 |  |  |  | 1.344 | 1.537 | 63027.4877 | Q-10 | 65.47 | 3599.5537 | 235662.7784 |  | 309937.2075 | 608627.4736 |  | 30 |  | 63027.4877 | Q-10 | 65.47 | 5939.2635 | 388843.5844 |  | 465061.8738 | 916932.9459 |  | 63027.4877 | Q-10 | 65.47 | 3599.5537 | 235662.7784 |  | 309937.2075 |  | 608627.4736 | 0 | 30 |  | 63027.4877 | Q-10 | 65.47 | 5939.2635 | 388843.5844 |  | 520955.5107 | 972826.5828 | 0
[17 empty] | 2B Phoenix 90.1-2010 |  |  |  |  | 50716.146 | 2B Phoenix 90.1-2010 |  |  |  |  | 50716.146 |  |  |  | 1.344 | 1.537 | 63463.7216 | Q-10 | 65.47 | 3760.6298 | 246208.4323 |  | 320689.2799 | 630361.4337 |  | 30 |  | 63463.7216 | Q-10 | 65.47 | 6205.0392 | 406243.9132 |  | 484319.7824 | 954027.4171 |  | 63463.7216 | Q-10 | 65.47 | 3760.6298 | 246208.4323 |  | 320689.2799 |  | 630361.4337 | 0 | 30 |  | 63463.7216 | Q-10 | 65.47 | 6205.0392 | 406243.9132 |  | 540600.2773 | 1010307.9121 | 0
[17 empty] | 2B Phoenix 90.1-2007 |  |  |  |  | 58073.314 | 2B Phoenix 90.1-2007 |  |  |  |  | 58073.314 |  |  |  | 1.344 | 1.537 | 70667.8186 | Q-10 | 65.47 | 4025.3779 | 263541.4906 |  | 346843.4032 | 681052.7125 |  | 30 |  | 70667.8186 | Q-10 | 65.47 | 6641.8735 | 434843.4596 |  | 520198.3219 | 1025709.6001 |  | 70667.8186 | Q-10 | 65.47 | 4025.3779 | 263541.4906 |  | 346843.4032 |  | 681052.7125 | 0 | 30 |  | 70667.8186 | Q-10 | 65.47 | 6641.8735 | 434843.4596 |  | 582867.5086 | 1088378.7868 | 0
[17 empty] | Small Hotel | Data shown used to create these: | Curve Fits |  |  |  | Small Hotel | Data shown used to create these: | Curve Fits | [17 empty] | 30 | [16 empty] | 0 |  |  |  | 30
[17 empty] | 3C San Francisco 90.1-2010 |  | Material |  |  | 3492.112 | 3C San Francisco 90.1-2010 |  | Material |  |  | 3492.112 |  |  |  | 1.344 | 1.537 | 8425.4318 | Q-10 | 65.47 | 532.8548 | 34886.0038 |  | 44698.1609 | 88009.5965 |  | 30 |  | 8425.4318 | Q-10 | 65.47 | 879.2104 | 57561.9062 |  | 68255.3964 | 134242.7344 |  | 8425.4318 | Q-10 | 65.47 | 532.8548 | 34886.0038 |  | 44698.1609 |  | 88009.5965 | 0 | 30 |  | 8425.4318 | Q-10 | 65.47 | 879.2104 | 57561.9062 |  | 75727.1844 | 141714.5224 | 0
[17 empty] | 8 Fairbanks 90.1-2010 | All climate zones | y = 0.7074x + 6086.9 |  |  | 3737.916 | 8 Fairbanks 90.1-2010 | All climate zones | y = 0.7074x + 6086.9 |  |  | 3737.916 |  |  |  | 1.344 | 1.537 | 8587.9865 | Q-10 | 65.47 | 547.4913 | 35844.2536 |  | 45835.8777 | 90268.1178 |  | 30 |  | 8587.9865 | Q-10 | 65.47 | 903.3606 | 59143.0184 |  | 70085.3708 | 137816.3757 |  | 8587.9865 | Q-10 | 65.47 | 547.4913 | 35844.2536 |  | 45835.8777 |  | 90268.1178 | 0 | 30 |  | 8587.9865 | Q-10 | 65.47 | 903.3606 | 59143.0184 |  | 77701.3145 | 145432.3194 | 0
[17 empty] | 5A Chicago 90.1-2010 |  | R² = 0.9622 |  |  | 4411.758 | 5A Chicago 90.1-2010 |  | R² = 0.9622 |  |  | 4411.758 |  |  |  | 1.344 | 1.537 | 9353.6082 | Q-10 | 65.47 | 613.6193 | 40173.6532 |  | 51016.9016 | 100544.163 |  | 30 |  | 9353.6082 | Q-10 | 65.47 | 1012.4718 | 66286.5278 |  | 78373.5677 | 154013.7037 |  | 9353.6082 | Q-10 | 65.47 | 613.6193 | 40173.6532 |  | 51016.9016 |  | 100544.163 | 0 | 30 |  | 9353.6082 | Q-10 | 65.47 | 1012.4718 | 66286.5278 |  | 86668.4752 | 162308.6113 | 0
[17 empty] | 7 Duluth 90.1-2010 |  | Labor |  |  | 4511.351 | 7 Duluth 90.1-2010 |  | Labor |  |  | 4511.351 |  |  |  | 1.344 | 1.537 | 9314.2037 | Q-10 | 65.47 | 611.6989 | 40047.9283 |  | 50843.9947 | 100206.1267 |  | 30 |  | 9314.2037 | Q-10 | 65.47 | 1009.3032 | 66079.0817 |  | 78121.6945 | 153514.9799 |  | 9314.2037 | Q-10 | 65.47 | 611.6989 | 40047.9283 |  | 50843.9947 |  | 100206.1267 | 0 | 30 |  | 9314.2037 | Q-10 | 65.47 | 1009.3032 | 66079.0817 |  | 86381.6575 | 161774.9429 | 0
[17 empty] | 2A Houston 90.1-2010 | All climate zones | y = 2.9572x + 16341 |  |  | 4593.992 | 2A Houston 90.1-2010 | All climate zones | y = 2.9572x + 16341 |  |  | 4593.992 |  |  |  | 1.344 | 1.537 | 9553.1801 | Q-10 | 65.47 | 633.9429 | 41504.243 |  | 52562.5077 | 103619.9308 |  | 30 |  | 9553.1801 | Q-10 | 65.47 | 1046.0058 | 68482.001 |  | 80897.5699 | 158932.7509 |  | 9553.1801 | Q-10 | 65.47 | 633.9429 | 41504.243 |  | 52562.5077 |  | 103619.9308 | 0 | 30 |  | 9553.1801 | Q-10 | 65.47 | 1046.0058 | 68482.001 |  | 89369.4605 | 167404.6415 | 0
[17 empty] | 7 Duluth 90.1-2007 |  | R² = 0.9466 |  |  | 4680.871 | 7 Duluth 90.1-2007 |  | R² = 0.9466 |  |  | 4680.871 |  |  |  | 1.344 | 1.537 | 9312.7364 | Q-10 | 65.47 | 614.8847 | 40256.5014 |  | 51043.4511 | 100612.6889 |  | 30 |  | 9312.7364 | Q-10 | 65.47 | 1014.5598 | 66423.2273 |  | 78496.0034 | 154231.9671 |  | 9312.7364 | Q-10 | 65.47 | 614.8847 | 40256.5014 |  | 51043.4511 |  | 100612.6889 | 0 | 30 |  | 9312.7364 | Q-10 | 65.47 | 1014.5598 | 66423.2273 |  | 86754.6652 | 162490.6289 | 0
[17 empty] | 3B El Paso 90.1-2010 |  |  |  |  | 5083.481 | 3B El Paso 90.1-2010 |  |  |  |  | 5083.481 |  |  |  | 1.344 | 1.537 | 9819.5651 | Q-10 | 65.47 | 659.927 | 43205.4181 |  | 54553.2667 | 107578.2499 |  | 30 |  | 9819.5651 | Q-10 | 65.47 | 1088.8795 | 71288.9399 |  | 84131.8525 | 165240.3574 |  | 9819.5651 | Q-10 | 65.47 | 659.927 | 43205.4181 |  | 54553.2667 |  | 107578.2499 | 0 | 30 |  | 9819.5651 | Q-10 | 65.47 | 1088.8795 | 71288.9399 |  | 92839.9769 | 173948.4819 | 0
[17 empty] | 3C San Francisco 90.1-2007 |  |  |  |  | 5085.6 | 3C San Francisco 90.1-2007 |  |  |  |  | 5085.6 |  |  |  | 1.344 | 1.537 | 9591.5348 | Q-10 | 65.47 | 640.6247 | 41941.6961 |  | 53035.0117 | 104568.2426 |  | 30 |  | 9591.5348 | Q-10 | 65.47 | 1057.0307 | 69203.7985 |  | 81709.6204 | 160504.9537 |  | 9591.5348 | Q-10 | 65.47 | 640.6247 | 41941.6961 |  | 53035.0117 |  | 104568.2426 | 0 | 30 |  | 9591.5348 | Q-10 | 65.47 | 1057.0307 | 69203.7985 |  | 90215.5244 | 169010.8578 | 0
[17 empty] | 2B Phoenix 90.1-2010 |  |  |  |  | 5094.076 | 2B Phoenix 90.1-2010 |  |  |  |  | 5094.076 |  |  |  | 1.344 | 1.537 | 9784.4779 | Q-10 | 65.47 | 656.0811 | 42953.6304 |  | 54264.2927 | 107002.4009 |  | 30 |  | 9784.4779 | Q-10 | 65.47 | 1082.5338 | 70873.4901 |  | 83655.9795 | 164313.9475 |  | 9784.4779 | Q-10 | 65.47 | 656.0811 | 42953.6304 |  | 54264.2927 |  | 107002.4009 | 0 | 30 |  | 9784.4779 | Q-10 | 65.47 | 1082.5338 | 70873.4901 |  | 92332.9881 | 172990.9561 | 0
[17 empty] | 8 Fairbanks 90.1-2007 |  |  |  |  | 5350.475 | 8 Fairbanks 90.1-2007 |  |  |  |  | 5350.475 |  |  |  | 1.344 | 1.537 | 9862.534 | Q-10 | 65.47 | 663.9704 | 43470.1439 |  | 54865.0377 | 108197.7156 |  | 30 |  | 9862.534 | Q-10 | 65.47 | 1095.5512 | 71725.7375 |  | 84636.138 | 166224.4095 |  | 9862.534 | Q-10 | 65.47 | 663.9704 | 43470.1439 |  | 54865.0377 |  | 108197.7156 | 0 | 30 |  | 9862.534 | Q-10 | 65.47 | 1095.5512 | 71725.7375 |  | 93382.3679 | 174970.6394 | 0
[17 empty] | 5A Chicago 90.1-2007 |  |  |  |  | 5405.569 | 5A Chicago 90.1-2007 |  |  |  |  | 5405.569 |  |  |  | 1.344 | 1.537 | 9917.4022 | Q-10 | 65.47 | 670.7663 | 43915.0697 |  | 55366.3476 | 109198.8195 |  | 30 |  | 9917.4022 | Q-10 | 65.47 | 1106.7644 | 72459.8651 |  | 85472.3906 | 167849.6578 |  | 9917.4022 | Q-10 | 65.47 | 670.7663 | 43915.0697 |  | 55366.3476 |  | 109198.8195 | 0 | 30 |  | 9917.4022 | Q-10 | 65.47 | 1106.7644 | 72459.8651 |  | 94267.2783 | 176644.5455 | 0
[17 empty] | 2A Houston 90.1-2007 |  |  |  |  | 5859.035 | 2A Houston 90.1-2007 |  |  |  |  | 5859.035 |  |  |  | 1.344 | 1.537 | 10203.735 | Q-10 | 65.47 | 688.2672 | 45060.8519 |  | 56846.963 | 112111.5498 |  | 30 |  | 10203.735 | Q-10 | 65.47 | 1135.6408 | 74350.4056 |  | 87720.4049 | 172274.5455 |  | 10203.735 | Q-10 | 65.47 | 688.2672 | 45060.8519 |  | 56846.963 |  | 112111.5498 | 0 | 30 |  | 10203.735 | Q-10 | 65.47 | 1135.6408 | 74350.4056 |  | 96769.2165 | 181323.3571 | 0
[17 empty] | 3B El Paso 90.1-2007 |  |  |  |  | 6164.171 | 3B El Paso 90.1-2007 |  |  |  |  | 6164.171 |  |  |  | 1.344 | 1.537 | 10465.5171 | Q-10 | 65.47 | 709.2653 | 46435.5989 |  | 58516.5414 | 115417.6575 |  | 30 |  | 10465.5171 | Q-10 | 65.47 | 1170.2877 | 76618.7382 |  | 90364.3799 | 177448.6352 |  | 10465.5171 | Q-10 | 65.47 | 709.2653 | 46435.5989 |  | 58516.5414 |  | 115417.6575 | 0 | 30 |  | 10465.5171 | Q-10 | 65.47 | 1170.2877 | 76618.7382 |  | 99645.3434 | 186729.5987 | 0
[17 empty] | 2B Phoenix 90.1-2007 |  |  |  |  | 6388.785 | 2B Phoenix 90.1-2007 |  |  |  |  | 6388.785 |  |  |  | 1.344 | 1.537 | 10445.111 | Q-10 | 65.47 | 701.6581 | 45937.5563 |  | 58009.0065 | 114391.6737 |  | 30 |  | 10445.111 | Q-10 | 65.47 | 1157.7359 | 75796.9679 |  | 89455.0088 | 175697.0877 |  | 10445.111 | Q-10 | 65.47 | 701.6581 | 45937.5563 |  | 58009.0065 |  | 114391.6737 | 0 | 30 |  | 10445.111 | Q-10 | 65.47 | 1157.7359 | 75796.9679 |  | 98717.8759 | 184959.9547 | 0
[16 empty] | VFD 90.1-2013 dd affects both heating and cooling pumps | Cost to add VFD to other listed equipment and integrated into the package. In some cases both base case and target case equipment are required to have VFDs, and in some cases not. The thresholds change, but changes can also occur as a result of load and system sizing changes. | Equipment information below. Labor from RS Means 2023 Mechanical Cost Data. Variable Frequency Drives/Adj. Frequency Drives 26 29 23.10 01XX |  |  |  | VFD motor horsepower controlled | Same as base code |  |  |  |  | VFD motor horsepower controlled |  |  |  |  | Inflation from 2012 to 2023
Manufacturer 1
[18 empty] | online | ABB |  |  | 1 | [5 empty] | 1 |  |  |  |  | 1.463 | 570 | Elec | 67.85 | 10 | 678.5 |  | 1337.0267 | 2585.5267 |  | 15 |  | 570 | Elec | 67.85 | 16.5 | 1119.525 |  | 2027.8943 | 3717.4193 |  | 570 | Elec | 67.85 | 10 | 678.5 |  | 1337.0267 |  | 2585.5267 | 0 | 15 |  | 570 | Elec | 67.85 | 16.5 | 1119.525 |  | 2027.8943 | 3717.4193 | 0
[16 empty] | used for load changes |  | www.joiliettech.com/abb_acs-550 | ABB |  |  | 2 | [5 empty] | 2 |  |  |  |  | 1.463 | 585 | 1 Elec | 67.85 | 10 | 678.5 |  | 1354.9726 | 2618.4726 |  | 15 |  | 585 | Elec | 67.85 | 16.5 | 1119.525 |  | 2049.1348 | 3753.6598 |  | 585 | 1 Elec | 67.85 | 10 | 678.5 |  | 1354.9726 |  | 2618.4726 | 0 | 15 |  | 585 | Elec | 67.85 | 16.5 | 1119.525 |  | 2049.1348 | 3753.6598 | 0
[18 empty] | -ac_drive_480v_ratings.htm | ABB |  |  | 3 | [5 empty] | 3 |  |  |  |  | 1.463 | 744 | 1 Elec | 67.85 | 10 | 678.5 |  | 1545.1988 | 2967.6988 |  | 15 |  | 744 | Elec | 67.85 | 16.5 | 1119.525 |  | 2274.2836 | 4137.8086 |  | 744 | 1 Elec | 67.85 | 10 | 678.5 |  | 1545.1988 |  | 2967.6988 | 0 | 15 |  | 744 | Elec | 67.85 | 16.5 | 1119.525 |  | 2274.2836 | 4137.8086 | 0
[19 empty] | ABB |  |  | 5 | [5 empty] | 5 |  |  |  |  | 1.463 | 954 | 1 Elec | 67.85 | 10 | 678.5 |  | 1796.441 | 3428.941 |  | 15 |  | 954 | Elec | 67.85 | 16.5 | 1119.525 |  | 2571.65 | 4645.175 |  | 954 | 1 Elec | 67.85 | 10 | 678.5 |  | 1796.441 |  | 3428.941 | 0 | 15 |  | 954 | Elec | 67.85 | 16.5 | 1119.525 |  | 2571.65 | 4645.175 | 0
[19 empty] | ABB |  |  | 10 | [5 empty] | 10 |  |  |  |  | 1.463 | 1300 | 1 Elec | 67.85 | 11.94 | 810.129 |  | 2337.4786 | 4447.6076 |  | 15 |  | 1300 | Elec | 67.85 | 19.701 | 1336.7128 |  | 3298.4234 | 5935.1363 |  | 1300 | 1 Elec | 67.85 | 11.94 | 810.129 |  | 2337.4786 |  | 4447.6076 | 0 | 15 |  | 1300 | Elec | 67.85 | 19.701 | 1336.7128 |  | 3298.4234 | 5935.1363 | 0
[19 empty] | ABB |  |  | 20 | [5 empty] | 20 |  |  |  |  | 1.463 | 2159 | 2 Elec | 67.6 | 17.8 | 1203.28 |  | 3744.7614 | 7107.0414 |  | 15 |  | 2159 | Elec | 67.6 | 29.37 | 1985.412 |  | 5222.1508 | 9366.5628 |  | 2159 | 2 Elec | 67.6 | 17.8 | 1203.28 |  | 3744.7614 |  | 7107.0414 | 0 | 15 |  | 2159 | Elec | 67.6 | 29.37 | 1985.412 |  | 5222.1508 | 9366.5628 | 0
[19 empty] | ABB |  |  | 50 | [5 empty] | 50 |  |  |  |  | 1.463 | 4113 | 2 Elec | 67.6 | 30.189 | 2040.7764 |  | 6891.1028 | 13044.8792 |  | 15 |  | 4113 | Elec | 67.6 | 49.8118 | 3367.2811 |  | 9495.8975 | 16976.1786 |  | 4113 | 2 Elec | 67.6 | 30.189 | 2040.7764 |  | 6891.1028 |  | 13044.8792 | 0 | 15 |  | 4113 | Elec | 67.6 | 49.8118 | 3367.2811 |  | 9495.8975 | 16976.1786 | 0
[19 empty] | ABB |  |  | 75 | [5 empty] | 75 |  |  |  |  | 1.463 | 6660 | R-3 | 67.34 | 35.174 | 2368.6172 |  | 10254.8379 | 19283.4551 |  | 15 |  | 6660 | Elec | 67.34 | 58.0371 | 3908.2183 |  | 13692.3782 | 24260.5965 |  | 6660 | R-3 | 67.34 | 35.174 | 2368.6172 |  | 10254.8379 |  | 19283.4551 | 0 | 15 |  | 6660 | Elec | 67.34 | 58.0371 | 3908.2183 |  | 13692.3782 | 24260.5965 | 0
[19 empty] | ABB |  |  | 100 | [5 empty] | 100 |  |  |  |  | 1.463 | 7758 | R-3 | 67.34 | 40 | 2693.6 |  | 11882.2427 | 22333.8427 |  | 15 |  | 7758 | Elec | 67.34 | 66 | 4444.44 |  | 15831.8887 | 28034.3287 |  | 7758 | R-3 | 67.34 | 40 | 2693.6 |  | 11882.2427 |  | 22333.8427 | 0 | 15 |  | 7758 | Elec | 67.34 | 66 | 4444.44 |  | 15831.8887 | 28034.3287 | 0
[16 empty] | VFD_Size | [16 empty] | 1.463 | [11 empty] | 0 | [27 empty] | 0
[18 empty] | PNNL from online | ABB |  |  | 1 | [5 empty] | 1 |  |  |  |  | 1.463 | 570 | 1 Elec | 67.85 | 10 | 678.5 |  | 1337.0267 | 2585.5267 |  | 15 |  | 570 | 1 Elec | 67.85 | 16.5 | 1119.525 |  | 2027.8943 | 3717.4193 |  | 570 | 1 Elec | 67.85 | 10 | 678.5 |  | 1337.0267 |  | 2585.5267 | 0 | 15 |  | 570 | 1 Elec | 67.85 | 16.5 | 1119.525 |  | 2027.8943 | 3717.4193 | 0
[18 empty] | www.joiliettech.com/abb_acs-550 | ABB |  |  | 2 | [5 empty] | 2 |  |  |  |  | 1.463 | 585 | 1 Elec | 67.85 | 10 | 678.5 |  | 1354.9726 | 2618.4726 |  | 15 |  | 585 | 1 Elec | 67.85 | 16.5 | 1119.525 |  | 2049.1348 | 3753.6598 |  | 585 | 1 Elec | 67.85 | 10 | 678.5 |  | 1354.9726 |  | 2618.4726 | 0 | 15 |  | 585 | 1 Elec | 67.85 | 16.5 | 1119.525 |  | 2049.1348 | 3753.6598 | 0
[18 empty] | -ac_drive_480v_ratings.htm | ABB |  |  | 3 | [5 empty] | 3 |  |  |  |  | 1.463 | 744 | 1 Elec | 67.85 | 10 | 678.5 |  | 1545.1988 | 2967.6988 |  | 15 |  | 744 | 1 Elec | 67.85 | 16.5 | 1119.525 |  | 2274.2836 | 4137.8086 |  | 744 | 1 Elec | 67.85 | 10 | 678.5 |  | 1545.1988 |  | 2967.6988 | 0 | 15 |  | 744 | 1 Elec | 67.85 | 16.5 | 1119.525 |  | 2274.2836 | 4137.8086 | 0
[19 empty] | ABB |  |  | 5 | [5 empty] | 5 |  |  |  |  | 1.463 | 954 | 1 Elec | 67.85 | 10 | 678.5 |  | 1796.441 | 3428.941 |  | 15 |  | 954 | 1 Elec | 67.85 | 16.5 | 1119.525 |  | 2571.65 | 4645.175 |  | 954 | 1 Elec | 67.85 | 10 | 678.5 |  | 1796.441 |  | 3428.941 | 0 | 15 |  | 954 | 1 Elec | 67.85 | 16.5 | 1119.525 |  | 2571.65 | 4645.175 | 0
[19 empty] | ABB |  |  | 10 | [5 empty] | 10 |  |  |  |  | 1.463 | 1300 | 1 Elec | 67.85 | 11.94 | 810.129 |  | 2337.4786 | 4447.6076 |  | 15 |  | 1300 | 1 Elec | 67.85 | 19.701 | 1336.7128 |  | 3298.4234 | 5935.1363 |  | 1300 | 1 Elec | 67.85 | 11.94 | 810.129 |  | 2337.4786 |  | 4447.6076 | 0 | 15 |  | 1300 | 1 Elec | 67.85 | 19.701 | 1336.7128 |  | 3298.4234 | 5935.1363 | 0
[19 empty] | ABB |  |  | 20 | [5 empty] | 20 |  |  |  |  | 1.463 | 2159 | 2 Elec | 67.6 | 17.8 | 1203.28 |  | 3744.7614 | 7107.0414 |  | 15 |  | 2159 | 2 Elec | 67.6 | 29.37 | 1985.412 |  | 5222.1508 | 9366.5628 |  | 2159 | 2 Elec | 67.6 | 17.8 | 1203.28 |  | 3744.7614 |  | 7107.0414 | 0 | 15 |  | 2159 | 2 Elec | 67.6 | 29.37 | 1985.412 |  | 5222.1508 | 9366.5628 | 0
[19 empty] | ABB |  |  | 50 | [5 empty] | 50 |  |  |  |  | 1.463 | 4113 | 2 Elec | 67.6 | 30.189 | 2040.7764 |  | 6891.1028 | 13044.8792 |  | 15 |  | 4113 | 2 Elec | 67.6 | 49.8118 | 3367.2811 |  | 9495.8975 | 16976.1786 |  | 4113 | 2 Elec | 67.6 | 30.189 | 2040.7764 |  | 6891.1028 |  | 13044.8792 | 0 | 15 |  | 4113 | 2 Elec | 67.6 | 49.8118 | 3367.2811 |  | 9495.8975 | 16976.1786 | 0
[19 empty] | ABB |  |  | 75 | [5 empty] | 75 |  |  |  |  | 1.463 | 6660 | R-3 | 67.34 | 35.174 | 2368.6172 |  | 10254.8379 | 19283.4551 |  | 15 |  | 6660 | R-3 | 67.34 | 58.0371 | 3908.2183 |  | 13692.3782 | 24260.5965 |  | 6660 | R-3 | 67.34 | 35.174 | 2368.6172 |  | 10254.8379 |  | 19283.4551 | 0 | 15 |  | 6660 | R-3 | 67.34 | 58.0371 | 3908.2183 |  | 13692.3782 | 24260.5965 | 0
[19 empty] | ABB |  |  | 100 | [5 empty] | 100 |  |  |  |  | 1.463 | 7758 | R-3 | 67.34 | 40 | 2693.6 |  | 11882.2427 | 22333.8427 |  | 15 |  | 7758 | R-3 | 67.34 | 66 | 4444.44 |  | 15831.8887 | 28034.3287 |  | 7758 | R-3 | 67.34 | 40 | 2693.6 |  | 11882.2427 |  | 22333.8427 | 0 | 15 |  | 7758 | R-3 | 67.34 | 66 | 4444.44 |  | 15831.8887 | 28034.3287 | 0
90.1-07bw | 6. HVAC |  | PTAC Efficiency | [12 empty] | PTAC_Efficiency | PTAC Adjustments for load changes resulting in capacity changes. 90.1-2013 and 90.1-2016 have the same efficiency requirements. | Equipment information below. Labor from RS Means 2014 Mechanical Cost Data. 28 81 13 - Packaged Terminal Air Conditioners 23 81 13.10 0220 |  |  |  |  | PTAC, 9,000 Btu/hr, minimum efficiency 11.3 EER
PTAC_Efficiency
[8 empty] | X |  | X | X | X | X | X |  |  | Two similar units, 9,000 Bthuh, electric heat, EER 11.3 | http://www.ptacunits.com | Amana | PTC094G25AXXX, PTC094G35AXXX |  | Each | Two similar units, 9,000 Bthuh, electric heat, EER 11.5 | www.ptacunits.com | Amana | PTC093G25AXXX, PTC093G35AXXX |  | Each |  |  |  |  | 1 | 704 | Q5 | 65.3 | 3.2 | 208.96 |  | 554.6585 | 1467.6185 |  | 15 |  | 704 | Q5 | 65.3 | 5.28 | 344.784 |  | 834.5619 | 1883.3459 |  | 739 | Q5 | 65.3 | 3.2 | 208.96 |  | 572.2038 | 0 | 1520.1638 | 0 | 15 |  | 739 | Q5 | 65.3 | 5.28 | 344.784 |  | 857.3617 | 1941.1457 | 52.5452
[16 empty] | N. Carolina hotel room HVAC control N. Carolina amendment | Base code for North Carolina only includes exception for automatic shutdown for hotel rooms. Base code model includes this type of control, assumed to be implemented with an occupancy sensor. Therefore, a credit for the cost of occupancy sensor control is provided. Need to add cost - see \\korea\comstd\90.1_IECC_ State_Cost_Eff\Costs and Cost-Effectiveness\HVAC\hotel guest room on-off control | PNNL staff experience |  |  |  |  | No cost or credit. | [36 empty] | 0 | [5 empty] | 0 | [5 empty] | 0
[16 empty] | NC_hotel_HVAC | [43 empty] | 0 | [5 empty] | 0 | [5 empty] | 0
90.1-07n and 90.1-07ca | 6. HVAC | 6.4.3.10 | Single zone fan speed control | [12 empty] | Singe Zone Fan Speed Control When capacity change creates change in requirement | Constant volume single zone DX units serve some individual zones in the prototypes. Base costs are included above. Sometimes with a change in capacity; the system may no longer require multiple speed fans or multiple stage compressors. | [5 empty] | Addendum AQ added fan control and staging requirements. For single zone control units; conversion is to a 2 speed fan, and addition of one stage of cooling. There are additional economizer integration requirements, but they are related to settings and configuration of the controller, and there are no incremental costs once the market adapts to the requirements. Requirements are applied as follows: All DX units over 65 MBH: add a stage of cooling. All single zone units over 65 MBH: add 2 speed fan control. All DX units serving multiple zones: add VSD fan. | Incremental cost is based on data gathered from manufacturers by AHRI and presented in a composite fashion at ASHRAE 90.1 SSPC.
Add 2 speed fan y = 6.458x + 206.12
[24 empty] | Cf_Fan2spd_I | 206.12 |  |  | tons
[24 empty] | Cf_Fan2spd_x | 6.458 |  |  | tons
[23 empty] | Add cooling stage: y = 51.075x - 44.585 |  |  |  |  | tons
[24 empty] | cf_CoolStage_I | -44.585 |  |  | tons
[24 empty] | cf_CoolStage_x | 51.075 |  |  | tons
90.1-07h | 6. HVAC | 6.5.2.1 exc. b. | VAV dual minimum damper control | [12 empty] | VAV Dual Minimum Damper Control 90.1-07h Note: Item includes no added costs as explained in description. | This addendum applies to multi-zone VAV systems. 90.1-07 models use standard VAV terminal unit damper control with a fixed minimum for cooling, with reheat operating only at this minimum position. DDC control of terminal units is included in the base case. No added cost. | Faithful+Gould, Solarc |  |  |  |  | The addendum allows the option of a dual minimum damper control with modulated heating airflow. The minimum is 20% when in reheat/recool or in deadband (or minimum required to meet ventilation requirement). The minimum is 50% when in reheat/recool or mixed mode when in peak heating, and airflow in heating and cooling outside of deadband shall be modulated to meet the load. No added costs are identified: terminal units selected for base case are capable of dual minimum. (90.1-2007 baseline assumed to have DDC control. | Faithful+Gould, Solarc | [8 empty] | 1
90.1-07bh | 6. HVAC | 6.5.3.4 | Supply air temperature reset | [12 empty] | Supply Air Temperature Reset 90.1-07bh | This addendum applies to multi-zone VAV systems. 90.1-07 models use standard VAV temperature controls with a supply air temperature of 55°F. Base cost for these systems is accounted for under the general HVAC capacity costs above. | [5 empty] | The addendum requires supply air temperature reset for multi-zone VAV systems. Supply air temperature is reset to at least 25% of the difference between the design supply air temperature and the design room air temperature (in prototype this is a reset from 55°F at full load, to 60°F at low load (based on outdoor air temperature (OAT)), Setting it up uses 4 inputs, e.g. 55°F at 70°F OAT; 60°F at 30°F OAT. Zones that experience relatively constant loads (core with consistent occupancy, etc.) require design for the air supply based on the reset supply air temperature instead of the higher OAT supply air temperature. The codes require that zones which experience relatively constant loads be designed to meet the load at the fully reset supply air temperature. The 90.1 MSC used an estimate of $0.19 per square foot of interior building area served by HVAC systems affected by the control requirement to account for increased air distribution equipment compared to VAV system air distribution without this requirement. Cost is shown as total cost, and is assumed to have a 20 year life like ductwork costs for replacement cost Area affected assumed to be portion of core area of open office type excluding top floor determined to be 98,600 ft2. There is also incremental cost for programming and commissioning added to the HVAC system cost developed above, for the 2010 case, with supply air temperature reset added. | Solarc commissioning estimate. This is consistent with information received from members of the 90.1 mechanical subcommittee and Faithful+Gould, and Solarc. | [8 empty] | 1
[16 empty] | Supply_Air_Temp_Reset | [16 empty] | 1
[23 empty] | 4 hours of programming, and 4 hours of commissioning per system | Solarc | [8 empty] | 1 | [21 empty] | Programming | 125 | 4 | 500 |  | 482.744 |  | 982.744 |  |  |  | 0 |  |  |  | 0 |  | 0 | 0 | 982.744
[23 empty] | Large office additional ductwork and other system costs for design at reset temperature. | prototype model for area, 90.1 MSC for cost/area | [8 empty] | 1 | [26 empty] | 0 |  | 18734 |  | 20 |  | 0 |  |  |  | 0 |  | 0 | 18734 | 18734
90.1-16ap | [15 empty] | Supply Air Temperature Reset 90.1-16ap | base case exempts 0A, 1A, 2A, 3A thus costs = 0 |  | Material cost = 4E-07x2 + 0.0307x + 1618 | where x = SA cfm |  | Supply airflow, cfm | only 0A, 1A, 2A, 3A MZ systems only <3000 cfm design OA is exempt only large office and primary school
[16 empty] | SAT_reset_16ap |  |  | Labor hours = 0.0054x + 3.6055 | where x = SA cfm
90.1-07ck | 6. HVAC | 6.5.3.3 | VAV system ventilation optimization | [12 empty] | VAV System Ventilation Optimization | 2013 baseline includes VAV optimized outside airflow based on the ASHRAE 62.1 ventilation requirements for multi-zone systems, except where excepted for DCV. 2016 VAV systems required to have ventilation optimization to meet 62.1 outside air requirements, wven where ERV is required. | [5 empty] | Under 90.1-2010 multi-zone VAV systems are required to provide control to automatically reduce outdoor intake flow below the maxium design outdoor airflow in response to changes in system ventilation efficiency as defined by the multi-zone requirements in Standard 62.1. The VAV systems modeled are assumed to have DDC control of zone dampers and outdoor airflow sensors in the AHU or RTU in order to meet other provisions of Standard 90.1 and requirements under Stanadard 62.1. With this equipment already in place, costs are limited to programming and checkout/commissioning. Costs include 30 minutes programming for each perimeter zone, and 1 hour (2 people 30 minutes each) for commissioning per perimeter zone. The number of perimeter zones is based on the ductwork layout prepared by the mechanical engineering consultant described under Duct Work and Zone Air Distribution costs above. Large office has 12 perimeter zones per floor, 12 floors total (basement is served by constant volume systems). Primary school has 28 perimeter zones served by variable air volume. | Solarc commissioning estimate. This is consistent but not identical with information received from members of the 90.1 mechanical subcommittee and Faithful+Gould, and Solarc. | [8 empty] | 1 | [38 empty] | 0
[16 empty] | Vent_Optimize | [6 empty] | Costs applied based on the number of perimeter zones for each affected prototype system. | [9 empty] | 1.242 | [26 empty] | 0 | [5 empty] | 0 | [5 empty] | 0
[33 empty] | 1.242 |  | Programming | 125 | 0.5 | 62.5 |  | 60.343 | 122.843 |  |  |  | 0 |  |  | 0.825 |  |  | 0 |  |  |  | Programming | 125 | 0.5 | 62.5 |  | 60.343 |  | 122.843 |  |  |  | 0 |  |  |  | 0 |  | 0 | 0 | 0
[16 empty] | VAV Fan Control Type Threshold 2009 to 2012 IECC Primary school only | Fan motor horsepower 10 hp and greater requires VFD. Costs shown for base are zero. Costs shown for target are incremental cost for going from non-VFD <inlet vanes?> to VFD. | [5 empty] | Fan motor hp 7.5 hp and greater requires VFD. Costs shown for target are incremental cost for going from non-VFD <inlet vanes?> to VFD. Cost added if fan nameplate motor hp equals 7.5 hp. Applies for IECC 2009 or 90.1-2007 to IECC 2012 | [9 empty] | 1 | [11 empty] | 0 | [5 empty] | 0 | [8 empty] | 0 | [5 empty] | 0 | [5 empty] | 0
[16 empty] | VAV_fan_control | [6 empty] | Incremental cost for non-VFD <inlet vanes> to VFD fan motor control at 7.5 hp motor | [9 empty] | 1 | [11 empty] | 0 | [5 empty] | 0 | [8 empty] | 0 | [5 empty] | 0 | [5 empty] | 0
90.1-16a | 6. HVAC | 6.4.3.4.2 and 6.4.3.4.3 | Automatic dampers | X |  | X | X | [8 empty] | Automatic Outdoor Air Dampers 90.1-16a | Return dampers are NOT required to be low leakage Maintenance: Carnes, online http://www.carnes.com/ventilation/pdf/1511.pdf http://www.nextag.com/replacement-damper-motor/products-html RS Means Facilities Maintenance and Repair 2004 Guidebook for labor hours - unit heater motor replacement labor hours. | Equipment information below. Labor from RS Means 2012 Mechanical Cost Data. 23 33 13 Dampers. Multi-blade opposed blade 23.33.13.13 (motorized 7500+) Prices adjusted to 2023$ |  |  |  | Outside Airflow, cfm | Return dampers ARE required to be low leakage | major manufacturer of return air dampers |  |  |  | Outside Airflow, cfm |  |  |  |  | 1 | [38 empty] | 0
0
[16 empty] | Outdoor_ Air_ Dampers | [49 empty] | 0 | [5 empty] | 0
[17 empty] | Gravity outdoor intake dampers | Faithful+Gould from Honeywell representative | 8" x 6" | A2OAB006006NAA |  | 50 | Same as the 90.1-2007 |  |  |  |  | 50 |  |  |  |  | 1.239 | 144.82 | 1 Shee | 63.13 | 0.333 | 21.0223 |  | 144.8567 | 310.699 | 102.2833 | 20 |  | 144.82 | 1 Shee | 63.13 | 0.54945 | 34.6868 |  | 132.1622 | 311.669 |  | 159.302 | 1 Shee | 63.13 | 0.333 | 21.0223 |  | 157.3127 |  | 337.637 | 102.2833 | 20 |  | 159.302 | 1 Shee | 63.13 | 0.54945 | 34.6868 |  | 204.471 | 398.4598 | 26.938
[19 empty] | 8" x 8" | A2OAB008008NAA |  | 100 | [5 empty] | 100 |  |  |  |  | 1.239 | 144.82 | 1 Shee | 63.13 | 0.364 | 22.9793 |  | 146.7462 | 314.5455 | 102.9947 | 20 |  | 144.82 | 1 Shee | 63.13 | 0.6006 | 37.9159 |  | 135.6833 | 318.4192 |  | 159.302 | 1 Shee | 63.13 | 0.364 | 22.9793 |  | 159.2022 |  | 341.4835 | 102.9947 | 20 |  | 159.302 | 1 Shee | 63.13 | 0.6006 | 37.9159 |  | 207.9921 | 405.21 | 26.938
[19 empty] | 10" x 10" | A2OAB0010010NAA |  | 250 | Cost premium = |  |  |  |  | 250 |  |  |  |  | 1.239 | 144.82 | 1 Shee | 63.13 | 0.382 | 24.1157 |  | 147.8433 | 316.779 | 103.706 | 20 |  | 144.82 | 1 Shee | 63.13 | 0.6303 | 39.7908 |  | 137.7278 | 322.3387 |  | 159.302 | 1 Shee | 63.13 | 0.382 | 24.1157 |  | 160.2993 |  | 343.717 | 103.706 | 20 |  | 159.302 | 1 Shee | 63.13 | 0.6303 | 39.7908 |  | 210.0366 | 409.1295 | 26.938
[19 empty] | 12" x 12" | A2OAB0012012NAA |  | 500 | 10% |  |  |  |  | 500 |  |  |  |  | 1.239 | 144.82 | 1 Shee | 63.13 | 0.381 | 24.0525 |  | 147.7824 | 316.6549 | 105.8401 | 20 |  | 144.82 | 1 Shee | 63.13 | 0.62865 | 39.6867 |  | 137.6142 | 322.1209 |  | 159.302 | 1 Shee | 63.13 | 0.381 | 24.0525 |  | 160.2384 |  | 343.5929 | 105.8401 | 20 |  | 159.302 | 1 Shee | 63.13 | 0.62865 | 39.6867 |  | 209.923 | 408.9117 | 26.938
[19 empty] | 16" x 10" | A2OAB0016010NAA |  | 1000 | [5 empty] | 1000 |  |  |  |  | 1.239 | 152.6 | 1 Shee | 63.13 | 0.444 | 28.0297 |  | 158.3139 | 338.9436 | 109.3968 | 20 |  | 152.6 | 1 Shee | 63.13 | 0.7326 | 46.249 |  | 149.8381 | 348.6871 |  | 167.86 | 1 Shee | 63.13 | 0.444 | 28.0297 |  | 171.439 |  | 367.3288 | 109.3968 | 20 |  | 167.86 | 1 Shee | 63.13 | 0.7326 | 46.249 |  | 226.0314 | 440.1405 | 28.3852
[19 empty] | 18" x 16" | A2OAB0018016NAA |  | 2000 | [5 empty] | 2000 |  |  |  |  | 1.239 | 188.56 | 1 Shee | 63.13 | 0.533 | 33.6483 |  | 194.6678 | 416.8761 | 116.5103 | 20 |  | 188.56 | 1 Shee | 63.13 | 0.87945 | 55.5197 |  | 183.3721 | 427.4518 |  | 207.416 | 1 Shee | 63.13 | 0.533 | 33.6483 |  | 210.8859 |  | 451.9502 | 116.5103 | 20 |  | 207.416 | 1 Shee | 63.13 | 0.87945 | 55.5197 |  | 277.5203 | 540.456 | 35.0741
[19 empty] | 28" x 16" | A2OAB0028016NAA |  | 3000 | [5 empty] | 3000 |  |  |  |  | 1.239 | 254.66 | 1 Shee | 63.13 | 0.615 | 38.825 |  | 256.5185 | 550.0035 | 130.7374 | 20 |  | 254.66 | 1 Shee | 63.13 | 1.0148 | 64.0612 |  | 235.745 | 554.4661 |  | 280.126 | 1 Shee | 63.13 | 0.615 | 38.825 |  | 278.4219 |  | 597.3728 | 130.7374 | 20 |  | 280.126 | 1 Shee | 63.13 | 1.0148 | 64.0612 |  | 362.897 | 707.0842 | 47.3694
[19 empty] | 24" x 24" | pro-rated |  | 4000 | [5 empty] | 4000 |  |  |  |  | 1.239 | 298.596 | 1 Shee | 63.13 | 1 | 63.13 |  | 317.7742 | 679.5002 | 144.9644 | 20 |  | 298.596 | 1 Shee | 63.13 | 1.65 | 104.1645 |  | 308.0955 | 710.856 |  | 328.4556 | 1 Shee | 63.13 | 1 | 63.13 |  | 343.4565 |  | 735.0421 | 144.9644 | 20 |  | 328.4556 | 1 Shee | 63.13 | 1.65 | 104.1645 |  | 457.1848 | 889.8049 | 55.5419
[19 empty] | 30" x 30" | pro-rated |  | 7000 | [5 empty] | 7000 |  |  |  |  | 1.239 | 463.65 | 1 Shee | 63.13 | 2.424 | 153.0271 |  | 546.532 | 1163.2092 | 159.1914 | 20 |  | 463.65 | 1 Shee | 63.13 | 3.9996 | 252.4947 |  | 577.3582 | 1293.5029 |  | 510.015 | 1 Shee | 63.13 | 2.424 | 153.0271 |  | 586.4107 |  | 1249.4528 | 159.1914 | 20 |  | 510.015 | 1 Shee | 63.13 | 3.9996 | 252.4947 |  | 808.8591 | 1571.3689 | 86.2436
[19 empty] | 36" x 36" | pro-rated |  | 10000 | [5 empty] | 10000 |  |  |  |  | 1.239 | 620.3925 | 1 Shee | 63.13 | 2.667 | 168.3677 |  | 696.1577 | 1484.9179 | 201.8725 | 20 |  | 620.3925 | 1 Shee | 63.13 | 4.4005 | 277.8067 |  | 707.0645 | 1605.2637 |  | 682.4317 | 1 Shee | 63.13 | 2.667 | 168.3677 |  | 749.5178 |  | 1600.3172 | 201.8725 | 20 |  | 682.4317 | 1 Shee | 63.13 | 4.4005 | 277.8067 |  | 1016.8271 | 1977.0656 | 115.3993
[19 empty] | 56" x 36" | pro-rated |  | 14000 | [5 empty] | 14000 |  |  |  |  | 1.239 | 834.9235 | 1 Shee | 63.13 | 2.963 | 187.0542 |  | 898.7178 | 1920.6955 | 244.5536 | 20 |  | 834.9235 | 1 Shee | 63.13 | 4.889 | 308.6394 |  | 880.4354 | 2023.9983 |  | 918.4158 | 1 Shee | 63.13 | 2.963 | 187.0542 |  | 970.5297 |  | 2075.9997 | 244.5536 | 20 |  | 918.4158 | 1 Shee | 63.13 | 4.889 | 308.6394 |  | 1297.3136 | 2524.3689 | 155.3043
[33 empty] | 1.239 | [26 empty] | 0 | [11 empty] | 0
[17 empty] | Motorized return air dampers not low leakage | Faithful+Gould from Honeywell representative |  | ZD6x6 |  | 50 | Motorized return air dampers Motorized with class II Leakage, 3 V blade w/seals, opposed galvanized frame, w/ galvanized linkages & axles, Acetal Bearings/Vinyl Seal. One manufacturer only | major damper manufacturer |  |  |  | 50 |  |  |  |  | 1.239 | 314.06 | 1 Shee | 63.13 | 0.533 | 33.6483 |  | 302.6106 | 650.3189 | 102.2833 | 20 |  | 314.06 | 1 Shee | 63.13 | 0.87945 | 55.5197 |  | 265.1256 | 634.7053 |  | 361.169 | 1 Shee | 63.13 | 0.533 | 33.6483 |  | 343.1291 |  | 737.9464 | 102.2833 | 20 |  | 361.169 | 1 Shee | 63.13 | 0.87945 | 55.5197 |  | 438.3632 | 855.0519 | 87.6275
[20 empty] | ZD8X8 |  | 100 | [5 empty] | 100 |  |  |  |  | 1.239 | 321.11 | 1 Shee | 63.13 | 0.571 | 36.0472 |  | 310.9905 | 668.1477 | 102.9947 | 20 |  | 321.11 | 1 Shee | 63.13 | 0.94215 | 59.4779 |  | 274.0343 | 654.6222 |  | 369.2765 | 1 Shee | 63.13 | 0.571 | 36.0472 |  | 352.4185 |  | 757.7423 | 102.9947 | 20 |  | 369.2765 | 1 Shee | 63.13 | 0.94215 | 59.4779 |  | 451.1607 | 879.9152 | 89.5946
[20 empty] | ZD10X10 |  | 250 | [5 empty] | 250 |  |  |  |  | 1.239 | 342.01 | 1 Shee | 63.13 | 0.615 | 38.825 |  | 331.6484 | 712.4834 | 103.706 | 20 |  | 342.01 | 1 Shee | 63.13 | 1.0148 | 64.0612 |  | 292.6467 | 698.7179 |  | 393.3115 | 1 Shee | 63.13 | 0.615 | 38.825 |  | 375.7729 |  | 807.9094 | 103.706 | 20 |  | 393.3115 | 1 Shee | 63.13 | 1.0148 | 64.0612 |  | 481.3017 | 938.6744 | 95.426
[20 empty] | ZD12X12 |  | 500 | [5 empty] | 500 |  |  |  |  | 1.239 | 352.42 | 1 Shee | 63.13 | 0.667 | 42.1077 |  | 343.7716 | 738.2993 | 105.8401 | 20 |  | 352.42 | 1 Shee | 63.13 | 1.1005 | 69.4777 |  | 305.3343 | 727.2321 |  | 405.283 | 1 Shee | 63.13 | 0.667 | 42.1077 |  | 389.2391 |  | 836.6298 | 105.8401 | 20 |  | 405.283 | 1 Shee | 63.13 | 1.1005 | 69.4777 |  | 499.7316 | 974.4923 | 98.3306
[20 empty] | ZD16X10 |  | 1000 | [5 empty] | 1000 |  |  |  |  | 1.239 | 370.71 | 1 Shee | 63.13 | 0.667 | 42.1077 |  | 359.5028 | 772.3205 | 109.3968 | 20 |  | 370.71 | 1 Shee | 63.13 | 1.1005 | 69.4777 |  | 317.2489 | 757.4366 |  | 426.3165 | 1 Shee | 63.13 | 0.667 | 42.1077 |  | 407.3301 |  | 875.7543 | 109.3968 | 20 |  | 426.3165 | 1 Shee | 63.13 | 1.1005 | 69.4777 |  | 521.735 | 1017.5292 | 103.4337
[20 empty] | ZD18X16 |  | 2000 | [5 empty] | 2000 |  |  |  |  | 1.239 | 428.16 | 1 Shee | 63.13 | 0.889 | 56.1226 |  | 422.4468 | 906.7294 | 116.5103 | 20 |  | 428.16 | 1 Shee | 63.13 | 1.4668 | 92.6022 |  | 379.8886 | 900.6508 |  | 492.384 | 1 Shee | 63.13 | 0.889 | 56.1226 |  | 477.686 |  | 1026.1926 | 116.5103 | 20 |  | 492.384 | 1 Shee | 63.13 | 1.4668 | 92.6022 |  | 616.0645 | 1201.0507 | 119.4632
[20 empty] | ZD28X16 |  | 3000 | Cost premium = |  |  |  |  | 3000 |  |  |  |  | 1.239 | 509.09 | 1 Shee | 63.13 | 1.333 | 84.1523 |  | 519.1172 | 1112.3595 | 130.7374 | 20 |  | 509.09 | 1 Shee | 63.13 | 2.1995 | 138.8513 |  | 483.0392 | 1130.9805 |  | 585.4535 | 1 Shee | 63.13 | 1.333 | 84.1523 |  | 584.7976 |  | 1254.4034 | 130.7374 | 20 |  | 585.4535 | 1 Shee | 63.13 | 2.1995 | 138.8513 |  | 763.8567 | 1488.1615 | 142.0439
[20 empty] | ZD28X20 |  | 4000 | 15% |  |  |  |  | 4000 |  |  |  |  | 1.239 | 558.68 | 1 Shee | 63.13 | 1.4665 | 92.5801 |  | 569.9067 | 1221.1668 | 144.9644 | 20 |  | 558.68 | 1 Shee | 63.13 | 2.4197 | 152.7572 |  | 530.5066 | 1241.9439 |  | 642.482 | 1 Shee | 63.13 | 1.4665 | 92.5801 |  | 641.9849 |  | 1377.0471 | 144.9644 | 20 |  | 642.482 | 1 Shee | 63.13 | 2.4197 | 152.7572 |  | 838.6783 | 1633.9175 | 155.8802
[19 empty] | 30" x 30" | pro-rated |  | 7000 | [5 empty] | 7000 |  |  |  |  | 1.239 | 707.45 | 1 Shee | 63.13 | 2.21 | 139.5173 |  | 743.1813 | 1590.1486 | 159.1914 | 20 |  | 707.45 | 1 Shee | 63.13 | 3.6465 | 230.2035 |  | 711.868 | 1649.5216 |  | 813.5675 | 1 Shee | 63.13 | 2.21 | 139.5173 |  | 834.4531 |  | 1787.5379 | 159.1914 | 20 |  | 813.5675 | 1 Shee | 63.13 | 3.6465 | 230.2035 |  | 1102.1022 | 2145.8732 | 197.3894
[19 empty] | 36" x 36" | pro-rated |  | 10000 | [5 empty] | 10000 |  |  |  |  | 1.239 | 856.22 | 1 Shee | 63.13 | 2.32 | 146.4616 |  | 877.8433 | 1880.5249 | 201.8725 | 20 |  | 856.22 | 1 Shee | 63.13 | 3.828 | 241.6616 |  | 821.2743 | 1919.1559 |  | 984.653 | 1 Shee | 63.13 | 2.32 | 146.4616 |  | 988.3087 |  | 2119.4233 | 201.8725 | 20 |  | 984.653 | 1 Shee | 63.13 | 3.828 | 241.6616 |  | 1293.5709 | 2519.8856 | 238.8985
[19 empty] | 48" x 48" | pro-rated |  | 14000 | [5 empty] | 14000 |  |  |  |  | 1.239 | 1054.58 | 1 Shee | 63.13 | 2.667 | 168.3677 |  | 1069.6031 | 2292.5508 | 244.5536 | 20 |  | 1054.58 | 1 Shee | 63.13 | 4.4005 | 277.8067 |  | 989.9038 | 2322.2905 |  | 1212.767 | 1 Shee | 63.13 | 2.667 | 168.3677 |  | 1205.6601 |  | 2586.7948 | 244.5536 | 20 |  | 1212.767 | 1 Shee | 63.13 | 4.4005 | 277.8067 |  | 1571.6172 | 3062.1909 | 294.2439
90.1-07cy | 6. HVAC | 6.5.1 | Economizers | X |  | X | X | [8 empty] | Economizer 90.1-07cy | The 90.1-2007 costs entered include economizers at the same cost as for 90.1-2010 costs. Under 90.l-2007 some systems are not required to have economizers. Increased costs will occur when the costs are applied to the prototypes when economizers are not required under 90.1-2007, but are required under 90.1- 2010. Maintenance - Verification that the economizer opens, closes, and appears to function properly using cold spray or ice on the outside air sensor. Estimated 45 minutes. To allow for periodic actuator replacement, an additonal 30 minutes is added annually, as well as $25 for a portion of the actuator cost. A web search showed costs in the $50 to $100 range for actuators. Since entire economizers are replaced, not repaired, at typical life, assuming motor replacement costs are accounted for. Adding 5 minutes and $5 for material per 1000 cfm above 1000 cfm. | Equipment from cost estimator estimate with some size units from supplier. Labor estimated approximately from motorized damper costs from RS Means 2012 Mechanical Cost Data. 23 33 13 Dampers. Multi-blade opposed blade 23.33.13.13 (gravity 5990+, motorized 7500+) Maintenance PNNL staff, prior experience with an energy services and commissioning firm. http://www.nextag.com/replacement-damper-motor/products-html RS Means Facilities Maintenance and Repair Guidebook - unit heater motor replacement labor hours. | Faithful and Gould, Aireco representative estimate from some Carrier units |  |  | supply airflow, cfm | Addendum 90.1-07cy adds economizer requirements for climate zones 1a, 2a, 3a, 4a, as shown in 90.1-2010, Table 6.5.1A, Economizers are added in some cases for the climate zone and system types where the new cooling capacity thresholds are lowered under Table 6.5.1A in 90.1-2010. Other provisions require integrated vs. non-integrated economizers, but as noted under the 90.1-2007 case, no costs were identified for this. Costs shown apply to both AHU and DX system economizers, and are added to the base system cost. Costs are the same for sytems for 90.1-2007 and 90.1-2010 for systems that have an economizer. |  | same as for 90.1-2007 | same as for 90.1-2007 |  | supply airflow, cfm |  |  |  |  | 1.239 | [38 empty] | 0
[16 empty] | AHU_Economizer |  | Faithful+Gould | [7 empty] | Aireco - Carrier (pro rated- 3T) |  | SA cfm |  |  |  |  | 1.239 | Mat$ |  |  |  | Lab$ | [33 empty] | 0
[17 empty] | Air-side economizer suitable for an AHU. | Aireco - rep | Carrier | Series 39M |  | 50 |  | Aireco - rep | Carrier | Series 39M |  | 50 |  |  |  |  | 1.239 | 600 | 1 Shee | 63.13 | 0.4995 | 31.5334 |  | 546.5062 | 1178.0397 | 178.7366 | 15 |  | 600 | 1 Shee | 63.13 | 0.82417 | 52.0302 |  | 447.5882 | 1099.6184 |  | 600 | 1 Shee | 63.13 | 0.4995 | 31.5334 |  | 546.5062 |  | 1178.0397 | 178.7366 | 15 |  | 600 | 1 Shee | 63.13 | 0.82417 | 52.0302 |  | 684.4021 | 1336.4323 | 0
[20 empty] | 3T |  | 100 |  |  |  | 3T |  | 100 |  |  |  |  | 1.239 | 700 | 1 Shee | 63.13 | 0.4995 | 31.5334 |  | 632.5164 | 1364.0498 | 179.2279 | 15 |  | 700 | 1 Shee | 63.13 | 0.82417 | 52.0302 |  | 512.7304 | 1264.7606 |  | 700 | 1 Shee | 63.13 | 0.4995 | 31.5334 |  | 632.5164 |  | 1364.0498 | 179.2279 | 15 |  | 700 | 1 Shee | 63.13 | 0.82417 | 52.0302 |  | 789.0133 | 1541.0435 | 0
[16 empty] | These apply to computer rooms |  |  |  | (pro rated- 3T) |  | 250 |  | Vendor indicated costs varied directly with outdoor airflow in proportion to 100 cfm and 1000 cfm units up to 5,000 cfm. Cost estimator estimated larger sizes. |  | (pro rated- 3T) |  | 250 |  |  |  |  | 1.239 | 800 | 1 Shee | 63.13 | 0.4995 | 31.5334 |  | 718.5266 | 1550.06 | 180.7021 | 15 |  | 800 | 1 Shee | 63.13 | 0.82417 | 52.0302 |  | 577.8726 | 1429.9028 |  | 800 | 1 Shee | 63.13 | 0.4995 | 31.5334 |  | 718.5266 |  | 1550.06 | 180.7021 | 15 |  | 800 | 1 Shee | 63.13 | 0.82417 | 52.0302 |  | 893.6245 | 1745.6547 | 0
[16 empty] | 90.1-13 i |  | Vendor indicated costs varied directly with outdoor airflow in proportion to 100 cfm and 1000 cfm units up to 5,000 cfm. Cost estimator estimated larger sizes. |  | (pro rated- 3T) |  | 500 |  |  |  | (pro rated- 3T) |  | 500 |  |  |  |  | 1.239 | 950 | 1 Shee | 63.13 | 0.5715 | 36.0788 |  | 851.9303 | 1838.0091 | 183.1589 | 15 |  | 950 | 1 Shee | 63.13 | 0.94298 | 59.53 |  | 1058.7193 | 2068.2493 |  | 950 | 1 Shee | 63.13 | 0.5715 | 36.0788 |  | 851.9303 |  | 1838.0091 | 183.1589 | 15 |  | 950 | 1 Shee | 63.13 | 0.94298 | 59.53 |  | 1058.7193 | 2068.2493 | 0
[20 empty] | (pro rated- 3T) |  | 1000 |  |  |  | (pro rated- 3T) |  | 1000 |  |  |  |  | 1.239 | 1350 | 1 Shee | 63.13 | 0.666 | 42.0446 |  | 1201.7309 | 2593.7755 | 188.0726 | 15 |  | 1350 | 1 Shee | 63.13 | 1.0989 | 69.3736 |  | 1487.8977 | 2907.2713 |  | 1350 | 1 Shee | 63.13 | 0.666 | 42.0446 |  | 1201.7309 |  | 2593.7755 | 188.0726 | 15 |  | 1350 | 1 Shee | 63.13 | 1.0989 | 69.3736 |  | 1487.8977 | 2907.2713 | 0
[20 empty] | (pro rated- 3T) |  | 2000 |  |  |  | (pro rated- 3T) |  | 2000 |  |  |  |  | 1.239 | 1805 | 1 Shee | 63.13 | 0.7995 | 50.4724 |  | 1601.2142 | 3456.6867 | 197.9001 | 15 |  | 1805 | 1 Shee | 63.13 | 1.3192 | 83.2795 |  | 1979.0421 | 3867.3216 |  | 1805 | 1 Shee | 63.13 | 0.7995 | 50.4724 |  | 1601.2142 |  | 3456.6867 | 197.9001 | 15 |  | 1805 | 1 Shee | 63.13 | 1.3192 | 83.2795 |  | 1979.0421 | 3867.3216 | 0
[20 empty] | (pro rated- 3T) |  | 3000 |  |  |  | (pro rated- 3T) |  | 3000 |  |  |  |  | 1.239 | 2137.5 | 1 Shee | 63.13 | 0.9225 | 58.2374 |  | 1894.6951 | 4090.4325 | 207.7275 | 15 |  | 2137.5 | 1 Shee | 63.13 | 1.5221 | 96.0918 |  | 2340.8451 | 4574.4368 |  | 2137.5 | 1 Shee | 63.13 | 0.9225 | 58.2374 |  | 1894.6951 |  | 4090.4325 | 207.7275 | 15 |  | 2137.5 | 1 Shee | 63.13 | 1.5221 | 96.0918 |  | 2340.8451 | 4574.4368 | 0
[20 empty] | (pro rated- 3T) |  | 4000 |  |  |  | (pro rated- 3T) |  | 4000 |  |  |  |  | 1.239 | 2850 | 1 Shee | 63.13 | 1.0455 | 66.0024 |  | 2515.0146 | 5431.017 | 217.555 | 15 |  | 2850 | 1 Shee | 63.13 | 1.7251 | 108.904 |  | 3100.1706 | 6059.0746 |  | 2850 | 1 Shee | 63.13 | 1.0455 | 66.0024 |  | 2515.0146 |  | 5431.017 | 217.555 | 15 |  | 2850 | 1 Shee | 63.13 | 1.7251 | 108.904 |  | 3100.1706 | 6059.0746 | 0
[20 empty] | (pro rated- 3T) |  | 5000 |  |  |  | (pro rated- 3T) |  | 5000 |  |  |  |  | 1.239 | 3384.375 | 1 Shee | 63.13 | 1.1685 | 73.7674 |  | 2982.1285 | 6440.2709 | 227.3824 | 15 |  | 3384.375 | 1 Shee | 63.13 | 1.928 | 121.7162 |  | 3673.1574 | 7179.2487 |  | 3384.375 | 1 Shee | 63.13 | 1.1685 | 73.7674 |  | 2982.1285 |  | 6440.2709 | 227.3824 | 15 |  | 3384.375 | 1 Shee | 63.13 | 1.928 | 121.7162 |  | 3673.1574 | 7179.2487 | 0
[20 empty] | cost estimator |  | 6000 |  |  |  | cost estimator |  | 6000 |  |  |  |  | 1.239 | 4061.25 | 1 Shee | 63.13 | 1.2915 | 81.5324 |  | 3571.8069 | 7714.5893 | 237.2098 | 15 |  | 4061.25 | 1 Shee | 63.13 | 2.131 | 134.5285 |  | 4395.2152 | 8590.9937 |  | 4061.25 | 1 Shee | 63.13 | 1.2915 | 81.5324 |  | 3571.8069 |  | 7714.5893 | 237.2098 | 15 |  | 4061.25 | 1 Shee | 63.13 | 2.131 | 134.5285 |  | 4395.2152 | 8590.9937 | 0
[20 empty] | cost estimator |  | 7000 |  |  |  | cost estimator |  | 7000 |  |  |  |  | 1.239 | 4738.125 | 1 Shee | 63.13 | 1.4145 | 89.2974 |  | 4161.4853 | 8988.9077 | 247.0373 | 15 |  | 4738.125 | 1 Shee | 63.13 | 2.3339 | 147.3407 |  | 5117.273 | 10002.7387 |  | 4738.125 | 1 Shee | 63.13 | 1.4145 | 89.2974 |  | 4161.4853 |  | 8988.9077 | 247.0373 | 15 |  | 4738.125 | 1 Shee | 63.13 | 2.3339 | 147.3407 |  | 5117.273 | 10002.7387 | 0
[20 empty] | cost estimator |  | 10000 |  |  |  | cost estimator |  | 10000 |  |  |  |  | 1.239 | 6410 | 1 Shee | 63.13 | 2.02 | 127.5226 |  | 5636.3739 | 12173.8965 | 276.5196 | 15 |  | 6410 | 1 Shee | 63.13 | 3.333 | 210.4123 |  | 6935.0163 | 13555.4285 |  | 6410 | 1 Shee | 63.13 | 2.02 | 127.5226 |  | 5636.3739 |  | 12173.8965 | 276.5196 | 15 |  | 6410 | 1 Shee | 63.13 | 3.333 | 210.4123 |  | 6935.0163 | 13555.4285 | 0
[20 empty] | cost estimator |  | 20000 |  |  |  | cost estimator |  | 20000 |  |  |  |  | 1.239 | 12820 | 1 Shee | 63.13 | 4.04 | 255.0452 |  | 11272.7479 | 24347.7931 | 374.794 | 15 |  | 12820 | 1 Shee | 63.13 | 6.666 | 420.8246 |  | 13870.0325 | 27110.8571 |  | 12820 | 1 Shee | 63.13 | 4.04 | 255.0452 |  | 11272.7479 |  | 24347.7931 | 374.794 | 15 |  | 12820 | 1 Shee | 63.13 | 6.666 | 420.8246 |  | 13870.0325 | 27110.8571 | 0
[20 empty] | cost estimator |  | 30000 |  |  |  | cost estimator |  | 30000 |  |  |  |  | 1.239 | 19230 | 1 Shee | 63.13 | 6.06 | 382.5678 |  | 16909.1218 | 36521.6896 | 473.0684 | 15 |  | 19230 | 1 Shee | 63.13 | 9.999 | 631.2369 |  | 20805.0488 | 40666.2856 |  | 19230 | 1 Shee | 63.13 | 6.06 | 382.5678 |  | 16909.1218 |  | 36521.6896 | 473.0684 | 15 |  | 19230 | 1 Shee | 63.13 | 9.999 | 631.2369 |  | 20805.0488 | 40666.2856 | 0
[20 empty] | cost estimator |  | 40000 |  |  |  | cost estimator |  | 40000 |  |  |  |  | 1.239 | 25640 | 1 Shee | 63.13 | 8.08 | 510.0904 |  | 22545.4958 | 48695.5862 | 571.3428 | 15 |  | 25640 | 1 Shee | 63.13 | 13.332 | 841.6492 |  | 27740.065 | 54221.7142 |  | 25640 | 1 Shee | 63.13 | 8.08 | 510.0904 |  | 22545.4958 |  | 48695.5862 | 571.3428 | 15 |  | 25640 | 1 Shee | 63.13 | 13.332 | 841.6492 |  | 27740.065 | 54221.7142 | 0
[20 empty] | cost estimator |  | 50000 |  |  |  | cost estimator |  | 50000 |  |  |  |  | 1.239 | 32050 | 1 Shee | 63.13 | 10.1 | 637.613 |  | 28181.8697 | 60869.4827 | 669.6172 | 15 |  | 32050 | 1 Shee | 63.13 | 16.665 | 1052.0614 |  | 34675.0813 | 67777.1427 |  | 32050 | 1 Shee | 63.13 | 10.1 | 637.613 |  | 28181.8697 |  | 60869.4827 | 669.6172 | 15 |  | 32050 | 1 Shee | 63.13 | 16.665 | 1052.0614 |  | 34675.0813 | 67777.1427 | 0
[20 empty] | cost estimator |  | 100000 |  |  |  | cost estimator |  | 100000 |  |  |  |  | 1.239 | 63275.09 | 1 Shee | 63.13 | 17.2391 | 1088.307 |  | 55473.7648 | 119837.1618 | 1160.9892 | 15 |  | 63275.09 | 1 Shee | 63.13 | 28.4446 | 1795.7066 |  | 68150.9098 | 133221.7063 |  | 63275.09 | 1 Shee | 63.13 | 17.2391 | 1088.307 |  | 55473.7648 |  | 119837.1618 | 1160.9892 | 15 |  | 63275.09 | 1 Shee | 63.13 | 28.4446 | 1795.7066 |  | 68150.9098 | 133221.7063 | 0
[16 empty] | DX_Economizer | Economizer | [15 empty] | 1.239 | [11 empty] | 0 | [8 empty] | 0 | [17 empty] | 0
[17 empty] | Air-side economizer suitable for a DX Packaged rooftop unit. | Aireco - rep | Carrier | Series 39M |  | 50 |  | Aireco - rep | Carrier | Carrier (pro rated- 3T) 39M |  | 50 |  |  |  |  | 1.239 | 600 | 1 Shee | 63.13 | 0.4995 | 31.5334 |  | 546.5062 | 1178.0397 | 134.8431 | 15 |  | 600 | 1 Shee | 63.13 | 0.82417 | 52.0302 |  | 684.4021 | 1336.4323 |  | 600 | 1 Shee | 63.13 | 0.4995 | 31.5334 |  | 546.5062 |  | 1178.0397 | 134.8431 | 15 |  | 600 | 1 Shee | 63.13 | 0.82417 | 52.0302 |  | 684.4021 | 1336.4323 | 0
[16 empty] | used for load changes |  |  |  | 3T |  | 100 |  |  |  | 3T |  | 100 |  |  |  |  | 1.239 | 700 | 1 Shee | 63.13 | 0.4995 | 31.5334 |  | 632.5164 | 1364.0498 | 134.8431 | 15 |  | 700 | 1 Shee | 63.13 | 0.82417 | 52.0302 |  | 789.0133 | 1541.0435 |  | 700 | 1 Shee | 63.13 | 0.4995 | 31.5334 |  | 632.5164 |  | 1364.0498 | 134.8431 | 15 |  | 700 | 1 Shee | 63.13 | 0.82417 | 52.0302 |  | 789.0133 | 1541.0435 | 0
[18 empty] | Vendor indicated costs varied directly with outdoor airflow in proportion to 100 cfm and 1000 cfm units up to 5,000 cfm. Cost estimator estimated larger sizes. |  | (pro rated- 3T) |  | 250 |  | Vendor indicated costs varied directly with outdoor airflow in proportion to 100 cfm and 1000 cfm units up to 5,000 cfm. Cost estimator estimated larger sizes. |  | (pro rated- 3T) |  | 250 |  |  |  |  | 1.239 | 800 | 1 Shee | 63.13 | 0.4995 | 31.5334 |  | 718.5266 | 1550.06 | 134.8431 | 15 |  | 800 | 1 Shee | 63.13 | 0.82417 | 52.0302 |  | 893.6245 | 1745.6547 |  | 800 | 1 Shee | 63.13 | 0.4995 | 31.5334 |  | 718.5266 |  | 1550.06 | 134.8431 | 15 |  | 800 | 1 Shee | 63.13 | 0.82417 | 52.0302 |  | 893.6245 | 1745.6547 | 0
[20 empty] | (pro rated- 3T) |  | 500 |  |  |  | (pro rated- 3T) |  | 500 |  |  |  |  | 1.239 | 950 | 1 Shee | 63.13 | 0.5715 | 36.0788 |  | 851.9303 | 1838.0091 | 134.8431 | 15 |  | 950 | 1 Shee | 63.13 | 0.94298 | 59.53 |  | 1058.7193 | 2068.2493 |  | 950 | 1 Shee | 63.13 | 0.5715 | 36.0788 |  | 851.9303 |  | 1838.0091 | 134.8431 | 15 |  | 950 | 1 Shee | 63.13 | 0.94298 | 59.53 |  | 1058.7193 | 2068.2493 | 0
[20 empty] | (pro rated- 3T) |  | 1000 |  |  |  | 3T |  | 1000 |  |  |  |  | 1.239 | 1350 | 1 Shee | 63.13 | 0.666 | 42.0446 |  | 1201.7309 | 2593.7755 | 134.8431 | 15 |  | 1350 | 1 Shee | 63.13 | 1.0989 | 69.3736 |  | 1487.8977 | 2907.2713 |  | 1350 | 1 Shee | 63.13 | 0.666 | 42.0446 |  | 1201.7309 |  | 2593.7755 | 134.8431 | 15 |  | 1350 | 1 Shee | 63.13 | 1.0989 | 69.3736 |  | 1487.8977 | 2907.2713 | 0
[20 empty] | (pro rated- 3T) |  | 2000 |  |  |  | 3T |  | 2000 |  |  |  |  | 1.239 | 1805 | 1 Shee | 63.13 | 0.7995 | 50.4724 |  | 1601.2142 | 3456.6867 | 148.1301 | 15 |  | 1805 | 1 Shee | 63.13 | 1.3192 | 83.2795 |  | 1979.0421 | 3867.3216 |  | 1805 | 1 Shee | 63.13 | 0.7995 | 50.4724 |  | 1601.2142 |  | 3456.6867 | 148.1301 | 15 |  | 1805 | 1 Shee | 63.13 | 1.3192 | 83.2795 |  | 1979.0421 | 3867.3216 | 0
[20 empty] | (pro rated- 3T) |  | 3000 |  |  |  | 3T |  | 3000 |  |  |  |  | 1.239 | 2137.5 | 1 Shee | 63.13 | 0.9225 | 58.2374 |  | 1894.6951 | 4090.4325 | 161.4171 | 15 |  | 2137.5 | 1 Shee | 63.13 | 1.5221 | 96.0918 |  | 2340.8451 | 4574.4368 |  | 2137.5 | 1 Shee | 63.13 | 0.9225 | 58.2374 |  | 1894.6951 |  | 4090.4325 | 161.4171 | 15 |  | 2137.5 | 1 Shee | 63.13 | 1.5221 | 96.0918 |  | 2340.8451 | 4574.4368 | 0
[20 empty] | (pro rated- 3T) |  | 4000 |  |  |  | 3T |  | 4000 |  |  |  |  | 1.239 | 2850 | 1 Shee | 63.13 | 0.666 | 42.0446 |  | 2491.8836 | 5383.9282 | 174.7042 | 15 |  | 2850 | 1 Shee | 63.13 | 1.0989 | 69.3736 |  | 3057.0657 | 5976.4392 |  | 2850 | 1 Shee | 63.13 | 0.666 | 42.0446 |  | 2491.8836 |  | 5383.9282 | 174.7042 | 15 |  | 2850 | 1 Shee | 63.13 | 1.0989 | 69.3736 |  | 3057.0657 | 5976.4392 | 0
[20 empty] | (pro rated- 3T) |  | 5000 |  |  |  | (pro-rated) |  | 5000 |  |  |  |  | 1.239 | 3384.375 | 1 Shee | 63.13 | 1.4145 | 89.2974 |  | 2997.1225 | 6470.7949 | 214.5653 | 15 |  | 3384.375 | 1 Shee | 63.13 | 2.3339 | 147.3407 |  | 3701.099 | 7232.8147 |  | 3384.375 | 1 Shee | 63.13 | 1.4145 | 89.2974 |  | 2997.1225 |  | 6470.7949 | 214.5653 | 15 |  | 3384.375 | 1 Shee | 63.13 | 2.3339 | 147.3407 |  | 3701.099 | 7232.8147 | 0
[20 empty] | cost estimator |  | 6000 |  |  |  | (pro-rated) |  | 6000 |  |  |  |  | 1.239 | 4061.25 | 1 Shee | 63.13 | 2.02 | 127.5226 |  | 3616.2099 | 7804.9825 | 214.5653 | 15 |  | 4061.25 | 1 Shee | 63.13 | 3.333 | 210.4123 |  | 4477.9608 | 8749.6231 |  | 4061.25 | 1 Shee | 63.13 | 2.02 | 127.5226 |  | 3616.2099 |  | 7804.9825 | 214.5653 | 15 |  | 4061.25 | 1 Shee | 63.13 | 3.333 | 210.4123 |  | 4477.9608 | 8749.6231 | 0
[20 empty] | cost estimator |  | 7000 |  |  |  | 3T |  | 7000 |  |  |  |  | 1.239 | 4738.125 | 1 Shee | 63.13 | 1.0455 | 66.0024 |  | 4138.9943 | 8943.1217 | 174.7042 | 15 |  | 4738.125 | 1 Shee | 63.13 | 1.7251 | 108.904 |  | 5075.3607 | 9922.3897 |  | 4738.125 | 1 Shee | 63.13 | 1.0455 | 66.0024 |  | 4138.9943 |  | 8943.1217 | 174.7042 | 15 |  | 4738.125 | 1 Shee | 63.13 | 1.7251 | 108.904 |  | 5075.3607 | 9922.3897 | 0
[20 empty] | cost estimator |  | 10000 |  |  |  | (pro-rated) |  | 10000 |  |  |  |  | 1.239 | 6410 | 1 Shee | 63.13 | 6.06 | 382.5678 |  | 5882.617 | 12675.1848 | 214.5653 | 15 |  | 6410 | 1 Shee | 63.13 | 9.999 | 631.2369 |  | 7393.8935 | 14435.1303 |  | 6410 | 1 Shee | 63.13 | 6.06 | 382.5678 |  | 5882.617 |  | 12675.1848 | 214.5653 | 15 |  | 6410 | 1 Shee | 63.13 | 9.999 | 631.2369 |  | 7393.8935 | 14435.1303 | 0
[20 empty] | cost estimator |  | 15000 |  |  |  | (pro-rated) |  | 15000 |  |  |  |  | 1.239 | 9615 | 1 Shee | 63.13 | 8.08 | 510.0904 |  | 8762.3648 | 18887.4552 | 214.5653 | 15 |  | 9615 | 1 Shee | 63.13 | 13.332 | 841.6492 |  | 10976.1209 | 21432.7701 |  | 9615 | 1 Shee | 63.13 | 8.08 | 510.0904 |  | 8762.3648 |  | 18887.4552 | 214.5653 | 15 |  | 9615 | 1 Shee | 63.13 | 13.332 | 841.6492 |  | 10976.1209 | 21432.7701 | 0
[20 empty] | cost estimator |  | 20000 |  |  |  | (pro-rated) |  | 20000 |  |  |  |  | 1.239 | 12820 | 1 Shee | 63.13 | 17.2391 | 1088.307 |  | 12077.2522 | 25985.5592 | 214.5653 | 15 |  | 12820 | 1 Shee | 63.13 | 28.4446 | 1795.7066 |  | 15369.2368 | 29984.9434 |  | 12820 | 1 Shee | 63.13 | 17.2391 | 1088.307 |  | 12077.2522 |  | 25985.5592 | 214.5653 | 15 |  | 12820 | 1 Shee | 63.13 | 28.4446 | 1795.7066 |  | 15369.2368 | 29984.9434 | 0
Transfer Grilles 90.1-2013 u
[16 empty] | Transfer_Door_Louvers | Addendum 90.1-2013 u requires that transfer air be generally used for restrooms, not just kitchens. In base case, restrooms will have supply air grilles connected to supply air for temperaturer control. Basis 200 cfm | Means Mechanical 2018 Diffuser: 23 37 13.10 Duct: | 6" aluminum diffuser 6" duct, 20 ft long |  |  |  | Addendum 90.1-2013 u requires that transfer air be generally used for restrooms, not just kitchens. For the prototypes analyzed; transfer air requirements can be met with door grilles to allow transfer air to enter restrooms where it is exhausted. The transfer air can be met by one 24x24" door louver being added to the restroom door. | RS Means Building 2018. 08 91 26.10 Steel louvers, painted |  | 24" x 24" | [6 empty] | 1 | 66.2 | Q-10 | 65.47 | 1.473 | 96.4373 |  | 126.2946 | 288.932 | 0 | 30 |  | 66.2 |  |  |  | 96.4373 |  | 148.2817 | 310.919 |  | 131 |  |  |  | 17.65 |  | 82.7102 |  | 231.3602 | 0 | 30 |  | 131 |  |  |  | 17.65 |  | 104.5823 | 253.2323 | -57.5717
90.1-07e and 90.1-07 dj | 6. HVAC | 6.5.6 | Energy recovery - yes/no | X |  | X | X | [8 empty] | Energy Recovery Adjustments for when ERV is required based on load changes | 90.1 includes criteria for when energy recovery is required that varies by climate and percentage of outside in the design supply airflow. Energy recovery units with wheel type exchange devices are priced and are commonly used. Note that the cost estimate did not identify a different cost for adding energy recovery for AHU vs. Packaged DX. Energy recovery are priced as added stand alone equipment, not manufacturer integrated add-ons. Costs shown under material include labor. Maintenance for an ERV is similar to that for a packaged DX unit and includes lubrication, checking dampers, adjusting belts, replacing filters, checking doorseals and cleaning coils. RS Means provided a rough estimate for a set of routine AC maintenace activities that total about 2.5 hours. In addition, the energy recovery wheels need to be cleaned. At least one manufacturer claims the media will last the life of the system, and cleaning can take about 15 minutes with frequency from every six months to 10 year depending on conditions, so including 15 minutes each year. | Michael J. Witte, M.J. and R.H. Henninger. 2006. ASHRAE 1254-RP Evaluating the ability of Unitary Equipment to maintain adequate space humidity levels, Phase II. Gard Analytics Park Ridge, Illinois. Approach recommended by SSPC 90.1 MSC. Maintenance RS Means Mechanical 01 93 13.15 http://www.airxchange.com/faqs.htm |  |  |  | Outside Airflow, cfm | Costs used to adjust for ERV size based on load, or when changes in load or airflow result in changed requirement for ERV. Same as base code. | Same as base code. |  |  |  | Outside Airflow, cfm |  |  |  |  | Inflation from 2012 to 2023
[16 empty] | Energy_Recovery_AHU | Energy Recovery for AHU | [5 empty] | Energy Recovery for AHU
[22 empty] | 500 | [5 empty] | 500 |  | 1.5 |  |  | 1.235 | 1875 | Q9 | 63.13 | 11.1106 | 701.4094 |  | 2278.6335 | 4855.0428 | 255.0825 | 15 |  | 1875 | Q9 | 63.13 | 18.3324 | 1157.3255 |  | 3211.0497 | 6243.3752 |  | 1875 | Q9 | 63.13 | 11.1106 | 701.4094 |  | 2278.6335 |  | 4855.0428 | 255.0825 | 15 |  | 1875 | Q9 | 63.13 | 18.3324 | 1157.3255 |  | 3211.0497 | 6243.3752 | 0
[16 empty] | used for load changes | [5 empty] | 1000 | [5 empty] | 1000 |  | 3 |  |  | 1.235 | 3750 | Q9 | 63.13 | 13.333 | 841.7123 |  | 4015.5254 | 8607.2377 | 255.0825 | 15 |  | 3750 | Q9 | 63.13 | 21.9994 | 1388.8253 |  | 5412.5569 | 10551.3822 |  | 3750 | Q9 | 63.13 | 13.333 | 841.7123 |  | 4015.5254 |  | 8607.2377 | 255.0825 | 15 |  | 3750 | Q9 | 63.13 | 21.9994 | 1388.8253 |  | 5412.5569 | 10551.3822 | 0
[22 empty] | 2000 | [5 empty] | 2000 |  | 5 |  |  | 1.235 | 7500 | Q9 | 63.13 | 16 | 1010.08 |  | 7380.9447 | 15891.0247 | 255.0825 | 15 |  | 7500 | Q9 | 63.13 | 26.4 | 1666.632 |  | 9613.6325 | 18780.2645 |  | 7500 | Q9 | 63.13 | 16 | 1010.08 |  | 7380.9447 |  | 15891.0247 | 255.0825 | 15 |  | 7500 | Q9 | 63.13 | 26.4 | 1666.632 |  | 9613.6325 | 18780.2645 | 0
[22 empty] | 4000 | [5 empty] | 4000 |  | 7.5 |  |  | 1.235 | 15000 | Q9 | 63.13 | 20 | 1262.6 |  | 14030.4743 | 30293.0743 | 255.0825 | 15 |  | 15000 | Q9 | 63.13 | 33 | 2083.29 |  | 17864.2634 | 34947.5534 |  | 15000 | Q9 | 63.13 | 20 | 1262.6 |  | 14030.4743 |  | 30293.0743 | 255.0825 | 15 |  | 15000 | Q9 | 63.13 | 33 | 2083.29 |  | 17864.2634 | 34947.5534 | 0
[22 empty] | 6000 | [5 empty] | 6000 |  | 10 |  |  | 1.235 | 22500 | Q9 | 63.13 | 22.857 | 1442.9624 |  | 20610.3366 | 44553.299 | 255.0825 | 15 |  | 22500 | Q9 | 63.13 | 37.7141 | 2380.888 |  | 25985.0684 | 50865.9564 |  | 22500 | Q9 | 63.13 | 22.857 | 1442.9624 |  | 20610.3366 |  | 44553.299 | 255.0825 | 15 |  | 22500 | Q9 | 63.13 | 37.7141 | 2380.888 |  | 25985.0684 | 50865.9564 | 0
[22 empty] | 8000 | [5 empty] | 8000 |  | 15 |  |  | 1.235 | 30000 | Q9 | 63.13 | 24 | 1515.12 |  | 27085.7284 | 58600.8484 | 255.0825 | 15 |  | 30000 | Q9 | 63.13 | 39.6 | 2499.948 |  | 33911.1914 | 66411.1394 |  | 30000 | Q9 | 63.13 | 24 | 1515.12 |  | 27085.7284 |  | 58600.8484 | 255.0825 | 15 |  | 30000 | Q9 | 63.13 | 39.6 | 2499.948 |  | 33911.1914 | 66411.1394 | 0
[22 empty] | 10000 | [5 empty] | 10000 |  | 20 |  |  | 1.235 | 37500 | Q9 | 63.13 | 26.667 | 1683.4877 |  | 33654.01 | 72837.4977 | 255.0825 | 15 |  | 37500 | Q9 | 63.13 | 44.0005 | 2777.7547 |  | 42010.4155 | 82288.1702 |  | 37500 | Q9 | 63.13 | 26.667 | 1683.4877 |  | 33654.01 |  | 72837.4977 | 255.0825 | 15 |  | 37500 | Q9 | 63.13 | 44.0005 | 2777.7547 |  | 42010.4155 | 82288.1702 | 0
[22 empty] | 15000 | [5 empty] | 15000 |  | 25 |  |  | 1.235 | 56250 | Q9 | 63.13 | 28.3335 | 1788.6939 |  | 49769.8967 | 107808.5905 | 255.0825 | 15 |  | 56250 | Q9 | 63.13 | 46.7503 | 2951.3449 |  | 61690.4449 | 120891.7897 |  | 56250 | Q9 | 63.13 | 28.3335 | 1788.6939 |  | 49769.8967 |  | 107808.5905 | 255.0825 | 15 |  | 56250 | Q9 | 63.13 | 46.7503 | 2951.3449 |  | 61690.4449 | 120891.7897 | 0
[16 empty] | Energy_Recovery_Packaged | Energy Recovery for Packaged DX Rooftop | [5 empty] | Energy Recovery for Packaged DX Rooftop | [9 empty] | 1.235 | [6 empty] | 0 | [10 empty] | 0
[22 empty] | 500 |  | Same as for AHU energy recovery |  |  |  | 500 |  | 1.5 |  |  | 1.235 | 1875 | Q9 | 63.13 | 11.1106 | 701.4094 |  | 2278.6335 | 4855.0428 | 255.0825 | 15 |  | 1875 | Q9 | 63.13 | 18.3324 | 1157.3255 |  | 3211.0497 | 6243.3752 |  | 1875 | Q9 | 63.13 | 11.1106 | 701.4094 |  | 2278.6335 |  | 4855.0428 | 255.0825 | 15 |  | 1875 | Q9 | 63.13 | 18.3324 | 1157.3255 |  | 3211.0497 | 6243.3752 | 0
[16 empty] | used for load changes | [5 empty] | 1000 |  | mechanical subcommittee |  |  |  | 1000 |  | 3 |  |  | 1.235 | 3750 | Q9 | 63.13 | 13.333 | 841.7123 |  | 4015.5254 | 8607.2377 | 255.0825 | 15 |  | 3750 | Q9 | 63.13 | 21.9994 | 1388.8253 |  | 5412.5569 | 10551.3822 |  | 3750 | Q9 | 63.13 | 13.333 | 841.7123 |  | 4015.5254 |  | 8607.2377 | 255.0825 | 15 |  | 3750 | Q9 | 63.13 | 21.9994 | 1388.8253 |  | 5412.5569 | 10551.3822 | 0
[22 empty] | 2000 | [5 empty] | 2000 |  | 5 |  |  | 1.235 | 7500 | Q9 | 63.13 | 16 | 1010.08 |  | 7380.9447 | 15891.0247 | 255.0825 | 15 |  | 7500 | Q9 | 63.13 | 26.4 | 1666.632 |  | 9613.6325 | 18780.2645 |  | 7500 | Q9 | 63.13 | 16 | 1010.08 |  | 7380.9447 |  | 15891.0247 | 255.0825 | 15 |  | 7500 | Q9 | 63.13 | 26.4 | 1666.632 |  | 9613.6325 | 18780.2645 | 0
[22 empty] | 4000 |  | Maintenance - estimated from hours for the wheel maintenance only under RS Means Facilities and Maintenance Guidebook 2004 ed. 0.5 hrs, cleaning and checking, plus 5 minutes/1000 cfm above 1,000 cfm. |  |  |  | 4000 |  | 7.5 |  |  | 1.235 | 15000 | Q9 | 63.13 | 20 | 1262.6 |  | 14030.4743 | 30293.0743 | 255.0825 | 15 |  | 15000 | Q9 | 63.13 | 33 | 2083.29 |  | 17864.2634 | 34947.5534 |  | 15000 | Q9 | 63.13 | 20 | 1262.6 |  | 14030.4743 |  | 30293.0743 | 255.0825 | 15 |  | 15000 | Q9 | 63.13 | 33 | 2083.29 |  | 17864.2634 | 34947.5534 | 0
[22 empty] | 6000 | [5 empty] | 6000 |  | 10 |  |  | 1.235 | 22500 | Q9 | 63.13 | 22.857 | 1442.9624 |  | 20610.3366 | 44553.299 | 255.0825 | 15 |  | 22500 | Q9 | 63.13 | 37.7141 | 2380.888 |  | 25985.0684 | 50865.9564 |  | 22500 | Q9 | 63.13 | 22.857 | 1442.9624 |  | 20610.3366 |  | 44553.299 | 255.0825 | 15 |  | 22500 | Q9 | 63.13 | 37.7141 | 2380.888 |  | 25985.0684 | 50865.9564 | 0
[22 empty] | 8000 | [5 empty] | 8000 |  | 15 |  |  | 1.235 | 30000 | Q9 | 63.13 | 24 | 1515.12 |  | 27085.7284 | 58600.8484 | 255.0825 | 15 |  | 30000 | Q9 | 63.13 | 39.6 | 2499.948 |  | 33911.1914 | 66411.1394 |  | 30000 | Q9 | 63.13 | 24 | 1515.12 |  | 27085.7284 |  | 58600.8484 | 255.0825 | 15 |  | 30000 | Q9 | 63.13 | 39.6 | 2499.948 |  | 33911.1914 | 66411.1394 | 0
[22 empty] | 10000 | [5 empty] | 10000 |  | 20 |  |  | 1.235 | 37500 | Q9 | 63.13 | 26.667 | 1683.4877 |  | 33654.01 | 72837.4977 | 255.0825 | 15 |  | 37500 | Q9 | 63.13 | 44.0005 | 2777.7547 |  | 42010.4155 | 82288.1702 |  | 37500 | Q9 | 63.13 | 26.667 | 1683.4877 |  | 33654.01 |  | 72837.4977 | 255.0825 | 15 |  | 37500 | Q9 | 63.13 | 44.0005 | 2777.7547 |  | 42010.4155 | 82288.1702 | 0
[22 empty] | 15000 | [5 empty] | 15000 |  | 25 |  |  | 1.235 | 56250 | Q9 | 63.13 | 28.3335 | 1788.6939 |  | 49769.8967 | 107808.5905 | 255.0825 | 15 |  | 56250 | Q9 | 63.13 | 46.7503 | 2951.3449 |  | 61690.4449 | 120891.7897 |  | 56250 | Q9 | 63.13 | 28.3335 | 1788.6939 |  | 49769.8967 |  | 107808.5905 | 255.0825 | 15 |  | 56250 | Q9 | 63.13 | 46.7503 | 2951.3449 |  | 61690.4449 | 120891.7897 | 0
[16 empty] | 90.1-16g | Occupied standby control. When a zone is scheduled to be occupied and an occupant sensor indicates zero population, the zone shall have heating and cooling thermostat setback of 1F and should completely shut off HVAC supply air within the deadband | [15 empty] | 2023 costs
[16 empty] | occ_standby | No occupied standby control installed | [5 empty] | Occupied standby control installed labor is per conditioned zone | 2023 RSMeans | [8 empty] | 1 | 0 |  |  |  | 0 |  | 0 | 0 | 0 |  |  | 0 |  |  |  | 0 |  | 0 | 0 |  | 0 | 1 elec | 67.85 | 0.25 | 16.9625 |  | 16.3771 |  | 33.3396 | 0 | 15 |  | 0 | Q5 | 67.85 | 0.4125 | 27.9881 |  | 30.5189 | 58.507 | 33.3396
[16 empty] | 90.1-16 h & ay | Energy Recovery Ventilator for midrise apartments | [15 empty] | 2023 costs
[16 empty] | ERV_multifamily | No ERV installed. Central fan integrated (CFI) system installed with two bathroom exhaust fans. Common low-cost supply ventilation | Energy Cost Analysis for Energy Recovery Ventilation in Dwelling Units. Presentation to ASHRAE 90.1 MSC. 5-31-18 |  |  |  |  | ERV installed. Fan efficacy: 1.2 cfm/W (minimum set in IECC for residential ERVs). Displaces two bathroom exhaust fans. No: defrost, economizing, bypass Costs in Climate Zones 1-3 | Energy Cost Analysis for Energy Recovery Ventilation in Dwelling Units. Presentation to ASHRAE 90.1 MSC. 5-31-18 |  |  |  | 1 ea |  |  |  |  | 1 | 564 |  |  |  | 610 |  | 871.6768 | 2045.6768 | 0 | 15 |  | 564 |  |  |  | 610 |  | 1032.5607 | 2206.5607 |  | 1010 |  |  |  | 437 |  | 928.224 |  | 2375.224 | 15 | 15 |  | 1010 |  |  |  | 437 |  | 1134.4516 | 2581.4516 | 329.5472
[23 empty] | Higher costs in Climate Zones 4-8 due to ERV defrost equipment in colder climates |  |  |  |  | 1 ea |  |  |  |  | 1 | 564 |  |  |  | 610 |  | 871.6768 | 2045.6768 | 0 | 15 |  | 564 |  |  |  | 610 |  | 1032.5607 | 2206.5607 |  | 1081 |  |  |  | 437 |  | 963.8158 |  | 2481.8158 | 15 | 15 |  | 1081 |  |  |  | 437 |  | 1180.7026 | 2698.7026 | 436.139
[16 empty] | DCV_Requirement | For cases where DCV is now required due to reduction in people density threshold. | Based on staff review of recent bid and quote information | \\korea\comstd\90.1_IECC_ State_Cost_Eff\Costs and Cost-Effectiveness\HVAC\DCV\RE primary school cafeteria DCV cost.msg | [12 empty] | DCV_Requirement | 1.0903 | 0 |  |  |  | 0 |  | 0 | 0 | 0 | 15 |  | 0 | Q9 | 0 | 1.5 | 0 |  | 0 | 0 |  | 350 | Q9 | 63.13 | 1.5 | 94.695 |  | 314.316 |  | 759.011 | 0 | 15 |  | 350 | Q9 | 63.13 | 1.5 | 94.695 |  | 383.4358 | 828.1308 | 759.011
[16 empty] | Refrigeration | [15 empty] | Find
[16 empty] | 90.1-16 br | 2 refrigerators, 24 cubic feet each, which implies single door, with daily energy usage described as 0.10V + 2.04, where V is the capacity in cubic feet. | Material costs are from the appliance standard rulemaking | Various | Various |  | ea 24 cu ft refridg | 2 refrigerators, 24 cubic feet each, which implies single door, with daily energy usage described as 0.05V + 1.36, where V is the capacity in cubic feet. | Material costs are from the appliance standard rulemaking | Various | Various |  | ea 24 cu ft refridg |  |  |  | eff_Refr | 1 | 4133 | NA | 0 | 0 | 0 |  | 2071.8431 | 6204.8431 | 0 | 15 |  | 4133 | NA | 0 | 0 | 0 |  | 2692.3275 | 6825.3275 |  | 7242 | NA | 0 | 0 | 0 |  | 3630.3625 |  | 10872.3625 |  | 15 |  | 7242 | NA | 0 | 0 | 0 |  | 4717.5987 | 11959.5987 | 4667.5193
[16 empty] | 90.1-16 br | 2 freezers, 48 cubic feet each, which implies double door, with daily energy usage described as 0.40 x V + 1.38, where V is the capacity in cubic feet. | Material costs are from the appliance standard rulemaking | Various | Various |  | ea 48 cu ft freezer | 2 freezers, 48 cubic feet each, which implies double door, with daily energy usage described as 0.22 x V + 1.38, where V is the capacity in cubic feet. | Material costs are from the appliance standard rulemaking | Various | Various |  | ea 48 cu ft freezer |  |  |  | eff_Frzr | 1 | 4483 | NA | 0 | 0 | 0 |  | 2247.2956 | 6730.2956 | 0 | 15 |  | 4483 | NA | 0 | 0 | 0 |  | 2920.3252 | 7403.3252 |  | 5201 | NA | 0 | 0 | 0 |  | 2607.2239 |  | 7808.2239 |  | 15 |  | 5201 | NA | 0 | 0 | 0 |  | 3388.0462 | 8589.0462 | 1077.9282
[16 empty] | 90.1-16 cn | primary school walk-in refrigerator, COP 3.0 | Material costs are from the appliance standard rulemaking |  |  |  | 1 ea | primary school walk-in refrigerator, COP 6.98 | Material costs are from the appliance standard rulemaking |  |  |  | 1 ea |  |  |  | eff_WI_Refr | 1 | 5146 | 1 elec | 67.85 | 1.5 | 101.775 |  | 2677.9153 | 7925.6903 | 0 | 15 |  | 5146 | 1 elec | 67.85 | 2.475 | 167.9288 |  | 3535.3316 | 8849.2603 |  | 5602 | 1 elec | 67.85 | 1.5 | 101.775 |  | 2906.5048 |  | 8610.2798 |  | 15 |  | 5602 | 1 elec | 67.85 | 2.475 | 167.9288 |  | 3832.38 | 9602.3088 | 684.5895
[16 empty] | 90.1-16 cn | primary school walk-in freezer, COP 1.5 | Material costs are from the appliance standard rulemaking |  |  |  | 1 ea | primary school walk-in freezer, COP 2.32 | Material costs are from the appliance standard rulemaking |  |  |  | 1 ea |  |  |  | eff_WI_Frzr | 1 | 6422 | 1 elec | 67.85 | 1.5 | 101.775 |  | 3317.5649 | 9841.3399 | 0 | 15 |  | 6422 | 1 elec | 67.85 | 2.475 | 167.9288 |  | 4366.5461 | 10956.4749 |  | 6777 | 1 elec | 67.85 | 1.5 | 101.775 |  | 3495.5238 |  | 10374.2988 |  | 15 |  | 6777 | 1 elec | 67.85 | 2.475 | 167.9288 |  | 4597.801 | 11542.7297 | 532.9589
[16 empty] | 90.1-10g | Addendum G Commercial Refrigerators for Primary School: 2 refrigerators, 24 cubic feet each, which implies single door, with daily energy usage described as 0.125V+4.22, where V is the capacity in cubic feet. | RSMeans 2014 Green Building Data plus 5 commercial refrigeration equipment websites | Various | Various |  | ea 24 cu ft refridg | 2 refrigerators, 24 cubic feet each, which implies single door, with daily energy usage described as 0.10V + 2.04, where V is the capacity in cubic feet. | RSMeans 2014 Green Building Data plus 5 commercial refrigeration equipment websites | Various | Various |  | ea 24 cu ft refridg |  |  |  | eff_Refr_OLD | 1 | 2982.56 | NA | 0 | 0 | 0 |  | 1495.1359 | 4477.6959 | 0 | 15 |  | 2982.56 | NA | 0 | 0 | 0 |  | 1942.9054 | 4925.4654 |  | 3007.85 | NA | 0 | 0 | 0 |  | 1507.8135 |  | 4515.6635 | 0 | 15 |  | 3007.85 | Q5 | 0 | 0 | 0 |  | 1959.3799 | 4967.2299 | 37.9677
[17 empty] | Addendum G Commercial Freezer for Primary School8/27/2014 2 freezers, 48 cubic feet each, which implies double door, with daily energy usage described as 0.398 V+2.83, where V is the capacity in cubic feet. | RSMeans 2014 Green Building Data plus 4 commercial refrigeration equipment websites | Various | Various |  | ea 48 cu ft freezer | 2 freezers, 48 cubic feet each, which implies double door, with daily energy usage described as 0.40 x V + 1.38, where V is the capacity in cubic feet. | RSMeans 2014 Green Building Data plus 4 commercial refrigeration equipment websites | Various | Various |  | ea 48 cu ft freezer |  |  |  | eff_Frzr_OLD | 1 | 1857.34 | NA | 0 | 0 | 0 |  | 931.0712 | 2788.4112 | 0 | 15 |  | 1857.34 | NA | 0 | 0 | 0 |  | 1209.9123 | 3067.2523 |  | 5385.58 | NA | 0 | 0 | 0 |  | 2699.7525 |  | 8085.3325 | 0 | 15 |  | 5385.58 | Q5 | 0 | 0 | 0 |  | 3508.2857 | 8893.8657 | 5296.9213
[16 empty] | 90.1-10ar | Addendum AR 1/20 hp motor for primary school walk-in refrigerator evaporator fan: 1/20 hp shaded pole motor | Grainger Catalog (www.grainger.com) | Dayton | 6NZR7 |  | 1 ea | 1/20 hp ECM motor for primary school walk-in refrigerator evaporator fan | Grainger Catalog (www.grainger.com) | Morrill | 12V783 |  | 1 ea |  |  |  | WI_Refr_ECM | 1 | 89.4 | 1 elec | 67.85 | 1.501 | 101.8428 |  | 143.1436 | 334.3865 | 0 | 15 |  | 89.4 | 1 elec | 67.85 | 2.4766 | 168.0407 |  | 241.4727 | 498.9135 |  | 126.85 | 1 elec | 67.85 | 1.501 | 101.8428 |  | 161.917 |  | 390.6099 | 0 | 15 |  | 126.85 | Q5 | 67.85 | 2.4766 | 168.0407 |  | 265.8685 | 560.7592 | 56.2234
[17 empty] | Addendum AR 1/40 hp motor for primary school walk-in freezer evaporator fan: 1/40 hp shaded pole motor | Grainger Catalog (www.grainger.com) | Dayton | 3M724 |  | 1 ea | 1/40 hp ECM motor for primary school walk-in freezer evaporator fan (1/40 hp ECM motor not available so cost interpolated from 1/30 and 1/50 hp motors | Grainger Catalog (www.grainger.com) | Morrill | Interpolated (See below) |  | 1 ea |  |  |  | WI_Frzr_ECM | 1 | 93.25 | 1 elec | 67.85 | 1.501 | 101.8428 |  | 145.0736 | 340.1665 | 0 | 15 |  | 93.25 | 1 elec | 67.85 | 2.4766 | 168.0407 |  | 243.9807 | 505.2714 |  | 112.98 | 1 elec | 67.85 | 1.501 | 101.8428 |  | 154.9641 |  | 369.787 | 0 | 15 |  | 112.98 | Q5 | 67.85 | 2.4766 | 168.0407 |  | 256.8333 | 537.854 | 29.6205
[17 empty] | No walk-in lighting controls required required in base code | Not required | Not required | NA |  | 1 ea | Low Temperature Occupancy Sensor; Addendum AR low Temperature Occupancy Sensor for walk-in refrigerator and for walk-in freezer | Grainger Catalog (www.grainger.com) | Hubbell Wiring Device- Kellems | AHP1500CRP |  | 2 ea |  |  |  | WI_OccSnsr | 1 | 0 | NA | 0 | 0 | 0 |  | 0 | 0 | 0 | 15 |  | 0 | NA | 0 | 0 | 0 |  | 0 | 0 |  | 275 | 1 elec | 67.85 | 1.143 | 77.5525 |  | 212.7316 |  | 565.2841 | 0 | 15 |  | 275 | Q5 | 67.85 | 1.886 | 127.9617 |  | 318.6736 | 721.6353 | 565.2841
|  |  | Kitchen Exhaust | [12 empty] | Kitchen Exhaust 90.1-07ax | 90.1-07 section 6.5.7.1 includes which requires at least 50% make-up air. The make-up air units are accounted for separately from the kitchen exhaust and their costs are included under the general capacity changes above. | [5 empty] | 90.1-2010 includes multiple provisions that affect the design and exhaust volume of kitchen exhaust hoods. 1) The exhaust maximum airflow values in Table 6.5.7.1.3 are 30% below the values allowed in ASHRAE Standard 154-2003. For the savings analysis, it was assumed that many systems already meet these lower exhaust airflow requirements, and the 90.1-2010 exhaust airflow is set 10% below the value inlcuded for the 90.1-2007 models. The costs in this section are for the different airflow capacity units. 2) Transfer air from surrounding spaces on the same floor as the kitchens required to be used as the first source of exhaust makeup air. No costs are identified for this, and the assumption is that this transfer can be transferred through standards doors or other openings between the spaces. Differences in the makeup air volume for the case with the use of transfer air are accounted for under the general HVAC capacity costs.
[16 empty] | Kitchen_Exhaust | [11 empty] | 3480 | [8 empty] | 25
[17 empty] | Belt drive centrifugal upblast exhaust fan with 24 in. wheel. Nominal size of selected unit is 5,400 cfm. Primary school kitchen is the only prototype affected. | Restaurant Max Inc. online http://www.restaurant-services.com/hoods.htm RS Means 2012 23 34 16 0326 for labor. |  | BDU-24 |  | 5000 | Belt drive centrifugal upblast exhaust fan with 20.75 in. wheel. Nominal airflow of selected unit is 4,500 cfm. | Restaurant Max Inc. online http://www.restaurant-services.com/hoods.htm. RS Means 2012 23 34 16 0326 for labor. |  | BDU-20 |  | 4500 |  |  |  |  | 1 | 1392 | Q-20 | 63.97 | 26.0627 | 1667.2317 |  | 2307.4918 | 5366.7235 |  | 25 |  | 1392 | Q-20 | 63.97 | 43.0035 | 2750.9323 |  | 3906.4622 | 8049.3945 |  | 1061 | Q-20 | 48 | 26.0646 | 1251.102 |  | 1739.7956 |  | 4051.8976 | 0 | 25 |  | 1061 | Q-20 | 48 | 43.0066 | 2064.3183 |  | 2942.141 | 6067.4593 | -1314.8259
HVAC Plant - Capacity Change |  |  | General: Load Changes Plant Equipment and Piping | [12 empty] | HVAC Plant Capacity Costs | Costs used to account for changes in plant capacity due to changes in 90.1. Costs are base costs for system that meets 90.1 base case standard requirements before application of addenda. Difference in cost by capacity will be calculated in final summary sheet based on the base case and target case capacity for a particular prototype and climate zone. | [5 empty] | For central plants, there are separate costs where there are efficiency increases or changes in requirements. Difference in cost for capacity between base case and target case models is also accounted for on prototype sheets. Difference in cost by capacity will be calculated in final summary sheet based on the base and target capacity for a particular prototype and climate zone. | [51 empty] | 21% OHP contractor 10% overhead multiplied by 10% , 1st overhead for sub, 10% for labor and material
|  |  | Chillers |  | X | [10 empty] | Chillers Plant Capacity Adjustments | 90.1 base case chiller efficiency is the same as target case. Costs account for changes in chiller capacity due to other measures. Costs are for 90.1 base code efficiency chillers, Path A centrifugal. Chiller type modeled depending on base case capacity and all are centrifugal. Minimum efficiency for Path A Centrifugal. (only need up to 500 Tons). | Equipment information below. Labor from RS Means 2023 Mechanical Cost Data. RS Means Centrifugal Type Water Chillers 23 64 16.10 |  |  |  | Cooling Capacity, tons | 90.1 base case chiller efficiency is the same as target case. Costs account for changes in chiller capacity due to other measures. Costs are for 90.1 base code efficiency chillers, Path A centrifugal. Chiller type modeled depending on base case capacity and all are centrifugal. Minimum efficiency for Path A Centrifugal. (only need up to 500 Tons). |  |  |  |  | Cooling Capacity, tons |  |  |  |  | Inflation from 2012 to 2023
[16 empty] | Chillers same cost 2013/2015 | Manufacturer 1 | Brad Wagner (Airefco) (via Mike Rosenberg) |  |  |  |  | Manufacturer 1 | Brad Wagner (Airefco) | [47 empty] | 0
[28 empty] | 200 | [5 empty] | 93204.7415 | [19 empty] | 93204.7415
[16 empty] | Use inflation from 2012 to 2018 | minimum efficiency full load 0.559 kW/ton, IPLV 0.399 kW/ton* | NW Air reps | YORKTrane, Carrier or McQuay |  |  | 300 | minimum efficiency full load 0.559 kW/ton, IPLV 0.399 kW/ton* | Airefco | Carrier | 19XRV3031323CES64 |  | 300 |  |  |  |  | 1.104 | 114043.2 | [18 empty] | 100% | 114043.2 | [17 empty] | 0
[17 empty] | minimum efficiency full load 0.556 kW/ton, IPLV 0.384 kW/ton |  | Estimated for multiple |  |  | 400 | minimum efficiency full load 0.556 kW/ton, IPLV 0.384 kW/ton | Airefco | Carrier | 19XRV3132204BHH64 |  | 400 |  |  |  |  | 1.104 | 115257.6 | [18 empty] | 100% | 115257.6 | [17 empty] | 0
[17 empty] | minimum efficiency full load 0.545 kW/ton, IPLV 0.370 kW/ton |  | manufacturers |  |  | 500 | minimum efficiency full load 0.545 kW/ton, IPLV 0.370 kW/ton | Airefco | Carrier | 19XRV4140383CPS64 |  | 500 |  |  |  |  | 1.104 | 133584 | [18 empty] | 100% | 133584 | [17 empty] | 0
[17 empty] | *Full load kW/Ton near requirment. IPLV exceeds due to product availability (includes VFD). | [5 empty] | *Full load kW/Ton near requirment. IPLV exceeds due to product availability (includes VFD). | [30 empty] | 0 | [17 empty] | 0
[28 empty] | 200 | [5 empty] | 123000 | [19 empty] | 123000
[22 empty] | 300 | [5 empty] | 300 | [5 empty] | 150500 | [19 empty] | 150500 | [17 empty] | 0
[17 empty] | Means 2018: 23 64 16.10 |  |  |  |  | 400 | Means 23 64 16.10 |  |  |  |  | 400 | [5 empty] | 152000 | [19 empty] | 152000 | [17 empty] | 0
[22 empty] | 500 | [5 empty] | 500 | [5 empty] | 185500 | [19 empty] | 185500 | [17 empty] | 0
[16 empty] | Cent_WC_Chiller_Capacity | Average of two manufacturers (Path A Chillers) & Means 2018 | [5 empty] | Average of two manufacturers (Path A Chillers)
[17 empty] | minimum efficiency full load 0.560 kW/ton, IPLV 0.520 kW/ton |  |  |  |  | 200 | minimum efficiency full load 0.560 kW/ton, IPLV 0.520 kW/ton |  |  |  |  | 200 |  |  |  |  | 1.104 | 108102.3708 | Q7 | 69.05 | 231 | 15950.55 |  | 86469.5091 | 210522.4298 |  | 23 |  | 108102.3708 | Q7 | 69.05 | 381.15 | 26318.4075 |  | 117684.8492 | 252105.6274 |  | 108102.3708 | Q7 | 69.05 | 231 | 15950.55 |  | 86469.5091 |  | 210522.4298 | 0 | 23 |  | 108102.3708 | Q7 | 69.05 | 381.15 | 26318.4075 |  | 117684.8492 | 252105.6274 | 0
[17 empty] | minimum efficiency full load 0.560 kW/ton, IPLV 0.520 kW/ton |  |  |  |  | 300 | minimum efficiency full load 0.560 kW/ton, IPLV 0.520 kW/ton |  |  |  |  | 300 |  |  |  |  | 1.104 | 132271.6 | Q7 | 69.05 | 257 | 17745.85 |  | 104092.3596 | 254109.8096 |  | 23 |  | 132271.6 | Q7 | 69.05 | 424.05 | 29280.6525 |  | 140810.3361 | 302362.5886 |  | 132271.6 | Q7 | 69.05 | 257 | 17745.85 |  | 104092.3596 |  | 254109.8096 | 0 | 23 |  | 132271.6 | Q7 | 69.05 | 424.05 | 29280.6525 |  | 140810.3361 | 302362.5886 | 0
[17 empty] | minimum efficiency full load 0.560 kW/ton, IPLV 0.520 kW/ton |  |  |  |  | 400 | minimum efficiency full load 0.560 kW/ton, IPLV 0.520 kW/ton |  |  |  |  | 400 |  |  |  |  | 1.104 | 133628.8 | Q7 | 69.05 | 283 | 19541.15 |  | 106717.9605 | 259887.9105 |  | 23 |  | 133628.8 | Q7 | 69.05 | 466.95 | 32242.8975 |  | 145157.6454 | 311029.3429 |  | 133628.8 | Q7 | 69.05 | 283 | 19541.15 |  | 106717.9605 |  | 259887.9105 | 0 | 23 |  | 133628.8 | Q7 | 69.05 | 466.95 | 32242.8975 |  | 145157.6454 | 311029.3429 | 0
[17 empty] | minimum efficiency full load 0.560 kW/ton, IPLV 0.520 kW/ton |  |  |  |  | 500 | minimum efficiency full load 0.560 kW/ton, IPLV 0.520 kW/ton |  |  |  |  | 500 |  |  |  |  | 1.104 | 159542 | Q7 | 69.05 | 296 | 20438.8 |  | 124620.6746 | 304601.4746 |  | 23 |  | 159542 | Q7 | 69.05 | 488.4 | 33724.02 |  | 168103.6651 | 361369.6851 |  | 159542 | Q7 | 69.05 | 296 | 20438.8 |  | 124620.6746 |  | 304601.4746 | 0 | 23 |  | 159542 | Q7 | 69.05 | 488.4 | 33724.02 |  | 168103.6651 | 361369.6851 | 0
|  |  | Cooling Towers |  | X | [10 empty] | Cooling Towers Plant Capacity Changes | Same costs for both base case and target case, reflecting increase in efficiency requirements to 40.2 gpm/hp in 2013. There is also a difference in cost for capacity when there is a change in cooling capacity due to other measures. Difference in cost by capacity will be calculated in final summary sheet based on the base and target code capacity for a particular prototype and climate zone. | Equipment information below. Labor from RS Means 2023 Mechanical Cost Data. Forced-Draft Type Cooling Towers 23 65 13.10 25XX |  |  |  | Size of Chiller Cooling Load Served, tons | Same costs for both base case and target case, reflecting increase in efficiency requirements to 40.2 gpm/hp in 2013. There is also a difference in cost for capacity when there is a change in cooling capacity due to other measures. Difference in cost by capacity will be calculated in final summary sheet based on the base and target code capacity for a particular prototype and climate zone. |  |  |  |  | Size of Chiller Cooling Load Served, tons
[16 empty] | Plant Capacity difference | Required performance of 40.2 gpm/hp | [5 empty] | Required performance of 40.2 gpm/hp | [6 empty] | Base 2010 Cost (Mat) | Adder per ton
[17 empty] | Average cost increase of $1.00/Ton | NW Air Reps | BAC | S15E-1285-06JN |  | 233 | Average cost increase of $1.00/Ton | NW Air Reps | BAC | S1500 - various |  | 233 |  | 19264 | 1 |  |  | 19497 | [19 empty] | 19497
[17 empty] | Average cost increase of $0.66/Ton | NW Air Reps | BAC | S15E-1285-09LN |  | 354 | Average cost increase of $0.66/Ton | NW Air Reps | BAC | S1500 - various |  | 354 |  | 25934 | 0.66 |  |  | 26167.64 | [19 empty] | 26167.64
[17 empty] | Average cost increase of $1.04/Ton | NW Air Reps | BAC | S3E-8518-06M |  | 467 | Average cost increase of $1.04/Ton | NW Air Reps | BAC | S3000 - various |  | 467 |  | 31907 | 1.04 |  |  | 32392.68 | [19 empty] | 32392.68
[17 empty] | Required performance of 40.2 gpm/hp | [5 empty] | Required performance of 40.2 gpm/hp
[17 empty] | Average cost increase of $3.30/Ton | Trane Oregon | SPX | NC8401MAN1 |  | 233 | Average cost increase of $3.30/Ton | Trane Oregon | SPX | NC Steel- various |  | 233 |  | 46559 | 3.3 |  |  | 47327.9 | [19 empty] | 47327.9
[17 empty] | Average cost increase of $3.23/Ton | Trane Oregon | SPX | NC8402NAN1 |  | 354 | Average cost increase of $3.23/Ton | Trane Oregon | SPX | NC Steel- various |  | 354 |  | 61903 | 3.23 |  |  | 63046.42 | [19 empty] | 63046.42
[17 empty] | Average cost increase of $2.30/Ton | Trane Oregon | SPX | NC8407QLS1 |  | 467 | Average cost increase of $2.30/Ton | Trane Oregon | SPX | NC Steel- various |  | 467 |  | 88630 | 2.3 |  |  | 89704.1 | [19 empty] | 89704.1
[16 empty] | Cooling_Tower_Capacity | Required performance of 40.2 gpm/hp | [5 empty] | Required performance of 40.2 gpm/hp | [9 empty] | 2012 to 2023
[22 empty] | 233 | [5 empty] | 233 |  |  |  |  | 1.3839 | 33412.45 | Q7 | 69.05 | 39.216 | 2707.8648 |  | 38621.2175 | 74741.5323 |  | 20 |  | 33412.45 | Q7 | 69.05 | 64.7064 | 4467.9769 |  | 47820.7215 | 85701.1484 |  | 33412.45 | Q7 | 69.05 | 39.216 | 2707.8648 |  | 38621.2175 |  | 74741.5323 | 0 | 20 |  | 33412.45 | Q7 | 69.05 | 64.7064 | 4467.9769 |  | 47820.7215 | 85701.1484 | 0
[22 empty] | 354 | [5 empty] | 354 |  |  |  |  | 1.3839 | 44607.03 | Q7 | 69.05 | 59.259 | 4091.834 |  | 52021.222 | 100720.0859 |  | 20 |  | 44607.03 | Q7 | 69.05 | 97.7773 | 6751.526 |  | 64700.395 | 116058.951 |  | 44607.03 | Q7 | 69.05 | 59.259 | 4091.834 |  | 52021.222 |  | 100720.0859 | 0 | 20 |  | 44607.03 | Q7 | 69.05 | 97.7773 | 6751.526 |  | 64700.395 | 116058.951 | 0
[22 empty] | 467 | [5 empty] | 467 |  |  |  |  | 1.3839 | 61048.39 | Q7 | 69.05 | 100 | 6905 |  | 72455.2725 | 140408.6625 |  | 20 |  | 61048.39 | Q7 | 69.05 | 165 | 11393.25 |  | 90895.7479 | 163337.3879 |  | 61048.39 | Q7 | 69.05 | 100 | 6905 |  | 72455.2725 |  | 140408.6625 | 0 | 20 |  | 61048.39 | Q7 | 69.05 | 165 | 11393.25 |  | 90895.7479 | 163337.3879 | 0
|  |  | Boilers |  | X |  | X | [8 empty] | Boiler Capacity Adjustment | Natural gas boiler, hot water, cast iron heat exchanger. Size ranges correspond to efficiency categories in 90.1. Size <300 kBtu/h 80% AFUE 2. Size 300 kBtu/h to 2,500 kBtu/h 80% Et, size above 2,500 kBtu/h 82% Ec. Boiler capacity shown below in millions of Btu/h. | Equipment information below. Labor from RS Means 2023 Mechanical Cost Data. Gas-Fired Boilers 23 52 23.20 3020+ |  |  |  | Million Btu/h | Based on 2012 costs. Difference in cost for capacity between base code and target code. Difference in cost by capacity will be calculated in final summary sheet based on the capacity difference based on other changes affecting heating load for a particular prototype and climate zone. |  |  |  |  | Million Btu/h |  |  |  |  | 2012 to 2023 | [20 empty] | 0
Manufacturer 1
[17 empty] | 0.3 | F&G 2012 | Proctor Sales - Weil-McCain | 81% CGT-5 |  | 0.3 | [5 empty] | 0.3 |  |  |  |  | 1.314 | 4106.85 | Q7 | 69.05 | 37.778 | 2608.5709 |  | 6513.2717 | 13228.6926 |  | 35 |  | 4106.85 | Q7 | 69.05 | 62.3337 | 4304.142 |  | 9498.2253 | 17909.2173 |  | 4106.85 | Q7 | 69.05 | 37.778 | 2608.5709 |  | 6513.2717 |  | 13228.6926 |  | 35 |  | 4106.85 | Q7 | 69.05 | 62.3337 | 4304.142 |  | 9498.2253 | 17909.2173 | 0
[17 empty] | 2.5 | F&G 2012 | Proctor Sales - Weil-McCain | 82% H1688 |  | 2.5 | [5 empty] | 2.5 |  |  |  |  | 1.314 | 13987.3909 | Q7 | 69.05 | 152.1471 | 10505.7544 |  | 23748.6973 | 48241.8426 |  | 35 |  | 13987.3909 | Q7 | 69.05 | 251.0426 | 17334.4948 |  | 35266.7574 | 66588.6431 |  | 13987.3909 | Q7 | 69.05 | 152.1471 | 10505.7544 |  | 23748.6973 |  | 48241.8426 |  | 35 |  | 13987.3909 | Q7 | 69.05 | 251.0426 | 17334.4948 |  | 35266.7574 | 66588.6431 | 0
[17 empty] | 7.5 | F&G 2012 | Proctor Sales - Weil-McCain | 82% H1688 |  | 7.5 | [5 empty] | 7.5 |  |  |  |  | 1.314 | 41962.1726 | Q7 | 69.05 | 386 | 26653.3 |  | 66549.9937 | 135165.4664 |  | 35 |  | 41962.1726 | Q7 | 69.05 | 636.9 | 43977.945 |  | 97049.0316 | 182989.1493 |  | 41962.1726 | Q7 | 69.05 | 386 | 26653.3 |  | 66549.9937 |  | 135165.4664 |  | 35 |  | 41962.1726 | Q7 | 69.05 | 636.9 | 43977.945 |  | 97049.0316 | 182989.1493 | 0
[17 empty] | 15 | F&G 2012 | Proctor Sales - Hurst | fire tube |  | 15 | larger sizes not referenced in prototypes |  |  |  |  | 15 |  |  |  |  | 1.314 | 141075 | Q7 | 69.05 | 727 | 50199.35 |  | 185690.3447 | 376964.6947 |  | 35 |  | 141075 | Q7 | 69.05 | 1199.55 | 82828.9275 |  | 255371.9725 | 479275.9 |  | 141075 | Q7 | 69.05 | 727 | 50199.35 |  | 185690.3447 |  | 376964.6947 |  | 35 |  | 141075 | Q7 | 69.05 | 1199.55 | 82828.9275 |  | 255371.9725 | 479275.9 | 0
[17 empty] | 25 | F&G 2012 | Proctor Sales - Hurst | fire tube |  | 25 | larger sizes not referenced in prototypes |  |  |  |  | 25 |  |  |  |  | 1.314 | 184062.5 | Q7 | 69.05 | 1211.6667 | 83665.5833 |  | 259815.4784 | 527543.5617 |  | 35 |  | 184062.5 | Q7 | 69.05 | 1999.25 | 138048.2125 |  | 365878.4319 | 687989.1444 |  | 184062.5 | Q7 | 69.05 | 1211.6667 | 83665.5833 |  | 259815.4784 |  | 527543.5617 |  | 35 |  | 184062.5 | Q7 | 69.05 | 1999.25 | 138048.2125 |  | 365878.4319 | 687989.1444 | 0
[17 empty] | Manufacturer 2 | [27 empty] | 0
[17 empty] | 0.3 | F&G 2012 | Columbia Hydronics - Smith | 80% Et H480 |  | 0.3 | [5 empty] | 0.3 |  |  |  |  | 1.314 | 6650 | Q7 | 69.05 | 37.778 | 2608.5709 |  | 8986.9905 | 18245.5614 |  | 35 |  | 6650 | Q7 | 69.05 | 62.3337 | 4304.142 |  | 12473.631 | 23427.773 |  | 6650 | Q7 | 69.05 | 37.778 | 2608.5709 |  | 8986.9905 |  | 18245.5614 |  | 35 |  | 6650 | Q7 | 69.05 | 62.3337 | 4304.142 |  | 12473.631 | 23427.773 | 0
[17 empty] | 2.5 | F&G 2012 | Columbia Hydronics - Smith | 82% Ec H1688 |  | 2.5 | [5 empty] | 2.5 |  |  |  |  | 1.314 | 23750 | Q7 | 69.05 | 152.1471 | 10505.7544 |  | 33244.7749 | 67500.5293 |  | 35 |  | 23750 | Q7 | 69.05 | 251.0426 | 17334.4948 |  | 46688.7037 | 87773.1985 |  | 23750 | Q7 | 69.05 | 152.1471 | 10505.7544 |  | 33244.7749 |  | 67500.5293 |  | 35 |  | 23750 | Q7 | 69.05 | 251.0426 | 17334.4948 |  | 46688.7037 | 87773.1985 | 0
[17 empty] | 7.5 | F&G 2012 | Columbia Hydronics - Smith | 82% Ec H1688 |  | 7.5 | [5 empty] | 7.5 |  |  |  |  | 1.314 | 69701.087 | Q7 | 69.05 | 386 | 26653.3 |  | 93531.6007 | 189885.9877 |  | 35 |  | 69701.087 | Q7 | 69.05 | 636.9 | 43977.945 |  | 129502.6907 | 243181.7227 |  | 69701.087 | Q7 | 69.05 | 386 | 26653.3 |  | 93531.6007 |  | 189885.9877 |  | 35 |  | 69701.087 | Q7 | 69.05 | 636.9 | 43977.945 |  | 129502.6907 | 243181.7227 | 0
[17 empty] | 15 | F&G 2012 | costs not available for this size |  |  | 15 | larger sizes not referenced in prototypes |  |  |  |  | 15
[17 empty] | 25 | F&G 2012 | costs not available for this size |  |  | 25 | larger sizes not referenced in prototypes |  |  |  |  | 25
[16 empty] | Boiler_Capacity | Average costs from two manufacturers | [15 empty] | 1.314
[17 empty] | 0.3 |  |  |  |  | 0.3 | [5 empty] | 0.3 |  |  |  |  | 1.314 | 5378.425 | Q7 | 69.05 | 37.778 | 2608.5709 |  | 7750.1311 | 15737.127 |  | 35 |  | 5378.425 | Q7 | 69.05 | 62.3337 | 4304.142 |  | 10985.9282 | 20668.4951 |  | 5378.425 | Q7 | 69.05 | 37.778 | 2608.5709 |  | 7750.1311 |  | 15737.127 |  | 35 |  | 5378.425 | Q7 | 69.05 | 62.3337 | 4304.142 |  | 10985.9282 | 20668.4951 | 0
[17 empty] | 2.5 |  |  |  |  | 2.5 | [5 empty] | 2.5 |  |  |  |  | 1.314 | 18868.6954 | Q7 | 69.05 | 152.1471 | 10505.7544 |  | 28496.7361 | 57871.1859 |  | 35 |  | 18868.6954 | Q7 | 69.05 | 251.0426 | 17334.4948 |  | 40977.7306 | 77180.9208 |  | 18868.6954 | Q7 | 69.05 | 152.1471 | 10505.7544 |  | 28496.7361 |  | 57871.1859 |  | 35 |  | 18868.6954 | Q7 | 69.05 | 251.0426 | 17334.4948 |  | 40977.7306 | 77180.9208 | 0
[17 empty] | 7.5 |  |  |  |  | 7.5 | [5 empty] | 7.5 |  |  |  |  | 1.314 | 55831.6298 | Q7 | 69.05 | 386 | 26653.3 |  | 80040.7972 | 162525.727 |  | 35 |  | 55831.6298 | Q7 | 69.05 | 636.9 | 43977.945 |  | 113275.8612 | 213085.436 |  | 55831.6298 | Q7 | 69.05 | 386 | 26653.3 |  | 80040.7972 |  | 162525.727 |  | 35 |  | 55831.6298 | Q7 | 69.05 | 636.9 | 43977.945 |  | 113275.8612 | 213085.436 | 0
[17 empty] | 15 |  |  |  |  | 15 | [5 empty] | 15 |  |  |  |  | 1.314 | 141075 | Q7 | 69.05 | 727 | 50199.35 |  | 185690.3447 | 376964.6947 |  | 35 |  | 141075 | Q7 | 69.05 | 1199.55 | 82828.9275 |  | 255371.9725 | 479275.9 |  | 141075 | Q7 | 69.05 | 727 | 50199.35 |  | 185690.3447 |  | 376964.6947 |  | 35 |  | 141075 | Q7 | 69.05 | 1199.55 | 82828.9275 |  | 255371.9725 | 479275.9 | 0
[17 empty] | 25 |  |  |  |  | 25 | [5 empty] | 25 |  |  |  |  | 1.314 | 184062.5 | Q7 | 69.05 | 1211.6667 | 83665.5833 |  | 259815.4784 | 527543.5617 |  | 35 |  | 184062.5 | Q7 | 69.05 | 1999.25 | 138048.2125 |  | 365878.4319 | 687989.1444 |  | 184062.5 | Q7 | 69.05 | 1211.6667 | 83665.5833 |  | 259815.4784 |  | 527543.5617 |  | 35 |  | 184062.5 | Q7 | 69.05 | 1999.25 | 138048.2125 |  | 365878.4319 | 687989.1444 | 0
[16 empty] | SHW Runout Insulation 90.1-2013 - by | No runout insulation required in base code 90.1-2013 | RSMeans 2018 mechanical 22 07 19.1 | Mineral wool: 1" wall on 3/4" CU pipe (use 1/2" IPS) |  |  | ea 8' runout | Addendum by requires first 8' of SHW runout piping to be insulated on recirculation or heat traced SHW systems. Priced per runout. 1" fiberglas insulation assumed. | RSMeans 2018 mechanical 22 07 19.1 | Mineral wool: 1" wall on 3/4" CU pipe (use 1/2" IPS) | 35 year life used as CU piping assumed, and located in areas not subject to wear; likely same as building life. |  | ea 8' runout insulated |  |  |  | SHW_runout | 1 | 0 | NA | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 |  | 0 | NA | 0 | 0 | 0 |  | 0 | 0 |  | 13.2 | Q14 | 58.73 | 0.56 | 32.8888 |  | 38.3708 |  | 84.4596 | 0 | 35 |  | 13.2 | Q5 | 58.73 | 0.924 | 54.2665 |  | 67.7723 | 135.2388 | 84.4596
|  |  | Pumps |  | X |  | X | [8 empty] | Pumps General load impact | Pumps for chilled, condenser and heating water. Based on most common type used. Without VFD. Pump efficiency 90.9% | Equipment and Labor from RS Means 2023 Mechanical Cost Data. General Utility Pumps centrifugal, end suction, mounted on base, horizontal mounted with drip proof motor, and accessories; Assembly D3020 330 & 340 |  |  |  | Flow, GPM | No separate costs for target code. Difference in cost for capacity between base and target models is without any addenda changes. Difference in cost by capacity will be calculated in final summary sheet based on the base and target capacity for a particular prototype and climate zone. |  |  |  |  | Flow, GPM |  |  |  |  | 2020 to 2023
[16 empty] | Pump_Flow | Pumps - costs from RS Means; secondary pumps with 50-70 ft of head
[17 empty] | Means 2023 Assembly D3020 330, page 536 | Means 2023 |  |  |  | 150 | Material cost premium = |  |  |  |  | 150 |  |  |  |  | 1.433 | 15700 | Q1 | 64.85 | 77.2201 | 5007.722 |  | 22911.131 | 43618.8531 |  | 20 |  | 15700 | Q1 | 64.85 | 127.4131 | 8262.7413 |  | 30463.7505 | 54426.4918 |  | 15700 | Q1 | 64.85 | 77.2201 | 5007.722 |  | 22911.131 |  | 43618.8531 | 0 | 20 |  | 15700 | Q1 | 64.85 | 127.4131 | 8262.7413 |  | 30463.7505 | 54426.4918 | 0
[17 empty] | Includes basemounted pump, local piping, fittings, valve, strainer, expansion joints, gauges, control & electrical connection, balancing |  |  |  |  | 200 | 0% |  |  |  |  | 200 |  |  |  |  | 1.433 | 17967 | Q1 | 64.85 | 88.3205 | 5727.582 |  | 26216.2636 | 49910.8456 |  | 20 |  | 17967 | Q1 | 64.85 | 145.7288 | 9450.5104 |  | 34856.7504 | 62274.2607 |  | 17967 | Q1 | 64.85 | 88.3205 | 5727.582 |  | 26216.2636 |  | 49910.8456 | 0 | 20 |  | 17967 | Q1 | 64.85 | 145.7288 | 9450.5104 |  | 34856.7504 | 62274.2607 | 0
[18 empty] | Means 2023 |  |  |  | 300 | [5 empty] | 300 |  |  |  |  | 1.433 | 20660 | Q1 | 64.85 | 106.6602 | 6916.916 |  | 30465.1438 | 58042.0598 |  | 20 |  | 20660 | Q1 | 64.85 | 175.9894 | 11412.9114 |  | 40676.5513 | 72749.4628 |  | 20660 | Q1 | 64.85 | 106.6602 | 6916.916 |  | 30465.1438 |  | 58042.0598 | 0 | 20 |  | 20660 | Q1 | 64.85 | 175.9894 | 11412.9114 |  | 40676.5513 | 72749.4628 | 0
[18 empty] | Means 2023 |  |  |  | 1500 | [5 empty] | 1500 |  |  |  |  | 1.433 | 42491 | Q2 | 67.25 | 155.901 | 10484.3401 |  | 59044.6271 | 112019.9672 |  | 20 |  | 42491 | Q2 | 67.25 | 257.2366 | 17299.1612 |  | 76926.8553 | 136717.0165 |  | 42491 | Q2 | 67.25 | 155.901 | 10484.3401 |  | 59044.6271 |  | 112019.9672 | 0 | 20 |  | 42491 | Q2 | 67.25 | 257.2366 | 17299.1612 |  | 76926.8553 | 136717.0165 | 0
[18 empty] | Means 2023 |  |  |  | 2000 | [5 empty] | 2000 |  |  |  |  | 1.433 | 52582 | Q2 | 67.25 | 188.0119 | 12643.8012 |  | 72747.8598 | 137973.661 |  | 20 |  | 52582 | Q2 | 67.25 | 310.2197 | 20862.272 |  | 94601.3857 | 168045.6576 |  | 52582 | Q2 | 67.25 | 188.0119 | 12643.8012 |  | 72747.8598 |  | 137973.661 | 0 | 20 |  | 52582 | Q2 | 67.25 | 310.2197 | 20862.272 |  | 94601.3857 | 168045.6576 | 0
[18 empty] | Means 2023 |  |  |  | 2500 | [5 empty] | 2500 |  |  |  |  | 1.433 | 62673 | Q2 | 67.25 | 368.5778 | 24786.8578 |  | 96090.1341 | 183549.9919 |  | 20 |  | 62673 | Q2 | 67.25 | 608.1534 | 40898.3153 |  | 130238.397 | 233809.7124 |  | 62673 | Q2 | 67.25 | 368.5778 | 24786.8578 |  | 96090.1341 |  | 183549.9919 | 0 | 20 |  | 62673 | Q2 | 67.25 | 608.1534 | 40898.3153 |  | 130238.397 | 233809.7124 | 0
[18 empty] | Means 2023 |  |  |  | 3000 | [5 empty] | 3000 |  |  |  |  | 1.433 | 72764 | Q2 | 67.25 | 411.3924 | 27666.1392 |  | 110488.3447 | 210918.484 |  | 20 |  | 72764 | Q2 | 67.25 | 678.7975 | 45649.1297 |  | 149208.0279 | 267621.1576 |  | 72764 | Q2 | 67.25 | 411.3924 | 27666.1392 |  | 110488.3447 |  | 210918.484 | 0 | 20 |  | 72764 | Q2 | 67.25 | 678.7975 | 45649.1297 |  | 149208.0279 | 267621.1576 | 0
[16 empty] | Pump_FlPri | Pumps - costs from RS Means; primary pumps with 25-40 ft of head
[17 empty] | Means 2023 Assembly D3020 340, page 536 | Prorated from 225 gpm based on Means 23 21 23.13 |  |  |  | 50 | [5 empty] | 50 |  |  |  |  | 1.433 | 8175 | Q1 | 64.85 | 57.2889 | 3715.1884 |  | 12999.2771 | 24889.4655 |  | 20 |  | 8175 | Q1 | 64.85 | 94.5268 | 6130.0608 |  | 17855.4035 | 32160.4643 |  | 8175 | Q1 | 64.85 | 57.2889 | 3715.1884 |  | 12999.2771 |  | 24889.4655 | 0 | 20 |  | 8175 | Q1 | 64.85 | 94.5268 | 6130.0608 |  | 17855.4035 | 32160.4643 | 0
[17 empty] | but adjusted to smaller pump size for lower pump head required | Prorated from 225 gpm based on Means 23 21 23.13 |  |  |  | 90 | [5 empty] | 90 |  |  |  |  | 1.433 | 9000 | Q1 | 64.85 | 66.0414 | 4282.7866 |  | 14497.1523 | 27779.9389 |  | 20 |  | 9000 | Q1 | 64.85 | 108.9684 | 7066.5978 |  | 20003.9785 | 36070.5763 |  | 9000 | Q1 | 64.85 | 66.0414 | 4282.7866 |  | 14497.1523 |  | 27779.9389 | 0 | 20 |  | 9000 | Q1 | 64.85 | 108.9684 | 7066.5978 |  | 20003.9785 | 36070.5763 | 0
[18 empty] | Means 2023 |  |  |  | 225 | [5 empty] | 225 |  |  |  |  | 1.433 | 11300 | Q1 | 64.85 | 77.2201 | 5007.722 |  | 17845.1797 | 34152.9017 |  | 20 |  | 11300 | Q1 | 64.85 | 127.4131 | 8262.7413 |  | 24451.204 | 44013.9453 |  | 11300 | Q1 | 64.85 | 77.2201 | 5007.722 |  | 17845.1797 |  | 34152.9017 | 0 | 20 |  | 11300 | Q1 | 64.85 | 127.4131 | 8262.7413 |  | 24451.204 | 44013.9453 | 0
[17 empty] | Includes basemounted pump, local piping, fittings, valve, strainer, expansion joints, gauges, control & electrical connection, balancing |  |  |  |  | 350 | [5 empty] | 350 |  |  |  |  | 1.433 | 14100 | Q1 | 64.85 | 88.3205 | 5727.582 |  | 21763.9831 | 41591.5652 |  | 20 |  | 14100 | Q1 | 64.85 | 145.7288 | 9450.5104 |  | 29572.5419 | 53123.0523 |  | 14100 | Q1 | 64.85 | 88.3205 | 5727.582 |  | 21763.9831 |  | 41591.5652 | 0 | 20 |  | 14100 | Q1 | 64.85 | 145.7288 | 9450.5104 |  | 29572.5419 | 53123.0523 | 0
[18 empty] | Means 2023 |  |  |  | 1000 | [5 empty] | 1000 |  |  |  |  | 1.433 | 20900 | Q1 | 64.85 | 106.6602 | 6916.916 |  | 30741.4684 | 58558.3844 |  | 20 |  | 20900 | Q1 | 64.85 | 175.9894 | 11412.9114 |  | 41004.5084 | 73317.4198 |  | 20900 | Q1 | 64.85 | 106.6602 | 6916.916 |  | 30741.4684 |  | 58558.3844 | 0 | 20 |  | 20900 | Q1 | 64.85 | 175.9894 | 11412.9114 |  | 41004.5084 | 73317.4198 | 0
[18 empty] | Means 2023 |  |  |  | 2000 | [5 empty] | 2000 |  |  |  |  | 1.433 | 33962 | Q2 | 67.25 | 155.901 | 10484.3401 |  | 49224.741 | 93671.0811 |  | 20 |  | 33962 | Q2 | 67.25 | 257.2366 | 17299.1612 |  | 65272.0806 | 116533.2417 |  | 33962 | Q2 | 67.25 | 155.901 | 10484.3401 |  | 49224.741 |  | 93671.0811 | 0 | 20 |  | 33962 | Q2 | 67.25 | 257.2366 | 17299.1612 |  | 65272.0806 | 116533.2417 | 0
[18 empty] | Means 2023 |  |  |  | 2750 | [5 empty] | 2750 |  |  |  |  | 1.433 | 46500 | Q2 | 67.25 | 188.0119 | 12643.8012 |  | 65745.3334 | 124889.1346 |  | 20 |  | 46500 | Q2 | 67.25 | 310.2197 | 20862.272 |  | 86290.4066 | 153652.6786 |  | 46500 | Q2 | 67.25 | 188.0119 | 12643.8012 |  | 65745.3334 |  | 124889.1346 | 0 | 20 |  | 46500 | Q2 | 67.25 | 310.2197 | 20862.272 |  | 86290.4066 | 153652.6786 | 0
|  |  | Hot water piping |  | X | [10 empty] | Heating Water Piping used for load changes | Heating water piping and insulation costs are calculated from the model output flow rates for the base and target models. The estimating process was developed in 2012, so cost factors were updated using a Means comparison from 2012 to 2023. No addenda directly affect heating water piping. The differences in cost are due just to changes in capacity. Costs were developed for a range of climates to cover the range of expected loads. Regressions are based on reheat coil flow related to total piping costs. | Solarc one line diagram component analysis. |  |  |  | Reheat coil Hot water flow, gpm Not current values; prior calculated values to develop the regressions | Cost is for all heating water piping including hot water to air handlers from boiler and terminal unit reheat. Estimate cost based on whole building prototype flow at zone reheat, air handling systems and plant equipment. No addenda directly affect this cost. Cost difference occurs only for differences in heating requirements. | Solarc one line diagram component analysis. |  |  |  | Reheat coil Hot water flow, gpm Not current values; prior calculated values to develop the regressions |  |  |  |  | Note: Inflation from 2012 to 2014 included in material and labor before regression is developed; Infl from 2014 to 2023
[17 empty] | Large Office | [6 empty] | Regression coefficents below used on prototype tab
[23 empty] | Large Office |  | y = -0.7891x2 + 1089.7x - 127182+cf_HW_Mat_I*##+cf_HW_Mat_x*##^2
[17 empty] | 1B Riyadh 90.1-2010 |  |  |  |  | 530.7 | 1B Riyadh 90.1-2013 | y = -0.7891x2 + 1089.7x - 127182 |  |  |  | 486.27 |  |  |  |  | 1.817 | 233055.3302 | Q-1 | 64.85 | 3208.5998 | 208077.6973 |  | 603580.9432 | 1044713.9707 | [12 empty] | 212559.7357 | Q-1 | 64.85 | 3208.5998 | 201456.4325 |  | 561774.8987 |  | 975791.0669 | [11 empty] | -68922.9039
[17 empty] | 2A Houston 90.1-2010 |  |  |  |  | 534.42 | 2A Houston 90.1-2013 | cf_HW_Mat_I | -127182 | cf_HW_Mat_I+cf_HW_Mat_x*##+cf_HW_Mat_x2*##^2 |  | 501.11 |  |  |  |  | 1.817 | 231889.7547 | Q-1 | 64.85 | 3201.6159 | 207624.7928 |  | 601129.7307 | 1040644.2782 |  |  |  |  | Replacement values calculated on prototype tab | [7 empty] | 224336.6898 | Q-1 | 64.85 | 3201.6159 | 205188.7582 |  | 585727.2129 |  | 1015252.6609 | [5 empty] | Replacement values calculated on prototype tab | [5 empty] | -25391.6173
[17 empty] | 3B El Paso 90.1-2010 |  |  |  |  | 478.42 | 3B El Paso 90.1-2013 | cf_HW_Mat_x | 1089.7 |  |  | 481.77 |  |  |  |  | 1.817 | 210170.1133 | Q-1 | 64.85 | 3061.1732 | 198517.0798 |  | 554808.0822 | 963495.2754 | [12 empty] | 211786.4609 | Q-1 | 64.85 | 3061.1732 | 201492.1395 |  | 560473.2712 |  | 973751.8716 | [11 empty] | 10256.5962
[17 empty] | 3C San Francisco 90.1-2010 |  |  |  |  | 441.65 | 3C San Francisco 90.1-2013 | cf_HW_Mat_x2 | -0.7891 |  |  | 437.09 |  |  |  |  | 1.817 | 201371.7481 | Q-1 | 64.85 | 3016.6249 | 195628.1222 |  | 536816.5817 | 933816.452 | [12 empty] | 199674.3656 | Q-1 | 64.85 | 3016.6249 | 196570.0598 |  | 534793.1903 |  | 931037.6156 | [11 empty] | -2778.8364
[17 empty] | 5A Chicago 90.1-2010 |  |  |  |  | 601.68 | 5A Chicago 90.1-2013 | y = 102.35x + 152141 | cf_HW_Lab_I+cf_HW_Lab_x*##+cf_HW_Lab_x2*##^2 |  |  | 576.47 |  |  |  |  | 1.817 | 242628.6199 | Q-1 | 64.85 | 3342.0436 | 216731.5252 |  | 628477.3093 | 1087837.4545 | [12 empty] | 237810.675 | Q-1 | 64.85 | 3342.0436 | 212635.4103 |  | 616197.8781 |  | 1066643.9633 | [11 empty] | -21193.4911
[17 empty] | 7 Duluth 90.1-2010 |  |  |  |  | 625.46 | 7 Duluth 90.1-2013 | cf_HW_Lab_I | 152141 | cf_HW_Lab_I+cf_HW_Lab_x*##+cf_HW_Lab_x2*##^2 |  | 598.02 |  |  |  |  | 1.817 | 243258.7652 | Q-1 | 64.85 | 3299.0967 | 213946.4217 |  | 626877.1212 | 1084082.308 | [12 empty] | 242605.0423 | Q-1 | 64.85 | 3299.0967 | 215264.837 |  | 627020.501 |  | 1084890.3803 | [11 empty] | 808.0723
[17 empty] | 8 Fairbanks 90.1-2010 |  |  |  |  | 669.06 | 8 Fairbanks 90.1-2013 | cf_HW_Lab_x | 102.35 |  |  | 618.27 |  |  |  |  | 1.817 | 250198.4471 | Q-1 | 64.85 | 3343.4415 | 216822.1817 |  | 641644.3556 | 1108664.9844 | [12 empty] | 243779.5637 | Q-1 | 64.85 | 3343.4415 | 215850.3634 |  | 629615.2153 |  | 1089245.1425 | [11 empty] | -19419.8419
[24 empty] | cf_HW_Lab_x2 | 0
[17 empty] | Primary School |  |  |  |  | Reheat Coil GPM |  | Regression coefficents below used on prototype tab |  |  |  | Reheat Coil GPM |  |  |  |  | Note: Inflation from 2012 to 2014 included in material and labor before regression is developed; Infl from 2014 to 2023
[17 empty] | 1B Riyadh 90.1-2010 |  |  |  |  | 112.8054 | 1B Riyadh 90.1-2013 | y = 4.7569x2 - 768.94x + 63199 |  | cf_HW_PS_Mat_I+cf_HW_PS_Mat_x*##+cf_HW_PS_Mat_x2*##^2 |  | 98.4193 |  |  |  |  | 1.817 | 36699.6837 | Q-2 | 67.25 | 407.3796 | 27396.2781 |  | 89862.2901 | 153958.2518 | [12 empty] | 33705.6193 | Q-2 | 67.25 | 387.1648 | 26036.8346 |  | 83376.4725 |  | 143118.9263 | [11 empty] | -10839.3255
[17 empty] | 2A Houston 90.1-2010 |  |  |  |  | 102.7261 | 2A Houston 90.1-2013 | cf_HW_PS_Mat_I | 63199 | cf_HW_PS_Mat_I+cf_HW_PS_Mat_x*##+cf_HW_PS_Mat_x2*##^2 |  | 96.5647 |  |  |  |  | 1.817 | 35914.5876 | Q-2 | 67.25 | 398.5146 | 26800.1074 |  | 87930.167 | 150644.862 | [12 empty] | 33468.4137 | Q-2 | 67.25 | 386.4614 | 25989.5309 |  | 82920.946 |  | 142378.8907 | [11 empty] | -8265.9714
[17 empty] | 2B Phoenix 90.1-2010 |  |  |  |  | 109.907 | 2B Phoenix 90.1-2013 | cf_HW_PS_Mat_x | -768.94 |  |  | 96.0422 |  |  |  |  | 1.817 | 36787.6368 | Q-2 | 67.25 | 404.6589 | 27213.3088 |  | 89837.6052 | 153838.5508 |  |  |  |  | Replacement values calculated on prototype tab | [7 empty] | 33705.6193 | Q-2 | 67.25 | 387.1648 | 26036.8346 |  | 83376.4725 |  | 143118.9263 | [5 empty] | Replacement values calculated on prototype tab | [5 empty] | -10719.6245
[17 empty] | 3B El Paso 90.1-2010 |  |  |  |  | 97.518 | 3B El Paso 90.1-2013 | cf_HW_PS_Mat_x2 | 4.7569 |  |  | 86.614 |  |  |  |  | 1.817 | 32533.6186 | Q-2 | 67.25 | 392.4028 | 26389.0909 |  | 81691.5315 | 140614.241 | [12 empty] | 32360.1153 | Q-2 | 67.25 | 381.6151 | 25663.6166 |  | 80691.3073 |  | 138715.0392 | [11 empty] | -1899.2018
[17 empty] | 3C San Francisco 90.1-2010 |  |  |  |  | 95.6616 | 3C San Francisco 90.1-2013 | y = 1.546x2 - 245.21x + 35280 |  | cf_HW_PS_Lab_I+cf_HW_PS_Lab_x*##+cf_HW_PS_Lab_x2*##^2 |  | 94.7518 |  |  |  |  | 1.817 | 33468.4137 | Q-2 | 67.25 | 386.4614 | 25989.5309 |  | 82920.946 | 142378.8907 | [12 empty] | 32930.9133 | Q-2 | 67.25 | 384.8825 | 25883.3504 |  | 81889.7103 |  | 140703.974 | [11 empty] | -1674.9166
[17 empty] | 5A Chicago 90.1-2010 |  |  |  |  | 105.175 | 5A Chicago 90.1-2013 | cf_HW_PS_Lab_I | 35280 | cf_HW_PS_Lab_I+cf_HW_PS_Lab_x*##+cf_HW_PS_Lab_x2*##^2 |  | 98.303 |  |  |  |  | 1.817 | 35914.5876 | Q-2 | 67.25 | 398.5146 | 26800.1074 |  | 87930.167 | 150644.862 | [12 empty] | 33468.4137 | Q-2 | 67.25 | 386.4614 | 25989.5309 |  | 82920.946 |  | 142378.8907 | [11 empty] | -8265.9714
[17 empty] | 7 Duluth 90.1-2010 |  |  |  |  | 105.67 | 7 Duluth 90.1-2013 | cf_HW_PS_Lab_x | -245.21 |  |  | 97 |  |  |  |  | 1.817 | 33466.4836 | Q-2 | 67.25 | 390.3704 | 26252.4087 |  | 83171.4164 | 142890.3087 | [12 empty] | 32930.9133 | Q-2 | 67.25 | 384.8825 | 25883.3504 |  | 81889.7103 |  | 140703.974 | [11 empty] | -2186.3346
[17 empty] | 8 Fairbanks 90.1-2010 |  |  |  |  | 114.124 | 8 Fairbanks 90.1-2013 | cf_HW_PS_Lab_x2 | 1.546 |  |  | 101.5412 |  |  |  |  | 1.817 | 37324.0913 | Q-2 | 67.25 | 405.0957 | 27242.683 |  | 90792.878 | 155359.6523 | [12 empty] | 33468.4137 | Q-2 | 67.25 | 386.4614 | 25989.5309 |  | 82920.946 |  | 142378.8907 | [11 empty] | -12980.7616
|  |  | CHW and CW piping |  | X | [10 empty] | Chilled Water and Condenser Water Piping Includes CHW and CW Flow Rates and Pipe Sizing used for load changes | Cost is for all chilled water (CHW) and condenser water (CW) piping including water to and from air handlers from chiller and cooling tower in the mechanical penthouse. No addenda directly affect this cost as pipe sizing. Cost difference occurs only for differences in cooling requirements. Note that the 90.1-2007 standard did not include requirements for sizing pipe relative to flow and they were added in 2010. Cost for piping network was increased for 2010 relative to typical practice prior to the 2010 requirements. The prior analysis by PNNL of pipe sizing relative to flow with the 2010 requirements is used for base and target costs. The 2007 numbers in the graphs are not used. Inflation factors from 2012 to 2023 are applied where used in the prototype costs | Solarc one line diagram component analysis. | Only 2010 material values are used. |  |  | flow, gpm from chilled water secondary pump | Base and target costs are the same, and in the prototype tabs, will be adjusted for change in sizing due to the changes in capacity and flow for CHW and CW piping. | Solarc one line diagram component analysis. | Only 2010 labor values are used. |  |  | flow, gpm from chilled water secondary pump |  |  |  | 2012 to 2023 Labor inflation adjustment, applied after regression results developed in 2012 | 2012 to 2023 Material inflation adjustment, applied after regression results developed in 2012 | [31 empty] | delta on size
[18 empty] | y = 97.923x - 34003 | CF_CHW_2010_Mat_I+CF_CHW_2010_Mat_x*##+CF_CHW_2010_Mat_x2*##^2 |  |  |  |  | y = 97.923x - 34003 | CF_CHW_2013_Mat_I+CF_CHW_2013_Mat_x*##+CF_CHW_2013_Mat_x2*##^2 | [9 empty] | Values shown are calculated for 2010 | [20 empty] | Values shown are calculated for 2010
[18 empty] | CF_CHW_2010_Mat_I | -34003 | CF_CHW_2010_Mat_I+CF_CHW_2010_Mat_x*##+CF_CHW_2010_Mat_x2*##^2 |  |  |  | CF_CHW_2013_Mat_I | -34003 | [6 empty] | inf_lab_CHW | inf_mat_CHW
[17 empty] | 8 Fairbanks 90.1-2010 | CF_CHW_2010_Mat_x | 97.923 |  |  | 1235 | 8 Fairbanks 90.1-2010 | CF_CHW_2013_Mat_x | 97.923 | CF_CHW_2013_Mat_I+CF_CHW_2013_Mat_x*##+CF_CHW_2013_Mat_x2*##^2 |  | 1235 |  |  |  | 1.137 | 0.619 | 90250.9795 | Q-1 | 64.85 | 442.0519 | 28667.066 |  | 21296.9859 | 140215.0314 | [12 empty] | 90250.9795 | Q-1 | 64.85 | 442.0519 | 28667.066 |  | 21296.9859 |  | 140215.0314 |  |  | 0 | [8 empty] | 0
[17 empty] | 3B El Paso 90.1-2010 | CF_CHW_2010_Mat_x2 | 0 |  |  | 1453 | 3B El Paso 90.1-2010 | CF_CHW_2013_Mat_x2 | 0 |  |  | 1453 |  |  |  | 1.137 | 0.619 | 103807.072 | Q-1 | 64.85 | 447.169 | 28998.9095 |  | 20658.9644 | 153464.9459 | [12 empty] | 103807.072 | Q-1 | 64.85 | 447.169 | 28998.9095 |  | 20658.9644 |  | 153464.9459 |  |  | 0 | [8 empty] | 0
[17 empty] | 7 Duluth 90.1-2010 | y = 1E-05x3 - 0.0854x2 + 222.14x - 160407 | CF_CHW_2010_Lab_I+CF_CHW_2010_Lab_x*##+CF_CHW_2010_Lab_x2*##^2+CF_CHW_2010_Lab_x3*##^3 |  |  | 1497 | 7 Duluth 90.1-2010 | y = 0.0028x2 - 6.6968x + 32805 | CF_CHW_2013_Lab_I+CF_CHW_2013_Lab_x*##+CF_CHW_2013_Lab_x2*##^2 |  |  | 1497 |  |  |  | 1.137 | 0.619 | 103807.072 | Q-1 | 64.85 | 447.169 | 28998.9095 |  | 20658.9644 | 153464.9459 |  |  |  |  | Replacement values calculated on prototype tab | [7 empty] | 103807.072 | Q-1 | 64.85 | 447.169 | 28998.9095 |  | 20658.9644 |  | 153464.9459 |  |  | 0 |  |  | Replacement values calculated on prototype tab | [5 empty] | 0
[17 empty] | 5A Chicago 90.1-2010 | CF_CHW_2010_Lab_I | 32805 | CF_CHW_2010_Lab_I+CF_CHW_2010_Lab_x*##+CF_CHW_2010_Lab_x2*##^2+CF_CHW_2010_Lab_x3*##^3 |  | 1831 | 5A Chicago 90.1-2010 | CF_CHW_2013_Lab_I | 32805 | CF_CHW_2013_Lab_I+CF_CHW_2013_Lab_x*##+CF_CHW_2013_Lab_x2*##^2 |  | 1831 |  |  |  | 1.137 | 0.619 | 158739.722 | Q-1 | 64.85 | 465.4689 | 30185.6595 |  | 17921.0323 | 206846.4138 | [12 empty] | 158739.722 | Q-1 | 64.85 | 465.4689 | 30185.6595 |  | 17921.0323 |  | 206846.4138 |  |  | 0 | [8 empty] | 0
[17 empty] | 3C San Francisco 90.1-2010 | CF_CHW_2010_Lab_x | -6.6968 |  |  | 1949 | 3C San Francisco 90.1-2010 | CF_CHW_2013_Lab_x | -6.6968 |  |  | 1949 |  |  |  | 1.137 | 0.619 | 157364.722 | Q-1 | 64.85 | 464.4666 | 30120.6595 |  | 17955.4877 | 205440.8692 | [12 empty] | 157364.722 | Q-1 | 64.85 | 464.4666 | 30120.6595 |  | 17955.4877 |  | 205440.8692 |  |  | 0 | [8 empty] | 0
[17 empty] | 2A Houston 90.1-2010 | CF_CHW_2010_Lab_x2 | 0.0028 |  |  | 1982 | 2A Houston 90.1-2010 | CF_CHW_2013_Lab_x2 | 0.0028 |  |  | 1982 |  |  |  | 1.137 | 0.619 | 158739.722 | Q-1 | 64.85 | 465.4689 | 30185.6595 |  | 17921.0323 | 206846.4138 | [12 empty] | 158739.722 | Q-1 | 64.85 | 465.4689 | 30185.6595 |  | 17921.0323 |  | 206846.4138 |  |  | 0 | [8 empty] | 0
[17 empty] | 1B Riyadh 90.1-2010 | CF_CHW_2010_Lab_x3 | 0 |  |  | 2763 | 1B Riyadh 90.1-2010 |  |  |  |  | 2763 |  |  |  | 1.137 | 0.619 | 233872.759 | Q-1 | 64.85 | 547.1281 | 35481.26 |  | 17721.9836 | 287076.0026 | [12 empty] | 233872.759 | Q-1 | 64.85 | 547.1281 | 35481.26 |  | 17721.9836 |  | 287076.0026 |  |  | 0 | [8 empty] | 0
90.1-16be | [15 empty] | CRAC efficiency 90.1-16 be | CRAC baseline efficiency CRAC units are serving the IT equipment and are hard sized based on the modeled IT equipment load basement units: 6 x 20 tons, SCOP 2.5, E+ COP 3.56 | material costs from Federal Appliance Standards rulemaking TSDs Labor from 2023 Means |  |  |  | 20 tons capacity, cost is per unit | Adds CRAC efficiency requirements CRAC units are serving the IT equipment and are hard sized based on the modeled IT equipment load basement units: 6 x 20 tons, SCOP 2.73, E+ COP 3.88 | material costs from Federal Appliance Standards rulemaking TSDs Labor from 2023 Means |  |  |  | 20 tons capacity, cost is per unit |  |  |  |  | 1 | 45178 |  |  |  | 3675 |  | 26195.5745 | 75048.5745 |  | 20 |  | 45178 |  |  |  | 6063.75 |  | 36042.0053 | 87283.7553 |  | 59962 |  |  |  | 3675 |  | 33606.6873 |  | 97243.6873 |  | 20 |  | 59962 |  |  |  | 6063.75 |  | 45672.6293 | 111698.3793 | 22195.1128
[17 empty] | other 12 units: 2.5 tons, SCOP 2.6, E+ COP 3.70 |  |  |  |  | 2.5 tons capacity, cost is per unit | other 12 units: 2.5 tons, SCOP 2.82, E+ COP 4.01 |  |  |  |  | 2.5 tons capacity, cost is per unit |  |  |  |  | 1 | 21974 |  |  |  | 1350 |  | 12318.8168 | 35642.8168 |  | 20 |  | 21974 |  |  |  | 2227.5 |  | 16743.2682 | 40944.7682 |  | 18421 |  |  |  | 1350 |  | 10537.7235 |  | 30308.7235 |  | 20 |  | 18421 |  |  |  | 2227.5 |  | 14428.7656 | 35077.2656 | -5334.0933
90.1-16bq | [15 empty] | Dry_Cooler | 90.1-16bq Dry cooler baseline efficiency Dry coolers are serving the IT equipment and are hard sized based on the modeled IT equipment load | Manufacturer on 90.1 committee estimates baseline material cost is 4% cheaper |  |  |  | 50 tons capacity | 90.1-16bq Adds dry cooler efficiency requirements Dry coolers are serving the IT equipment and are hard sized based on the modeled IT equipment load | Means 2023 Mechanical 23.65.33 Liquid Coolers |  |  |  | 50 tons capacity |  |  |  |  | 1 | 35040 | Q-6 | 67.72 | 12 | 812.64 | 0 | 18349.8939 | 54202.5339 | 0 | 20 |  | 35040 | Q-6 | 67.72 | 19.8 | 1340.856 | 0 | 24287.9312 | 60668.7872 |  | 36500 | Q-6 | 67.72 | 12 | 812.64 | 0 | 19081.7814 |  | 56394.4214 |  | 20 |  | 36500 | Q5 | 67.72 | 19.8 | 1340.856 | 0 | 25239.0075 | 63079.8635 | 2191.8875
90.1-07af and 90.1-07cc | 6. HVAC | 6.5.4.5 and Table 6.5.4.5 | CHW, CW flow rates and pipe sizing |  | X | [10 empty] | CHW and CW Flow Rates and Pipe Sizing 90.1-07n and 90.1-07ca Note: Item includes no added cost in this section. Pipe sizing in general plant capacity section above includes the difference in pipe sizing between the two versions of 90.1. | 90.1 2007 does not include requirements for pipe sizing relative to design flow for chilled and condenser water piping. The baseline costs are based on an estimated typical design relationship between flow and pipe sizing which was developed for the savings analysis for 90.1-2010. | Solarc one line diagram component analysis. See Large Office HVAC example, and other worksheets |  |  |  |  | These addenda introduce pipe size requirements for different levels of chilled and condenser water flows. This applies only in the critical circuit (circuit with highest pressure drop). W174 90.1-2010 includes pipe sizing minimums relative to flow requirements. This cost estimate accounts for two changes between the 2007 and 2010 cases. 1. Change due to change in capacity and flow in the CHW and CW above under the costs associated with the change in plant capacity, using the typical practice baseline relationship between flow and pipe sizing. This isolated the capacity change related cost difference. This incremental cost will be included above on the general capacity change cost. 2. Change of cost due to change in the relationship of pipe size to flow due to addenda af/cc. This is the incremental cost between the pipe sizing for the 2010 case with the typical 2007 baseline pipe size to flow relationship, and the 2010 pipe size to flow relationship. This isolates the cost impact of the addendum. This incremental cost will be included below in this section. | [9 empty] | 1
90.1-07ak | 90.1-07ak | 6. HVAC | 6.5.4.1 | [12 empty] | Pump Differential Pressure Reset Control 90.1-07ak | Pumps are usually controlled with differential pressure control. The pressure setpoint is fixed over time after being set initially. No base cost. Individual pumps serving variable flow pumping systems with pump head exceeding 100 ft. and motor larger than 50 hp shall have controls such as VFD. VFD costs are calculated from the general load change listed VFD costs above and applied to the corresponding prototypes in the "HVAC Prototype Name" cost worksheets. . | [5 empty] | This addenda has a number of requirements that affect flow control in pumping systems for the 2010 case, primarily for chilled water pumping. Two items affect costs for the large office prototype, 1) VFDs for CHW pumps, and 2) differential pressure reset control. Differential pressure reset control means that the pumping system resets the pressure setpoint downward based on valve positions until one valve is nearly wide open. The 2007 case includes the CHW pump riding the curve providing variable flow but without a VFD and a constant differential pressure. Individual pumps serving variable flow pumping systems with motor larger than 5 hp shall have controls such as VFD. VFD costs are calculated from the general load change listed VFD costs above. | [9 empty] | 1
[16 empty] | Pump_Pressure_Control | [16 empty] | 1 | [38 empty] | 0
[23 empty] | 2 hours of programming and 2 hours of commissioning | Solarc | [8 empty] | 1 | [21 empty] | programming | 125 | 2 | 250 |  | 241.372 | 250 | 741.372 |  |  |  | 0 |  |  |  | 0 |  | 0 | 0 | 741.372
90.1-07u | 6. HVAC | 6.5.5.3, Table 6.8.1G | Cooling tower efficiency |  | X | [9 empty] | Only need to validate two assumptions and provide cost if the assumptions are incorrect. : 1. Designers will go to axial to meet more stringent efficiency requirements. 2. Cost of axial cooling tower is less than or equal to centrifugal cooling tower same cooling capacity | Cooling Tower Efficiency 90.1-07u No added costs for this item. See descriptions. | Table 6.8.1G set minimum performance for propeller or axial fan cooling towers to 38.2 gpm per gallon. No costs shown here – see comments under 90.1-2010. | [5 empty] | This addendum increases the minimum efficiency of centrifugal fan cooling towers to 38.2 gallons/hp from 20 gpm per horsepower. This is the same efficiency required of axial fan cooling towers. According to members of the 90.1 mechanical committee the incremental cost of the change in 2010 efficiency requirement for cooling towers is negligible or a net savings, since projects will use axial fan cooling towers which will require about half the fan power, and therefore be about the same or lower cost as an equivalent capacity centrifugal fan cooling tower. Centrifugal cooling towers will continue to be used when needed for noise control, space limitations, etc. and in these cases are exempt from the higher efficiency requirements. This was confirmed by our cost estimating consultant | [9 empty] | 1 | [38 empty] | 0
90.1-07m | 6. HVAC | Table 6.8.1C | Chiller efficiency |  | X | [10 empty] | Chiller Efficiency 90.1-07m | 90.1-2007 code efficiency chillers, centrifugal. No cost shown here; accounted for under general plant capacity section above. | [5 empty] | Higher efficiency water cooled centrifugal chillers for 2010 standard. Per the Manufacture Representative, prior to (2009) 90.1 2007 implementation the chillers for that time period met the 2007 efficiencies. When 90.1 2010 went into effect, to meet the new standards VFD's were then incorporated into the chiller design. Models are based on centrifugal chillers meeting Path B efficiency. minimum 90.1-2010 Path B efficiency 0.639 kW/ton, IPLV 0.450 kWh/ton, 2010 efficiency for 150 tons to 300 tons. minimum 90.1-2010 Path B efficiency 0.600 kW/ton, IPLV 0.400 kWh/ton, 2010 efficiency for 300 tons to 600 tons Costs shown are incremental cost for chillers that meet Path B efficiency versus the 90.1-2007 efficiency requirements |  |  |  |  | Cooling Capacity |  |  |  |  | 1
[16 empty] | Cent_WC_Chiller_2010_eff | [16 empty] | 1
[24 empty] | Faithful+Gould with | Carrier | IPLV .468kW/ton 30XW |  | 200 |  |  |  |  | 1 | [20 empty] | 75000 | Labor same as for chiller with 90.1-2007 efficiency |  |  |  |  | 37596.96 | 0 | 112596.96 |  |  |  | 75000 | Q7 |  | 0 | 0 |  | 48856.656 | 123856.656 | 112596.96
[24 empty] | Aerco | Carrier | IPLV .468kW/ton 30XW |  | 299 |  | Are these |  |  | 1 | [20 empty] | 105000 | [5 empty] | 52635.744 | 0 | 157635.744 |  |  |  | 105000 | Q7 |  | 0 | 0 |  | 68399.3184 | 173399.3184 | 157635.744
[25 empty] | Carrier | IPLV .299kW/ton 23XRV |  | 300 |  | sizes |  |  | 1 | [20 empty] | 110000 | [5 empty] | 55142.208 | 0 | 165142.208 |  |  |  | 110000 | Q7 |  | 0 | 0 |  | 71656.4288 | 181656.4288 | 165142.208
[25 empty] | Carrier (pro rated- 450T) | IPLV .299kW/ton 23XRV |  | 400 |  | used? |  |  | 1 | [20 empty] | 133300 | [5 empty] | 66822.3302 | 0 | 200122.3302 |  |  |  | 133300 | Q7 |  | 0 | 0 |  | 86834.5633 | 220134.5633 | 200122.3302
[25 empty] | Carrier (pro rated- 600T) | IPLV .299kW/ton 23XRV |  | 500 |  |  |  |  | 1 | [20 empty] | 162500 | [5 empty] | 81460.08 | 0 | 243960.08 |  |  |  | 162500 | Q7 |  | 0 | 0 |  | 105856.088 | 268356.088 | 243960.08
90.1-07-aj | 8. Power | 10.4.1, Tables 10.8A-C | Motor efficiency | X | X | X | X | X | X | X | X | X | X | X | X | Motor Efficiency 90.1-07aj | Fan and pump motors that just meet 90.1-2007 efficiency standards shown in 90.1-2007 Table 10.8 and under other parameters in this table. Totally enclosed, 1800 rpm motors selected for pricing. Motor HP shown under 90.1-2007 cost parameter. | Equipment information below. Labor from RS Means 2012 Electrical Cost Data, motors, 26 71 13.20 1800 rpm , totally enclosed |  | 2007 Efficiency |  | Power, HP | Fan and pump motors that just meet 90.1-2010 efficiency standards shown in 90.1-2010 Table 10.8b and in other parameters in this section. Totally enclosed, 1800 rpm motors selected for pricing. Motor HP shown under 90.1-2007 Cost Parameter. |  | type | Premium Eff. Super-E 90.1 2010 efficiency |  | Power, HP
Motor_Efficiency
[20 empty] | 82.5 |  | 1 |  | Baldor*Reliance | TEFC | 85.5 |  | 1 |  |  |  |  | 1 | 793.25 | R-1A | 60.63 | 6.132 | 371.7832 |  | 756.6027 | 1921.6359 |  | 18 |  | 793.25 | R-1A | 60.63 | 10.1178 | 613.4422 |  | 1185.6527 | 2592.3449 |  | 835 | R-1A | 60.63 | 6.132 | 371.7832 |  | 777.5317 | 0 | 1984.3148 |  | 18 |  | 835 | R-1A | 60.63 | 10.1178 | 613.4422 |  | 1212.8495 | 2661.2918 | 62.679
[17 empty] | The Energy Independence and Security Act of 2007 (EISA) set the new efficiency requirements that are now in 90.1-2010. The cost difference for the cost-effectiveness analysis is based on the change in efficiency requirements when incorporated in 90.1. There is no current impact for the change, as motors are already meeting the Federal requirement. Motors compliant with 90.1-2007 efficiency requirement prior to requirements of EISA are estimated to be 5% less expensive than the EPACT 2005 90.1-2010 compliant motors. Quotes are for 90.1-2010 motors. | Faithful+Gould, conversation with Baldor representative. The impact when the Federal change went into effect was estimated to be about a 5% increase in price according to discussion with a Baldor representative. This was due to some increase in materials, copper, and to ramping up production of the premium efficiency motors they were already making. Cost estimate reflects a 5% discount from the current prices. |  | 84 |  | 1.5 | Because Baldor Manufacturing was producing Premium Eff Motors, (which meet the 90.1 2007 requirements) before FY 2008, there was no impact to meet 90.1 2007 eff ratings. Instituting that regulation required the public to only purchase Premium Eff. Motors. Labor from RS Means 2012 | " | TEFC | 86.5 |  | 1.5 |  |  |  |  | 1 | 831.25 | R-1A | 60.63 | 6.132 | 371.7832 |  | 775.6518 | 1978.685 |  | 18 |  | 831.25 | R-1A | 60.63 | 10.1178 | 613.4422 |  | 1210.4067 | 2655.0989 |  | 875 | R-1A | 60.63 | 6.132 | 371.7832 |  | 797.5834 | 0 | 2044.3665 |  | 18 |  | 875 | R-1A | 60.63 | 10.1178 | 613.4422 |  | 1238.9064 | 2727.3486 | 65.6816
[20 empty] | 84 |  | 2 |  | " | TEFC | 86.5 |  | 2 |  |  |  |  | 1 | 943.35 | R-1A | 60.63 | 6.475 | 392.5793 |  | 851.9251 | 2187.8544 |  | 18 |  | 943.35 | R-1A | 60.63 | 10.6837 | 647.7558 |  | 1320.8474 | 2911.9532 |  | 993 | R-1A | 60.63 | 6.475 | 392.5793 |  | 876.8143 | 0 | 2262.3936 |  | 18 |  | 993 | R-1A | 60.63 | 10.6837 | 647.7558 |  | 1353.1906 | 2993.9463 | 74.5392
[20 empty] | 86.5 |  | 3 |  | " | TEFC | 89.5 |  | 3 |  |  |  |  | 1 | 965.2 | R-1A | 60.63 | 6.475 | 392.5793 |  | 862.8784 | 2220.6576 |  | 18 |  | 965.2 | R-1A | 60.63 | 10.6837 | 647.7558 |  | 1335.081 | 2948.0368 |  | 1016 | R-1A | 60.63 | 6.475 | 392.5793 |  | 888.344 | 0 | 2296.9233 |  | 18 |  | 1016 | R-1A | 60.63 | 10.6837 | 647.7558 |  | 1368.1733 | 3031.929 | 76.2657
[20 empty] | 87.5 |  | 5 |  | " | TEFC | 89.5 |  | 5 |  |  |  |  | 1 | 1259.7 | R-1A | 60.63 | 6.475 | 392.5793 |  | 1010.5091 | 2662.7883 |  | 18 |  | 1259.7 | R-1A | 60.63 | 10.6837 | 647.7558 |  | 1526.9248 | 3434.3806 |  | 1326 | R-1A | 60.63 | 6.475 | 392.5793 |  | 1043.7448 | 0 | 2762.3241 |  | 18 |  | 1326 | R-1A | 60.63 | 10.6837 | 647.7558 |  | 1570.1141 | 3543.8699 | 99.5357
[20 empty] | 88.5 |  | 7.5 |  | " | TEFC | 91 |  | 7.5 |  |  |  |  | 1 | 1412.65 | R-1A | 60.63 | 6.825 | 413.7998 |  | 1107.67 | 2934.1197 |  | 18 |  | 1412.65 | R-1A | 60.63 | 11.2613 | 682.7696 |  | 1664.7397 | 3760.1593 |  | 1487 | R-1A | 60.63 | 6.825 | 413.7998 |  | 1144.9411 | 0 | 3045.7408 |  | 18 |  | 1487 | R-1A | 60.63 | 11.2613 | 682.7696 |  | 1713.173 | 3882.9426 | 111.6211
[20 empty] | 89.5 |  | 10 |  | " | TEFC | 91.7 |  | 10 |  |  |  |  | 1 | 1935.15 | R-1A | 60.63 | 8.876 | 538.1519 |  | 1489.6559 | 3962.9578 |  | 18 |  | 1935.15 | R-1A | 60.63 | 14.6454 | 887.9506 |  | 2228.8421 | 5051.9427 |  | 2037 | R-1A | 60.63 | 8.876 | 538.1519 |  | 1540.7126 | 0 | 4115.8645 |  | 18 |  | 2037 | R-1A | 60.63 | 14.6454 | 887.9506 |  | 2295.1894 | 5220.14 | 152.9067
[20 empty] | 91 |  | 15 |  | " | TEFC | 93 |  | 15 |  |  |  |  | 1 | 2346.5 | R-1A | 60.63 | 9.576 | 580.5929 |  | 1736.839 | 4663.9319 |  | 18 |  | 2346.5 | R-1A | 60.63 | 15.8004 | 957.9783 |  | 2573.1644 | 5877.6426 |  | 2470 | R-1A | 60.63 | 9.576 | 580.5929 |  | 1798.7487 | 0 | 4849.3416 |  | 18 |  | 2470 | R-1A | 60.63 | 15.8004 | 957.9783 |  | 2653.615 | 6081.5933 | 185.4097
[20 empty] | 91 |  | 20 |  | " | TEFC | 93 |  | 20 |  |  |  |  | 1 | 3134.05 | R-1A | 60.63 | 10.276 | 623.0339 |  | 2172.6084 | 5929.6923 |  | 18 |  | 3134.05 | R-1A | 60.63 | 16.9554 | 1028.0059 |  | 3162.5517 | 7324.6076 |  | 3299 | R-1A | 60.63 | 10.276 | 623.0339 |  | 2255.2967 | 0 | 6177.3306 |  | 18 |  | 3299 | R-1A | 60.63 | 16.9554 | 1028.0059 |  | 3270.0037 | 7597.0097 | 247.6382
[20 empty] | 91.7 |  | 25 |  | " | TEFC | 93.6 |  | 25 |  |  |  |  | 1 | 3648.95 | R-1A | 60.63 | 10.5 | 636.615 |  | 2443.8365 | 6729.4015 |  | 18 |  | 3648.95 | R-1A | 60.63 | 17.325 | 1050.4147 |  | 3522.4041 | 8221.7688 |  | 3841 | R-1A | 60.63 | 10.5 | 636.615 |  | 2540.1098 | 0 | 7017.7248 |  | 18 |  | 3841 | R-1A | 60.63 | 17.325 | 1050.4147 |  | 3647.5097 | 8538.9244 | 288.3233
[20 empty] | 92.4 |  | 30 |  | " | TEFC | 94.1 |  | 30 |  |  |  |  | 1 | 4864.95 | R-1A | 60.63 | 12.775 | 774.5483 |  | 3186.5814 | 8826.0797 |  | 18 |  | 4864.95 | R-1A | 60.63 | 21.0787 | 1278.0046 |  | 4562.7027 | 10705.6574 |  | 5121 | R-1A | 60.63 | 12.775 | 774.5483 |  | 3314.9375 | 0 | 9210.4857 |  | 18 |  | 5121 | R-1A | 60.63 | 21.0787 | 1278.0046 |  | 4729.4994 | 11128.504 | 384.406
[20 empty] | 93 |  | 40 |  | " | TEFC | 94.1 |  | 40 |  |  |  |  | 1 | 5308.6 | R-1A | 60.63 | 14.525 | 880.6508 |  | 3511.4207 | 9700.6714 |  | 18 |  | 5308.6 | R-1A | 60.63 | 23.9662 | 1453.0737 |  | 5042.6057 | 11804.2795 |  | 5588 | R-1A | 60.63 | 14.525 | 880.6508 |  | 3651.4819 | 0 | 10120.1326 |  | 18 |  | 5588 | R-1A | 60.63 | 23.9662 | 1453.0737 |  | 5224.6131 | 12265.6868 | 419.4612
[20 empty] | 93 |  | 50 |  | " | TEFC | 94.5 |  | 50 |  |  |  |  | 1 | 7653.2 | R-1A | 60.63 | 16.275 | 986.7532 |  | 4789.1925 | 13429.1457 |  | 18 |  | 7653.2 | R-1A | 60.63 | 26.8538 | 1628.1429 |  | 6760.8295 | 16042.1724 |  | 8056 | R-1A | 60.63 | 16.275 | 986.7532 |  | 4991.1132 | 0 | 14033.8665 |  | 18 |  | 8056 | R-1A | 60.63 | 26.8538 | 1628.1429 |  | 7023.2223 | 16707.3652 | 604.7207
[20 empty] | 93.6 |  | 60 |  | " | TEFC | 95 |  | 60 |  |  |  |  | 1 | 8958.5 | R-1A | 60.63 | 18.9 | 1145.907 |  | 5597.191 | 15701.598 |  | 18 |  | 8958.5 | R-1A | 60.63 | 31.185 | 1890.7466 |  | 7897.4801 | 18746.7267 |  | 9430 | R-1A | 60.63 | 18.9 | 1145.907 |  | 5833.5506 | 0 | 16409.4576 |  | 18 |  | 9430 | R-1A | 60.63 | 31.185 | 1890.7466 |  | 8204.6256 | 19525.3722 | 707.8596
[20 empty] | 94.1 |  | 75 |  | " | TEFC | 95 |  | 75 |  |  |  |  | 1 | 10850.9 | R3 | 67.34 | 23.45 | 1579.123 |  | 6964.1024 | 19394.1254 |  | 18 |  | 10850.9 | R3 | 67.34 | 38.6925 | 2605.5529 |  | 9909.6733 | 23366.1263 |  | 11422 | R3 | 67.34 | 23.45 | 1579.123 |  | 7250.3907 | 0 | 20251.5137 |  | 18 |  | 11422 | R3 | 67.34 | 38.6925 | 2605.5529 |  | 10281.7005 | 24309.2534 | 857.3883
90.1-07ak | 90.1-07ak | 6. HVAC | 6.5.4.1 | [12 empty] | ECM Motors 90.1-10aj | For Stand Alone Retail, for 90.1-2010 a programmable thermostat or thermostat with a timed lockout are adequate to meet the vestibule heating control requirements. | [5 empty] | Adding an outside air lockout will not add any additional complexity if there is a DDC system in place. Otherwise, the required control can be obtained with a series outside air lockout combined with electro-mechanical controls. A setpoint limit or locking cover is also required. | [5 empty] | HP | Shaft W
[16 empty] | ECM_Motor_1/12 | Shaded Pole | Grainger |  |  |  |  | ECM motor actullly 1/10 HP | Grainger | No labor as this comes integrated into a product |  | 0.58378 |  | 0.083333 | 62.1417 |  | ECM_Motor_1/12 | 1 | 216 | 1 Elec | 67.85 | 0 | 0 |  | 108.2792 | 324.2792 |  | 15 |  | 216 | 1 Elec | 67.85 | 0 | 0 |  | 140.7072 | 356.7072 |  | 370 | 1 Elec | 67.85 | 0 | 0 |  | 185.4783 |  | 555.4783 | 0 | 15 |  | 370 | 1 Elec | 67.85 | 0 | 0 |  | 241.0262 | 611.0262 | 231.1991
[16 empty] | ECM_Motor_1/3 | Shaded Pole | Grainger |  |  |  |  | ECM motor | Grainger |  |  | 0.62326 |  | 0.33333 | 248.5667 |  | ECM_Motor_1/3 | 1 | 201 | 1 Elec | 67.85 | 0 | 0 |  | 100.7599 | 301.7599 |  | 15 |  | 201 | 1 Elec | 67.85 | 0 | 0 |  | 130.9358 | 331.9358 |  | 322.5 | 1 Elec | 67.85 | 0 | 0 |  | 161.6669 |  | 484.1669 | 0 | 15 |  | 322.5 | 1 Elec | 67.85 | 0 | 0 |  | 210.0836 | 532.5836 | 182.4071
[16 empty] | ECM_Motor_1/2 | PSC | Grainger | Marathon OEM 048A11O1062 |  |  |  | ECM motor | Grainger |  |  | 0.60352 |  | 0.5 | 372.85 |  | ECM_Motor_1/2 | 1 | 213 | 1 Elec | 67.85 | 0 | 0 |  | 106.7754 | 319.7754 |  | 15 |  | 213 | 1 Elec | 67.85 | 0 | 0 |  | 138.7529 | 351.7529 |  | 387.5 | 1 Elec | 67.85 | 0 | 0 |  | 194.251 |  | 581.751 | 0 | 15 |  | 387.5 | 1 Elec | 67.85 | 0 | 0 |  | 252.4261 | 639.9261 | 261.9756
[16 empty] | ECM_Motor_3/4 | PSC | Grainger | Marathon OEM 048A110697 |  |  |  | ECM motor | Grainger |  |  | 0.60352 |  | 0.75 | 559.275 |  | ECM_Motor_3/4 | 1 | 220.75 | 1 Elec | 67.85 | 0 | 0 |  | 110.6604 | 331.4104 |  | 15 |  | 220.75 | 1 Elec | 67.85 | 0 | 0 |  | 143.8014 | 364.5514 |  | 404.75 | 1 Elec | 67.85 | 0 | 0 |  | 202.8983 |  | 607.6483 | 0 | 15 |  | 404.75 | 1 Elec | 67.85 | 0 | 0 |  | 263.6631 | 668.4131 | 276.2379
[16 empty] | ECM_Motor_1 | PSC | Grainger | Century OLE1106H |  |  |  | ECM motor | Grainger |  |  | 0.60352 |  | 1 | 745.7 |  | ECM_Motor_1 | 1 | 386 | 1 Elec | 67.85 | 0 | 0 |  | 193.499 | 579.499 |  | 15 |  | 386 | 1 Elec | 67.85 | 0 | 0 |  | 251.4489 | 637.4489 |  | 518 | 1 Elec | 67.85 | 0 | 0 |  | 259.6697 |  | 777.6697 | 0 | 15 |  | 518 | 1 Elec | 67.85 | 0 | 0 |  | 337.4366 | 855.4366 | 198.1706
90.1-07ak | 90.1-07ak | 6. HVAC | 6.5.4.1 | [12 empty] | Vestibule Controls 90.1-10ca | For Stand Alone Retail, for 90.1-2010 a programmable thermostat or thermostat with a timed lockout are adequate to meet the vestibule heating control requirements. | [5 empty] | Adding an outside air lockout will not add any additional complexity if there is a DDC system in place. Otherwise, the required control can be obtained with a series outside air lockout combined with electro-mechanical controls. A setpoint limit or locking cover is also required.
[16 empty] | Vestibule_Control | Heating thermostat | 2014 Means Mechanical 23 09 53.10 |  |  |  |  | Heating thermostat with outside air lockout and wiring; locking thermostat cover | 2014 Means Mechanical 23 09 53.10 | [7 empty] | Vestibule_Control | 1 | 158 | 1 Elec | 67.85 | 1 | 67.85 |  | 144.7126 | 370.5626 |  | 15 |  | 158 | 1 Elec | 67.85 | 1.65 | 111.9525 |  | 225.0004 | 494.9529 |  | 231.3 | 1 Elec | 67.85 | 2 | 135.7 |  | 246.9657 |  | 613.9657 | 0 | 15 |  | 231.3 | 1 Elec | 67.85 | 1.65 | 111.9525 |  | 272.7496 | 616.0021 | 243.4031
0
90.1-07ak | 90.1-07ak | 6. HVAC | 6.5.4.1 | [12 empty] | Optimum Start Controls & DDC 90.1-10aa 90.1-10cb | For most building prototypes, DDC controls were generally required to meet the control requirements. For Stand Alone Retail, for 90.1-2010 programmable thermostats are adequate to meet the control requirements. | [5 empty] | For most building prototypes, the increased requirements for optimum start control will not add any additional complexity if there is a DDC system in place. For Stand Alone Retail, Addendum 90.1-10aa requires DDC control of the units. While it is not appropriate to include the entire front end cost of a DDC system for the optimum start addenda, the difference in unit controls is captured. For 90.1-2013 DDC zone controllers are used for each package unit to meet the control requirements.
[16 empty] | Optimum_Start_Control | Programmable thermostat | 2014 Means Mechanical 23 09 53.10 |  |  |  |  | Zone controller adapted to unitary system | 2014 Means Mechanical 23 09 23.10 | [7 empty] | Optimum_Start_Control | 1 | 249 | 1 Elec | 67.85 | 1 | 67.85 |  | 190.3303 | 507.1803 |  | 15 |  | 249 | 1 Elec | 67.85 | 1.65 | 111.9525 |  | 284.2798 | 645.2323 |  | 660 | 1 Elec | 67.85 | 1.1054 | 75 |  | 403.2648 |  | 1138.2648 | 0 | 15 |  | 660 | 1 Elec | 67.85 | 1.65 | 111.9525 |  | 552.0143 | 1323.9668 | 631.0846
90.1-07ak | 90.1-07ak | 6. HVAC | 6.5.4.1 | [12 empty] | Door Switch Control 90.1-10ba | No requirements for door control; programmable thermostat required | [5 empty] | Add door switch. The control requirements are very similar to typical occupancy sensor controlled thermostats and the cost of a door switch (Kele) was found to be quite similar to a door switch. | PECI, and Taylor Engineering. “Light Commercial Unitary HVAC, 2013 California Building Energy Efficiency Standards, CODES AND STANDARDS ENHANCEMENT INITIATIVE (CASE).” California Utilities Statewide Codes and Standards Team for California Energy Commission, November 2011. http://www.energy.ca.gov/title24/2013standards/prerulemaking/documents/current/Reports/Nonresidential/HVAC/2013_CASE_NR_Light_Commercial_Unitary_UPDATED_Nov_2011.pdf. | Multiple | [7 empty] | Inflation adjustment only for target code
[16 empty] | Door_Switch_Control | Standard Programmable thermostat | [5 empty] | Adaptive programmable thermostat with door switch | [8 empty] | Door_Switch_Control | 1.0462 | 249 | 1 Elec | 67.85 | 1 | 67.85 |  | 190.3303 | 507.1803 |  | 15 |  | 249 | 1 Elec | 67.85 | 1.65 | 111.9525 |  | 303.285 | 664.2375 |  | 358 | 1 Elec | 67.85 | 1.5 | 101.775 |  | 302.5661 |  | 762.3411 | 0 | 15 |  | 358 | 1 Elec | 67.85 | 1.65 | 111.9525 |  | 382.6096 | 852.5621 | 255.1608
90.1-10as
[16 empty] | Humidifier_Insulation | Humidifier injector array, uninsulated |  | Dri-STEEM |  |  |  | Humidifier injector array, with insulation | [8 empty] | Humidifier_Insulation | 1 | 3300 | Q-14 | 58.73 | 4 | 234.92 |  | 1881.0787 | 5415.9987 |  | 15 |  | 3300 | Q-14 | 58.73 | 6.6 | 387.618 |  | 2572.3608 | 6259.9788 |  | 5300 | Q-14 | 58.73 | 4.5 | 264.285 |  | 2912.0158 |  | 8476.3008 | 0 | 15 |  | 5300 | Q-14 | 58.73 | 6.6 | 387.618 |  | 3875.205 | 9562.823 | 3060.3022
Note on R3: Reid Hart: Recommend not changing the range name extensions at right, even though they do not match the current cycle. 2007 is the base code and 2010 is the target code.

## Adm_dd_Pump_VFD (hidden)
Chilled-Water Pumps in
These Climate Zones
Heating Water Pumps in
These Climate Zones Motor Nameplate Horsepower
0A, 0B, 1A, 1B, 2B NR 2 hp
2A, 3B NR 3 hp
3A, 3C, 4A, 4B 7, 8 5 hp
4C, 5A, 5B, 5C, 6A, 6B 3C, 5A, 5C, 6A, 6B 7.5 hp
4A, 4C, 5B 10 hp
7, 8 4B 15 hp
2A, 2B, 3A, 3B 25 hp
1B 100 hp
0A, 0B, 1A 200 hp
|  |  | 1.1 | 1.1
| Pump Motor Size |  | Theoretical HP
| CHW | HW | CHW | HW
0A | 2 | 200 | 1.8182 | 181.8182
0B | 2 | 200 | 1.8182 | 181.8182
1A | 2 | 200 | 1.8182 | 181.8182
1B | 2 | 100 | 1.8182 | 90.9091
2A | 3 | 25 | 2.7273 | 22.7273
2B | 2 | 25 | 1.8182 | 22.7273
3A | 5 | 25 | 4.5455 | 22.7273
3B | 3 | 25 | 2.7273 | 22.7273
3C | 5 | 7.5 | 4.5455 | 6.8182
4A | 5 | 10 | 4.5455 | 9.0909
4B | 5 | 15 | 4.5455 | 13.6364
4C | 7.5 | 10 | 6.8182 | 9.0909
5A | 7.5 | 7.5 | 6.8182 | 6.8182
5B | 7.5 | 10 | 6.8182 | 9.0909
5C | 7.5 | 7.5 | 6.8182 | 6.8182
6A | 7.5 | 7.5 | 6.8182 | 6.8182
6B | 7.5 | 7.5 | 6.8182 | 6.8182
7 | 15 | 5 | 13.6364 | 4.5455
8 | 15 | 5 | 13.6364 | 4.5455
90.1-16 dd; VSD required on pump above thresholds above
Look_Adm_dd_pump_VFD

## HVAC_Data (hidden)
State Commercial Energy Code Cost Effectiveness - HVAC data
|  | 2A |  | 3A |  | 3B |  | 4A |  | 5A
Current_HVAC_Data - upper table starting in column B, one set of current state HVAC data
State_HVAC_Data - lower table includes all state data - replacement data can be pasted in column B starting below Current_HVAC_ Data
Current State | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12
US National |  | Climate Zone 1 |  | Climate Zone 2 |  | Climate Zone 3 |  | Climate Zone 4 |  | Climate Zone 5
US |  | ZoneXX(City) Base Code | ZoneXX(City) Target Code | ZoneXX(City) Base Code | ZoneXX(City) Target Code | ZoneXX(City) Base Code | ZoneXX(City) Target Code | ZoneXX(City) Base Code | ZoneXX(City) Target Code | ZoneXX(City) Base Code | ZoneXX(City) Target Code
OfficeSmall | OfficeSmall
Names used to place data from State_HVAC_Data to Current_State_Data
US_SO_PSZ-AC:1 Cooling Capacity [ton] | PSZ-AC:1 Cooling Capacity [ton] | 1.9478 | 1.9013 | 1.848 | 1.8009 | 1.7121 | 1.6619 | 1.7143 | 1.6663 | 1.599 | 1.5518
US_SO_PSZ-AC:2 Cooling Capacity [ton] | PSZ-AC:2 Cooling Capacity [ton] | 2.0037 | 1.9189 | 1.8169 | 1.7245 | 1.8117 | 1.7264 | 1.7795 | 1.662 | 1.6576 | 1.5536
US_SO_PSZ-AC:3 Cooling Capacity [ton] | PSZ-AC:3 Cooling Capacity [ton] | 1.3979 | 1.347 | 1.2647 | 1.2078 | 1.2673 | 1.2215 | 1.2359 | 1.164 | 1.1516 | 1.0873
US_SO_PSZ-AC:4 Cooling Capacity [ton] | PSZ-AC:4 Cooling Capacity [ton] | 1.9331 | 1.8491 | 1.7858 | 1.6931 | 1.789 | 1.7062 | 1.6317 | 1.5177 | 1.4392 | 1.3431
US_SO_PSZ-AC:5 Cooling Capacity [ton] | PSZ-AC:5 Cooling Capacity [ton] | 1.5698 | 1.5158 | 1.4221 | 1.3661 | 1.5252 | 1.4725 | 1.4041 | 1.3202 | 1.3208 | 1.2482
US_SO_PSZ-AC:1 Supply Flow Rate [cfm] | PSZ-AC:1 Supply Flow Rate [cfm] | 635.664 | 614.4752 | 656.8528 | 635.664 | 741.608 | 720.4192 | 593.2864 | 572.0976 | 593.2864 | 572.0976
US_SO_PSZ-AC:2 Supply Flow Rate [cfm] | PSZ-AC:2 Supply Flow Rate [cfm] | 699.2304 | 678.0416 | 678.0416 | 635.664 | 805.1744 | 783.9856 | 656.8528 | 614.4752 | 656.8528 | 614.4752
US_SO_PSZ-AC:3 Supply Flow Rate [cfm] | PSZ-AC:3 Supply Flow Rate [cfm] | 529.72 | 529.72 | 508.5312 | 487.3424 | 572.0976 | 550.9088 | 508.5312 | 466.1536 | 487.3424 | 466.1536
US_SO_PSZ-AC:4 Supply Flow Rate [cfm] | PSZ-AC:4 Supply Flow Rate [cfm] | 678.0416 | 635.664 | 656.8528 | 614.4752 | 805.1744 | 762.7968 | 593.2864 | 550.9088 | 550.9088 | 508.5312
US_SO_PSZ-AC:5 Supply Flow Rate [cfm] | PSZ-AC:5 Supply Flow Rate [cfm] | 614.4752 | 593.2864 | 572.0976 | 550.9088 | 678.0416 | 656.8528 | 572.0976 | 529.72 | 572.0976 | 550.9088
US_SO_PSZ-AC:1 OA Rate [cfm] | PSZ-AC:1 OA Rate [cfm] | 136.9265 | 136.9265 | 136.9265 | 136.9265 | 136.9265 | 136.9265 | 136.9265 | 136.9265 | 136.9265 | 136.9265
US_SO_PSZ-AC:2 OA Rate [cfm] | PSZ-AC:2 OA Rate [cfm] | 103.7991 | 103.7991 | 103.7991 | 103.7991 | 103.7991 | 103.7991 | 103.7991 | 103.7991 | 103.7991 | 103.7991
US_SO_PSZ-AC:3 OA Rate [cfm] | PSZ-AC:3 OA Rate [cfm] | 61.5749 | 61.5749 | 61.5749 | 61.5749 | 61.5749 | 61.5749 | 61.5749 | 61.5749 | 61.5749 | 61.5749
US_SO_PSZ-AC:4 OA Rate [cfm] | PSZ-AC:4 OA Rate [cfm] | 103.7991 | 103.7991 | 103.7991 | 103.7991 | 103.7991 | 103.7991 | 103.7991 | 103.7991 | 103.7991 | 103.7991
US_SO_PSZ-AC:5 OA Rate [cfm] | PSZ-AC:5 OA Rate [cfm] | 61.5749 | 61.5749 | 61.5749 | 61.5749 | 61.5749 | 61.5749 | 61.5749 | 61.5749 | 61.5749 | 61.5749
US_SO_PSZ-AC:1 heating Capacity [kBtu/hr] | PSZ-AC:1 heating Capacity [kBtu/hr] | 9.4372 | 9.4372 | 11.9101 | 11.9101 | 10.459 | 10.459 | 13.5207 | 13.5207 | 14.6441 | 14.6441
US_SO_PSZ-AC:2 heating Capacity [kBtu/hr] | PSZ-AC:2 heating Capacity [kBtu/hr] | 10.2494 | 9.8884 | 18.3714 | 17.0959 | 15.0465 | 14.5909 | 20.5594 | 17.983 | 22.3722 | 20.1705
US_SO_PSZ-AC:3 heating Capacity [kBtu/hr] | PSZ-AC:3 heating Capacity [kBtu/hr] | 6.2949 | 6.0543 | 11.4014 | 10.5511 | 9.296 | 8.9923 | 12.7753 | 11.0437 | 13.7429 | 12.2624
US_SO_PSZ-AC:4 heating Capacity [kBtu/hr] | PSZ-AC:4 heating Capacity [kBtu/hr] | 10.1221 | 9.7612 | 18.2675 | 16.9921 | 14.9264 | 14.4708 | 20.5245 | 17.9426 | 22.2137 | 20.0117
US_SO_PSZ-AC:5 heating Capacity [kBtu/hr] | PSZ-AC:5 heating Capacity [kBtu/hr] | 6.284 | 6.0434 | 11.4579 | 10.6076 | 9.2592 | 8.9554 | 12.8321 | 11.0969 | 13.8076 | 12.3231
OfficeLarge
Zone, City, Code
US_LO_CAV_BAS Supply Flow Rate [cfm] | CAV_BAS Supply Flow Rate [cfm] | 11060.5536 | 10615.5888 | 10891.0432 | 10424.8896 | 12289.504 | 11780.9728 | 10657.9664 | 10213.0016 | 10848.6656 | 10382.512
US_LO_VAV_BOT WITH REHEAT Supply Flow Rate [cfm] | VAV_BOT WITH REHEAT Supply Flow Rate [cfm] | 18455.4448 | 17925.7248 | 18963.976 | 18413.0672 | 21633.7648 | 21040.4784 | 19430.1296 | 18858.032 | 19514.8848 | 18942.7872
US_LO_VAV_MID WITH REHEAT Supply Flow Rate [cfm] | VAV_MID WITH REHEAT Supply Flow Rate [cfm] | 170718.1619 | 165632.8499 | 176523.8931 | 171205.5043 | 202204.7187 | 196314.2323 | 182329.6243 | 176841.7251 | 181376.1283 | 175845.8515
US_LO_VAV_TOP WITH REHEAT Supply Flow Rate [cfm] | VAV_TOP WITH REHEAT Supply Flow Rate [cfm] | 18858.032 | 18413.0672 | 19451.3184 | 18985.1648 | 22756.7712 | 22248.24 | 20086.9824 | 19578.4512 | 20192.9264 | 19684.3952
US_LO_Supply Air Temp. Reset Flag | Supply Air Temp. Reset Flag | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes
US_LO_CAV_BAS OA Rate [cfm] | CAV_BAS OA Rate [cfm] | 2542.8255 | 2542.8255 | 2542.8255 | 2542.8255 | 2542.8255 | 2542.8255 | 2542.8255 | 2542.8255 | 2542.8255 | 2542.8255
US_LO_VAV_BOT WITH REHEAT OA Rate [cfm] | VAV_BOT WITH REHEAT OA Rate [cfm] | 4302.3858 | 4302.3858 | 4302.3858 | 4302.3858 | 4302.3858 | 4302.3858 | 4302.3858 | 4302.3858 | 4302.3858 | 4302.3858
US_LO_VAV_MID WITH REHEAT OA Rate [cfm] | VAV_MID WITH REHEAT OA Rate [cfm] | 43025.9773 | 43025.9773 | 43025.9773 | 43025.9773 | 43025.9773 | 43025.9773 | 43025.9773 | 43025.9773 | 43025.9773 | 43025.9773
US_LO_VAV_TOP WITH REHEAT OA Rate [cfm] | VAV_TOP WITH REHEAT OA Rate [cfm] | 4302.3858 | 4302.3858 | 4302.3858 | 4302.3858 | 4302.3858 | 4302.3858 | 4302.3858 | 4302.3858 | 4302.3858 | 4302.3858
US_LO_AIRLOOP DATACENTER BASEMENT OA Rate [cfm] | AIRLOOP DATACENTER BASEMENT OA Rate [cfm] | 716.9654 | 716.9654 | 716.9654 | 716.9654 | 716.9654 | 716.9654 | 716.9654 | 716.9654 | 716.9654 | 716.9654
US_LO_VAV_bot_WITH_REHEAT ERV Flag | VAV_bot_WITH_REHEAT ERV Flag | Yes | Yes | Yes | Yes | No | No | Yes | Yes | Yes | Yes
US_LO_VAV_mid_WITH_REHEAT ERV Flag | VAV_mid_WITH_REHEAT ERV Flag | Yes | Yes | Yes | Yes | No | No | Yes | Yes | Yes | Yes
US_LO_VAV_top_WITH_REHEAT ERV Flag | VAV_top_WITH_REHEAT ERV Flag | Yes | Yes | Yes | Yes | No | No | Yes | Yes | Yes | Yes
US_LO_COOLSYS1 CHILLER1 Capacity [ton] | COOLSYS1 CHILLER1 Capacity [ton] | 396.6465 | 389.1686 | 372.4976 | 364.9993 | 319.9492 | 312.4729 | 375.6304 | 367.7189 | 349.3208 | 341.5012
US_LO_COOLSYS1 CHILLER2 Capacity [ton] | COOLSYS1 CHILLER2 Capacity [ton] | 396.6465 | 389.1686 | 372.4976 | 364.9993 | 319.9492 | 312.4729 | 375.6304 | 367.7189 | 349.3208 | 341.5012
US_LO_TOWERWATERSYS COOLTOWER 1 Capacity [ton] | TOWERWATERSYS COOLTOWER 1 Capacity [ton] | 470.6199 | 461.7427 | 441.9538 | 433.0602 | 379.9332 | 371.0487 | 445.6785 | 436.2927 | 414.4809 | 405.1933
US_LO_TOWERWATERSYS COOLTOWER 2 Capacity [ton] | TOWERWATERSYS COOLTOWER 2 Capacity [ton] | 470.6199 | 461.7427 | 441.9538 | 433.0602 | 379.9332 | 371.0487 | 445.6785 | 436.2927 | 414.4809 | 405.1933
US_LO_HEATSYS1 BOILER Capacity [MMBTU/h] | HEATSYS1 BOILER Capacity [MMBTU/h] | 4.8398 | 4.8297 | 7.4525 | 7.438 | 6.3656 | 6.3509 | 8.6261 | 8.5184 | 9.2714 | 9.0739
US_LO_COOLSYS1 PUMP Flow Rate [gal/min] | COOLSYS1 PUMP Flow Rate [gal/min] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
US_LO_COOLSYS1 CHILLER1 PUMP Flow Rate [gal/min] | COOLSYS1 CHILLER1 PUMP Flow Rate [gal/min] | 622.3931 | 610.724 | 584.0226 | 572.3282 | 499.9667 | 488.3532 | 588.8411 | 576.4984 | 550.0696 | 537.8126
US_LO_COOLSYS1 CHILLER2 PUMP Flow Rate [gal/min] | COOLSYS1 CHILLER2 PUMP Flow Rate [gal/min] | 622.3931 | 610.724 | 584.0226 | 572.3282 | 499.9667 | 488.3532 | 588.8411 | 576.4984 | 550.0696 | 537.8126
US_LO_COOLSYS1 PUMP SECONDARY Flow Rate [gal/min] | COOLSYS1 PUMP SECONDARY Flow Rate [gal/min] | 1244.7861 | 1221.4497 | 1168.0452 | 1144.658 | 999.9319 | 976.7064 | 1177.6822 | 1152.9969 | 1100.1392 | 1075.6251
US_LO_HEATSYS1 PUMP Flow Rate [gal/min] | HEATSYS1 PUMP Flow Rate [gal/min] | 196.6835 | 196.2746 | 302.86 | 302.272 | 258.6915 | 258.0924 | 350.5553 | 346.179 | 376.7796 | 368.7514
US_LO_TOWERWATERSYS PUMP Flow Rate [gal/min] | TOWERWATERSYS PUMP Flow Rate [gal/min] | 2188.2956 | 2132.978 | 2055.1529 | 2000.6278 | 1765.2505 | 1712.6274 | 2072.4298 | 2015.5271 | 1927.2408 | 1860.5109
US_LO_PLANT CIRC PUMP Flow Rate [gal/min] | PLANT CIRC PUMP Flow Rate [gal/min] | 210.7649 | 210.1737 | 211.1406 | 210.5494 | 225.1237 | 224.4865 | 209.7695 | 209.1466 | 211.307 | 210.6777
US_LO_COOLSYS1 PUMP SECONDARY Pressure setpoint reset [yes,no] | COOLSYS1 PUMP SECONDARY Pressure setpoint reset [yes,no] | pump_ride_on_curve | pump_ride_on_curve | pump_ride_on_curve | pump_ride_on_curve | pump_ride_on_curve | pump_ride_on_curve | pump_ride_on_curve | pump_ride_on_curve | pump_ride_on_curve | pump_ride_on_curve
US_LO_COOLSYS1 CHILLER1 PUMP Pump Power [hp] | COOLSYS1 CHILLER1 PUMP Pump Power [hp] | 5.8933 | 5.7828 | 5.53 | 5.4193 | 4.7341 | 4.6241 | 5.5756 | 5.4588 | 5.2085 | 5.0925
US_LO_COOLSYS1 CHILLER2 PUMP Pump Power [hp] | COOLSYS1 CHILLER2 PUMP Pump Power [hp] | 5.8933 | 5.7828 | 5.53 | 5.4193 | 4.7341 | 4.6241 | 5.5756 | 5.4588 | 5.2085 | 5.0925
US_LO_COOLSYS1 PUMP SECONDARY Pump Power [hp] | COOLSYS1 PUMP SECONDARY Pump Power [hp] | 17.0246 | 16.7054 | 15.975 | 15.6551 | 13.6758 | 13.3581 | 16.1068 | 15.7692 | 15.0463 | 14.711
US_LO_HEATSYS1 PUMP Pump Power [hp] | HEATSYS1 PUMP Pump Power [hp] | 4.9618 | 4.9515 | 7.6403 | 7.6255 | 6.526 | 6.5109 | 8.8435 | 8.7331 | 9.5051 | 9.3025
US_LO_TOWERWATERSYS PUMP Pump Power [hp] | TOWERWATERSYS PUMP Pump Power [hp] | 45.3836 | 44.2368 | 42.6205 | 41.4894 | 36.6081 | 35.5188 | 42.979 | 41.7986 | 39.9687 | 38.5861
US_LO_PLANT CIRC PUMP Pump Power [hp] | PLANT CIRC PUMP Pump Power [hp] | 4.503 | 4.4904 | 4.511 | 4.4984 | 4.8098 | 4.7961 | 4.4817 | 4.4684 | 4.5146 | 4.5011
US_LO_Datacenter PLANT CIRC PUMP Pump Power [hp] | Datacenter PLANT CIRC PUMP Pump Power [hp] | 4.503 | 4.4904 | 4.511 | 4.4984 | 4.8098 | 4.7961 | 4.4817 | 4.4684 | 4.5146 | 4.5011
US_LO_ZN_VAV_BOXes_Max_Reheat_Water_Flow_GPM | ZN_VAV_BOXes_Max_Reheat_Water_Flow_GPM | 134.6933 | 134.6907 | 198.3482 | 198.3626 | 169.1855 | 169.1476 | 224.9228 | 220.9673 | 230.9027 | 224.0883
US_LO_COOLSYS1 PUMP SECONDARY VSD | COOLSYS1 PUMP SECONDARY VSD | No | No | No | No | No | No | No | No | No | No
US_LO_HEATSYS1 PUMP VSD | HEATSYS1 PUMP VSD | No | No | No | No | No | No | No | VFD | No | VFD
US_LO_DATACENTER BASEMENT Cooling Capacity [ton] | DATACENTER BASEMENT Cooling Capacity [ton] | 122.4648 | 122.1084 | 123.007 | 122.6466 | 131.6564 | 131.2668 | 121.5049 | 121.1445 | 122.0827 | 121.7198
US_LO_DATACENTER BOT Cooling Capacity [ton] | DATACENTER BOT Cooling Capacity [ton] | 2.6497 | 2.623 | 2.6194 | 2.6185 | 2.7947 | 2.7651 | 2.6393 | 2.616 | 2.6839 | 2.6602
US_LO_DATACENTER MID Cooling Capacity [ton] | DATACENTER MID Cooling Capacity [ton] | 25.1989 | 24.9535 | 25.17 | 24.9168 | 26.5498 | 26.2782 | 25.2438 | 25.0406 | 25.7149 | 25.5063
US_LO_DATACENTER TOP Cooling Capacity [ton] | DATACENTER TOP Cooling Capacity [ton] | 2.5595 | 2.5385 | 2.5325 | 2.5129 | 2.6748 | 2.6533 | 2.5698 | 2.5501 | 2.6144 | 2.5943
RetailStandalone
Zone, City, Code
US_RS_PSZ-AC:1 Cooling Capacity [ton] | PSZ-AC:1 Cooling Capacity [ton] | 8.986 | 8.7948 | 8.0656 | 7.8931 | 8.9189 | 8.6917 | 7.9086 | 7.7983 | 8.5417 | 8.2697
US_RS_PSZ-AC:2 Cooling Capacity [ton] | PSZ-AC:2 Cooling Capacity [ton] | 49.5632 | 46.5549 | 48.5186 | 46.3815 | 46.77 | 44.4285 | 47.2543 | 45.0837 | 43.5262 | 39.9594
US_RS_PSZ-AC:3 Cooling Capacity [ton] | PSZ-AC:3 Cooling Capacity [ton] | 6.9714 | 6.7039 | 6.4897 | 6.2459 | 6.6598 | 6.3564 | 6.7001 | 6.0487 | 6.3109 | 5.5947
US_RS_PSZ-AC:4 Cooling Capacity [ton] | PSZ-AC:4 Cooling Capacity [ton] | 6.0091 | 5.668 | 5.4903 | 5.1573 | 5.5488 | 5.1647 | 5.7137 | 5.0315 | 5.3139 | 4.5501
US_RS_PSZ-AC:1 Supply Flow Rate [cfm] | PSZ-AC:1 Supply Flow Rate [cfm] | 3284.264 | 3199.5088 | 3157.1312 | 3051.1872 | 3729.2288 | 3623.2848 | 3008.8096 | 2924.0544 | 3199.5088 | 3072.376
US_RS_PSZ-AC:2 Supply Flow Rate [cfm] | PSZ-AC:2 Supply Flow Rate [cfm] | 14874.5376 | 13963.4192 | 15065.2368 | 14111.7408 | 17120.5504 | 16061.1104 | 15107.6144 | 14111.7408 | 14874.5376 | 13370.1328
US_RS_PSZ-AC:3 Supply Flow Rate [cfm] | PSZ-AC:3 Supply Flow Rate [cfm] | 2373.1456 | 2246.0128 | 2309.5792 | 2182.4464 | 2690.9776 | 2542.656 | 2457.9008 | 2161.2576 | 2457.9008 | 2118.88
US_RS_PSZ-AC:4 Supply Flow Rate [cfm] | PSZ-AC:4 Supply Flow Rate [cfm] | 1928.1808 | 1779.8592 | 1843.4256 | 1695.104 | 2161.2576 | 1991.7472 | 2012.936 | 1695.104 | 1970.5584 | 1610.3488
US_RS_PSZ-AC:1 OA Rate [cfm] | PSZ-AC:1 OA Rate [cfm] | 490.6902 | 490.6902 | 490.6902 | 490.6902 | 490.6902 | 490.6902 | 490.6902 | 490.6902 | 490.6902 | 490.6902
US_RS_PSZ-AC:2 OA Rate [cfm] | PSZ-AC:2 OA Rate [cfm] | 4005.3824 | 4005.3824 | 4005.3824 | 4005.3824 | 4005.3824 | 4005.3824 | 4005.3824 | 4005.3824 | 4005.3824 | 4005.3824
US_RS_PSZ-AC:3 OA Rate [cfm] | PSZ-AC:3 OA Rate [cfm] | 377.4149 | 377.4149 | 377.4149 | 377.4149 | 377.4149 | 377.4149 | 377.4149 | 377.4149 | 377.4149 | 377.4149
US_RS_PSZ-AC:4 OA Rate [cfm] | PSZ-AC:4 OA Rate [cfm] | 377.4149 | 377.4149 | 377.4149 | 377.4149 | 377.4149 | 377.4149 | 377.4149 | 377.4149 | 377.4149 | 377.4149
US_RS_PSZ-AC:1 OA Damper [gravity, motorized] | PSZ-AC:1 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | motorized | motorized | motorized | motorized | motorized | motorized
US_RS_PSZ-AC:2 OA Damper [gravity, motorized] | PSZ-AC:2 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | motorized | motorized | motorized | motorized | motorized | motorized
US_RS_PSZ-AC:3 OA Damper [gravity, motorized] | PSZ-AC:3 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | motorized | motorized | motorized | motorized | motorized | motorized
US_RS_PSZ-AC:4 OA Damper [gravity, motorized] | PSZ-AC:4 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | motorized | motorized | motorized | motorized | motorized | motorized
US_RS_PSZ-AC:1 Heating Capacity [kBtu/hr] | PSZ-AC:1 Heating Capacity [kBtu/hr] | 136.1719 | 132.4379 | 135.2809 | 131.3371 | 140.7602 | 136.8695 | 141.4647 | 139.1773 | 150.0818 | 145.4489
US_RS_PSZ-AC:2 Heating Capacity [kBtu/hr] | PSZ-AC:2 Heating Capacity [kBtu/hr] | 664.1331 | 626.9925 | 727.1552 | 689.4494 | 714.9049 | 677.4665 | 788.7654 | 748.1381 | 801.0698 | 769.5641
US_RS_PSZ-AC:3 Heating Capacity [kBtu/hr] | PSZ-AC:3 Heating Capacity [kBtu/hr] | 98.3531 | 95.2133 | 101.1773 | 97.6554 | 102.0155 | 98.3994 | 114.6335 | 102.5713 | 115.585 | 103.0189
US_RS_PSZ-AC:4 Heating Capacity [kBtu/hr] | PSZ-AC:4 Heating Capacity [kBtu/hr] | 83.5312 | 77.9769 | 85.4206 | 79.9418 | 86.4304 | 78.6418 | 97.5221 | 85.8454 | 98.0308 | 84.8739
SchoolPrimary
Zone, City, Code
US_PS_VAV_POD_1 Cooling Capacity [ton] | VAV_POD_1 Cooling Capacity [ton] | 36.0114 | 35.7792 | 36.1392 | 35.8981 | 39.7677 | 39.5895 | 36.5221 | 35.2485 | 37.1085 | 35.8919
US_PS_VAV_POD_2 Cooling Capacity [ton] | VAV_POD_2 Cooling Capacity [ton] | 35.7567 | 35.5264 | 35.8205 | 35.5815 | 39.5021 | 39.3251 | 36.0875 | 34.8309 | 36.6966 | 35.4943
US_PS_VAV_POD_3 Cooling Capacity [ton] | VAV_POD_3 Cooling Capacity [ton] | 31.857 | 31.6546 | 31.9029 | 31.6928 | 34.859 | 34.7043 | 32.3938 | 31.2386 | 32.9832 | 31.8743
US_PS_VAV_OTHER Cooling Capacity [ton] | VAV_OTHER Cooling Capacity [ton] | 37.6916 | 37.6653 | 37.2384 | 37.2189 | 34.3939 | 34.3748 | 36.8219 | 35.9801 | 34.8169 | 34.0344
US_PS_PSZ-AC_1:6 Cooling Capacity [ton] | PSZ-AC_1:6 Cooling Capacity [ton] | 9.1929 | 9.2251 | 9.2129 | 9.2355 | 9.2506 | 9.2756 | 8.9017 | 8.8402 | 8.5616 | 8.5016
US_PS_PSZ-AC_2:5 Cooling Capacity [ton] | PSZ-AC_2:5 Cooling Capacity [ton] | 9.5784 | 9.4416 | 9.7576 | 9.6157 | 9.972 | 9.8617 | 9.9045 | 9.5347 | 9.7754 | 9.5076
US_PS_PSZ-AC_2:7 Cooling Capacity [ton] | PSZ-AC_2:7 Cooling Capacity [ton] | 15.6326 | 15.5445 | 16.0142 | 15.9228 | 18.1683 | 18.0664 | 15.6959 | 15.3996 | 15.868 | 15.5919
US_PS_VAV_POD_1 Supply Flow Rate [cfm] | VAV_POD_1 Supply Flow Rate [cfm] | 10806.288 | 10742.7216 | 10848.6656 | 10763.9104 | 12649.7136 | 12564.9584 | 10954.6096 | 10573.2112 | 11145.3088 | 10763.9104
US_PS_VAV_POD_2 Supply Flow Rate [cfm] | VAV_POD_2 Supply Flow Rate [cfm] | 10721.5328 | 10657.9664 | 10742.7216 | 10679.1552 | 12522.5808 | 12437.8256 | 10827.4768 | 10446.0784 | 11018.176 | 10657.9664
US_PS_VAV_POD_3 Supply Flow Rate [cfm] | VAV_POD_3 Supply Flow Rate [cfm] | 9556.1488 | 9492.5824 | 9577.3376 | 9513.7712 | 11145.3088 | 11081.7424 | 9725.6592 | 9365.4496 | 9895.1696 | 9556.1488
US_PS_VAV_OTHER Supply Flow Rate [cfm] | VAV_OTHER Supply Flow Rate [cfm] | 11314.8192 | 11293.6304 | 11420.7632 | 11420.7632 | 13306.5664 | 13285.3776 | 11526.7072 | 11166.4976 | 11717.4064 | 11378.3856
US_PS_PSZ-AC_2:5 Supply Flow Rate [cfm] | PSZ-AC_2:5 Supply Flow Rate [cfm] | 2881.6768 | 2839.2992 | 2924.0544 | 2881.6768 | 3326.6416 | 3284.264 | 2966.432 | 2860.488 | 3008.8096 | 2902.8656
US_PS_PSZ-AC_1:6 Supply Flow Rate [cfm] | PSZ-AC_1:6 Supply Flow Rate [cfm] | 2754.544 | 2775.7328 | 2839.2992 | 2839.2992 | 3178.32 | 3178.32 | 2775.7328 | 2754.544 | 2839.2992 | 2796.9216
US_PS_PSZ-AC_2:7 Supply Flow Rate [cfm] | PSZ-AC_2:7 Supply Flow Rate [cfm] | 4682.7248 | 4661.536 | 4809.8576 | 4788.6688 | 5445.5216 | 5424.3328 | 4703.9136 | 4619.1584 | 4767.48 | 4682.7248
US_PS_Supply Air Temp. Reset Flag | Supply Air Temp. Reset Flag | No | No | No | No | Yes | Yes | Yes | Yes | Yes | Yes
US_PS_VAV_POD_1 OA Rate [cfm] | VAV_POD_1 OA Rate [cfm] | 6282.6911 | 6282.6911 | 6282.6911 | 6282.6911 | 6282.6911 | 6282.6911 | 6282.6911 | 6282.6911 | 6282.6911 | 6282.6911
US_PS_VAV_POD_2 OA Rate [cfm] | VAV_POD_2 OA Rate [cfm] | 6282.6911 | 6282.6911 | 6282.6911 | 6282.6911 | 6282.6911 | 6282.6911 | 6282.6911 | 6282.6911 | 6282.6911 | 6282.6911
US_PS_VAV_POD_3 OA Rate [cfm] | VAV_POD_3 OA Rate [cfm] | 5422.4258 | 5422.4258 | 5422.4258 | 5422.4258 | 5422.4258 | 5422.4258 | 5422.4258 | 5422.4258 | 5422.4258 | 5422.4258
US_PS_VAV_OTHER OA Rate [cfm] | VAV_OTHER OA Rate [cfm] | 3111.7872 | 3111.7872 | 3111.7872 | 3111.7872 | 3111.7872 | 3111.7872 | 3111.7872 | 3111.7872 | 3111.7872 | 3111.7872
US_PS_PSZ-AC_2:5 OA Rate [cfm] | PSZ-AC_2:5 OA Rate [cfm] | 1152.7343 | 1152.7343 | 1152.7343 | 1152.7343 | 1152.7343 | 1152.7343 | 1152.7343 | 1152.7343 | 1152.7343 | 1152.7343
US_PS_PSZ-AC_1:6 OA Rate [cfm] | PSZ-AC_1:6 OA Rate [cfm] | 539.9118 | 539.9118 | 539.9118 | 539.9118 | 539.9118 | 539.9118 | 539.9118 | 539.9118 | 539.9118 | 539.9118
US_PS_PSZ-AC_2:7 OA Rate [cfm] | PSZ-AC_2:7 OA Rate [cfm] | 3153.0841 | 3153.0841 | 3153.0841 | 3153.0841 | 3153.0841 | 3153.0841 | 3153.0841 | 3153.0841 | 3153.0841 | 3153.0841
US_PS_VAV_POD_1 OA Damper [gravity, motorized] | VAV_POD_1 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | motorized | motorized | motorized | motorized | motorized | motorized
US_PS_VAV_POD_2 OA Damper [gravity, motorized] | VAV_POD_2 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | motorized | motorized | motorized | motorized | motorized | motorized
US_PS_VAV_POD_3 OA Damper [gravity, motorized] | VAV_POD_3 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | motorized | motorized | motorized | motorized | motorized | motorized
US_PS_VAV_OTHER OA Damper [gravity, motorized] | VAV_OTHER OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | motorized | motorized | motorized | motorized | motorized | motorized
US_PS_PSZ-AC_2:5 OA Damper [gravity, motorized] | PSZ-AC_2:5 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | motorized | motorized | motorized | motorized | motorized | motorized
US_PS_PSZ-AC_1:6 OA Damper [gravity, motorized] | PSZ-AC_1:6 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | motorized | motorized | motorized | motorized | motorized | motorized
US_PS_PSZ-AC_2:7 OA Damper [gravity, motorized] | PSZ-AC_2:7 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | motorized | motorized | motorized | motorized | motorized | motorized
US_PS_VAV_POD_1 (economizer) | VAV_POD_1 (economizer) | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialDryBulb | DifferentialDryBulb | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialDryBulb | DifferentialDryBulb
US_PS_VAV_POD_2 (economizer) | VAV_POD_2 (economizer) | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialDryBulb | DifferentialDryBulb | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialDryBulb | DifferentialDryBulb
US_PS_VAV_POD_3 (economizer) | VAV_POD_3 (economizer) | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialDryBulb | DifferentialDryBulb | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialDryBulb | DifferentialDryBulb
US_PS_VAV_OTHER (economizer) | VAV_OTHER (economizer) | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialDryBulb | DifferentialDryBulb | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialDryBulb | DifferentialDryBulb
US_PS_PSZ-AC_2:5 (economizer) | PSZ-AC_2:5 (economizer) | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialDryBulb | DifferentialDryBulb | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialDryBulb | DifferentialDryBulb
US_PS_PSZ-AC_1:6 (economizer) | PSZ-AC_1:6 (economizer) | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialDryBulb | DifferentialDryBulb | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialDryBulb | DifferentialDryBulb
US_PS_PSZ-AC_2:7 (economizer) | PSZ-AC_2:7 (economizer) | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialDryBulb | DifferentialDryBulb | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialDryBulb | DifferentialDryBulb
US_PS_VAV_Pod_1_ERV Flag | VAV_Pod_1_ERV Flag | Yes | Yes | Yes | Yes | No | No | Yes | Yes | Yes | Yes
US_PS_VAV_Pod_2_ERV Flag | VAV_Pod_2_ERV Flag | Yes | Yes | Yes | Yes | No | No | Yes | Yes | Yes | Yes
US_PS_VAV_Pod_3_ERV Flag | VAV_Pod_3_ERV Flag | Yes | Yes | Yes | Yes | No | No | Yes | Yes | Yes | Yes
US_PS_VAV_OTHER_ERV Flag | VAV_OTHER_ERV Flag | Yes | Yes | Yes | Yes | No | No | Yes | Yes | Yes | Yes
US_PS_PSZ_AC_2_5_ERV Flag | PSZ_AC_2_5_ERV Flag | Yes | Yes | Yes | Yes | No | No | Yes | Yes | Yes | Yes
US_PS_PSZ_AC_2_7_ERV Flag | PSZ_AC_2_7_ERV Flag | Yes | Yes | Yes | Yes | No | No | Yes | Yes | Yes | Yes
US_PS_HEATSYS1 Capacity [MMBTU/h] | HEATSYS1 Capacity [MMBTU/h] | 0.81758 | 0.81683 | 1.2177 | 1.2155 | 1.0872 | 1.085 | 1.4034 | 1.3462 | 1.5808 | 1.5131
US_PS_HEATSYS1 Flow Rate [gal/min] | HEATSYS1 Flow Rate [gal/min] | 33.2256 | 33.1952 | 49.4847 | 49.3955 | 44.184 | 44.0946 | 57.0331 | 54.7069 | 64.2406 | 61.4904
US_PS_VAV_POD_1 Fan Power [hp] | VAV_POD_1 Fan Power [hp] | 15.7199 | 15.6185 | 15.7756 | 15.6704 | 18.3894 | 18.272 | 15.9428 | 15.3869 | 16.1988 | 15.6677
US_PS_VAV_POD_2 Fan Power [hp] | VAV_POD_2 Fan Power [hp] | 15.6087 | 15.5082 | 15.6365 | 15.5322 | 18.215 | 18.0986 | 15.7531 | 15.2045 | 16.019 | 15.4941
US_PS_VAV_POD_3 Fan Power [hp] | VAV_POD_3 Fan Power [hp] | 13.9967 | 13.9077 | 14.0168 | 13.9245 | 16.2235 | 16.1212 | 14.2325 | 13.725 | 14.4915 | 14.0043
US_PS_VAV_OTHER Fan Power [hp] | VAV_OTHER Fan Power [hp] | 15.5687 | 15.5579 | 15.7206 | 15.7091 | 18.303 | 18.2903 | 16.7771 | 16.25 | 17.0458 | 16.5406
US_PS_HEATSYS1 Pump Power [hp] | HEATSYS1 Pump Power [hp] | 0.83819 | 0.83741 | 1.2484 | 1.2461 | 1.1146 | 1.1124 | 1.4388 | 1.3801 | 1.6206 | 1.5512
US_PS_PSZ-AC_1:6 Heating Capacity [kBtu/hr] | PSZ-AC_1:6 Heating Capacity [kBtu/hr] | 210.0011 | 210.7532 | 219.7686 | 220.5206 | 218.9184 | 219.6727 | 227.1288 | 225.0276 | 231.7554 | 229.6802
US_PS_PSZ-AC_2:5 Heating Capacity [kBtu/hr] | PSZ-AC_2:5 Heating Capacity [kBtu/hr] | 143.1357 | 141.617 | 163.6429 | 162.1231 | 157.944 | 156.4203 | 181.1611 | 177.0547 | 190.6368 | 186.6034
US_PS_PSZ-AC_2:7 Heating Capacity [kBtu/hr] | PSZ-AC_2:7 Heating Capacity [kBtu/hr] | 274.2161 | 273.2409 | 333.2598 | 332.2856 | 314.6732 | 313.692 | 368.9821 | 365.6973 | 395.2944 | 392.3096
US_PS_ZN_VAV_BOXes_Max_Reheat_Water_Flow_GPM | ZN_VAV_BOXes_Max_Reheat_Water_Flow_GPM | 94.3097 | 93.4261 | 93.0721 | 92.1725 | 85.0563 | 84.1331 | 95.9294 | 95.578 | 94.7918 | 93.9035
HotelSmall
Zone, City, Code
US_SH_SAC_FRONTOFFICE Cooling Capacity [ton] | SAC_FRONTOFFICE Cooling Capacity [ton] | 2.4822 | 2.3852 | 2.3242 | 2.23 | 2.3038 | 2.1979 | 2.2421 | 2.0767 | 2.1015 | 1.9304
US_SH_SAC_FRONTLOUNGE Cooling Capacity [ton] | SAC_FRONTLOUNGE Cooling Capacity [ton] | 6.2755 | 6.0879 | 6.3408 | 6.144 | 6.1201 | 5.7757 | 6.0679 | 5.7836 | 5.7091 | 5.525
US_SH_SAC_MEETINGROOM Cooling Capacity [ton] | SAC_MEETINGROOM Cooling Capacity [ton] | 2.8867 | 2.7775 | 2.9279 | 2.8141 | 3.124 | 3.0237 | 2.8132 | 2.6688 | 2.8193 | 2.6747
US_SH_SAC_EXC_EMPLGE_RESTRM Cooling Capacity [ton] | SAC_EXC_EMPLGE_RESTRM Cooling Capacity [ton] | 5.8622 | 5.7063 | 5.8208 | 5.6535 | 5.9275 | 5.8099 | 5.6095 | 5.415 | 5.4108 | 5.286
US_SH_SAC_FO_ADDAQ SUPPLY FAN Supply Flow Rate [cfm] | SAC_FO_ADDAQ SUPPLY FAN Supply Flow Rate [cfm] | 805.1744 | 762.7968 | 783.9856 | 741.608 | 911.1184 | 847.552 | 783.9856 | 699.2304 | 762.7968 | 699.2304
US_SH_SAC_FL_ADDAQ SUPPLY FAN Supply Flow Rate [cfm] | SAC_FL_ADDAQ SUPPLY FAN Supply Flow Rate [cfm] | 1885.8032 | 1822.2368 | 1906.992 | 1843.4256 | 2182.4464 | 2097.6912 | 1822.2368 | 1737.4816 | 1822.2368 | 1737.4816
US_SH_SAC_MR_ADDAQ SUPPLY FAN Supply Flow Rate [cfm] | SAC_MR_ADDAQ SUPPLY FAN Supply Flow Rate [cfm] | 868.7408 | 826.3632 | 868.7408 | 847.552 | 995.8736 | 953.496 | 847.552 | 805.1744 | 847.552 | 805.1744
US_SH_SAC_EXC_ADDAQ SUPPLY FAN Supply Flow Rate [cfm] | SAC_EXC_ADDAQ SUPPLY FAN Supply Flow Rate [cfm] | 2097.6912 | 2012.936 | 2118.88 | 2055.3136 | 2415.5232 | 2309.5792 | 2097.6912 | 2034.1248 | 2140.0688 | 2034.1248
US_SH_SAC_Exc_EmpLge_RestRm OA Rate [cfm] | SAC_Exc_EmpLge_RestRm OA Rate [cfm] | 200.0697 | 200.0697 | 200.0697 | 200.0697 | 200.0697 | 200.0697 | 200.0697 | 200.0697 | 200.0697 | 200.0697
US_SH_SAC_FrontLounge OA Rate [cfm] | SAC_FrontLounge OA Rate [cfm] | 500.204 | 500.204 | 500.204 | 500.204 | 500.204 | 500.204 | 500.204 | 500.204 | 500.204 | 500.204
US_SH_SAC_FrontOffice OA Rate [cfm] | SAC_FrontOffice OA Rate [cfm] | 119.34 | 119.34 | 119.34 | 119.34 | 119.34 | 119.34 | 119.34 | 119.34 | 119.34 | 119.34
US_SH_SAC_MeetingRoom OA Rate [cfm] | SAC_MeetingRoom OA Rate [cfm] | 267.8688 | 267.8688 | 267.8688 | 267.8688 | 267.8688 | 267.8688 | 267.8688 | 267.8688 | 267.8688 | 267.8688
US_SH_SAC_FrontLounge OA Damper [gravity, motorized] | SAC_FrontLounge OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | motorized | motorized | motorized | motorized | motorized | motorized
US_SH_SAC_FrontOffice (economizer) | SAC_FrontOffice (economizer) | No | No | No | No | No | No | No | No | No | No
US_SH_SAC_FrontLounge (economizer) | SAC_FrontLounge (economizer) | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialDryBulb | DifferentialDryBulb | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialDryBulb | DifferentialDryBulb
US_SH_SAC_MeetingRoom (economizer) | SAC_MeetingRoom (economizer) | No | DifferentialEnthalpy | No | DifferentialEnthalpy | No | DifferentialDryBulb | No | No | No | No
US_SH_SAC_Exc_EmpLge_RestRm (economizer) | SAC_Exc_EmpLge_RestRm (economizer) | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialDryBulb | DifferentialDryBulb | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialDryBulb | DifferentialDryBulb
US_SH_SAC_FRONTOFFICE Heating Capacity [kBtu/hr] | SAC_FRONTOFFICE Heating Capacity [kBtu/hr] | 33.6824 | 32.1545 | 34.1941 | 32.735 | 34.2057 | 32.678 | 35.9521 | 33.2853 | 36.1535 | 33.3538
US_SH_SAC_FRONTLOUNGE Heating Capacity [kBtu/hr] | SAC_FRONTLOUNGE Heating Capacity [kBtu/hr] | 85.3354 | 83.3479 | 93.2826 | 91.3206 | 91.6755 | 89.5017 | 97.9817 | 95.0036 | 100.7647 | 97.8985
US_SH_SAC_MEETINGROOM Heating Capacity [kBtu/hr] | SAC_MEETINGROOM Heating Capacity [kBtu/hr] | 40.4681 | 39.2302 | 44.9729 | 43.7092 | 43.8412 | 42.5072 | 47.6536 | 45.996 | 49.3933 | 47.7641
US_SH_SAC_EXC_EMPLGE_RESTRM Heating Capacity [kBtu/hr] | SAC_EXC_EMPLGE_RESTRM Heating Capacity [kBtu/hr] | 83.6622 | 83.6215 | 86.3944 | 87.6475 | 85.8058 | 86.5301 | 89.328 | 90.611 | 90.6545 | 92.4892
ApartmentMidRise
Zone, City, Code
US_MA_SPLIT GSW COOLING COIL Cooling Capacity [ton] | SPLIT GSW COOLING COIL Cooling Capacity [ton] | 1.2618 | 1.1808 | 1.1494 | 1.0663 | 1.1782 | 1.0779 | 1.1439 | 1.0167 | 1.0469 | 0.9264
US_MA_SPLIT GNW COOLING COIL Cooling Capacity [ton] | SPLIT GNW COOLING COIL Cooling Capacity [ton] | 1.1779 | 1.0973 | 1.0883 | 1.006 | 1.1333 | 1.0335 | 1.0541 | 0.93561 | 0.94349 | 0.83088
US_MA_SPLIT OFFICE COOLING COIL Cooling Capacity [ton] | SPLIT OFFICE COOLING COIL Cooling Capacity [ton] | 1.3948 | 1.3643 | 1.2558 | 1.224 | 1.2237 | 1.1898 | 1.2373 | 1.1657 | 1.1334 | 1.0658
US_MA_SPLIT GNE COOLING COIL Cooling Capacity [ton] | SPLIT GNE COOLING COIL Cooling Capacity [ton] | 1.0817 | 1.0013 | 0.99228 | 0.90981 | 1.0134 | 0.91521 | 0.95085 | 0.83768 | 0.83948 | 0.73416
US_MA_SPLIT GN1 COOLING COIL Cooling Capacity [ton] | SPLIT GN1 COOLING COIL Cooling Capacity [ton] | 0.91377 | 0.83301 | 0.85287 | 0.76943 | 0.85571 | 0.75622 | 0.81034 | 0.71356 | 0.71209 | 0.61994
US_MA_SPLIT GN2 COOLING COIL Cooling Capacity [ton] | SPLIT GN2 COOLING COIL Cooling Capacity [ton] | 0.91186 | 0.83112 | 0.85112 | 0.76771 | 0.85369 | 0.75423 | 0.80808 | 0.71143 | 0.70963 | 0.61761
US_MA_SPLIT GS1 COOLING COIL Cooling Capacity [ton] | SPLIT GS1 COOLING COIL Cooling Capacity [ton] | 1.0294 | 0.94574 | 0.91441 | 0.83106 | 0.89268 | 0.79288 | 0.94956 | 0.83932 | 0.87716 | 0.7702
US_MA_SPLIT GS2 COOLING COIL Cooling Capacity [ton] | SPLIT GS2 COOLING COIL Cooling Capacity [ton] | 1.0312 | 0.94992 | 0.91304 | 0.83214 | 0.89089 | 0.79399 | 0.95013 | 0.84312 | 0.87873 | 0.77408
US_MA_SPLIT MSW COOLING COIL Cooling Capacity [ton] | SPLIT MSW COOLING COIL Cooling Capacity [ton] | 2.6914 | 2.527 | 2.6063 | 2.4405 | 2.6674 | 2.4677 | 2.7386 | 2.4736 | 2.5815 | 2.3274
US_MA_SPLIT MNW COOLING COIL Cooling Capacity [ton] | SPLIT MNW COOLING COIL Cooling Capacity [ton] | 2.49 | 2.3266 | 2.4716 | 2.3064 | 2.5514 | 2.3524 | 2.5108 | 2.2626 | 2.3521 | 2.1169
US_MA_SPLIT MSE COOLING COIL Cooling Capacity [ton] | SPLIT MSE COOLING COIL Cooling Capacity [ton] | 2.5333 | 2.3674 | 2.4638 | 2.2952 | 2.4041 | 2.2075 | 2.616 | 2.3596 | 2.4774 | 2.2302
US_MA_SPLIT MNE COOLING COIL Cooling Capacity [ton] | SPLIT MNE COOLING COIL Cooling Capacity [ton] | 2.2511 | 2.0882 | 2.216 | 2.0514 | 2.2181 | 2.0234 | 2.2285 | 2.0022 | 2.0488 | 1.8298
US_MA_SPLIT MN1 COOLING COIL Cooling Capacity [ton] | SPLIT MN1 COOLING COIL Cooling Capacity [ton] | 1.853 | 1.6906 | 1.8322 | 1.6668 | 1.8263 | 1.6299 | 1.8096 | 1.6133 | 1.6396 | 1.453
US_MA_SPLIT MN2 COOLING COIL Cooling Capacity [ton] | SPLIT MN2 COOLING COIL Cooling Capacity [ton] | 1.8484 | 1.686 | 1.8278 | 1.6625 | 1.8213 | 1.625 | 1.8036 | 1.6076 | 1.6328 | 1.4465
US_MA_SPLIT MS1 COOLING COIL Cooling Capacity [ton] | SPLIT MS1 COOLING COIL Cooling Capacity [ton] | 2.1175 | 1.9499 | 1.9676 | 1.8031 | 1.9348 | 1.7548 | 2.1486 | 1.9238 | 2.0449 | 1.8274
US_MA_SPLIT MS2 COOLING COIL Cooling Capacity [ton] | SPLIT MS2 COOLING COIL Cooling Capacity [ton] | 2.1205 | 1.9528 | 2.0383 | 1.8686 | 1.9367 | 1.7568 | 2.1526 | 1.9279 | 2.0495 | 1.8319
US_MA_SPLIT TSW COOLING COIL Cooling Capacity [ton] | SPLIT TSW COOLING COIL Cooling Capacity [ton] | 1.6543 | 1.5743 | 1.6132 | 1.5324 | 1.7216 | 1.6243 | 1.7115 | 1.5503 | 1.6166 | 1.4614
US_MA_SPLIT TNW COOLING COIL Cooling Capacity [ton] | SPLIT TNW COOLING COIL Cooling Capacity [ton] | 1.5124 | 1.4333 | 1.5036 | 1.424 | 1.6233 | 1.5267 | 1.5346 | 1.3898 | 1.434 | 1.2931
US_MA_SPLIT TSE COOLING COIL Cooling Capacity [ton] | SPLIT TSE COOLING COIL Cooling Capacity [ton] | 1.57 | 1.4891 | 1.5382 | 1.456 | 1.5761 | 1.4792 | 1.6373 | 1.4797 | 1.5506 | 1.3988
US_MA_SPLIT TNE COOLING COIL Cooling Capacity [ton] | SPLIT TNE COOLING COIL Cooling Capacity [ton] | 1.3647 | 1.2845 | 1.3533 | 1.2742 | 1.42 | 1.3242 | 1.3679 | 1.2307 | 1.2458 | 1.1183
US_MA_SPLIT TN1 COOLING COIL Cooling Capacity [ton] | SPLIT TN1 COOLING COIL Cooling Capacity [ton] | 1.1335 | 1.0528 | 1.1111 | 1.0317 | 1.1477 | 1.0521 | 1.1102 | 1.0035 | 0.9877 | 0.90916
US_MA_SPLIT TN2 COOLING COIL Cooling Capacity [ton] | SPLIT TN2 COOLING COIL Cooling Capacity [ton] | 1.1351 | 1.0543 | 1.1061 | 1.0268 | 1.1446 | 1.048 | 1.1119 | 1.004 | 1.0121 | 0.91055
US_MA_SPLIT TS1 COOLING COIL Cooling Capacity [ton] | SPLIT TS1 COOLING COIL Cooling Capacity [ton] | 1.3291 | 1.2471 | 1.2886 | 1.2056 | 1.2896 | 1.1915 | 1.3708 | 1.2391 | 1.3062 | 1.1776
US_MA_SPLIT TS2 COOLING COIL Cooling Capacity [ton] | SPLIT TS2 COOLING COIL Cooling Capacity [ton] | 1.3315 | 1.2496 | 1.2926 | 1.2094 | 1.291 | 1.1929 | 1.3742 | 1.2421 | 1.3097 | 1.1809
US_MA_Split GN1 Furnace with DX Cooling OA Rate [cfm] | Split GN1 Furnace with DX Cooling OA Rate [cfm] | 54.9947 | 54.9947 | 54.9947 | 54.9947 | 54.9947 | 54.9947 | 54.9947 | 54.9947 | 54.9947 | 54.9947
US_MA_Split GN2 Furnace with DX Cooling OA Rate [cfm] | Split GN2 Furnace with DX Cooling OA Rate [cfm] | 54.9947 | 54.9947 | 54.9947 | 54.9947 | 54.9947 | 54.9947 | 54.9947 | 54.9947 | 54.9947 | 54.9947
US_MA_Split GNE Furnace with DX Cooling OA Rate [cfm] | Split GNE Furnace with DX Cooling OA Rate [cfm] | 54.9947 | 54.9947 | 54.9947 | 54.9947 | 54.9947 | 54.9947 | 54.9947 | 54.9947 | 54.9947 | 54.9947
US_MA_Split GNW Furnace with DX Cooling OA Rate [cfm] | Split GNW Furnace with DX Cooling OA Rate [cfm] | 54.9947 | 54.9947 | 54.9947 | 54.9947 | 54.9947 | 54.9947 | 54.9947 | 54.9947 | 54.9947 | 54.9947
US_MA_Split GS1 Furnace with DX Cooling OA Rate [cfm] | Split GS1 Furnace with DX Cooling OA Rate [cfm] | 54.9947 | 54.9947 | 54.9947 | 54.9947 | 54.9947 | 54.9947 | 54.9947 | 54.9947 | 54.9947 | 54.9947
US_MA_Split GS2 Furnace with DX Cooling OA Rate [cfm] | Split GS2 Furnace with DX Cooling OA Rate [cfm] | 54.9947 | 54.9947 | 54.9947 | 54.9947 | 54.9947 | 54.9947 | 54.9947 | 54.9947 | 54.9947 | 54.9947
US_MA_Split GSW Furnace with DX Cooling OA Rate [cfm] | Split GSW Furnace with DX Cooling OA Rate [cfm] | 54.9947 | 54.9947 | 54.9947 | 54.9947 | 54.9947 | 54.9947 | 54.9947 | 54.9947 | 54.9947 | 54.9947
US_MA_Split MN1 Furnace with DX Cooling OA Rate [cfm] | Split MN1 Furnace with DX Cooling OA Rate [cfm] | 109.9892 | 109.9892 | 109.9892 | 109.9892 | 109.9892 | 109.9892 | 109.9892 | 109.9892 | 109.9892 | 109.9892
US_MA_Split MN2 Furnace with DX Cooling OA Rate [cfm] | Split MN2 Furnace with DX Cooling OA Rate [cfm] | 109.9892 | 109.9892 | 109.9892 | 109.9892 | 109.9892 | 109.9892 | 109.9892 | 109.9892 | 109.9892 | 109.9892
US_MA_Split MNE Furnace with DX Cooling OA Rate [cfm] | Split MNE Furnace with DX Cooling OA Rate [cfm] | 109.9892 | 109.9892 | 109.9892 | 109.9892 | 109.9892 | 109.9892 | 109.9892 | 109.9892 | 109.9892 | 109.9892
US_MA_Split MNW Furnace with DX Cooling OA Rate [cfm] | Split MNW Furnace with DX Cooling OA Rate [cfm] | 109.9892 | 109.9892 | 109.9892 | 109.9892 | 109.9892 | 109.9892 | 109.9892 | 109.9892 | 109.9892 | 109.9892
US_MA_Split MS1 Furnace with DX Cooling OA Rate [cfm] | Split MS1 Furnace with DX Cooling OA Rate [cfm] | 109.9892 | 109.9892 | 109.9892 | 109.9892 | 109.9892 | 109.9892 | 109.9892 | 109.9892 | 109.9892 | 109.9892
US_MA_Split MS2 Furnace with DX Cooling OA Rate [cfm] | Split MS2 Furnace with DX Cooling OA Rate [cfm] | 109.9892 | 109.9892 | 109.9892 | 109.9892 | 109.9892 | 109.9892 | 109.9892 | 109.9892 | 109.9892 | 109.9892
US_MA_Split MSE Furnace with DX Cooling OA Rate [cfm] | Split MSE Furnace with DX Cooling OA Rate [cfm] | 109.9892 | 109.9892 | 109.9892 | 109.9892 | 109.9892 | 109.9892 | 109.9892 | 109.9892 | 109.9892 | 109.9892
US_MA_Split MSW Furnace with DX Cooling OA Rate [cfm] | Split MSW Furnace with DX Cooling OA Rate [cfm] | 109.9892 | 109.9892 | 109.9892 | 109.9892 | 109.9892 | 109.9892 | 109.9892 | 109.9892 | 109.9892 | 109.9892
US_MA_Split Office Furnace with DX Cooling OA Rate [cfm] | Split Office Furnace with DX Cooling OA Rate [cfm] | 80.742 | 80.742 | 80.742 | 80.742 | 80.742 | 80.742 | 80.742 | 80.742 | 80.742 | 80.742
US_MA_Split TN1 Furnace with DX Cooling OA Rate [cfm] | Split TN1 Furnace with DX Cooling OA Rate [cfm] | 54.9947 | 54.9947 | 54.9947 | 54.9947 | 54.9947 | 54.9947 | 54.9947 | 54.9947 | 54.9947 | 54.9947
US_MA_Split TN2 Furnace with DX Cooling OA Rate [cfm] | Split TN2 Furnace with DX Cooling OA Rate [cfm] | 54.9947 | 54.9947 | 54.9947 | 54.9947 | 54.9947 | 54.9947 | 54.9947 | 54.9947 | 54.9947 | 54.9947
US_MA_Split TNE Furnace with DX Cooling OA Rate [cfm] | Split TNE Furnace with DX Cooling OA Rate [cfm] | 54.9947 | 54.9947 | 54.9947 | 54.9947 | 54.9947 | 54.9947 | 54.9947 | 54.9947 | 54.9947 | 54.9947
US_MA_Split TNW Furnace with DX Cooling OA Rate [cfm] | Split TNW Furnace with DX Cooling OA Rate [cfm] | 54.9947 | 54.9947 | 54.9947 | 54.9947 | 54.9947 | 54.9947 | 54.9947 | 54.9947 | 54.9947 | 54.9947
US_MA_Split TS1 Furnace with DX Cooling OA Rate [cfm] | Split TS1 Furnace with DX Cooling OA Rate [cfm] | 54.9947 | 54.9947 | 54.9947 | 54.9947 | 54.9947 | 54.9947 | 54.9947 | 54.9947 | 54.9947 | 54.9947
US_MA_Split TS2 Furnace with DX Cooling OA Rate [cfm] | Split TS2 Furnace with DX Cooling OA Rate [cfm] | 54.9947 | 54.9947 | 54.9947 | 54.9947 | 54.9947 | 54.9947 | 54.9947 | 54.9947 | 54.9947 | 54.9947
US_MA_Split TSE Furnace with DX Cooling OA Rate [cfm] | Split TSE Furnace with DX Cooling OA Rate [cfm] | 54.9947 | 54.9947 | 54.9947 | 54.9947 | 54.9947 | 54.9947 | 54.9947 | 54.9947 | 54.9947 | 54.9947
US_MA_Split TSW Furnace with DX Cooling OA Rate [cfm] | Split TSW Furnace with DX Cooling OA Rate [cfm] | 54.9947 | 54.9947 | 54.9947 | 54.9947 | 54.9947 | 54.9947 | 54.9947 | 54.9947 | 54.9947 | 54.9947
US_MA_SPLIT GSW HEATING COIL Heating Capacity [kBtu/hr] | SPLIT GSW HEATING COIL Heating Capacity [kBtu/hr] | 19.1969 | 17.7784 | 18.9147 | 17.4764 | 19.3848 | 17.9419 | 19.7949 | 17.5833 | 19.4932 | 17.3399
US_MA_SPLIT GNW HEATING COIL Heating Capacity [kBtu/hr] | SPLIT GNW HEATING COIL Heating Capacity [kBtu/hr] | 17.9218 | 16.5118 | 18.0696 | 16.639 | 18.7381 | 17.3039 | 18.484 | 16.3919 | 17.8751 | 15.8616
US_MA_SPLIT OFFICE HEATING COIL Heating Capacity [kBtu/hr] | SPLIT OFFICE HEATING COIL Heating Capacity [kBtu/hr] | 20.3168 | 19.7908 | 20.2489 | 19.7087 | 20.6275 | 20.0868 | 21.7215 | 20.4661 | 21.5567 | 20.3602
US_MA_SPLIT GNE HEATING COIL Heating Capacity [kBtu/hr] | SPLIT GNE HEATING COIL Heating Capacity [kBtu/hr] | 16.1776 | 14.78 | 16.2288 | 14.8144 | 17.0144 | 15.6031 | 16.7021 | 14.7461 | 15.9794 | 14.1081
US_MA_SPLIT GN1 HEATING COIL Heating Capacity [kBtu/hr] | SPLIT GN1 HEATING COIL Heating Capacity [kBtu/hr] | 13.6339 | 12.2302 | 14.3033 | 12.8795 | 14.7475 | 13.317 | 14.5018 | 12.7993 | 14.0879 | 12.4496
US_MA_SPLIT GN2 HEATING COIL Heating Capacity [kBtu/hr] | SPLIT GN2 HEATING COIL Heating Capacity [kBtu/hr] | 13.6007 | 12.1977 | 14.2731 | 12.8501 | 14.7184 | 13.2885 | 14.4622 | 12.7623 | 14.044 | 12.4087
US_MA_SPLIT GS1 HEATING COIL Heating Capacity [kBtu/hr] | SPLIT GS1 HEATING COIL Heating Capacity [kBtu/hr] | 14.8942 | 13.4673 | 15.0561 | 13.6228 | 15.2793 | 13.8443 | 16.3235 | 14.4221 | 16.2359 | 14.3609
US_MA_SPLIT GS2 HEATING COIL Heating Capacity [kBtu/hr] | SPLIT GS2 HEATING COIL Heating Capacity [kBtu/hr] | 14.9249 | 13.5386 | 15.0326 | 13.6416 | 15.2535 | 13.8603 | 16.3478 | 14.4882 | 16.2637 | 14.4291
US_MA_SPLIT MSW HEATING COIL Heating Capacity [kBtu/hr] | SPLIT MSW HEATING COIL Heating Capacity [kBtu/hr] | 40.674 | 37.8076 | 42.6082 | 39.7386 | 43.2417 | 40.3698 | 46.6856 | 42.0176 | 47.0127 | 42.4712
US_MA_SPLIT MNW HEATING COIL Heating Capacity [kBtu/hr] | SPLIT MNW HEATING COIL Heating Capacity [kBtu/hr] | 37.7025 | 34.8482 | 40.6798 | 37.8173 | 41.573 | 38.7116 | 43.4943 | 39.1065 | 43.4412 | 39.2285
US_MA_SPLIT MSE HEATING COIL Heating Capacity [kBtu/hr] | SPLIT MSE HEATING COIL Heating Capacity [kBtu/hr] | 37.1006 | 34.2597 | 38.8681 | 36.0258 | 39.4548 | 36.6148 | 44.205 | 39.7231 | 44.327 | 39.9694
US_MA_SPLIT MNE HEATING COIL Heating Capacity [kBtu/hr] | SPLIT MNE HEATING COIL Heating Capacity [kBtu/hr] | 33.4745 | 30.6496 | 36.08 | 33.2524 | 36.7806 | 33.9815 | 38.8684 | 34.8585 | 38.2145 | 34.3996
US_MA_SPLIT MN1 HEATING COIL Heating Capacity [kBtu/hr] | SPLIT MN1 HEATING COIL Heating Capacity [kBtu/hr] | 27.2984 | 24.4924 | 30.5336 | 27.7127 | 31.1468 | 28.3235 | 31.9866 | 28.5294 | 31.7888 | 28.4567
US_MA_SPLIT MN2 HEATING COIL Heating Capacity [kBtu/hr] | SPLIT MN2 HEATING COIL Heating Capacity [kBtu/hr] | 27.2189 | 24.4149 | 30.4574 | 27.6382 | 31.0749 | 28.2531 | 31.8805 | 28.4289 | 31.6678 | 28.3421
US_MA_SPLIT MS1 HEATING COIL Heating Capacity [kBtu/hr] | SPLIT MS1 HEATING COIL Heating Capacity [kBtu/hr] | 30.5137 | 27.662 | 32.2434 | 29.4143 | 32.3095 | 29.4594 | 36.6719 | 32.7856 | 37.2727 | 33.4464
US_MA_SPLIT MS2 HEATING COIL Heating Capacity [kBtu/hr] | SPLIT MS2 HEATING COIL Heating Capacity [kBtu/hr] | 30.5632 | 27.7118 | 32.2528 | 29.4012 | 32.3396 | 29.4902 | 36.7435 | 32.8568 | 37.3536 | 33.5227
US_MA_SPLIT TSW HEATING COIL Heating Capacity [kBtu/hr] | SPLIT TSW HEATING COIL Heating Capacity [kBtu/hr] | 25.2574 | 23.8628 | 26.2091 | 24.8146 | 27.1984 | 25.8 | 28.8876 | 26.0257 | 28.7494 | 25.9475
US_MA_SPLIT TNW HEATING COIL Heating Capacity [kBtu/hr] | SPLIT TNW HEATING COIL Heating Capacity [kBtu/hr] | 23.1743 | 21.7909 | 24.7454 | 23.3614 | 25.7846 | 24.3958 | 26.2374 | 23.6196 | 26.0221 | 23.4974
US_MA_SPLIT TSE HEATING COIL Heating Capacity [kBtu/hr] | SPLIT TSE HEATING COIL Heating Capacity [kBtu/hr] | 23.491 | 22.0965 | 24.3863 | 22.9915 | 25.1065 | 23.713 | 27.5357 | 24.7698 | 27.3696 | 24.6838
US_MA_SPLIT TNE HEATING COIL Heating Capacity [kBtu/hr] | SPLIT TNE HEATING COIL Heating Capacity [kBtu/hr] | 20.4866 | 19.0951 | 21.8358 | 20.4429 | 22.8621 | 21.484 | 23.4306 | 21.0067 | 22.6531 | 20.3803
US_MA_SPLIT TN1 HEATING COIL Heating Capacity [kBtu/hr] | SPLIT TN1 HEATING COIL Heating Capacity [kBtu/hr] | 16.6701 | 15.2851 | 18.3365 | 16.9641 | 18.9456 | 17.5708 | 18.9961 | 17.1147 | 18.5312 | 16.7399
US_MA_SPLIT TN2 HEATING COIL Heating Capacity [kBtu/hr] | SPLIT TN2 HEATING COIL Heating Capacity [kBtu/hr] | 16.675 | 15.2902 | 18.2511 | 16.8798 | 18.9019 | 17.5122 | 19.0057 | 17.1249 | 18.5305 | 16.7429
US_MA_SPLIT TS1 HEATING COIL Heating Capacity [kBtu/hr] | SPLIT TS1 HEATING COIL Heating Capacity [kBtu/hr] | 19.7411 | 18.3312 | 20.5733 | 19.1645 | 20.9864 | 19.5753 | 23.3352 | 21.0242 | 23.4776 | 21.2004
US_MA_SPLIT TS2 HEATING COIL Heating Capacity [kBtu/hr] | SPLIT TS2 HEATING COIL Heating Capacity [kBtu/hr] | 19.7823 | 18.3736 | 20.6101 | 19.1992 | 21.0068 | 19.5967 | 23.3953 | 21.0764 | 23.5403 | 21.2594
US_MA_Split_GSW ERV Flag | Split_GSW ERV Flag | No | Yes | No | Yes | No | Yes | Yes | Yes | Yes | Yes
US_MA_Split_GNW ERV Flag | Split_GNW ERV Flag | No | Yes | No | Yes | No | Yes | Yes | Yes | Yes | Yes
US_MA_Split_GNE ERV Flag | Split_GNE ERV Flag | No | Yes | No | Yes | No | Yes | Yes | Yes | Yes | Yes
US_MA_Split_GN1 ERV Flag | Split_GN1 ERV Flag | No | Yes | No | Yes | No | Yes | Yes | Yes | Yes | Yes
US_MA_Split_GN2 ERV Flag | Split_GN2 ERV Flag | No | Yes | No | Yes | No | Yes | Yes | Yes | Yes | Yes
US_MA_Split_GS1 ERV Flag | Split_GS1 ERV Flag | No | Yes | No | Yes | No | Yes | Yes | Yes | Yes | Yes
US_MA_Split_GS2 ERV Flag | Split_GS2 ERV Flag | No | Yes | No | Yes | No | Yes | Yes | Yes | Yes | Yes
US_MA_Split_MSW ERV Flag | Split_MSW ERV Flag | No | Yes | No | Yes | No | Yes | Yes | Yes | Yes | Yes
US_MA_Split_MNW ERV Flag | Split_MNW ERV Flag | No | Yes | No | Yes | No | Yes | Yes | Yes | Yes | Yes
US_MA_Split_MSE ERV Flag | Split_MSE ERV Flag | No | Yes | No | Yes | No | Yes | Yes | Yes | Yes | Yes
US_MA_Split_MNE ERV Flag | Split_MNE ERV Flag | No | Yes | No | Yes | No | Yes | Yes | Yes | Yes | Yes
US_MA_Split_MN1 ERV Flag | Split_MN1 ERV Flag | No | Yes | No | Yes | No | Yes | Yes | Yes | Yes | Yes
US_MA_Split_MN2 ERV Flag | Split_MN2 ERV Flag | No | Yes | No | Yes | No | Yes | Yes | Yes | Yes | Yes
US_MA_Split_MS1 ERV Flag | Split_MS1 ERV Flag | No | Yes | No | Yes | No | Yes | Yes | Yes | Yes | Yes
US_MA_Split_MS2 ERV Flag | Split_MS2 ERV Flag | No | Yes | No | Yes | No | Yes | Yes | Yes | Yes | Yes
US_MA_Split_TSW ERV Flag | Split_TSW ERV Flag | No | Yes | No | Yes | No | Yes | Yes | Yes | Yes | Yes
US_MA_Split_TNW ERV Flag | Split_TNW ERV Flag | No | Yes | No | Yes | No | Yes | Yes | Yes | Yes | Yes
US_MA_Split_TSE ERV Flag | Split_TSE ERV Flag | No | Yes | No | Yes | No | Yes | Yes | Yes | Yes | Yes
US_MA_Split_TNE ERV Flag | Split_TNE ERV Flag | No | Yes | No | Yes | No | Yes | Yes | Yes | Yes | Yes
US_MA_Split_TN1 ERV Flag | Split_TN1 ERV Flag | No | Yes | No | Yes | No | Yes | Yes | Yes | Yes | Yes
US_MA_Split_TN2 ERV Flag | Split_TN2 ERV Flag | No | Yes | No | Yes | No | Yes | Yes | Yes | Yes | Yes
US_MA_Split_TS1 ERV Flag | Split_TS1 ERV Flag | No | Yes | No | Yes | No | Yes | Yes | Yes | Yes | Yes
US_MA_Split_TS2 ERV Flag | Split_TS2 ERV Flag | No | Yes | No | Yes | No | Yes | Yes | Yes | Yes | Yes
US National | US | [10 empty] | 2023-10-09
US | 2023-10-09 | [10 empty] | 2023-10-09
| OfficeSmall | [10 empty] | 2023-10-09
|  | Zone2A(Tampa) ASHRAE901_2019 | Zone2A(Tampa) ASHRAE901_2022 | Zone3A(Atlanta) ASHRAE901_2019 | Zone3A(Atlanta) ASHRAE901_2022 | Zone3B(ElPaso) ASHRAE901_2019 | Zone3B(ElPaso) ASHRAE901_2022 | Zone4A(NewYork) ASHRAE901_2019 | Zone4A(NewYork) ASHRAE901_2022 | Zone5A(Buffalo) ASHRAE901_2019 | Zone5A(Buffalo) ASHRAE901_2022 | 2023-10-09
US_SO_PSZ-AC:1 Cooling Capacity [ton] | PSZ-AC:1 Cooling Capacity [ton] | 1.9478 | 1.9013 | 1.848 | 1.8009 | 1.7121 | 1.6619 | 1.7143 | 1.6663 | 1.599 | 1.5518 | 2023-10-09
US_SO_PSZ-AC:2 Cooling Capacity [ton] | PSZ-AC:2 Cooling Capacity [ton] | 2.0037 | 1.9189 | 1.8169 | 1.7245 | 1.8117 | 1.7264 | 1.7795 | 1.662 | 1.6576 | 1.5536 | 2023-10-09
US_SO_PSZ-AC:3 Cooling Capacity [ton] | PSZ-AC:3 Cooling Capacity [ton] | 1.3979 | 1.347 | 1.2647 | 1.2078 | 1.2673 | 1.2215 | 1.2359 | 1.164 | 1.1516 | 1.0873 | 2023-10-09
US_SO_PSZ-AC:4 Cooling Capacity [ton] | PSZ-AC:4 Cooling Capacity [ton] | 1.9331 | 1.8491 | 1.7858 | 1.6931 | 1.789 | 1.7062 | 1.6317 | 1.5177 | 1.4392 | 1.3431 | 2023-10-09
US_SO_PSZ-AC:5 Cooling Capacity [ton] | PSZ-AC:5 Cooling Capacity [ton] | 1.5698 | 1.5158 | 1.4221 | 1.3661 | 1.5252 | 1.4725 | 1.4041 | 1.3202 | 1.3208 | 1.2482 | 2023-10-09
US_SO_PSZ-AC:1 Supply Flow Rate [cfm] | PSZ-AC:1 Supply Flow Rate [cfm] | 635.664 | 614.4752 | 656.8528 | 635.664 | 741.608 | 720.4192 | 593.2864 | 572.0976 | 593.2864 | 572.0976 | 2023-10-09
US_SO_PSZ-AC:2 Supply Flow Rate [cfm] | PSZ-AC:2 Supply Flow Rate [cfm] | 699.2304 | 678.0416 | 678.0416 | 635.664 | 805.1744 | 783.9856 | 656.8528 | 614.4752 | 656.8528 | 614.4752 | 2023-10-09
US_SO_PSZ-AC:3 Supply Flow Rate [cfm] | PSZ-AC:3 Supply Flow Rate [cfm] | 529.72 | 529.72 | 508.5312 | 487.3424 | 572.0976 | 550.9088 | 508.5312 | 466.1536 | 487.3424 | 466.1536 | 2023-10-09
US_SO_PSZ-AC:4 Supply Flow Rate [cfm] | PSZ-AC:4 Supply Flow Rate [cfm] | 678.0416 | 635.664 | 656.8528 | 614.4752 | 805.1744 | 762.7968 | 593.2864 | 550.9088 | 550.9088 | 508.5312 | 2023-10-09
US_SO_PSZ-AC:5 Supply Flow Rate [cfm] | PSZ-AC:5 Supply Flow Rate [cfm] | 614.4752 | 593.2864 | 572.0976 | 550.9088 | 678.0416 | 656.8528 | 572.0976 | 529.72 | 572.0976 | 550.9088 | 2023-10-09
US_SO_PSZ-AC:1 OA Rate [cfm] | PSZ-AC:1 OA Rate [cfm] | 136.9265 | 136.9265 | 136.9265 | 136.9265 | 136.9265 | 136.9265 | 136.9265 | 136.9265 | 136.9265 | 136.9265 | 2023-10-09
US_SO_PSZ-AC:2 OA Rate [cfm] | PSZ-AC:2 OA Rate [cfm] | 103.7991 | 103.7991 | 103.7991 | 103.7991 | 103.7991 | 103.7991 | 103.7991 | 103.7991 | 103.7991 | 103.7991 | 2023-10-09
US_SO_PSZ-AC:3 OA Rate [cfm] | PSZ-AC:3 OA Rate [cfm] | 61.5749 | 61.5749 | 61.5749 | 61.5749 | 61.5749 | 61.5749 | 61.5749 | 61.5749 | 61.5749 | 61.5749 | 2023-10-09
US_SO_PSZ-AC:4 OA Rate [cfm] | PSZ-AC:4 OA Rate [cfm] | 103.7991 | 103.7991 | 103.7991 | 103.7991 | 103.7991 | 103.7991 | 103.7991 | 103.7991 | 103.7991 | 103.7991 | 2023-10-09
US_SO_PSZ-AC:5 OA Rate [cfm] | PSZ-AC:5 OA Rate [cfm] | 61.5749 | 61.5749 | 61.5749 | 61.5749 | 61.5749 | 61.5749 | 61.5749 | 61.5749 | 61.5749 | 61.5749 | 2023-10-09
US_SO_PSZ-AC:1 heating Capacity [kBtu/hr] | PSZ-AC:1 heating Capacity [kBtu/hr] | 9.4372 | 9.4372 | 11.9101 | 11.9101 | 10.459 | 10.459 | 13.5207 | 13.5207 | 14.6441 | 14.6441 | 2023-10-09
US_SO_PSZ-AC:2 heating Capacity [kBtu/hr] | PSZ-AC:2 heating Capacity [kBtu/hr] | 10.2494 | 9.8884 | 18.3714 | 17.0959 | 15.0465 | 14.5909 | 20.5594 | 17.983 | 22.3722 | 20.1705 | 2023-10-09
US_SO_PSZ-AC:3 heating Capacity [kBtu/hr] | PSZ-AC:3 heating Capacity [kBtu/hr] | 6.2949 | 6.0543 | 11.4014 | 10.5511 | 9.296 | 8.9923 | 12.7753 | 11.0437 | 13.7429 | 12.2624 | 2023-10-09
US_SO_PSZ-AC:4 heating Capacity [kBtu/hr] | PSZ-AC:4 heating Capacity [kBtu/hr] | 10.1221 | 9.7612 | 18.2675 | 16.9921 | 14.9264 | 14.4708 | 20.5245 | 17.9426 | 22.2137 | 20.0117 | 2023-10-09
US_SO_PSZ-AC:5 heating Capacity [kBtu/hr] | PSZ-AC:5 heating Capacity [kBtu/hr] | 6.284 | 6.0434 | 11.4579 | 10.6076 | 9.2592 | 8.9554 | 12.8321 | 11.0969 | 13.8076 | 12.3231 | 2023-10-09
US_SO_PSZ-AC:1 HEATING COIL heating Capacity [kBtu/hr] | PSZ-AC:1 HEATING COIL heating Capacity [kBtu/hr] | 23.3738 | 22.8156 | 22.1755 | 21.6108 | 20.545 | 19.9431 | 20.5711 | 19.9957 | 19.1884 | 18.622 | 2023-10-09
US_SO_PSZ-AC:2 HEATING COIL heating Capacity [kBtu/hr] | PSZ-AC:2 HEATING COIL heating Capacity [kBtu/hr] | 24.0439 | 23.0265 | 21.8028 | 20.6938 | 21.7404 | 20.7165 | 21.354 | 19.9435 | 19.8915 | 18.6432 | 2023-10-09
US_SO_PSZ-AC:3 HEATING COIL heating Capacity [kBtu/hr] | PSZ-AC:3 HEATING COIL heating Capacity [kBtu/hr] | 16.7747 | 16.1644 | 15.1764 | 14.4937 | 15.2074 | 14.6575 | 14.8312 | 13.9685 | 13.8197 | 13.0478 | 2023-10-09
US_SO_PSZ-AC:4 HEATING COIL heating Capacity [kBtu/hr] | PSZ-AC:4 HEATING COIL heating Capacity [kBtu/hr] | 23.1972 | 22.1892 | 21.4298 | 20.3167 | 21.4681 | 20.4748 | 19.5806 | 18.2129 | 17.27 | 16.1168 | 2023-10-09
US_SO_PSZ-AC:5 HEATING COIL heating Capacity [kBtu/hr] | PSZ-AC:5 HEATING COIL heating Capacity [kBtu/hr] | 18.8382 | 18.1894 | 17.0652 | 16.3932 | 18.3019 | 17.6699 | 16.8488 | 15.8423 | 15.85 | 14.9785 | 2023-10-09
US_LO_OfficeLarge | OfficeLarge | [10 empty] | 2023-10-09
|  | Zone2A(Tampa) ASHRAE901_2019 | Zone2A(Tampa) ASHRAE901_2022 | Zone3A(Atlanta) ASHRAE901_2019 | Zone3A(Atlanta) ASHRAE901_2022 | Zone3B(ElPaso) ASHRAE901_2019 | Zone3B(ElPaso) ASHRAE901_2022 | Zone4A(NewYork) ASHRAE901_2019 | Zone4A(NewYork) ASHRAE901_2022 | Zone5A(Buffalo) ASHRAE901_2019 | Zone5A(Buffalo) ASHRAE901_2022 | 2023-10-09
US_LO_CAV_BAS Supply Flow Rate [cfm] | CAV_BAS Supply Flow Rate [cfm] | 11060.5536 | 10615.5888 | 10891.0432 | 10424.8896 | 12289.504 | 11780.9728 | 10657.9664 | 10213.0016 | 10848.6656 | 10382.512 | 2023-10-09
US_LO_VAV_BOT WITH REHEAT Supply Flow Rate [cfm] | VAV_BOT WITH REHEAT Supply Flow Rate [cfm] | 18455.4448 | 17925.7248 | 18963.976 | 18413.0672 | 21633.7648 | 21040.4784 | 19430.1296 | 18858.032 | 19514.8848 | 18942.7872 | 2023-10-09
US_LO_VAV_MID WITH REHEAT Supply Flow Rate [cfm] | VAV_MID WITH REHEAT Supply Flow Rate [cfm] | 170718.1619 | 165632.8499 | 176523.8931 | 171205.5043 | 202204.7187 | 196314.2323 | 182329.6243 | 176841.7251 | 181376.1283 | 175845.8515 | 2023-10-09
US_LO_VAV_TOP WITH REHEAT Supply Flow Rate [cfm] | VAV_TOP WITH REHEAT Supply Flow Rate [cfm] | 18858.032 | 18413.0672 | 19451.3184 | 18985.1648 | 22756.7712 | 22248.24 | 20086.9824 | 19578.4512 | 20192.9264 | 19684.3952 | 2023-10-09
US_LO_Supply Air Temp. Reset Flag | Supply Air Temp. Reset Flag | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 2023-10-09
US_LO_CAV_BAS OA Rate [cfm] | CAV_BAS OA Rate [cfm] | 2542.8255 | 2542.8255 | 2542.8255 | 2542.8255 | 2542.8255 | 2542.8255 | 2542.8255 | 2542.8255 | 2542.8255 | 2542.8255 | 2023-10-09
US_LO_VAV_BOT WITH REHEAT OA Rate [cfm] | VAV_BOT WITH REHEAT OA Rate [cfm] | 4302.3858 | 4302.3858 | 4302.3858 | 4302.3858 | 4302.3858 | 4302.3858 | 4302.3858 | 4302.3858 | 4302.3858 | 4302.3858 | 2023-10-09
US_LO_VAV_MID WITH REHEAT OA Rate [cfm] | VAV_MID WITH REHEAT OA Rate [cfm] | 43025.9773 | 43025.9773 | 43025.9773 | 43025.9773 | 43025.9773 | 43025.9773 | 43025.9773 | 43025.9773 | 43025.9773 | 43025.9773 | 2023-10-09
US_LO_VAV_TOP WITH REHEAT OA Rate [cfm] | VAV_TOP WITH REHEAT OA Rate [cfm] | 4302.3858 | 4302.3858 | 4302.3858 | 4302.3858 | 4302.3858 | 4302.3858 | 4302.3858 | 4302.3858 | 4302.3858 | 4302.3858 | 2023-10-09
US_LO_AIRLOOP DATACENTER BASEMENT OA Rate [cfm] | AIRLOOP DATACENTER BASEMENT OA Rate [cfm] | 716.9654 | 716.9654 | 716.9654 | 716.9654 | 716.9654 | 716.9654 | 716.9654 | 716.9654 | 716.9654 | 716.9654 | 2023-10-09
US_LO_VAV_bot_WITH_REHEAT ERV Flag | VAV_bot_WITH_REHEAT ERV Flag | Yes | Yes | Yes | Yes | No | No | Yes | Yes | Yes | Yes | 2023-10-09
US_LO_VAV_mid_WITH_REHEAT ERV Flag | VAV_mid_WITH_REHEAT ERV Flag | Yes | Yes | Yes | Yes | No | No | Yes | Yes | Yes | Yes | 2023-10-09
US_LO_VAV_top_WITH_REHEAT ERV Flag | VAV_top_WITH_REHEAT ERV Flag | Yes | Yes | Yes | Yes | No | No | Yes | Yes | Yes | Yes | 2023-10-09
US_LO_COOLSYS1 CHILLER1 Capacity [ton] | COOLSYS1 CHILLER1 Capacity [ton] | 396.6465 | 389.1686 | 372.4976 | 364.9993 | 319.9492 | 312.4729 | 375.6304 | 367.7189 | 349.3208 | 341.5012 | 2023-10-09
US_LO_COOLSYS1 CHILLER2 Capacity [ton] | COOLSYS1 CHILLER2 Capacity [ton] | 396.6465 | 389.1686 | 372.4976 | 364.9993 | 319.9492 | 312.4729 | 375.6304 | 367.7189 | 349.3208 | 341.5012 | 2023-10-09
US_LO_TOWERWATERSYS COOLTOWER 1 Capacity [ton] | TOWERWATERSYS COOLTOWER 1 Capacity [ton] | 470.6199 | 461.7427 | 441.9538 | 433.0602 | 379.9332 | 371.0487 | 445.6785 | 436.2927 | 414.4809 | 405.1933 | 2023-10-09
US_LO_TOWERWATERSYS COOLTOWER 2 Capacity [ton] | TOWERWATERSYS COOLTOWER 2 Capacity [ton] | 470.6199 | 461.7427 | 441.9538 | 433.0602 | 379.9332 | 371.0487 | 445.6785 | 436.2927 | 414.4809 | 405.1933 | 2023-10-09
US_LO_HEATSYS1 BOILER Capacity [MMBTU/h] | HEATSYS1 BOILER Capacity [MMBTU/h] | 4.8398 | 4.8297 | 7.4525 | 7.438 | 6.3656 | 6.3509 | 8.6261 | 8.5184 | 9.2714 | 9.0739 | 2023-10-09
US_LO_COOLSYS1 PUMP Flow Rate [gal/min] | COOLSYS1 PUMP Flow Rate [gal/min] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2023-10-09
US_LO_COOLSYS1 CHILLER1 PUMP Flow Rate [gal/min] | COOLSYS1 CHILLER1 PUMP Flow Rate [gal/min] | 622.3931 | 610.724 | 584.0226 | 572.3282 | 499.9667 | 488.3532 | 588.8411 | 576.4984 | 550.0696 | 537.8126 | 2023-10-09
US_LO_COOLSYS1 CHILLER2 PUMP Flow Rate [gal/min] | COOLSYS1 CHILLER2 PUMP Flow Rate [gal/min] | 622.3931 | 610.724 | 584.0226 | 572.3282 | 499.9667 | 488.3532 | 588.8411 | 576.4984 | 550.0696 | 537.8126 | 2023-10-09
US_LO_COOLSYS1 PUMP SECONDARY Flow Rate [gal/min] | COOLSYS1 PUMP SECONDARY Flow Rate [gal/min] | 1244.7861 | 1221.4497 | 1168.0452 | 1144.658 | 999.9319 | 976.7064 | 1177.6822 | 1152.9969 | 1100.1392 | 1075.6251 | 2023-10-09
US_LO_HEATSYS1 PUMP Flow Rate [gal/min] | HEATSYS1 PUMP Flow Rate [gal/min] | 196.6835 | 196.2746 | 302.86 | 302.272 | 258.6915 | 258.0924 | 350.5553 | 346.179 | 376.7796 | 368.7514 | 2023-10-09
US_LO_TOWERWATERSYS PUMP Flow Rate [gal/min] | TOWERWATERSYS PUMP Flow Rate [gal/min] | 2188.2956 | 2132.978 | 2055.1529 | 2000.6278 | 1765.2505 | 1712.6274 | 2072.4298 | 2015.5271 | 1927.2408 | 1860.5109 | 2023-10-09
US_LO_PLANT CIRC PUMP Flow Rate [gal/min] | PLANT CIRC PUMP Flow Rate [gal/min] | 210.7649 | 210.1737 | 211.1406 | 210.5494 | 225.1237 | 224.4865 | 209.7695 | 209.1466 | 211.307 | 210.6777 | 2023-10-09
US_LO_COOLSYS1 PUMP SECONDARY Pressure setpoint reset [yes,no] | COOLSYS1 PUMP SECONDARY Pressure setpoint reset [yes,no] | pump_ride_on_curve | pump_ride_on_curve | pump_ride_on_curve | pump_ride_on_curve | pump_ride_on_curve | pump_ride_on_curve | pump_ride_on_curve | pump_ride_on_curve | pump_ride_on_curve | pump_ride_on_curve | 2023-10-09
US_LO_COOLSYS1 CHILLER1 PUMP Pump Power [hp] | COOLSYS1 CHILLER1 PUMP Pump Power [hp] | 5.8933 | 5.7828 | 5.53 | 5.4193 | 4.7341 | 4.6241 | 5.5756 | 5.4588 | 5.2085 | 5.0925 | 2023-10-09
US_LO_COOLSYS1 CHILLER2 PUMP Pump Power [hp] | COOLSYS1 CHILLER2 PUMP Pump Power [hp] | 5.8933 | 5.7828 | 5.53 | 5.4193 | 4.7341 | 4.6241 | 5.5756 | 5.4588 | 5.2085 | 5.0925 | 2023-10-09
US_LO_COOLSYS1 PUMP SECONDARY Pump Power [hp] | COOLSYS1 PUMP SECONDARY Pump Power [hp] | 17.0246 | 16.7054 | 15.975 | 15.6551 | 13.6758 | 13.3581 | 16.1068 | 15.7692 | 15.0463 | 14.711 | 2023-10-09
US_LO_HEATSYS1 PUMP Pump Power [hp] | HEATSYS1 PUMP Pump Power [hp] | 4.9618 | 4.9515 | 7.6403 | 7.6255 | 6.526 | 6.5109 | 8.8435 | 8.7331 | 9.5051 | 9.3025 | 2023-10-09
US_LO_TOWERWATERSYS PUMP Pump Power [hp] | TOWERWATERSYS PUMP Pump Power [hp] | 45.3836 | 44.2368 | 42.6205 | 41.4894 | 36.6081 | 35.5188 | 42.979 | 41.7986 | 39.9687 | 38.5861 | 2023-10-09
US_LO_PLANT CIRC PUMP Pump Power [hp] | PLANT CIRC PUMP Pump Power [hp] | 4.503 | 4.4904 | 4.511 | 4.4984 | 4.8098 | 4.7961 | 4.4817 | 4.4684 | 4.5146 | 4.5011 | 2023-10-09
US_LO_Datacenter PLANT CIRC PUMP Pump Power [hp] | Datacenter PLANT CIRC PUMP Pump Power [hp] | 4.503 | 4.4904 | 4.511 | 4.4984 | 4.8098 | 4.7961 | 4.4817 | 4.4684 | 4.5146 | 4.5011 | 2023-10-09
US_LO_ZN_VAV_BOXes_Max_Reheat_Water_Flow_GPM | ZN_VAV_BOXes_Max_Reheat_Water_Flow_GPM | 134.6933 | 134.6907 | 198.3482 | 198.3626 | 169.1855 | 169.1476 | 224.9228 | 220.9673 | 230.9027 | 224.0883 | 2023-10-09
US_LO_COOLSYS1 PUMP SECONDARY VSD | COOLSYS1 PUMP SECONDARY VSD | No | No | No | No | No | No | No | No | No | No | 2023-10-09
US_LO_HEATSYS1 PUMP VSD | HEATSYS1 PUMP VSD | No | No | No | No | No | No | No | VFD | No | VFD | 2023-10-09
US_LO_DATACENTER BASEMENT Cooling Capacity [ton] | DATACENTER BASEMENT Cooling Capacity [ton] | 122.4648 | 122.1084 | 123.007 | 122.6466 | 131.6564 | 131.2668 | 121.5049 | 121.1445 | 122.0827 | 121.7198 | 2023-10-09
US_LO_DATACENTER BOT Cooling Capacity [ton] | DATACENTER BOT Cooling Capacity [ton] | 2.6497 | 2.623 | 2.6194 | 2.6185 | 2.7947 | 2.7651 | 2.6393 | 2.616 | 2.6839 | 2.6602 | 2023-10-09
US_LO_DATACENTER MID Cooling Capacity [ton] | DATACENTER MID Cooling Capacity [ton] | 25.1989 | 24.9535 | 25.17 | 24.9168 | 26.5498 | 26.2782 | 25.2438 | 25.0406 | 25.7149 | 25.5063 | 2023-10-09
US_LO_DATACENTER TOP Cooling Capacity [ton] | DATACENTER TOP Cooling Capacity [ton] | 2.5595 | 2.5385 | 2.5325 | 2.5129 | 2.6748 | 2.6533 | 2.5698 | 2.5501 | 2.6144 | 2.5943 | 2023-10-09
US_RS_RetailStandalone | RetailStandalone | [10 empty] | 2023-10-09
|  | Zone2A(Tampa) ASHRAE901_2019 | Zone2A(Tampa) ASHRAE901_2022 | Zone3A(Atlanta) ASHRAE901_2019 | Zone3A(Atlanta) ASHRAE901_2022 | Zone3B(ElPaso) ASHRAE901_2019 | Zone3B(ElPaso) ASHRAE901_2022 | Zone4A(NewYork) ASHRAE901_2019 | Zone4A(NewYork) ASHRAE901_2022 | Zone5A(Buffalo) ASHRAE901_2019 | Zone5A(Buffalo) ASHRAE901_2022 | 2023-10-09
US_RS_PSZ-AC:1 Cooling Capacity [ton] | PSZ-AC:1 Cooling Capacity [ton] | 8.986 | 8.7948 | 8.0656 | 7.8931 | 8.9189 | 8.6917 | 7.9086 | 7.7983 | 8.5417 | 8.2697 | 2023-10-09
US_RS_PSZ-AC:2 Cooling Capacity [ton] | PSZ-AC:2 Cooling Capacity [ton] | 49.5632 | 46.5549 | 48.5186 | 46.3815 | 46.77 | 44.4285 | 47.2543 | 45.0837 | 43.5262 | 39.9594 | 2023-10-09
US_RS_PSZ-AC:3 Cooling Capacity [ton] | PSZ-AC:3 Cooling Capacity [ton] | 6.9714 | 6.7039 | 6.4897 | 6.2459 | 6.6598 | 6.3564 | 6.7001 | 6.0487 | 6.3109 | 5.5947 | 2023-10-09
US_RS_PSZ-AC:4 Cooling Capacity [ton] | PSZ-AC:4 Cooling Capacity [ton] | 6.0091 | 5.668 | 5.4903 | 5.1573 | 5.5488 | 5.1647 | 5.7137 | 5.0315 | 5.3139 | 4.5501 | 2023-10-09
US_RS_PSZ-AC:1 Supply Flow Rate [cfm] | PSZ-AC:1 Supply Flow Rate [cfm] | 3284.264 | 3199.5088 | 3157.1312 | 3051.1872 | 3729.2288 | 3623.2848 | 3008.8096 | 2924.0544 | 3199.5088 | 3072.376 | 2023-10-09
US_RS_PSZ-AC:2 Supply Flow Rate [cfm] | PSZ-AC:2 Supply Flow Rate [cfm] | 14874.5376 | 13963.4192 | 15065.2368 | 14111.7408 | 17120.5504 | 16061.1104 | 15107.6144 | 14111.7408 | 14874.5376 | 13370.1328 | 2023-10-09
US_RS_PSZ-AC:3 Supply Flow Rate [cfm] | PSZ-AC:3 Supply Flow Rate [cfm] | 2373.1456 | 2246.0128 | 2309.5792 | 2182.4464 | 2690.9776 | 2542.656 | 2457.9008 | 2161.2576 | 2457.9008 | 2118.88 | 2023-10-09
US_RS_PSZ-AC:4 Supply Flow Rate [cfm] | PSZ-AC:4 Supply Flow Rate [cfm] | 1928.1808 | 1779.8592 | 1843.4256 | 1695.104 | 2161.2576 | 1991.7472 | 2012.936 | 1695.104 | 1970.5584 | 1610.3488 | 2023-10-09
US_RS_PSZ-AC:1 OA Rate [cfm] | PSZ-AC:1 OA Rate [cfm] | 490.6902 | 490.6902 | 490.6902 | 490.6902 | 490.6902 | 490.6902 | 490.6902 | 490.6902 | 490.6902 | 490.6902 | 2023-10-09
US_RS_PSZ-AC:2 OA Rate [cfm] | PSZ-AC:2 OA Rate [cfm] | 4005.3824 | 4005.3824 | 4005.3824 | 4005.3824 | 4005.3824 | 4005.3824 | 4005.3824 | 4005.3824 | 4005.3824 | 4005.3824 | 2023-10-09
US_RS_PSZ-AC:3 OA Rate [cfm] | PSZ-AC:3 OA Rate [cfm] | 377.4149 | 377.4149 | 377.4149 | 377.4149 | 377.4149 | 377.4149 | 377.4149 | 377.4149 | 377.4149 | 377.4149 | 2023-10-09
US_RS_PSZ-AC:4 OA Rate [cfm] | PSZ-AC:4 OA Rate [cfm] | 377.4149 | 377.4149 | 377.4149 | 377.4149 | 377.4149 | 377.4149 | 377.4149 | 377.4149 | 377.4149 | 377.4149 | 2023-10-09
US_RS_PSZ-AC:1 OA Damper [gravity, motorized] | PSZ-AC:1 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | motorized | motorized | motorized | motorized | motorized | motorized | 2023-10-09
US_RS_PSZ-AC:2 OA Damper [gravity, motorized] | PSZ-AC:2 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | motorized | motorized | motorized | motorized | motorized | motorized | 2023-10-09
US_RS_PSZ-AC:3 OA Damper [gravity, motorized] | PSZ-AC:3 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | motorized | motorized | motorized | motorized | motorized | motorized | 2023-10-09
US_RS_PSZ-AC:4 OA Damper [gravity, motorized] | PSZ-AC:4 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | motorized | motorized | motorized | motorized | motorized | motorized | 2023-10-09
US_RS_PSZ-AC:1 Heating Capacity [kBtu/hr] | PSZ-AC:1 Heating Capacity [kBtu/hr] | 136.1719 | 132.4379 | 135.2809 | 131.3371 | 140.7602 | 136.8695 | 141.4647 | 139.1773 | 150.0818 | 145.4489 | 2023-10-09
US_RS_PSZ-AC:2 Heating Capacity [kBtu/hr] | PSZ-AC:2 Heating Capacity [kBtu/hr] | 664.1331 | 626.9925 | 727.1552 | 689.4494 | 714.9049 | 677.4665 | 788.7654 | 748.1381 | 801.0698 | 769.5641 | 2023-10-09
US_RS_PSZ-AC:3 Heating Capacity [kBtu/hr] | PSZ-AC:3 Heating Capacity [kBtu/hr] | 98.3531 | 95.2133 | 101.1773 | 97.6554 | 102.0155 | 98.3994 | 114.6335 | 102.5713 | 115.585 | 103.0189 | 2023-10-09
US_RS_PSZ-AC:4 Heating Capacity [kBtu/hr] | PSZ-AC:4 Heating Capacity [kBtu/hr] | 83.5312 | 77.9769 | 85.4206 | 79.9418 | 86.4304 | 78.6418 | 97.5221 | 85.8454 | 98.0308 | 84.8739 | 2023-10-09
| FRONT_ENTRY UNIT HEATER HEATING COIL Heating Capacity [kBtu/hr] | 84.9947 | 84.7477 | 111.598 | 111.2307 | 94.7554 | 94.4119 | 140.9863 | 140.6209 | 169.6705 | 169.2301 | 2023-10-09
US_PS_SchoolPrimary | SchoolPrimary | [10 empty] | 2023-10-09
US_PS_ |  | Zone2A(Tampa) ASHRAE901_2019 | Zone2A(Tampa) ASHRAE901_2022 | Zone3A(Atlanta) ASHRAE901_2019 | Zone3A(Atlanta) ASHRAE901_2022 | Zone3B(ElPaso) ASHRAE901_2019 | Zone3B(ElPaso) ASHRAE901_2022 | Zone4A(NewYork) ASHRAE901_2019 | Zone4A(NewYork) ASHRAE901_2022 | Zone5A(Buffalo) ASHRAE901_2019 | Zone5A(Buffalo) ASHRAE901_2022 | 2023-10-09
US_PS_VAV_POD_1 Cooling Capacity [ton] | VAV_POD_1 Cooling Capacity [ton] | 36.0114 | 35.7792 | 36.1392 | 35.8981 | 39.7677 | 39.5895 | 36.5221 | 35.2485 | 37.1085 | 35.8919 | 2023-10-09
US_PS_VAV_POD_2 Cooling Capacity [ton] | VAV_POD_2 Cooling Capacity [ton] | 35.7567 | 35.5264 | 35.8205 | 35.5815 | 39.5021 | 39.3251 | 36.0875 | 34.8309 | 36.6966 | 35.4943 | 2023-10-09
US_PS_VAV_POD_3 Cooling Capacity [ton] | VAV_POD_3 Cooling Capacity [ton] | 31.857 | 31.6546 | 31.9029 | 31.6928 | 34.859 | 34.7043 | 32.3938 | 31.2386 | 32.9832 | 31.8743 | 2023-10-09
US_PS_VAV_OTHER Cooling Capacity [ton] | VAV_OTHER Cooling Capacity [ton] | 37.6916 | 37.6653 | 37.2384 | 37.2189 | 34.3939 | 34.3748 | 36.8219 | 35.9801 | 34.8169 | 34.0344 | 2023-10-09
US_PS_PSZ-AC_1:6 Cooling Capacity [ton] | PSZ-AC_1:6 Cooling Capacity [ton] | 9.1929 | 9.2251 | 9.2129 | 9.2355 | 9.2506 | 9.2756 | 8.9017 | 8.8402 | 8.5616 | 8.5016 | 2023-10-09
US_PS_PSZ-AC_2:5 Cooling Capacity [ton] | PSZ-AC_2:5 Cooling Capacity [ton] | 9.5784 | 9.4416 | 9.7576 | 9.6157 | 9.972 | 9.8617 | 9.9045 | 9.5347 | 9.7754 | 9.5076 | 2023-10-09
US_PS_PSZ-AC_2:7 Cooling Capacity [ton] | PSZ-AC_2:7 Cooling Capacity [ton] | 15.6326 | 15.5445 | 16.0142 | 15.9228 | 18.1683 | 18.0664 | 15.6959 | 15.3996 | 15.868 | 15.5919 | 2023-10-09
US_PS_VAV_POD_1 Supply Flow Rate [cfm] | VAV_POD_1 Supply Flow Rate [cfm] | 10806.288 | 10742.7216 | 10848.6656 | 10763.9104 | 12649.7136 | 12564.9584 | 10954.6096 | 10573.2112 | 11145.3088 | 10763.9104 | 2023-10-09
US_PS_VAV_POD_2 Supply Flow Rate [cfm] | VAV_POD_2 Supply Flow Rate [cfm] | 10721.5328 | 10657.9664 | 10742.7216 | 10679.1552 | 12522.5808 | 12437.8256 | 10827.4768 | 10446.0784 | 11018.176 | 10657.9664 | 2023-10-09
US_PS_VAV_POD_3 Supply Flow Rate [cfm] | VAV_POD_3 Supply Flow Rate [cfm] | 9556.1488 | 9492.5824 | 9577.3376 | 9513.7712 | 11145.3088 | 11081.7424 | 9725.6592 | 9365.4496 | 9895.1696 | 9556.1488 | 2023-10-09
US_PS_VAV_OTHER Supply Flow Rate [cfm] | VAV_OTHER Supply Flow Rate [cfm] | 11314.8192 | 11293.6304 | 11420.7632 | 11420.7632 | 13306.5664 | 13285.3776 | 11526.7072 | 11166.4976 | 11717.4064 | 11378.3856 | 2023-10-09
US_PS_PSZ-AC_2:5 Supply Flow Rate [cfm] | PSZ-AC_2:5 Supply Flow Rate [cfm] | 2881.6768 | 2839.2992 | 2924.0544 | 2881.6768 | 3326.6416 | 3284.264 | 2966.432 | 2860.488 | 3008.8096 | 2902.8656 | 2023-10-09
US_PS_PSZ-AC_1:6 Supply Flow Rate [cfm] | PSZ-AC_1:6 Supply Flow Rate [cfm] | 2754.544 | 2775.7328 | 2839.2992 | 2839.2992 | 3178.32 | 3178.32 | 2775.7328 | 2754.544 | 2839.2992 | 2796.9216 | 2023-10-09
US_PS_PSZ-AC_2:7 Supply Flow Rate [cfm] | PSZ-AC_2:7 Supply Flow Rate [cfm] | 4682.7248 | 4661.536 | 4809.8576 | 4788.6688 | 5445.5216 | 5424.3328 | 4703.9136 | 4619.1584 | 4767.48 | 4682.7248 | 2023-10-09
US_PS_Supply Air Temp. Reset Flag | Supply Air Temp. Reset Flag | No | No | No | No | Yes | Yes | Yes | Yes | Yes | Yes | 2023-10-09
US_PS_VAV_POD_1 OA Rate [cfm] | VAV_POD_1 OA Rate [cfm] | 6282.6911 | 6282.6911 | 6282.6911 | 6282.6911 | 6282.6911 | 6282.6911 | 6282.6911 | 6282.6911 | 6282.6911 | 6282.6911 | 2023-10-09
US_PS_VAV_POD_2 OA Rate [cfm] | VAV_POD_2 OA Rate [cfm] | 6282.6911 | 6282.6911 | 6282.6911 | 6282.6911 | 6282.6911 | 6282.6911 | 6282.6911 | 6282.6911 | 6282.6911 | 6282.6911 | 2023-10-09
US_PS_VAV_POD_3 OA Rate [cfm] | VAV_POD_3 OA Rate [cfm] | 5422.4258 | 5422.4258 | 5422.4258 | 5422.4258 | 5422.4258 | 5422.4258 | 5422.4258 | 5422.4258 | 5422.4258 | 5422.4258 | 2023-10-09
US_PS_VAV_OTHER OA Rate [cfm] | VAV_OTHER OA Rate [cfm] | 3111.7872 | 3111.7872 | 3111.7872 | 3111.7872 | 3111.7872 | 3111.7872 | 3111.7872 | 3111.7872 | 3111.7872 | 3111.7872 | 2023-10-09
US_PS_PSZ-AC_2:5 OA Rate [cfm] | PSZ-AC_2:5 OA Rate [cfm] | 1152.7343 | 1152.7343 | 1152.7343 | 1152.7343 | 1152.7343 | 1152.7343 | 1152.7343 | 1152.7343 | 1152.7343 | 1152.7343 | 2023-10-09
US_PS_PSZ-AC_1:6 OA Rate [cfm] | PSZ-AC_1:6 OA Rate [cfm] | 539.9118 | 539.9118 | 539.9118 | 539.9118 | 539.9118 | 539.9118 | 539.9118 | 539.9118 | 539.9118 | 539.9118 | 2023-10-09
US_PS_PSZ-AC_2:7 OA Rate [cfm] | PSZ-AC_2:7 OA Rate [cfm] | 3153.0841 | 3153.0841 | 3153.0841 | 3153.0841 | 3153.0841 | 3153.0841 | 3153.0841 | 3153.0841 | 3153.0841 | 3153.0841 | 2023-10-09
US_PS_VAV_POD_1 OA Damper [gravity, motorized] | VAV_POD_1 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | motorized | motorized | motorized | motorized | motorized | motorized | 2023-10-09
US_PS_VAV_POD_2 OA Damper [gravity, motorized] | VAV_POD_2 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | motorized | motorized | motorized | motorized | motorized | motorized | 2023-10-09
US_PS_VAV_POD_3 OA Damper [gravity, motorized] | VAV_POD_3 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | motorized | motorized | motorized | motorized | motorized | motorized | 2023-10-09
US_PS_VAV_OTHER OA Damper [gravity, motorized] | VAV_OTHER OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | motorized | motorized | motorized | motorized | motorized | motorized | 2023-10-09
US_PS_PSZ-AC_2:5 OA Damper [gravity, motorized] | PSZ-AC_2:5 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | motorized | motorized | motorized | motorized | motorized | motorized | 2023-10-09
US_PS_PSZ-AC_1:6 OA Damper [gravity, motorized] | PSZ-AC_1:6 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | motorized | motorized | motorized | motorized | motorized | motorized | 2023-10-09
US_PS_PSZ-AC_2:7 OA Damper [gravity, motorized] | PSZ-AC_2:7 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | motorized | motorized | motorized | motorized | motorized | motorized | 2023-10-09
US_PS_VAV_POD_1 (economizer) | VAV_POD_1 (economizer) | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialDryBulb | DifferentialDryBulb | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialDryBulb | DifferentialDryBulb | 2023-10-09
US_PS_VAV_POD_2 (economizer) | VAV_POD_2 (economizer) | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialDryBulb | DifferentialDryBulb | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialDryBulb | DifferentialDryBulb | 2023-10-09
US_PS_VAV_POD_3 (economizer) | VAV_POD_3 (economizer) | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialDryBulb | DifferentialDryBulb | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialDryBulb | DifferentialDryBulb | 2023-10-09
US_PS_VAV_OTHER (economizer) | VAV_OTHER (economizer) | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialDryBulb | DifferentialDryBulb | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialDryBulb | DifferentialDryBulb | 2023-10-09
US_PS_PSZ-AC_2:5 (economizer) | PSZ-AC_2:5 (economizer) | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialDryBulb | DifferentialDryBulb | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialDryBulb | DifferentialDryBulb | 2023-10-09
US_PS_PSZ-AC_1:6 (economizer) | PSZ-AC_1:6 (economizer) | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialDryBulb | DifferentialDryBulb | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialDryBulb | DifferentialDryBulb | 2023-10-09
US_PS_PSZ-AC_2:7 (economizer) | PSZ-AC_2:7 (economizer) | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialDryBulb | DifferentialDryBulb | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialDryBulb | DifferentialDryBulb | 2023-10-09
US_PS_VAV_Pod_1_ERV Flag | VAV_Pod_1_ERV Flag | Yes | Yes | Yes | Yes | No | No | Yes | Yes | Yes | Yes | 2023-10-09
US_PS_VAV_Pod_2_ERV Flag | VAV_Pod_2_ERV Flag | Yes | Yes | Yes | Yes | No | No | Yes | Yes | Yes | Yes | 2023-10-09
US_PS_VAV_Pod_3_ERV Flag | VAV_Pod_3_ERV Flag | Yes | Yes | Yes | Yes | No | No | Yes | Yes | Yes | Yes | 2023-10-09
US_PS_VAV_OTHER_ERV Flag | VAV_OTHER_ERV Flag | Yes | Yes | Yes | Yes | No | No | Yes | Yes | Yes | Yes | 2023-10-09
US_PS_PSZ_AC_2_5_ERV Flag | PSZ_AC_2_5_ERV Flag | Yes | Yes | Yes | Yes | No | No | Yes | Yes | Yes | Yes | 2023-10-09
US_PS_PSZ_AC_2_7_ERV Flag | PSZ_AC_2_7_ERV Flag | Yes | Yes | Yes | Yes | No | No | Yes | Yes | Yes | Yes | 2023-10-09
US_PS_HEATSYS1 Capacity [MMBTU/h] | HEATSYS1 Capacity [MMBTU/h] | 0.81758 | 0.81683 | 1.2177 | 1.2155 | 1.0872 | 1.085 | 1.4034 | 1.3462 | 1.5808 | 1.5131 | 2023-10-09
US_PS_HEATSYS1 Flow Rate [gal/min] | HEATSYS1 Flow Rate [gal/min] | 33.2256 | 33.1952 | 49.4847 | 49.3955 | 44.184 | 44.0946 | 57.0331 | 54.7069 | 64.2406 | 61.4904 | 2023-10-09
US_PS_VAV_POD_1 Fan Power [hp] | VAV_POD_1 Fan Power [hp] | 15.7199 | 15.6185 | 15.7756 | 15.6704 | 18.3894 | 18.272 | 15.9428 | 15.3869 | 16.1988 | 15.6677 | 2023-10-09
US_PS_VAV_POD_2 Fan Power [hp] | VAV_POD_2 Fan Power [hp] | 15.6087 | 15.5082 | 15.6365 | 15.5322 | 18.215 | 18.0986 | 15.7531 | 15.2045 | 16.019 | 15.4941 | 2023-10-09
US_PS_VAV_POD_3 Fan Power [hp] | VAV_POD_3 Fan Power [hp] | 13.9967 | 13.9077 | 14.0168 | 13.9245 | 16.2235 | 16.1212 | 14.2325 | 13.725 | 14.4915 | 14.0043 | 2023-10-09
US_PS_VAV_OTHER Fan Power [hp] | VAV_OTHER Fan Power [hp] | 15.5687 | 15.5579 | 15.7206 | 15.7091 | 18.303 | 18.2903 | 16.7771 | 16.25 | 17.0458 | 16.5406 | 2023-10-09
US_PS_HEATSYS1 Pump Power [hp] | HEATSYS1 Pump Power [hp] | 0.83819 | 0.83741 | 1.2484 | 1.2461 | 1.1146 | 1.1124 | 1.4388 | 1.3801 | 1.6206 | 1.5512 | 2023-10-09
US_PS_PSZ-AC_1:6 Heating Capacity [kBtu/hr] | PSZ-AC_1:6 Heating Capacity [kBtu/hr] | 210.0011 | 210.7532 | 219.7686 | 220.5206 | 218.9184 | 219.6727 | 227.1288 | 225.0276 | 231.7554 | 229.6802 | 2023-10-09
US_PS_PSZ-AC_2:5 Heating Capacity [kBtu/hr] | PSZ-AC_2:5 Heating Capacity [kBtu/hr] | 143.1357 | 141.617 | 163.6429 | 162.1231 | 157.944 | 156.4203 | 181.1611 | 177.0547 | 190.6368 | 186.6034 | 2023-10-09
US_PS_PSZ-AC_2:7 Heating Capacity [kBtu/hr] | PSZ-AC_2:7 Heating Capacity [kBtu/hr] | 274.2161 | 273.2409 | 333.2598 | 332.2856 | 314.6732 | 313.692 | 368.9821 | 365.6973 | 395.2944 | 392.3096 | 2023-10-09
US_PS_ZN_VAV_BOXes_Max_Reheat_Water_Flow_GPM | ZN_VAV_BOXes_Max_Reheat_Water_Flow_GPM | 94.3097 | 93.4261 | 93.0721 | 92.1725 | 85.0563 | 84.1331 | 95.9294 | 95.578 | 94.7918 | 93.9035 | 2023-10-09
US_SH_HotelSmall | HotelSmall | [10 empty] | 2023-10-09
US_SH_ |  | Zone2A(Tampa) ASHRAE901_2019 | Zone2A(Tampa) ASHRAE901_2022 | Zone3A(Atlanta) ASHRAE901_2019 | Zone3A(Atlanta) ASHRAE901_2022 | Zone3B(ElPaso) ASHRAE901_2019 | Zone3B(ElPaso) ASHRAE901_2022 | Zone4A(NewYork) ASHRAE901_2019 | Zone4A(NewYork) ASHRAE901_2022 | Zone5A(Buffalo) ASHRAE901_2019 | Zone5A(Buffalo) ASHRAE901_2022 | 2023-10-09
US_SH_SAC_FRONTOFFICE Cooling Capacity [ton] | SAC_FRONTOFFICE Cooling Capacity [ton] | 2.4822 | 2.3852 | 2.3242 | 2.23 | 2.3038 | 2.1979 | 2.2421 | 2.0767 | 2.1015 | 1.9304 | 2023-10-09
US_SH_SAC_FRONTLOUNGE Cooling Capacity [ton] | SAC_FRONTLOUNGE Cooling Capacity [ton] | 6.2755 | 6.0879 | 6.3408 | 6.144 | 6.1201 | 5.7757 | 6.0679 | 5.7836 | 5.7091 | 5.525 | 2023-10-09
US_SH_SAC_MEETINGROOM Cooling Capacity [ton] | SAC_MEETINGROOM Cooling Capacity [ton] | 2.8867 | 2.7775 | 2.9279 | 2.8141 | 3.124 | 3.0237 | 2.8132 | 2.6688 | 2.8193 | 2.6747 | 2023-10-09
US_SH_SAC_EXC_EMPLGE_RESTRM Cooling Capacity [ton] | SAC_EXC_EMPLGE_RESTRM Cooling Capacity [ton] | 5.8622 | 5.7063 | 5.8208 | 5.6535 | 5.9275 | 5.8099 | 5.6095 | 5.415 | 5.4108 | 5.286 | 2023-10-09
US_SH_SAC_FO_ADDAQ SUPPLY FAN Supply Flow Rate [cfm] | SAC_FO_ADDAQ SUPPLY FAN Supply Flow Rate [cfm] | 805.1744 | 762.7968 | 783.9856 | 741.608 | 911.1184 | 847.552 | 783.9856 | 699.2304 | 762.7968 | 699.2304 | 2023-10-09
US_SH_SAC_FL_ADDAQ SUPPLY FAN Supply Flow Rate [cfm] | SAC_FL_ADDAQ SUPPLY FAN Supply Flow Rate [cfm] | 1885.8032 | 1822.2368 | 1906.992 | 1843.4256 | 2182.4464 | 2097.6912 | 1822.2368 | 1737.4816 | 1822.2368 | 1737.4816 | 2023-10-09
US_SH_SAC_MR_ADDAQ SUPPLY FAN Supply Flow Rate [cfm] | SAC_MR_ADDAQ SUPPLY FAN Supply Flow Rate [cfm] | 868.7408 | 826.3632 | 868.7408 | 847.552 | 995.8736 | 953.496 | 847.552 | 805.1744 | 847.552 | 805.1744 | 2023-10-09
US_SH_SAC_EXC_ADDAQ SUPPLY FAN Supply Flow Rate [cfm] | SAC_EXC_ADDAQ SUPPLY FAN Supply Flow Rate [cfm] | 2097.6912 | 2012.936 | 2118.88 | 2055.3136 | 2415.5232 | 2309.5792 | 2097.6912 | 2034.1248 | 2140.0688 | 2034.1248 | 2023-10-09
US_SH_SAC_Exc_EmpLge_RestRm OA Rate [cfm] | SAC_Exc_EmpLge_RestRm OA Rate [cfm] | 200.0697 | 200.0697 | 200.0697 | 200.0697 | 200.0697 | 200.0697 | 200.0697 | 200.0697 | 200.0697 | 200.0697 | 2023-10-09
US_SH_SAC_FrontLounge OA Rate [cfm] | SAC_FrontLounge OA Rate [cfm] | 500.204 | 500.204 | 500.204 | 500.204 | 500.204 | 500.204 | 500.204 | 500.204 | 500.204 | 500.204 | 2023-10-09
US_SH_SAC_FrontOffice OA Rate [cfm] | SAC_FrontOffice OA Rate [cfm] | 119.34 | 119.34 | 119.34 | 119.34 | 119.34 | 119.34 | 119.34 | 119.34 | 119.34 | 119.34 | 2023-10-09
US_SH_SAC_MeetingRoom OA Rate [cfm] | SAC_MeetingRoom OA Rate [cfm] | 267.8688 | 267.8688 | 267.8688 | 267.8688 | 267.8688 | 267.8688 | 267.8688 | 267.8688 | 267.8688 | 267.8688 | 2023-10-09
US_SH_SAC_FrontLounge OA Damper [gravity, motorized] | SAC_FrontLounge OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | motorized | motorized | motorized | motorized | motorized | motorized | 2023-10-09
US_SH_SAC_FrontOffice (economizer) | SAC_FrontOffice (economizer) | No | No | No | No | No | No | No | No | No | No | 2023-10-09
US_SH_SAC_FrontLounge (economizer) | SAC_FrontLounge (economizer) | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialDryBulb | DifferentialDryBulb | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialDryBulb | DifferentialDryBulb | 2023-10-09
US_SH_SAC_MeetingRoom (economizer) | SAC_MeetingRoom (economizer) | No | DifferentialEnthalpy | No | DifferentialEnthalpy | No | DifferentialDryBulb | No | No | No | No | 2023-10-09
US_SH_SAC_Exc_EmpLge_RestRm (economizer) | SAC_Exc_EmpLge_RestRm (economizer) | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialDryBulb | DifferentialDryBulb | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialDryBulb | DifferentialDryBulb | 2023-10-09
US_SH_SAC_FRONTOFFICE Heating Capacity [kBtu/hr] | SAC_FRONTOFFICE Heating Capacity [kBtu/hr] | 33.6824 | 32.1545 | 34.1941 | 32.735 | 34.2057 | 32.678 | 35.9521 | 33.2853 | 36.1535 | 33.3538 | 2023-10-09
US_SH_SAC_FRONTLOUNGE Heating Capacity [kBtu/hr] | SAC_FRONTLOUNGE Heating Capacity [kBtu/hr] | 85.3354 | 83.3479 | 93.2826 | 91.3206 | 91.6755 | 89.5017 | 97.9817 | 95.0036 | 100.7647 | 97.8985 | 2023-10-09
US_SH_SAC_MEETINGROOM Heating Capacity [kBtu/hr] | SAC_MEETINGROOM Heating Capacity [kBtu/hr] | 40.4681 | 39.2302 | 44.9729 | 43.7092 | 43.8412 | 42.5072 | 47.6536 | 45.996 | 49.3933 | 47.7641
US_SH_SAC_EXC_EMPLGE_RESTRM Heating Capacity [kBtu/hr] | SAC_EXC_EMPLGE_RESTRM Heating Capacity [kBtu/hr] | 83.6622 | 83.6215 | 86.3944 | 87.6475 | 85.8058 | 86.5301 | 89.328 | 90.611 | 90.6545 | 92.4892
US_MA_ApartmentMidRise | ApartmentMidRise | [10 empty] | 2023-10-09
US_MA_ |  | Zone2A(Tampa) ASHRAE901_2019 | Zone2A(Tampa) ASHRAE901_2022 | Zone3A(Atlanta) ASHRAE901_2019 | Zone3A(Atlanta) ASHRAE901_2022 | Zone3B(ElPaso) ASHRAE901_2019 | Zone3B(ElPaso) ASHRAE901_2022 | Zone4A(NewYork) ASHRAE901_2019 | Zone4A(NewYork) ASHRAE901_2022 | Zone5A(Buffalo) ASHRAE901_2019 | Zone5A(Buffalo) ASHRAE901_2022 | 2023-10-09
US_MA_SPLIT GSW COOLING COIL Cooling Capacity [ton] | SPLIT GSW COOLING COIL Cooling Capacity [ton] | 1.2618 | 1.1808 | 1.1494 | 1.0663 | 1.1782 | 1.0779 | 1.1439 | 1.0167 | 1.0469 | 0.9264 | 2023-10-09
US_MA_SPLIT GNW COOLING COIL Cooling Capacity [ton] | SPLIT GNW COOLING COIL Cooling Capacity [ton] | 1.1779 | 1.0973 | 1.0883 | 1.006 | 1.1333 | 1.0335 | 1.0541 | 0.93561 | 0.94349 | 0.83088 | 2023-10-09
US_MA_SPLIT OFFICE COOLING COIL Cooling Capacity [ton] | SPLIT OFFICE COOLING COIL Cooling Capacity [ton] | 1.3948 | 1.3643 | 1.2558 | 1.224 | 1.2237 | 1.1898 | 1.2373 | 1.1657 | 1.1334 | 1.0658 | 2023-10-09
US_MA_SPLIT GNE COOLING COIL Cooling Capacity [ton] | SPLIT GNE COOLING COIL Cooling Capacity [ton] | 1.0817 | 1.0013 | 0.99228 | 0.90981 | 1.0134 | 0.91521 | 0.95085 | 0.83768 | 0.83948 | 0.73416 | 2023-10-09
US_MA_SPLIT GN1 COOLING COIL Cooling Capacity [ton] | SPLIT GN1 COOLING COIL Cooling Capacity [ton] | 0.91377 | 0.83301 | 0.85287 | 0.76943 | 0.85571 | 0.75622 | 0.81034 | 0.71356 | 0.71209 | 0.61994 | 2023-10-09
US_MA_SPLIT GN2 COOLING COIL Cooling Capacity [ton] | SPLIT GN2 COOLING COIL Cooling Capacity [ton] | 0.91186 | 0.83112 | 0.85112 | 0.76771 | 0.85369 | 0.75423 | 0.80808 | 0.71143 | 0.70963 | 0.61761 | 2023-10-09
US_MA_SPLIT GS1 COOLING COIL Cooling Capacity [ton] | SPLIT GS1 COOLING COIL Cooling Capacity [ton] | 1.0294 | 0.94574 | 0.91441 | 0.83106 | 0.89268 | 0.79288 | 0.94956 | 0.83932 | 0.87716 | 0.7702 | 2023-10-09
US_MA_SPLIT GS2 COOLING COIL Cooling Capacity [ton] | SPLIT GS2 COOLING COIL Cooling Capacity [ton] | 1.0312 | 0.94992 | 0.91304 | 0.83214 | 0.89089 | 0.79399 | 0.95013 | 0.84312 | 0.87873 | 0.77408 | 2023-10-09
US_MA_SPLIT MSW COOLING COIL Cooling Capacity [ton] | SPLIT MSW COOLING COIL Cooling Capacity [ton] | 2.6914 | 2.527 | 2.6063 | 2.4405 | 2.6674 | 2.4677 | 2.7386 | 2.4736 | 2.5815 | 2.3274 | 2023-10-09
US_MA_SPLIT MNW COOLING COIL Cooling Capacity [ton] | SPLIT MNW COOLING COIL Cooling Capacity [ton] | 2.49 | 2.3266 | 2.4716 | 2.3064 | 2.5514 | 2.3524 | 2.5108 | 2.2626 | 2.3521 | 2.1169 | 2023-10-09
US_MA_SPLIT MSE COOLING COIL Cooling Capacity [ton] | SPLIT MSE COOLING COIL Cooling Capacity [ton] | 2.5333 | 2.3674 | 2.4638 | 2.2952 | 2.4041 | 2.2075 | 2.616 | 2.3596 | 2.4774 | 2.2302 | 2023-10-09
US_MA_SPLIT MNE COOLING COIL Cooling Capacity [ton] | SPLIT MNE COOLING COIL Cooling Capacity [ton] | 2.2511 | 2.0882 | 2.216 | 2.0514 | 2.2181 | 2.0234 | 2.2285 | 2.0022 | 2.0488 | 1.8298 | 2023-10-09
US_MA_SPLIT MN1 COOLING COIL Cooling Capacity [ton] | SPLIT MN1 COOLING COIL Cooling Capacity [ton] | 1.853 | 1.6906 | 1.8322 | 1.6668 | 1.8263 | 1.6299 | 1.8096 | 1.6133 | 1.6396 | 1.453 | 2023-10-09
US_MA_SPLIT MN2 COOLING COIL Cooling Capacity [ton] | SPLIT MN2 COOLING COIL Cooling Capacity [ton] | 1.8484 | 1.686 | 1.8278 | 1.6625 | 1.8213 | 1.625 | 1.8036 | 1.6076 | 1.6328 | 1.4465 | 2023-10-09
US_MA_SPLIT MS1 COOLING COIL Cooling Capacity [ton] | SPLIT MS1 COOLING COIL Cooling Capacity [ton] | 2.1175 | 1.9499 | 1.9676 | 1.8031 | 1.9348 | 1.7548 | 2.1486 | 1.9238 | 2.0449 | 1.8274 | 2023-10-09
US_MA_SPLIT MS2 COOLING COIL Cooling Capacity [ton] | SPLIT MS2 COOLING COIL Cooling Capacity [ton] | 2.1205 | 1.9528 | 2.0383 | 1.8686 | 1.9367 | 1.7568 | 2.1526 | 1.9279 | 2.0495 | 1.8319 | 2023-10-09
US_MA_SPLIT TSW COOLING COIL Cooling Capacity [ton] | SPLIT TSW COOLING COIL Cooling Capacity [ton] | 1.6543 | 1.5743 | 1.6132 | 1.5324 | 1.7216 | 1.6243 | 1.7115 | 1.5503 | 1.6166 | 1.4614 | 2023-10-09
US_MA_SPLIT TNW COOLING COIL Cooling Capacity [ton] | SPLIT TNW COOLING COIL Cooling Capacity [ton] | 1.5124 | 1.4333 | 1.5036 | 1.424 | 1.6233 | 1.5267 | 1.5346 | 1.3898 | 1.434 | 1.2931 | 2023-10-09
US_MA_SPLIT TSE COOLING COIL Cooling Capacity [ton] | SPLIT TSE COOLING COIL Cooling Capacity [ton] | 1.57 | 1.4891 | 1.5382 | 1.456 | 1.5761 | 1.4792 | 1.6373 | 1.4797 | 1.5506 | 1.3988 | 2023-10-09
US_MA_SPLIT TNE COOLING COIL Cooling Capacity [ton] | SPLIT TNE COOLING COIL Cooling Capacity [ton] | 1.3647 | 1.2845 | 1.3533 | 1.2742 | 1.42 | 1.3242 | 1.3679 | 1.2307 | 1.2458 | 1.1183 | 2023-10-09
US_MA_SPLIT TN1 COOLING COIL Cooling Capacity [ton] | SPLIT TN1 COOLING COIL Cooling Capacity [ton] | 1.1335 | 1.0528 | 1.1111 | 1.0317 | 1.1477 | 1.0521 | 1.1102 | 1.0035 | 0.9877 | 0.90916 | 2023-10-09
US_MA_SPLIT TN2 COOLING COIL Cooling Capacity [ton] | SPLIT TN2 COOLING COIL Cooling Capacity [ton] | 1.1351 | 1.0543 | 1.1061 | 1.0268 | 1.1446 | 1.048 | 1.1119 | 1.004 | 1.0121 | 0.91055 | 2023-10-09
US_MA_SPLIT TS1 COOLING COIL Cooling Capacity [ton] | SPLIT TS1 COOLING COIL Cooling Capacity [ton] | 1.3291 | 1.2471 | 1.2886 | 1.2056 | 1.2896 | 1.1915 | 1.3708 | 1.2391 | 1.3062 | 1.1776 | 2023-10-09
US_MA_SPLIT TS2 COOLING COIL Cooling Capacity [ton] | SPLIT TS2 COOLING COIL Cooling Capacity [ton] | 1.3315 | 1.2496 | 1.2926 | 1.2094 | 1.291 | 1.1929 | 1.3742 | 1.2421 | 1.3097 | 1.1809 | 2023-10-09
US_MA_Split GN1 Furnace with DX Cooling OA Rate [cfm] | Split GN1 Furnace with DX Cooling OA Rate [cfm] | 54.9947 | 54.9947 | 54.9947 | 54.9947 | 54.9947 | 54.9947 | 54.9947 | 54.9947 | 54.9947 | 54.9947 | 2023-10-09
US_MA_Split GN2 Furnace with DX Cooling OA Rate [cfm] | Split GN2 Furnace with DX Cooling OA Rate [cfm] | 54.9947 | 54.9947 | 54.9947 | 54.9947 | 54.9947 | 54.9947 | 54.9947 | 54.9947 | 54.9947 | 54.9947 | 2023-10-09
US_MA_Split GNE Furnace with DX Cooling OA Rate [cfm] | Split GNE Furnace with DX Cooling OA Rate [cfm] | 54.9947 | 54.9947 | 54.9947 | 54.9947 | 54.9947 | 54.9947 | 54.9947 | 54.9947 | 54.9947 | 54.9947 | 2023-10-09
US_MA_Split GNW Furnace with DX Cooling OA Rate [cfm] | Split GNW Furnace with DX Cooling OA Rate [cfm] | 54.9947 | 54.9947 | 54.9947 | 54.9947 | 54.9947 | 54.9947 | 54.9947 | 54.9947 | 54.9947 | 54.9947 | 2023-10-09
US_MA_Split GS1 Furnace with DX Cooling OA Rate [cfm] | Split GS1 Furnace with DX Cooling OA Rate [cfm] | 54.9947 | 54.9947 | 54.9947 | 54.9947 | 54.9947 | 54.9947 | 54.9947 | 54.9947 | 54.9947 | 54.9947 | 2023-10-09
US_MA_Split GS2 Furnace with DX Cooling OA Rate [cfm] | Split GS2 Furnace with DX Cooling OA Rate [cfm] | 54.9947 | 54.9947 | 54.9947 | 54.9947 | 54.9947 | 54.9947 | 54.9947 | 54.9947 | 54.9947 | 54.9947 | 2023-10-09
US_MA_Split GSW Furnace with DX Cooling OA Rate [cfm] | Split GSW Furnace with DX Cooling OA Rate [cfm] | 54.9947 | 54.9947 | 54.9947 | 54.9947 | 54.9947 | 54.9947 | 54.9947 | 54.9947 | 54.9947 | 54.9947 | 2023-10-09
US_MA_Split MN1 Furnace with DX Cooling OA Rate [cfm] | Split MN1 Furnace with DX Cooling OA Rate [cfm] | 109.9892 | 109.9892 | 109.9892 | 109.9892 | 109.9892 | 109.9892 | 109.9892 | 109.9892 | 109.9892 | 109.9892 | 2023-10-09
US_MA_Split MN2 Furnace with DX Cooling OA Rate [cfm] | Split MN2 Furnace with DX Cooling OA Rate [cfm] | 109.9892 | 109.9892 | 109.9892 | 109.9892 | 109.9892 | 109.9892 | 109.9892 | 109.9892 | 109.9892 | 109.9892 | 2023-10-09
US_MA_Split MNE Furnace with DX Cooling OA Rate [cfm] | Split MNE Furnace with DX Cooling OA Rate [cfm] | 109.9892 | 109.9892 | 109.9892 | 109.9892 | 109.9892 | 109.9892 | 109.9892 | 109.9892 | 109.9892 | 109.9892 | 2023-10-09
US_MA_Split MNW Furnace with DX Cooling OA Rate [cfm] | Split MNW Furnace with DX Cooling OA Rate [cfm] | 109.9892 | 109.9892 | 109.9892 | 109.9892 | 109.9892 | 109.9892 | 109.9892 | 109.9892 | 109.9892 | 109.9892 | 2023-10-09
US_MA_Split MS1 Furnace with DX Cooling OA Rate [cfm] | Split MS1 Furnace with DX Cooling OA Rate [cfm] | 109.9892 | 109.9892 | 109.9892 | 109.9892 | 109.9892 | 109.9892 | 109.9892 | 109.9892 | 109.9892 | 109.9892 | 2023-10-09
US_MA_Split MS2 Furnace with DX Cooling OA Rate [cfm] | Split MS2 Furnace with DX Cooling OA Rate [cfm] | 109.9892 | 109.9892 | 109.9892 | 109.9892 | 109.9892 | 109.9892 | 109.9892 | 109.9892 | 109.9892 | 109.9892 | 2023-10-09
US_MA_Split MSE Furnace with DX Cooling OA Rate [cfm] | Split MSE Furnace with DX Cooling OA Rate [cfm] | 109.9892 | 109.9892 | 109.9892 | 109.9892 | 109.9892 | 109.9892 | 109.9892 | 109.9892 | 109.9892 | 109.9892 | 2023-10-09
US_MA_Split MSW Furnace with DX Cooling OA Rate [cfm] | Split MSW Furnace with DX Cooling OA Rate [cfm] | 109.9892 | 109.9892 | 109.9892 | 109.9892 | 109.9892 | 109.9892 | 109.9892 | 109.9892 | 109.9892 | 109.9892 | 2023-10-09
US_MA_Split Office Furnace with DX Cooling OA Rate [cfm] | Split Office Furnace with DX Cooling OA Rate [cfm] | 80.742 | 80.742 | 80.742 | 80.742 | 80.742 | 80.742 | 80.742 | 80.742 | 80.742 | 80.742 | 2023-10-09
US_MA_Split TN1 Furnace with DX Cooling OA Rate [cfm] | Split TN1 Furnace with DX Cooling OA Rate [cfm] | 54.9947 | 54.9947 | 54.9947 | 54.9947 | 54.9947 | 54.9947 | 54.9947 | 54.9947 | 54.9947 | 54.9947 | 2023-10-09
US_MA_Split TN2 Furnace with DX Cooling OA Rate [cfm] | Split TN2 Furnace with DX Cooling OA Rate [cfm] | 54.9947 | 54.9947 | 54.9947 | 54.9947 | 54.9947 | 54.9947 | 54.9947 | 54.9947 | 54.9947 | 54.9947 | 2023-10-09
US_MA_Split TNE Furnace with DX Cooling OA Rate [cfm] | Split TNE Furnace with DX Cooling OA Rate [cfm] | 54.9947 | 54.9947 | 54.9947 | 54.9947 | 54.9947 | 54.9947 | 54.9947 | 54.9947 | 54.9947 | 54.9947 | 2023-10-09
US_MA_Split TNW Furnace with DX Cooling OA Rate [cfm] | Split TNW Furnace with DX Cooling OA Rate [cfm] | 54.9947 | 54.9947 | 54.9947 | 54.9947 | 54.9947 | 54.9947 | 54.9947 | 54.9947 | 54.9947 | 54.9947 | 2023-10-09
US_MA_Split TS1 Furnace with DX Cooling OA Rate [cfm] | Split TS1 Furnace with DX Cooling OA Rate [cfm] | 54.9947 | 54.9947 | 54.9947 | 54.9947 | 54.9947 | 54.9947 | 54.9947 | 54.9947 | 54.9947 | 54.9947 | 2023-10-09
US_MA_Split TS2 Furnace with DX Cooling OA Rate [cfm] | Split TS2 Furnace with DX Cooling OA Rate [cfm] | 54.9947 | 54.9947 | 54.9947 | 54.9947 | 54.9947 | 54.9947 | 54.9947 | 54.9947 | 54.9947 | 54.9947 | 2023-10-09
US_MA_Split TSE Furnace with DX Cooling OA Rate [cfm] | Split TSE Furnace with DX Cooling OA Rate [cfm] | 54.9947 | 54.9947 | 54.9947 | 54.9947 | 54.9947 | 54.9947 | 54.9947 | 54.9947 | 54.9947 | 54.9947 | 2023-10-09
US_MA_Split TSW Furnace with DX Cooling OA Rate [cfm] | Split TSW Furnace with DX Cooling OA Rate [cfm] | 54.9947 | 54.9947 | 54.9947 | 54.9947 | 54.9947 | 54.9947 | 54.9947 | 54.9947 | 54.9947 | 54.9947 | 2023-10-09
US_MA_SPLIT GSW HEATING COIL Heating Capacity [kBtu/hr] | SPLIT GSW HEATING COIL Heating Capacity [kBtu/hr] | 19.1969 | 17.7784 | 18.9147 | 17.4764 | 19.3848 | 17.9419 | 19.7949 | 17.5833 | 19.4932 | 17.3399 | 2023-10-09
US_MA_SPLIT GNW HEATING COIL Heating Capacity [kBtu/hr] | SPLIT GNW HEATING COIL Heating Capacity [kBtu/hr] | 17.9218 | 16.5118 | 18.0696 | 16.639 | 18.7381 | 17.3039 | 18.484 | 16.3919 | 17.8751 | 15.8616 | 2023-10-09
US_MA_SPLIT OFFICE HEATING COIL Heating Capacity [kBtu/hr] | SPLIT OFFICE HEATING COIL Heating Capacity [kBtu/hr] | 20.3168 | 19.7908 | 20.2489 | 19.7087 | 20.6275 | 20.0868 | 21.7215 | 20.4661 | 21.5567 | 20.3602 | 2023-10-09
US_MA_SPLIT GNE HEATING COIL Heating Capacity [kBtu/hr] | SPLIT GNE HEATING COIL Heating Capacity [kBtu/hr] | 16.1776 | 14.78 | 16.2288 | 14.8144 | 17.0144 | 15.6031 | 16.7021 | 14.7461 | 15.9794 | 14.1081 | 2023-10-09
US_MA_SPLIT GN1 HEATING COIL Heating Capacity [kBtu/hr] | SPLIT GN1 HEATING COIL Heating Capacity [kBtu/hr] | 13.6339 | 12.2302 | 14.3033 | 12.8795 | 14.7475 | 13.317 | 14.5018 | 12.7993 | 14.0879 | 12.4496 | 2023-10-09
US_MA_SPLIT GN2 HEATING COIL Heating Capacity [kBtu/hr] | SPLIT GN2 HEATING COIL Heating Capacity [kBtu/hr] | 13.6007 | 12.1977 | 14.2731 | 12.8501 | 14.7184 | 13.2885 | 14.4622 | 12.7623 | 14.044 | 12.4087 | 2023-10-09
US_MA_SPLIT GS1 HEATING COIL Heating Capacity [kBtu/hr] | SPLIT GS1 HEATING COIL Heating Capacity [kBtu/hr] | 14.8942 | 13.4673 | 15.0561 | 13.6228 | 15.2793 | 13.8443 | 16.3235 | 14.4221 | 16.2359 | 14.3609 | 2023-10-09
US_MA_SPLIT GS2 HEATING COIL Heating Capacity [kBtu/hr] | SPLIT GS2 HEATING COIL Heating Capacity [kBtu/hr] | 14.9249 | 13.5386 | 15.0326 | 13.6416 | 15.2535 | 13.8603 | 16.3478 | 14.4882 | 16.2637 | 14.4291 | 2023-10-09
US_MA_SPLIT MSW HEATING COIL Heating Capacity [kBtu/hr] | SPLIT MSW HEATING COIL Heating Capacity [kBtu/hr] | 40.674 | 37.8076 | 42.6082 | 39.7386 | 43.2417 | 40.3698 | 46.6856 | 42.0176 | 47.0127 | 42.4712 | 2023-10-09
US_MA_SPLIT MNW HEATING COIL Heating Capacity [kBtu/hr] | SPLIT MNW HEATING COIL Heating Capacity [kBtu/hr] | 37.7025 | 34.8482 | 40.6798 | 37.8173 | 41.573 | 38.7116 | 43.4943 | 39.1065 | 43.4412 | 39.2285 | 2023-10-09
US_MA_SPLIT MSE HEATING COIL Heating Capacity [kBtu/hr] | SPLIT MSE HEATING COIL Heating Capacity [kBtu/hr] | 37.1006 | 34.2597 | 38.8681 | 36.0258 | 39.4548 | 36.6148 | 44.205 | 39.7231 | 44.327 | 39.9694 | 2023-10-09
US_MA_SPLIT MNE HEATING COIL Heating Capacity [kBtu/hr] | SPLIT MNE HEATING COIL Heating Capacity [kBtu/hr] | 33.4745 | 30.6496 | 36.08 | 33.2524 | 36.7806 | 33.9815 | 38.8684 | 34.8585 | 38.2145 | 34.3996 | 2023-10-09
US_MA_SPLIT MN1 HEATING COIL Heating Capacity [kBtu/hr] | SPLIT MN1 HEATING COIL Heating Capacity [kBtu/hr] | 27.2984 | 24.4924 | 30.5336 | 27.7127 | 31.1468 | 28.3235 | 31.9866 | 28.5294 | 31.7888 | 28.4567 | 2023-10-09
US_MA_SPLIT MN2 HEATING COIL Heating Capacity [kBtu/hr] | SPLIT MN2 HEATING COIL Heating Capacity [kBtu/hr] | 27.2189 | 24.4149 | 30.4574 | 27.6382 | 31.0749 | 28.2531 | 31.8805 | 28.4289 | 31.6678 | 28.3421 | 2023-10-09
US_MA_SPLIT MS1 HEATING COIL Heating Capacity [kBtu/hr] | SPLIT MS1 HEATING COIL Heating Capacity [kBtu/hr] | 30.5137 | 27.662 | 32.2434 | 29.4143 | 32.3095 | 29.4594 | 36.6719 | 32.7856 | 37.2727 | 33.4464 | 2023-10-09
US_MA_SPLIT MS2 HEATING COIL Heating Capacity [kBtu/hr] | SPLIT MS2 HEATING COIL Heating Capacity [kBtu/hr] | 30.5632 | 27.7118 | 32.2528 | 29.4012 | 32.3396 | 29.4902 | 36.7435 | 32.8568 | 37.3536 | 33.5227 | 2023-10-09
US_MA_SPLIT TSW HEATING COIL Heating Capacity [kBtu/hr] | SPLIT TSW HEATING COIL Heating Capacity [kBtu/hr] | 25.2574 | 23.8628 | 26.2091 | 24.8146 | 27.1984 | 25.8 | 28.8876 | 26.0257 | 28.7494 | 25.9475 | 2023-10-09
US_MA_SPLIT TNW HEATING COIL Heating Capacity [kBtu/hr] | SPLIT TNW HEATING COIL Heating Capacity [kBtu/hr] | 23.1743 | 21.7909 | 24.7454 | 23.3614 | 25.7846 | 24.3958 | 26.2374 | 23.6196 | 26.0221 | 23.4974 | 2023-10-09
US_MA_SPLIT TSE HEATING COIL Heating Capacity [kBtu/hr] | SPLIT TSE HEATING COIL Heating Capacity [kBtu/hr] | 23.491 | 22.0965 | 24.3863 | 22.9915 | 25.1065 | 23.713 | 27.5357 | 24.7698 | 27.3696 | 24.6838 | 2023-10-09
US_MA_SPLIT TNE HEATING COIL Heating Capacity [kBtu/hr] | SPLIT TNE HEATING COIL Heating Capacity [kBtu/hr] | 20.4866 | 19.0951 | 21.8358 | 20.4429 | 22.8621 | 21.484 | 23.4306 | 21.0067 | 22.6531 | 20.3803 | 2023-10-09
US_MA_SPLIT TN1 HEATING COIL Heating Capacity [kBtu/hr] | SPLIT TN1 HEATING COIL Heating Capacity [kBtu/hr] | 16.6701 | 15.2851 | 18.3365 | 16.9641 | 18.9456 | 17.5708 | 18.9961 | 17.1147 | 18.5312 | 16.7399 | 2023-10-09
US_MA_SPLIT TN2 HEATING COIL Heating Capacity [kBtu/hr] | SPLIT TN2 HEATING COIL Heating Capacity [kBtu/hr] | 16.675 | 15.2902 | 18.2511 | 16.8798 | 18.9019 | 17.5122 | 19.0057 | 17.1249 | 18.5305 | 16.7429 | 2023-10-09
US_MA_SPLIT TS1 HEATING COIL Heating Capacity [kBtu/hr] | SPLIT TS1 HEATING COIL Heating Capacity [kBtu/hr] | 19.7411 | 18.3312 | 20.5733 | 19.1645 | 20.9864 | 19.5753 | 23.3352 | 21.0242 | 23.4776 | 21.2004 | 2023-10-09
US_MA_SPLIT TS2 HEATING COIL Heating Capacity [kBtu/hr] | SPLIT TS2 HEATING COIL Heating Capacity [kBtu/hr] | 19.7823 | 18.3736 | 20.6101 | 19.1992 | 21.0068 | 19.5967 | 23.3953 | 21.0764 | 23.5403 | 21.2594 | 2023-10-09
US_MA_Split_GSW ERV Flag | Split_GSW ERV Flag | No | Yes | No | Yes | No | Yes | Yes | Yes | Yes | Yes | 2023-10-09
US_MA_Split_GNW ERV Flag | Split_GNW ERV Flag | No | Yes | No | Yes | No | Yes | Yes | Yes | Yes | Yes | 2023-10-09
US_MA_Split_GNE ERV Flag | Split_GNE ERV Flag | No | Yes | No | Yes | No | Yes | Yes | Yes | Yes | Yes | 2023-10-09
US_MA_Split_GN1 ERV Flag | Split_GN1 ERV Flag | No | Yes | No | Yes | No | Yes | Yes | Yes | Yes | Yes | 2023-10-09
US_MA_Split_GN2 ERV Flag | Split_GN2 ERV Flag | No | Yes | No | Yes | No | Yes | Yes | Yes | Yes | Yes | 2023-10-09
US_MA_Split_GS1 ERV Flag | Split_GS1 ERV Flag | No | Yes | No | Yes | No | Yes | Yes | Yes | Yes | Yes | 2023-10-09
US_MA_Split_GS2 ERV Flag | Split_GS2 ERV Flag | No | Yes | No | Yes | No | Yes | Yes | Yes | Yes | Yes | 2023-10-09
US_MA_Split_MSW ERV Flag | Split_MSW ERV Flag | No | Yes | No | Yes | No | Yes | Yes | Yes | Yes | Yes | 2023-10-09
US_MA_Split_MNW ERV Flag | Split_MNW ERV Flag | No | Yes | No | Yes | No | Yes | Yes | Yes | Yes | Yes | 2023-10-09
US_MA_Split_MSE ERV Flag | Split_MSE ERV Flag | No | Yes | No | Yes | No | Yes | Yes | Yes | Yes | Yes | 2023-10-09
US_MA_Split_MNE ERV Flag | Split_MNE ERV Flag | No | Yes | No | Yes | No | Yes | Yes | Yes | Yes | Yes | 2023-10-09
US_MA_Split_MN1 ERV Flag | Split_MN1 ERV Flag | No | Yes | No | Yes | No | Yes | Yes | Yes | Yes | Yes | 2023-10-09
US_MA_Split_MN2 ERV Flag | Split_MN2 ERV Flag | No | Yes | No | Yes | No | Yes | Yes | Yes | Yes | Yes | 2023-10-09
US_MA_Split_MS1 ERV Flag | Split_MS1 ERV Flag | No | Yes | No | Yes | No | Yes | Yes | Yes | Yes | Yes | 2023-10-09
US_MA_Split_MS2 ERV Flag | Split_MS2 ERV Flag | No | Yes | No | Yes | No | Yes | Yes | Yes | Yes | Yes | 2023-10-09
US_MA_Split_TSW ERV Flag | Split_TSW ERV Flag | No | Yes | No | Yes | No | Yes | Yes | Yes | Yes | Yes | 2023-10-09
US_MA_Split_TNW ERV Flag | Split_TNW ERV Flag | No | Yes | No | Yes | No | Yes | Yes | Yes | Yes | Yes | 2023-10-09
US_MA_Split_TSE ERV Flag | Split_TSE ERV Flag | No | Yes | No | Yes | No | Yes | Yes | Yes | Yes | Yes | 2023-10-09
US_MA_Split_TNE ERV Flag | Split_TNE ERV Flag | No | Yes | No | Yes | No | Yes | Yes | Yes | Yes | Yes | 2023-10-09
US_MA_Split_TN1 ERV Flag | Split_TN1 ERV Flag | No | Yes | No | Yes | No | Yes | Yes | Yes | Yes | Yes | 2023-10-09
US_MA_Split_TN2 ERV Flag | Split_TN2 ERV Flag | No | Yes | No | Yes | No | Yes | Yes | Yes | Yes | Yes | 2023-10-09
US_MA_Split_TS1 ERV Flag | Split_TS1 ERV Flag | No | Yes | No | Yes | No | Yes | Yes | Yes | Yes | Yes | 2023-10-09
US_MA_Split_TS2 ERV Flag | Split_TS2 ERV Flag | No | Yes | No | Yes | No | Yes | Yes | Yes | Yes | Yes | 2023-10-09
id | item | Zone5C(AK-Ketchikan-AK) ASHRAE901-state_STD2016 | Zone5C(AK-Ketchikan-AK) ASHRAE901-state_STD2019 | Zone6A(AK-Juneau-AK) ASHRAE901-state_STD2016 | Zone6A(AK-Juneau-AK) ASHRAE901-state_STD2019 | Zone7(AK-Anchorage-AK) ASHRAE901-state_STD2016 | Zone7(AK-Anchorage-AK) ASHRAE901-state_STD2019 | Zone8(AK-Fairbanks-AK) ASHRAE901-state_STD2016 | Zone8(AK-Fairbanks-AK) ASHRAE901-state_STD2019
AK_SO_PSZ-AC:1 Cooling Capacity [ton] | PSZ-AC:1 Cooling Capacity [ton] | 1.3227 | 1.2243 | 1.344 | 1.2408 | 1.3451 | 1.2317 | 1.3978 | 1.2844 |  |  | 2021-05-06
AK_SO_PSZ-AC:2 Cooling Capacity [ton] | PSZ-AC:2 Cooling Capacity [ton] | 1.6596 | 1.591 | 1.5232 | 1.4015 | 1.7522 | 1.5433 | 1.9644 | 1.766 |  |  | 2021-05-06
AK_SO_PSZ-AC:3 Cooling Capacity [ton] | PSZ-AC:3 Cooling Capacity [ton] | 0.88208 | 0.84057 | 0.93328 | 0.86473 | 1.0347 | 0.92088 | 1.0748 | 0.96556 |  |  | 2021-05-06
AK_SO_PSZ-AC:4 Cooling Capacity [ton] | PSZ-AC:4 Cooling Capacity [ton] | 0.86911 | 0.78721 | 0.93005 | 0.84185 | 0.89824 | 0.80125 | 1.0117 | 0.91399 |  |  | 2021-05-06
AK_SO_PSZ-AC:5 Cooling Capacity [ton] | PSZ-AC:5 Cooling Capacity [ton] | 1.0497 | 1.0078 | 1.079 | 1.0072 | 1.165 | 1.0404 | 1.2235 | 1.0945 |  |  | 2021-05-06
AK_SO_PSZ-AC:1 Supply Flow Rate [cfm] | PSZ-AC:1 Supply Flow Rate [cfm] | 593.2864 | 550.9088 | 614.4752 | 550.9088 | 614.4752 | 550.9088 | 635.664 | 572.0976 |  |  | 2021-05-06
AK_SO_PSZ-AC:2 Supply Flow Rate [cfm] | PSZ-AC:2 Supply Flow Rate [cfm] | 741.608 | 720.4192 | 678.0416 | 635.664 | 783.9856 | 699.2304 | 889.9296 | 805.1744 |  |  | 2021-05-06
AK_SO_PSZ-AC:3 Supply Flow Rate [cfm] | PSZ-AC:3 Supply Flow Rate [cfm] | 402.5872 | 381.3984 | 423.776 | 381.3984 | 466.1536 | 423.776 | 487.3424 | 444.9648 |  |  | 2021-05-06
AK_SO_PSZ-AC:4 Supply Flow Rate [cfm] | PSZ-AC:4 Supply Flow Rate [cfm] | 381.3984 | 360.2096 | 423.776 | 381.3984 | 402.5872 | 360.2096 | 444.9648 | 402.5872 |  |  | 2021-05-06
AK_SO_PSZ-AC:5 Supply Flow Rate [cfm] | PSZ-AC:5 Supply Flow Rate [cfm] | 466.1536 | 444.9648 | 487.3424 | 444.9648 | 529.72 | 466.1536 | 550.9088 | 487.3424 |  |  | 2021-05-06
AK_SO_PSZ-AC:1 OA Rate [cfm] | PSZ-AC:1 OA Rate [cfm] | 136.9178 | 136.9178 | 136.9178 | 136.9178 | 136.9178 | 136.9178 | 136.9178 | 136.9178 |  |  | 2021-05-06
AK_SO_PSZ-AC:2 OA Rate [cfm] | PSZ-AC:2 OA Rate [cfm] | 103.7925 | 103.7925 | 103.7925 | 103.7925 | 103.7925 | 103.7925 | 103.7925 | 103.7925 |  |  | 2021-05-06
AK_SO_PSZ-AC:3 OA Rate [cfm] | PSZ-AC:3 OA Rate [cfm] | 61.5711 | 61.5711 | 61.5711 | 61.5711 | 61.5711 | 61.5711 | 61.5711 | 61.5711 |  |  | 2021-05-06
AK_SO_PSZ-AC:4 OA Rate [cfm] | PSZ-AC:4 OA Rate [cfm] | 103.7925 | 103.7925 | 103.7925 | 103.7925 | 103.7925 | 103.7925 | 103.7925 | 103.7925 |  |  | 2021-05-06
AK_SO_PSZ-AC:5 OA Rate [cfm] | PSZ-AC:5 OA Rate [cfm] | 61.5711 | 61.5711 | 61.5711 | 61.5711 | 61.5711 | 61.5711 | 61.5711 | 61.5711 |  |  | 2021-05-06
AK_SO_PSZ-AC:1 heating Capacity [kBtu/hr] | PSZ-AC:1 heating Capacity [kBtu/hr] | 13.5177 | 13.5177 | 14.855 | 14.855 | 16.6605 | 16.6605 | 21.9816 | 21.9137 |  |  | 2021-05-06
AK_SO_PSZ-AC:2 heating Capacity [kBtu/hr] | PSZ-AC:2 heating Capacity [kBtu/hr] | 17.024 | 16.8366 | 19.2645 | 19.0448 | 22.0473 | 21.5067 | 26.9014 | 26.3139 |  |  | 2021-05-06
AK_SO_PSZ-AC:3 heating Capacity [kBtu/hr] | PSZ-AC:3 heating Capacity [kBtu/hr] | 10.3467 | 10.2431 | 11.7517 | 11.6262 | 13.4818 | 13.1744 | 16.2053 | 15.8771 |  |  | 2021-05-06
AK_SO_PSZ-AC:4 heating Capacity [kBtu/hr] | PSZ-AC:4 heating Capacity [kBtu/hr] | 16.9194 | 16.7607 | 19.1835 | 18.9978 | 22.0169 | 21.5619 | 26.9455 | 26.4595 |  |  | 2021-05-06
AK_SO_PSZ-AC:5 heating Capacity [kBtu/hr] | PSZ-AC:5 heating Capacity [kBtu/hr] | 10.3799 | 10.2726 | 11.7517 | 11.6262 | 13.4818 | 13.1744 | 16.1784 | 15.8547 |  |  | 2021-05-06
id | item | Zone5C(AK-Ketchikan-AK) ASHRAE901-state_STD2016 | Zone5C(AK-Ketchikan-AK) ASHRAE901-state_STD2019 | Zone6A(AK-Juneau-AK) ASHRAE901-state_STD2016 | Zone6A(AK-Juneau-AK) ASHRAE901-state_STD2019 | Zone7(AK-Anchorage-AK) ASHRAE901-state_STD2016 | Zone7(AK-Anchorage-AK) ASHRAE901-state_STD2019 | Zone8(AK-Fairbanks-AK) ASHRAE901-state_STD2016 | Zone8(AK-Fairbanks-AK) ASHRAE901-state_STD2019 |  |  | 2021-05-06
AK_LO_CAV_BAS Supply Flow Rate [cfm] | CAV_BAS Supply Flow Rate [cfm] | 11484.3296 | 10615.5888 | 11547.896 | 10679.1552 | 11717.4064 | 10806.288 | 11908.1056 | 10996.9872 |  |  | 2021-05-06
AK_LO_VAV_BOT WITH REHEAT Supply Flow Rate [cfm] | VAV_BOT WITH REHEAT Supply Flow Rate [cfm] | 18752.088 | 17840.9696 | 19154.6752 | 18095.2352 | 19536.0736 | 18243.5568 | 20404.8144 | 19069.92 |  |  | 2021-05-06
AK_LO_VAV_MID WITH REHEAT Supply Flow Rate [cfm] | VAV_MID WITH REHEAT Supply Flow Rate [cfm] | 172159.0003 | 163323.2706 | 177710.4659 | 167200.8211 | 181185.4291 | 168472.1491 | 191144.1651 | 177922.3539 |  |  | 2021-05-06
AK_LO_VAV_TOP WITH REHEAT Supply Flow Rate [cfm] | VAV_TOP WITH REHEAT Supply Flow Rate [cfm] | 17565.5152 | 16781.5296 | 18074.0464 | 16972.2288 | 18730.8992 | 17184.1168 | 20002.2272 | 18497.8224 |  |  | 2021-05-06
AK_LO_Supply Air Temp. Reset Flag | Supply Air Temp. Reset Flag | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  |  | 2021-05-06
AK_LO_CAV_BAS OA Rate [cfm] | CAV_BAS OA Rate [cfm] | 2542.8255 | 2542.8255 | 2542.8255 | 2542.8255 | 2542.8255 | 2542.8255 | 2542.8255 | 2542.8255 |  |  | 2021-05-06
AK_LO_VAV_BOT WITH REHEAT OA Rate [cfm] | VAV_BOT WITH REHEAT OA Rate [cfm] | 5377.8022 | 4302.174 | 5377.8022 | 4302.174 | 5377.8022 | 4302.174 | 5377.8022 | 4302.174 |  |  | 2021-05-06
AK_LO_VAV_MID WITH REHEAT OA Rate [cfm] | VAV_MID WITH REHEAT OA Rate [cfm] | 53777.9373 | 43021.7396 | 53777.9373 | 43021.7396 | 53777.9373 | 43021.7396 | 53777.9373 | 43021.7396 |  |  | 2021-05-06
AK_LO_VAV_TOP WITH REHEAT OA Rate [cfm] | VAV_TOP WITH REHEAT OA Rate [cfm] | 5377.8022 | 4302.174 | 5377.8022 | 4302.174 | 5377.8022 | 4302.174 | 5377.8022 | 4302.174 |  |  | 2021-05-06
AK_LO_AIRLOOP DATACENTER BASEMENT OA Rate [cfm] | AIRLOOP DATACENTER BASEMENT OA Rate [cfm] | 716.9654 | 716.9654 | 716.9654 | 716.9654 | 716.9654 | 716.9654 | 716.9654 | 716.9654 |  |  | 2021-05-06
AK_LO_VAV_bot_WITH_REHEAT ERV Flag | VAV_bot_WITH_REHEAT ERV Flag | No | No | Yes | Yes | Yes | Yes | Yes | Yes |  |  | 2021-05-06
AK_LO_VAV_mid_WITH_REHEAT ERV Flag | VAV_mid_WITH_REHEAT ERV Flag | No | No | Yes | Yes | Yes | Yes | Yes | Yes |  |  | 2021-05-06
AK_LO_VAV_top_WITH_REHEAT ERV Flag | VAV_top_WITH_REHEAT ERV Flag | No | No | Yes | Yes | Yes | Yes | Yes | Yes |  |  | 2021-05-06
AK_LO_COOLSYS1 CHILLER1 Capacity [ton] | COOLSYS1 CHILLER1 Capacity [ton] | 240.7353 | 231.0915 | 240.672 | 229.8673 | 239.88 | 226.9701 | 292.8603 | 272.1225 |  |  | 2021-05-06
AK_LO_COOLSYS1 CHILLER2 Capacity [ton] | COOLSYS1 CHILLER2 Capacity [ton] | 240.7353 | 231.0915 | 240.672 | 229.8673 | 239.88 | 226.9701 | 292.8603 | 272.1225 |  |  | 2021-05-06
AK_LO_TOWERWATERSYS COOLTOWER 1 Capacity [ton] | TOWERWATERSYS COOLTOWER 1 Capacity [ton] | 228.788 | 219.627 | 228.7223 | 218.4573 | 227.9731 | 215.7103 | 278.3257 | 258.6236 |  |  | 2021-05-06
AK_LO_TOWERWATERSYS COOLTOWER 2 Capacity [ton] | TOWERWATERSYS COOLTOWER 2 Capacity [ton] | 228.788 | 219.627 | 228.7223 | 218.4573 | 227.9731 | 215.7103 | 278.3257 | 258.6236 |  |  | 2021-05-06
AK_LO_HEATSYS1 BOILER Capacity [MMBTU/h] | HEATSYS1 BOILER Capacity [MMBTU/h] | 3907.3757 | 3513.1042 | 4396.1062 | 3879.2936 | 4988.8296 | 4301.8289 | 6375.9808 | 5456.1609 |  |  | 2021-05-06
AK_LO_COOLSYS1 PUMP Flow Rate [gal/min] | COOLSYS1 PUMP Flow Rate [gal/min] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 2021-05-06
AK_LO_COOLSYS1 CHILLER1 PUMP Flow Rate [gal/min] | COOLSYS1 CHILLER1 PUMP Flow Rate [gal/min] | 378.2838 | 360.5806 | 378.119 | 361.1987 | 376.8129 | 356.5879 | 460.5185 | 427.9365 |  |  | 2021-05-06
AK_LO_COOLSYS1 CHILLER2 PUMP Flow Rate [gal/min] | COOLSYS1 CHILLER2 PUMP Flow Rate [gal/min] | 378.2838 | 360.5806 | 378.119 | 361.1987 | 376.8129 | 356.5879 | 460.5185 | 427.9365 |  |  | 2021-05-06
AK_LO_COOLSYS1 PUMP SECONDARY Flow Rate [gal/min] | COOLSYS1 PUMP SECONDARY Flow Rate [gal/min] | 756.5692 | 721.1596 | 756.2395 | 722.3959 | 753.6258 | 713.1758 | 921.0385 | 855.8731 |  |  | 2021-05-06
AK_LO_HEATSYS1 PUMP Flow Rate [gal/min] | HEATSYS1 PUMP Flow Rate [gal/min] | 802.0406 | 721.1105 | 902.3589 | 796.2759 | 1024.0228 | 883.0072 | 1308.7548 | 1119.949 |  |  | 2021-05-06
AK_LO_TOWERWATERSYS PUMP Flow Rate [gal/min] | TOWERWATERSYS PUMP Flow Rate [gal/min] | 1360.6662 | 1306.1586 | 1360.3096 | 1299.2399 | 1355.8335 | 1282.8649 | 1655.2492 | 1538.071 |  |  | 2021-05-06
AK_LO_PLANT CIRC PUMP Flow Rate [gal/min] | PLANT CIRC PUMP Flow Rate [gal/min] | 204.512 | 203.6735 | 203.8193 | 202.6543 | 205.5866 | 203.786 | 215.5802 | 213.6798 |  |  | 2021-05-06
AK_LO_COOLSYS1 PUMP SECONDARY Pressure setpoint reset [yes,no] | COOLSYS1 PUMP SECONDARY Pressure setpoint reset [yes,no] | pump_ride_on_curve | pump_ride_on_curve | pump_ride_on_curve | pump_ride_on_curve | pump_ride_on_curve | pump_ride_on_curve | pump_ride_on_curve | pump_ride_on_curve |  |  | 2021-05-06
AK_LO_COOLSYS1 CHILLER1 PUMP Pump Power [hp] | COOLSYS1 CHILLER1 PUMP Pump Power [hp] | 2.0407 | 1.9259 | 2.0398 | 1.9292 | 2.0328 | 1.9046 | 2.4843 | 2.2857 |  |  | 2021-05-06
AK_LO_COOLSYS1 CHILLER2 PUMP Pump Power [hp] | COOLSYS1 CHILLER2 PUMP Pump Power [hp] | 2.0407 | 1.9259 | 2.0398 | 1.9292 | 2.0328 | 1.9046 | 2.4843 | 2.2857 |  |  | 2021-05-06
AK_LO_COOLSYS1 PUMP SECONDARY Pump Power [hp] | COOLSYS1 PUMP SECONDARY Pump Power [hp] | 12.2443 | 11.5557 | 12.2389 | 11.5755 | 12.1966 | 11.4277 | 14.906 | 13.7143 |  |  | 2021-05-06
AK_LO_HEATSYS1 PUMP Pump Power [hp] | HEATSYS1 PUMP Pump Power [hp] | 17.3366 | 15.4329 | 19.505 | 17.0416 | 22.1349 | 18.8977 | 28.2895 | 23.9687 |  |  | 2021-05-06
AK_LO_TOWERWATERSYS PUMP Pump Power [hp] | TOWERWATERSYS PUMP Pump Power [hp] | 24.3615 | 23.1541 | 24.3551 | 23.0314 | 24.275 | 22.7411 | 29.6364 | 27.2652 |  |  | 2021-05-06
AK_LO_PLANT CIRC PUMP Pump Power [hp] | PLANT CIRC PUMP Pump Power [hp] | 4.4131 | 4.3515 | 4.3982 | 4.3297 | 4.4362 | 4.3539 | 4.6519 | 4.5652 |  |  | 2021-05-06
AK_LO_Datacenter PLANT CIRC PUMP Pump Power [hp] | Datacenter PLANT CIRC PUMP Pump Power [hp] | 4.4131 | 4.3515 | 4.3982 | 4.3297 | 4.4362 | 4.3539 | 4.6519 | 4.5652 |  |  | 2021-05-06
AK_LO_ZN_VAV_BOXes_Max_Reheat_Water_Flow_GPM | ZN_VAV_BOXes_Max_Reheat_Water_Flow_GPM | 411.5065 | 395.6109 | 436.8503 | 418.2882 | 463.9398 | 433.0107 | 503.9413 | 471.2087 |  |  | 2021-05-06
AK_LO_COOLSYS1 PUMP SECONDARY VSD | COOLSYS1 PUMP SECONDARY VSD | No | No | No | No | No | No | No | No |  |  | 2021-05-06
AK_LO_HEATSYS1 PUMP VSD | HEATSYS1 PUMP VSD | No | No | No | No | No | No | No | No |  |  | 2021-05-06
AK_LO_DATACENTER BASEMENT Cooling Capacity [ton] | DATACENTER BASEMENT Cooling Capacity [ton] | 119.0955 | 118.7358 | 119.1757 | 118.8052 | 119.3649 | 118.9736 | 124.9545 | 124.5448 |  |  | 2021-05-06
AK_LO_DATACENTER BOT Cooling Capacity [ton] | DATACENTER BOT Cooling Capacity [ton] | 2.6606 | 2.6369 | 2.608 | 2.5668 | 2.6938 | 2.6189 | 2.8392 | 2.7598 |  |  | 2021-05-06
AK_LO_DATACENTER MID Cooling Capacity [ton] | DATACENTER MID Cooling Capacity [ton] | 25.483 | 25.2718 | 24.9937 | 24.5913 | 25.9264 | 25.1514 | 27.3629 | 26.5417 |  |  | 2021-05-06
AK_LO_DATACENTER TOP Cooling Capacity [ton] | DATACENTER TOP Cooling Capacity [ton] | 2.5705 | 2.5501 | 2.5249 | 2.4852 | 2.6108 | 2.5338 | 2.7598 | 2.6781 |  |  | 2021-05-06
id | item | Zone5C(AK-Ketchikan-AK) ASHRAE901-state_STD2016 | Zone5C(AK-Ketchikan-AK) ASHRAE901-state_STD2019 | Zone6A(AK-Juneau-AK) ASHRAE901-state_STD2016 | Zone6A(AK-Juneau-AK) ASHRAE901-state_STD2019 | Zone7(AK-Anchorage-AK) ASHRAE901-state_STD2016 | Zone7(AK-Anchorage-AK) ASHRAE901-state_STD2019 | Zone8(AK-Fairbanks-AK) ASHRAE901-state_STD2016 | Zone8(AK-Fairbanks-AK) ASHRAE901-state_STD2019 |  |  | 2021-05-06
AK_RS_PSZ-AC:1 Cooling Capacity [ton] | PSZ-AC:1 Cooling Capacity [ton] | 7.1262 | 6.4442 | 7.3868 | 6.866 | 7.1651 | 6.5407 | 8.2713 | 7.8027 |  |  | 2021-05-06
AK_RS_PSZ-AC:2 Cooling Capacity [ton] | PSZ-AC:2 Cooling Capacity [ton] | 31.2898 | 28.8781 | 31.9366 | 30.1509 | 31.4591 | 29.5564 | 35.4548 | 33.6356 |  |  | 2021-05-06
AK_RS_PSZ-AC:3 Cooling Capacity [ton] | PSZ-AC:3 Cooling Capacity [ton] | 5.4486 | 5.3057 | 5.3145 | 5.0572 | 5.6779 | 5.2492 | 6.1949 | 5.8098 |  |  | 2021-05-06
AK_RS_PSZ-AC:4 Cooling Capacity [ton] | PSZ-AC:4 Cooling Capacity [ton] | 4.3356 | 4.1757 | 4.2041 | 3.9302 | 4.5877 | 4.1387 | 5.1537 | 4.7667 |  |  | 2021-05-06
AK_RS_PSZ-AC:1 Supply Flow Rate [cfm] | PSZ-AC:1 Supply Flow Rate [cfm] | 3051.1872 | 2690.9776 | 3305.4528 | 2987.6208 | 3199.5088 | 2860.488 | 3580.9072 | 3263.0752 |  |  | 2021-05-06
AK_RS_PSZ-AC:2 Supply Flow Rate [cfm] | PSZ-AC:2 Supply Flow Rate [cfm] | 14090.552 | 13009.9232 | 14387.1952 | 13582.0208 | 14154.1184 | 13306.5664 | 14789.7824 | 13942.2304 |  |  | 2021-05-06
AK_RS_PSZ-AC:3 Supply Flow Rate [cfm] | PSZ-AC:3 Supply Flow Rate [cfm] | 2457.9008 | 2394.3344 | 2394.3344 | 2267.2016 | 2563.8448 | 2373.1456 | 2796.9216 | 2606.2224 |  |  | 2021-05-06
AK_RS_PSZ-AC:4 Supply Flow Rate [cfm] | PSZ-AC:4 Supply Flow Rate [cfm] | 1949.3696 | 1885.8032 | 1885.8032 | 1758.6704 | 2055.3136 | 1864.6144 | 2288.3904 | 2097.6912 |  |  | 2021-05-06
AK_RS_PSZ-AC:1 OA Rate [cfm] | PSZ-AC:1 OA Rate [cfm] | 490.669 | 490.669 | 490.669 | 490.669 | 490.669 | 490.669 | 490.669 | 490.669 |  |  | 2021-05-06
AK_RS_PSZ-AC:2 OA Rate [cfm] | PSZ-AC:2 OA Rate [cfm] | 4005.1282 | 4005.1282 | 4005.1282 | 4005.1282 | 4005.1282 | 4005.1282 | 4005.1282 | 4005.1282 |  |  | 2021-05-06
AK_RS_PSZ-AC:3 OA Rate [cfm] | PSZ-AC:3 OA Rate [cfm] | 377.3937 | 377.3937 | 377.3937 | 377.3937 | 377.3937 | 377.3937 | 377.3937 | 377.3937 |  |  | 2021-05-06
AK_RS_PSZ-AC:4 OA Rate [cfm] | PSZ-AC:4 OA Rate [cfm] | 377.3937 | 377.3937 | 377.3937 | 377.3937 | 377.3937 | 377.3937 | 377.3937 | 377.3937 |  |  | 2021-05-06
AK_RS_PSZ-AC:1 OA Damper [gravity, motorized] | PSZ-AC:1 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | motorized | motorized | motorized | motorized |  |  | 2021-05-06
AK_RS_PSZ-AC:2 OA Damper [gravity, motorized] | PSZ-AC:2 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | motorized | motorized | motorized | motorized |  |  | 2021-05-06
AK_RS_PSZ-AC:3 OA Damper [gravity, motorized] | PSZ-AC:3 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | motorized | motorized | motorized | motorized |  |  | 2021-05-06
AK_RS_PSZ-AC:4 OA Damper [gravity, motorized] | PSZ-AC:4 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | motorized | motorized | motorized | motorized |  |  | 2021-05-06
AK_RS_PSZ-AC:1 Heating Capacity [kBtu/hr] | PSZ-AC:1 Heating Capacity [kBtu/hr] | 143.7116 | 126.085 | 153.4825 | 141.039 | 155.2823 | 143.2055 | 187.6558 | 173.9313 |  |  | 2021-05-06
AK_RS_PSZ-AC:2 Heating Capacity [kBtu/hr] | PSZ-AC:2 Heating Capacity [kBtu/hr] | 748.2549 | 709.0106 | 802.1991 | 769.2912 | 844.9291 | 810.9804 | 1006.9687 | 973.2906 |  |  | 2021-05-06
AK_RS_PSZ-AC:3 Heating Capacity [kBtu/hr] | PSZ-AC:3 Heating Capacity [kBtu/hr] | 114.2764 | 111.8872 | 115.8956 | 111.5869 | 126.3965 | 119.2658 | 147.3391 | 140.6806 |  |  | 2021-05-06
AK_RS_PSZ-AC:4 Heating Capacity [kBtu/hr] | PSZ-AC:4 Heating Capacity [kBtu/hr] | 95.6828 | 93.0105 | 97.3031 | 92.7167 | 108.2681 | 100.8014 | 129.0699 | 122.2392 |  |  | 2021-05-06
id | item | Zone5C(AK-Ketchikan-AK) ASHRAE901-state_STD2016 | Zone5C(AK-Ketchikan-AK) ASHRAE901-state_STD2019 | Zone6A(AK-Juneau-AK) ASHRAE901-state_STD2016 | Zone6A(AK-Juneau-AK) ASHRAE901-state_STD2019 | Zone7(AK-Anchorage-AK) ASHRAE901-state_STD2016 | Zone7(AK-Anchorage-AK) ASHRAE901-state_STD2019 | Zone8(AK-Fairbanks-AK) ASHRAE901-state_STD2016 | Zone8(AK-Fairbanks-AK) ASHRAE901-state_STD2019 |  |  | 2021-05-06
AK_PS_VAV_POD_1 Cooling Capacity [ton] | VAV_POD_1 Cooling Capacity [ton] | 12.9192 | 12.4729 | 12.7886 | 12.1108 | 13.5978 | 12.5145 | 17.1989 | 16.0018 |  |  | 2021-05-06
AK_PS_VAV_POD_2 Cooling Capacity [ton] | VAV_POD_2 Cooling Capacity [ton] | 12.7465 | 12.2921 | 12.5596 | 11.8859 | 13.3423 | 12.2877 | 16.8903 | 15.7222 |  |  | 2021-05-06
AK_PS_VAV_POD_3 Cooling Capacity [ton] | VAV_POD_3 Cooling Capacity [ton] | 11.7375 | 11.2121 | 11.5776 | 10.8291 | 12.3803 | 11.2379 | 15.7616 | 14.4622 |  |  | 2021-05-06
AK_PS_VAV_OTHER Cooling Capacity [ton] | VAV_OTHER Cooling Capacity [ton] | 15.139 | 14.2105 | 15.9101 | 14.5565 | 16.3669 | 14.5808 | 19.1852 | 17.2178 |  |  | 2021-05-06
AK_PS_PSZ-AC_1:6 Cooling Capacity [ton] | PSZ-AC_1:6 Cooling Capacity [ton] | 5.966 | 5.7208 | 5.9646 | 5.6983 | 5.9406 | 5.6301 | 6.794 | 6.4828 |  |  | 2021-05-06
AK_PS_PSZ-AC_2:5 Cooling Capacity [ton] | PSZ-AC_2:5 Cooling Capacity [ton] | 2.779 | 2.874 | 3.0588 | 2.999 | 3.2477 | 3.1885 | 3.7718 | 3.6951 |  |  | 2021-05-06
AK_PS_PSZ-AC_2:7 Cooling Capacity [ton] | PSZ-AC_2:7 Cooling Capacity [ton] | 7.0043 | 7.0043 | 7.0043 | 7.0043 | 7.0043 | 7.0043 | 7.9406 | 7.9406 |  |  | 2021-05-06
AK_PS_VAV_POD_1 Supply Flow Rate [cfm] | VAV_POD_1 Supply Flow Rate [cfm] | 5805.7312 | 5615.032 | 5763.3536 | 5445.5216 | 6123.5632 | 5636.2208 | 6504.9616 | 6059.9968 |  |  | 2021-05-06
AK_PS_VAV_POD_2 Supply Flow Rate [cfm] | VAV_POD_2 Supply Flow Rate [cfm] | 5742.1648 | 5530.2768 | 5657.4096 | 5360.7664 | 5996.4304 | 5530.2768 | 6399.0176 | 5954.0528 |  |  | 2021-05-06
AK_PS_VAV_POD_3 Supply Flow Rate [cfm] | VAV_POD_3 Supply Flow Rate [cfm] | 5276.0112 | 5042.9344 | 5212.4448 | 4873.424 | 5572.6544 | 5064.1232 | 5954.0528 | 5487.8992 |  |  | 2021-05-06
AK_PS_VAV_OTHER Supply Flow Rate [cfm] | VAV_OTHER Supply Flow Rate [cfm] | 6822.7936 | 6399.0176 | 7161.8144 | 6547.3392 | 7373.7024 | 6568.528 | 7966.9888 | 7204.192 |  |  | 2021-05-06
AK_PS_PSZ-AC_2:5 Supply Flow Rate [cfm] | PSZ-AC_2:5 Supply Flow Rate [cfm] | 1250.1392 | 1292.5168 | 1377.272 | 1356.0832 | 1462.0272 | 1440.8384 | 1525.5936 | 1483.216 |  |  | 2021-05-06
AK_PS_PSZ-AC_1:6 Supply Flow Rate [cfm] | PSZ-AC_1:6 Supply Flow Rate [cfm] | 2415.5232 | 2309.5792 | 2457.9008 | 2351.9568 | 2500.2784 | 2351.9568 | 2542.656 | 2415.5232 |  |  | 2021-05-06
AK_PS_PSZ-AC_2:7 Supply Flow Rate [cfm] | PSZ-AC_2:7 Supply Flow Rate [cfm] | 3157.1312 | 3157.1312 | 3157.1312 | 3157.1312 | 3157.1312 | 3157.1312 | 3157.1312 | 3157.1312 |  |  | 2021-05-06
AK_PS_Supply Air Temp. Reset Flag | Supply Air Temp. Reset Flag | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  |  | 2021-05-06
AK_PS_VAV_POD_1 OA Rate [cfm] | VAV_POD_1 OA Rate [cfm] | 5812.7871 | 5614.8413 | 5755.4714 | 5451.8147 | 6121.2324 | 5633.5722 | 6504.5166 | 6053.5554 |  |  | 2021-05-06
AK_PS_VAV_POD_2 OA Rate [cfm] | VAV_POD_2 OA Rate [cfm] | 5737.0159 | 5533.4551 | 5652.1548 | 5350.5746 | 6006.2196 | 5531.4422 | 6387.7452 | 5947.7597 |  |  | 2021-05-06
AK_PS_VAV_POD_3 OA Rate [cfm] | VAV_POD_3 OA Rate [cfm] | 5283.7663 | 5047.2569 | 5211.788 | 4874.886 | 5572.2306 | 5058.8896 | 5962.6767 | 5422.002 |  |  | 2021-05-06
AK_PS_VAV_OTHER OA Rate [cfm] | VAV_OTHER OA Rate [cfm] | 3736.1787 | 2988.8921 | 3736.1787 | 2988.8921 | 3736.1787 | 2988.8921 | 3736.1787 | 2988.8921 |  |  | 2021-05-06
AK_PS_PSZ-AC_2:5 OA Rate [cfm] | PSZ-AC_2:5 OA Rate [cfm] | 1152.7343 | 1152.7343 | 1152.7343 | 1152.7343 | 1152.7343 | 1152.7343 | 1152.7343 | 1152.7343 |  |  | 2021-05-06
AK_PS_PSZ-AC_1:6 OA Rate [cfm] | PSZ-AC_1:6 OA Rate [cfm] | 539.9118 | 539.9118 | 539.9118 | 539.9118 | 539.9118 | 539.9118 | 539.9118 | 539.9118 |  |  | 2021-05-06
AK_PS_PSZ-AC_2:7 OA Rate [cfm] | PSZ-AC_2:7 OA Rate [cfm] | 3153.0841 | 3153.0841 | 3153.0841 | 3153.0841 | 3153.0841 | 3153.0841 | 3153.0841 | 3153.0841 |  |  | 2021-05-06
AK_PS_VAV_POD_1 OA Damper [gravity, motorized] | VAV_POD_1 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | motorized | motorized | motorized | motorized |  |  | 2021-05-06
AK_PS_VAV_POD_2 OA Damper [gravity, motorized] | VAV_POD_2 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | motorized | motorized | motorized | motorized |  |  | 2021-05-06
AK_PS_VAV_POD_3 OA Damper [gravity, motorized] | VAV_POD_3 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | motorized | motorized | motorized | motorized |  |  | 2021-05-06
AK_PS_VAV_OTHER OA Damper [gravity, motorized] | VAV_OTHER OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | motorized | motorized | motorized | motorized |  |  | 2021-05-06
AK_PS_PSZ-AC_2:5 OA Damper [gravity, motorized] | PSZ-AC_2:5 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | motorized | motorized | motorized | motorized |  |  | 2021-05-06
AK_PS_PSZ-AC_1:6 OA Damper [gravity, motorized] | PSZ-AC_1:6 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | motorized | motorized | motorized | motorized |  |  | 2021-05-06
AK_PS_PSZ-AC_2:7 OA Damper [gravity, motorized] | PSZ-AC_2:7 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | motorized | motorized | motorized | motorized |  |  | 2021-05-06
AK_PS_VAV_POD_1 (economizer) | VAV_POD_1 (economizer) | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb |  |  | 2021-05-06
AK_PS_VAV_POD_2 (economizer) | VAV_POD_2 (economizer) | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb |  |  | 2021-05-06
AK_PS_VAV_POD_3 (economizer) | VAV_POD_3 (economizer) | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb |  |  | 2021-05-06
AK_PS_VAV_OTHER (economizer) | VAV_OTHER (economizer) | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb |  |  | 2021-05-06
AK_PS_PSZ-AC_2:5 (economizer) | PSZ-AC_2:5 (economizer) | No | No | No | No | No | No | No | No |  |  | 2021-05-06
AK_PS_PSZ-AC_1:6 (economizer) | PSZ-AC_1:6 (economizer) | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb |  |  | 2021-05-06
AK_PS_PSZ-AC_2:7 (economizer) | PSZ-AC_2:7 (economizer) | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb |  |  | 2021-05-06
AK_PS_VAV_Pod_1_ERV Flag | VAV_Pod_1_ERV Flag | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  |  | 2021-05-06
AK_PS_VAV_Pod_2_ERV Flag | VAV_Pod_2_ERV Flag | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  |  | 2021-05-06
AK_PS_VAV_Pod_3_ERV Flag | VAV_Pod_3_ERV Flag | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  |  | 2021-05-06
AK_PS_VAV_OTHER_ERV Flag | VAV_OTHER_ERV Flag | No | No | Yes | Yes | Yes | Yes | Yes | Yes |  |  | 2021-05-06
AK_PS_PSZ_AC_2_5_ERV Flag | PSZ_AC_2_5_ERV Flag | No | No | Yes | Yes | Yes | Yes | Yes | Yes |  |  | 2021-05-06
AK_PS_PSZ_AC_2_7_ERV Flag | PSZ_AC_2_7_ERV Flag | No | No | Yes | Yes | Yes | Yes | Yes | Yes |  |  | 2021-05-06
AK_PS_HEATSYS1 Capacity [MMBTU/h] | HEATSYS1 Capacity [MMBTU/h] | 0.9659 | 0.92512 | 1.0739 | 1.0212 | 1.2529 | 1.1601 | 1.6966 | 1.5934 |  |  | 2021-05-06
AK_PS_HEATSYS1 Flow Rate [gal/min] | HEATSYS1 Flow Rate [gal/min] | 99.1317 | 94.9468 | 110.2143 | 104.8093 | 128.587 | 119.0667 | 174.1221 | 163.5325 |  |  | 2021-05-06
AK_PS_VAV_POD_1 Fan Power [hp] | VAV_POD_1 Fan Power [hp] | 8.58 | 8.2836 | 8.4933 | 8.0431 | 9.0307 | 8.3112 | 9.5989 | 8.9308 |  |  | 2021-05-06
AK_PS_VAV_POD_2 Fan Power [hp] | VAV_POD_2 Fan Power [hp] | 8.4653 | 8.1635 | 8.3411 | 7.8937 | 8.861 | 8.1605 | 9.4266 | 8.7747 |  |  | 2021-05-06
AK_PS_VAV_POD_3 Fan Power [hp] | VAV_POD_3 Fan Power [hp] | 7.7951 | 7.4462 | 7.689 | 7.1919 | 8.2221 | 7.4634 | 8.7968 | 8.089 |  |  | 2021-05-06
AK_PS_VAV_OTHER Fan Power [hp] | VAV_OTHER Fan Power [hp] | 9.978 | 9.4375 | 10.4862 | 9.6673 | 10.7873 | 9.6835 | 11.6633 | 10.5439 |  |  | 2021-05-06
AK_PS_HEATSYS1 Pump Power [hp] | HEATSYS1 Pump Power [hp] | 2.1428 | 2.032 | 2.3823 | 2.2431 | 2.7795 | 2.5482 | 3.7637 | 3.4998 |  |  | 2021-05-06
AK_PS_PSZ-AC_1:6 Heating Capacity [kBtu/hr] | PSZ-AC_1:6 Heating Capacity [kBtu/hr] | 199.5815 | 191.0629 | 208.2912 | 199.002 | 217.9587 | 207.0534 | 239.1654 | 228.7632 |  |  | 2021-05-06
AK_PS_PSZ-AC_2:5 Heating Capacity [kBtu/hr] | PSZ-AC_2:5 Heating Capacity [kBtu/hr] | 117.4364 | 119.0166 | 133.3663 | 132.3694 | 151.6716 | 150.6885 | 194.451 | 193.2558 |  |  | 2021-05-06
AK_PS_PSZ-AC_2:7 Heating Capacity [kBtu/hr] | PSZ-AC_2:7 Heating Capacity [kBtu/hr] | 311.2999 | 311.2999 | 342.0969 | 342.0969 | 383.6759 | 383.6759 | 495.3649 | 495.3649 |  |  | 2021-05-06
AK_PS_ZN_VAV_BOXes_Max_Reheat_Water_Flow_GPM | ZN_VAV_BOXes_Max_Reheat_Water_Flow_GPM | 65.7299 | 63.0418 | 69.5603 | 66.8128 | 75.4108 | 70.7284 | 87.4591 | 83.7803 |  |  | 2021-05-06
id | item | Zone5C(AK-Ketchikan-AK) ASHRAE901-state_STD2016 | Zone5C(AK-Ketchikan-AK) ASHRAE901-state_STD2019 | Zone6A(AK-Juneau-AK) ASHRAE901-state_STD2016 | Zone6A(AK-Juneau-AK) ASHRAE901-state_STD2019 | Zone7(AK-Anchorage-AK) ASHRAE901-state_STD2016 | Zone7(AK-Anchorage-AK) ASHRAE901-state_STD2019 | Zone8(AK-Fairbanks-AK) ASHRAE901-state_STD2016 | Zone8(AK-Fairbanks-AK) ASHRAE901-state_STD2019 |  |  | 2021-05-06
AK_SH_SAC_FRONTOFFICE Cooling Capacity [ton] | SAC_FRONTOFFICE Cooling Capacity [ton] | 1.6659 | 1.571 | 1.6175 | 1.5067 | 1.6879 | 1.549 | 1.8144 | 1.6861 |  |  | 2021-05-06
AK_SH_SAC_FRONTLOUNGE Cooling Capacity [ton] | SAC_FRONTLOUNGE Cooling Capacity [ton] | 3.6064 | 3.5929 | 3.7752 | 3.5781 | 3.6792 | 3.47 | 4.2018 | 3.9769 |  |  | 2021-05-06
AK_SH_SAC_MEETINGROOM Cooling Capacity [ton] | SAC_MEETINGROOM Cooling Capacity [ton] | 2.037 | 1.9777 | 2.0085 | 1.9402 | 1.971 | 1.8888 | 2.2346 | 2.149 |  |  | 2021-05-06
AK_SH_SAC_EXC_EMPLGE_RESTRM Cooling Capacity [ton] | SAC_EXC_EMPLGE_RESTRM Cooling Capacity [ton] | 4.7738 | 4.7353 | 4.7838 | 4.7337 | 4.8544 | 4.7852 | 5.0668 | 5.0035 |  |  | 2021-05-06
AK_SH_SAC_FO_ADDAQ SUPPLY FAN Supply Flow Rate [cfm] | SAC_FO_ADDAQ SUPPLY FAN Supply Flow Rate [cfm] | 741.608 | 699.2304 | 720.4192 | 678.0416 | 762.7968 | 699.2304 | 805.1744 | 741.608 |  |  | 2021-05-06
AK_SH_SAC_FL_ADDAQ SUPPLY FAN Supply Flow Rate [cfm] | SAC_FL_ADDAQ SUPPLY FAN Supply Flow Rate [cfm] | 1610.3488 | 1525.5936 | 1631.5376 | 1546.7824 | 1631.5376 | 1546.7824 | 1716.2928 | 1631.5376 |  |  | 2021-05-06
AK_SH_SAC_MR_ADDAQ SUPPLY FAN Supply Flow Rate [cfm] | SAC_MR_ADDAQ SUPPLY FAN Supply Flow Rate [cfm] | 805.1744 | 762.7968 | 805.1744 | 762.7968 | 805.1744 | 762.7968 | 847.552 | 805.1744 |  |  | 2021-05-06
AK_SH_SAC_EXC_ADDAQ SUPPLY FAN Supply Flow Rate [cfm] | SAC_EXC_ADDAQ SUPPLY FAN Supply Flow Rate [cfm] | 2140.0688 | 2140.0688 | 2161.2576 | 2140.0688 | 2182.4464 | 2161.2576 | 2267.2016 | 2224.824 |  |  | 2021-05-06
AK_SH_SAC_Exc_EmpLge_RestRm OA Rate [cfm] | SAC_Exc_EmpLge_RestRm OA Rate [cfm] | 199.9928 | 199.9928 | 199.9928 | 199.9928 | 199.9928 | 199.9928 | 199.9928 | 199.9928 |  |  | 2021-05-06
AK_SH_SAC_FrontLounge OA Rate [cfm] | SAC_FrontLounge OA Rate [cfm] | 500.0133 | 500.0133 | 500.0133 | 500.0133 | 500.0133 | 500.0133 | 500.0133 | 500.0133 |  |  | 2021-05-06
AK_SH_SAC_FrontOffice OA Rate [cfm] | SAC_FrontOffice OA Rate [cfm] | 119.2938 | 119.2938 | 119.2938 | 119.2938 | 119.2938 | 119.2938 | 119.2938 | 119.2938 |  |  | 2021-05-06
AK_SH_SAC_MeetingRoom OA Rate [cfm] | SAC_MeetingRoom OA Rate [cfm] | 267.7629 | 267.7629 | 267.7629 | 267.7629 | 267.7629 | 267.7629 | 267.7629 | 267.7629 |  |  | 2021-05-06
AK_SH_SAC_FrontLounge OA Damper [gravity, motorized] | SAC_FrontLounge OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | motorized | motorized | motorized | motorized |  |  | 2021-05-06
AK_SH_SAC_FrontOffice (economizer) | SAC_FrontOffice (economizer) | No | No | No | No | No | No | No | No |  |  | 2021-05-06
AK_SH_SAC_FrontLounge (economizer) | SAC_FrontLounge (economizer) | No | No | No | No | No | No | No | No |  |  | 2021-05-06
AK_SH_SAC_MeetingRoom (economizer) | SAC_MeetingRoom (economizer) | No | No | No | No | No | No | No | No |  |  | 2021-05-06
AK_SH_SAC_Exc_EmpLge_RestRm (economizer) | SAC_Exc_EmpLge_RestRm (economizer) | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb |  |  | 2021-05-06
AK_SH_SAC_FRONTOFFICE Heating Capacity [kBtu/hr] | SAC_FRONTOFFICE Heating Capacity [kBtu/hr] | 34.9286 | 33.3593 | 35.3446 | 33.5091 | 37.9975 | 35.705 | 43.7499 | 41.5327 |  |  | 2021-05-06
AK_SH_SAC_FRONTLOUNGE Heating Capacity [kBtu/hr] | SAC_FRONTLOUNGE Heating Capacity [kBtu/hr] | 90.0219 | 86.7095 | 96.2029 | 92.8738 | 102.4408 | 98.9149 | 122.725 | 119.2425 |  |  | 2021-05-06
AK_SH_SAC_MEETINGROOM Heating Capacity [kBtu/hr] | SAC_MEETINGROOM Heating Capacity [kBtu/hr] | 45.8147 | 44.8754 | 48.6962 | 47.6091 | 52.239 | 50.9336 | 62.8455 | 61.5316 |  |  | 2021-05-06
AK_SH_SAC_EXC_EMPLGE_RESTRM Heating Capacity [kBtu/hr] | SAC_EXC_EMPLGE_RESTRM Heating Capacity [kBtu/hr] | 91.2904 | 90.6545 | 93.5699 | 92.7405 | 97.1082 | 95.966 | 106.1764 | 105.0718 |  |  | 2021-05-06
id | item | Zone5C(AK-Ketchikan-AK) ASHRAE901-state_STD2016 | Zone5C(AK-Ketchikan-AK) ASHRAE901-state_STD2019 | Zone6A(AK-Juneau-AK) ASHRAE901-state_STD2016 | Zone6A(AK-Juneau-AK) ASHRAE901-state_STD2019 | Zone7(AK-Anchorage-AK) ASHRAE901-state_STD2016 | Zone7(AK-Anchorage-AK) ASHRAE901-state_STD2019 | Zone8(AK-Fairbanks-AK) ASHRAE901-state_STD2016 | Zone8(AK-Fairbanks-AK) ASHRAE901-state_STD2019 |  |  | 2021-05-06
AK_MA_SPLIT GSW COOLING COIL Cooling Capacity [ton] | SPLIT GSW COOLING COIL Cooling Capacity [ton] | 0.59118 | 0.57236 | 0.62675 | 0.58639 | 0.69054 | 0.61191 | 0.77118 | 0.69485 |  |  | 2021-05-06
AK_MA_SPLIT GNW COOLING COIL Cooling Capacity [ton] | SPLIT GNW COOLING COIL Cooling Capacity [ton] | 0.41172 | 0.39745 | 0.49779 | 0.46754 | 0.52072 | 0.46738 | 0.59664 | 0.54471 |  |  | 2021-05-06
AK_MA_SPLIT OFFICE COOLING COIL Cooling Capacity [ton] | SPLIT OFFICE COOLING COIL Cooling Capacity [ton] | 1.4117 | 1.2487 | 1.5009 | 1.3051 | 1.5774 | 1.3339 | 1.7201 | 1.5038 |  |  | 2021-05-06
AK_MA_SPLIT GNE COOLING COIL Cooling Capacity [ton] | SPLIT GNE COOLING COIL Cooling Capacity [ton] | 0.30895 | 0.29497 | 0.39092 | 0.36156 | 0.43237 | 0.37693 | 0.49773 | 0.47127 |  |  | 2021-05-06
AK_MA_SPLIT GN1 COOLING COIL Cooling Capacity [ton] | SPLIT GN1 COOLING COIL Cooling Capacity [ton] | 0.28164 | 0.27197 | 0.3411 | 0.32391 | 0.34537 | 0.31547 | 0.40271 | 0.37567 |  |  | 2021-05-06
AK_MA_SPLIT GN2 COOLING COIL Cooling Capacity [ton] | SPLIT GN2 COOLING COIL Cooling Capacity [ton] | 0.27943 | 0.26983 | 0.33875 | 0.32174 | 0.3425 | 0.31336 | 0.39976 | 0.37308 |  |  | 2021-05-06
AK_MA_SPLIT GS1 COOLING COIL Cooling Capacity [ton] | SPLIT GS1 COOLING COIL Cooling Capacity [ton] | 0.51357 | 0.49566 | 0.49657 | 0.46004 | 0.55532 | 0.48789 | 0.62569 | 0.56809 |  |  | 2021-05-06
AK_MA_SPLIT GS2 COOLING COIL Cooling Capacity [ton] | SPLIT GS2 COOLING COIL Cooling Capacity [ton] | 0.55668 | 0.53295 | 0.54113 | 0.49837 | 0.60105 | 0.5268 | 0.67398 | 0.6104 |  |  | 2021-05-06
AK_MA_SPLIT MSW COOLING COIL Cooling Capacity [ton] | SPLIT MSW COOLING COIL Cooling Capacity [ton] | 1.5833 | 1.5421 | 1.6358 | 1.5438 | 1.8548 | 1.6691 | 2.0248 | 1.8423 |  |  | 2021-05-06
AK_MA_SPLIT MNW COOLING COIL Cooling Capacity [ton] | SPLIT MNW COOLING COIL Cooling Capacity [ton] | 1.2006 | 1.1691 | 1.3735 | 1.3007 | 1.4966 | 1.3625 | 1.6581 | 1.5244 |  |  | 2021-05-06
AK_MA_SPLIT MSE COOLING COIL Cooling Capacity [ton] | SPLIT MSE COOLING COIL Cooling Capacity [ton] | 1.5854 | 1.5388 | 1.5688 | 1.4589 | 1.8001 | 1.5864 | 2.0089 | 1.8091 |  |  | 2021-05-06
AK_MA_SPLIT MNE COOLING COIL Cooling Capacity [ton] | SPLIT MNE COOLING COIL Cooling Capacity [ton] | 0.96199 | 0.93159 | 1.117 | 1.0473 | 1.259 | 1.128 | 1.4068 | 1.2798 |  |  | 2021-05-06
AK_MA_SPLIT MN1 COOLING COIL Cooling Capacity [ton] | SPLIT MN1 COOLING COIL Cooling Capacity [ton] | 0.73393 | 0.71634 | 0.85804 | 0.82382 | 0.90144 | 0.83821 | 1.0269 | 0.96557 |  |  | 2021-05-06
AK_MA_SPLIT MN2 COOLING COIL Cooling Capacity [ton] | SPLIT MN2 COOLING COIL Cooling Capacity [ton] | 0.72731 | 0.70991 | 0.85105 | 0.81736 | 0.89291 | 0.83082 | 1.0182 | 0.95801 |  |  | 2021-05-06
AK_MA_SPLIT MS1 COOLING COIL Cooling Capacity [ton] | SPLIT MS1 COOLING COIL Cooling Capacity [ton] | 1.366 | 1.3255 | 1.294 | 1.2064 | 1.4857 | 1.3178 | 1.6487 | 1.4943 |  |  | 2021-05-06
AK_MA_SPLIT MS2 COOLING COIL Cooling Capacity [ton] | SPLIT MS2 COOLING COIL Cooling Capacity [ton] | 1.3712 | 1.3306 | 1.2995 | 1.2116 | 1.492 | 1.3233 | 1.6548 | 1.4998 |  |  | 2021-05-06
AK_MA_SPLIT TSW COOLING COIL Cooling Capacity [ton] | SPLIT TSW COOLING COIL Cooling Capacity [ton] | 0.94414 | 0.91662 | 0.96376 | 0.91323 | 1.0773 | 0.97354 | 1.1881 | 1.0861 |  |  | 2021-05-06
AK_MA_SPLIT TNW COOLING COIL Cooling Capacity [ton] | SPLIT TNW COOLING COIL Cooling Capacity [ton] | 0.70842 | 0.69104 | 0.82908 | 0.78873 | 0.8864 | 0.81106 | 0.9925 | 0.91781 |  |  | 2021-05-06
AK_MA_SPLIT TSE COOLING COIL Cooling Capacity [ton] | SPLIT TSE COOLING COIL Cooling Capacity [ton] | 0.96169 | 0.93552 | 0.97255 | 0.91003 | 1.0823 | 0.96119 | 1.2162 | 1.103 |  |  | 2021-05-06
AK_MA_SPLIT TNE COOLING COIL Cooling Capacity [ton] | SPLIT TNE COOLING COIL Cooling Capacity [ton] | 0.52304 | 0.50571 | 0.62978 | 0.58874 | 0.70152 | 0.62535 | 0.7912 | 0.71989 |  |  | 2021-05-06
AK_MA_SPLIT TN1 COOLING COIL Cooling Capacity [ton] | SPLIT TN1 COOLING COIL Cooling Capacity [ton] | 0.41125 | 0.40219 | 0.50158 | 0.485 | 0.51141 | 0.48473 | 0.58599 | 0.56032 |  |  | 2021-05-06
AK_MA_SPLIT TN2 COOLING COIL Cooling Capacity [ton] | SPLIT TN2 COOLING COIL Cooling Capacity [ton] | 0.40448 | 0.39472 | 0.49393 | 0.47792 | 0.50516 | 0.47945 | 0.57924 | 0.55453 |  |  | 2021-05-06
AK_MA_SPLIT TS1 COOLING COIL Cooling Capacity [ton] | SPLIT TS1 COOLING COIL Cooling Capacity [ton] | 0.85594 | 0.83281 | 0.83952 | 0.78755 | 0.93406 | 0.83418 | 1.0455 | 0.95284 |  |  | 2021-05-06
AK_MA_SPLIT TS2 COOLING COIL Cooling Capacity [ton] | SPLIT TS2 COOLING COIL Cooling Capacity [ton] | 0.86037 | 0.83718 | 0.84406 | 0.79186 | 0.93928 | 0.83888 | 1.0503 | 0.95713 |  |  | 2021-05-06
AK_MA_Split GN1 Furnace with DX Cooling OA Rate [cfm] | Split GN1 Furnace with DX Cooling OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 |  |  | 2021-05-06
AK_MA_Split GN2 Furnace with DX Cooling OA Rate [cfm] | Split GN2 Furnace with DX Cooling OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 |  |  | 2021-05-06
AK_MA_Split GNE Furnace with DX Cooling OA Rate [cfm] | Split GNE Furnace with DX Cooling OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 |  |  | 2021-05-06
AK_MA_Split GNW Furnace with DX Cooling OA Rate [cfm] | Split GNW Furnace with DX Cooling OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 |  |  | 2021-05-06
AK_MA_Split GS1 Furnace with DX Cooling OA Rate [cfm] | Split GS1 Furnace with DX Cooling OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 |  |  | 2021-05-06
AK_MA_Split GS2 Furnace with DX Cooling OA Rate [cfm] | Split GS2 Furnace with DX Cooling OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 |  |  | 2021-05-06
AK_MA_Split GSW Furnace with DX Cooling OA Rate [cfm] | Split GSW Furnace with DX Cooling OA Rate [cfm] | 56.9945 | 56.9945 | 56.9945 | 56.9945 | 56.9945 | 56.9945 | 56.9945 | 56.9945 |  |  | 2021-05-06
AK_MA_Split MN1 Furnace with DX Cooling OA Rate [cfm] | Split MN1 Furnace with DX Cooling OA Rate [cfm] | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824 |  |  | 2021-05-06
AK_MA_Split MN2 Furnace with DX Cooling OA Rate [cfm] | Split MN2 Furnace with DX Cooling OA Rate [cfm] | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824 |  |  | 2021-05-06
AK_MA_Split MNE Furnace with DX Cooling OA Rate [cfm] | Split MNE Furnace with DX Cooling OA Rate [cfm] | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824 |  |  | 2021-05-06
AK_MA_Split MNW Furnace with DX Cooling OA Rate [cfm] | Split MNW Furnace with DX Cooling OA Rate [cfm] | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824 |  |  | 2021-05-06
AK_MA_Split MS1 Furnace with DX Cooling OA Rate [cfm] | Split MS1 Furnace with DX Cooling OA Rate [cfm] | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824 |  |  | 2021-05-06
AK_MA_Split MS2 Furnace with DX Cooling OA Rate [cfm] | Split MS2 Furnace with DX Cooling OA Rate [cfm] | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824 |  |  | 2021-05-06
AK_MA_Split MSE Furnace with DX Cooling OA Rate [cfm] | Split MSE Furnace with DX Cooling OA Rate [cfm] | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824 |  |  | 2021-05-06
AK_MA_Split MSW Furnace with DX Cooling OA Rate [cfm] | Split MSW Furnace with DX Cooling OA Rate [cfm] | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824 |  |  | 2021-05-06
AK_MA_Split Office Furnace with DX Cooling OA Rate [cfm] | Split Office Furnace with DX Cooling OA Rate [cfm] | 80.7372 | 80.7372 | 80.7372 | 80.7372 | 80.7372 | 80.7372 | 80.7372 | 80.7372 |  |  | 2021-05-06
AK_MA_Split TN1 Furnace with DX Cooling OA Rate [cfm] | Split TN1 Furnace with DX Cooling OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 |  |  | 2021-05-06
AK_MA_Split TN2 Furnace with DX Cooling OA Rate [cfm] | Split TN2 Furnace with DX Cooling OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 |  |  | 2021-05-06
AK_MA_Split TNE Furnace with DX Cooling OA Rate [cfm] | Split TNE Furnace with DX Cooling OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 |  |  | 2021-05-06
AK_MA_Split TNW Furnace with DX Cooling OA Rate [cfm] | Split TNW Furnace with DX Cooling OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 |  |  | 2021-05-06
AK_MA_Split TS1 Furnace with DX Cooling OA Rate [cfm] | Split TS1 Furnace with DX Cooling OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 |  |  | 2021-05-06
AK_MA_Split TS2 Furnace with DX Cooling OA Rate [cfm] | Split TS2 Furnace with DX Cooling OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 |  |  | 2021-05-06
AK_MA_Split TSE Furnace with DX Cooling OA Rate [cfm] | Split TSE Furnace with DX Cooling OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 |  |  | 2021-05-06
AK_MA_Split TSW Furnace with DX Cooling OA Rate [cfm] | Split TSW Furnace with DX Cooling OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 |  |  | 2021-05-06
AK_MA_SPLIT GSW HEATING COIL Heating Capacity [kBtu/hr] | SPLIT GSW HEATING COIL Heating Capacity [kBtu/hr] | 7.9168 | 7.962 | 9.0239 | 9.0833 | 10.7475 | 10.6387 | 14.5615 | 14.5026 |  |  | 2021-05-06
AK_MA_SPLIT GNW HEATING COIL Heating Capacity [kBtu/hr] | SPLIT GNW HEATING COIL Heating Capacity [kBtu/hr] | 7.846 | 7.8913 | 8.9396 | 8.9992 | 10.6429 | 10.5312 | 14.3855 | 14.3258 |  |  | 2021-05-06
AK_MA_SPLIT OFFICE HEATING COIL Heating Capacity [kBtu/hr] | SPLIT OFFICE HEATING COIL Heating Capacity [kBtu/hr] | 19.8877 | 19.9218 | 21.7556 | 21.8584 | 24.23 | 24.1472 | 29.7552 | 29.6904 |  |  | 2021-05-06
AK_MA_SPLIT GNE HEATING COIL Heating Capacity [kBtu/hr] | SPLIT GNE HEATING COIL Heating Capacity [kBtu/hr] | 7.8325 | 7.8777 | 8.9396 | 8.9992 | 10.6429 | 10.5312 | 14.3974 | 14.337 |  |  | 2021-05-06
AK_MA_SPLIT GN1 HEATING COIL Heating Capacity [kBtu/hr] | SPLIT GN1 HEATING COIL Heating Capacity [kBtu/hr] | 5.7679 | 5.8083 | 6.7195 | 6.7791 | 8.1826 | 8.13 | 11.6349 | 11.6165 |  |  | 2021-05-06
AK_MA_SPLIT GN2 HEATING COIL Heating Capacity [kBtu/hr] | SPLIT GN2 HEATING COIL Heating Capacity [kBtu/hr] | 5.7675 | 5.8079 | 6.7195 | 6.7791 | 8.1826 | 8.13 | 11.6352 | 11.6168 |  |  | 2021-05-06
AK_MA_SPLIT GS1 HEATING COIL Heating Capacity [kBtu/hr] | SPLIT GS1 HEATING COIL Heating Capacity [kBtu/hr] | 5.7296 | 5.7697 | 6.6762 | 6.7358 | 8.1337 | 8.0839 | 11.5864 | 11.5688 |  |  | 2021-05-06
AK_MA_SPLIT GS2 HEATING COIL Heating Capacity [kBtu/hr] | SPLIT GS2 HEATING COIL Heating Capacity [kBtu/hr] | 6.2015 | 6.2403 | 7.1722 | 7.2337 | 8.6534 | 8.6033 | 12.1422 | 12.1248 |  |  | 2021-05-06
AK_MA_SPLIT MSW HEATING COIL Heating Capacity [kBtu/hr] | SPLIT MSW HEATING COIL Heating Capacity [kBtu/hr] | 12.8331 | 12.9611 | 14.733 | 14.8635 | 17.0322 | 16.8176 | 21.7586 | 21.6496 |  |  | 2021-05-06
AK_MA_SPLIT MNW HEATING COIL Heating Capacity [kBtu/hr] | SPLIT MNW HEATING COIL Heating Capacity [kBtu/hr] | 12.8923 | 13.0199 | 14.8005 | 14.9306 | 17.1065 | 16.884 | 21.817 | 21.705 |  |  | 2021-05-06
AK_MA_SPLIT MSE HEATING COIL Heating Capacity [kBtu/hr] | SPLIT MSE HEATING COIL Heating Capacity [kBtu/hr] | 12.8004 | 12.9284 | 14.733 | 14.8635 | 17.0322 | 16.8176 | 21.7871 | 21.6765 |  |  | 2021-05-06
AK_MA_SPLIT MNE HEATING COIL Heating Capacity [kBtu/hr] | SPLIT MNE HEATING COIL Heating Capacity [kBtu/hr] | 12.8596 | 12.9873 | 14.8005 | 14.9306 | 17.1065 | 16.884 | 21.8456 | 21.732 |  |  | 2021-05-06
AK_MA_SPLIT MN1 HEATING COIL Heating Capacity [kBtu/hr] | SPLIT MN1 HEATING COIL Heating Capacity [kBtu/hr] | 10.8584 | 10.8584 | 11.9326 | 11.9326 | 13.3829 | 13.3829 | 17.2787 | 17.2787 |  |  | 2021-05-06
AK_MA_SPLIT MN2 HEATING COIL Heating Capacity [kBtu/hr] | SPLIT MN2 HEATING COIL Heating Capacity [kBtu/hr] | 10.8584 | 10.8584 | 11.9326 | 11.9326 | 13.3829 | 13.3829 | 17.2787 | 17.2787 |  |  | 2021-05-06
AK_MA_SPLIT MS1 HEATING COIL Heating Capacity [kBtu/hr] | SPLIT MS1 HEATING COIL Heating Capacity [kBtu/hr] | 10.8584 | 10.8584 | 11.9326 | 11.9326 | 13.3829 | 13.3829 | 17.2787 | 17.2787 |  |  | 2021-05-06
AK_MA_SPLIT MS2 HEATING COIL Heating Capacity [kBtu/hr] | SPLIT MS2 HEATING COIL Heating Capacity [kBtu/hr] | 10.8584 | 10.8584 | 11.9326 | 11.9326 | 13.3829 | 13.3829 | 17.2787 | 17.2787 |  |  | 2021-05-06
AK_MA_SPLIT TSW HEATING COIL Heating Capacity [kBtu/hr] | SPLIT TSW HEATING COIL Heating Capacity [kBtu/hr] | 9.3883 | 9.4501 | 10.7184 | 10.7804 | 11.9705 | 11.8652 | 15.2673 | 15.2131 |  |  | 2021-05-06
AK_MA_SPLIT TNW HEATING COIL Heating Capacity [kBtu/hr] | SPLIT TNW HEATING COIL Heating Capacity [kBtu/hr] | 9.4259 | 9.4878 | 10.7612 | 10.8233 | 12.0177 | 11.9085 | 15.3082 | 15.2529 |  |  | 2021-05-06
AK_MA_SPLIT TSE HEATING COIL Heating Capacity [kBtu/hr] | SPLIT TSE HEATING COIL Heating Capacity [kBtu/hr] | 9.3709 | 9.4327 | 10.7184 | 10.7804 | 11.9705 | 11.8652 | 15.2831 | 15.2279 |  |  | 2021-05-06
AK_MA_SPLIT TNE HEATING COIL Heating Capacity [kBtu/hr] | SPLIT TNE HEATING COIL Heating Capacity [kBtu/hr] | 9.4085 | 9.4704 | 10.7612 | 10.8233 | 12.0177 | 11.9085 | 15.324 | 15.2678 |  |  | 2021-05-06
AK_MA_SPLIT TN1 HEATING COIL Heating Capacity [kBtu/hr] | SPLIT TN1 HEATING COIL Heating Capacity [kBtu/hr] | 7.3616 | 7.4234 | 8.524 | 8.586 | 9.6071 | 9.559 | 12.906 | 12.8926 |  |  | 2021-05-06
AK_MA_SPLIT TN2 HEATING COIL Heating Capacity [kBtu/hr] | SPLIT TN2 HEATING COIL Heating Capacity [kBtu/hr] | 7.3611 | 7.4228 | 8.524 | 8.586 | 9.6071 | 9.559 | 12.9065 | 12.893 |  |  | 2021-05-06
AK_MA_SPLIT TS1 HEATING COIL Heating Capacity [kBtu/hr] | SPLIT TS1 HEATING COIL Heating Capacity [kBtu/hr] | 7.3168 | 7.3784 | 8.4741 | 8.536 | 9.5533 | 9.5088 | 12.8593 | 12.8469 |  |  | 2021-05-06
AK_MA_SPLIT TS2 HEATING COIL Heating Capacity [kBtu/hr] | SPLIT TS2 HEATING COIL Heating Capacity [kBtu/hr] | 7.3162 | 7.3779 | 8.4741 | 8.536 | 9.5533 | 9.5088 | 12.8597 | 12.8473 |  |  | 2021-05-06
AK_MA_Split_GSW ERV Flag | Split_GSW ERV Flag | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  |  | 2021-05-06
AK_MA_Split_GNW ERV Flag | Split_GNW ERV Flag | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  |  | 2021-05-06
AK_MA_Split_GNE ERV Flag | Split_GNE ERV Flag | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  |  | 2021-05-06
AK_MA_Split_GN1 ERV Flag | Split_GN1 ERV Flag | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  |  | 2021-05-06
AK_MA_Split_GN2 ERV Flag | Split_GN2 ERV Flag | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  |  | 2021-05-06
AK_MA_Split_GS1 ERV Flag | Split_GS1 ERV Flag | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  |  | 2021-05-06
AK_MA_Split_GS2 ERV Flag | Split_GS2 ERV Flag | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  |  | 2021-05-06
AK_MA_Split_MSW ERV Flag | Split_MSW ERV Flag | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  |  | 2021-05-06
AK_MA_Split_MNW ERV Flag | Split_MNW ERV Flag | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  |  | 2021-05-06
AK_MA_Split_MSE ERV Flag | Split_MSE ERV Flag | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  |  | 2021-05-06
AK_MA_Split_MNE ERV Flag | Split_MNE ERV Flag | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  |  | 2021-05-06
AK_MA_Split_MN1 ERV Flag | Split_MN1 ERV Flag | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  |  | 2021-05-06
AK_MA_Split_MN2 ERV Flag | Split_MN2 ERV Flag | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  |  | 2021-05-06
AK_MA_Split_MS1 ERV Flag | Split_MS1 ERV Flag | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  |  | 2021-05-06
AK_MA_Split_MS2 ERV Flag | Split_MS2 ERV Flag | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  |  | 2021-05-06
AK_MA_Split_TSW ERV Flag | Split_TSW ERV Flag | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  |  | 2021-05-06
AK_MA_Split_TNW ERV Flag | Split_TNW ERV Flag | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  |  | 2021-05-06
AK_MA_Split_TSE ERV Flag | Split_TSE ERV Flag | No | Yes | Yes | Yes | Yes | Yes | No | Yes |  |  | 2021-05-06
AK_MA_Split_TNE ERV Flag | Split_TNE ERV Flag | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  |  | 2021-05-06
AK_MA_Split_TN1 ERV Flag | Split_TN1 ERV Flag | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  |  | 2021-05-06
AK_MA_Split_TN2 ERV Flag | Split_TN2 ERV Flag | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  |  | 2021-05-06
AK_MA_Split_TS1 ERV Flag | Split_TS1 ERV Flag | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  |  | 2021-05-06
AK_MA_Split_TS2 ERV Flag | Split_TS2 ERV Flag | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  |  | 2021-05-06
id | item | Zone2A(AL-Mobile-AL) ASHRAE901-state_STD2016 | Zone2A(AL-Mobile-AL) ASHRAE901-state_STD2019 | Zone3A(AL-Birmingham-AL) ASHRAE901-state_STD2016 | Zone3A(AL-Birmingham-AL) ASHRAE901-state_STD2019 | [6 empty] | 2021-05-06
AL_SO_PSZ-AC:1 Cooling Capacity [ton] | PSZ-AC:1 Cooling Capacity [ton] | 2.039 | 1.9412 | 1.9985 | 1.9023 | [6 empty] | 2021-05-06
AL_SO_PSZ-AC:2 Cooling Capacity [ton] | PSZ-AC:2 Cooling Capacity [ton] | 1.8074 | 1.7152 | 1.7563 | 1.693 | [6 empty] | 2021-05-06
AL_SO_PSZ-AC:3 Cooling Capacity [ton] | PSZ-AC:3 Cooling Capacity [ton] | 1.1801 | 1.1355 | 1.1323 | 1.0925 | [6 empty] | 2021-05-06
AL_SO_PSZ-AC:4 Cooling Capacity [ton] | PSZ-AC:4 Cooling Capacity [ton] | 1.7974 | 1.7082 | 1.7546 | 1.6728 | [6 empty] | 2021-05-06
AL_SO_PSZ-AC:5 Cooling Capacity [ton] | PSZ-AC:5 Cooling Capacity [ton] | 1.4067 | 1.3556 | 1.3595 | 1.3134 | [6 empty] | 2021-05-06
AL_SO_PSZ-AC:1 Supply Flow Rate [cfm] | PSZ-AC:1 Supply Flow Rate [cfm] | 678.0416 | 635.664 | 678.0416 | 635.664 | [6 empty] | 2021-05-06
AL_SO_PSZ-AC:2 Supply Flow Rate [cfm] | PSZ-AC:2 Supply Flow Rate [cfm] | 635.664 | 593.2864 | 635.664 | 593.2864 | [6 empty] | 2021-05-06
AL_SO_PSZ-AC:3 Supply Flow Rate [cfm] | PSZ-AC:3 Supply Flow Rate [cfm] | 444.9648 | 423.776 | 444.9648 | 423.776 | [6 empty] | 2021-05-06
AL_SO_PSZ-AC:4 Supply Flow Rate [cfm] | PSZ-AC:4 Supply Flow Rate [cfm] | 614.4752 | 572.0976 | 635.664 | 593.2864 | [6 empty] | 2021-05-06
AL_SO_PSZ-AC:5 Supply Flow Rate [cfm] | PSZ-AC:5 Supply Flow Rate [cfm] | 550.9088 | 508.5312 | 529.72 | 508.5312 | [6 empty] | 2021-05-06
AL_SO_PSZ-AC:1 OA Rate [cfm] | PSZ-AC:1 OA Rate [cfm] | 136.9178 | 136.9178 | 136.9178 | 136.9178 | [6 empty] | 2021-05-06
AL_SO_PSZ-AC:2 OA Rate [cfm] | PSZ-AC:2 OA Rate [cfm] | 103.7925 | 103.7925 | 103.7925 | 103.7925 | [6 empty] | 2021-05-06
AL_SO_PSZ-AC:3 OA Rate [cfm] | PSZ-AC:3 OA Rate [cfm] | 61.5711 | 61.5711 | 61.5711 | 61.5711 | [6 empty] | 2021-05-06
AL_SO_PSZ-AC:4 OA Rate [cfm] | PSZ-AC:4 OA Rate [cfm] | 103.7925 | 103.7925 | 103.7925 | 103.7925 | [6 empty] | 2021-05-06
AL_SO_PSZ-AC:5 OA Rate [cfm] | PSZ-AC:5 OA Rate [cfm] | 61.5711 | 61.5711 | 61.5711 | 61.5711 | [6 empty] | 2021-05-06
AL_SO_PSZ-AC:1 heating Capacity [kBtu/hr] | PSZ-AC:1 heating Capacity [kBtu/hr] | 11.3309 | 11.3309 | 12.2361 | 12.2361 | [6 empty] | 2021-05-06
AL_SO_PSZ-AC:2 heating Capacity [kBtu/hr] | PSZ-AC:2 heating Capacity [kBtu/hr] | 15.1982 | 14.6931 | 17.0873 | 16.8548 | [6 empty] | 2021-05-06
AL_SO_PSZ-AC:3 heating Capacity [kBtu/hr] | PSZ-AC:3 heating Capacity [kBtu/hr] | 9.324 | 9.0298 | 10.5178 | 10.3835 | [6 empty] | 2021-05-06
AL_SO_PSZ-AC:4 heating Capacity [kBtu/hr] | PSZ-AC:4 heating Capacity [kBtu/hr] | 14.9586 | 14.523 | 16.9111 | 16.7123 | [6 empty] | 2021-05-06
AL_SO_PSZ-AC:5 heating Capacity [kBtu/hr] | PSZ-AC:5 heating Capacity [kBtu/hr] | 9.324 | 9.0298 | 10.5178 | 10.3835 | [6 empty] | 2021-05-06
id | item | Zone2A(AL-Mobile-AL) ASHRAE901-state_STD2016 | Zone2A(AL-Mobile-AL) ASHRAE901-state_STD2019 | Zone3A(AL-Birmingham-AL) ASHRAE901-state_STD2016 | Zone3A(AL-Birmingham-AL) ASHRAE901-state_STD2019 | [6 empty] | 2021-05-06
AL_LO_CAV_BAS Supply Flow Rate [cfm] | CAV_BAS Supply Flow Rate [cfm] | 11675.0288 | 10806.288 | 11759.784 | 10869.8544 | [6 empty] | 2021-05-06
AL_LO_VAV_BOT WITH REHEAT Supply Flow Rate [cfm] | VAV_BOT WITH REHEAT Supply Flow Rate [cfm] | 19218.2416 | 18285.9344 | 19493.696 | 18540.2 | [6 empty] | 2021-05-06
AL_LO_VAV_MID WITH REHEAT Supply Flow Rate [cfm] | VAV_MID WITH REHEAT Supply Flow Rate [cfm] | 178388.5075 | 169531.5891 | 181164.2403 | 172053.0563 | [6 empty] | 2021-05-06
AL_LO_VAV_TOP WITH REHEAT Supply Flow Rate [cfm] | VAV_TOP WITH REHEAT Supply Flow Rate [cfm] | 18603.7664 | 17735.0256 | 18921.5984 | 18095.2352 | [6 empty] | 2021-05-06
AL_LO_Supply Air Temp. Reset Flag | Supply Air Temp. Reset Flag | No | No | No | Yes | [6 empty] | 2021-05-06
AL_LO_CAV_BAS OA Rate [cfm] | CAV_BAS OA Rate [cfm] | 2542.8255 | 2542.8255 | 2542.8255 | 2542.8255 | [6 empty] | 2021-05-06
AL_LO_VAV_BOT WITH REHEAT OA Rate [cfm] | VAV_BOT WITH REHEAT OA Rate [cfm] | 5377.8022 | 4302.174 | 5377.8022 | 4302.174 | [6 empty] | 2021-05-06
AL_LO_VAV_MID WITH REHEAT OA Rate [cfm] | VAV_MID WITH REHEAT OA Rate [cfm] | 53777.9373 | 43021.7396 | 53777.9373 | 43021.7396 | [6 empty] | 2021-05-06
AL_LO_VAV_TOP WITH REHEAT OA Rate [cfm] | VAV_TOP WITH REHEAT OA Rate [cfm] | 5377.8022 | 4302.174 | 5377.8022 | 4302.174 | [6 empty] | 2021-05-06
AL_LO_AIRLOOP DATACENTER BASEMENT OA Rate [cfm] | AIRLOOP DATACENTER BASEMENT OA Rate [cfm] | 716.9654 | 716.9654 | 716.9654 | 716.9654 | [6 empty] | 2021-05-06
AL_LO_VAV_bot_WITH_REHEAT ERV Flag | VAV_bot_WITH_REHEAT ERV Flag | Yes | Yes | Yes | Yes | [6 empty] | 2021-05-06
AL_LO_VAV_mid_WITH_REHEAT ERV Flag | VAV_mid_WITH_REHEAT ERV Flag | Yes | Yes | Yes | Yes | [6 empty] | 2021-05-06
AL_LO_VAV_top_WITH_REHEAT ERV Flag | VAV_top_WITH_REHEAT ERV Flag | Yes | Yes | Yes | Yes | [6 empty] | 2021-05-06
AL_LO_COOLSYS1 CHILLER1 Capacity [ton] | COOLSYS1 CHILLER1 Capacity [ton] | 440.5384 | 395.609 | 420.7813 | 378.6701 | [6 empty] | 2021-05-06
AL_LO_COOLSYS1 CHILLER2 Capacity [ton] | COOLSYS1 CHILLER2 Capacity [ton] | 440.5384 | 395.609 | 420.7813 | 378.6701 | [6 empty] | 2021-05-06
AL_LO_TOWERWATERSYS COOLTOWER 1 Capacity [ton] | TOWERWATERSYS COOLTOWER 1 Capacity [ton] | 418.1479 | 375.4982 | 399.4025 | 359.4308 | [6 empty] | 2021-05-06
AL_LO_TOWERWATERSYS COOLTOWER 2 Capacity [ton] | TOWERWATERSYS COOLTOWER 2 Capacity [ton] | 418.1479 | 375.4982 | 399.4025 | 359.4308 | [6 empty] | 2021-05-06
AL_LO_HEATSYS1 BOILER Capacity [MMBTU/h] | HEATSYS1 BOILER Capacity [MMBTU/h] | 3511.8649 | 3106.194 | 3765.3746 | 3335.0971 | [6 empty] | 2021-05-06
AL_LO_COOLSYS1 PUMP Flow Rate [gal/min] | COOLSYS1 PUMP Flow Rate [gal/min] | 0 | 0 | 0 | 0 | [6 empty] | 2021-05-06
AL_LO_COOLSYS1 CHILLER1 PUMP Flow Rate [gal/min] | COOLSYS1 CHILLER1 PUMP Flow Rate [gal/min] | 691.6146 | 620.8001 | 663.1458 | 593.9132 | [6 empty] | 2021-05-06
AL_LO_COOLSYS1 CHILLER2 PUMP Flow Rate [gal/min] | COOLSYS1 CHILLER2 PUMP Flow Rate [gal/min] | 691.6146 | 620.8001 | 663.1458 | 593.9132 | [6 empty] | 2021-05-06
AL_LO_COOLSYS1 PUMP SECONDARY Flow Rate [gal/min] | COOLSYS1 PUMP SECONDARY Flow Rate [gal/min] | 1383.2292 | 1241.5986 | 1326.2901 | 1187.8264 | [6 empty] | 2021-05-06
AL_LO_HEATSYS1 PUMP Flow Rate [gal/min] | HEATSYS1 PUMP Flow Rate [gal/min] | 720.8568 | 637.5872 | 772.8935 | 684.5723 | [6 empty] | 2021-05-06
AL_LO_TOWERWATERSYS PUMP Flow Rate [gal/min] | TOWERWATERSYS PUMP Flow Rate [gal/min] | 2430.4886 | 2182.5895 | 2321.4383 | 2089.0726 | [6 empty] | 2021-05-06
AL_LO_PLANT CIRC PUMP Flow Rate [gal/min] | PLANT CIRC PUMP Flow Rate [gal/min] | 208.5078 | 207.625 | 208.7694 | 207.8691 | [6 empty] | 2021-05-06
AL_LO_COOLSYS1 PUMP SECONDARY Pressure setpoint reset [yes,no] | COOLSYS1 PUMP SECONDARY Pressure setpoint reset [yes,no] | pump_ride_on_curve | pump_ride_on_curve | pump_ride_on_curve | pump_ride_on_curve | [6 empty] | 2021-05-06
AL_LO_COOLSYS1 CHILLER1 PUMP Pump Power [hp] | COOLSYS1 CHILLER1 PUMP Pump Power [hp] | 3.731 | 3.3158 | 3.5774 | 3.1722 | [6 empty] | 2021-05-06
AL_LO_COOLSYS1 CHILLER2 PUMP Pump Power [hp] | COOLSYS1 CHILLER2 PUMP Pump Power [hp] | 3.731 | 3.3158 | 3.5774 | 3.1722 | [6 empty] | 2021-05-06
AL_LO_COOLSYS1 PUMP SECONDARY Pump Power [hp] | COOLSYS1 PUMP SECONDARY Pump Power [hp] | 22.3861 | 19.895 | 21.4646 | 19.0334 | [6 empty] | 2021-05-06
AL_LO_HEATSYS1 PUMP Pump Power [hp] | HEATSYS1 PUMP Pump Power [hp] | 15.5817 | 13.6454 | 16.7065 | 14.6509 | [6 empty] | 2021-05-06
AL_LO_TOWERWATERSYS PUMP Pump Power [hp] | TOWERWATERSYS PUMP Pump Power [hp] | 43.5155 | 38.6905 | 41.5639 | 37.0339 | [6 empty] | 2021-05-06
AL_LO_PLANT CIRC PUMP Pump Power [hp] | PLANT CIRC PUMP Pump Power [hp] | 4.4993 | 4.4359 | 4.505 | 4.4411 | [6 empty] | 2021-05-06
AL_LO_Datacenter PLANT CIRC PUMP Pump Power [hp] | Datacenter PLANT CIRC PUMP Pump Power [hp] | 4.4993 | 4.4359 | 4.505 | 4.4411 | [6 empty] | 2021-05-06
AL_LO_ZN_VAV_BOXes_Max_Reheat_Water_Flow_GPM | ZN_VAV_BOXes_Max_Reheat_Water_Flow_GPM | 427.872 | 400.8238 | 429.8372 | 411.3473 | [6 empty] | 2021-05-06
AL_LO_COOLSYS1 PUMP SECONDARY VSD | COOLSYS1 PUMP SECONDARY VSD | No | No | No | No | [6 empty] | 2021-05-06
AL_LO_HEATSYS1 PUMP VSD | HEATSYS1 PUMP VSD | No | No | No | No | [6 empty] | 2021-05-06
AL_LO_DATACENTER BASEMENT Cooling Capacity [ton] | DATACENTER BASEMENT Cooling Capacity [ton] | 122.3604 | 122.0038 | 122.5951 | 122.2361 | [6 empty] | 2021-05-06
AL_LO_DATACENTER BOT Cooling Capacity [ton] | DATACENTER BOT Cooling Capacity [ton] | 2.6465 | 2.6201 | 2.644 | 2.6165 | [6 empty] | 2021-05-06
AL_LO_DATACENTER MID Cooling Capacity [ton] | DATACENTER MID Cooling Capacity [ton] | 25.1851 | 24.9419 | 25.1579 | 24.9046 | [6 empty] | 2021-05-06
AL_LO_DATACENTER TOP Cooling Capacity [ton] | DATACENTER TOP Cooling Capacity [ton] | 2.5445 | 2.5238 | 2.5315 | 2.5119 | [6 empty] | 2021-05-06
id | item | Zone2A(AL-Mobile-AL) ASHRAE901-state_STD2016 | Zone2A(AL-Mobile-AL) ASHRAE901-state_STD2019 | Zone3A(AL-Birmingham-AL) ASHRAE901-state_STD2016 | Zone3A(AL-Birmingham-AL) ASHRAE901-state_STD2019 | [6 empty] | 2021-05-06
AL_RS_PSZ-AC:1 Cooling Capacity [ton] | PSZ-AC:1 Cooling Capacity [ton] | 11.0913 | 10.7503 | 10.7698 | 10.4345 | [6 empty] | 2021-05-06
AL_RS_PSZ-AC:2 Cooling Capacity [ton] | PSZ-AC:2 Cooling Capacity [ton] | 51.2051 | 48.3375 | 51.2092 | 48.6532 | [6 empty] | 2021-05-06
AL_RS_PSZ-AC:3 Cooling Capacity [ton] | PSZ-AC:3 Cooling Capacity [ton] | 6.8125 | 6.6753 | 6.7165 | 6.5592 | [6 empty] | 2021-05-06
AL_RS_PSZ-AC:4 Cooling Capacity [ton] | PSZ-AC:4 Cooling Capacity [ton] | 5.5983 | 5.4627 | 5.498 | 5.345 | [6 empty] | 2021-05-06
AL_RS_PSZ-AC:1 Supply Flow Rate [cfm] | PSZ-AC:1 Supply Flow Rate [cfm] | 4131.816 | 3898.7392 | 4131.816 | 3898.7392 | [6 empty] | 2021-05-06
AL_RS_PSZ-AC:2 Supply Flow Rate [cfm] | PSZ-AC:2 Supply Flow Rate [cfm] | 15361.88 | 14514.328 | 15467.824 | 14599.0832 | [6 empty] | 2021-05-06
AL_RS_PSZ-AC:3 Supply Flow Rate [cfm] | PSZ-AC:3 Supply Flow Rate [cfm] | 2288.3904 | 2224.824 | 2330.768 | 2267.2016 | [6 empty] | 2021-05-06
AL_RS_PSZ-AC:4 Supply Flow Rate [cfm] | PSZ-AC:4 Supply Flow Rate [cfm] | 1758.6704 | 1695.104 | 1801.048 | 1716.2928 | [6 empty] | 2021-05-06
AL_RS_PSZ-AC:1 OA Rate [cfm] | PSZ-AC:1 OA Rate [cfm] | 490.669 | 490.669 | 490.669 | 490.669 | [6 empty] | 2021-05-06
AL_RS_PSZ-AC:2 OA Rate [cfm] | PSZ-AC:2 OA Rate [cfm] | 4005.1282 | 4005.1282 | 4005.1282 | 4005.1282 | [6 empty] | 2021-05-06
AL_RS_PSZ-AC:3 OA Rate [cfm] | PSZ-AC:3 OA Rate [cfm] | 377.3937 | 377.3937 | 377.3937 | 377.3937 | [6 empty] | 2021-05-06
AL_RS_PSZ-AC:4 OA Rate [cfm] | PSZ-AC:4 OA Rate [cfm] | 377.3937 | 377.3937 | 377.3937 | 377.3937 | [6 empty] | 2021-05-06
AL_RS_PSZ-AC:1 OA Damper [gravity, motorized] | PSZ-AC:1 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2021-05-06
AL_RS_PSZ-AC:2 OA Damper [gravity, motorized] | PSZ-AC:2 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2021-05-06
AL_RS_PSZ-AC:3 OA Damper [gravity, motorized] | PSZ-AC:3 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2021-05-06
AL_RS_PSZ-AC:4 OA Damper [gravity, motorized] | PSZ-AC:4 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2021-05-06
AL_RS_PSZ-AC:1 Heating Capacity [kBtu/hr] | PSZ-AC:1 Heating Capacity [kBtu/hr] | 174.1187 | 164.2095 | 175.7237 | 165.7345 | [6 empty] | 2021-05-06
AL_RS_PSZ-AC:2 Heating Capacity [kBtu/hr] | PSZ-AC:2 Heating Capacity [kBtu/hr] | 736.3535 | 700.5125 | 758.1167 | 724.6185 | [6 empty] | 2021-05-06
AL_RS_PSZ-AC:3 Heating Capacity [kBtu/hr] | PSZ-AC:3 Heating Capacity [kBtu/hr] | 101.9474 | 99.4746 | 104.9808 | 102.3448 | [6 empty] | 2021-05-06
AL_RS_PSZ-AC:4 Heating Capacity [kBtu/hr] | PSZ-AC:4 Heating Capacity [kBtu/hr] | 82.0639 | 79.4189 | 85.2313 | 82.4582 | [6 empty] | 2021-05-06
id | item | Zone2A(AL-Mobile-AL) ASHRAE901-state_STD2016 | Zone2A(AL-Mobile-AL) ASHRAE901-state_STD2019 | Zone3A(AL-Birmingham-AL) ASHRAE901-state_STD2016 | Zone3A(AL-Birmingham-AL) ASHRAE901-state_STD2019 | [6 empty] | 2021-05-06
AL_PS_VAV_POD_1 Cooling Capacity [ton] | VAV_POD_1 Cooling Capacity [ton] | 18.5544 | 18.1427 | 18.6981 | 18.171 | [6 empty] | 2021-05-06
AL_PS_VAV_POD_2 Cooling Capacity [ton] | VAV_POD_2 Cooling Capacity [ton] | 18.5804 | 18.1142 | 18.6404 | 18.1352 | [6 empty] | 2021-05-06
AL_PS_VAV_POD_3 Cooling Capacity [ton] | VAV_POD_3 Cooling Capacity [ton] | 16.929 | 16.0361 | 17.0662 | 16.1973 | [6 empty] | 2021-05-06
AL_PS_VAV_OTHER Cooling Capacity [ton] | VAV_OTHER Cooling Capacity [ton] | 25.8806 | 24.2116 | 26.1091 | 24.5195 | [6 empty] | 2021-05-06
AL_PS_PSZ-AC_1:6 Cooling Capacity [ton] | PSZ-AC_1:6 Cooling Capacity [ton] | 8.3738 | 7.9939 | 8.4803 | 8.0989 | [6 empty] | 2021-05-06
AL_PS_PSZ-AC_2:5 Cooling Capacity [ton] | PSZ-AC_2:5 Cooling Capacity [ton] | 5.2294 | 5.0494 | 5.1965 | 5.0287 | [6 empty] | 2021-05-06
AL_PS_PSZ-AC_2:7 Cooling Capacity [ton] | PSZ-AC_2:7 Cooling Capacity [ton] | 10.5074 | 10.5074 | 10.5074 | 10.5074 | [6 empty] | 2021-05-06
AL_PS_VAV_POD_1 Supply Flow Rate [cfm] | VAV_POD_1 Supply Flow Rate [cfm] | 5572.6544 | 5445.5216 | 5615.032 | 5445.5216 | [6 empty] | 2021-05-06
AL_PS_VAV_POD_2 Supply Flow Rate [cfm] | VAV_POD_2 Supply Flow Rate [cfm] | 5572.6544 | 5445.5216 | 5593.8432 | 5445.5216 | [6 empty] | 2021-05-06
AL_PS_VAV_POD_3 Supply Flow Rate [cfm] | VAV_POD_3 Supply Flow Rate [cfm] | 5085.312 | 4809.8576 | 5127.6896 | 4852.2352 | [6 empty] | 2021-05-06
AL_PS_VAV_OTHER Supply Flow Rate [cfm] | VAV_OTHER Supply Flow Rate [cfm] | 7776.2896 | 7267.7584 | 7839.856 | 7352.5136 | [6 empty] | 2021-05-06
AL_PS_PSZ-AC_2:5 Supply Flow Rate [cfm] | PSZ-AC_2:5 Supply Flow Rate [cfm] | 1567.9712 | 1525.5936 | 1567.9712 | 1504.4048 | [6 empty] | 2021-05-06
AL_PS_PSZ-AC_1:6 Supply Flow Rate [cfm] | PSZ-AC_1:6 Supply Flow Rate [cfm] | 2521.4672 | 2394.3344 | 2542.656 | 2436.712 | [6 empty] | 2021-05-06
AL_PS_PSZ-AC_2:7 Supply Flow Rate [cfm] | PSZ-AC_2:7 Supply Flow Rate [cfm] | 3157.1312 | 3157.1312 | 3157.1312 | 3157.1312 | [6 empty] | 2021-05-06
AL_PS_Supply Air Temp. Reset Flag | Supply Air Temp. Reset Flag | No | No | No | No | [6 empty] | 2021-05-06
AL_PS_VAV_POD_1 OA Rate [cfm] | VAV_POD_1 OA Rate [cfm] | 5565.9587 | 5444.335 | 5610.9849 | 5452.8317 | [6 empty] | 2021-05-06
AL_PS_VAV_POD_2 OA Rate [cfm] | VAV_POD_2 OA Rate [cfm] | 5575.1547 | 5435.7959 | 5593.6737 | 5442.0678 | [6 empty] | 2021-05-06
AL_PS_VAV_POD_3 OA Rate [cfm] | VAV_POD_3 OA Rate [cfm] | 5078.129 | 4812.1672 | 5120.3795 | 4860.5412 | [6 empty] | 2021-05-06
AL_PS_VAV_OTHER OA Rate [cfm] | VAV_OTHER OA Rate [cfm] | 3736.1787 | 2988.8921 | 3736.1787 | 2988.8921 | [6 empty] | 2021-05-06
AL_PS_PSZ-AC_2:5 OA Rate [cfm] | PSZ-AC_2:5 OA Rate [cfm] | 1152.7343 | 1152.7343 | 1152.7343 | 1152.7343 | [6 empty] | 2021-05-06
AL_PS_PSZ-AC_1:6 OA Rate [cfm] | PSZ-AC_1:6 OA Rate [cfm] | 539.9118 | 539.9118 | 539.9118 | 539.9118 | [6 empty] | 2021-05-06
AL_PS_PSZ-AC_2:7 OA Rate [cfm] | PSZ-AC_2:7 OA Rate [cfm] | 3153.0841 | 3153.0841 | 3153.0841 | 3153.0841 | [6 empty] | 2021-05-06
AL_PS_VAV_POD_1 OA Damper [gravity, motorized] | VAV_POD_1 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2021-05-06
AL_PS_VAV_POD_2 OA Damper [gravity, motorized] | VAV_POD_2 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2021-05-06
AL_PS_VAV_POD_3 OA Damper [gravity, motorized] | VAV_POD_3 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2021-05-06
AL_PS_VAV_OTHER OA Damper [gravity, motorized] | VAV_OTHER OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2021-05-06
AL_PS_PSZ-AC_2:5 OA Damper [gravity, motorized] | PSZ-AC_2:5 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2021-05-06
AL_PS_PSZ-AC_1:6 OA Damper [gravity, motorized] | PSZ-AC_1:6 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2021-05-06
AL_PS_PSZ-AC_2:7 OA Damper [gravity, motorized] | PSZ-AC_2:7 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2021-05-06
AL_PS_VAV_POD_1 (economizer) | VAV_POD_1 (economizer) | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialEnthalpy | [6 empty] | 2021-05-06
AL_PS_VAV_POD_2 (economizer) | VAV_POD_2 (economizer) | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialEnthalpy | [6 empty] | 2021-05-06
AL_PS_VAV_POD_3 (economizer) | VAV_POD_3 (economizer) | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialEnthalpy | [6 empty] | 2021-05-06
AL_PS_VAV_OTHER (economizer) | VAV_OTHER (economizer) | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialEnthalpy | [6 empty] | 2021-05-06
AL_PS_PSZ-AC_2:5 (economizer) | PSZ-AC_2:5 (economizer) | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialEnthalpy | [6 empty] | 2021-05-06
AL_PS_PSZ-AC_1:6 (economizer) | PSZ-AC_1:6 (economizer) | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialEnthalpy | [6 empty] | 2021-05-06
AL_PS_PSZ-AC_2:7 (economizer) | PSZ-AC_2:7 (economizer) | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialEnthalpy | [6 empty] | 2021-05-06
AL_PS_VAV_Pod_1_ERV Flag | VAV_Pod_1_ERV Flag | Yes | Yes | Yes | Yes | [6 empty] | 2021-05-06
AL_PS_VAV_Pod_2_ERV Flag | VAV_Pod_2_ERV Flag | Yes | Yes | Yes | Yes | [6 empty] | 2021-05-06
AL_PS_VAV_Pod_3_ERV Flag | VAV_Pod_3_ERV Flag | Yes | Yes | Yes | Yes | [6 empty] | 2021-05-06
AL_PS_VAV_OTHER_ERV Flag | VAV_OTHER_ERV Flag | Yes | Yes | Yes | Yes | [6 empty] | 2021-05-06
AL_PS_PSZ_AC_2_5_ERV Flag | PSZ_AC_2_5_ERV Flag | Yes | Yes | Yes | Yes | [6 empty] | 2021-05-06
AL_PS_PSZ_AC_2_7_ERV Flag | PSZ_AC_2_7_ERV Flag | Yes | Yes | Yes | Yes | [6 empty] | 2021-05-06
AL_PS_HEATSYS1 Capacity [MMBTU/h] | HEATSYS1 Capacity [MMBTU/h] | 0.82674 | 0.77479 | 0.91241 | 0.86899 | [6 empty] | 2021-05-06
AL_PS_HEATSYS1 Flow Rate [gal/min] | HEATSYS1 Flow Rate [gal/min] | 84.8499 | 79.5177 | 93.6416 | 89.1858 | [6 empty] | 2021-05-06
AL_PS_VAV_POD_1 Fan Power [hp] | VAV_POD_1 Fan Power [hp] | 8.2143 | 8.032 | 8.2779 | 8.0446 | [6 empty] | 2021-05-06
AL_PS_VAV_POD_2 Fan Power [hp] | VAV_POD_2 Fan Power [hp] | 8.2258 | 8.0194 | 8.2523 | 8.0287 | [6 empty] | 2021-05-06
AL_PS_VAV_POD_3 Fan Power [hp] | VAV_POD_3 Fan Power [hp] | 7.4947 | 7.0994 | 7.5554 | 7.1708 | [6 empty] | 2021-05-06
AL_PS_VAV_OTHER Fan Power [hp] | VAV_OTHER Fan Power [hp] | 11.3709 | 10.6376 | 11.4713 | 10.7729 | [6 empty] | 2021-05-06
AL_PS_HEATSYS1 Pump Power [hp] | HEATSYS1 Pump Power [hp] | 1.8341 | 1.7018 | 2.0241 | 1.9087 | [6 empty] | 2021-05-06
AL_PS_PSZ-AC_1:6 Heating Capacity [kBtu/hr] | PSZ-AC_1:6 Heating Capacity [kBtu/hr] | 197.2746 | 188.4578 | 201.0653 | 192.3398 | [6 empty] | 2021-05-06
AL_PS_PSZ-AC_2:5 Heating Capacity [kBtu/hr] | PSZ-AC_2:5 Heating Capacity [kBtu/hr] | 110.7002 | 108.7157 | 117.7413 | 115.9182 | [6 empty] | 2021-05-06
AL_PS_PSZ-AC_2:7 Heating Capacity [kBtu/hr] | PSZ-AC_2:7 Heating Capacity [kBtu/hr] | 260.9412 | 260.9412 | 281.7865 | 281.7865 | [6 empty] | 2021-05-06
AL_PS_ZN_VAV_BOXes_Max_Reheat_Water_Flow_GPM | ZN_VAV_BOXes_Max_Reheat_Water_Flow_GPM | 62.5698 | 58.1962 | 65.7167 | 62.4716 | [6 empty] | 2021-05-06
id | item | Zone2A(AL-Mobile-AL) ASHRAE901-state_STD2016 | Zone2A(AL-Mobile-AL) ASHRAE901-state_STD2019 | Zone3A(AL-Birmingham-AL) ASHRAE901-state_STD2016 | Zone3A(AL-Birmingham-AL) ASHRAE901-state_STD2019 | [6 empty] | 2021-05-06
AL_SH_SAC_FRONTOFFICE Cooling Capacity [ton] | SAC_FRONTOFFICE Cooling Capacity [ton] | 2.4943 | 2.3639 | 2.4691 | 2.3271 | [6 empty] | 2021-05-06
AL_SH_SAC_FRONTLOUNGE Cooling Capacity [ton] | SAC_FRONTLOUNGE Cooling Capacity [ton] | 6.1703 | 5.8538 | 6.2459 | 5.9314 | [6 empty] | 2021-05-06
AL_SH_SAC_MEETINGROOM Cooling Capacity [ton] | SAC_MEETINGROOM Cooling Capacity [ton] | 2.938 | 2.843 | 2.966 | 2.8773 | [6 empty] | 2021-05-06
AL_SH_SAC_EXC_EMPLGE_RESTRM Cooling Capacity [ton] | SAC_EXC_EMPLGE_RESTRM Cooling Capacity [ton] | 6.1317 | 6.0975 | 6.1536 | 6.1118 | [6 empty] | 2021-05-06
AL_SH_SAC_FO_ADDAQ SUPPLY FAN Supply Flow Rate [cfm] | SAC_FO_ADDAQ SUPPLY FAN Supply Flow Rate [cfm] | 805.1744 | 741.608 | 805.1744 | 762.7968 | [6 empty] | 2021-05-06
AL_SH_SAC_FL_ADDAQ SUPPLY FAN Supply Flow Rate [cfm] | SAC_FL_ADDAQ SUPPLY FAN Supply Flow Rate [cfm] | 1843.4256 | 1758.6704 | 1864.6144 | 1779.8592 | [6 empty] | 2021-05-06
AL_SH_SAC_MR_ADDAQ SUPPLY FAN Supply Flow Rate [cfm] | SAC_MR_ADDAQ SUPPLY FAN Supply Flow Rate [cfm] | 889.9296 | 847.552 | 889.9296 | 868.7408 | [6 empty] | 2021-05-06
AL_SH_SAC_EXC_ADDAQ SUPPLY FAN Supply Flow Rate [cfm] | SAC_EXC_ADDAQ SUPPLY FAN Supply Flow Rate [cfm] | 2161.2576 | 2161.2576 | 2203.6352 | 2182.4464 | [6 empty] | 2021-05-06
AL_SH_SAC_Exc_EmpLge_RestRm OA Rate [cfm] | SAC_Exc_EmpLge_RestRm OA Rate [cfm] | 199.9928 | 199.9928 | 199.9928 | 199.9928 | [6 empty] | 2021-05-06
AL_SH_SAC_FrontLounge OA Rate [cfm] | SAC_FrontLounge OA Rate [cfm] | 500.0133 | 500.0133 | 500.0133 | 500.0133 | [6 empty] | 2021-05-06
AL_SH_SAC_FrontOffice OA Rate [cfm] | SAC_FrontOffice OA Rate [cfm] | 119.2938 | 119.2938 | 119.2938 | 119.2938 | [6 empty] | 2021-05-06
AL_SH_SAC_MeetingRoom OA Rate [cfm] | SAC_MeetingRoom OA Rate [cfm] | 267.7629 | 267.7629 | 267.7629 | 267.7629 | [6 empty] | 2021-05-06
AL_SH_SAC_FrontLounge OA Damper [gravity, motorized] | SAC_FrontLounge OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2021-05-06
AL_SH_SAC_FrontOffice (economizer) | SAC_FrontOffice (economizer) | No | No | No | No | [6 empty] | 2021-05-06
AL_SH_SAC_FrontLounge (economizer) | SAC_FrontLounge (economizer) | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialEnthalpy | [6 empty] | 2021-05-06
AL_SH_SAC_MeetingRoom (economizer) | SAC_MeetingRoom (economizer) | No | No | No | No | [6 empty] | 2021-05-06
AL_SH_SAC_Exc_EmpLge_RestRm (economizer) | SAC_Exc_EmpLge_RestRm (economizer) | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialEnthalpy | [6 empty] | 2021-05-06
AL_SH_SAC_FRONTOFFICE Heating Capacity [kBtu/hr] | SAC_FRONTOFFICE Heating Capacity [kBtu/hr] | 34.7792 | 32.7596 | 35.6347 | 33.4523 | [6 empty] | 2021-05-06
AL_SH_SAC_FRONTLOUNGE Heating Capacity [kBtu/hr] | SAC_FRONTLOUNGE Heating Capacity [kBtu/hr] | 90.7448 | 87.2755 | 94.1499 | 90.753 | [6 empty] | 2021-05-06
AL_SH_SAC_MEETINGROOM Heating Capacity [kBtu/hr] | SAC_MEETINGROOM Heating Capacity [kBtu/hr] | 44.5797 | 43.5389 | 46.3272 | 45.3686 | [6 empty] | 2021-05-06
AL_SH_SAC_EXC_EMPLGE_RESTRM Heating Capacity [kBtu/hr] | SAC_EXC_EMPLGE_RESTRM Heating Capacity [kBtu/hr] | 88.3329 | 87.8053 | 90.1451 | 89.4935 | [6 empty] | 2021-05-06
id | item | Zone2A(AL-Mobile-AL) ASHRAE901-state_STD2016 | Zone2A(AL-Mobile-AL) ASHRAE901-state_STD2019 | Zone3A(AL-Birmingham-AL) ASHRAE901-state_STD2016 | Zone3A(AL-Birmingham-AL) ASHRAE901-state_STD2019 | [6 empty] | 2021-05-06
AL_MA_SPLIT GSW COOLING COIL Cooling Capacity [ton] | SPLIT GSW COOLING COIL Cooling Capacity [ton] | 0.88639 | 0.87606 | 0.87144 | 0.85898 | [6 empty] | 2021-05-06
AL_MA_SPLIT GNW COOLING COIL Cooling Capacity [ton] | SPLIT GNW COOLING COIL Cooling Capacity [ton] | 0.88001 | 0.86933 | 0.85043 | 0.84007 | [6 empty] | 2021-05-06
AL_MA_SPLIT OFFICE COOLING COIL Cooling Capacity [ton] | SPLIT OFFICE COOLING COIL Cooling Capacity [ton] | 1.7179 | 1.6347 | 1.705 | 1.5878 | [6 empty] | 2021-05-06
AL_MA_SPLIT GNE COOLING COIL Cooling Capacity [ton] | SPLIT GNE COOLING COIL Cooling Capacity [ton] | 0.79075 | 0.78105 | 0.77249 | 0.76281 | [6 empty] | 2021-05-06
AL_MA_SPLIT GN1 COOLING COIL Cooling Capacity [ton] | SPLIT GN1 COOLING COIL Cooling Capacity [ton] | 0.6949 | 0.68634 | 0.66988 | 0.66178 | [6 empty] | 2021-05-06
AL_MA_SPLIT GN2 COOLING COIL Cooling Capacity [ton] | SPLIT GN2 COOLING COIL Cooling Capacity [ton] | 0.69327 | 0.68472 | 0.66843 | 0.66033 | [6 empty] | 2021-05-06
AL_MA_SPLIT GS1 COOLING COIL Cooling Capacity [ton] | SPLIT GS1 COOLING COIL Cooling Capacity [ton] | 0.69458 | 0.68451 | 0.68376 | 0.67504 | [6 empty] | 2021-05-06
AL_MA_SPLIT GS2 COOLING COIL Cooling Capacity [ton] | SPLIT GS2 COOLING COIL Cooling Capacity [ton] | 0.72776 | 0.71514 | 0.71532 | 0.70302 | [6 empty] | 2021-05-06
AL_MA_SPLIT MSW COOLING COIL Cooling Capacity [ton] | SPLIT MSW COOLING COIL Cooling Capacity [ton] | 1.9698 | 1.9474 | 1.9371 | 1.9163 | [6 empty] | 2021-05-06
AL_MA_SPLIT MNW COOLING COIL Cooling Capacity [ton] | SPLIT MNW COOLING COIL Cooling Capacity [ton] | 1.963 | 1.9404 | 1.9031 | 1.8823 | [6 empty] | 2021-05-06
AL_MA_SPLIT MSE COOLING COIL Cooling Capacity [ton] | SPLIT MSE COOLING COIL Cooling Capacity [ton] | 1.7019 | 1.6825 | 1.7548 | 1.7346 | [6 empty] | 2021-05-06
AL_MA_SPLIT MNE COOLING COIL Cooling Capacity [ton] | SPLIT MNE COOLING COIL Cooling Capacity [ton] | 1.7127 | 1.6924 | 1.671 | 1.6518 | [6 empty] | 2021-05-06
AL_MA_SPLIT MN1 COOLING COIL Cooling Capacity [ton] | SPLIT MN1 COOLING COIL Cooling Capacity [ton] | 1.4553 | 1.4375 | 1.4084 | 1.3921 | [6 empty] | 2021-05-06
AL_MA_SPLIT MN2 COOLING COIL Cooling Capacity [ton] | SPLIT MN2 COOLING COIL Cooling Capacity [ton] | 1.451 | 1.4333 | 1.4046 | 1.3883 | [6 empty] | 2021-05-06
AL_MA_SPLIT MS1 COOLING COIL Cooling Capacity [ton] | SPLIT MS1 COOLING COIL Cooling Capacity [ton] | 1.4492 | 1.4322 | 1.4264 | 1.4096 | [6 empty] | 2021-05-06
AL_MA_SPLIT MS2 COOLING COIL Cooling Capacity [ton] | SPLIT MS2 COOLING COIL Cooling Capacity [ton] | 1.445 | 1.428 | 1.4226 | 1.4058 | [6 empty] | 2021-05-06
AL_MA_SPLIT TSW COOLING COIL Cooling Capacity [ton] | SPLIT TSW COOLING COIL Cooling Capacity [ton] | 1.2133 | 1.2016 | 1.2056 | 1.1947 | [6 empty] | 2021-05-06
AL_MA_SPLIT TNW COOLING COIL Cooling Capacity [ton] | SPLIT TNW COOLING COIL Cooling Capacity [ton] | 1.1974 | 1.1856 | 1.1743 | 1.1635 | [6 empty] | 2021-05-06
AL_MA_SPLIT TSE COOLING COIL Cooling Capacity [ton] | SPLIT TSE COOLING COIL Cooling Capacity [ton] | 1.097 | 1.0864 | 1.1054 | 1.0953 | [6 empty] | 2021-05-06
AL_MA_SPLIT TNE COOLING COIL Cooling Capacity [ton] | SPLIT TNE COOLING COIL Cooling Capacity [ton] | 1.0707 | 1.0598 | 1.0604 | 1.0502 | [6 empty] | 2021-05-06
AL_MA_SPLIT TN1 COOLING COIL Cooling Capacity [ton] | SPLIT TN1 COOLING COIL Cooling Capacity [ton] | 0.8766 | 0.86777 | 0.85446 | 0.84587 | [6 empty] | 2021-05-06
AL_MA_SPLIT TN2 COOLING COIL Cooling Capacity [ton] | SPLIT TN2 COOLING COIL Cooling Capacity [ton] | 0.87171 | 0.86291 | 0.88412 | 0.87512 | [6 empty] | 2021-05-06
AL_MA_SPLIT TS1 COOLING COIL Cooling Capacity [ton] | SPLIT TS1 COOLING COIL Cooling Capacity [ton] | 0.92261 | 0.91354 | 0.92762 | 0.91875 | [6 empty] | 2021-05-06
AL_MA_SPLIT TS2 COOLING COIL Cooling Capacity [ton] | SPLIT TS2 COOLING COIL Cooling Capacity [ton] | 0.92318 | 0.91421 | 0.92872 | 0.91983 | [6 empty] | 2021-05-06
AL_MA_Split GN1 Furnace with DX Cooling OA Rate [cfm] | Split GN1 Furnace with DX Cooling OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | [6 empty] | 2021-05-06
AL_MA_Split GN2 Furnace with DX Cooling OA Rate [cfm] | Split GN2 Furnace with DX Cooling OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | [6 empty] | 2021-05-06
AL_MA_Split GNE Furnace with DX Cooling OA Rate [cfm] | Split GNE Furnace with DX Cooling OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | [6 empty] | 2021-05-06
AL_MA_Split GNW Furnace with DX Cooling OA Rate [cfm] | Split GNW Furnace with DX Cooling OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | [6 empty] | 2021-05-06
AL_MA_Split GS1 Furnace with DX Cooling OA Rate [cfm] | Split GS1 Furnace with DX Cooling OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | [6 empty] | 2021-05-06
AL_MA_Split GS2 Furnace with DX Cooling OA Rate [cfm] | Split GS2 Furnace with DX Cooling OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | [6 empty] | 2021-05-06
AL_MA_Split GSW Furnace with DX Cooling OA Rate [cfm] | Split GSW Furnace with DX Cooling OA Rate [cfm] | 56.9945 | 56.9945 | 56.9945 | 56.9945 | [6 empty] | 2021-05-06
AL_MA_Split MN1 Furnace with DX Cooling OA Rate [cfm] | Split MN1 Furnace with DX Cooling OA Rate [cfm] | 109.9824 | 109.9824 | 109.9824 | 109.9824 | [6 empty] | 2021-05-06
AL_MA_Split MN2 Furnace with DX Cooling OA Rate [cfm] | Split MN2 Furnace with DX Cooling OA Rate [cfm] | 109.9824 | 109.9824 | 109.9824 | 109.9824 | [6 empty] | 2021-05-06
AL_MA_Split MNE Furnace with DX Cooling OA Rate [cfm] | Split MNE Furnace with DX Cooling OA Rate [cfm] | 109.9824 | 109.9824 | 109.9824 | 109.9824 | [6 empty] | 2021-05-06
AL_MA_Split MNW Furnace with DX Cooling OA Rate [cfm] | Split MNW Furnace with DX Cooling OA Rate [cfm] | 109.9824 | 109.9824 | 109.9824 | 109.9824 | [6 empty] | 2021-05-06
AL_MA_Split MS1 Furnace with DX Cooling OA Rate [cfm] | Split MS1 Furnace with DX Cooling OA Rate [cfm] | 109.9824 | 109.9824 | 109.9824 | 109.9824 | [6 empty] | 2021-05-06
AL_MA_Split MS2 Furnace with DX Cooling OA Rate [cfm] | Split MS2 Furnace with DX Cooling OA Rate [cfm] | 109.9824 | 109.9824 | 109.9824 | 109.9824 | [6 empty] | 2021-05-06
AL_MA_Split MSE Furnace with DX Cooling OA Rate [cfm] | Split MSE Furnace with DX Cooling OA Rate [cfm] | 109.9824 | 109.9824 | 109.9824 | 109.9824 | [6 empty] | 2021-05-06
AL_MA_Split MSW Furnace with DX Cooling OA Rate [cfm] | Split MSW Furnace with DX Cooling OA Rate [cfm] | 109.9824 | 109.9824 | 109.9824 | 109.9824 | [6 empty] | 2021-05-06
AL_MA_Split Office Furnace with DX Cooling OA Rate [cfm] | Split Office Furnace with DX Cooling OA Rate [cfm] | 80.7372 | 80.7372 | 80.7372 | 80.7372 | [6 empty] | 2021-05-06
AL_MA_Split TN1 Furnace with DX Cooling OA Rate [cfm] | Split TN1 Furnace with DX Cooling OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | [6 empty] | 2021-05-06
AL_MA_Split TN2 Furnace with DX Cooling OA Rate [cfm] | Split TN2 Furnace with DX Cooling OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | [6 empty] | 2021-05-06
AL_MA_Split TNE Furnace with DX Cooling OA Rate [cfm] | Split TNE Furnace with DX Cooling OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | [6 empty] | 2021-05-06
AL_MA_Split TNW Furnace with DX Cooling OA Rate [cfm] | Split TNW Furnace with DX Cooling OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | [6 empty] | 2021-05-06
AL_MA_Split TS1 Furnace with DX Cooling OA Rate [cfm] | Split TS1 Furnace with DX Cooling OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | [6 empty] | 2021-05-06
AL_MA_Split TS2 Furnace with DX Cooling OA Rate [cfm] | Split TS2 Furnace with DX Cooling OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | [6 empty] | 2021-05-06
AL_MA_Split TSE Furnace with DX Cooling OA Rate [cfm] | Split TSE Furnace with DX Cooling OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | [6 empty] | 2021-05-06
AL_MA_Split TSW Furnace with DX Cooling OA Rate [cfm] | Split TSW Furnace with DX Cooling OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | [6 empty] | 2021-05-06
AL_MA_SPLIT GSW HEATING COIL Heating Capacity [kBtu/hr] | SPLIT GSW HEATING COIL Heating Capacity [kBtu/hr] | 6.2828 | 6.1758 | 7.1578 | 7.0686 | [6 empty] | 2021-05-06
AL_MA_SPLIT GNW HEATING COIL Heating Capacity [kBtu/hr] | SPLIT GNW HEATING COIL Heating Capacity [kBtu/hr] | 6.2472 | 6.1352 | 7.1027 | 7.0098 | [6 empty] | 2021-05-06
AL_MA_SPLIT OFFICE HEATING COIL Heating Capacity [kBtu/hr] | SPLIT OFFICE HEATING COIL Heating Capacity [kBtu/hr] | 16.5454 | 16.382 | 18.3749 | 18.2143 | [6 empty] | 2021-05-06
AL_MA_SPLIT GNE HEATING COIL Heating Capacity [kBtu/hr] | SPLIT GNE HEATING COIL Heating Capacity [kBtu/hr] | 6.2472 | 6.1352 | 7.1027 | 7.0098 | [6 empty] | 2021-05-06
AL_MA_SPLIT GN1 HEATING COIL Heating Capacity [kBtu/hr] | SPLIT GN1 HEATING COIL Heating Capacity [kBtu/hr] | 4.5509 | 4.5509 | 5.0733 | 5.0309 | [6 empty] | 2021-05-06
AL_MA_SPLIT GN2 HEATING COIL Heating Capacity [kBtu/hr] | SPLIT GN2 HEATING COIL Heating Capacity [kBtu/hr] | 4.5509 | 4.5509 | 5.0733 | 5.0309 | [6 empty] | 2021-05-06
AL_MA_SPLIT GS1 HEATING COIL Heating Capacity [kBtu/hr] | SPLIT GS1 HEATING COIL Heating Capacity [kBtu/hr] | 4.5509 | 4.5509 | 5.0346 | 4.9958 | [6 empty] | 2021-05-06
AL_MA_SPLIT GS2 HEATING COIL Heating Capacity [kBtu/hr] | SPLIT GS2 HEATING COIL Heating Capacity [kBtu/hr] | 4.7953 | 4.7393 | 5.5132 | 5.4704 | [6 empty] | 2021-05-06
AL_MA_SPLIT MSW HEATING COIL Heating Capacity [kBtu/hr] | SPLIT MSW HEATING COIL Heating Capacity [kBtu/hr] | 11.2378 | 11.0279 | 12.8883 | 12.714 | [6 empty] | 2021-05-06
AL_MA_SPLIT MNW HEATING COIL Heating Capacity [kBtu/hr] | SPLIT MNW HEATING COIL Heating Capacity [kBtu/hr] | 11.32 | 11.0975 | 12.9716 | 12.7871 | [6 empty] | 2021-05-06
AL_MA_SPLIT MSE HEATING COIL Heating Capacity [kBtu/hr] | SPLIT MSE HEATING COIL Heating Capacity [kBtu/hr] | 11.2378 | 11.0279 | 12.8883 | 12.714 | [6 empty] | 2021-05-06
AL_MA_SPLIT MNE HEATING COIL Heating Capacity [kBtu/hr] | SPLIT MNE HEATING COIL Heating Capacity [kBtu/hr] | 11.32 | 11.0975 | 12.9716 | 12.7871 | [6 empty] | 2021-05-06
AL_MA_SPLIT MN1 HEATING COIL Heating Capacity [kBtu/hr] | SPLIT MN1 HEATING COIL Heating Capacity [kBtu/hr] | 9.1019 | 9.1019 | 9.8289 | 9.8289 | [6 empty] | 2021-05-06
AL_MA_SPLIT MN2 HEATING COIL Heating Capacity [kBtu/hr] | SPLIT MN2 HEATING COIL Heating Capacity [kBtu/hr] | 9.1019 | 9.1019 | 9.8289 | 9.8289 | [6 empty] | 2021-05-06
AL_MA_SPLIT MS1 HEATING COIL Heating Capacity [kBtu/hr] | SPLIT MS1 HEATING COIL Heating Capacity [kBtu/hr] | 9.1019 | 9.1019 | 9.8289 | 9.8289 | [6 empty] | 2021-05-06
AL_MA_SPLIT MS2 HEATING COIL Heating Capacity [kBtu/hr] | SPLIT MS2 HEATING COIL Heating Capacity [kBtu/hr] | 9.1019 | 9.1019 | 9.8289 | 9.8289 | [6 empty] | 2021-05-06
AL_MA_SPLIT TSW HEATING COIL Heating Capacity [kBtu/hr] | SPLIT TSW HEATING COIL Heating Capacity [kBtu/hr] | 8.5 | 8.3971 | 9.6681 | 9.5828 | [6 empty] | 2021-05-06
AL_MA_SPLIT TNW HEATING COIL Heating Capacity [kBtu/hr] | SPLIT TNW HEATING COIL Heating Capacity [kBtu/hr] | 8.5479 | 8.439 | 9.7175 | 9.6273 | [6 empty] | 2021-05-06
AL_MA_SPLIT TSE HEATING COIL Heating Capacity [kBtu/hr] | SPLIT TSE HEATING COIL Heating Capacity [kBtu/hr] | 8.5 | 8.3971 | 9.6681 | 9.5828 | [6 empty] | 2021-05-06
AL_MA_SPLIT TNE HEATING COIL Heating Capacity [kBtu/hr] | SPLIT TNE HEATING COIL Heating Capacity [kBtu/hr] | 8.5479 | 8.439 | 9.7175 | 9.6273 | [6 empty] | 2021-05-06
AL_MA_SPLIT TN1 HEATING COIL Heating Capacity [kBtu/hr] | SPLIT TN1 HEATING COIL Heating Capacity [kBtu/hr] | 6.4254 | 6.3761 | 7.4468 | 7.4099 | [6 empty] | 2021-05-06
AL_MA_SPLIT TN2 HEATING COIL Heating Capacity [kBtu/hr] | SPLIT TN2 HEATING COIL Heating Capacity [kBtu/hr] | 6.4254 | 6.3761 | 7.4468 | 7.4099 | [6 empty] | 2021-05-06
AL_MA_SPLIT TS1 HEATING COIL Heating Capacity [kBtu/hr] | SPLIT TS1 HEATING COIL Heating Capacity [kBtu/hr] | 6.3704 | 6.327 | 7.3904 | 7.3582 | [6 empty] | 2021-05-06
AL_MA_SPLIT TS2 HEATING COIL Heating Capacity [kBtu/hr] | SPLIT TS2 HEATING COIL Heating Capacity [kBtu/hr] | 6.3704 | 6.327 | 7.3904 | 7.3582 | [6 empty] | 2021-05-06
AL_MA_Split_GSW ERV Flag | Split_GSW ERV Flag | No | Yes | No | Yes | [6 empty] | 2021-05-06
AL_MA_Split_GNW ERV Flag | Split_GNW ERV Flag | No | Yes | No | Yes | [6 empty] | 2021-05-06
AL_MA_Split_GNE ERV Flag | Split_GNE ERV Flag | No | Yes | No | Yes | [6 empty] | 2021-05-06
AL_MA_Split_GN1 ERV Flag | Split_GN1 ERV Flag | No | Yes | No | Yes | [6 empty] | 2021-05-06
AL_MA_Split_GN2 ERV Flag | Split_GN2 ERV Flag | No | Yes | No | Yes | [6 empty] | 2021-05-06
AL_MA_Split_GS1 ERV Flag | Split_GS1 ERV Flag | No | Yes | No | Yes | [6 empty] | 2021-05-06
AL_MA_Split_GS2 ERV Flag | Split_GS2 ERV Flag | No | Yes | No | Yes | [6 empty] | 2021-05-06
AL_MA_Split_MSW ERV Flag | Split_MSW ERV Flag | No | Yes | No | Yes | [6 empty] | 2021-05-06
AL_MA_Split_MNW ERV Flag | Split_MNW ERV Flag | No | Yes | No | Yes | [6 empty] | 2021-05-06
AL_MA_Split_MSE ERV Flag | Split_MSE ERV Flag | No | Yes | No | Yes | [6 empty] | 2021-05-06
AL_MA_Split_MNE ERV Flag | Split_MNE ERV Flag | No | Yes | No | Yes | [6 empty] | 2021-05-06
AL_MA_Split_MN1 ERV Flag | Split_MN1 ERV Flag | No | Yes | No | Yes | [6 empty] | 2021-05-06
AL_MA_Split_MN2 ERV Flag | Split_MN2 ERV Flag | No | Yes | No | Yes | [6 empty] | 2021-05-06
AL_MA_Split_MS1 ERV Flag | Split_MS1 ERV Flag | No | Yes | No | Yes | [6 empty] | 2021-05-06
AL_MA_Split_MS2 ERV Flag | Split_MS2 ERV Flag | No | Yes | No | Yes | [6 empty] | 2021-05-06
AL_MA_Split_TSW ERV Flag | Split_TSW ERV Flag | No | Yes | No | Yes | [6 empty] | 2021-05-06
AL_MA_Split_TNW ERV Flag | Split_TNW ERV Flag | No | Yes | No | Yes | [6 empty] | 2021-05-06
AL_MA_Split_TSE ERV Flag | Split_TSE ERV Flag | No | Yes | No | Yes | [6 empty] | 2021-05-06
AL_MA_Split_TNE ERV Flag | Split_TNE ERV Flag | No | Yes | No | Yes | [6 empty] | 2021-05-06
AL_MA_Split_TN1 ERV Flag | Split_TN1 ERV Flag | No | Yes | No | Yes | [6 empty] | 2021-05-06
AL_MA_Split_TN2 ERV Flag | Split_TN2 ERV Flag | No | Yes | No | Yes | [6 empty] | 2021-05-06
AL_MA_Split_TS1 ERV Flag | Split_TS1 ERV Flag | No | Yes | No | Yes | [6 empty] | 2021-05-06
AL_MA_Split_TS2 ERV Flag | Split_TS2 ERV Flag | No | Yes | No | Yes | [6 empty] | 2021-05-06
id | item | Zone3A(AR-LittleRock-AR) ASHRAE901-state_STD2016 | Zone3A(AR-LittleRock-AR) ASHRAE901-state_STD2019 | Zone4A(AR-Fayetteville-AR) ASHRAE901-state_STD2016 | Zone4A(AR-Fayetteville-AR) ASHRAE901-state_STD2019 | [6 empty] | 2021-05-06
AR_SO_PSZ-AC:1 Cooling Capacity [ton] | PSZ-AC:1 Cooling Capacity [ton] | 2.1102 | 2.011 | 1.9657 | 1.8644 | [6 empty] | 2021-05-06
AR_SO_PSZ-AC:2 Cooling Capacity [ton] | PSZ-AC:2 Cooling Capacity [ton] | 1.898 | 1.8145 | 1.7436 | 1.6728 | [6 empty] | 2021-05-06
AR_SO_PSZ-AC:3 Cooling Capacity [ton] | PSZ-AC:3 Cooling Capacity [ton] | 1.2357 | 1.1941 | 1.198 | 1.1587 | [6 empty] | 2021-05-06
AR_SO_PSZ-AC:4 Cooling Capacity [ton] | PSZ-AC:4 Cooling Capacity [ton] | 1.8739 | 1.7953 | 1.7218 | 1.6327 | [6 empty] | 2021-05-06
AR_SO_PSZ-AC:5 Cooling Capacity [ton] | PSZ-AC:5 Cooling Capacity [ton] | 1.4526 | 1.4078 | 1.4391 | 1.3978 | [6 empty] | 2021-05-06
AR_SO_PSZ-AC:1 Supply Flow Rate [cfm] | PSZ-AC:1 Supply Flow Rate [cfm] | 678.0416 | 635.664 | 678.0416 | 635.664 | [6 empty] | 2021-05-06
AR_SO_PSZ-AC:2 Supply Flow Rate [cfm] | PSZ-AC:2 Supply Flow Rate [cfm] | 656.8528 | 614.4752 | 614.4752 | 593.2864 | [6 empty] | 2021-05-06
AR_SO_PSZ-AC:3 Supply Flow Rate [cfm] | PSZ-AC:3 Supply Flow Rate [cfm] | 466.1536 | 444.9648 | 487.3424 | 466.1536 | [6 empty] | 2021-05-06
AR_SO_PSZ-AC:4 Supply Flow Rate [cfm] | PSZ-AC:4 Supply Flow Rate [cfm] | 635.664 | 593.2864 | 614.4752 | 572.0976 | [6 empty] | 2021-05-06
AR_SO_PSZ-AC:5 Supply Flow Rate [cfm] | PSZ-AC:5 Supply Flow Rate [cfm] | 550.9088 | 529.72 | 593.2864 | 572.0976 | [6 empty] | 2021-05-06
AR_SO_PSZ-AC:1 OA Rate [cfm] | PSZ-AC:1 OA Rate [cfm] | 136.9178 | 136.9178 | 136.9178 | 136.9178 | [6 empty] | 2021-05-06
AR_SO_PSZ-AC:2 OA Rate [cfm] | PSZ-AC:2 OA Rate [cfm] | 103.7925 | 103.7925 | 103.7925 | 103.7925 | [6 empty] | 2021-05-06
AR_SO_PSZ-AC:3 OA Rate [cfm] | PSZ-AC:3 OA Rate [cfm] | 61.5711 | 61.5711 | 61.5711 | 61.5711 | [6 empty] | 2021-05-06
AR_SO_PSZ-AC:4 OA Rate [cfm] | PSZ-AC:4 OA Rate [cfm] | 103.7925 | 103.7925 | 103.7925 | 103.7925 | [6 empty] | 2021-05-06
AR_SO_PSZ-AC:5 OA Rate [cfm] | PSZ-AC:5 OA Rate [cfm] | 61.5711 | 61.5711 | 61.5711 | 61.5711 | [6 empty] | 2021-05-06
AR_SO_PSZ-AC:1 heating Capacity [kBtu/hr] | PSZ-AC:1 heating Capacity [kBtu/hr] | 12.7424 | 12.7424 | 13.5909 | 13.5909 | [6 empty] | 2021-05-06
AR_SO_PSZ-AC:2 heating Capacity [kBtu/hr] | PSZ-AC:2 heating Capacity [kBtu/hr] | 18.1238 | 17.8788 | 18.4901 | 18.2865 | [6 empty] | 2021-05-06
AR_SO_PSZ-AC:3 heating Capacity [kBtu/hr] | PSZ-AC:3 heating Capacity [kBtu/hr] | 11.1691 | 11.0271 | 11.339 | 11.2215 | [6 empty] | 2021-05-06
AR_SO_PSZ-AC:4 heating Capacity [kBtu/hr] | PSZ-AC:4 heating Capacity [kBtu/hr] | 17.9472 | 17.7369 | 18.3913 | 18.2174 | [6 empty] | 2021-05-06
AR_SO_PSZ-AC:5 heating Capacity [kBtu/hr] | PSZ-AC:5 heating Capacity [kBtu/hr] | 11.1691 | 11.0271 | 11.339 | 11.2215 | [6 empty] | 2021-05-06
id | item | Zone3A(AR-LittleRock-AR) ASHRAE901-state_STD2016 | Zone3A(AR-LittleRock-AR) ASHRAE901-state_STD2019 | Zone4A(AR-Fayetteville-AR) ASHRAE901-state_STD2016 | Zone4A(AR-Fayetteville-AR) ASHRAE901-state_STD2019 | [6 empty] | 2021-05-06
AR_LO_CAV_BAS Supply Flow Rate [cfm] | CAV_BAS Supply Flow Rate [cfm] | 11569.0848 | 10700.344 | 12268.3152 | 11378.3856 | [6 empty] | 2021-05-06
AR_LO_VAV_BOT WITH REHEAT Supply Flow Rate [cfm] | VAV_BOT WITH REHEAT Supply Flow Rate [cfm] | 19472.5072 | 18519.0112 | 20468.3808 | 19514.8848 | [6 empty] | 2021-05-06
AR_LO_VAV_MID WITH REHEAT Supply Flow Rate [cfm] | VAV_MID WITH REHEAT Supply Flow Rate [cfm] | 181630.3939 | 172540.3987 | 190084.7251 | 180825.2195 | [6 empty] | 2021-05-06
AR_LO_VAV_TOP WITH REHEAT Supply Flow Rate [cfm] | VAV_TOP WITH REHEAT Supply Flow Rate [cfm] | 19133.4864 | 18307.1232 | 20277.6816 | 19451.3184 | [6 empty] | 2021-05-06
AR_LO_Supply Air Temp. Reset Flag | Supply Air Temp. Reset Flag | No | Yes | Yes | Yes | [6 empty] | 2021-05-06
AR_LO_CAV_BAS OA Rate [cfm] | CAV_BAS OA Rate [cfm] | 2542.8255 | 2542.8255 | 2542.8255 | 2542.8255 | [6 empty] | 2021-05-06
AR_LO_VAV_BOT WITH REHEAT OA Rate [cfm] | VAV_BOT WITH REHEAT OA Rate [cfm] | 5377.8022 | 4302.174 | 5377.8022 | 4302.174 | [6 empty] | 2021-05-06
AR_LO_VAV_MID WITH REHEAT OA Rate [cfm] | VAV_MID WITH REHEAT OA Rate [cfm] | 53777.9373 | 43021.7396 | 53777.9373 | 43021.7396 | [6 empty] | 2021-05-06
AR_LO_VAV_TOP WITH REHEAT OA Rate [cfm] | VAV_TOP WITH REHEAT OA Rate [cfm] | 5377.8022 | 4302.174 | 5377.8022 | 4302.174 | [6 empty] | 2021-05-06
AR_LO_AIRLOOP DATACENTER BASEMENT OA Rate [cfm] | AIRLOOP DATACENTER BASEMENT OA Rate [cfm] | 716.9654 | 716.9654 | 716.9654 | 716.9654 | [6 empty] | 2021-05-06
AR_LO_VAV_bot_WITH_REHEAT ERV Flag | VAV_bot_WITH_REHEAT ERV Flag | Yes | Yes | Yes | Yes | [6 empty] | 2021-05-06
AR_LO_VAV_mid_WITH_REHEAT ERV Flag | VAV_mid_WITH_REHEAT ERV Flag | Yes | Yes | Yes | Yes | [6 empty] | 2021-05-06
AR_LO_VAV_top_WITH_REHEAT ERV Flag | VAV_top_WITH_REHEAT ERV Flag | Yes | Yes | Yes | Yes | [6 empty] | 2021-05-06
AR_LO_COOLSYS1 CHILLER1 Capacity [ton] | COOLSYS1 CHILLER1 Capacity [ton] | 449.7017 | 402.6451 | 429.2355 | 386.3488 | [6 empty] | 2021-05-06
AR_LO_COOLSYS1 CHILLER2 Capacity [ton] | COOLSYS1 CHILLER2 Capacity [ton] | 449.7017 | 402.6451 | 429.2355 | 386.3488 | [6 empty] | 2021-05-06
AR_LO_TOWERWATERSYS COOLTOWER 1 Capacity [ton] | TOWERWATERSYS COOLTOWER 1 Capacity [ton] | 426.8511 | 382.1799 | 407.4231 | 366.7163 | [6 empty] | 2021-05-06
AR_LO_TOWERWATERSYS COOLTOWER 2 Capacity [ton] | TOWERWATERSYS COOLTOWER 2 Capacity [ton] | 426.8511 | 382.1799 | 407.4231 | 366.7163 | [6 empty] | 2021-05-06
AR_LO_HEATSYS1 BOILER Capacity [MMBTU/h] | HEATSYS1 BOILER Capacity [MMBTU/h] | 3968.456 | 3532.1811 | 4260.4008 | 3778.0245 | [6 empty] | 2021-05-06
AR_LO_COOLSYS1 PUMP Flow Rate [gal/min] | COOLSYS1 PUMP Flow Rate [gal/min] | 0 | 0 | 0 | 0 | [6 empty] | 2021-05-06
AR_LO_COOLSYS1 CHILLER1 PUMP Flow Rate [gal/min] | COOLSYS1 CHILLER1 PUMP Flow Rate [gal/min] | 708.9295 | 631.8589 | 676.3317 | 605.7835 | [6 empty] | 2021-05-06
AR_LO_COOLSYS1 CHILLER2 PUMP Flow Rate [gal/min] | COOLSYS1 CHILLER2 PUMP Flow Rate [gal/min] | 708.9295 | 631.8589 | 676.3317 | 605.7835 | [6 empty] | 2021-05-06
AR_LO_COOLSYS1 PUMP SECONDARY Flow Rate [gal/min] | COOLSYS1 PUMP SECONDARY Flow Rate [gal/min] | 1417.859 | 1263.7193 | 1352.665 | 1211.567 | [6 empty] | 2021-05-06
AR_LO_HEATSYS1 PUMP Flow Rate [gal/min] | HEATSYS1 PUMP Flow Rate [gal/min] | 814.5782 | 725.0271 | 874.5035 | 775.4897 | [6 empty] | 2021-05-06
AR_LO_TOWERWATERSYS PUMP Flow Rate [gal/min] | TOWERWATERSYS PUMP Flow Rate [gal/min] | 2481.0511 | 2221.4228 | 2368.0383 | 2131.5515 | [6 empty] | 2021-05-06
AR_LO_PLANT CIRC PUMP Flow Rate [gal/min] | PLANT CIRC PUMP Flow Rate [gal/min] | 208.6663 | 207.7708 | 212.4292 | 211.578 | [6 empty] | 2021-05-06
AR_LO_COOLSYS1 PUMP SECONDARY Pressure setpoint reset [yes,no] | COOLSYS1 PUMP SECONDARY Pressure setpoint reset [yes,no] | pump_ride_on_curve | pump_ride_on_curve | pump_ride_on_curve | pump_ride_on_curve | [6 empty] | 2021-05-06
AR_LO_COOLSYS1 CHILLER1 PUMP Pump Power [hp] | COOLSYS1 CHILLER1 PUMP Pump Power [hp] | 3.8244 | 3.3749 | 3.6486 | 3.2356 | [6 empty] | 2021-05-06
AR_LO_COOLSYS1 CHILLER2 PUMP Pump Power [hp] | COOLSYS1 CHILLER2 PUMP Pump Power [hp] | 3.8244 | 3.3749 | 3.6486 | 3.2356 | [6 empty] | 2021-05-06
AR_LO_COOLSYS1 PUMP SECONDARY Pump Power [hp] | COOLSYS1 PUMP SECONDARY Pump Power [hp] | 22.9466 | 20.2495 | 21.8915 | 19.4138 | [6 empty] | 2021-05-06
AR_LO_HEATSYS1 PUMP Pump Power [hp] | HEATSYS1 PUMP Pump Power [hp] | 17.6076 | 15.5167 | 18.9029 | 16.5967 | [6 empty] | 2021-05-06
AR_LO_TOWERWATERSYS PUMP Pump Power [hp] | TOWERWATERSYS PUMP Pump Power [hp] | 44.4206 | 39.3787 | 42.399 | 37.7849 | [6 empty] | 2021-05-06
AR_LO_PLANT CIRC PUMP Pump Power [hp] | PLANT CIRC PUMP Pump Power [hp] | 4.5027 | 4.439 | 4.5839 | 4.5204 | [6 empty] | 2021-05-06
AR_LO_Datacenter PLANT CIRC PUMP Pump Power [hp] | Datacenter PLANT CIRC PUMP Pump Power [hp] | 4.5027 | 4.439 | 4.5839 | 4.5204 | [6 empty] | 2021-05-06
AR_LO_ZN_VAV_BOXes_Max_Reheat_Water_Flow_GPM | ZN_VAV_BOXes_Max_Reheat_Water_Flow_GPM | 451.4781 | 433.0839 | 457.7188 | 439.3441 | [6 empty] | 2021-05-06
AR_LO_COOLSYS1 PUMP SECONDARY VSD | COOLSYS1 PUMP SECONDARY VSD | No | No | No | No | [6 empty] | 2021-05-06
AR_LO_HEATSYS1 PUMP VSD | HEATSYS1 PUMP VSD | No | No | No | No | [6 empty] | 2021-05-06
AR_LO_DATACENTER BASEMENT Cooling Capacity [ton] | DATACENTER BASEMENT Cooling Capacity [ton] | 122.3809 | 122.0236 | 124.0545 | 123.6883 | [6 empty] | 2021-05-06
AR_LO_DATACENTER BOT Cooling Capacity [ton] | DATACENTER BOT Cooling Capacity [ton] | 2.6522 | 2.6248 | 2.7314 | 2.7074 | [6 empty] | 2021-05-06
AR_LO_DATACENTER MID Cooling Capacity [ton] | DATACENTER MID Cooling Capacity [ton] | 25.2618 | 25.0093 | 26.1544 | 25.9421 | [6 empty] | 2021-05-06
AR_LO_DATACENTER TOP Cooling Capacity [ton] | DATACENTER TOP Cooling Capacity [ton] | 2.558 | 2.5382 | 2.668 | 2.6475 | [6 empty] | 2021-05-06
id | item | Zone3A(AR-LittleRock-AR) ASHRAE901-state_STD2016 | Zone3A(AR-LittleRock-AR) ASHRAE901-state_STD2019 | Zone4A(AR-Fayetteville-AR) ASHRAE901-state_STD2016 | Zone4A(AR-Fayetteville-AR) ASHRAE901-state_STD2019 | [6 empty] | 2021-05-06
AR_RS_PSZ-AC:1 Cooling Capacity [ton] | PSZ-AC:1 Cooling Capacity [ton] | 11.2798 | 10.8959 | 10.7726 | 10.4193 | [6 empty] | 2021-05-06
AR_RS_PSZ-AC:2 Cooling Capacity [ton] | PSZ-AC:2 Cooling Capacity [ton] | 51.8128 | 48.7445 | 52.1678 | 50.0799 | [6 empty] | 2021-05-06
AR_RS_PSZ-AC:3 Cooling Capacity [ton] | PSZ-AC:3 Cooling Capacity [ton] | 7.0942 | 6.9279 | 6.8004 | 6.6319 | [6 empty] | 2021-05-06
AR_RS_PSZ-AC:4 Cooling Capacity [ton] | PSZ-AC:4 Cooling Capacity [ton] | 5.8445 | 5.6777 | 5.5311 | 5.3643 | [6 empty] | 2021-05-06
AR_RS_PSZ-AC:1 Supply Flow Rate [cfm] | PSZ-AC:1 Supply Flow Rate [cfm] | 4216.5712 | 3962.3056 | 4237.76 | 3983.4944 | [6 empty] | 2021-05-06
AR_RS_PSZ-AC:2 Supply Flow Rate [cfm] | PSZ-AC:2 Supply Flow Rate [cfm] | 15552.5792 | 14620.272 | 16103.488 | 15171.1808 | [6 empty] | 2021-05-06
AR_RS_PSZ-AC:3 Supply Flow Rate [cfm] | PSZ-AC:3 Supply Flow Rate [cfm] | 2351.9568 | 2267.2016 | 2394.3344 | 2309.5792 | [6 empty] | 2021-05-06
AR_RS_PSZ-AC:4 Supply Flow Rate [cfm] | PSZ-AC:4 Supply Flow Rate [cfm] | 1822.2368 | 1737.4816 | 1822.2368 | 1758.6704 | [6 empty] | 2021-05-06
AR_RS_PSZ-AC:1 OA Rate [cfm] | PSZ-AC:1 OA Rate [cfm] | 490.669 | 490.669 | 490.669 | 490.669 | [6 empty] | 2021-05-06
AR_RS_PSZ-AC:2 OA Rate [cfm] | PSZ-AC:2 OA Rate [cfm] | 4005.1282 | 4005.1282 | 4005.1282 | 4005.1282 | [6 empty] | 2021-05-06
AR_RS_PSZ-AC:3 OA Rate [cfm] | PSZ-AC:3 OA Rate [cfm] | 377.3937 | 377.3937 | 377.3937 | 377.3937 | [6 empty] | 2021-05-06
AR_RS_PSZ-AC:4 OA Rate [cfm] | PSZ-AC:4 OA Rate [cfm] | 377.3937 | 377.3937 | 377.3937 | 377.3937 | [6 empty] | 2021-05-06
AR_RS_PSZ-AC:1 OA Damper [gravity, motorized] | PSZ-AC:1 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2021-05-06
AR_RS_PSZ-AC:2 OA Damper [gravity, motorized] | PSZ-AC:2 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2021-05-06
AR_RS_PSZ-AC:3 OA Damper [gravity, motorized] | PSZ-AC:3 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2021-05-06
AR_RS_PSZ-AC:4 OA Damper [gravity, motorized] | PSZ-AC:4 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2021-05-06
AR_RS_PSZ-AC:1 Heating Capacity [kBtu/hr] | PSZ-AC:1 Heating Capacity [kBtu/hr] | 182.1779 | 172.0055 | 181.1256 | 170.802 | [6 empty] | 2021-05-06
AR_RS_PSZ-AC:2 Heating Capacity [kBtu/hr] | PSZ-AC:2 Heating Capacity [kBtu/hr] | 784.7029 | 745.9895 | 814.2662 | 776.258 | [6 empty] | 2021-05-06
AR_RS_PSZ-AC:3 Heating Capacity [kBtu/hr] | PSZ-AC:3 Heating Capacity [kBtu/hr] | 107.8316 | 105.0699 | 109.0084 | 106.2774 | [6 empty] | 2021-05-06
AR_RS_PSZ-AC:4 Heating Capacity [kBtu/hr] | PSZ-AC:4 Heating Capacity [kBtu/hr] | 88.1353 | 85.2788 | 88.8619 | 85.9817 | [6 empty] | 2021-05-06
id | item | Zone3A(AR-LittleRock-AR) ASHRAE901-state_STD2016 | Zone3A(AR-LittleRock-AR) ASHRAE901-state_STD2019 | Zone4A(AR-Fayetteville-AR) ASHRAE901-state_STD2016 | Zone4A(AR-Fayetteville-AR) ASHRAE901-state_STD2019 | [6 empty] | 2021-05-06
AR_PS_VAV_POD_1 Cooling Capacity [ton] | VAV_POD_1 Cooling Capacity [ton] | 19.2087 | 18.348 | 20.1474 | 19.1668 | [6 empty] | 2021-05-06
AR_PS_VAV_POD_2 Cooling Capacity [ton] | VAV_POD_2 Cooling Capacity [ton] | 19.2138 | 18.3191 | 20.0469 | 18.9019 | [6 empty] | 2021-05-06
AR_PS_VAV_POD_3 Cooling Capacity [ton] | VAV_POD_3 Cooling Capacity [ton] | 17.4616 | 16.5325 | 18.4656 | 17.3725 | [6 empty] | 2021-05-06
AR_PS_VAV_OTHER Cooling Capacity [ton] | VAV_OTHER Cooling Capacity [ton] | 26.6791 | 25.0895 | 28.4652 | 26.8392 | [6 empty] | 2021-05-06
AR_PS_PSZ-AC_1:6 Cooling Capacity [ton] | PSZ-AC_1:6 Cooling Capacity [ton] | 8.4435 | 8.0653 | 8.7592 | 8.4874 | [6 empty] | 2021-05-06
AR_PS_PSZ-AC_2:5 Cooling Capacity [ton] | PSZ-AC_2:5 Cooling Capacity [ton] | 5.3134 | 5.1391 | 5.864 | 5.8405 | [6 empty] | 2021-05-06
AR_PS_PSZ-AC_2:7 Cooling Capacity [ton] | PSZ-AC_2:7 Cooling Capacity [ton] | 10.5074 | 10.5074 | 10.5074 | 10.5074 | [6 empty] | 2021-05-06
AR_PS_VAV_POD_1 Supply Flow Rate [cfm] | VAV_POD_1 Supply Flow Rate [cfm] | 5763.3536 | 5509.088 | 6038.808 | 5742.1648 | [6 empty] | 2021-05-06
AR_PS_VAV_POD_2 Supply Flow Rate [cfm] | VAV_POD_2 Supply Flow Rate [cfm] | 5763.3536 | 5487.8992 | 6017.6192 | 5678.5984 | [6 empty] | 2021-05-06
AR_PS_VAV_POD_3 Supply Flow Rate [cfm] | VAV_POD_3 Supply Flow Rate [cfm] | 5233.6336 | 4958.1792 | 5551.4656 | 5212.4448 | [6 empty] | 2021-05-06
AR_PS_VAV_OTHER Supply Flow Rate [cfm] | VAV_OTHER Supply Flow Rate [cfm] | 8009.3664 | 7522.024 | 8539.0864 | 8051.744 | [6 empty] | 2021-05-06
AR_PS_PSZ-AC_2:5 Supply Flow Rate [cfm] | PSZ-AC_2:5 Supply Flow Rate [cfm] | 1589.16 | 1546.7824 | 1758.6704 | 1758.6704 | [6 empty] | 2021-05-06
AR_PS_PSZ-AC_1:6 Supply Flow Rate [cfm] | PSZ-AC_1:6 Supply Flow Rate [cfm] | 2542.656 | 2415.5232 | 2669.7888 | 2563.8448 | [6 empty] | 2021-05-06
AR_PS_PSZ-AC_2:7 Supply Flow Rate [cfm] | PSZ-AC_2:7 Supply Flow Rate [cfm] | 3157.1312 | 3157.1312 | 3157.1312 | 3157.1312 | [6 empty] | 2021-05-06
AR_PS_Supply Air Temp. Reset Flag | Supply Air Temp. Reset Flag | No | No | Yes | Yes | [6 empty] | 2021-05-06
AR_PS_VAV_POD_1 OA Rate [cfm] | VAV_POD_1 OA Rate [cfm] | 5764.2223 | 5505.9309 | 6044.6985 | 5751.6362 | [6 empty] | 2021-05-06
AR_PS_VAV_POD_2 OA Rate [cfm] | VAV_POD_2 OA Rate [cfm] | 5764.6037 | 5497.2647 | 6015.7334 | 5672.157 | [6 empty] | 2021-05-06
AR_PS_VAV_POD_3 OA Rate [cfm] | VAV_POD_3 OA Rate [cfm] | 5238.7189 | 4961.1456 | 5540.7229 | 5213.1864 | [6 empty] | 2021-05-06
AR_PS_VAV_OTHER OA Rate [cfm] | VAV_OTHER OA Rate [cfm] | 3736.1787 | 2988.8921 | 3736.1787 | 2988.8921 | [6 empty] | 2021-05-06
AR_PS_PSZ-AC_2:5 OA Rate [cfm] | PSZ-AC_2:5 OA Rate [cfm] | 1152.7343 | 1152.7343 | 1152.7343 | 1152.7343 | [6 empty] | 2021-05-06
AR_PS_PSZ-AC_1:6 OA Rate [cfm] | PSZ-AC_1:6 OA Rate [cfm] | 539.9118 | 539.9118 | 539.9118 | 539.9118 | [6 empty] | 2021-05-06
AR_PS_PSZ-AC_2:7 OA Rate [cfm] | PSZ-AC_2:7 OA Rate [cfm] | 3153.0841 | 3153.0841 | 3153.0841 | 3153.0841 | [6 empty] | 2021-05-06
AR_PS_VAV_POD_1 OA Damper [gravity, motorized] | VAV_POD_1 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2021-05-06
AR_PS_VAV_POD_2 OA Damper [gravity, motorized] | VAV_POD_2 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2021-05-06
AR_PS_VAV_POD_3 OA Damper [gravity, motorized] | VAV_POD_3 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2021-05-06
AR_PS_VAV_OTHER OA Damper [gravity, motorized] | VAV_OTHER OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2021-05-06
AR_PS_PSZ-AC_2:5 OA Damper [gravity, motorized] | PSZ-AC_2:5 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2021-05-06
AR_PS_PSZ-AC_1:6 OA Damper [gravity, motorized] | PSZ-AC_1:6 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2021-05-06
AR_PS_PSZ-AC_2:7 OA Damper [gravity, motorized] | PSZ-AC_2:7 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2021-05-06
AR_PS_VAV_POD_1 (economizer) | VAV_POD_1 (economizer) | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialEnthalpy | [6 empty] | 2021-05-06
AR_PS_VAV_POD_2 (economizer) | VAV_POD_2 (economizer) | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialEnthalpy | [6 empty] | 2021-05-06
AR_PS_VAV_POD_3 (economizer) | VAV_POD_3 (economizer) | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialEnthalpy | [6 empty] | 2021-05-06
AR_PS_VAV_OTHER (economizer) | VAV_OTHER (economizer) | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialEnthalpy | [6 empty] | 2021-05-06
AR_PS_PSZ-AC_2:5 (economizer) | PSZ-AC_2:5 (economizer) | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialEnthalpy | [6 empty] | 2021-05-06
AR_PS_PSZ-AC_1:6 (economizer) | PSZ-AC_1:6 (economizer) | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialEnthalpy | [6 empty] | 2021-05-06
AR_PS_PSZ-AC_2:7 (economizer) | PSZ-AC_2:7 (economizer) | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialEnthalpy | [6 empty] | 2021-05-06
AR_PS_VAV_Pod_1_ERV Flag | VAV_Pod_1_ERV Flag | Yes | Yes | Yes | Yes | [6 empty] | 2021-05-06
AR_PS_VAV_Pod_2_ERV Flag | VAV_Pod_2_ERV Flag | Yes | Yes | Yes | Yes | [6 empty] | 2021-05-06
AR_PS_VAV_Pod_3_ERV Flag | VAV_Pod_3_ERV Flag | Yes | Yes | Yes | Yes | [6 empty] | 2021-05-06
AR_PS_VAV_OTHER_ERV Flag | VAV_OTHER_ERV Flag | Yes | Yes | Yes | Yes | [6 empty] | 2021-05-06
AR_PS_PSZ_AC_2_5_ERV Flag | PSZ_AC_2_5_ERV Flag | Yes | Yes | No | No | [6 empty] | 2021-05-06
AR_PS_PSZ_AC_2_7_ERV Flag | PSZ_AC_2_7_ERV Flag | Yes | Yes | Yes | Yes | [6 empty] | 2021-05-06
AR_PS_HEATSYS1 Capacity [MMBTU/h] | HEATSYS1 Capacity [MMBTU/h] | 0.97554 | 0.92572 | 1.0588 | 1.0016 | [6 empty] | 2021-05-06
AR_PS_HEATSYS1 Flow Rate [gal/min] | HEATSYS1 Flow Rate [gal/min] | 100.1214 | 95.0081 | 108.6687 | 102.8001 | [6 empty] | 2021-05-06
AR_PS_VAV_POD_1 Fan Power [hp] | VAV_POD_1 Fan Power [hp] | 8.5039 | 8.1229 | 8.9195 | 8.4854 | [6 empty] | 2021-05-06
AR_PS_VAV_POD_2 Fan Power [hp] | VAV_POD_2 Fan Power [hp] | 8.5062 | 8.1101 | 8.875 | 8.3681 | [6 empty] | 2021-05-06
AR_PS_VAV_POD_3 Fan Power [hp] | VAV_POD_3 Fan Power [hp] | 7.7305 | 7.3192 | 8.175 | 7.691 | [6 empty] | 2021-05-06
AR_PS_VAV_OTHER Fan Power [hp] | VAV_OTHER Fan Power [hp] | 11.7217 | 11.0233 | 12.5065 | 11.7921 | [6 empty] | 2021-05-06
AR_PS_HEATSYS1 Pump Power [hp] | HEATSYS1 Pump Power [hp] | 2.1642 | 2.0333 | 2.3489 | 2.2001 | [6 empty] | 2021-05-06
AR_PS_PSZ-AC_1:6 Heating Capacity [kBtu/hr] | PSZ-AC_1:6 Heating Capacity [kBtu/hr] | 204.2394 | 195.4735 | 212.1515 | 203.5947 | [6 empty] | 2021-05-06
AR_PS_PSZ-AC_2:5 Heating Capacity [kBtu/hr] | PSZ-AC_2:5 Heating Capacity [kBtu/hr] | 123.4866 | 121.5671 | 135.9023 | 135.6525 | [6 empty] | 2021-05-06
AR_PS_PSZ-AC_2:7 Heating Capacity [kBtu/hr] | PSZ-AC_2:7 Heating Capacity [kBtu/hr] | 293.4452 | 293.4452 | 312.9857 | 312.9857 | [6 empty] | 2021-05-06
AR_PS_ZN_VAV_BOXes_Max_Reheat_Water_Flow_GPM | ZN_VAV_BOXes_Max_Reheat_Water_Flow_GPM | 69.1903 | 65.6783 | 69.5405 | 65.8478 | [6 empty] | 2021-05-06
id | item | Zone3A(AR-LittleRock-AR) ASHRAE901-state_STD2016 | Zone3A(AR-LittleRock-AR) ASHRAE901-state_STD2019 | Zone4A(AR-Fayetteville-AR) ASHRAE901-state_STD2016 | Zone4A(AR-Fayetteville-AR) ASHRAE901-state_STD2019 | [6 empty] | 2021-05-06
AR_SH_SAC_FRONTOFFICE Cooling Capacity [ton] | SAC_FRONTOFFICE Cooling Capacity [ton] | 2.6171 | 2.4852 | 2.5045 | 2.3774 | [6 empty] | 2021-05-06
AR_SH_SAC_FRONTLOUNGE Cooling Capacity [ton] | SAC_FRONTLOUNGE Cooling Capacity [ton] | 6.2527 | 5.9412 | 6.4252 | 6.1051 | [6 empty] | 2021-05-06
AR_SH_SAC_MEETINGROOM Cooling Capacity [ton] | SAC_MEETINGROOM Cooling Capacity [ton] | 2.9878 | 2.8771 | 3.0506 | 2.9551 | [6 empty] | 2021-05-06
AR_SH_SAC_EXC_EMPLGE_RESTRM Cooling Capacity [ton] | SAC_EXC_EMPLGE_RESTRM Cooling Capacity [ton] | 6.3692 | 6.3269 | 6.2776 | 6.2342 | [6 empty] | 2021-05-06
AR_SH_SAC_FO_ADDAQ SUPPLY FAN Supply Flow Rate [cfm] | SAC_FO_ADDAQ SUPPLY FAN Supply Flow Rate [cfm] | 826.3632 | 762.7968 | 826.3632 | 762.7968 | [6 empty] | 2021-05-06
AR_SH_SAC_FL_ADDAQ SUPPLY FAN Supply Flow Rate [cfm] | SAC_FL_ADDAQ SUPPLY FAN Supply Flow Rate [cfm] | 1885.8032 | 1779.8592 | 1928.1808 | 1822.2368 | [6 empty] | 2021-05-06
AR_SH_SAC_MR_ADDAQ SUPPLY FAN Supply Flow Rate [cfm] | SAC_MR_ADDAQ SUPPLY FAN Supply Flow Rate [cfm] | 889.9296 | 868.7408 | 911.1184 | 889.9296 | [6 empty] | 2021-05-06
AR_SH_SAC_EXC_ADDAQ SUPPLY FAN Supply Flow Rate [cfm] | SAC_EXC_ADDAQ SUPPLY FAN Supply Flow Rate [cfm] | 2182.4464 | 2161.2576 | 2288.3904 | 2267.2016 | [6 empty] | 2021-05-06
AR_SH_SAC_Exc_EmpLge_RestRm OA Rate [cfm] | SAC_Exc_EmpLge_RestRm OA Rate [cfm] | 199.9928 | 199.9928 | 199.9928 | 199.9928 | [6 empty] | 2021-05-06
AR_SH_SAC_FrontLounge OA Rate [cfm] | SAC_FrontLounge OA Rate [cfm] | 500.0133 | 500.0133 | 500.0133 | 500.0133 | [6 empty] | 2021-05-06
AR_SH_SAC_FrontOffice OA Rate [cfm] | SAC_FrontOffice OA Rate [cfm] | 119.2938 | 119.2938 | 119.2938 | 119.2938 | [6 empty] | 2021-05-06
AR_SH_SAC_MeetingRoom OA Rate [cfm] | SAC_MeetingRoom OA Rate [cfm] | 267.7629 | 267.7629 | 267.7629 | 267.7629 | [6 empty] | 2021-05-06
AR_SH_SAC_FrontLounge OA Damper [gravity, motorized] | SAC_FrontLounge OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2021-05-06
AR_SH_SAC_FrontOffice (economizer) | SAC_FrontOffice (economizer) | No | No | No | No | [6 empty] | 2021-05-06
AR_SH_SAC_FrontLounge (economizer) | SAC_FrontLounge (economizer) | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialEnthalpy | [6 empty] | 2021-05-06
AR_SH_SAC_MeetingRoom (economizer) | SAC_MeetingRoom (economizer) | No | No | No | No | [6 empty] | 2021-05-06
AR_SH_SAC_Exc_EmpLge_RestRm (economizer) | SAC_Exc_EmpLge_RestRm (economizer) | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialEnthalpy | [6 empty] | 2021-05-06
AR_SH_SAC_FRONTOFFICE Heating Capacity [kBtu/hr] | SAC_FRONTOFFICE Heating Capacity [kBtu/hr] | 36.6186 | 34.6448 | 36.9671 | 34.7905 | [6 empty] | 2021-05-06
AR_SH_SAC_FRONTLOUNGE Heating Capacity [kBtu/hr] | SAC_FRONTLOUNGE Heating Capacity [kBtu/hr] | 96.7303 | 93.3215 | 99.8706 | 96.4914 | [6 empty] | 2021-05-06
AR_SH_SAC_MEETINGROOM Heating Capacity [kBtu/hr] | SAC_MEETINGROOM Heating Capacity [kBtu/hr] | 47.8534 | 46.6419 | 49.3623 | 48.3543 | [6 empty] | 2021-05-06
AR_SH_SAC_EXC_EMPLGE_RESTRM Heating Capacity [kBtu/hr] | SAC_EXC_EMPLGE_RESTRM Heating Capacity [kBtu/hr] | 91.0566 | 90.4083 | 93.2055 | 92.5343 | [6 empty] | 2021-05-06
id | item | Zone3A(AR-LittleRock-AR) ASHRAE901-state_STD2016 | Zone3A(AR-LittleRock-AR) ASHRAE901-state_STD2019 | Zone4A(AR-Fayetteville-AR) ASHRAE901-state_STD2016 | Zone4A(AR-Fayetteville-AR) ASHRAE901-state_STD2019 | [6 empty] | 2021-05-06
AR_MA_SPLIT GSW COOLING COIL Cooling Capacity [ton] | SPLIT GSW COOLING COIL Cooling Capacity [ton] | 0.96493 | 0.95375 | 0.94793 | 0.93392 | [6 empty] | 2021-05-06
AR_MA_SPLIT GNW COOLING COIL Cooling Capacity [ton] | SPLIT GNW COOLING COIL Cooling Capacity [ton] | 0.94508 | 0.93385 | 0.92197 | 0.90812 | [6 empty] | 2021-05-06
AR_MA_SPLIT OFFICE COOLING COIL Cooling Capacity [ton] | SPLIT OFFICE COOLING COIL Cooling Capacity [ton] | 1.807 | 1.7014 | 1.7528 | 1.6612 | [6 empty] | 2021-05-06
AR_MA_SPLIT GNE COOLING COIL Cooling Capacity [ton] | SPLIT GNE COOLING COIL Cooling Capacity [ton] | 0.84131 | 0.83178 | 0.80523 | 0.79306 | [6 empty] | 2021-05-06
AR_MA_SPLIT GN1 COOLING COIL Cooling Capacity [ton] | SPLIT GN1 COOLING COIL Cooling Capacity [ton] | 0.72845 | 0.71916 | 0.67233 | 0.66258 | [6 empty] | 2021-05-06
AR_MA_SPLIT GN2 COOLING COIL Cooling Capacity [ton] | SPLIT GN2 COOLING COIL Cooling Capacity [ton] | 0.72679 | 0.71751 | 0.67 | 0.66031 | [6 empty] | 2021-05-06
AR_MA_SPLIT GS1 COOLING COIL Cooling Capacity [ton] | SPLIT GS1 COOLING COIL Cooling Capacity [ton] | 0.74318 | 0.73432 | 0.7071 | 0.69689 | [6 empty] | 2021-05-06
AR_MA_SPLIT GS2 COOLING COIL Cooling Capacity [ton] | SPLIT GS2 COOLING COIL Cooling Capacity [ton] | 0.77881 | 0.76605 | 0.73788 | 0.72397 | [6 empty] | 2021-05-06
AR_MA_SPLIT MSW COOLING COIL Cooling Capacity [ton] | SPLIT MSW COOLING COIL Cooling Capacity [ton] | 2.1552 | 2.1272 | 2.1713 | 2.1398 | [6 empty] | 2021-05-06
AR_MA_SPLIT MNW COOLING COIL Cooling Capacity [ton] | SPLIT MNW COOLING COIL Cooling Capacity [ton] | 2.1204 | 2.0977 | 2.1352 | 2.1041 | [6 empty] | 2021-05-06
AR_MA_SPLIT MSE COOLING COIL Cooling Capacity [ton] | SPLIT MSE COOLING COIL Cooling Capacity [ton] | 1.9527 | 1.9294 | 1.8757 | 1.8493 | [6 empty] | 2021-05-06
AR_MA_SPLIT MNE COOLING COIL Cooling Capacity [ton] | SPLIT MNE COOLING COIL Cooling Capacity [ton] | 1.8469 | 1.8262 | 1.7259 | 1.7406 | [6 empty] | 2021-05-06
AR_MA_SPLIT MN1 COOLING COIL Cooling Capacity [ton] | SPLIT MN1 COOLING COIL Cooling Capacity [ton] | 1.5295 | 1.5112 | 1.4318 | 1.4131 | [6 empty] | 2021-05-06
AR_MA_SPLIT MN2 COOLING COIL Cooling Capacity [ton] | SPLIT MN2 COOLING COIL Cooling Capacity [ton] | 1.5252 | 1.5069 | 1.4256 | 1.407 | [6 empty] | 2021-05-06
AR_MA_SPLIT MS1 COOLING COIL Cooling Capacity [ton] | SPLIT MS1 COOLING COIL Cooling Capacity [ton] | 1.5675 | 1.549 | 1.4949 | 1.4757 | [6 empty] | 2021-05-06
AR_MA_SPLIT MS2 COOLING COIL Cooling Capacity [ton] | SPLIT MS2 COOLING COIL Cooling Capacity [ton] | 1.5634 | 1.545 | 1.4892 | 1.4701 | [6 empty] | 2021-05-06
AR_MA_SPLIT TSW COOLING COIL Cooling Capacity [ton] | SPLIT TSW COOLING COIL Cooling Capacity [ton] | 1.3323 | 1.3202 | 1.3593 | 1.342 | [6 empty] | 2021-05-06
AR_MA_SPLIT TNW COOLING COIL Cooling Capacity [ton] | SPLIT TNW COOLING COIL Cooling Capacity [ton] | 1.2976 | 1.2862 | 1.3346 | 1.3177 | [6 empty] | 2021-05-06
AR_MA_SPLIT TSE COOLING COIL Cooling Capacity [ton] | SPLIT TSE COOLING COIL Cooling Capacity [ton] | 1.2301 | 1.2184 | 1.2143 | 1.2009 | [6 empty] | 2021-05-06
AR_MA_SPLIT TNE COOLING COIL Cooling Capacity [ton] | SPLIT TNE COOLING COIL Cooling Capacity [ton] | 1.179 | 1.1678 | 1.1609 | 1.1481 | [6 empty] | 2021-05-06
AR_MA_SPLIT TN1 COOLING COIL Cooling Capacity [ton] | SPLIT TN1 COOLING COIL Cooling Capacity [ton] | 0.95013 | 0.94125 | 0.92365 | 0.914 | [6 empty] | 2021-05-06
AR_MA_SPLIT TN2 COOLING COIL Cooling Capacity [ton] | SPLIT TN2 COOLING COIL Cooling Capacity [ton] | 0.94521 | 0.93635 | 0.91907 | 0.90733 | [6 empty] | 2021-05-06
AR_MA_SPLIT TS1 COOLING COIL Cooling Capacity [ton] | SPLIT TS1 COOLING COIL Cooling Capacity [ton] | 1.0217 | 1.0117 | 1.0044 | 0.99359 | [6 empty] | 2021-05-06
AR_MA_SPLIT TS2 COOLING COIL Cooling Capacity [ton] | SPLIT TS2 COOLING COIL Cooling Capacity [ton] | 1.0234 | 1.0134 | 1.0067 | 0.99596 | [6 empty] | 2021-05-06
AR_MA_Split GN1 Furnace with DX Cooling OA Rate [cfm] | Split GN1 Furnace with DX Cooling OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | [6 empty] | 2021-05-06
AR_MA_Split GN2 Furnace with DX Cooling OA Rate [cfm] | Split GN2 Furnace with DX Cooling OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | [6 empty] | 2021-05-06
AR_MA_Split GNE Furnace with DX Cooling OA Rate [cfm] | Split GNE Furnace with DX Cooling OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | [6 empty] | 2021-05-06
AR_MA_Split GNW Furnace with DX Cooling OA Rate [cfm] | Split GNW Furnace with DX Cooling OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | [6 empty] | 2021-05-06
AR_MA_Split GS1 Furnace with DX Cooling OA Rate [cfm] | Split GS1 Furnace with DX Cooling OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | [6 empty] | 2021-05-06
AR_MA_Split GS2 Furnace with DX Cooling OA Rate [cfm] | Split GS2 Furnace with DX Cooling OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | [6 empty] | 2021-05-06
AR_MA_Split GSW Furnace with DX Cooling OA Rate [cfm] | Split GSW Furnace with DX Cooling OA Rate [cfm] | 56.9945 | 56.9945 | 56.9945 | 56.9945 | [6 empty] | 2021-05-06
AR_MA_Split MN1 Furnace with DX Cooling OA Rate [cfm] | Split MN1 Furnace with DX Cooling OA Rate [cfm] | 109.9824 | 109.9824 | 109.9824 | 109.9824 | [6 empty] | 2021-05-06
AR_MA_Split MN2 Furnace with DX Cooling OA Rate [cfm] | Split MN2 Furnace with DX Cooling OA Rate [cfm] | 109.9824 | 109.9824 | 109.9824 | 109.9824 | [6 empty] | 2021-05-06
AR_MA_Split MNE Furnace with DX Cooling OA Rate [cfm] | Split MNE Furnace with DX Cooling OA Rate [cfm] | 109.9824 | 109.9824 | 109.9824 | 109.9824 | [6 empty] | 2021-05-06
AR_MA_Split MNW Furnace with DX Cooling OA Rate [cfm] | Split MNW Furnace with DX Cooling OA Rate [cfm] | 109.9824 | 109.9824 | 109.9824 | 109.9824 | [6 empty] | 2021-05-06
AR_MA_Split MS1 Furnace with DX Cooling OA Rate [cfm] | Split MS1 Furnace with DX Cooling OA Rate [cfm] | 109.9824 | 109.9824 | 109.9824 | 109.9824 | [6 empty] | 2021-05-06
AR_MA_Split MS2 Furnace with DX Cooling OA Rate [cfm] | Split MS2 Furnace with DX Cooling OA Rate [cfm] | 109.9824 | 109.9824 | 109.9824 | 109.9824 | [6 empty] | 2021-05-06
AR_MA_Split MSE Furnace with DX Cooling OA Rate [cfm] | Split MSE Furnace with DX Cooling OA Rate [cfm] | 109.9824 | 109.9824 | 109.9824 | 109.9824 | [6 empty] | 2021-05-06
AR_MA_Split MSW Furnace with DX Cooling OA Rate [cfm] | Split MSW Furnace with DX Cooling OA Rate [cfm] | 109.9824 | 109.9824 | 109.9824 | 109.9824 | [6 empty] | 2021-05-06
AR_MA_Split Office Furnace with DX Cooling OA Rate [cfm] | Split Office Furnace with DX Cooling OA Rate [cfm] | 80.7372 | 80.7372 | 80.7372 | 80.7372 | [6 empty] | 2021-05-06
AR_MA_Split TN1 Furnace with DX Cooling OA Rate [cfm] | Split TN1 Furnace with DX Cooling OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | [6 empty] | 2021-05-06
AR_MA_Split TN2 Furnace with DX Cooling OA Rate [cfm] | Split TN2 Furnace with DX Cooling OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | [6 empty] | 2021-05-06
AR_MA_Split TNE Furnace with DX Cooling OA Rate [cfm] | Split TNE Furnace with DX Cooling OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | [6 empty] | 2021-05-06
AR_MA_Split TNW Furnace with DX Cooling OA Rate [cfm] | Split TNW Furnace with DX Cooling OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | [6 empty] | 2021-05-06
AR_MA_Split TS1 Furnace with DX Cooling OA Rate [cfm] | Split TS1 Furnace with DX Cooling OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | [6 empty] | 2021-05-06
AR_MA_Split TS2 Furnace with DX Cooling OA Rate [cfm] | Split TS2 Furnace with DX Cooling OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | [6 empty] | 2021-05-06
AR_MA_Split TSE Furnace with DX Cooling OA Rate [cfm] | Split TSE Furnace with DX Cooling OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | [6 empty] | 2021-05-06
AR_MA_Split TSW Furnace with DX Cooling OA Rate [cfm] | Split TSW Furnace with DX Cooling OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | [6 empty] | 2021-05-06
AR_MA_SPLIT GSW HEATING COIL Heating Capacity [kBtu/hr] | SPLIT GSW HEATING COIL Heating Capacity [kBtu/hr] | 7.8133 | 7.7161 | 8.8052 | 8.8646 | [6 empty] | 2021-05-06
AR_MA_SPLIT GNW HEATING COIL Heating Capacity [kBtu/hr] | SPLIT GNW HEATING COIL Heating Capacity [kBtu/hr] | 7.766 | 7.6643 | 8.7389 | 8.7985 | [6 empty] | 2021-05-06
AR_MA_SPLIT OFFICE HEATING COIL Heating Capacity [kBtu/hr] | SPLIT OFFICE HEATING COIL Heating Capacity [kBtu/hr] | 19.5275 | 19.352 | 21.2249 | 21.316 | [6 empty] | 2021-05-06
AR_MA_SPLIT GNE HEATING COIL Heating Capacity [kBtu/hr] | SPLIT GNE HEATING COIL Heating Capacity [kBtu/hr] | 7.766 | 7.6643 | 8.7389 | 8.7985 | [6 empty] | 2021-05-06
AR_MA_SPLIT GN1 HEATING COIL Heating Capacity [kBtu/hr] | SPLIT GN1 HEATING COIL Heating Capacity [kBtu/hr] | 5.5505 | 5.5029 | 6.3805 | 6.4401 | [6 empty] | 2021-05-06
AR_MA_SPLIT GN2 HEATING COIL Heating Capacity [kBtu/hr] | SPLIT GN2 HEATING COIL Heating Capacity [kBtu/hr] | 5.5505 | 5.5029 | 6.3805 | 6.4401 | [6 empty] | 2021-05-06
AR_MA_SPLIT GS1 HEATING COIL Heating Capacity [kBtu/hr] | SPLIT GS1 HEATING COIL Heating Capacity [kBtu/hr] | 5.4995 | 5.4562 | 6.3341 | 6.3935 | [6 empty] | 2021-05-06
AR_MA_SPLIT GS2 HEATING COIL Heating Capacity [kBtu/hr] | SPLIT GS2 HEATING COIL Heating Capacity [kBtu/hr] | 5.9986 | 5.9502 | 6.8266 | 6.8874 | [6 empty] | 2021-05-06
AR_MA_SPLIT MSW HEATING COIL Heating Capacity [kBtu/hr] | SPLIT MSW HEATING COIL Heating Capacity [kBtu/hr] | 14.4351 | 14.2434 | 16.0426 | 16.171 | [6 empty] | 2021-05-06
AR_MA_SPLIT MNW HEATING COIL Heating Capacity [kBtu/hr] | SPLIT MNW HEATING COIL Heating Capacity [kBtu/hr] | 14.5314 | 14.3285 | 16.1232 | 16.2517 | [6 empty] | 2021-05-06
AR_MA_SPLIT MSE HEATING COIL Heating Capacity [kBtu/hr] | SPLIT MSE HEATING COIL Heating Capacity [kBtu/hr] | 14.4351 | 14.2434 | 16.0426 | 16.171 | [6 empty] | 2021-05-06
AR_MA_SPLIT MNE HEATING COIL Heating Capacity [kBtu/hr] | SPLIT MNE HEATING COIL Heating Capacity [kBtu/hr] | 14.5314 | 14.3285 | 16.1232 | 16.2517 | [6 empty] | 2021-05-06
AR_MA_SPLIT MN1 HEATING COIL Heating Capacity [kBtu/hr] | SPLIT MN1 HEATING COIL Heating Capacity [kBtu/hr] | 10.2356 | 10.2356 | 11.0479 | 11.1733 | [6 empty] | 2021-05-06
AR_MA_SPLIT MN2 HEATING COIL Heating Capacity [kBtu/hr] | SPLIT MN2 HEATING COIL Heating Capacity [kBtu/hr] | 10.2356 | 10.2356 | 11.0479 | 11.1733 | [6 empty] | 2021-05-06
AR_MA_SPLIT MS1 HEATING COIL Heating Capacity [kBtu/hr] | SPLIT MS1 HEATING COIL Heating Capacity [kBtu/hr] | 10.2356 | 10.2356 | 10.9755 | 11.1009 | [6 empty] | 2021-05-06
AR_MA_SPLIT MS2 HEATING COIL Heating Capacity [kBtu/hr] | SPLIT MS2 HEATING COIL Heating Capacity [kBtu/hr] | 10.2356 | 10.2356 | 10.9755 | 11.1009 | [6 empty] | 2021-05-06
AR_MA_SPLIT TSW HEATING COIL Heating Capacity [kBtu/hr] | SPLIT TSW HEATING COIL Heating Capacity [kBtu/hr] | 10.6484 | 10.5547 | 11.3655 | 11.4271 | [6 empty] | 2021-05-06
AR_MA_SPLIT TNW HEATING COIL Heating Capacity [kBtu/hr] | SPLIT TNW HEATING COIL Heating Capacity [kBtu/hr] | 10.7047 | 10.6054 | 11.414 | 11.4757 | [6 empty] | 2021-05-06
AR_MA_SPLIT TSE HEATING COIL Heating Capacity [kBtu/hr] | SPLIT TSE HEATING COIL Heating Capacity [kBtu/hr] | 10.6484 | 10.5547 | 11.3655 | 11.4271 | [6 empty] | 2021-05-06
AR_MA_SPLIT TNE HEATING COIL Heating Capacity [kBtu/hr] | SPLIT TNE HEATING COIL Heating Capacity [kBtu/hr] | 10.7047 | 10.6054 | 11.414 | 11.4757 | [6 empty] | 2021-05-06
AR_MA_SPLIT TN1 HEATING COIL Heating Capacity [kBtu/hr] | SPLIT TN1 HEATING COIL Heating Capacity [kBtu/hr] | 8.161 | 8.1184 | 8.6983 | 8.7599 | [6 empty] | 2021-05-06
AR_MA_SPLIT TN2 HEATING COIL Heating Capacity [kBtu/hr] | SPLIT TN2 HEATING COIL Heating Capacity [kBtu/hr] | 8.161 | 8.1184 | 8.6983 | 8.7599 | [6 empty] | 2021-05-06
AR_MA_SPLIT TS1 HEATING COIL Heating Capacity [kBtu/hr] | SPLIT TS1 HEATING COIL Heating Capacity [kBtu/hr] | 8.0978 | 8.0606 | 8.6427 | 8.7042 | [6 empty] | 2021-05-06
AR_MA_SPLIT TS2 HEATING COIL Heating Capacity [kBtu/hr] | SPLIT TS2 HEATING COIL Heating Capacity [kBtu/hr] | 8.0978 | 8.0606 | 8.6427 | 8.7042 | [6 empty] | 2021-05-06
AR_MA_Split_GSW ERV Flag | Split_GSW ERV Flag | No | Yes | Yes | Yes | [6 empty] | 2021-05-06
AR_MA_Split_GNW ERV Flag | Split_GNW ERV Flag | No | Yes | Yes | Yes | [6 empty] | 2021-05-06
AR_MA_Split_GNE ERV Flag | Split_GNE ERV Flag | No | Yes | Yes | Yes | [6 empty] | 2021-05-06
AR_MA_Split_GN1 ERV Flag | Split_GN1 ERV Flag | No | Yes | Yes | Yes | [6 empty] | 2021-05-06
AR_MA_Split_GN2 ERV Flag | Split_GN2 ERV Flag | No | Yes | Yes | Yes | [6 empty] | 2021-05-06
AR_MA_Split_GS1 ERV Flag | Split_GS1 ERV Flag | No | Yes | Yes | Yes | [6 empty] | 2021-05-06
AR_MA_Split_GS2 ERV Flag | Split_GS2 ERV Flag | No | Yes | Yes | Yes | [6 empty] | 2021-05-06
AR_MA_Split_MSW ERV Flag | Split_MSW ERV Flag | No | Yes | Yes | Yes | [6 empty] | 2021-05-06
AR_MA_Split_MNW ERV Flag | Split_MNW ERV Flag | No | Yes | Yes | Yes | [6 empty] | 2021-05-06
AR_MA_Split_MSE ERV Flag | Split_MSE ERV Flag | No | Yes | Yes | Yes | [6 empty] | 2021-05-06
AR_MA_Split_MNE ERV Flag | Split_MNE ERV Flag | No | Yes | Yes | Yes | [6 empty] | 2021-05-06
AR_MA_Split_MN1 ERV Flag | Split_MN1 ERV Flag | No | Yes | Yes | Yes | [6 empty] | 2021-05-06
AR_MA_Split_MN2 ERV Flag | Split_MN2 ERV Flag | No | Yes | Yes | Yes | [6 empty] | 2021-05-06
AR_MA_Split_MS1 ERV Flag | Split_MS1 ERV Flag | No | Yes | Yes | Yes | [6 empty] | 2021-05-06
AR_MA_Split_MS2 ERV Flag | Split_MS2 ERV Flag | No | Yes | Yes | Yes | [6 empty] | 2021-05-06
AR_MA_Split_TSW ERV Flag | Split_TSW ERV Flag | No | Yes | Yes | Yes | [6 empty] | 2021-05-06
AR_MA_Split_TNW ERV Flag | Split_TNW ERV Flag | No | Yes | Yes | Yes | [6 empty] | 2021-05-06
AR_MA_Split_TSE ERV Flag | Split_TSE ERV Flag | No | Yes | Yes | Yes | [6 empty] | 2021-05-06
AR_MA_Split_TNE ERV Flag | Split_TNE ERV Flag | No | Yes | Yes | Yes | [6 empty] | 2021-05-06
AR_MA_Split_TN1 ERV Flag | Split_TN1 ERV Flag | No | Yes | Yes | Yes | [6 empty] | 2021-05-06
AR_MA_Split_TN2 ERV Flag | Split_TN2 ERV Flag | No | Yes | Yes | Yes | [6 empty] | 2021-05-06
AR_MA_Split_TS1 ERV Flag | Split_TS1 ERV Flag | No | Yes | Yes | Yes | [6 empty] | 2021-05-06
AR_MA_Split_TS2 ERV Flag | Split_TS2 ERV Flag | No | Yes | Yes | Yes | [6 empty] | 2021-05-06
id | item | Zone2B(AZ-Tucson-AZ) ASHRAE901-state_STD2016 | Zone2B(AZ-Tucson-AZ) ASHRAE901-state_STD2019 | Zone3B(AZ-Kingman-AZ) ASHRAE901-state_STD2016 | Zone3B(AZ-Kingman-AZ) ASHRAE901-state_STD2019 | Zone4B(AZ-Prescott-AZ) ASHRAE901-state_STD2016 | Zone4B(AZ-Prescott-AZ) ASHRAE901-state_STD2019 | Zone5B(AZ-Gallup-NM) ASHRAE901-state_STD2016 | Zone5B(AZ-Gallup-NM) ASHRAE901-state_STD2019 |  |  | 2021-05-06
AZ_SO_PSZ-AC:1 Cooling Capacity [ton] | PSZ-AC:1 Cooling Capacity [ton] | 1.8993 | 1.7928 | 1.7763 | 1.6743 | 1.716 | 1.5985 | 1.7691 | 1.6436 |  |  | 2021-05-06
AZ_SO_PSZ-AC:2 Cooling Capacity [ton] | PSZ-AC:2 Cooling Capacity [ton] | 1.8663 | 1.7754 | 1.6931 | 1.6156 | 1.4991 | 1.4173 | 1.4307 | 1.3449 |  |  | 2021-05-06
AZ_SO_PSZ-AC:3 Cooling Capacity [ton] | PSZ-AC:3 Cooling Capacity [ton] | 1.2048 | 1.1445 | 1.1972 | 1.147 | 1.1898 | 1.1391 | 1.1844 | 1.1309 |  |  | 2021-05-06
AZ_SO_PSZ-AC:4 Cooling Capacity [ton] | PSZ-AC:4 Cooling Capacity [ton] | 1.8702 | 1.7711 | 1.6684 | 1.5841 | 1.4754 | 1.3807 | 1.4132 | 1.3075 |  |  | 2021-05-06
AZ_SO_PSZ-AC:5 Cooling Capacity [ton] | PSZ-AC:5 Cooling Capacity [ton] | 1.442 | 1.38 | 1.4276 | 1.3743 | 1.4531 | 1.4007 | 1.5035 | 1.4475 |  |  | 2021-05-06
AZ_SO_PSZ-AC:1 Supply Flow Rate [cfm] | PSZ-AC:1 Supply Flow Rate [cfm] | 762.7968 | 720.4192 | 762.7968 | 720.4192 | 762.7968 | 720.4192 | 805.1744 | 741.608 |  |  | 2021-05-06
AZ_SO_PSZ-AC:2 Supply Flow Rate [cfm] | PSZ-AC:2 Supply Flow Rate [cfm] | 783.9856 | 741.608 | 762.7968 | 720.4192 | 678.0416 | 635.664 | 635.664 | 614.4752 |  |  | 2021-05-06
AZ_SO_PSZ-AC:3 Supply Flow Rate [cfm] | PSZ-AC:3 Supply Flow Rate [cfm] | 550.9088 | 508.5312 | 529.72 | 508.5312 | 529.72 | 508.5312 | 529.72 | 508.5312 |  |  | 2021-05-06
AZ_SO_PSZ-AC:4 Supply Flow Rate [cfm] | PSZ-AC:4 Supply Flow Rate [cfm] | 783.9856 | 720.4192 | 741.608 | 699.2304 | 656.8528 | 614.4752 | 635.664 | 593.2864 |  |  | 2021-05-06
AZ_SO_PSZ-AC:5 Supply Flow Rate [cfm] | PSZ-AC:5 Supply Flow Rate [cfm] | 656.8528 | 614.4752 | 635.664 | 614.4752 | 656.8528 | 635.664 | 678.0416 | 656.8528 |  |  | 2021-05-06
AZ_SO_PSZ-AC:1 OA Rate [cfm] | PSZ-AC:1 OA Rate [cfm] | 136.9178 | 136.9178 | 136.9178 | 136.9178 | 136.9178 | 136.9178 | 136.9178 | 136.9178 |  |  | 2021-05-06
AZ_SO_PSZ-AC:2 OA Rate [cfm] | PSZ-AC:2 OA Rate [cfm] | 103.7925 | 103.7925 | 103.7925 | 103.7925 | 103.7925 | 103.7925 | 103.7925 | 103.7925 |  |  | 2021-05-06
AZ_SO_PSZ-AC:3 OA Rate [cfm] | PSZ-AC:3 OA Rate [cfm] | 61.5711 | 61.5711 | 61.5711 | 61.5711 | 61.5711 | 61.5711 | 61.5711 | 61.5711 |  |  | 2021-05-06
AZ_SO_PSZ-AC:4 OA Rate [cfm] | PSZ-AC:4 OA Rate [cfm] | 103.7925 | 103.7925 | 103.7925 | 103.7925 | 103.7925 | 103.7925 | 103.7925 | 103.7925 |  |  | 2021-05-06
AZ_SO_PSZ-AC:5 OA Rate [cfm] | PSZ-AC:5 OA Rate [cfm] | 61.5711 | 61.5711 | 61.5711 | 61.5711 | 61.5711 | 61.5711 | 61.5711 | 61.5711 |  |  | 2021-05-06
AZ_SO_PSZ-AC:1 heating Capacity [kBtu/hr] | PSZ-AC:1 heating Capacity [kBtu/hr] | 9.7743 | 9.7743 | 10.419 | 10.419 | 10.6616 | 10.6616 | 12.3338 | 12.3053 |  |  | 2021-05-06
AZ_SO_PSZ-AC:2 heating Capacity [kBtu/hr] | PSZ-AC:2 heating Capacity [kBtu/hr] | 12.016 | 11.5549 | 13.7011 | 13.4865 | 14.0628 | 13.888 | 16.8792 | 16.6588 |  |  | 2021-05-06
AZ_SO_PSZ-AC:3 heating Capacity [kBtu/hr] | PSZ-AC:3 heating Capacity [kBtu/hr] | 7.2612 | 7.0058 | 8.3336 | 8.2147 | 8.5152 | 8.4217 | 10.1731 | 10.0513 |  |  | 2021-05-06
AZ_SO_PSZ-AC:4 heating Capacity [kBtu/hr] | PSZ-AC:4 heating Capacity [kBtu/hr] | 11.6628 | 11.3011 | 13.4662 | 13.2905 | 13.8579 | 13.7198 | 16.6442 | 16.4677 |  |  | 2021-05-06
AZ_SO_PSZ-AC:5 heating Capacity [kBtu/hr] | PSZ-AC:5 heating Capacity [kBtu/hr] | 7.2265 | 6.9819 | 8.3013 | 8.187 | 8.5436 | 8.4469 | 10.1468 | 10.0275 |  |  | 2021-05-06
id | item | Zone2B(AZ-Tucson-AZ) ASHRAE901-state_STD2016 | Zone2B(AZ-Tucson-AZ) ASHRAE901-state_STD2019 | Zone3B(AZ-Kingman-AZ) ASHRAE901-state_STD2016 | Zone3B(AZ-Kingman-AZ) ASHRAE901-state_STD2019 | Zone4B(AZ-Prescott-AZ) ASHRAE901-state_STD2016 | Zone4B(AZ-Prescott-AZ) ASHRAE901-state_STD2019 | Zone5B(AZ-Gallup-NM) ASHRAE901-state_STD2016 | Zone5B(AZ-Gallup-NM) ASHRAE901-state_STD2019 |  |  | 2021-05-06
AZ_LO_CAV_BAS Supply Flow Rate [cfm] | CAV_BAS Supply Flow Rate [cfm] | 12755.6576 | 11802.1616 | 13094.6784 | 12119.9936 | 13984.608 | 12946.3568 | 14577.8944 | 13476.0768 |  |  | 2021-05-06
AZ_LO_VAV_BOT WITH REHEAT Supply Flow Rate [cfm] | VAV_BOT WITH REHEAT Supply Flow Rate [cfm] | 21421.8768 | 20362.4368 | 21443.0656 | 20383.6256 | 22883.904 | 21782.0864 | 23943.344 | 22799.1488 |  |  | 2021-05-06
AZ_LO_VAV_MID WITH REHEAT Supply Flow Rate [cfm] | VAV_MID WITH REHEAT Supply Flow Rate [cfm] | 200446.0483 | 190317.8019 | 198984.0211 | 188834.5859 | 211252.3363 | 200615.5587 | 220702.5411 | 209578.4211 |  |  | 2021-05-06
AZ_LO_VAV_TOP WITH REHEAT Supply Flow Rate [cfm] | VAV_TOP WITH REHEAT Supply Flow Rate [cfm] | 22121.1072 | 21061.6672 | 21697.3312 | 20765.024 | 23011.0368 | 22078.7296 | 23922.1552 | 22926.2816 |  |  | 2021-05-06
AZ_LO_Supply Air Temp. Reset Flag | Supply Air Temp. Reset Flag | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  |  | 2021-05-06
AZ_LO_CAV_BAS OA Rate [cfm] | CAV_BAS OA Rate [cfm] | 2542.8255 | 2542.8255 | 2542.8255 | 2542.8255 | 2542.8255 | 2542.8255 | 2542.8255 | 2542.8255 |  |  | 2021-05-06
AZ_LO_VAV_BOT WITH REHEAT OA Rate [cfm] | VAV_BOT WITH REHEAT OA Rate [cfm] | 5377.8022 | 4302.174 | 5377.8022 | 4302.174 | 5377.8022 | 4302.174 | 5377.8022 | 4302.174 |  |  | 2021-05-06
AZ_LO_VAV_MID WITH REHEAT OA Rate [cfm] | VAV_MID WITH REHEAT OA Rate [cfm] | 53777.9373 | 43021.7396 | 53777.9373 | 43021.7396 | 53777.9373 | 43021.7396 | 53777.9373 | 43021.7396 |  |  | 2021-05-06
AZ_LO_VAV_TOP WITH REHEAT OA Rate [cfm] | VAV_TOP WITH REHEAT OA Rate [cfm] | 5377.8022 | 4302.174 | 5377.8022 | 4302.174 | 5377.8022 | 4302.174 | 5377.8022 | 4302.174 |  |  | 2021-05-06
AZ_LO_AIRLOOP DATACENTER BASEMENT OA Rate [cfm] | AIRLOOP DATACENTER BASEMENT OA Rate [cfm] | 716.9654 | 716.9654 | 716.9654 | 716.9654 | 716.9654 | 716.9654 | 716.9654 | 716.9654 |  |  | 2021-05-06
AZ_LO_VAV_bot_WITH_REHEAT ERV Flag | VAV_bot_WITH_REHEAT ERV Flag | No | No | No | No | No | No | No | No |  |  | 2021-05-06
AZ_LO_VAV_mid_WITH_REHEAT ERV Flag | VAV_mid_WITH_REHEAT ERV Flag | No | No | No | No | No | No | No | No |  |  | 2021-05-06
AZ_LO_VAV_top_WITH_REHEAT ERV Flag | VAV_top_WITH_REHEAT ERV Flag | No | No | No | No | No | No | No | No |  |  | 2021-05-06
AZ_LO_COOLSYS1 CHILLER1 Capacity [ton] | COOLSYS1 CHILLER1 Capacity [ton] | 351.0896 | 320.5842 | 332.0408 | 306.7449 | 307.5919 | 286.8799 | 291.6229 | 270.5693 |  |  | 2021-05-06
AZ_LO_COOLSYS1 CHILLER2 Capacity [ton] | COOLSYS1 CHILLER2 Capacity [ton] | 351.0896 | 320.5842 | 332.0408 | 306.7449 | 307.5919 | 286.8799 | 291.6229 | 270.5693 |  |  | 2021-05-06
AZ_LO_TOWERWATERSYS COOLTOWER 1 Capacity [ton] | TOWERWATERSYS COOLTOWER 1 Capacity [ton] | 333.3914 | 304.4334 | 315.4292 | 291.3998 | 292.3234 | 272.6477 | 277.1559 | 257.1384 |  |  | 2021-05-06
AZ_LO_TOWERWATERSYS COOLTOWER 2 Capacity [ton] | TOWERWATERSYS COOLTOWER 2 Capacity [ton] | 333.3914 | 304.4334 | 315.4292 | 291.3998 | 292.3234 | 272.6477 | 277.1559 | 257.1384 |  |  | 2021-05-06
AZ_LO_HEATSYS1 BOILER Capacity [MMBTU/h] | HEATSYS1 BOILER Capacity [MMBTU/h] | 2999.3671 | 2659.67 | 3243.2949 | 2890.4698 | 3391.7248 | 2999.5443 | 4030.4415 | 3562.4946 |  |  | 2021-05-06
AZ_LO_COOLSYS1 PUMP Flow Rate [gal/min] | COOLSYS1 PUMP Flow Rate [gal/min] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 2021-05-06
AZ_LO_COOLSYS1 CHILLER1 PUMP Flow Rate [gal/min] | COOLSYS1 CHILLER1 PUMP Flow Rate [gal/min] | 549.2787 | 501.3901 | 519.1456 | 479.5008 | 480.0255 | 447.6211 | 457.686 | 421.5203 |  |  | 2021-05-06
AZ_LO_COOLSYS1 CHILLER2 PUMP Flow Rate [gal/min] | COOLSYS1 CHILLER2 PUMP Flow Rate [gal/min] | 549.2787 | 501.3901 | 519.1456 | 479.5008 | 480.0255 | 447.6211 | 457.686 | 421.5203 |  |  | 2021-05-06
AZ_LO_COOLSYS1 PUMP SECONDARY Flow Rate [gal/min] | COOLSYS1 PUMP SECONDARY Flow Rate [gal/min] | 1098.5574 | 1002.7786 | 1038.2897 | 959.0016 | 960.0525 | 895.2405 | 915.372 | 843.0406 |  |  | 2021-05-06
AZ_LO_HEATSYS1 PUMP Flow Rate [gal/min] | HEATSYS1 PUMP Flow Rate [gal/min] | 615.6598 | 545.9327 | 665.7294 | 593.3077 | 696.1969 | 615.6963 | 827.3013 | 731.2483 |  |  | 2021-05-06
AZ_LO_TOWERWATERSYS PUMP Flow Rate [gal/min] | TOWERWATERSYS PUMP Flow Rate [gal/min] | 1936.9095 | 1768.7376 | 1831.8218 | 1692.339 | 1696.9356 | 1621.4881 | 1648.2751 | 1529.2915 |  |  | 2021-05-06
AZ_LO_PLANT CIRC PUMP Flow Rate [gal/min] | PLANT CIRC PUMP Flow Rate [gal/min] | 212.3499 | 211.4259 | 221.8237 | 220.8616 | 228.1591 | 227.2318 | 233.5006 | 232.548 |  |  | 2021-05-06
AZ_LO_COOLSYS1 PUMP SECONDARY Pressure setpoint reset [yes,no] | COOLSYS1 PUMP SECONDARY Pressure setpoint reset [yes,no] | pump_ride_on_curve | pump_ride_on_curve | pump_ride_on_curve | pump_ride_on_curve | pump_ride_on_curve | pump_ride_on_curve | pump_ride_on_curve | pump_ride_on_curve |  |  | 2021-05-06
AZ_LO_COOLSYS1 CHILLER1 PUMP Pump Power [hp] | COOLSYS1 CHILLER1 PUMP Pump Power [hp] | 2.9632 | 2.678 | 2.8006 | 2.5611 | 2.5896 | 2.3908 | 2.469 | 2.2514 |  |  | 2021-05-06
AZ_LO_COOLSYS1 CHILLER2 PUMP Pump Power [hp] | COOLSYS1 CHILLER2 PUMP Pump Power [hp] | 2.9632 | 2.678 | 2.8006 | 2.5611 | 2.5896 | 2.3908 | 2.469 | 2.2514 |  |  | 2021-05-06
AZ_LO_COOLSYS1 PUMP SECONDARY Pump Power [hp] | COOLSYS1 PUMP SECONDARY Pump Power [hp] | 17.779 | 16.0682 | 16.8036 | 15.3668 | 15.5374 | 14.3451 | 14.8143 | 13.5086 |  |  | 2021-05-06
AZ_LO_HEATSYS1 PUMP Pump Power [hp] | HEATSYS1 PUMP Pump Power [hp] | 13.3078 | 11.6838 | 14.3901 | 12.6977 | 15.0487 | 13.1769 | 17.8826 | 15.6499 |  |  | 2021-05-06
AZ_LO_TOWERWATERSYS PUMP Pump Power [hp] | TOWERWATERSYS PUMP Pump Power [hp] | 34.6799 | 31.3531 | 32.7983 | 29.9996 | 30.3833 | 28.7437 | 29.5112 | 27.1095 |  |  | 2021-05-06
AZ_LO_PLANT CIRC PUMP Pump Power [hp] | PLANT CIRC PUMP Pump Power [hp] | 4.5822 | 4.5171 | 4.7866 | 4.7187 | 4.9233 | 4.8548 | 5.0386 | 4.9684 |  |  | 2021-05-06
AZ_LO_Datacenter PLANT CIRC PUMP Pump Power [hp] | Datacenter PLANT CIRC PUMP Pump Power [hp] | 4.5822 | 4.5171 | 4.7866 | 4.7187 | 4.9233 | 4.8548 | 5.0386 | 4.9684 |  |  | 2021-05-06
AZ_LO_ZN_VAV_BOXes_Max_Reheat_Water_Flow_GPM | ZN_VAV_BOXes_Max_Reheat_Water_Flow_GPM | 379.7153 | 354.4367 | 386.3659 | 366.8082 | 389.2768 | 371.0146 | 435.3121 | 415.7291 |  |  | 2021-05-06
AZ_LO_COOLSYS1 PUMP SECONDARY VSD | COOLSYS1 PUMP SECONDARY VSD | No | No | No | No | No | No | No | No |  |  | 2021-05-06
AZ_LO_HEATSYS1 PUMP VSD | HEATSYS1 PUMP VSD | No | No | No | No | No | No | No | No |  |  | 2021-05-06
AZ_LO_DATACENTER BASEMENT Cooling Capacity [ton] | DATACENTER BASEMENT Cooling Capacity [ton] | 124.8994 | 124.5296 | 130.7472 | 130.3608 | 133.8279 | 133.4274 | 136.4638 | 136.0551 |  |  | 2021-05-06
AZ_LO_DATACENTER BOT Cooling Capacity [ton] | DATACENTER BOT Cooling Capacity [ton] | 2.6691 | 2.6413 | 2.7669 | 2.7376 | 2.886 | 2.8599 | 2.9921 | 2.9651 |  |  | 2021-05-06
AZ_LO_DATACENTER MID Cooling Capacity [ton] | DATACENTER MID Cooling Capacity [ton] | 25.4099 | 25.1547 | 26.2978 | 26.0303 | 27.6016 | 27.3711 | 28.6669 | 28.4271 |  |  | 2021-05-06
AZ_LO_DATACENTER TOP Cooling Capacity [ton] | DATACENTER TOP Cooling Capacity [ton] | 2.5728 | 2.5484 | 2.6785 | 2.657 | 2.8155 | 2.7932 | 2.9216 | 2.8985 |  |  | 2021-05-06
id | item | Zone2B(AZ-Tucson-AZ) ASHRAE901-state_STD2016 | Zone2B(AZ-Tucson-AZ) ASHRAE901-state_STD2019 | Zone3B(AZ-Kingman-AZ) ASHRAE901-state_STD2016 | Zone3B(AZ-Kingman-AZ) ASHRAE901-state_STD2019 | Zone4B(AZ-Prescott-AZ) ASHRAE901-state_STD2016 | Zone4B(AZ-Prescott-AZ) ASHRAE901-state_STD2019 | Zone5B(AZ-Gallup-NM) ASHRAE901-state_STD2016 | Zone5B(AZ-Gallup-NM) ASHRAE901-state_STD2019 |  |  | 2021-05-06
AZ_RS_PSZ-AC:1 Cooling Capacity [ton] | PSZ-AC:1 Cooling Capacity [ton] | 10.6344 | 9.9987 | 10.2134 | 9.6102 | 10.0831 | 9.7609 | 9.6267 | 8.7706 |  |  | 2021-05-06
AZ_RS_PSZ-AC:2 Cooling Capacity [ton] | PSZ-AC:2 Cooling Capacity [ton] | 47.0467 | 44.8921 | 46.9012 | 44.6615 | 42.7876 | 40.5977 | 40.3316 | 37.7736 |  |  | 2021-05-06
AZ_RS_PSZ-AC:3 Cooling Capacity [ton] | PSZ-AC:3 Cooling Capacity [ton] | 6.672 | 6.5073 | 6.4639 | 6.2932 | 5.7796 | 5.6079 | 5.567 | 5.3842 |  |  | 2021-05-06
AZ_RS_PSZ-AC:4 Cooling Capacity [ton] | PSZ-AC:4 Cooling Capacity [ton] | 5.4797 | 5.2801 | 5.2649 | 5.0889 | 4.5694 | 4.4042 | 4.189 | 3.9989 |  |  | 2021-05-06
AZ_RS_PSZ-AC:1 Supply Flow Rate [cfm] | PSZ-AC:1 Supply Flow Rate [cfm] | 4788.6688 | 4492.0256 | 4597.9696 | 4322.5152 | 4534.4032 | 4216.5712 | 4343.704 | 3941.1168 |  |  | 2021-05-06
AZ_RS_PSZ-AC:2 Supply Flow Rate [cfm] | PSZ-AC:2 Supply Flow Rate [cfm] | 17056.984 | 16061.1104 | 17035.7952 | 15997.544 | 17798.592 | 16717.9632 | 18158.8016 | 17014.6064 |  |  | 2021-05-06
AZ_RS_PSZ-AC:3 Supply Flow Rate [cfm] | PSZ-AC:3 Supply Flow Rate [cfm] | 2669.7888 | 2585.0336 | 2563.8448 | 2479.0896 | 2563.8448 | 2479.0896 | 2500.2784 | 2415.5232 |  |  | 2021-05-06
AZ_RS_PSZ-AC:4 Supply Flow Rate [cfm] | PSZ-AC:4 Supply Flow Rate [cfm] | 2118.88 | 2034.1248 | 2012.936 | 1928.1808 | 1970.5584 | 1885.8032 | 1885.8032 | 1801.048 |  |  | 2021-05-06
AZ_RS_PSZ-AC:1 OA Rate [cfm] | PSZ-AC:1 OA Rate [cfm] | 490.669 | 490.669 | 490.669 | 490.669 | 490.669 | 490.669 | 490.669 | 490.669 |  |  | 2021-05-06
AZ_RS_PSZ-AC:2 OA Rate [cfm] | PSZ-AC:2 OA Rate [cfm] | 4005.1282 | 4005.1282 | 4005.1282 | 4005.1282 | 4005.1282 | 4005.1282 | 4005.1282 | 4005.1282 |  |  | 2021-05-06
AZ_RS_PSZ-AC:3 OA Rate [cfm] | PSZ-AC:3 OA Rate [cfm] | 377.3937 | 377.3937 | 377.3937 | 377.3937 | 377.3937 | 377.3937 | 377.3937 | 377.3937 |  |  | 2021-05-06
AZ_RS_PSZ-AC:4 OA Rate [cfm] | PSZ-AC:4 OA Rate [cfm] | 377.3937 | 377.3937 | 377.3937 | 377.3937 | 377.3937 | 377.3937 | 377.3937 | 377.3937 |  |  | 2021-05-06
AZ_RS_PSZ-AC:1 OA Damper [gravity, motorized] | PSZ-AC:1 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | motorized | motorized | motorized | motorized |  |  | 2021-05-06
AZ_RS_PSZ-AC:2 OA Damper [gravity, motorized] | PSZ-AC:2 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | motorized | motorized | motorized | motorized |  |  | 2021-05-06
AZ_RS_PSZ-AC:3 OA Damper [gravity, motorized] | PSZ-AC:3 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | motorized | motorized | motorized | motorized |  |  | 2021-05-06
AZ_RS_PSZ-AC:4 OA Damper [gravity, motorized] | PSZ-AC:4 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | motorized | motorized | motorized | motorized |  |  | 2021-05-06
AZ_RS_PSZ-AC:1 Heating Capacity [kBtu/hr] | PSZ-AC:1 Heating Capacity [kBtu/hr] | 180.6647 | 170.8138 | 172.2675 | 162.3864 | 162.5968 | 151.2068 | 153.4469 | 140.2664 |  |  | 2021-05-06
AZ_RS_PSZ-AC:2 Heating Capacity [kBtu/hr] | PSZ-AC:2 Heating Capacity [kBtu/hr] | 720.0791 | 681.9391 | 723.6857 | 685.6779 | 727.4217 | 690.2364 | 755.1017 | 716.8587 |  |  | 2021-05-06
AZ_RS_PSZ-AC:3 Heating Capacity [kBtu/hr] | PSZ-AC:3 Heating Capacity [kBtu/hr] | 104.3196 | 101.6695 | 100.575 | 97.9734 | 96.805 | 94.1673 | 95.4223 | 92.8637 |  |  | 2021-05-06
AZ_RS_PSZ-AC:4 Heating Capacity [kBtu/hr] | PSZ-AC:4 Heating Capacity [kBtu/hr] | 85.0595 | 82.2326 | 80.9188 | 78.2227 | 76.4521 | 75.7054 | 77.3011 | 74.801 |  |  | 2021-05-06
id | item | Zone2B(AZ-Tucson-AZ) ASHRAE901-state_STD2016 | Zone2B(AZ-Tucson-AZ) ASHRAE901-state_STD2019 | Zone3B(AZ-Kingman-AZ) ASHRAE901-state_STD2016 | Zone3B(AZ-Kingman-AZ) ASHRAE901-state_STD2019 | Zone4B(AZ-Prescott-AZ) ASHRAE901-state_STD2016 | Zone4B(AZ-Prescott-AZ) ASHRAE901-state_STD2019 | Zone5B(AZ-Gallup-NM) ASHRAE901-state_STD2016 | Zone5B(AZ-Gallup-NM) ASHRAE901-state_STD2019 |  |  | 2021-05-06
AZ_PS_VAV_POD_1 Cooling Capacity [ton] | VAV_POD_1 Cooling Capacity [ton] | 22.9822 | 21.568 | 22.1201 | 20.7243 | 21.9988 | 20.4657 | 19.2948 | 18.073 |  |  | 2021-05-06
AZ_PS_VAV_POD_2 Cooling Capacity [ton] | VAV_POD_2 Cooling Capacity [ton] | 22.9533 | 21.4121 | 22.1306 | 20.5721 | 21.8008 | 20.1542 | 19.2245 | 17.77 |  |  | 2021-05-06
AZ_PS_VAV_POD_3 Cooling Capacity [ton] | VAV_POD_3 Cooling Capacity [ton] | 20.9649 | 19.5729 | 20.0913 | 18.8385 | 20.0304 | 18.6976 | 17.6333 | 16.4769 |  |  | 2021-05-06
AZ_PS_VAV_OTHER Cooling Capacity [ton] | VAV_OTHER Cooling Capacity [ton] | 29.6342 | 26.4771 | 26.4771 | 23.8434 | 23.4951 | 21.3394 | 21.6849 | 20.2201 |  |  | 2021-05-06
AZ_PS_PSZ-AC_1:6 Cooling Capacity [ton] | PSZ-AC_1:6 Cooling Capacity [ton] | 8.1547 | 7.8521 | 8.3236 | 8.0248 | 7.9452 | 7.6616 | 7.6011 | 7.3191 |  |  | 2021-05-06
AZ_PS_PSZ-AC_2:5 Cooling Capacity [ton] | PSZ-AC_2:5 Cooling Capacity [ton] | 6.1517 | 5.9435 | 5.9514 | 5.8147 | 5.3734 | 5.359 | 5.0956 | 5.0823 |  |  | 2021-05-06
AZ_PS_PSZ-AC_2:7 Cooling Capacity [ton] | PSZ-AC_2:7 Cooling Capacity [ton] | 10.5074 | 10.5074 | 10.5074 | 10.5074 | 10.1392 | 10.1392 | 9.3685 | 9.3685 |  |  | 2021-05-06
AZ_PS_VAV_POD_1 Supply Flow Rate [cfm] | VAV_POD_1 Supply Flow Rate [cfm] | 6886.36 | 6462.584 | 6632.0944 | 6229.5072 | 6716.8496 | 6271.8848 | 6632.0944 | 6229.5072 |  |  | 2021-05-06
AZ_PS_VAV_POD_2 Supply Flow Rate [cfm] | VAV_POD_2 Supply Flow Rate [cfm] | 6886.36 | 6420.2064 | 6632.0944 | 6165.9408 | 6653.2832 | 6187.1296 | 6610.9056 | 6123.5632 |  |  | 2021-05-06
AZ_PS_VAV_POD_3 Supply Flow Rate [cfm] | VAV_POD_3 Supply Flow Rate [cfm] | 6293.0736 | 5869.2976 | 6038.808 | 5657.4096 | 6144.752 | 5763.3536 | 6123.5632 | 5699.7872 |  |  | 2021-05-06
AZ_PS_VAV_OTHER Supply Flow Rate [cfm] | VAV_OTHER Supply Flow Rate [cfm] | 9386.6384 | 8814.5408 | 9132.3728 | 8602.6528 | 9598.5264 | 9005.24 | 9704.4704 | 9111.184 |  |  | 2021-05-06
AZ_PS_PSZ-AC_2:5 Supply Flow Rate [cfm] | PSZ-AC_2:5 Supply Flow Rate [cfm] | 1843.4256 | 1779.8592 | 1822.2368 | 1758.6704 | 1991.7472 | 1970.5584 | 2055.3136 | 2034.1248 |  |  | 2021-05-06
AZ_PS_PSZ-AC_1:6 Supply Flow Rate [cfm] | PSZ-AC_1:6 Supply Flow Rate [cfm] | 2796.9216 | 2669.7888 | 2839.2992 | 2712.1664 | 3029.9984 | 2902.8656 | 3178.32 | 3029.9984 |  |  | 2021-05-06
AZ_PS_PSZ-AC_2:7 Supply Flow Rate [cfm] | PSZ-AC_2:7 Supply Flow Rate [cfm] | 3157.1312 | 3157.1312 | 3157.1312 | 3157.1312 | 3157.1312 | 3157.1312 | 3157.1312 | 3157.1312 |  |  | 2021-05-06
AZ_PS_Supply Air Temp. Reset Flag | Supply Air Temp. Reset Flag | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  |  | 2021-05-06
AZ_PS_VAV_POD_1 OA Rate [cfm] | VAV_POD_1 OA Rate [cfm] | 6896.5942 | 6282.2673 | 6637.9001 | 6219.0399 | 6709.3276 | 6282.2038 | 6639.9978 | 6221.4343 |  |  | 2021-05-06
AZ_PS_VAV_POD_2 OA Rate [cfm] | VAV_POD_2 OA Rate [cfm] | 6885.682 | 6282.2673 | 6637.9849 | 6173.3569 | 6647.7953 | 6186.5575 | 6617.8132 | 6117.1218 |  |  | 2021-05-06
AZ_PS_VAV_POD_3 OA Rate [cfm] | VAV_POD_3 OA Rate [cfm] | 6288.2214 | 5422.002 | 6027.7263 | 5422.002 | 6147.3159 | 5422.002 | 6121.296 | 5422.002 |  |  | 2021-05-06
AZ_PS_VAV_OTHER OA Rate [cfm] | VAV_OTHER OA Rate [cfm] | 3736.1787 | 2988.8921 | 3736.1787 | 2988.8921 | 3736.1787 | 2988.8921 | 3736.1787 | 2988.8921 |  |  | 2021-05-06
AZ_PS_PSZ-AC_2:5 OA Rate [cfm] | PSZ-AC_2:5 OA Rate [cfm] | 1152.7343 | 1152.7343 | 1152.7343 | 1152.7343 | 1152.7343 | 1152.7343 | 1152.7343 | 1152.7343 |  |  | 2021-05-06
AZ_PS_PSZ-AC_1:6 OA Rate [cfm] | PSZ-AC_1:6 OA Rate [cfm] | 539.9118 | 539.9118 | 539.9118 | 539.9118 | 539.9118 | 539.9118 | 539.9118 | 539.9118 |  |  | 2021-05-06
AZ_PS_PSZ-AC_2:7 OA Rate [cfm] | PSZ-AC_2:7 OA Rate [cfm] | 3153.0841 | 3153.0841 | 3153.0841 | 3153.0841 | 3153.0841 | 3153.0841 | 3153.0841 | 3153.0841 |  |  | 2021-05-06
AZ_PS_VAV_POD_1 OA Damper [gravity, motorized] | VAV_POD_1 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | motorized | motorized | motorized | motorized |  |  | 2021-05-06
AZ_PS_VAV_POD_2 OA Damper [gravity, motorized] | VAV_POD_2 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | motorized | motorized | motorized | motorized |  |  | 2021-05-06
AZ_PS_VAV_POD_3 OA Damper [gravity, motorized] | VAV_POD_3 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | motorized | motorized | motorized | motorized |  |  | 2021-05-06
AZ_PS_VAV_OTHER OA Damper [gravity, motorized] | VAV_OTHER OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | motorized | motorized | motorized | motorized |  |  | 2021-05-06
AZ_PS_PSZ-AC_2:5 OA Damper [gravity, motorized] | PSZ-AC_2:5 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | motorized | motorized | motorized | motorized |  |  | 2021-05-06
AZ_PS_PSZ-AC_1:6 OA Damper [gravity, motorized] | PSZ-AC_1:6 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | motorized | motorized | motorized | motorized |  |  | 2021-05-06
AZ_PS_PSZ-AC_2:7 OA Damper [gravity, motorized] | PSZ-AC_2:7 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | motorized | motorized | motorized | motorized |  |  | 2021-05-06
AZ_PS_VAV_POD_1 (economizer) | VAV_POD_1 (economizer) | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb |  |  | 2021-05-06
AZ_PS_VAV_POD_2 (economizer) | VAV_POD_2 (economizer) | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb |  |  | 2021-05-06
AZ_PS_VAV_POD_3 (economizer) | VAV_POD_3 (economizer) | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb |  |  | 2021-05-06
AZ_PS_VAV_OTHER (economizer) | VAV_OTHER (economizer) | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb |  |  | 2021-05-06
AZ_PS_PSZ-AC_2:5 (economizer) | PSZ-AC_2:5 (economizer) | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb |  |  | 2021-05-06
AZ_PS_PSZ-AC_1:6 (economizer) | PSZ-AC_1:6 (economizer) | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb |  |  | 2021-05-06
AZ_PS_PSZ-AC_2:7 (economizer) | PSZ-AC_2:7 (economizer) | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb |  |  | 2021-05-06
AZ_PS_VAV_Pod_1_ERV Flag | VAV_Pod_1_ERV Flag | Yes | Yes | No | No | No | No | No | No |  |  | 2021-05-06
AZ_PS_VAV_Pod_2_ERV Flag | VAV_Pod_2_ERV Flag | Yes | Yes | No | No | No | No | No | No |  |  | 2021-05-06
AZ_PS_VAV_Pod_3_ERV Flag | VAV_Pod_3_ERV Flag | Yes | Yes | No | No | No | No | No | No |  |  | 2021-05-06
AZ_PS_VAV_OTHER_ERV Flag | VAV_OTHER_ERV Flag | No | No | No | No | No | No | No | No |  |  | 2021-05-06
AZ_PS_PSZ_AC_2_5_ERV Flag | PSZ_AC_2_5_ERV Flag | No | No | No | No | No | No | No | No |  |  | 2021-05-06
AZ_PS_PSZ_AC_2_7_ERV Flag | PSZ_AC_2_7_ERV Flag | No | No | No | No | No | No | No | No |  |  | 2021-05-06
AZ_PS_HEATSYS1 Capacity [MMBTU/h] | HEATSYS1 Capacity [MMBTU/h] | 0.78384 | 0.70545 | 0.84261 | 0.77762 | 0.8759 | 0.81015 | 1.0503 | 0.98115 |  |  | 2021-05-06
AZ_PS_HEATSYS1 Flow Rate [gal/min] | HEATSYS1 Flow Rate [gal/min] | 80.4466 | 72.4019 | 86.4781 | 79.808 | 89.8948 | 83.1465 | 107.7923 | 100.6973 |  |  | 2021-05-06
AZ_PS_VAV_POD_1 Fan Power [hp] | VAV_POD_1 Fan Power [hp] | 10.0975 | 9.5484 | 9.7929 | 9.1749 | 9.8983 | 9.2681 | 9.799 | 9.1785 |  |  | 2021-05-06
AZ_PS_VAV_POD_2 Fan Power [hp] | VAV_POD_2 Fan Power [hp] | 10.0848 | 9.4794 | 9.7975 | 9.1076 | 9.8092 | 9.127 | 9.7633 | 9.0246 |  |  | 2021-05-06
AZ_PS_VAV_POD_3 Fan Power [hp] | VAV_POD_3 Fan Power [hp] | 9.2814 | 8.6652 | 8.8947 | 8.3401 | 9.071 | 8.5118 | 9.0308 | 8.4241 |  |  | 2021-05-06
AZ_PS_VAV_OTHER Fan Power [hp] | VAV_OTHER Fan Power [hp] | 13.0126 | 12.2037 | 13.3829 | 12.5937 | 14.0459 | 13.1899 | 14.2125 | 13.3269 |  |  | 2021-05-06
AZ_PS_HEATSYS1 Pump Power [hp] | HEATSYS1 Pump Power [hp] | 1.7389 | 1.5495 | 1.8693 | 1.708 | 1.9431 | 1.7795 | 2.33 | 2.1551 |  |  | 2021-05-06
AZ_PS_PSZ-AC_1:6 Heating Capacity [kBtu/hr] | PSZ-AC_1:6 Heating Capacity [kBtu/hr] | 198.5262 | 189.6163 | 199.4904 | 190.8584 | 203.7587 | 195.3522 | 209.3004 | 200.9264 |  |  | 2021-05-06
AZ_PS_PSZ-AC_2:5 Heating Capacity [kBtu/hr] | PSZ-AC_2:5 Heating Capacity [kBtu/hr] | 105.6842 | 103.5763 | 109.33 | 107.3228 | 115.4528 | 115.2299 | 127.6765 | 127.4693 |  |  | 2021-05-06
AZ_PS_PSZ-AC_2:7 Heating Capacity [kBtu/hr] | PSZ-AC_2:7 Heating Capacity [kBtu/hr] | 225.0936 | 225.0936 | 239.9402 | 239.9402 | 245.5272 | 245.5272 | 277.7147 | 277.7147 |  |  | 2021-05-06
AZ_PS_ZN_VAV_BOXes_Max_Reheat_Water_Flow_GPM | ZN_VAV_BOXes_Max_Reheat_Water_Flow_GPM | 59.5006 | 52.7982 | 60.8417 | 55.795 | 59.5794 | 54.7618 | 66.2894 | 61.9586 |  |  | 2021-05-06
id | item | Zone2B(AZ-Tucson-AZ) ASHRAE901-state_STD2016 | Zone2B(AZ-Tucson-AZ) ASHRAE901-state_STD2019 | Zone3B(AZ-Kingman-AZ) ASHRAE901-state_STD2016 | Zone3B(AZ-Kingman-AZ) ASHRAE901-state_STD2019 | Zone4B(AZ-Prescott-AZ) ASHRAE901-state_STD2016 | Zone4B(AZ-Prescott-AZ) ASHRAE901-state_STD2019 | Zone5B(AZ-Gallup-NM) ASHRAE901-state_STD2016 | Zone5B(AZ-Gallup-NM) ASHRAE901-state_STD2019 |  |  | 2021-05-06
AZ_SH_SAC_FRONTOFFICE Cooling Capacity [ton] | SAC_FRONTOFFICE Cooling Capacity [ton] | 2.5754 | 2.4267 | 2.4145 | 2.2767 | 2.1035 | 1.966 | 2.0572 | 1.8911 |  |  | 2021-05-06
AZ_SH_SAC_FRONTLOUNGE Cooling Capacity [ton] | SAC_FRONTLOUNGE Cooling Capacity [ton] | 6.5112 | 6.2425 | 6.137 | 5.8706 | 5.4936 | 5.2555 | 5.0878 | 4.8308 |  |  | 2021-05-06
AZ_SH_SAC_MEETINGROOM Cooling Capacity [ton] | SAC_MEETINGROOM Cooling Capacity [ton] | 3.3333 | 3.2518 | 3.1754 | 3.0832 | 2.8714 | 2.7975 | 2.6864 | 2.6119 |  |  | 2021-05-06
AZ_SH_SAC_EXC_EMPLGE_RESTRM Cooling Capacity [ton] | SAC_EXC_EMPLGE_RESTRM Cooling Capacity [ton] | 6.3365 | 6.2958 | 6.0893 | 6.0445 | 5.8066 | 5.7605 | 6.0396 | 5.988 |  |  | 2021-05-06
AZ_SH_SAC_FO_ADDAQ SUPPLY FAN Supply Flow Rate [cfm] | SAC_FO_ADDAQ SUPPLY FAN Supply Flow Rate [cfm] | 953.496 | 889.9296 | 953.496 | 889.9296 | 932.3072 | 847.552 | 932.3072 | 847.552 |  |  | 2021-05-06
AZ_SH_SAC_FL_ADDAQ SUPPLY FAN Supply Flow Rate [cfm] | SAC_FL_ADDAQ SUPPLY FAN Supply Flow Rate [cfm] | 2161.2576 | 2055.3136 | 2161.2576 | 2055.3136 | 2182.4464 | 2076.5024 | 2224.824 | 2097.6912 |  |  | 2021-05-06
AZ_SH_SAC_MR_ADDAQ SUPPLY FAN Supply Flow Rate [cfm] | SAC_MR_ADDAQ SUPPLY FAN Supply Flow Rate [cfm] | 1017.0624 | 974.6848 | 1017.0624 | 995.8736 | 1038.2512 | 995.8736 | 1059.44 | 1038.2512 |  |  | 2021-05-06
AZ_SH_SAC_EXC_ADDAQ SUPPLY FAN Supply Flow Rate [cfm] | SAC_EXC_ADDAQ SUPPLY FAN Supply Flow Rate [cfm] | 2415.5232 | 2394.3344 | 2457.9008 | 2436.712 | 2606.2224 | 2585.0336 | 2712.1664 | 2690.9776 |  |  | 2021-05-06
AZ_SH_SAC_Exc_EmpLge_RestRm OA Rate [cfm] | SAC_Exc_EmpLge_RestRm OA Rate [cfm] | 199.9928 | 199.9928 | 199.9928 | 199.9928 | 199.9928 | 199.9928 | 199.9928 | 199.9928 |  |  | 2021-05-06
AZ_SH_SAC_FrontLounge OA Rate [cfm] | SAC_FrontLounge OA Rate [cfm] | 500.0133 | 500.0133 | 500.0133 | 500.0133 | 500.0133 | 500.0133 | 500.0133 | 500.0133 |  |  | 2021-05-06
AZ_SH_SAC_FrontOffice OA Rate [cfm] | SAC_FrontOffice OA Rate [cfm] | 119.2938 | 119.2938 | 119.2938 | 119.2938 | 119.2938 | 119.2938 | 119.2938 | 119.2938 |  |  | 2021-05-06
AZ_SH_SAC_MeetingRoom OA Rate [cfm] | SAC_MeetingRoom OA Rate [cfm] | 267.7629 | 267.7629 | 267.7629 | 267.7629 | 267.7629 | 267.7629 | 267.7629 | 267.7629 |  |  | 2021-05-06
AZ_SH_SAC_FrontLounge OA Damper [gravity, motorized] | SAC_FrontLounge OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | motorized | motorized | motorized | motorized |  |  | 2021-05-06
AZ_SH_SAC_FrontOffice (economizer) | SAC_FrontOffice (economizer) | No | No | No | No | No | No | No | No |  |  | 2021-05-06
AZ_SH_SAC_FrontLounge (economizer) | SAC_FrontLounge (economizer) | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb |  |  | 2021-05-06
AZ_SH_SAC_MeetingRoom (economizer) | SAC_MeetingRoom (economizer) | No | No | No | No | No | No | No | No |  |  | 2021-05-06
AZ_SH_SAC_Exc_EmpLge_RestRm (economizer) | SAC_Exc_EmpLge_RestRm (economizer) | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb |  |  | 2021-05-06
AZ_SH_SAC_FRONTOFFICE Heating Capacity [kBtu/hr] | SAC_FRONTOFFICE Heating Capacity [kBtu/hr] | 36.6163 | 34.5073 | 36.2469 | 34.2512 | 33.9224 | 31.793 | 33.8903 | 31.7237 |  |  | 2021-05-06
AZ_SH_SAC_FRONTLOUNGE Heating Capacity [kBtu/hr] | SAC_FRONTLOUNGE Heating Capacity [kBtu/hr] | 91.1726 | 87.5451 | 92.1268 | 88.7119 | 90.2631 | 86.8829 | 94.0087 | 90.6474 |  |  | 2021-05-06
AZ_SH_SAC_MEETINGROOM Heating Capacity [kBtu/hr] | SAC_MEETINGROOM Heating Capacity [kBtu/hr] | 43.9252 | 42.8886 | 45.0178 | 43.8135 | 44.3114 | 43.3206 | 46.705 | 45.6996 |  |  | 2021-05-06
AZ_SH_SAC_EXC_EMPLGE_RESTRM Heating Capacity [kBtu/hr] | SAC_EXC_EMPLGE_RESTRM Heating Capacity [kBtu/hr] | 88.5318 | 87.9533 | 88.848 | 88.2 | 89.1298 | 88.461 | 90.6157 | 89.9432 |  |  | 2021-05-06
id | item | Zone2B(AZ-Tucson-AZ) ASHRAE901-state_STD2016 | Zone2B(AZ-Tucson-AZ) ASHRAE901-state_STD2019 | Zone3B(AZ-Kingman-AZ) ASHRAE901-state_STD2016 | Zone3B(AZ-Kingman-AZ) ASHRAE901-state_STD2019 | Zone4B(AZ-Prescott-AZ) ASHRAE901-state_STD2016 | Zone4B(AZ-Prescott-AZ) ASHRAE901-state_STD2019 | Zone5B(AZ-Gallup-NM) ASHRAE901-state_STD2016 | Zone5B(AZ-Gallup-NM) ASHRAE901-state_STD2019 |  |  | 2021-05-06
AZ_MA_SPLIT GSW COOLING COIL Cooling Capacity [ton] | SPLIT GSW COOLING COIL Cooling Capacity [ton] | 0.94627 | 0.93186 | 0.87991 | 0.86679 | 0.82029 | 0.80269 | 0.76937 | 0.75029 |  |  | 2021-05-06
AZ_MA_SPLIT GNW COOLING COIL Cooling Capacity [ton] | SPLIT GNW COOLING COIL Cooling Capacity [ton] | 0.93507 | 0.92016 | 0.85602 | 0.84302 | 0.79861 | 0.78103 | 0.74874 | 0.72968 |  |  | 2021-05-06
AZ_MA_SPLIT OFFICE COOLING COIL Cooling Capacity [ton] | SPLIT OFFICE COOLING COIL Cooling Capacity [ton] | 1.7792 | 1.713 | 1.7793 | 1.6813 | 1.8191 | 1.6335 | 1.7224 | 1.5214 |  |  | 2021-05-06
AZ_MA_SPLIT GNE COOLING COIL Cooling Capacity [ton] | SPLIT GNE COOLING COIL Cooling Capacity [ton] | 0.82697 | 0.81375 | 0.74119 | 0.72938 | 0.6609 | 0.64566 | 0.59488 | 0.57871 |  |  | 2021-05-06
AZ_MA_SPLIT GN1 COOLING COIL Cooling Capacity [ton] | SPLIT GN1 COOLING COIL Cooling Capacity [ton] | 0.68937 | 0.67316 | 0.61053 | 0.60023 | 0.54684 | 0.53491 | 0.50222 | 0.48948 |  |  | 2021-05-06
AZ_MA_SPLIT GN2 COOLING COIL Cooling Capacity [ton] | SPLIT GN2 COOLING COIL Cooling Capacity [ton] | 0.68769 | 0.67151 | 0.6085 | 0.59822 | 0.54404 | 0.53219 | 0.49901 | 0.48637 |  |  | 2021-05-06
AZ_MA_SPLIT GS1 COOLING COIL Cooling Capacity [ton] | SPLIT GS1 COOLING COIL Cooling Capacity [ton] | 0.703 | 0.68698 | 0.6376 | 0.62802 | 0.57004 | 0.55743 | 0.52379 | 0.51041 |  |  | 2021-05-06
AZ_MA_SPLIT GS2 COOLING COIL Cooling Capacity [ton] | SPLIT GS2 COOLING COIL Cooling Capacity [ton] | 0.73446 | 0.72074 | 0.67559 | 0.66002 | 0.61613 | 0.59756 | 0.56836 | 0.54849 |  |  | 2021-05-06
AZ_MA_SPLIT MSW COOLING COIL Cooling Capacity [ton] | SPLIT MSW COOLING COIL Cooling Capacity [ton] | 2.107 | 2.0753 | 2.0041 | 1.977 | 2.0507 | 2.0108 | 2.0657 | 2.0226 |  |  | 2021-05-06
AZ_MA_SPLIT MNW COOLING COIL Cooling Capacity [ton] | SPLIT MNW COOLING COIL Cooling Capacity [ton] | 2.0816 | 2.0496 | 1.9529 | 1.9266 | 2.0088 | 1.9692 | 2.0303 | 1.9873 |  |  | 2021-05-06
AZ_MA_SPLIT MSE COOLING COIL Cooling Capacity [ton] | SPLIT MSE COOLING COIL Cooling Capacity [ton] | 1.959 | 1.7924 | 1.7829 | 1.7582 | 1.6046 | 1.5725 | 1.5589 | 1.525 |  |  | 2021-05-06
AZ_MA_SPLIT MNE COOLING COIL Cooling Capacity [ton] | SPLIT MNE COOLING COIL Cooling Capacity [ton] | 1.8065 | 1.7776 | 1.6214 | 1.5978 | 1.5561 | 1.5271 | 1.4998 | 1.4695 |  |  | 2021-05-06
AZ_MA_SPLIT MN1 COOLING COIL Cooling Capacity [ton] | SPLIT MN1 COOLING COIL Cooling Capacity [ton] | 1.4152 | 1.3922 | 1.2841 | 1.2639 | 1.2389 | 1.2162 | 1.2153 | 1.191 |  |  | 2021-05-06
AZ_MA_SPLIT MN2 COOLING COIL Cooling Capacity [ton] | SPLIT MN2 COOLING COIL Cooling Capacity [ton] | 1.411 | 1.388 | 1.2789 | 1.2588 | 1.2313 | 1.2088 | 1.2062 | 1.1822 |  |  | 2021-05-06
AZ_MA_SPLIT MS1 COOLING COIL Cooling Capacity [ton] | SPLIT MS1 COOLING COIL Cooling Capacity [ton] | 1.4681 | 1.4452 | 1.3321 | 1.3133 | 1.2763 | 1.2528 | 1.2423 | 1.2178 |  |  | 2021-05-06
AZ_MA_SPLIT MS2 COOLING COIL Cooling Capacity [ton] | SPLIT MS2 COOLING COIL Cooling Capacity [ton] | 1.4641 | 1.4413 | 1.3282 | 1.3095 | 1.2698 | 1.2465 | 1.2344 | 1.2101 |  |  | 2021-05-06
AZ_MA_SPLIT TSW COOLING COIL Cooling Capacity [ton] | SPLIT TSW COOLING COIL Cooling Capacity [ton] | 1.3497 | 1.3329 | 1.2797 | 1.2658 | 1.3293 | 1.3077 | 1.3362 | 1.3128 |  |  | 2021-05-06
AZ_MA_SPLIT TNW COOLING COIL Cooling Capacity [ton] | SPLIT TNW COOLING COIL Cooling Capacity [ton] | 1.3257 | 1.3088 | 1.2484 | 1.235 | 1.3063 | 1.2846 | 1.3148 | 1.2913 |  |  | 2021-05-06
AZ_MA_SPLIT TSE COOLING COIL Cooling Capacity [ton] | SPLIT TSE COOLING COIL Cooling Capacity [ton] | 1.2668 | 1.2505 | 1.151 | 1.1384 | 1.1029 | 1.0862 | 1.0728 | 1.0552 |  |  | 2021-05-06
AZ_MA_SPLIT TNE COOLING COIL Cooling Capacity [ton] | SPLIT TNE COOLING COIL Cooling Capacity [ton] | 1.229 | 1.2123 | 1.0918 | 1.0798 | 1.0417 | 1.0258 | 1.014 | 0.99709 |  |  | 2021-05-06
AZ_MA_SPLIT TN1 COOLING COIL Cooling Capacity [ton] | SPLIT TN1 COOLING COIL Cooling Capacity [ton] | 0.93477 | 0.92281 | 0.84922 | 0.83894 | 0.84176 | 0.8297 | 0.81237 | 0.79962 |  |  | 2021-05-06
AZ_MA_SPLIT TN2 COOLING COIL Cooling Capacity [ton] | SPLIT TN2 COOLING COIL Cooling Capacity [ton] | 0.92995 | 0.91803 | 0.84379 | 0.83354 | 0.83374 | 0.82185 | 0.80646 | 0.79338 |  |  | 2021-05-06
AZ_MA_SPLIT TS1 COOLING COIL Cooling Capacity [ton] | SPLIT TS1 COOLING COIL Cooling Capacity [ton] | 1.02 | 1.0071 | 0.92716 | 0.91647 | 0.89004 | 0.87665 | 0.86939 | 0.85521 |  |  | 2021-05-06
AZ_MA_SPLIT TS2 COOLING COIL Cooling Capacity [ton] | SPLIT TS2 COOLING COIL Cooling Capacity [ton] | 1.0232 | 1.0103 | 0.93103 | 0.92029 | 0.89105 | 0.8777 | 0.86976 | 0.85567 |  |  | 2021-05-06
AZ_MA_Split GN1 Furnace with DX Cooling OA Rate [cfm] | Split GN1 Furnace with DX Cooling OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 |  |  | 2021-05-06
AZ_MA_Split GN2 Furnace with DX Cooling OA Rate [cfm] | Split GN2 Furnace with DX Cooling OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 |  |  | 2021-05-06
AZ_MA_Split GNE Furnace with DX Cooling OA Rate [cfm] | Split GNE Furnace with DX Cooling OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 |  |  | 2021-05-06
AZ_MA_Split GNW Furnace with DX Cooling OA Rate [cfm] | Split GNW Furnace with DX Cooling OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 |  |  | 2021-05-06
AZ_MA_Split GS1 Furnace with DX Cooling OA Rate [cfm] | Split GS1 Furnace with DX Cooling OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 |  |  | 2021-05-06
AZ_MA_Split GS2 Furnace with DX Cooling OA Rate [cfm] | Split GS2 Furnace with DX Cooling OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 |  |  | 2021-05-06
AZ_MA_Split GSW Furnace with DX Cooling OA Rate [cfm] | Split GSW Furnace with DX Cooling OA Rate [cfm] | 56.9945 | 56.9945 | 56.9945 | 56.9945 | 56.9945 | 56.9945 | 56.9945 | 56.9945 |  |  | 2021-05-06
AZ_MA_Split MN1 Furnace with DX Cooling OA Rate [cfm] | Split MN1 Furnace with DX Cooling OA Rate [cfm] | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824 |  |  | 2021-05-06
AZ_MA_Split MN2 Furnace with DX Cooling OA Rate [cfm] | Split MN2 Furnace with DX Cooling OA Rate [cfm] | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824 |  |  | 2021-05-06
AZ_MA_Split MNE Furnace with DX Cooling OA Rate [cfm] | Split MNE Furnace with DX Cooling OA Rate [cfm] | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824 |  |  | 2021-05-06
AZ_MA_Split MNW Furnace with DX Cooling OA Rate [cfm] | Split MNW Furnace with DX Cooling OA Rate [cfm] | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824 |  |  | 2021-05-06
AZ_MA_Split MS1 Furnace with DX Cooling OA Rate [cfm] | Split MS1 Furnace with DX Cooling OA Rate [cfm] | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824 |  |  | 2021-05-06
AZ_MA_Split MS2 Furnace with DX Cooling OA Rate [cfm] | Split MS2 Furnace with DX Cooling OA Rate [cfm] | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824 |  |  | 2021-05-06
AZ_MA_Split MSE Furnace with DX Cooling OA Rate [cfm] | Split MSE Furnace with DX Cooling OA Rate [cfm] | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824 |  |  | 2021-05-06
AZ_MA_Split MSW Furnace with DX Cooling OA Rate [cfm] | Split MSW Furnace with DX Cooling OA Rate [cfm] | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824 |  |  | 2021-05-06
AZ_MA_Split Office Furnace with DX Cooling OA Rate [cfm] | Split Office Furnace with DX Cooling OA Rate [cfm] | 80.7372 | 80.7372 | 80.7372 | 80.7372 | 80.7372 | 80.7372 | 80.7372 | 80.7372 |  |  | 2021-05-06
AZ_MA_Split TN1 Furnace with DX Cooling OA Rate [cfm] | Split TN1 Furnace with DX Cooling OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 |  |  | 2021-05-06
AZ_MA_Split TN2 Furnace with DX Cooling OA Rate [cfm] | Split TN2 Furnace with DX Cooling OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 |  |  | 2021-05-06
AZ_MA_Split TNE Furnace with DX Cooling OA Rate [cfm] | Split TNE Furnace with DX Cooling OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 |  |  | 2021-05-06
AZ_MA_Split TNW Furnace with DX Cooling OA Rate [cfm] | Split TNW Furnace with DX Cooling OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 |  |  | 2021-05-06
AZ_MA_Split TS1 Furnace with DX Cooling OA Rate [cfm] | Split TS1 Furnace with DX Cooling OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 |  |  | 2021-05-06
AZ_MA_Split TS2 Furnace with DX Cooling OA Rate [cfm] | Split TS2 Furnace with DX Cooling OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 |  |  | 2021-05-06
AZ_MA_Split TSE Furnace with DX Cooling OA Rate [cfm] | Split TSE Furnace with DX Cooling OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 |  |  | 2021-05-06
AZ_MA_Split TSW Furnace with DX Cooling OA Rate [cfm] | Split TSW Furnace with DX Cooling OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 |  |  | 2021-05-06
AZ_MA_SPLIT GSW HEATING COIL Heating Capacity [kBtu/hr] | SPLIT GSW HEATING COIL Heating Capacity [kBtu/hr] | 4.1679 | 4.0792 | 5.1548 | 5.0871 | 5.8734 | 5.9315 | 7.5862 | 7.6465 |  |  | 2021-05-06
AZ_MA_SPLIT GNW HEATING COIL Heating Capacity [kBtu/hr] | SPLIT GNW HEATING COIL Heating Capacity [kBtu/hr] | 4.0837 | 3.9991 | 5.0837 | 5.0163 | 5.7813 | 5.8396 | 7.4829 | 7.5435 |  |  | 2021-05-06
AZ_MA_SPLIT OFFICE HEATING COIL Heating Capacity [kBtu/hr] | SPLIT OFFICE HEATING COIL Heating Capacity [kBtu/hr] | 12.5315 | 12.3617 | 14.4881 | 14.382 | 15.9878 | 16.1323 | 19.2366 | 19.3694 |  |  | 2021-05-06
AZ_MA_SPLIT GNE HEATING COIL Heating Capacity [kBtu/hr] | SPLIT GNE HEATING COIL Heating Capacity [kBtu/hr] | 4.0973 | 4.0102 | 5.0985 | 5.0288 | 5.7702 | 5.8285 | 7.494 | 7.5545 |  |  | 2021-05-06
AZ_MA_SPLIT GN1 HEATING COIL Heating Capacity [kBtu/hr] | SPLIT GN1 HEATING COIL Heating Capacity [kBtu/hr] | 3.9257 | 3.9257 | 4.1847 | 4.1847 | 4.2821 | 4.2821 | 5.5124 | 5.573 |  |  | 2021-05-06
AZ_MA_SPLIT GN2 HEATING COIL Heating Capacity [kBtu/hr] | SPLIT GN2 HEATING COIL Heating Capacity [kBtu/hr] | 3.9257 | 3.9257 | 4.1847 | 4.1847 | 4.2821 | 4.2821 | 5.5128 | 5.5734 |  |  | 2021-05-06
AZ_MA_SPLIT GS1 HEATING COIL Heating Capacity [kBtu/hr] | SPLIT GS1 HEATING COIL Heating Capacity [kBtu/hr] | 3.9257 | 3.9257 | 4.1847 | 4.1847 | 4.2821 | 4.2821 | 5.513 | 5.5734 |  |  | 2021-05-06
AZ_MA_SPLIT GS2 HEATING COIL Heating Capacity [kBtu/hr] | SPLIT GS2 HEATING COIL Heating Capacity [kBtu/hr] | 3.9257 | 3.9257 | 4.1847 | 4.1847 | 4.5212 | 4.5833 | 5.9849 | 6.0488 |  |  | 2021-05-06
AZ_MA_SPLIT MSW HEATING COIL Heating Capacity [kBtu/hr] | SPLIT MSW HEATING COIL Heating Capacity [kBtu/hr] | 8.2187 | 8.0401 | 9.9134 | 9.7732 | 10.6909 | 10.823 | 12.7789 | 12.9111 |  |  | 2021-05-06
AZ_MA_SPLIT MNW HEATING COIL Heating Capacity [kBtu/hr] | SPLIT MNW HEATING COIL Heating Capacity [kBtu/hr] | 8.1729 | 8.0027 | 9.9215 | 9.7811 | 10.6594 | 10.7911 | 12.75 | 12.8818 |  |  | 2021-05-06
AZ_MA_SPLIT MSE HEATING COIL Heating Capacity [kBtu/hr] | SPLIT MSE HEATING COIL Heating Capacity [kBtu/hr] | 8.2521 | 8.0674 | 9.9491 | 9.8038 | 10.664 | 10.7961 | 12.8058 | 12.938 |  |  | 2021-05-06
AZ_MA_SPLIT MNE HEATING COIL Heating Capacity [kBtu/hr] | SPLIT MNE HEATING COIL Heating Capacity [kBtu/hr] | 8.2063 | 8.03 | 9.9571 | 9.8116 | 10.6325 | 10.7642 | 12.777 | 12.9088 |  |  | 2021-05-06
AZ_MA_SPLIT MN1 HEATING COIL Heating Capacity [kBtu/hr] | SPLIT MN1 HEATING COIL Heating Capacity [kBtu/hr] | 7.8514 | 7.8514 | 8.3693 | 8.3693 | 8.5642 | 8.5642 | 9.6869 | 9.6869 |  |  | 2021-05-06
AZ_MA_SPLIT MN2 HEATING COIL Heating Capacity [kBtu/hr] | SPLIT MN2 HEATING COIL Heating Capacity [kBtu/hr] | 7.8514 | 7.8514 | 8.3693 | 8.3693 | 8.5642 | 8.5642 | 9.6869 | 9.6869 |  |  | 2021-05-06
AZ_MA_SPLIT MS1 HEATING COIL Heating Capacity [kBtu/hr] | SPLIT MS1 HEATING COIL Heating Capacity [kBtu/hr] | 7.8514 | 7.8514 | 8.3693 | 8.3693 | 8.5642 | 8.5642 | 9.6869 | 9.6869 |  |  | 2021-05-06
AZ_MA_SPLIT MS2 HEATING COIL Heating Capacity [kBtu/hr] | SPLIT MS2 HEATING COIL Heating Capacity [kBtu/hr] | 7.8514 | 7.8514 | 8.3693 | 8.3693 | 8.5642 | 8.5642 | 9.6869 | 9.6869 |  |  | 2021-05-06
AZ_MA_SPLIT TSW HEATING COIL Heating Capacity [kBtu/hr] | SPLIT TSW HEATING COIL Heating Capacity [kBtu/hr] | 6.6544 | 6.5713 | 7.8343 | 7.7644 | 8.0635 | 8.125 | 9.6477 | 9.7097 |  |  | 2021-05-06
AZ_MA_SPLIT TNW HEATING COIL Heating Capacity [kBtu/hr] | SPLIT TNW HEATING COIL Heating Capacity [kBtu/hr] | 6.6364 | 6.5589 | 7.8438 | 7.7744 | 8.0526 | 8.1142 | 9.6382 | 9.7003 |  |  | 2021-05-06
AZ_MA_SPLIT TSE HEATING COIL Heating Capacity [kBtu/hr] | SPLIT TSE HEATING COIL Heating Capacity [kBtu/hr] | 6.6719 | 6.5855 | 7.8532 | 7.7805 | 8.0493 | 8.1108 | 9.6624 | 9.7243 |  |  | 2021-05-06
AZ_MA_SPLIT TNE HEATING COIL Heating Capacity [kBtu/hr] | SPLIT TNE HEATING COIL Heating Capacity [kBtu/hr] | 6.654 | 6.5731 | 7.8627 | 7.7905 | 8.0383 | 8.0999 | 9.6529 | 9.715 |  |  | 2021-05-06
AZ_MA_SPLIT TN1 HEATING COIL Heating Capacity [kBtu/hr] | SPLIT TN1 HEATING COIL Heating Capacity [kBtu/hr] | 4.9904 | 4.9609 | 6.0122 | 5.9867 | 6.1274 | 6.1889 | 7.6678 | 7.7299 |  |  | 2021-05-06
AZ_MA_SPLIT TN2 HEATING COIL Heating Capacity [kBtu/hr] | SPLIT TN2 HEATING COIL Heating Capacity [kBtu/hr] | 4.991 | 4.9613 | 6.0127 | 5.9872 | 6.1269 | 6.1885 | 7.6682 | 7.7303 |  |  | 2021-05-06
AZ_MA_SPLIT TS1 HEATING COIL Heating Capacity [kBtu/hr] | SPLIT TS1 HEATING COIL Heating Capacity [kBtu/hr] | 5.0023 | 4.967 | 5.9961 | 5.97 | 6.1318 | 6.1932 | 7.6712 | 7.7332 |  |  | 2021-05-06
AZ_MA_SPLIT TS2 HEATING COIL Heating Capacity [kBtu/hr] | SPLIT TS2 HEATING COIL Heating Capacity [kBtu/hr] | 5.0028 | 4.9674 | 5.9967 | 5.9705 | 6.1313 | 6.1928 | 7.6717 | 7.7337 |  |  | 2021-05-06
AZ_MA_Split_GSW ERV Flag | Split_GSW ERV Flag | No | Yes | No | Yes | No | Yes | No | Yes |  |  | 2021-05-06
AZ_MA_Split_GNW ERV Flag | Split_GNW ERV Flag | No | Yes | No | Yes | No | Yes | No | Yes |  |  | 2021-05-06
AZ_MA_Split_GNE ERV Flag | Split_GNE ERV Flag | No | Yes | No | Yes | No | Yes | No | Yes |  |  | 2021-05-06
AZ_MA_Split_GN1 ERV Flag | Split_GN1 ERV Flag | No | Yes | No | Yes | No | Yes | No | Yes |  |  | 2021-05-06
AZ_MA_Split_GN2 ERV Flag | Split_GN2 ERV Flag | No | Yes | No | Yes | No | Yes | No | Yes |  |  | 2021-05-06
AZ_MA_Split_GS1 ERV Flag | Split_GS1 ERV Flag | No | Yes | No | Yes | No | Yes | No | Yes |  |  | 2021-05-06
AZ_MA_Split_GS2 ERV Flag | Split_GS2 ERV Flag | No | Yes | No | Yes | No | Yes | No | Yes |  |  | 2021-05-06
AZ_MA_Split_MSW ERV Flag | Split_MSW ERV Flag | No | Yes | No | Yes | No | Yes | No | Yes |  |  | 2021-05-06
AZ_MA_Split_MNW ERV Flag | Split_MNW ERV Flag | No | Yes | No | Yes | No | Yes | No | Yes |  |  | 2021-05-06
AZ_MA_Split_MSE ERV Flag | Split_MSE ERV Flag | No | Yes | No | Yes | No | Yes | No | Yes |  |  | 2021-05-06
AZ_MA_Split_MNE ERV Flag | Split_MNE ERV Flag | No | Yes | No | Yes | No | Yes | No | Yes |  |  | 2021-05-06
AZ_MA_Split_MN1 ERV Flag | Split_MN1 ERV Flag | No | Yes | No | Yes | No | Yes | No | Yes |  |  | 2021-05-06
AZ_MA_Split_MN2 ERV Flag | Split_MN2 ERV Flag | No | Yes | No | Yes | No | Yes | No | Yes |  |  | 2021-05-06
AZ_MA_Split_MS1 ERV Flag | Split_MS1 ERV Flag | No | Yes | No | Yes | No | Yes | No | Yes |  |  | 2021-05-06
AZ_MA_Split_MS2 ERV Flag | Split_MS2 ERV Flag | No | Yes | No | Yes | No | Yes | No | Yes |  |  | 2021-05-06
AZ_MA_Split_TSW ERV Flag | Split_TSW ERV Flag | No | No | No | No | No | No | No | No |  |  | 2021-05-06
AZ_MA_Split_TNW ERV Flag | Split_TNW ERV Flag | No | No | No | No | No | No | No | No |  |  | 2021-05-06
AZ_MA_Split_TSE ERV Flag | Split_TSE ERV Flag | No | Yes | No | Yes | No | Yes | No | Yes |  |  | 2021-05-06
AZ_MA_Split_TNE ERV Flag | Split_TNE ERV Flag | No | Yes | No | Yes | No | Yes | No | Yes |  |  | 2021-05-06
AZ_MA_Split_TN1 ERV Flag | Split_TN1 ERV Flag | No | Yes | No | Yes | No | Yes | No | Yes |  |  | 2021-05-06
AZ_MA_Split_TN2 ERV Flag | Split_TN2 ERV Flag | No | Yes | No | Yes | No | Yes | No | Yes |  |  | 2021-05-06
AZ_MA_Split_TS1 ERV Flag | Split_TS1 ERV Flag | No | Yes | No | Yes | No | Yes | No | Yes |  |  | 2021-05-06
AZ_MA_Split_TS2 ERV Flag | Split_TS2 ERV Flag | No | Yes | No | Yes | No | Yes | No | Yes |  |  | 2021-05-06
id | item | Zone2B(CA-Tucson-AZ) ASHRAE901-state_STD2016 | Zone2B(CA-Tucson-AZ) ASHRAE901-state_STD2019 | Zone3B(CA-LosAngeles-CA) ASHRAE901-state_STD2016 | Zone3B(CA-LosAngeles-CA) ASHRAE901-state_STD2019 | Zone3C(CA-SanFrancisco-CA) ASHRAE901-state_STD2016 | Zone3C(CA-SanFrancisco-CA) ASHRAE901-state_STD2019 | Zone4B(CA-Bishop-CA) ASHRAE901-state_STD2016 | Zone4B(CA-Bishop-CA) ASHRAE901-state_STD2019 | Zone5B(CA-Winnermucca-NV) ASHRAE901-state_STD2016 | Zone5B(CA-Winnermucca-NV) ASHRAE901-state_STD2019 | 2021-05-06
CA_SO_PSZ-AC:1 Cooling Capacity [ton] | PSZ-AC:1 Cooling Capacity [ton] | 1.8993 | 1.7928 | 1.452 | 1.3613 | 1.3934 | 1.2943 | 1.6666 | 1.5664 | 1.6619 | 1.5476 | 2021-05-06
CA_SO_PSZ-AC:2 Cooling Capacity [ton] | PSZ-AC:2 Cooling Capacity [ton] | 1.8663 | 1.7754 | 1.2728 | 1.1996 | 1.2749 | 1.193 | 1.5433 | 1.4654 | 1.4865 | 1.4081 | 2021-05-06
CA_SO_PSZ-AC:3 Cooling Capacity [ton] | PSZ-AC:3 Cooling Capacity [ton] | 1.2048 | 1.1445 | 0.93723 | 0.89449 | 0.90812 | 0.86614 | 1.0698 | 1.0219 | 1.0972 | 1.049 | 2021-05-06
CA_SO_PSZ-AC:4 Cooling Capacity [ton] | PSZ-AC:4 Cooling Capacity [ton] | 1.8702 | 1.7711 | 1.1734 | 1.099 | 1.072 | 0.99647 | 1.4886 | 1.4054 | 1.4 | 1.3161 | 2021-05-06
CA_SO_PSZ-AC:5 Cooling Capacity [ton] | PSZ-AC:5 Cooling Capacity [ton] | 1.442 | 1.38 | 1.0937 | 1.0496 | 1.0881 | 1.0445 | 1.4222 | 1.3707 | 1.4191 | 1.3674 | 2021-05-06
CA_SO_PSZ-AC:1 Supply Flow Rate [cfm] | PSZ-AC:1 Supply Flow Rate [cfm] | 762.7968 | 720.4192 | 635.664 | 593.2864 | 635.664 | 572.0976 | 741.608 | 699.2304 | 741.608 | 699.2304 | 2021-05-06
CA_SO_PSZ-AC:2 Supply Flow Rate [cfm] | PSZ-AC:2 Supply Flow Rate [cfm] | 783.9856 | 741.608 | 572.0976 | 529.72 | 572.0976 | 529.72 | 699.2304 | 656.8528 | 678.0416 | 635.664 | 2021-05-06
CA_SO_PSZ-AC:3 Supply Flow Rate [cfm] | PSZ-AC:3 Supply Flow Rate [cfm] | 550.9088 | 508.5312 | 423.776 | 402.5872 | 402.5872 | 381.3984 | 487.3424 | 466.1536 | 487.3424 | 466.1536 | 2021-05-06
CA_SO_PSZ-AC:4 Supply Flow Rate [cfm] | PSZ-AC:4 Supply Flow Rate [cfm] | 783.9856 | 720.4192 | 529.72 | 487.3424 | 487.3424 | 444.9648 | 678.0416 | 635.664 | 635.664 | 593.2864 | 2021-05-06
CA_SO_PSZ-AC:5 Supply Flow Rate [cfm] | PSZ-AC:5 Supply Flow Rate [cfm] | 656.8528 | 614.4752 | 487.3424 | 466.1536 | 487.3424 | 466.1536 | 635.664 | 614.4752 | 635.664 | 614.4752 | 2021-05-06
CA_SO_PSZ-AC:1 OA Rate [cfm] | PSZ-AC:1 OA Rate [cfm] | 136.9178 | 136.9178 | 136.9178 | 136.9178 | 136.9178 | 136.9178 | 136.9178 | 136.9178 | 136.9178 | 136.9178 | 2021-05-06
CA_SO_PSZ-AC:2 OA Rate [cfm] | PSZ-AC:2 OA Rate [cfm] | 103.7925 | 103.7925 | 103.7925 | 103.7925 | 103.7925 | 103.7925 | 103.7925 | 103.7925 | 103.7925 | 103.7925 | 2021-05-06
CA_SO_PSZ-AC:3 OA Rate [cfm] | PSZ-AC:3 OA Rate [cfm] | 61.5711 | 61.5711 | 61.5711 | 61.5711 | 61.5711 | 61.5711 | 61.5711 | 61.5711 | 61.5711 | 61.5711 | 2021-05-06
CA_SO_PSZ-AC:4 OA Rate [cfm] | PSZ-AC:4 OA Rate [cfm] | 103.7925 | 103.7925 | 103.7925 | 103.7925 | 103.7925 | 103.7925 | 103.7925 | 103.7925 | 103.7925 | 103.7925 | 2021-05-06
CA_SO_PSZ-AC:5 OA Rate [cfm] | PSZ-AC:5 OA Rate [cfm] | 61.5711 | 61.5711 | 61.5711 | 61.5711 | 61.5711 | 61.5711 | 61.5711 | 61.5711 | 61.5711 | 61.5711 | 2021-05-06
CA_SO_PSZ-AC:1 heating Capacity [kBtu/hr] | PSZ-AC:1 heating Capacity [kBtu/hr] | 9.7743 | 9.7743 | 8.8005 | 8.8005 | 9.6567 | 9.6567 | 11.3872 | 11.3872 | 12.8538 | 12.8538 | 2021-05-06
CA_SO_PSZ-AC:2 heating Capacity [kBtu/hr] | PSZ-AC:2 heating Capacity [kBtu/hr] | 12.016 | 11.5549 | 8.9588 | 8.835 | 11.0614 | 10.9123 | 14.9028 | 14.7247 | 17.6945 | 17.4708 | 2021-05-06
CA_SO_PSZ-AC:3 heating Capacity [kBtu/hr] | PSZ-AC:3 heating Capacity [kBtu/hr] | 7.2612 | 7.0058 | 5.4822 | 5.4136 | 6.7824 | 6.6998 | 9.0557 | 8.9571 | 10.6978 | 10.5741 | 2021-05-06
CA_SO_PSZ-AC:4 heating Capacity [kBtu/hr] | PSZ-AC:4 heating Capacity [kBtu/hr] | 11.6628 | 11.3011 | 8.8243 | 8.723 | 10.8819 | 10.7644 | 14.7998 | 14.6487 | 17.427 | 17.2502 | 2021-05-06
CA_SO_PSZ-AC:5 heating Capacity [kBtu/hr] | PSZ-AC:5 heating Capacity [kBtu/hr] | 7.2265 | 6.9819 | 5.4785 | 5.4123 | 6.7713 | 6.6917 | 9.088 | 8.9858 | 10.6553 | 10.5357 | 2021-05-06
id | item | Zone2B(CA-Tucson-AZ) ASHRAE901-state_STD2016 | Zone2B(CA-Tucson-AZ) ASHRAE901-state_STD2019 | Zone3B(CA-LosAngeles-CA) ASHRAE901-state_STD2016 | Zone3B(CA-LosAngeles-CA) ASHRAE901-state_STD2019 | Zone3C(CA-SanFrancisco-CA) ASHRAE901-state_STD2016 | Zone3C(CA-SanFrancisco-CA) ASHRAE901-state_STD2019 | Zone4B(CA-Bishop-CA) ASHRAE901-state_STD2016 | Zone4B(CA-Bishop-CA) ASHRAE901-state_STD2019 | Zone5B(CA-Winnermucca-NV) ASHRAE901-state_STD2016 | Zone5B(CA-Winnermucca-NV) ASHRAE901-state_STD2019 | 2021-05-06
CA_LO_CAV_BAS Supply Flow Rate [cfm] | CAV_BAS Supply Flow Rate [cfm] | 12755.6576 | 11802.1616 | 11463.1408 | 10594.4 | 11251.2528 | 10403.7008 | 13560.832 | 12564.9584 | 13539.6432 | 12522.5808 | 2021-05-06
CA_LO_VAV_BOT WITH REHEAT Supply Flow Rate [cfm] | VAV_BOT WITH REHEAT Supply Flow Rate [cfm] | 21421.8768 | 20362.4368 | 18582.5776 | 17650.2704 | 18095.2352 | 17162.928 | 21993.9744 | 20934.5344 | 22375.3728 | 21315.9328 | 2021-05-06
CA_LO_VAV_MID WITH REHEAT Supply Flow Rate [cfm] | VAV_MID WITH REHEAT Supply Flow Rate [cfm] | 200446.0483 | 190317.8019 | 171438.5811 | 162475.7186 | 165950.6819 | 157093.7634 | 202946.3267 | 192818.0803 | 207162.8979 | 197013.4627 | 2021-05-06
CA_LO_VAV_TOP WITH REHEAT Supply Flow Rate [cfm] | VAV_TOP WITH REHEAT Supply Flow Rate [cfm] | 22121.1072 | 21061.6672 | 17184.1168 | 16400.1312 | 16802.7184 | 16039.9216 | 22756.7712 | 21824.464 | 23032.2256 | 22099.9184 | 2021-05-06
CA_LO_Supply Air Temp. Reset Flag | Supply Air Temp. Reset Flag | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 2021-05-06
CA_LO_CAV_BAS OA Rate [cfm] | CAV_BAS OA Rate [cfm] | 2542.8255 | 2542.8255 | 2542.8255 | 2542.8255 | 2542.8255 | 2542.8255 | 2542.8255 | 2542.8255 | 2542.8255 | 2542.8255 | 2021-05-06
CA_LO_VAV_BOT WITH REHEAT OA Rate [cfm] | VAV_BOT WITH REHEAT OA Rate [cfm] | 5377.8022 | 4302.174 | 5377.8022 | 4302.174 | 5377.8022 | 4302.174 | 5377.8022 | 4302.174 | 5377.8022 | 4302.174 | 2021-05-06
CA_LO_VAV_MID WITH REHEAT OA Rate [cfm] | VAV_MID WITH REHEAT OA Rate [cfm] | 53777.9373 | 43021.7396 | 53777.9373 | 43021.7396 | 53777.9373 | 43021.7396 | 53777.9373 | 43021.7396 | 53777.9373 | 43021.7396 | 2021-05-06
CA_LO_VAV_TOP WITH REHEAT OA Rate [cfm] | VAV_TOP WITH REHEAT OA Rate [cfm] | 5377.8022 | 4302.174 | 5377.8022 | 4302.174 | 5377.8022 | 4302.174 | 5377.8022 | 4302.174 | 5377.8022 | 4302.174 | 2021-05-06
CA_LO_AIRLOOP DATACENTER BASEMENT OA Rate [cfm] | AIRLOOP DATACENTER BASEMENT OA Rate [cfm] | 716.9654 | 716.9654 | 716.9654 | 716.9654 | 716.9654 | 716.9654 | 716.9654 | 716.9654 | 716.9654 | 716.9654 | 2021-05-06
CA_LO_VAV_bot_WITH_REHEAT ERV Flag | VAV_bot_WITH_REHEAT ERV Flag | No | No | No | No | No | No | No | No | No | No | 2021-05-06
CA_LO_VAV_mid_WITH_REHEAT ERV Flag | VAV_mid_WITH_REHEAT ERV Flag | No | No | No | No | No | No | No | No | No | No | 2021-05-06
CA_LO_VAV_top_WITH_REHEAT ERV Flag | VAV_top_WITH_REHEAT ERV Flag | No | No | No | No | No | No | No | No | No | No | 2021-05-06
CA_LO_COOLSYS1 CHILLER1 Capacity [ton] | COOLSYS1 CHILLER1 Capacity [ton] | 351.0896 | 320.5842 | 300.5207 | 259.4351 | 256.8252 | 243.1706 | 324.4068 | 299.9455 | 322.432 | 298.9751 | 2021-05-06
CA_LO_COOLSYS1 CHILLER2 Capacity [ton] | COOLSYS1 CHILLER2 Capacity [ton] | 351.0896 | 320.5842 | 300.5207 | 259.4351 | 256.8252 | 243.1706 | 324.4068 | 299.9455 | 322.432 | 298.9751 | 2021-05-06
CA_LO_TOWERWATERSYS COOLTOWER 1 Capacity [ton] | TOWERWATERSYS COOLTOWER 1 Capacity [ton] | 333.3914 | 304.4334 | 285.4969 | 246.4628 | 244.0738 | 231.1013 | 308.3059 | 285.0551 | 306.4264 | 284.1351 | 2021-05-06
CA_LO_TOWERWATERSYS COOLTOWER 2 Capacity [ton] | TOWERWATERSYS COOLTOWER 2 Capacity [ton] | 333.3914 | 304.4334 | 285.4969 | 246.4628 | 244.0738 | 231.1013 | 308.3059 | 285.0551 | 306.4264 | 284.1351 | 2021-05-06
CA_LO_HEATSYS1 BOILER Capacity [MMBTU/h] | HEATSYS1 BOILER Capacity [MMBTU/h] | 2999.3671 | 2659.67 | 2126.6414 | 1908.1778 | 2473.9813 | 2255.9627 | 3609.1889 | 3190.9096 | 4181.3373 | 3697.073 | 2021-05-06
CA_LO_COOLSYS1 PUMP Flow Rate [gal/min] | COOLSYS1 PUMP Flow Rate [gal/min] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2021-05-06
CA_LO_COOLSYS1 CHILLER1 PUMP Flow Rate [gal/min] | COOLSYS1 CHILLER1 PUMP Flow Rate [gal/min] | 549.2787 | 501.3901 | 472.6852 | 405.4766 | 401.2018 | 379.8863 | 509.3042 | 468.5562 | 506.7126 | 469.4993 | 2021-05-06
CA_LO_COOLSYS1 CHILLER2 PUMP Flow Rate [gal/min] | COOLSYS1 CHILLER2 PUMP Flow Rate [gal/min] | 549.2787 | 501.3901 | 472.6852 | 405.4766 | 401.2018 | 379.8863 | 509.3042 | 468.5562 | 506.7126 | 469.4993 | 2021-05-06
CA_LO_COOLSYS1 PUMP SECONDARY Flow Rate [gal/min] | COOLSYS1 PUMP SECONDARY Flow Rate [gal/min] | 1098.5574 | 1002.7786 | 945.3703 | 810.9548 | 802.4036 | 759.7741 | 1018.6083 | 937.1107 | 1013.4253 | 939.0001 | 2021-05-06
CA_LO_HEATSYS1 PUMP Flow Rate [gal/min] | HEATSYS1 PUMP Flow Rate [gal/min] | 615.6598 | 545.9327 | 436.5211 | 391.6789 | 507.8174 | 463.0656 | 740.833 | 654.9766 | 858.2744 | 758.8723 | 2021-05-06
CA_LO_TOWERWATERSYS PUMP Flow Rate [gal/min] | TOWERWATERSYS PUMP Flow Rate [gal/min] | 1936.9095 | 1768.7376 | 1657.9438 | 1466.3609 | 1451.609 | 1374.4322 | 1789.8185 | 1695.3506 | 1778.8818 | 1689.803 | 2021-05-06
CA_LO_PLANT CIRC PUMP Flow Rate [gal/min] | PLANT CIRC PUMP Flow Rate [gal/min] | 212.3499 | 211.4259 | 211.1659 | 210.3179 | 202.6717 | 201.8507 | 225.3472 | 224.4327 | 226.2871 | 225.3662 | 2021-05-06
CA_LO_COOLSYS1 PUMP SECONDARY Pressure setpoint reset [yes,no] | COOLSYS1 PUMP SECONDARY Pressure setpoint reset [yes,no] | pump_ride_on_curve | pump_ride_on_curve | pump_ride_on_curve | pump_ride_on_curve | pump_ride_on_curve | pump_ride_on_curve | pump_ride_on_curve | pump_ride_on_curve | pump_ride_on_curve | pump_ride_on_curve | 2021-05-06
CA_LO_COOLSYS1 CHILLER1 PUMP Pump Power [hp] | COOLSYS1 CHILLER1 PUMP Pump Power [hp] | 2.9632 | 2.678 | 2.55 | 2.1658 | 2.1643 | 2.0291 | 2.7475 | 2.5027 | 2.7335 | 2.5077 | 2021-05-06
CA_LO_COOLSYS1 CHILLER2 PUMP Pump Power [hp] | COOLSYS1 CHILLER2 PUMP Pump Power [hp] | 2.9632 | 2.678 | 2.55 | 2.1658 | 2.1643 | 2.0291 | 2.7475 | 2.5027 | 2.7335 | 2.5077 | 2021-05-06
CA_LO_COOLSYS1 PUMP SECONDARY Pump Power [hp] | COOLSYS1 PUMP SECONDARY Pump Power [hp] | 17.779 | 16.0682 | 15.2998 | 12.9945 | 12.9861 | 12.1744 | 16.4851 | 15.016 | 16.4012 | 15.0463 | 2021-05-06
CA_LO_HEATSYS1 PUMP Pump Power [hp] | HEATSYS1 PUMP Pump Power [hp] | 13.3078 | 11.6838 | 9.4357 | 8.3825 | 10.9768 | 9.9103 | 16.0135 | 14.0175 | 18.5521 | 16.2411 | 2021-05-06
CA_LO_TOWERWATERSYS PUMP Pump Power [hp] | TOWERWATERSYS PUMP Pump Power [hp] | 34.6799 | 31.3531 | 29.6848 | 25.9939 | 25.9898 | 24.3643 | 32.0442 | 30.0529 | 31.8492 | 29.9556 | 2021-05-06
CA_LO_PLANT CIRC PUMP Pump Power [hp] | PLANT CIRC PUMP Pump Power [hp] | 4.5822 | 4.5171 | 4.5567 | 4.4934 | 4.3734 | 4.3125 | 4.8627 | 4.795 | 4.883 | 4.8149 | 2021-05-06
CA_LO_Datacenter PLANT CIRC PUMP Pump Power [hp] | Datacenter PLANT CIRC PUMP Pump Power [hp] | 4.5822 | 4.5171 | 4.5567 | 4.4934 | 4.3734 | 4.3125 | 4.8627 | 4.795 | 4.883 | 4.8149 | 2021-05-06
CA_LO_ZN_VAV_BOXes_Max_Reheat_Water_Flow_GPM | ZN_VAV_BOXes_Max_Reheat_Water_Flow_GPM | 379.7153 | 354.4367 | 275.5298 | 258.8899 | 311.3397 | 295.2501 | 405.2069 | 387.1491 | 446.8856 | 427.916 | 2021-05-06
CA_LO_COOLSYS1 PUMP SECONDARY VSD | COOLSYS1 PUMP SECONDARY VSD | No | No | No | No | No | No | No | No | No | No | 2021-05-06
CA_LO_HEATSYS1 PUMP VSD | HEATSYS1 PUMP VSD | No | No | No | No | No | No | No | No | No | No | 2021-05-06
CA_LO_DATACENTER BASEMENT Cooling Capacity [ton] | DATACENTER BASEMENT Cooling Capacity [ton] | 124.8994 | 124.5296 | 124.4026 | 124.0331 | 119.2443 | 118.8894 | 132.3693 | 131.9739 | 132.4826 | 132.0867 | 2021-05-06
CA_LO_DATACENTER BOT Cooling Capacity [ton] | DATACENTER BOT Cooling Capacity [ton] | 2.6691 | 2.6413 | 2.635 | 2.6111 | 2.5423 | 2.5191 | 2.8356 | 2.8098 | 2.8799 | 2.8539 | 2021-05-06
CA_LO_DATACENTER MID Cooling Capacity [ton] | DATACENTER MID Cooling Capacity [ton] | 25.4099 | 25.1547 | 25.1014 | 24.8938 | 24.2215 | 24.018 | 27.0958 | 26.8685 | 27.5798 | 27.349 | 2021-05-06
CA_LO_DATACENTER TOP Cooling Capacity [ton] | DATACENTER TOP Cooling Capacity [ton] | 2.5728 | 2.5484 | 2.5449 | 2.5247 | 2.4531 | 2.4334 | 2.7714 | 2.7492 | 2.8178 | 2.7955 | 2021-05-06
id | item | Zone2B(CA-Tucson-AZ) ASHRAE901-state_STD2016 | Zone2B(CA-Tucson-AZ) ASHRAE901-state_STD2019 | Zone3B(CA-LosAngeles-CA) ASHRAE901-state_STD2016 | Zone3B(CA-LosAngeles-CA) ASHRAE901-state_STD2019 | Zone3C(CA-SanFrancisco-CA) ASHRAE901-state_STD2016 | Zone3C(CA-SanFrancisco-CA) ASHRAE901-state_STD2019 | Zone4B(CA-Bishop-CA) ASHRAE901-state_STD2016 | Zone4B(CA-Bishop-CA) ASHRAE901-state_STD2019 | Zone5B(CA-Winnermucca-NV) ASHRAE901-state_STD2016 | Zone5B(CA-Winnermucca-NV) ASHRAE901-state_STD2019 | 2021-05-06
CA_RS_PSZ-AC:1 Cooling Capacity [ton] | PSZ-AC:1 Cooling Capacity [ton] | 10.6344 | 9.9987 | 9.1367 | 8.6777 | 7.5943 | 7.069 | 10.8592 | 10.1193 | 10.2201 | 9.4539 | 2021-05-06
CA_RS_PSZ-AC:2 Cooling Capacity [ton] | PSZ-AC:2 Cooling Capacity [ton] | 47.0467 | 44.8921 | 38.2996 | 36.3591 | 32.719 | 30.5812 | 45.723 | 43.7337 | 43.9728 | 41.9165 | 2021-05-06
CA_RS_PSZ-AC:3 Cooling Capacity [ton] | PSZ-AC:3 Cooling Capacity [ton] | 6.672 | 6.5073 | 5.1406 | 4.9881 | 4.5836 | 4.4428 | 6.207 | 6.05 | 5.9323 | 5.7747 | 2021-05-06
CA_RS_PSZ-AC:4 Cooling Capacity [ton] | PSZ-AC:4 Cooling Capacity [ton] | 5.4797 | 5.2801 | 4.0739 | 3.9129 | 3.5807 | 3.437 | 5.014 | 4.8423 | 4.7692 | 4.5951 | 2021-05-06
CA_RS_PSZ-AC:1 Supply Flow Rate [cfm] | PSZ-AC:1 Supply Flow Rate [cfm] | 4788.6688 | 4492.0256 | 3665.6624 | 3369.0192 | 3326.6416 | 3008.8096 | 4343.704 | 4004.6832 | 4195.3824 | 3835.1728 | 2021-05-06
CA_RS_PSZ-AC:2 Supply Flow Rate [cfm] | PSZ-AC:2 Supply Flow Rate [cfm] | 17056.984 | 16061.1104 | 14641.4608 | 13687.9648 | 14111.7408 | 13115.8672 | 17120.5504 | 16209.432 | 17120.5504 | 16124.6768 | 2021-05-06
CA_RS_PSZ-AC:3 Supply Flow Rate [cfm] | PSZ-AC:3 Supply Flow Rate [cfm] | 2669.7888 | 2585.0336 | 2118.88 | 2055.3136 | 2055.3136 | 1991.7472 | 2521.4672 | 2457.9008 | 2500.2784 | 2415.5232 | 2021-05-06
CA_RS_PSZ-AC:4 Supply Flow Rate [cfm] | PSZ-AC:4 Supply Flow Rate [cfm] | 2118.88 | 2034.1248 | 1610.3488 | 1546.7824 | 1589.16 | 1525.5936 | 1970.5584 | 1885.8032 | 1928.1808 | 1843.4256 | 2021-05-06
CA_RS_PSZ-AC:1 OA Rate [cfm] | PSZ-AC:1 OA Rate [cfm] | 490.669 | 490.669 | 490.669 | 490.669 | 490.669 | 490.669 | 490.669 | 490.669 | 490.669 | 490.669 | 2021-05-06
CA_RS_PSZ-AC:2 OA Rate [cfm] | PSZ-AC:2 OA Rate [cfm] | 4005.1282 | 4005.1282 | 4005.1282 | 4005.1282 | 4005.1282 | 4005.1282 | 4005.1282 | 4005.1282 | 4005.1282 | 4005.1282 | 2021-05-06
CA_RS_PSZ-AC:3 OA Rate [cfm] | PSZ-AC:3 OA Rate [cfm] | 377.3937 | 377.3937 | 377.3937 | 377.3937 | 377.3937 | 377.3937 | 377.3937 | 377.3937 | 377.3937 | 377.3937 | 2021-05-06
CA_RS_PSZ-AC:4 OA Rate [cfm] | PSZ-AC:4 OA Rate [cfm] | 377.3937 | 377.3937 | 377.3937 | 377.3937 | 377.3937 | 377.3937 | 377.3937 | 377.3937 | 377.3937 | 377.3937 | 2021-05-06
CA_RS_PSZ-AC:1 OA Damper [gravity, motorized] | PSZ-AC:1 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | motorized | motorized | motorized | motorized | motorized | motorized | 2021-05-06
CA_RS_PSZ-AC:2 OA Damper [gravity, motorized] | PSZ-AC:2 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | motorized | motorized | motorized | motorized | motorized | motorized | 2021-05-06
CA_RS_PSZ-AC:3 OA Damper [gravity, motorized] | PSZ-AC:3 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | motorized | gravity | motorized | motorized | motorized | motorized | 2021-05-06
CA_RS_PSZ-AC:4 OA Damper [gravity, motorized] | PSZ-AC:4 OA Damper [gravity, motorized] | motorized | motorized | gravity | gravity | gravity | gravity | motorized | motorized | motorized | motorized | 2021-05-06
CA_RS_PSZ-AC:1 Heating Capacity [kBtu/hr] | PSZ-AC:1 Heating Capacity [kBtu/hr] | 180.6647 | 170.8138 | 146.7748 | 134.3462 | 135.6411 | 128.678 | 162.6946 | 150.3619 | 161.9946 | 148.756 | 2021-05-06
CA_RS_PSZ-AC:2 Heating Capacity [kBtu/hr] | PSZ-AC:2 Heating Capacity [kBtu/hr] | 720.0791 | 681.9391 | 636.8952 | 596.605 | 638.9134 | 602.5878 | 740.5256 | 707.0841 | 778.5832 | 742.7497 | 2021-05-06
CA_RS_PSZ-AC:3 Heating Capacity [kBtu/hr] | PSZ-AC:3 Heating Capacity [kBtu/hr] | 104.3196 | 101.6695 | 88.8808 | 86.2072 | 86.8817 | 86.8909 | 98.9005 | 96.3005 | 101.5724 | 98.8633 | 2021-05-06
CA_RS_PSZ-AC:4 Heating Capacity [kBtu/hr] | PSZ-AC:4 Heating Capacity [kBtu/hr] | 85.0595 | 82.2326 | 68.3606 | 67.5078 | 71.6361 | 69.0548 | 82.0631 | 79.5136 | 84.738 | 82.0921 | 2021-05-06
id | item | Zone2B(CA-Tucson-AZ) ASHRAE901-state_STD2016 | Zone2B(CA-Tucson-AZ) ASHRAE901-state_STD2019 | Zone3B(CA-LosAngeles-CA) ASHRAE901-state_STD2016 | Zone3B(CA-LosAngeles-CA) ASHRAE901-state_STD2019 | Zone3C(CA-SanFrancisco-CA) ASHRAE901-state_STD2016 | Zone3C(CA-SanFrancisco-CA) ASHRAE901-state_STD2019 | Zone4B(CA-Bishop-CA) ASHRAE901-state_STD2016 | Zone4B(CA-Bishop-CA) ASHRAE901-state_STD2019 | Zone5B(CA-Winnermucca-NV) ASHRAE901-state_STD2016 | Zone5B(CA-Winnermucca-NV) ASHRAE901-state_STD2019 | 2021-05-06
CA_PS_VAV_POD_1 Cooling Capacity [ton] | VAV_POD_1 Cooling Capacity [ton] | 22.9822 | 21.568 | 17.8363 | 17.4637 | 14.8796 | 14.5574 | 22.5807 | 21.1798 | 22.2793 | 20.8811 | 2021-05-06
CA_PS_VAV_POD_2 Cooling Capacity [ton] | VAV_POD_2 Cooling Capacity [ton] | 22.9533 | 21.4121 | 17.8235 | 17.4419 | 14.8767 | 14.5481 | 22.2949 | 20.8416 | 21.9519 | 20.5271 | 2021-05-06
CA_PS_VAV_POD_3 Cooling Capacity [ton] | VAV_POD_3 Cooling Capacity [ton] | 20.9649 | 19.5729 | 15.8225 | 15.142 | 13.1968 | 12.3976 | 20.6621 | 19.4612 | 20.4459 | 19.259 | 2021-05-06
CA_PS_VAV_OTHER Cooling Capacity [ton] | VAV_OTHER Cooling Capacity [ton] | 29.6342 | 26.4771 | 20.2433 | 18.2901 | 17.1605 | 15.6116 | 26.3875 | 23.8114 | 24.8986 | 22.5471 | 2021-05-06
CA_PS_PSZ-AC_1:6 Cooling Capacity [ton] | PSZ-AC_1:6 Cooling Capacity [ton] | 8.1547 | 7.8521 | 7.0259 | 6.7624 | 6.31 | 6.0547 | 8.2364 | 7.945 | 8.0404 | 7.755 | 2021-05-06
CA_PS_PSZ-AC_2:5 Cooling Capacity [ton] | PSZ-AC_2:5 Cooling Capacity [ton] | 6.1517 | 5.9435 | 4.3007 | 4.196 | 3.4215 | 3.4087 | 6.0467 | 6.0456 | 5.6767 | 5.6596 | 2021-05-06
CA_PS_PSZ-AC_2:7 Cooling Capacity [ton] | PSZ-AC_2:7 Cooling Capacity [ton] | 10.5074 | 10.5074 | 10.1265 | 10.1265 | 8.3303 | 8.3303 | 10.5074 | 10.5074 | 10.5074 | 10.5074 | 2021-05-06
CA_PS_VAV_POD_1 Supply Flow Rate [cfm] | VAV_POD_1 Supply Flow Rate [cfm] | 6886.36 | 6462.584 | 5360.7664 | 5233.6336 | 5297.2 | 5191.256 | 6780.416 | 6356.64 | 6695.6608 | 6271.8848 | 2021-05-06
CA_PS_VAV_POD_2 Supply Flow Rate [cfm] | VAV_POD_2 Supply Flow Rate [cfm] | 6886.36 | 6420.2064 | 5339.5776 | 5233.6336 | 5297.2 | 5191.256 | 6695.6608 | 6250.696 | 6589.7168 | 6165.9408 | 2021-05-06
CA_PS_VAV_POD_3 Supply Flow Rate [cfm] | VAV_POD_3 Supply Flow Rate [cfm] | 6293.0736 | 5869.2976 | 4746.2912 | 4597.9696 | 4703.9136 | 4555.592 | 6208.3184 | 5848.1088 | 6144.752 | 5784.5424 | 2021-05-06
CA_PS_VAV_OTHER Supply Flow Rate [cfm] | VAV_OTHER Supply Flow Rate [cfm] | 9386.6384 | 8814.5408 | 7013.4928 | 6526.1504 | 6822.7936 | 6314.2624 | 9471.3936 | 8920.4848 | 9429.016 | 8878.1072 | 2021-05-06
CA_PS_PSZ-AC_2:5 Supply Flow Rate [cfm] | PSZ-AC_2:5 Supply Flow Rate [cfm] | 1843.4256 | 1779.8592 | 1398.4608 | 1356.0832 | 1334.8944 | 1334.8944 | 1906.992 | 1906.992 | 1928.1808 | 1906.992 | 2021-05-06
CA_PS_PSZ-AC_1:6 Supply Flow Rate [cfm] | PSZ-AC_1:6 Supply Flow Rate [cfm] | 2796.9216 | 2669.7888 | 2436.712 | 2330.768 | 2415.5232 | 2288.3904 | 2924.0544 | 2796.9216 | 2945.2432 | 2818.1104 | 2021-05-06
CA_PS_PSZ-AC_2:7 Supply Flow Rate [cfm] | PSZ-AC_2:7 Supply Flow Rate [cfm] | 3157.1312 | 3157.1312 | 3157.1312 | 3157.1312 | 3157.1312 | 3157.1312 | 3157.1312 | 3157.1312 | 3157.1312 | 3157.1312 | 2021-05-06
CA_PS_Supply Air Temp. Reset Flag | Supply Air Temp. Reset Flag | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 2021-05-06
CA_PS_VAV_POD_1 OA Rate [cfm] | VAV_POD_1 OA Rate [cfm] | 6896.5942 | 6282.2673 | 5352.3756 | 5240.5623 | 5305.2306 | 5190.3449 | 6774.1441 | 6282.2673 | 6684.1553 | 6266.0791 | 2021-05-06
CA_PS_VAV_POD_2 OA Rate [cfm] | VAV_POD_2 OA Rate [cfm] | 6885.682 | 6282.2673 | 5348.5405 | 5234.0362 | 5304.2135 | 5187.0606 | 6689.9186 | 6254.2345 | 6584.6951 | 6159.8384 | 2021-05-06
CA_PS_VAV_POD_3 OA Rate [cfm] | VAV_POD_3 OA Rate [cfm] | 6288.2214 | 5422.002 | 4748.0711 | 4606.2756 | 4705.2485 | 4557.2235 | 6199.1648 | 5422.002 | 6135.4925 | 5422.002 | 2021-05-06
CA_PS_VAV_OTHER OA Rate [cfm] | VAV_OTHER OA Rate [cfm] | 3736.1787 | 2988.8921 | 3736.1787 | 2988.8921 | 3736.1787 | 2988.8921 | 3736.1787 | 2988.8921 | 3736.1787 | 2988.8921 | 2021-05-06
CA_PS_PSZ-AC_2:5 OA Rate [cfm] | PSZ-AC_2:5 OA Rate [cfm] | 1152.7343 | 1152.7343 | 1152.7343 | 1152.7343 | 1152.7343 | 1152.7343 | 1152.7343 | 1152.7343 | 1152.7343 | 1152.7343 | 2021-05-06
CA_PS_PSZ-AC_1:6 OA Rate [cfm] | PSZ-AC_1:6 OA Rate [cfm] | 539.9118 | 539.9118 | 539.9118 | 539.9118 | 539.9118 | 539.9118 | 539.9118 | 539.9118 | 539.9118 | 539.9118 | 2021-05-06
CA_PS_PSZ-AC_2:7 OA Rate [cfm] | PSZ-AC_2:7 OA Rate [cfm] | 3153.0841 | 3153.0841 | 3153.0841 | 3153.0841 | 3153.0841 | 3153.0841 | 3153.0841 | 3153.0841 | 3153.0841 | 3153.0841 | 2021-05-06
CA_PS_VAV_POD_1 OA Damper [gravity, motorized] | VAV_POD_1 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | motorized | motorized | motorized | motorized | motorized | motorized | 2021-05-06
CA_PS_VAV_POD_2 OA Damper [gravity, motorized] | VAV_POD_2 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | motorized | motorized | motorized | motorized | motorized | motorized | 2021-05-06
CA_PS_VAV_POD_3 OA Damper [gravity, motorized] | VAV_POD_3 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | motorized | motorized | motorized | motorized | motorized | motorized | 2021-05-06
CA_PS_VAV_OTHER OA Damper [gravity, motorized] | VAV_OTHER OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | motorized | motorized | motorized | motorized | motorized | motorized | 2021-05-06
CA_PS_PSZ-AC_2:5 OA Damper [gravity, motorized] | PSZ-AC_2:5 OA Damper [gravity, motorized] | motorized | motorized | gravity | gravity | gravity | gravity | motorized | motorized | motorized | motorized | 2021-05-06
CA_PS_PSZ-AC_1:6 OA Damper [gravity, motorized] | PSZ-AC_1:6 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | motorized | motorized | motorized | motorized | motorized | motorized | 2021-05-06
CA_PS_PSZ-AC_2:7 OA Damper [gravity, motorized] | PSZ-AC_2:7 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | motorized | motorized | motorized | motorized | motorized | motorized | 2021-05-06
CA_PS_VAV_POD_1 (economizer) | VAV_POD_1 (economizer) | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | 2021-05-06
CA_PS_VAV_POD_2 (economizer) | VAV_POD_2 (economizer) | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | 2021-05-06
CA_PS_VAV_POD_3 (economizer) | VAV_POD_3 (economizer) | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | 2021-05-06
CA_PS_VAV_OTHER (economizer) | VAV_OTHER (economizer) | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | 2021-05-06
CA_PS_PSZ-AC_2:5 (economizer) | PSZ-AC_2:5 (economizer) | DifferentialDryBulb | DifferentialDryBulb | No | No | No | No | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | 2021-05-06
CA_PS_PSZ-AC_1:6 (economizer) | PSZ-AC_1:6 (economizer) | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | 2021-05-06
CA_PS_PSZ-AC_2:7 (economizer) | PSZ-AC_2:7 (economizer) | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | 2021-05-06
CA_PS_VAV_Pod_1_ERV Flag | VAV_Pod_1_ERV Flag | Yes | Yes | No | No | No | No | No | No | No | No | 2021-05-06
CA_PS_VAV_Pod_2_ERV Flag | VAV_Pod_2_ERV Flag | Yes | Yes | No | No | No | No | No | No | No | No | 2021-05-06
CA_PS_VAV_Pod_3_ERV Flag | VAV_Pod_3_ERV Flag | Yes | Yes | No | No | No | No | No | No | No | No | 2021-05-06
CA_PS_VAV_OTHER_ERV Flag | VAV_OTHER_ERV Flag | No | No | No | No | No | No | No | No | No | No | 2021-05-06
CA_PS_PSZ_AC_2_5_ERV Flag | PSZ_AC_2_5_ERV Flag | No | No | No | No | No | No | No | No | No | No | 2021-05-06
CA_PS_PSZ_AC_2_7_ERV Flag | PSZ_AC_2_7_ERV Flag | No | No | No | No | No | No | No | No | No | No | 2021-05-06
CA_PS_HEATSYS1 Capacity [MMBTU/h] | HEATSYS1 Capacity [MMBTU/h] | 0.78384 | 0.70545 | 0.55008 | 0.51858 | 0.63476 | 0.59665 | 0.93916 | 0.8696 | 1.0958 | 1.0228 | 2021-05-06
CA_PS_HEATSYS1 Flow Rate [gal/min] | HEATSYS1 Flow Rate [gal/min] | 80.4466 | 72.4019 | 56.4558 | 53.2232 | 65.1464 | 61.2355 | 96.3874 | 89.2479 | 112.4603 | 104.974 | 2021-05-06
CA_PS_VAV_POD_1 Fan Power [hp] | VAV_POD_1 Fan Power [hp] | 10.0975 | 9.5484 | 7.8964 | 7.7314 | 7.8268 | 7.6573 | 9.921 | 9.3766 | 9.8633 | 9.2443 | 2021-05-06
CA_PS_VAV_POD_2 Fan Power [hp] | VAV_POD_2 Fan Power [hp] | 10.0848 | 9.4794 | 7.8907 | 7.7218 | 7.8253 | 7.6525 | 9.8703 | 9.2269 | 9.7184 | 9.0876 | 2021-05-06
CA_PS_VAV_POD_3 Fan Power [hp] | VAV_POD_3 Fan Power [hp] | 9.2814 | 8.6652 | 7.0048 | 4.9912 | 6.9417 | 4.938 | 9.1474 | 8.6157 | 9.0517 | 8.5262 | 2021-05-06
CA_PS_VAV_OTHER Fan Power [hp] | VAV_OTHER Fan Power [hp] | 13.0126 | 12.2037 | 10.2678 | 9.6226 | 9.9827 | 9.328 | 13.8641 | 13.0574 | 13.7938 | 12.9837 | 2021-05-06
CA_PS_HEATSYS1 Pump Power [hp] | HEATSYS1 Pump Power [hp] | 1.7389 | 1.5495 | 1.2203 | 1.1391 | 1.4082 | 1.3105 | 2.0835 | 1.91 | 2.4309 | 2.2466 | 2021-05-06
CA_PS_PSZ-AC_1:6 Heating Capacity [kBtu/hr] | PSZ-AC_1:6 Heating Capacity [kBtu/hr] | 198.5262 | 189.6163 | 181.9993 | 173.3734 | 183.7796 | 175.1036 | 205.3164 | 196.8777 | 211.3057 | 202.8779 | 2021-05-06
CA_PS_PSZ-AC_2:5 Heating Capacity [kBtu/hr] | PSZ-AC_2:5 Heating Capacity [kBtu/hr] | 105.6842 | 103.5763 | 82.8574 | 81.2585 | 88.2399 | 88.0046 | 119.7099 | 119.8827 | 132.5886 | 132.3161 | 2021-05-06
CA_PS_PSZ-AC_2:7 Heating Capacity [kBtu/hr] | PSZ-AC_2:7 Heating Capacity [kBtu/hr] | 225.0936 | 225.0936 | 202.6668 | 202.6668 | 222.385 | 222.385 | 262.2368 | 262.2368 | 296.0123 | 296.0123 | 2021-05-06
CA_PS_ZN_VAV_BOXes_Max_Reheat_Water_Flow_GPM | ZN_VAV_BOXes_Max_Reheat_Water_Flow_GPM | 59.5006 | 52.7982 | 48.5324 | 45.6025 | 53.1971 | 49.7589 | 62.6932 | 57.5982 | 69.3163 | 64.4587 | 2021-05-06
id | item | Zone2B(CA-Tucson-AZ) ASHRAE901-state_STD2016 | Zone2B(CA-Tucson-AZ) ASHRAE901-state_STD2019 | Zone3B(CA-LosAngeles-CA) ASHRAE901-state_STD2016 | Zone3B(CA-LosAngeles-CA) ASHRAE901-state_STD2019 | Zone3C(CA-SanFrancisco-CA) ASHRAE901-state_STD2016 | Zone3C(CA-SanFrancisco-CA) ASHRAE901-state_STD2019 | Zone4B(CA-Bishop-CA) ASHRAE901-state_STD2016 | Zone4B(CA-Bishop-CA) ASHRAE901-state_STD2019 | Zone5B(CA-Winnermucca-NV) ASHRAE901-state_STD2016 | Zone5B(CA-Winnermucca-NV) ASHRAE901-state_STD2019 | 2021-05-06
CA_SH_SAC_FRONTOFFICE Cooling Capacity [ton] | SAC_FRONTOFFICE Cooling Capacity [ton] | 2.5754 | 2.4267 | 1.8469 | 1.7292 | 1.8046 | 1.6902 | 2.2651 | 2.1388 | 2.1448 | 2.0242 | 2021-05-06
CA_SH_SAC_FRONTLOUNGE Cooling Capacity [ton] | SAC_FRONTLOUNGE Cooling Capacity [ton] | 6.5112 | 6.2425 | 4.3991 | 4.4479 | 4.4632 | 4.2133 | 5.9139 | 5.6396 | 5.633 | 5.394 | 2021-05-06
CA_SH_SAC_MEETINGROOM Cooling Capacity [ton] | SAC_MEETINGROOM Cooling Capacity [ton] | 3.3333 | 3.2518 | 2.4491 | 2.3922 | 2.3677 | 2.2847 | 3.0651 | 3.0017 | 2.9415 | 2.8727 | 2021-05-06
CA_SH_SAC_EXC_EMPLGE_RESTRM Cooling Capacity [ton] | SAC_EXC_EMPLGE_RESTRM Cooling Capacity [ton] | 6.3365 | 6.2958 | 5.0361 | 4.9986 | 4.9014 | 4.8623 | 6.1073 | 6.0607 | 5.9215 | 5.8763 | 2021-05-06
CA_SH_SAC_FO_ADDAQ SUPPLY FAN Supply Flow Rate [cfm] | SAC_FO_ADDAQ SUPPLY FAN Supply Flow Rate [cfm] | 953.496 | 889.9296 | 762.7968 | 720.4192 | 762.7968 | 720.4192 | 911.1184 | 847.552 | 889.9296 | 826.3632 | 2021-05-06
CA_SH_SAC_FL_ADDAQ SUPPLY FAN Supply Flow Rate [cfm] | SAC_FL_ADDAQ SUPPLY FAN Supply Flow Rate [cfm] | 2161.2576 | 2055.3136 | 1737.4816 | 1652.7264 | 1737.4816 | 1610.3488 | 2140.0688 | 2034.1248 | 2118.88 | 2012.936 | 2021-05-06
CA_SH_SAC_MR_ADDAQ SUPPLY FAN Supply Flow Rate [cfm] | SAC_MR_ADDAQ SUPPLY FAN Supply Flow Rate [cfm] | 1017.0624 | 974.6848 | 847.552 | 826.3632 | 847.552 | 805.1744 | 1017.0624 | 974.6848 | 995.8736 | 974.6848 | 2021-05-06
CA_SH_SAC_EXC_ADDAQ SUPPLY FAN Supply Flow Rate [cfm] | SAC_EXC_ADDAQ SUPPLY FAN Supply Flow Rate [cfm] | 2415.5232 | 2394.3344 | 2118.88 | 2118.88 | 2097.6912 | 2076.5024 | 2542.656 | 2521.4672 | 2542.656 | 2521.4672 | 2021-05-06
CA_SH_SAC_Exc_EmpLge_RestRm OA Rate [cfm] | SAC_Exc_EmpLge_RestRm OA Rate [cfm] | 199.9928 | 199.9928 | 199.9928 | 199.9928 | 199.9928 | 199.9928 | 199.9928 | 199.9928 | 199.9928 | 199.9928 | 2021-05-06
CA_SH_SAC_FrontLounge OA Rate [cfm] | SAC_FrontLounge OA Rate [cfm] | 500.0133 | 500.0133 | 500.0133 | 500.0133 | 500.0133 | 500.0133 | 500.0133 | 500.0133 | 500.0133 | 500.0133 | 2021-05-06
CA_SH_SAC_FrontOffice OA Rate [cfm] | SAC_FrontOffice OA Rate [cfm] | 119.2938 | 119.2938 | 119.2938 | 119.2938 | 119.2938 | 119.2938 | 119.2938 | 119.2938 | 119.2938 | 119.2938 | 2021-05-06
CA_SH_SAC_MeetingRoom OA Rate [cfm] | SAC_MeetingRoom OA Rate [cfm] | 267.7629 | 267.7629 | 267.7629 | 267.7629 | 267.7629 | 267.7629 | 267.7629 | 267.7629 | 267.7629 | 267.7629 | 2021-05-06
CA_SH_SAC_FrontLounge OA Damper [gravity, motorized] | SAC_FrontLounge OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | motorized | motorized | motorized | motorized | motorized | motorized | 2021-05-06
CA_SH_SAC_FrontOffice (economizer) | SAC_FrontOffice (economizer) | No | No | No | No | No | No | No | No | No | No | 2021-05-06
CA_SH_SAC_FrontLounge (economizer) | SAC_FrontLounge (economizer) | DifferentialDryBulb | DifferentialDryBulb | No | No | No | No | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | 2021-05-06
CA_SH_SAC_MeetingRoom (economizer) | SAC_MeetingRoom (economizer) | No | No | No | No | No | No | No | No | No | No | 2021-05-06
CA_SH_SAC_Exc_EmpLge_RestRm (economizer) | SAC_Exc_EmpLge_RestRm (economizer) | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | 2021-05-06
CA_SH_SAC_FRONTOFFICE Heating Capacity [kBtu/hr] | SAC_FRONTOFFICE Heating Capacity [kBtu/hr] | 36.6163 | 34.5073 | 31.3605 | 29.3575 | 32.316 | 30.3563 | 34.9546 | 33.1412 | 35.3275 | 33.5503 | 2021-05-06
CA_SH_SAC_FRONTLOUNGE Heating Capacity [kBtu/hr] | SAC_FRONTLOUNGE Heating Capacity [kBtu/hr] | 91.1726 | 87.5451 | 77.6824 | 74.1908 | 80.4645 | 76.4334 | 93.6894 | 90.3104 | 97.5263 | 94.1818 | 2021-05-06
CA_SH_SAC_MEETINGROOM Heating Capacity [kBtu/hr] | SAC_MEETINGROOM Heating Capacity [kBtu/hr] | 43.9252 | 42.8886 | 38.346 | 37.4843 | 40.1762 | 38.9099 | 45.7285 | 44.9091 | 48.1269 | 47.2274 | 2021-05-06
CA_SH_SAC_EXC_EMPLGE_RESTRM Heating Capacity [kBtu/hr] | SAC_EXC_EMPLGE_RESTRM Heating Capacity [kBtu/hr] | 88.5318 | 87.9533 | 83.5388 | 82.8974 | 84.1725 | 83.5009 | 90.7251 | 90.0576 | 92.486 | 91.8232 | 2021-05-06
id | item | Zone2B(CA-Tucson-AZ) ASHRAE901-state_STD2016 | Zone2B(CA-Tucson-AZ) ASHRAE901-state_STD2019 | Zone3B(CA-LosAngeles-CA) ASHRAE901-state_STD2016 | Zone3B(CA-LosAngeles-CA) ASHRAE901-state_STD2019 | Zone3C(CA-SanFrancisco-CA) ASHRAE901-state_STD2016 | Zone3C(CA-SanFrancisco-CA) ASHRAE901-state_STD2019 | Zone4B(CA-Bishop-CA) ASHRAE901-state_STD2016 | Zone4B(CA-Bishop-CA) ASHRAE901-state_STD2019 | Zone5B(CA-Winnermucca-NV) ASHRAE901-state_STD2016 | Zone5B(CA-Winnermucca-NV) ASHRAE901-state_STD2019 | 2021-05-06
CA_MA_SPLIT GSW COOLING COIL Cooling Capacity [ton] | SPLIT GSW COOLING COIL Cooling Capacity [ton] | 0.94627 | 0.93186 | 0.59333 | 0.58532 | 0.5924 | 0.58501 | 0.82511 | 0.80799 | 0.79266 | 0.77454 | 2021-05-06
CA_MA_SPLIT GNW COOLING COIL Cooling Capacity [ton] | SPLIT GNW COOLING COIL Cooling Capacity [ton] | 0.93507 | 0.92016 | 0.54089 | 0.53315 | 0.52067 | 0.5135 | 0.79559 | 0.77893 | 0.74923 | 0.73186 | 2021-05-06
CA_MA_SPLIT OFFICE COOLING COIL Cooling Capacity [ton] | SPLIT OFFICE COOLING COIL Cooling Capacity [ton] | 1.7792 | 1.713 | 1.5159 | 1.3753 | 1.4071 | 1.2696 | 1.7624 | 1.5812 | 1.7292 | 1.5436 | 2021-05-06
CA_MA_SPLIT GNE COOLING COIL Cooling Capacity [ton] | SPLIT GNE COOLING COIL Cooling Capacity [ton] | 0.82697 | 0.81375 | 0.45298 | 0.44546 | 0.41256 | 0.40628 | 0.66915 | 0.65476 | 0.61655 | 0.60173 | 2021-05-06
CA_MA_SPLIT GN1 COOLING COIL Cooling Capacity [ton] | SPLIT GN1 COOLING COIL Cooling Capacity [ton] | 0.68937 | 0.67316 | 0.39489 | 0.38811 | 0.36498 | 0.35864 | 0.5526 | 0.54101 | 0.51188 | 0.50005 | 2021-05-06
CA_MA_SPLIT GN2 COOLING COIL Cooling Capacity [ton] | SPLIT GN2 COOLING COIL Cooling Capacity [ton] | 0.68769 | 0.67151 | 0.39327 | 0.38653 | 0.36315 | 0.35682 | 0.55001 | 0.53848 | 0.50918 | 0.49743 | 2021-05-06
CA_MA_SPLIT GS1 COOLING COIL Cooling Capacity [ton] | SPLIT GS1 COOLING COIL Cooling Capacity [ton] | 0.703 | 0.68698 | 0.44374 | 0.43646 | 0.43637 | 0.42908 | 0.58248 | 0.57017 | 0.55525 | 0.54235 | 2021-05-06
CA_MA_SPLIT GS2 COOLING COIL Cooling Capacity [ton] | SPLIT GS2 COOLING COIL Cooling Capacity [ton] | 0.73446 | 0.72074 | 0.48036 | 0.46826 | 0.47717 | 0.46364 | 0.62576 | 0.60765 | 0.59795 | 0.57913 | 2021-05-06
CA_MA_SPLIT MSW COOLING COIL Cooling Capacity [ton] | SPLIT MSW COOLING COIL Cooling Capacity [ton] | 2.107 | 2.0753 | 1.4018 | 1.3858 | 1.4518 | 1.4371 | 2.0153 | 1.977 | 2.0338 | 1.993 | 2021-05-06
CA_MA_SPLIT MNW COOLING COIL Cooling Capacity [ton] | SPLIT MNW COOLING COIL Cooling Capacity [ton] | 2.0816 | 2.0496 | 1.2857 | 1.2705 | 1.2944 | 1.2806 | 1.9495 | 1.9124 | 1.9413 | 1.9022 | 2021-05-06
CA_MA_SPLIT MSE COOLING COIL Cooling Capacity [ton] | SPLIT MSE COOLING COIL Cooling Capacity [ton] | 1.959 | 1.7924 | 1.2238 | 1.2073 | 1.2665 | 1.2504 | 1.6899 | 1.6616 | 1.6286 | 1.5959 | 2021-05-06
CA_MA_SPLIT MNE COOLING COIL Cooling Capacity [ton] | SPLIT MNE COOLING COIL Cooling Capacity [ton] | 1.8065 | 1.7776 | 1.0728 | 1.059 | 1.0145 | 1.0023 | 1.5433 | 1.516 | 1.4927 | 1.4648 | 2021-05-06
CA_MA_SPLIT MN1 COOLING COIL Cooling Capacity [ton] | SPLIT MN1 COOLING COIL Cooling Capacity [ton] | 1.4152 | 1.3922 | 0.86259 | 0.84966 | 0.83172 | 0.81957 | 1.2263 | 1.2041 | 1.1882 | 1.1657 | 2021-05-06
CA_MA_SPLIT MN2 COOLING COIL Cooling Capacity [ton] | SPLIT MN2 COOLING COIL Cooling Capacity [ton] | 1.411 | 1.388 | 0.85821 | 0.84535 | 0.82682 | 0.81469 | 1.2195 | 1.1974 | 1.1805 | 1.1582 | 2021-05-06
CA_MA_SPLIT MS1 COOLING COIL Cooling Capacity [ton] | SPLIT MS1 COOLING COIL Cooling Capacity [ton] | 1.4681 | 1.4452 | 0.97414 | 0.9594 | 1.0178 | 1.0016 | 1.2772 | 1.2544 | 1.2649 | 1.2411 | 2021-05-06
CA_MA_SPLIT MS2 COOLING COIL Cooling Capacity [ton] | SPLIT MS2 COOLING COIL Cooling Capacity [ton] | 1.4641 | 1.4413 | 0.97755 | 0.96281 | 1.0219 | 1.0057 | 1.2704 | 1.2477 | 1.2574 | 1.2338 | 2021-05-06
CA_MA_SPLIT TSW COOLING COIL Cooling Capacity [ton] | SPLIT TSW COOLING COIL Cooling Capacity [ton] | 1.3497 | 1.3329 | 0.8564 | 0.84841 | 0.86934 | 0.86185 | 1.3346 | 1.3135 | 1.3366 | 1.3143 | 2021-05-06
CA_MA_SPLIT TNW COOLING COIL Cooling Capacity [ton] | SPLIT TNW COOLING COIL Cooling Capacity [ton] | 1.3257 | 1.3088 | 0.78893 | 0.78116 | 0.78228 | 0.77522 | 1.2885 | 1.2679 | 1.2768 | 1.2553 | 2021-05-06
CA_MA_SPLIT TSE COOLING COIL Cooling Capacity [ton] | SPLIT TSE COOLING COIL Cooling Capacity [ton] | 1.2668 | 1.2505 | 0.77705 | 0.76878 | 0.79323 | 0.78496 | 1.1319 | 1.117 | 1.1173 | 1.0999 | 2021-05-06
CA_MA_SPLIT TNE COOLING COIL Cooling Capacity [ton] | SPLIT TNE COOLING COIL Cooling Capacity [ton] | 1.229 | 1.2123 | 0.64451 | 0.63769 | 0.61191 | 0.6054 | 1.0621 | 1.0482 | 1.0211 | 1.0054 | 2021-05-06
CA_MA_SPLIT TN1 COOLING COIL Cooling Capacity [ton] | SPLIT TN1 COOLING COIL Cooling Capacity [ton] | 0.93477 | 0.92281 | 0.52174 | 0.51548 | 0.49708 | 0.49094 | 0.85303 | 0.84216 | 0.80864 | 0.79637 | 2021-05-06
CA_MA_SPLIT TN2 COOLING COIL Cooling Capacity [ton] | SPLIT TN2 COOLING COIL Cooling Capacity [ton] | 0.92995 | 0.91803 | 0.52291 | 0.51668 | 0.49392 | 0.48728 | 0.85576 | 0.84493 | 0.80749 | 0.7953 | 2021-05-06
CA_MA_SPLIT TS1 COOLING COIL Cooling Capacity [ton] | SPLIT TS1 COOLING COIL Cooling Capacity [ton] | 1.02 | 1.0071 | 0.64659 | 0.63827 | 0.66384 | 0.65537 | 0.92509 | 0.91305 | 0.90191 | 0.88804 | 2021-05-06
CA_MA_SPLIT TS2 COOLING COIL Cooling Capacity [ton] | SPLIT TS2 COOLING COIL Cooling Capacity [ton] | 1.0232 | 1.0103 | 0.64951 | 0.6412 | 0.66702 | 0.65856 | 0.9289 | 0.91689 | 0.90179 | 0.88795 | 2021-05-06
CA_MA_Split GN1 Furnace with DX Cooling OA Rate [cfm] | Split GN1 Furnace with DX Cooling OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 2021-05-06
CA_MA_Split GN2 Furnace with DX Cooling OA Rate [cfm] | Split GN2 Furnace with DX Cooling OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 2021-05-06
CA_MA_Split GNE Furnace with DX Cooling OA Rate [cfm] | Split GNE Furnace with DX Cooling OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 2021-05-06
CA_MA_Split GNW Furnace with DX Cooling OA Rate [cfm] | Split GNW Furnace with DX Cooling OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 2021-05-06
CA_MA_Split GS1 Furnace with DX Cooling OA Rate [cfm] | Split GS1 Furnace with DX Cooling OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 2021-05-06
CA_MA_Split GS2 Furnace with DX Cooling OA Rate [cfm] | Split GS2 Furnace with DX Cooling OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 2021-05-06
CA_MA_Split GSW Furnace with DX Cooling OA Rate [cfm] | Split GSW Furnace with DX Cooling OA Rate [cfm] | 56.9945 | 56.9945 | 56.9945 | 56.9945 | 56.9945 | 56.9945 | 56.9945 | 56.9945 | 56.9945 | 56.9945 | 2021-05-06
CA_MA_Split MN1 Furnace with DX Cooling OA Rate [cfm] | Split MN1 Furnace with DX Cooling OA Rate [cfm] | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 2021-05-06
CA_MA_Split MN2 Furnace with DX Cooling OA Rate [cfm] | Split MN2 Furnace with DX Cooling OA Rate [cfm] | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 2021-05-06
CA_MA_Split MNE Furnace with DX Cooling OA Rate [cfm] | Split MNE Furnace with DX Cooling OA Rate [cfm] | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 2021-05-06
CA_MA_Split MNW Furnace with DX Cooling OA Rate [cfm] | Split MNW Furnace with DX Cooling OA Rate [cfm] | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 2021-05-06
CA_MA_Split MS1 Furnace with DX Cooling OA Rate [cfm] | Split MS1 Furnace with DX Cooling OA Rate [cfm] | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 2021-05-06
CA_MA_Split MS2 Furnace with DX Cooling OA Rate [cfm] | Split MS2 Furnace with DX Cooling OA Rate [cfm] | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 2021-05-06
CA_MA_Split MSE Furnace with DX Cooling OA Rate [cfm] | Split MSE Furnace with DX Cooling OA Rate [cfm] | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 2021-05-06
CA_MA_Split MSW Furnace with DX Cooling OA Rate [cfm] | Split MSW Furnace with DX Cooling OA Rate [cfm] | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 2021-05-06
CA_MA_Split Office Furnace with DX Cooling OA Rate [cfm] | Split Office Furnace with DX Cooling OA Rate [cfm] | 80.7372 | 80.7372 | 80.7372 | 80.7372 | 80.7372 | 80.7372 | 80.7372 | 80.7372 | 80.7372 | 80.7372 | 2021-05-06
CA_MA_Split TN1 Furnace with DX Cooling OA Rate [cfm] | Split TN1 Furnace with DX Cooling OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 2021-05-06
CA_MA_Split TN2 Furnace with DX Cooling OA Rate [cfm] | Split TN2 Furnace with DX Cooling OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 2021-05-06
CA_MA_Split TNE Furnace with DX Cooling OA Rate [cfm] | Split TNE Furnace with DX Cooling OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 2021-05-06
CA_MA_Split TNW Furnace with DX Cooling OA Rate [cfm] | Split TNW Furnace with DX Cooling OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 2021-05-06
CA_MA_Split TS1 Furnace with DX Cooling OA Rate [cfm] | Split TS1 Furnace with DX Cooling OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 2021-05-06
CA_MA_Split TS2 Furnace with DX Cooling OA Rate [cfm] | Split TS2 Furnace with DX Cooling OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 2021-05-06
CA_MA_Split TSE Furnace with DX Cooling OA Rate [cfm] | Split TSE Furnace with DX Cooling OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 2021-05-06
CA_MA_Split TSW Furnace with DX Cooling OA Rate [cfm] | Split TSW Furnace with DX Cooling OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 2021-05-06
CA_MA_SPLIT GSW HEATING COIL Heating Capacity [kBtu/hr] | SPLIT GSW HEATING COIL Heating Capacity [kBtu/hr] | 4.1679 | 4.0792 | 3.6633 | 3.6633 | 4.0198 | 4.0198 | 6.3936 | 6.4516 | 8.1847 | 8.2446 | 2021-05-06
CA_MA_SPLIT GNW HEATING COIL Heating Capacity [kBtu/hr] | SPLIT GNW HEATING COIL Heating Capacity [kBtu/hr] | 4.0837 | 3.9991 | 3.5346 | 3.5346 | 3.8785 | 3.8785 | 6.333 | 6.393 | 8.0651 | 8.1252 | 2021-05-06
CA_MA_SPLIT OFFICE HEATING COIL Heating Capacity [kBtu/hr] | SPLIT OFFICE HEATING COIL Heating Capacity [kBtu/hr] | 12.5315 | 12.3617 | 9.1975 | 8.6043 | 11.6849 | 11.6307 | 17.0006 | 17.137 | 20.234 | 20.3519 | 2021-05-06
CA_MA_SPLIT GNE HEATING COIL Heating Capacity [kBtu/hr] | SPLIT GNE HEATING COIL Heating Capacity [kBtu/hr] | 4.0973 | 4.0102 | 3.5346 | 3.5346 | 3.8785 | 3.8785 | 6.3201 | 6.3802 | 8.083 | 8.1431 | 2021-05-06
CA_MA_SPLIT GN1 HEATING COIL Heating Capacity [kBtu/hr] | SPLIT GN1 HEATING COIL Heating Capacity [kBtu/hr] | 3.9257 | 3.9257 | 3.5346 | 3.5346 | 3.8785 | 3.8785 | 4.5735 | 4.5933 | 5.9396 | 5.9998 | 2021-05-06
CA_MA_SPLIT GN2 HEATING COIL Heating Capacity [kBtu/hr] | SPLIT GN2 HEATING COIL Heating Capacity [kBtu/hr] | 3.9257 | 3.9257 | 3.5346 | 3.5346 | 3.8785 | 3.8785 | 4.5735 | 4.5928 | 5.9401 | 6.0004 | 2021-05-06
CA_MA_SPLIT GS1 HEATING COIL Heating Capacity [kBtu/hr] | SPLIT GS1 HEATING COIL Heating Capacity [kBtu/hr] | 3.9257 | 3.9257 | 3.5346 | 3.5346 | 3.8785 | 3.8785 | 4.5735 | 4.5735 | 5.9506 | 6.0106 | 2021-05-06
CA_MA_SPLIT GS2 HEATING COIL Heating Capacity [kBtu/hr] | SPLIT GS2 HEATING COIL Heating Capacity [kBtu/hr] | 3.9257 | 3.9257 | 3.5346 | 3.5346 | 3.8785 | 3.8785 | 4.9513 | 5.0132 | 6.4344 | 6.4971 | 2021-05-06
CA_MA_SPLIT MSW HEATING COIL Heating Capacity [kBtu/hr] | SPLIT MSW HEATING COIL Heating Capacity [kBtu/hr] | 8.2187 | 8.0401 | 7.0692 | 7.0692 | 7.757 | 7.757 | 11.7888 | 11.9194 | 14.344 | 14.4735 | 2021-05-06
CA_MA_SPLIT MNW HEATING COIL Heating Capacity [kBtu/hr] | SPLIT MNW HEATING COIL Heating Capacity [kBtu/hr] | 8.1729 | 8.0027 | 7.0692 | 7.0692 | 7.757 | 7.757 | 11.845 | 11.9753 | 14.2908 | 14.4197 | 2021-05-06
CA_MA_SPLIT MSE HEATING COIL Heating Capacity [kBtu/hr] | SPLIT MSE HEATING COIL Heating Capacity [kBtu/hr] | 8.2521 | 8.0674 | 7.0692 | 7.0692 | 7.757 | 7.757 | 11.758 | 11.8886 | 14.3866 | 14.5162 | 2021-05-06
CA_MA_SPLIT MNE HEATING COIL Heating Capacity [kBtu/hr] | SPLIT MNE HEATING COIL Heating Capacity [kBtu/hr] | 8.2063 | 8.03 | 7.0692 | 7.0692 | 7.757 | 7.757 | 11.8142 | 11.9444 | 14.3335 | 14.4625 | 2021-05-06
CA_MA_SPLIT MN1 HEATING COIL Heating Capacity [kBtu/hr] | SPLIT MN1 HEATING COIL Heating Capacity [kBtu/hr] | 7.8514 | 7.8514 | 7.0692 | 7.0692 | 7.757 | 7.757 | 9.147 | 9.147 | 10.3252 | 10.3252 | 2021-05-06
CA_MA_SPLIT MN2 HEATING COIL Heating Capacity [kBtu/hr] | SPLIT MN2 HEATING COIL Heating Capacity [kBtu/hr] | 7.8514 | 7.8514 | 7.0692 | 7.0692 | 7.757 | 7.757 | 9.147 | 9.147 | 10.3252 | 10.3252 | 2021-05-06
CA_MA_SPLIT MS1 HEATING COIL Heating Capacity [kBtu/hr] | SPLIT MS1 HEATING COIL Heating Capacity [kBtu/hr] | 7.8514 | 7.8514 | 7.0692 | 7.0692 | 7.757 | 7.757 | 9.147 | 9.147 | 10.3252 | 10.3252 | 2021-05-06
CA_MA_SPLIT MS2 HEATING COIL Heating Capacity [kBtu/hr] | SPLIT MS2 HEATING COIL Heating Capacity [kBtu/hr] | 7.8514 | 7.8514 | 7.0692 | 7.0692 | 7.757 | 7.757 | 9.147 | 9.147 | 10.3252 | 10.3252 | 2021-05-06
CA_MA_SPLIT TSW HEATING COIL Heating Capacity [kBtu/hr] | SPLIT TSW HEATING COIL Heating Capacity [kBtu/hr] | 6.6544 | 6.5713 | 3.9057 | 3.8884 | 5.0886 | 5.0565 | 8.7447 | 8.8063 | 10.5099 | 10.5718 | 2021-05-06
CA_MA_SPLIT TNW HEATING COIL Heating Capacity [kBtu/hr] | SPLIT TNW HEATING COIL Heating Capacity [kBtu/hr] | 6.6364 | 6.5589 | 3.9136 | 3.8966 | 5.086 | 5.0571 | 8.7801 | 8.8418 | 10.4877 | 10.5497 | 2021-05-06
CA_MA_SPLIT TSE HEATING COIL Heating Capacity [kBtu/hr] | SPLIT TSE HEATING COIL Heating Capacity [kBtu/hr] | 6.6719 | 6.5855 | 3.9089 | 3.89 | 5.096 | 5.062 | 8.7284 | 8.7899 | 10.5328 | 10.5947 | 2021-05-06
CA_MA_SPLIT TNE HEATING COIL Heating Capacity [kBtu/hr] | SPLIT TNE HEATING COIL Heating Capacity [kBtu/hr] | 6.654 | 6.5731 | 3.9168 | 3.8983 | 5.0934 | 5.0626 | 8.7638 | 8.8254 | 10.5106 | 10.5726 | 2021-05-06
CA_MA_SPLIT TN1 HEATING COIL Heating Capacity [kBtu/hr] | SPLIT TN1 HEATING COIL Heating Capacity [kBtu/hr] | 4.9904 | 4.9609 | 3.5346 | 3.5346 | 3.8785 | 3.8785 | 6.7165 | 6.778 | 8.1978 | 8.2598 | 2021-05-06
CA_MA_SPLIT TN2 HEATING COIL Heating Capacity [kBtu/hr] | SPLIT TN2 HEATING COIL Heating Capacity [kBtu/hr] | 4.991 | 4.9613 | 3.5346 | 3.5346 | 3.8785 | 3.8785 | 6.7159 | 6.7775 | 8.1985 | 8.2605 | 2021-05-06
CA_MA_SPLIT TS1 HEATING COIL Heating Capacity [kBtu/hr] | SPLIT TS1 HEATING COIL Heating Capacity [kBtu/hr] | 5.0023 | 4.967 | 3.5346 | 3.5346 | 3.8785 | 3.8785 | 6.6738 | 6.7353 | 8.2141 | 8.2759 | 2021-05-06
CA_MA_SPLIT TS2 HEATING COIL Heating Capacity [kBtu/hr] | SPLIT TS2 HEATING COIL Heating Capacity [kBtu/hr] | 5.0028 | 4.9674 | 3.5346 | 3.5346 | 3.8785 | 3.8785 | 6.6733 | 6.7348 | 8.2148 | 8.2766 | 2021-05-06
CA_MA_Split_GSW ERV Flag | Split_GSW ERV Flag | No | Yes | No | Yes | No | No | No | Yes | No | Yes | 2021-05-06
CA_MA_Split_GNW ERV Flag | Split_GNW ERV Flag | No | Yes | No | Yes | No | No | No | Yes | No | Yes | 2021-05-06
CA_MA_Split_GNE ERV Flag | Split_GNE ERV Flag | No | Yes | No | Yes | No | No | No | Yes | No | Yes | 2021-05-06
CA_MA_Split_GN1 ERV Flag | Split_GN1 ERV Flag | No | Yes | No | Yes | No | No | No | Yes | No | Yes | 2021-05-06
CA_MA_Split_GN2 ERV Flag | Split_GN2 ERV Flag | No | Yes | No | Yes | No | No | No | Yes | No | Yes | 2021-05-06
CA_MA_Split_GS1 ERV Flag | Split_GS1 ERV Flag | No | Yes | No | Yes | No | No | No | Yes | No | Yes | 2021-05-06
CA_MA_Split_GS2 ERV Flag | Split_GS2 ERV Flag | No | Yes | No | Yes | No | No | No | Yes | No | Yes | 2021-05-06
CA_MA_Split_MSW ERV Flag | Split_MSW ERV Flag | No | Yes | No | Yes | No | No | No | Yes | No | Yes | 2021-05-06
CA_MA_Split_MNW ERV Flag | Split_MNW ERV Flag | No | Yes | No | Yes | No | No | No | Yes | No | Yes | 2021-05-06
CA_MA_Split_MSE ERV Flag | Split_MSE ERV Flag | No | Yes | No | Yes | No | No | No | Yes | No | Yes | 2021-05-06
CA_MA_Split_MNE ERV Flag | Split_MNE ERV Flag | No | Yes | No | Yes | No | No | No | Yes | No | Yes | 2021-05-06
CA_MA_Split_MN1 ERV Flag | Split_MN1 ERV Flag | No | Yes | No | Yes | No | No | No | Yes | No | Yes | 2021-05-06
CA_MA_Split_MN2 ERV Flag | Split_MN2 ERV Flag | No | Yes | No | Yes | No | No | No | Yes | No | Yes | 2021-05-06
CA_MA_Split_MS1 ERV Flag | Split_MS1 ERV Flag | No | Yes | No | Yes | No | No | No | Yes | No | Yes | 2021-05-06
CA_MA_Split_MS2 ERV Flag | Split_MS2 ERV Flag | No | Yes | No | Yes | No | No | No | Yes | No | Yes | 2021-05-06
CA_MA_Split_TSW ERV Flag | Split_TSW ERV Flag | No | No | No | Yes | No | No | No | No | No | No | 2021-05-06
CA_MA_Split_TNW ERV Flag | Split_TNW ERV Flag | No | No | No | Yes | No | No | No | No | No | No | 2021-05-06
CA_MA_Split_TSE ERV Flag | Split_TSE ERV Flag | No | Yes | No | Yes | No | No | No | Yes | No | Yes | 2021-05-06
CA_MA_Split_TNE ERV Flag | Split_TNE ERV Flag | No | Yes | No | Yes | No | No | No | Yes | No | Yes | 2021-05-06
CA_MA_Split_TN1 ERV Flag | Split_TN1 ERV Flag | No | Yes | No | Yes | No | No | No | Yes | No | Yes | 2021-05-06
CA_MA_Split_TN2 ERV Flag | Split_TN2 ERV Flag | No | Yes | No | Yes | No | No | No | Yes | No | Yes | 2021-05-06
CA_MA_Split_TS1 ERV Flag | Split_TS1 ERV Flag | No | Yes | No | Yes | No | No | No | Yes | No | Yes | 2021-05-06
CA_MA_Split_TS2 ERV Flag | Split_TS2 ERV Flag | No | Yes | No | Yes | No | No | No | Yes | No | Yes | 2021-05-06
id | item | Zone4B(CO-Trinidad-CO) ASHRAE901-state_STD2016 | Zone4B(CO-Trinidad-CO) ASHRAE901-state_STD2019 | Zone5B(CO-ColoradoSprings-CO) ASHRAE901-state_STD2016 | Zone5B(CO-ColoradoSprings-CO) ASHRAE901-state_STD2019 | Zone6B(CO-EagleCounty-CO) ASHRAE901-state_STD2016 | Zone6B(CO-EagleCounty-CO) ASHRAE901-state_STD2019 | Zone7(CO-GunnisonCounty-CO) ASHRAE901-state_STD2016 | Zone7(CO-GunnisonCounty-CO) ASHRAE901-state_STD2019 |  |  | 2021-05-06
CO_SO_PSZ-AC:1 Cooling Capacity [ton] | PSZ-AC:1 Cooling Capacity [ton] | 1.7371 | 1.6155 | 1.7508 | 1.6281 | 1.7403 | 1.6094 | 1.7627 | 1.6172 |  |  | 2021-05-06
CO_SO_PSZ-AC:2 Cooling Capacity [ton] | PSZ-AC:2 Cooling Capacity [ton] | 1.4621 | 1.3787 | 1.4643 | 1.3815 | 1.3902 | 1.2876 | 1.3364 | 1.2005 |  |  | 2021-05-06
CO_SO_PSZ-AC:3 Cooling Capacity [ton] | PSZ-AC:3 Cooling Capacity [ton] | 1.1699 | 1.118 | 1.1881 | 1.136 | 1.1498 | 1.0612 | 1.2333 | 1.088 |  |  | 2021-05-06
CO_SO_PSZ-AC:4 Cooling Capacity [ton] | PSZ-AC:4 Cooling Capacity [ton] | 1.4309 | 1.3279 | 1.413 | 1.3131 | 1.3368 | 1.2203 | 1.2715 | 1.14 |  |  | 2021-05-06
CO_SO_PSZ-AC:5 Cooling Capacity [ton] | PSZ-AC:5 Cooling Capacity [ton] | 1.4916 | 1.4368 | 1.4834 | 1.4291 | 1.4754 | 1.3805 | 1.5627 | 1.3965 |  |  | 2021-05-06
CO_SO_PSZ-AC:1 Supply Flow Rate [cfm] | PSZ-AC:1 Supply Flow Rate [cfm] | 783.9856 | 720.4192 | 783.9856 | 741.608 | 783.9856 | 720.4192 | 783.9856 | 720.4192 |  |  | 2021-05-06
CO_SO_PSZ-AC:2 Supply Flow Rate [cfm] | PSZ-AC:2 Supply Flow Rate [cfm] | 656.8528 | 614.4752 | 656.8528 | 614.4752 | 635.664 | 572.0976 | 593.2864 | 550.9088 |  |  | 2021-05-06
CO_SO_PSZ-AC:3 Supply Flow Rate [cfm] | PSZ-AC:3 Supply Flow Rate [cfm] | 529.72 | 508.5312 | 529.72 | 508.5312 | 508.5312 | 487.3424 | 550.9088 | 487.3424 |  |  | 2021-05-06
CO_SO_PSZ-AC:4 Supply Flow Rate [cfm] | PSZ-AC:4 Supply Flow Rate [cfm] | 635.664 | 593.2864 | 635.664 | 593.2864 | 593.2864 | 550.9088 | 572.0976 | 508.5312 |  |  | 2021-05-06
CO_SO_PSZ-AC:5 Supply Flow Rate [cfm] | PSZ-AC:5 Supply Flow Rate [cfm] | 678.0416 | 656.8528 | 678.0416 | 635.664 | 656.8528 | 614.4752 | 699.2304 | 635.664 |  |  | 2021-05-06
CO_SO_PSZ-AC:1 OA Rate [cfm] | PSZ-AC:1 OA Rate [cfm] | 136.9178 | 136.9178 | 136.9178 | 136.9178 | 136.9178 | 136.9178 | 136.9178 | 136.9178 |  |  | 2021-05-06
CO_SO_PSZ-AC:2 OA Rate [cfm] | PSZ-AC:2 OA Rate [cfm] | 103.7925 | 103.7925 | 103.7925 | 103.7925 | 103.7925 | 103.7925 | 103.7925 | 103.7925 |  |  | 2021-05-06
CO_SO_PSZ-AC:3 OA Rate [cfm] | PSZ-AC:3 OA Rate [cfm] | 61.5711 | 61.5711 | 61.5711 | 61.5711 | 61.5711 | 61.5711 | 61.5711 | 61.5711 |  |  | 2021-05-06
CO_SO_PSZ-AC:4 OA Rate [cfm] | PSZ-AC:4 OA Rate [cfm] | 103.7925 | 103.7925 | 103.7925 | 103.7925 | 103.7925 | 103.7925 | 103.7925 | 103.7925 |  |  | 2021-05-06
CO_SO_PSZ-AC:5 OA Rate [cfm] | PSZ-AC:5 OA Rate [cfm] | 61.5711 | 61.5711 | 61.5711 | 61.5711 | 61.5711 | 61.5711 | 61.5711 | 61.5711 |  |  | 2021-05-06
CO_SO_PSZ-AC:1 heating Capacity [kBtu/hr] | PSZ-AC:1 heating Capacity [kBtu/hr] | 12.4454 | 12.4161 | 12.6234 | 12.5937 | 13.9437 | 13.9123 | 14.2623 | 14.1904 |  |  | 2021-05-06
CO_SO_PSZ-AC:2 heating Capacity [kBtu/hr] | PSZ-AC:2 heating Capacity [kBtu/hr] | 18.4945 | 18.2651 | 18.2943 | 18.0681 | 19.5599 | 19.3061 | 20.169 | 19.6009 |  |  | 2021-05-06
CO_SO_PSZ-AC:3 heating Capacity [kBtu/hr] | PSZ-AC:3 heating Capacity [kBtu/hr] | 11.2109 | 11.0888 | 11.1448 | 11.0147 | 11.8529 | 11.7128 | 12.2804 | 11.9613 |  |  | 2021-05-06
CO_SO_PSZ-AC:4 heating Capacity [kBtu/hr] | PSZ-AC:4 heating Capacity [kBtu/hr] | 18.2955 | 18.1078 | 18.1927 | 18.0002 | 19.3419 | 19.1389 | 20.1172 | 19.645 |  |  | 2021-05-06
CO_SO_PSZ-AC:5 heating Capacity [kBtu/hr] | PSZ-AC:5 heating Capacity [kBtu/hr] | 11.2638 | 11.1367 | 11.0927 | 10.9675 | 11.8214 | 11.6842 | 12.2525 | 11.9389 |  |  | 2021-05-06
id | item | Zone4B(CO-Trinidad-CO) ASHRAE901-state_STD2016 | Zone4B(CO-Trinidad-CO) ASHRAE901-state_STD2019 | Zone5B(CO-ColoradoSprings-CO) ASHRAE901-state_STD2016 | Zone5B(CO-ColoradoSprings-CO) ASHRAE901-state_STD2019 | Zone6B(CO-EagleCounty-CO) ASHRAE901-state_STD2016 | Zone6B(CO-EagleCounty-CO) ASHRAE901-state_STD2019 | Zone7(CO-GunnisonCounty-CO) ASHRAE901-state_STD2016 | Zone7(CO-GunnisonCounty-CO) ASHRAE901-state_STD2019 |  |  | 2021-05-06
CO_LO_CAV_BAS Supply Flow Rate [cfm] | CAV_BAS Supply Flow Rate [cfm] | 14238.8736 | 13158.2448 | 14471.9504 | 13370.1328 | 14620.272 | 13518.4544 | 15319.5024 | 14154.1184 |  |  | 2021-05-06
CO_LO_VAV_BOT WITH REHEAT Supply Flow Rate [cfm] | VAV_BOT WITH REHEAT Supply Flow Rate [cfm] | 23689.0784 | 22566.072 | 24112.8544 | 22968.6592 | 23858.5888 | 22502.5056 | 25214.672 | 23540.7568 |  |  | 2021-05-06
CO_LO_VAV_MID WITH REHEAT Supply Flow Rate [cfm] | VAV_MID WITH REHEAT Supply Flow Rate [cfm] | 219643.1011 | 208879.1907 | 223308.7635 | 212396.5315 | 219325.2691 | 205870.3811 | 231932.6052 | 214917.9987 |  |  | 2021-05-06
CO_LO_VAV_TOP WITH REHEAT Supply Flow Rate [cfm] | VAV_TOP WITH REHEAT Supply Flow Rate [cfm] | 23519.568 | 22544.8832 | 23816.2112 | 22841.5264 | 23561.9456 | 22248.24 | 24197.6096 | 22354.184 |  |  | 2021-05-06
CO_LO_Supply Air Temp. Reset Flag | Supply Air Temp. Reset Flag | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  |  | 2021-05-06
CO_LO_CAV_BAS OA Rate [cfm] | CAV_BAS OA Rate [cfm] | 2542.8255 | 2542.8255 | 2542.8255 | 2542.8255 | 2542.8255 | 2542.8255 | 2542.8255 | 2542.8255 |  |  | 2021-05-06
CO_LO_VAV_BOT WITH REHEAT OA Rate [cfm] | VAV_BOT WITH REHEAT OA Rate [cfm] | 5377.8022 | 4302.174 | 5377.8022 | 4302.174 | 5377.8022 | 4302.174 | 5377.8022 | 4302.174 |  |  | 2021-05-06
CO_LO_VAV_MID WITH REHEAT OA Rate [cfm] | VAV_MID WITH REHEAT OA Rate [cfm] | 53777.9373 | 43021.7396 | 53777.9373 | 43021.7396 | 53777.9373 | 43021.7396 | 53777.9373 | 43021.7396 |  |  | 2021-05-06
CO_LO_VAV_TOP WITH REHEAT OA Rate [cfm] | VAV_TOP WITH REHEAT OA Rate [cfm] | 5377.8022 | 4302.174 | 5377.8022 | 4302.174 | 5377.8022 | 4302.174 | 5377.8022 | 4302.174 |  |  | 2021-05-06
CO_LO_AIRLOOP DATACENTER BASEMENT OA Rate [cfm] | AIRLOOP DATACENTER BASEMENT OA Rate [cfm] | 716.9654 | 716.9654 | 716.9654 | 716.9654 | 716.9654 | 716.9654 | 716.9654 | 716.9654 |  |  | 2021-05-06
CO_LO_VAV_bot_WITH_REHEAT ERV Flag | VAV_bot_WITH_REHEAT ERV Flag | No | No | No | No | No | No | Yes | Yes |  |  | 2021-05-06
CO_LO_VAV_mid_WITH_REHEAT ERV Flag | VAV_mid_WITH_REHEAT ERV Flag | No | No | No | No | No | No | Yes | Yes |  |  | 2021-05-06
CO_LO_VAV_top_WITH_REHEAT ERV Flag | VAV_top_WITH_REHEAT ERV Flag | No | No | No | No | No | No | Yes | Yes |  |  | 2021-05-06
CO_LO_COOLSYS1 CHILLER1 Capacity [ton] | COOLSYS1 CHILLER1 Capacity [ton] | 308.7285 | 288.6304 | 299.3307 | 281.2607 | 282.1166 | 263.3018 | 269.3047 | 247.3926 |  |  | 2021-05-06
CO_LO_COOLSYS1 CHILLER2 Capacity [ton] | COOLSYS1 CHILLER2 Capacity [ton] | 308.7285 | 288.6304 | 299.3307 | 281.2607 | 282.1166 | 263.3018 | 269.3047 | 247.3926 |  |  | 2021-05-06
CO_LO_TOWERWATERSYS COOLTOWER 1 Capacity [ton] | TOWERWATERSYS COOLTOWER 1 Capacity [ton] | 293.4012 | 274.3038 | 284.4768 | 267.2983 | 268.1132 | 250.2381 | 255.9424 | 235.11 |  |  | 2021-05-06
CO_LO_TOWERWATERSYS COOLTOWER 2 Capacity [ton] | TOWERWATERSYS COOLTOWER 2 Capacity [ton] | 293.4012 | 274.3038 | 284.4768 | 267.2983 | 268.1132 | 250.2381 | 255.9424 | 235.11 |  |  | 2021-05-06
CO_LO_HEATSYS1 BOILER Capacity [MMBTU/h] | HEATSYS1 BOILER Capacity [MMBTU/h] | 4233.0978 | 3734.6152 | 4236.6183 | 3725.9141 | 4390.4168 | 3875.5863 | 4522.6395 | 3932.4573 |  |  | 2021-05-06
CO_LO_COOLSYS1 PUMP Flow Rate [gal/min] | COOLSYS1 PUMP Flow Rate [gal/min] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 2021-05-06
CO_LO_COOLSYS1 CHILLER1 PUMP Flow Rate [gal/min] | COOLSYS1 CHILLER1 PUMP Flow Rate [gal/min] | 481.3188 | 450.1603 | 469.867 | 438.3851 | 442.6551 | 413.1418 | 422.1702 | 387.7908 |  |  | 2021-05-06
CO_LO_COOLSYS1 CHILLER2 PUMP Flow Rate [gal/min] | COOLSYS1 CHILLER2 PUMP Flow Rate [gal/min] | 481.3188 | 450.1603 | 469.867 | 438.3851 | 442.6551 | 413.1418 | 422.1702 | 387.7908 |  |  | 2021-05-06
CO_LO_COOLSYS1 PUMP SECONDARY Flow Rate [gal/min] | COOLSYS1 PUMP SECONDARY Flow Rate [gal/min] | 962.6377 | 900.3221 | 939.7324 | 876.7701 | 885.3103 | 826.2837 | 844.3404 | 775.5801 |  |  | 2021-05-06
CO_LO_HEATSYS1 PUMP Flow Rate [gal/min] | HEATSYS1 PUMP Flow Rate [gal/min] | 868.8989 | 766.5787 | 869.6216 | 764.7924 | 901.1907 | 795.515 | 928.3312 | 807.1888 |  |  | 2021-05-06
CO_LO_TOWERWATERSYS PUMP Flow Rate [gal/min] | TOWERWATERSYS PUMP Flow Rate [gal/min] | 1703.2757 | 1631.3153 | 1691.8635 | 1589.7874 | 1594.5425 | 1488.2154 | 1522.1446 | 1398.2949 |  |  | 2021-05-06
CO_LO_PLANT CIRC PUMP Flow Rate [gal/min] | PLANT CIRC PUMP Flow Rate [gal/min] | 230.7649 | 229.8233 | 232.082 | 231.1358 | 233.4689 | 232.128 | 229.8614 | 227.9419 |  |  | 2021-05-06
CO_LO_COOLSYS1 PUMP SECONDARY Pressure setpoint reset [yes,no] | COOLSYS1 PUMP SECONDARY Pressure setpoint reset [yes,no] | pump_ride_on_curve | pump_ride_on_curve | pump_ride_on_curve | pump_ride_on_curve | pump_ride_on_curve | pump_ride_on_curve | pump_ride_on_curve | pump_ride_on_curve |  |  | 2021-05-06
CO_LO_COOLSYS1 CHILLER1 PUMP Pump Power [hp] | COOLSYS1 CHILLER1 PUMP Pump Power [hp] | 2.5965 | 2.4044 | 2.5348 | 2.3415 | 2.388 | 2.2067 | 2.2775 | 2.0713 |  |  | 2021-05-06
CO_LO_COOLSYS1 CHILLER2 PUMP Pump Power [hp] | COOLSYS1 CHILLER2 PUMP Pump Power [hp] | 2.5965 | 2.4044 | 2.5348 | 2.3415 | 2.388 | 2.2067 | 2.2775 | 2.0713 |  |  | 2021-05-06
CO_LO_COOLSYS1 PUMP SECONDARY Pump Power [hp] | COOLSYS1 PUMP SECONDARY Pump Power [hp] | 15.5793 | 14.4265 | 15.2086 | 14.0491 | 14.3278 | 13.2401 | 13.6648 | 12.4277 |  |  | 2021-05-06
CO_LO_HEATSYS1 PUMP Pump Power [hp] | HEATSYS1 PUMP Pump Power [hp] | 18.7818 | 16.406 | 18.7974 | 16.3678 | 19.4798 | 17.0253 | 20.0664 | 17.2751 |  |  | 2021-05-06
CO_LO_TOWERWATERSYS PUMP Pump Power [hp] | TOWERWATERSYS PUMP Pump Power [hp] | 30.4956 | 28.9191 | 30.2912 | 28.1807 | 28.5492 | 26.3814 | 27.2526 | 24.7873 |  |  | 2021-05-06
CO_LO_PLANT CIRC PUMP Pump Power [hp] | PLANT CIRC PUMP Pump Power [hp] | 4.9796 | 4.9102 | 5.008 | 4.9382 | 5.0379 | 4.9594 | 4.9601 | 4.8699 |  |  | 2021-05-06
CO_LO_Datacenter PLANT CIRC PUMP Pump Power [hp] | Datacenter PLANT CIRC PUMP Pump Power [hp] | 4.9796 | 4.9102 | 5.008 | 4.9382 | 5.0379 | 4.9594 | 4.9601 | 4.8699 |  |  | 2021-05-06
CO_LO_ZN_VAV_BOXes_Max_Reheat_Water_Flow_GPM | ZN_VAV_BOXes_Max_Reheat_Water_Flow_GPM | 470.9089 | 452.2409 | 465.4874 | 445.4912 | 455.9575 | 435.7632 | 454.6402 | 423.6394 |  |  | 2021-05-06
CO_LO_COOLSYS1 PUMP SECONDARY VSD | COOLSYS1 PUMP SECONDARY VSD | No | No | No | No | No | No | No | No |  |  | 2021-05-06
CO_LO_HEATSYS1 PUMP VSD | HEATSYS1 PUMP VSD | No | No | No | No | No | No | No | No |  |  | 2021-05-06
CO_LO_DATACENTER BASEMENT Cooling Capacity [ton] | DATACENTER BASEMENT Cooling Capacity [ton] | 135.0085 | 134.6039 | 135.7257 | 135.3189 | 136.3961 | 135.9758 | 133.7944 | 133.368 |  |  | 2021-05-06
CO_LO_DATACENTER BOT Cooling Capacity [ton] | DATACENTER BOT Cooling Capacity [ton] | 2.946 | 2.9194 | 2.9665 | 2.9398 | 2.9954 | 2.9476 | 2.9866 | 2.9071 |  |  | 2021-05-06
CO_LO_DATACENTER MID Cooling Capacity [ton] | DATACENTER MID Cooling Capacity [ton] | 28.21 | 27.9745 | 28.4176 | 28.181 | 28.7094 | 28.2412 | 28.6895 | 27.8709 |  |  | 2021-05-06
CO_LO_DATACENTER TOP Cooling Capacity [ton] | DATACENTER TOP Cooling Capacity [ton] | 2.8756 | 2.8528 | 2.8952 | 2.8724 | 2.9201 | 2.8738 | 2.9074 | 2.8257 |  |  | 2021-05-06
id | item | Zone4B(CO-Trinidad-CO) ASHRAE901-state_STD2016 | Zone4B(CO-Trinidad-CO) ASHRAE901-state_STD2019 | Zone5B(CO-ColoradoSprings-CO) ASHRAE901-state_STD2016 | Zone5B(CO-ColoradoSprings-CO) ASHRAE901-state_STD2019 | Zone6B(CO-EagleCounty-CO) ASHRAE901-state_STD2016 | Zone6B(CO-EagleCounty-CO) ASHRAE901-state_STD2019 | Zone7(CO-GunnisonCounty-CO) ASHRAE901-state_STD2016 | Zone7(CO-GunnisonCounty-CO) ASHRAE901-state_STD2019 |  |  | 2021-05-06
CO_RS_PSZ-AC:1 Cooling Capacity [ton] | PSZ-AC:1 Cooling Capacity [ton] | 10.0706 | 9.3663 | 9.9409 | 9.1001 | 9.0278 | 8.1693 | 8.838 | 7.9458 |  |  | 2021-05-06
CO_RS_PSZ-AC:2 Cooling Capacity [ton] | PSZ-AC:2 Cooling Capacity [ton] | 42.3674 | 40.3669 | 40.6484 | 38.5472 | 39.5192 | 37.2189 | 40.2206 | 37.8655 |  |  | 2021-05-06
CO_RS_PSZ-AC:3 Cooling Capacity [ton] | PSZ-AC:3 Cooling Capacity [ton] | 5.7463 | 5.5559 | 5.821 | 5.6207 | 5.4314 | 5.2236 | 5.5 | 5.2744 |  |  | 2021-05-06
CO_RS_PSZ-AC:4 Cooling Capacity [ton] | PSZ-AC:4 Cooling Capacity [ton] | 4.3759 | 4.2128 | 4.3089 | 4.1169 | 4.0063 | 3.7782 | 3.9343 | 3.7701 |  |  | 2021-05-06
CO_RS_PSZ-AC:1 Supply Flow Rate [cfm] | PSZ-AC:1 Supply Flow Rate [cfm] | 4492.0256 | 4131.816 | 4470.8368 | 4089.4384 | 4068.2496 | 3686.8512 | 3983.4944 | 3580.9072 |  |  | 2021-05-06
CO_RS_PSZ-AC:2 Supply Flow Rate [cfm] | PSZ-AC:2 Supply Flow Rate [cfm] | 18222.368 | 17205.3056 | 18307.1232 | 17247.6832 | 17798.592 | 16760.3408 | 18095.2352 | 17035.7952 |  |  | 2021-05-06
CO_RS_PSZ-AC:3 Supply Flow Rate [cfm] | PSZ-AC:3 Supply Flow Rate [cfm] | 2585.0336 | 2500.2784 | 2627.4112 | 2521.4672 | 2436.712 | 2351.9568 | 2479.0896 | 2373.1456 |  |  | 2021-05-06
CO_RS_PSZ-AC:4 Supply Flow Rate [cfm] | PSZ-AC:4 Supply Flow Rate [cfm] | 1928.1808 | 1843.4256 | 1949.3696 | 1843.4256 | 1801.048 | 1695.104 | 1779.8592 | 1695.104 |  |  | 2021-05-06
CO_RS_PSZ-AC:1 OA Rate [cfm] | PSZ-AC:1 OA Rate [cfm] | 490.669 | 490.669 | 490.669 | 490.669 | 490.669 | 490.669 | 490.669 | 490.669 |  |  | 2021-05-06
CO_RS_PSZ-AC:2 OA Rate [cfm] | PSZ-AC:2 OA Rate [cfm] | 4005.1282 | 4005.1282 | 4005.1282 | 4005.1282 | 4005.1282 | 4005.1282 | 4005.1282 | 4005.1282 |  |  | 2021-05-06
CO_RS_PSZ-AC:3 OA Rate [cfm] | PSZ-AC:3 OA Rate [cfm] | 377.3937 | 377.3937 | 377.3937 | 377.3937 | 377.3937 | 377.3937 | 377.3937 | 377.3937 |  |  | 2021-05-06
CO_RS_PSZ-AC:4 OA Rate [cfm] | PSZ-AC:4 OA Rate [cfm] | 377.3937 | 377.3937 | 377.3937 | 377.3937 | 377.3937 | 377.3937 | 377.3937 | 377.3937 |  |  | 2021-05-06
CO_RS_PSZ-AC:1 OA Damper [gravity, motorized] | PSZ-AC:1 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | motorized | motorized | motorized | motorized |  |  | 2021-05-06
CO_RS_PSZ-AC:2 OA Damper [gravity, motorized] | PSZ-AC:2 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | motorized | motorized | motorized | motorized |  |  | 2021-05-06
CO_RS_PSZ-AC:3 OA Damper [gravity, motorized] | PSZ-AC:3 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | motorized | motorized | motorized | motorized |  |  | 2021-05-06
CO_RS_PSZ-AC:4 OA Damper [gravity, motorized] | PSZ-AC:4 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | motorized | motorized | motorized | motorized |  |  | 2021-05-06
CO_RS_PSZ-AC:1 Heating Capacity [kBtu/hr] | PSZ-AC:1 Heating Capacity [kBtu/hr] | 163.272 | 151.2094 | 160.8367 | 148.1741 | 147.9252 | 139.9016 | 141.4262 | 134.3571 |  |  | 2021-05-06
CO_RS_PSZ-AC:2 Heating Capacity [kBtu/hr] | PSZ-AC:2 Heating Capacity [kBtu/hr] | 777.4173 | 742.4635 | 775.4252 | 739.534 | 772.8267 | 739.7297 | 776.7101 | 743.2615 |  |  | 2021-05-06
CO_RS_PSZ-AC:3 Heating Capacity [kBtu/hr] | PSZ-AC:3 Heating Capacity [kBtu/hr] | 100.3022 | 97.7296 | 100.4524 | 97.7855 | 96.4314 | 93.7002 | 95.6765 | 92.8403 |  |  | 2021-05-06
CO_RS_PSZ-AC:4 Heating Capacity [kBtu/hr] | PSZ-AC:4 Heating Capacity [kBtu/hr] | 78.872 | 78.1967 | 78.6731 | 77.7654 | 77.7098 | 74.714 | 76.0072 | 73.9441 |  |  | 2021-05-06
id | item | Zone4B(CO-Trinidad-CO) ASHRAE901-state_STD2016 | Zone4B(CO-Trinidad-CO) ASHRAE901-state_STD2019 | Zone5B(CO-ColoradoSprings-CO) ASHRAE901-state_STD2016 | Zone5B(CO-ColoradoSprings-CO) ASHRAE901-state_STD2019 | Zone6B(CO-EagleCounty-CO) ASHRAE901-state_STD2016 | Zone6B(CO-EagleCounty-CO) ASHRAE901-state_STD2019 | Zone7(CO-GunnisonCounty-CO) ASHRAE901-state_STD2016 | Zone7(CO-GunnisonCounty-CO) ASHRAE901-state_STD2019 |  |  | 2021-05-06
CO_PS_VAV_POD_1 Cooling Capacity [ton] | VAV_POD_1 Cooling Capacity [ton] | 20.6328 | 19.3861 | 19.1581 | 17.8961 | 17.0359 | 15.7589 | 14.0192 | 12.7747 |  |  | 2021-05-06
CO_PS_VAV_POD_2 Cooling Capacity [ton] | VAV_POD_2 Cooling Capacity [ton] | 20.5626 | 19.1262 | 18.9345 | 17.5901 | 16.8756 | 15.5118 | 13.794 | 12.6468 |  |  | 2021-05-06
CO_PS_VAV_POD_3 Cooling Capacity [ton] | VAV_POD_3 Cooling Capacity [ton] | 18.876 | 17.5236 | 17.6065 | 16.2805 | 15.733 | 14.4152 | 12.9815 | 11.6232 |  |  | 2021-05-06
CO_PS_VAV_OTHER Cooling Capacity [ton] | VAV_OTHER Cooling Capacity [ton] | 22.5535 | 20.5484 | 21.5159 | 20.1669 | 20.8651 | 19.2697 | 20.7705 | 18.693 |  |  | 2021-05-06
CO_PS_PSZ-AC_1:6 Cooling Capacity [ton] | PSZ-AC_1:6 Cooling Capacity [ton] | 7.8729 | 7.5893 | 7.6903 | 7.4098 | 7.4386 | 7.1388 | 7.2956 | 6.9106 |  |  | 2021-05-06
CO_PS_PSZ-AC_2:5 Cooling Capacity [ton] | PSZ-AC_2:5 Cooling Capacity [ton] | 5.2053 | 5.189 | 4.9116 | 4.8979 | 4.5954 | 4.5481 | 4.7351 | 4.6968 |  |  | 2021-05-06
CO_PS_PSZ-AC_2:7 Cooling Capacity [ton] | PSZ-AC_2:7 Cooling Capacity [ton] | 9.6283 | 9.6283 | 9.0115 | 9.0115 | 8.4851 | 8.4851 | 7.0064 | 7.0064 |  |  | 2021-05-06
CO_PS_VAV_POD_1 Supply Flow Rate [cfm] | VAV_POD_1 Supply Flow Rate [cfm] | 6674.472 | 6271.8848 | 6716.8496 | 6271.8848 | 6399.0176 | 5932.864 | 6314.2624 | 5742.1648 |  |  | 2021-05-06
CO_PS_VAV_POD_2 Supply Flow Rate [cfm] | VAV_POD_2 Supply Flow Rate [cfm] | 6653.2832 | 6187.1296 | 6632.0944 | 6165.9408 | 6335.4512 | 5826.92 | 6208.3184 | 5699.7872 |  |  | 2021-05-06
CO_PS_VAV_POD_3 Supply Flow Rate [cfm] | VAV_POD_3 Supply Flow Rate [cfm] | 6144.752 | 5763.3536 | 6165.9408 | 5784.5424 | 5911.6752 | 5424.3328 | 5848.1088 | 5233.6336 |  |  | 2021-05-06
CO_PS_VAV_OTHER Supply Flow Rate [cfm] | VAV_OTHER Supply Flow Rate [cfm] | 9640.904 | 9068.8064 | 9683.2816 | 9068.8064 | 9386.6384 | 8666.2192 | 9344.2608 | 8411.9536 |  |  | 2021-05-06
CO_PS_PSZ-AC_2:5 Supply Flow Rate [cfm] | PSZ-AC_2:5 Supply Flow Rate [cfm] | 2012.936 | 2012.936 | 2012.936 | 2012.936 | 1970.5584 | 1949.3696 | 2140.0688 | 2118.88 |  |  | 2021-05-06
CO_PS_PSZ-AC_1:6 Supply Flow Rate [cfm] | PSZ-AC_1:6 Supply Flow Rate [cfm] | 3093.5648 | 2966.432 | 3135.9424 | 3008.8096 | 3157.1312 | 3008.8096 | 3284.264 | 3114.7536 |  |  | 2021-05-06
CO_PS_PSZ-AC_2:7 Supply Flow Rate [cfm] | PSZ-AC_2:7 Supply Flow Rate [cfm] | 3157.1312 | 3157.1312 | 3157.1312 | 3157.1312 | 3157.1312 | 3157.1312 | 3157.1312 | 3157.1312 |  |  | 2021-05-06
CO_PS_Supply Air Temp. Reset Flag | Supply Air Temp. Reset Flag | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  |  | 2021-05-06
CO_PS_VAV_POD_1 OA Rate [cfm] | VAV_POD_1 OA Rate [cfm] | 6678.8369 | 6275.6776 | 6707.0604 | 6268.2827 | 6403.658 | 5924.4097 | 6307.8846 | 5750.6615 |  |  | 2021-05-06
CO_PS_VAV_POD_2 OA Rate [cfm] | VAV_POD_2 OA Rate [cfm] | 6656.5251 | 6191.5581 | 6629.4458 | 6161.0886 | 6342.3588 | 5831.4968 | 6206.5809 | 5693.0915 |  |  | 2021-05-06
CO_PS_VAV_POD_3 OA Rate [cfm] | VAV_POD_3 OA Rate [cfm] | 6153.7361 | 5422.002 | 6166.8096 | 5422.002 | 5914.684 | 5419.2687 | 5841.9852 | 5232.3199 |  |  | 2021-05-06
CO_PS_VAV_OTHER OA Rate [cfm] | VAV_OTHER OA Rate [cfm] | 3736.1787 | 2988.8921 | 3736.1787 | 2988.8921 | 3736.1787 | 2988.8921 | 3736.1787 | 2988.8921 |  |  | 2021-05-06
CO_PS_PSZ-AC_2:5 OA Rate [cfm] | PSZ-AC_2:5 OA Rate [cfm] | 1152.7343 | 1152.7343 | 1152.7343 | 1152.7343 | 1152.7343 | 1152.7343 | 1152.7343 | 1152.7343 |  |  | 2021-05-06
CO_PS_PSZ-AC_1:6 OA Rate [cfm] | PSZ-AC_1:6 OA Rate [cfm] | 539.9118 | 539.9118 | 539.9118 | 539.9118 | 539.9118 | 539.9118 | 539.9118 | 539.9118 |  |  | 2021-05-06
CO_PS_PSZ-AC_2:7 OA Rate [cfm] | PSZ-AC_2:7 OA Rate [cfm] | 3153.0841 | 3153.0841 | 3153.0841 | 3153.0841 | 3153.0841 | 3153.0841 | 3153.0841 | 3153.0841 |  |  | 2021-05-06
CO_PS_VAV_POD_1 OA Damper [gravity, motorized] | VAV_POD_1 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | motorized | motorized | motorized | motorized |  |  | 2021-05-06
CO_PS_VAV_POD_2 OA Damper [gravity, motorized] | VAV_POD_2 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | motorized | motorized | motorized | motorized |  |  | 2021-05-06
CO_PS_VAV_POD_3 OA Damper [gravity, motorized] | VAV_POD_3 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | motorized | motorized | motorized | motorized |  |  | 2021-05-06
CO_PS_VAV_OTHER OA Damper [gravity, motorized] | VAV_OTHER OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | motorized | motorized | motorized | motorized |  |  | 2021-05-06
CO_PS_PSZ-AC_2:5 OA Damper [gravity, motorized] | PSZ-AC_2:5 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | motorized | motorized | motorized | motorized |  |  | 2021-05-06
CO_PS_PSZ-AC_1:6 OA Damper [gravity, motorized] | PSZ-AC_1:6 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | motorized | motorized | motorized | motorized |  |  | 2021-05-06
CO_PS_PSZ-AC_2:7 OA Damper [gravity, motorized] | PSZ-AC_2:7 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | motorized | motorized | motorized | motorized |  |  | 2021-05-06
CO_PS_VAV_POD_1 (economizer) | VAV_POD_1 (economizer) | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb |  |  | 2021-05-06
CO_PS_VAV_POD_2 (economizer) | VAV_POD_2 (economizer) | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb |  |  | 2021-05-06
CO_PS_VAV_POD_3 (economizer) | VAV_POD_3 (economizer) | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb |  |  | 2021-05-06
CO_PS_VAV_OTHER (economizer) | VAV_OTHER (economizer) | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb |  |  | 2021-05-06
CO_PS_PSZ-AC_2:5 (economizer) | PSZ-AC_2:5 (economizer) | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb |  |  | 2021-05-06
CO_PS_PSZ-AC_1:6 (economizer) | PSZ-AC_1:6 (economizer) | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb |  |  | 2021-05-06
CO_PS_PSZ-AC_2:7 (economizer) | PSZ-AC_2:7 (economizer) | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb |  |  | 2021-05-06
CO_PS_VAV_Pod_1_ERV Flag | VAV_Pod_1_ERV Flag | No | No | No | No | Yes | Yes | Yes | Yes |  |  | 2021-05-06
CO_PS_VAV_Pod_2_ERV Flag | VAV_Pod_2_ERV Flag | No | No | No | No | Yes | Yes | Yes | Yes |  |  | 2021-05-06
CO_PS_VAV_Pod_3_ERV Flag | VAV_Pod_3_ERV Flag | No | No | No | No | Yes | Yes | Yes | Yes |  |  | 2021-05-06
CO_PS_VAV_OTHER_ERV Flag | VAV_OTHER_ERV Flag | No | No | No | No | No | No | Yes | Yes |  |  | 2021-05-06
CO_PS_PSZ_AC_2_5_ERV Flag | PSZ_AC_2_5_ERV Flag | No | No | No | No | No | No | Yes | Yes |  |  | 2021-05-06
CO_PS_PSZ_AC_2_7_ERV Flag | PSZ_AC_2_7_ERV Flag | No | No | No | No | Yes | Yes | Yes | Yes |  |  | 2021-05-06
CO_PS_HEATSYS1 Capacity [MMBTU/h] | HEATSYS1 Capacity [MMBTU/h] | 1.0975 | 1.0277 | 1.1063 | 1.0349 | 1.1437 | 1.0675 | 1.1653 | 1.0686 |  |  | 2021-05-06
CO_PS_HEATSYS1 Flow Rate [gal/min] | HEATSYS1 Flow Rate [gal/min] | 112.6403 | 105.4741 | 113.5403 | 106.2173 | 117.3761 | 109.5581 | 119.5961 | 109.67 |  |  | 2021-05-06
CO_PS_VAV_POD_1 Fan Power [hp] | VAV_POD_1 Fan Power [hp] | 9.8539 | 9.2585 | 9.8997 | 9.2476 | 9.4485 | 8.7403 | 9.3105 | 8.484 |  |  | 2021-05-06
CO_PS_VAV_POD_2 Fan Power [hp] | VAV_POD_2 Fan Power [hp] | 9.8204 | 9.1344 | 9.7842 | 9.0894 | 9.3596 | 8.6032 | 9.1609 | 8.399 |  |  | 2021-05-06
CO_PS_VAV_POD_3 Fan Power [hp] | VAV_POD_3 Fan Power [hp] | 9.0794 | 8.4913 | 9.0979 | 8.533 | 8.7259 | 7.9951 | 8.6213 | 7.7192 |  |  | 2021-05-06
CO_PS_VAV_OTHER Fan Power [hp] | VAV_OTHER Fan Power [hp] | 14.1214 | 13.2761 | 14.181 | 13.2919 | 13.7521 | 12.7006 | 13.6897 | 12.3205 |  |  | 2021-05-06
CO_PS_HEATSYS1 Pump Power [hp] | HEATSYS1 Pump Power [hp] | 2.4348 | 2.2573 | 2.4542 | 2.2732 | 2.5371 | 2.3447 | 2.5851 | 2.3471 |  |  | 2021-05-06
CO_PS_PSZ-AC_1:6 Heating Capacity [kBtu/hr] | PSZ-AC_1:6 Heating Capacity [kBtu/hr] | 210.215 | 201.8088 | 210.4605 | 202.0752 | 211.8741 | 202.7911 | 213.9867 | 203.8253 |  |  | 2021-05-06
CO_PS_PSZ-AC_2:5 Heating Capacity [kBtu/hr] | PSZ-AC_2:5 Heating Capacity [kBtu/hr] | 129.5895 | 129.3491 | 129.7363 | 129.5062 | 134.1872 | 133.4273 | 140.625 | 140.1453 |  |  | 2021-05-06
CO_PS_PSZ-AC_2:7 Heating Capacity [kBtu/hr] | PSZ-AC_2:7 Heating Capacity [kBtu/hr] | 283.8882 | 283.8882 | 285.0614 | 285.0614 | 301.5689 | 301.5689 | 310.0935 | 310.0935 |  |  | 2021-05-06
CO_PS_ZN_VAV_BOXes_Max_Reheat_Water_Flow_GPM | ZN_VAV_BOXes_Max_Reheat_Water_Flow_GPM | 70.3479 | 65.859 | 70.2543 | 65.7529 | 70.7705 | 66.6177 | 69.6946 | 64.4919 |  |  | 2021-05-06
id | item | Zone4B(CO-Trinidad-CO) ASHRAE901-state_STD2016 | Zone4B(CO-Trinidad-CO) ASHRAE901-state_STD2019 | Zone5B(CO-ColoradoSprings-CO) ASHRAE901-state_STD2016 | Zone5B(CO-ColoradoSprings-CO) ASHRAE901-state_STD2019 | Zone6B(CO-EagleCounty-CO) ASHRAE901-state_STD2016 | Zone6B(CO-EagleCounty-CO) ASHRAE901-state_STD2019 | Zone7(CO-GunnisonCounty-CO) ASHRAE901-state_STD2016 | Zone7(CO-GunnisonCounty-CO) ASHRAE901-state_STD2019 |  |  | 2021-05-06
CO_SH_SAC_FRONTOFFICE Cooling Capacity [ton] | SAC_FRONTOFFICE Cooling Capacity [ton] | 2.0619 | 1.918 | 2.0504 | 1.9052 | 1.9955 | 1.8393 | 1.9819 | 1.8242 |  |  | 2021-05-06
CO_SH_SAC_FRONTLOUNGE Cooling Capacity [ton] | SAC_FRONTLOUNGE Cooling Capacity [ton] | 5.3559 | 5.1201 | 5.1652 | 4.9166 | 4.916 | 4.6541 | 4.9568 | 4.6603 |  |  | 2021-05-06
CO_SH_SAC_MEETINGROOM Cooling Capacity [ton] | SAC_MEETINGROOM Cooling Capacity [ton] | 2.8228 | 2.749 | 2.7197 | 2.646 | 2.6054 | 2.5306 | 2.3719 | 2.3059 |  |  | 2021-05-06
CO_SH_SAC_EXC_EMPLGE_RESTRM Cooling Capacity [ton] | SAC_EXC_EMPLGE_RESTRM Cooling Capacity [ton] | 5.9022 | 5.852 | 5.9811 | 5.9306 | 6.0251 | 5.9672 | 6.2595 | 6.1933 |  |  | 2021-05-06
CO_SH_SAC_FO_ADDAQ SUPPLY FAN Supply Flow Rate [cfm] | SAC_FO_ADDAQ SUPPLY FAN Supply Flow Rate [cfm] | 932.3072 | 847.552 | 932.3072 | 847.552 | 889.9296 | 826.3632 | 889.9296 | 826.3632 |  |  | 2021-05-06
CO_SH_SAC_FL_ADDAQ SUPPLY FAN Supply Flow Rate [cfm] | SAC_FL_ADDAQ SUPPLY FAN Supply Flow Rate [cfm] | 2182.4464 | 2076.5024 | 2203.6352 | 2097.6912 | 2182.4464 | 2076.5024 | 2224.824 | 2097.6912 |  |  | 2021-05-06
CO_SH_SAC_MR_ADDAQ SUPPLY FAN Supply Flow Rate [cfm] | SAC_MR_ADDAQ SUPPLY FAN Supply Flow Rate [cfm] | 1038.2512 | 1017.0624 | 1059.44 | 1017.0624 | 1059.44 | 1017.0624 | 1059.44 | 1038.2512 |  |  | 2021-05-06
CO_SH_SAC_EXC_ADDAQ SUPPLY FAN Supply Flow Rate [cfm] | SAC_EXC_ADDAQ SUPPLY FAN Supply Flow Rate [cfm] | 2648.6 | 2627.4112 | 2690.9776 | 2669.7888 | 2712.1664 | 2690.9776 | 2818.1104 | 2796.9216 |  |  | 2021-05-06
CO_SH_SAC_Exc_EmpLge_RestRm OA Rate [cfm] | SAC_Exc_EmpLge_RestRm OA Rate [cfm] | 199.9928 | 199.9928 | 199.9928 | 199.9928 | 199.9928 | 199.9928 | 199.9928 | 199.9928 |  |  | 2021-05-06
CO_SH_SAC_FrontLounge OA Rate [cfm] | SAC_FrontLounge OA Rate [cfm] | 500.0133 | 500.0133 | 500.0133 | 500.0133 | 500.0133 | 500.0133 | 500.0133 | 500.0133 |  |  | 2021-05-06
CO_SH_SAC_FrontOffice OA Rate [cfm] | SAC_FrontOffice OA Rate [cfm] | 119.2938 | 119.2938 | 119.2938 | 119.2938 | 119.2938 | 119.2938 | 119.2938 | 119.2938 |  |  | 2021-05-06
CO_SH_SAC_MeetingRoom OA Rate [cfm] | SAC_MeetingRoom OA Rate [cfm] | 267.7629 | 267.7629 | 267.7629 | 267.7629 | 267.7629 | 267.7629 | 267.7629 | 267.7629 |  |  | 2021-05-06
CO_SH_SAC_FrontLounge OA Damper [gravity, motorized] | SAC_FrontLounge OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | motorized | motorized | motorized | motorized |  |  | 2021-05-06
CO_SH_SAC_FrontOffice (economizer) | SAC_FrontOffice (economizer) | No | No | No | No | No | No | No | No |  |  | 2021-05-06
CO_SH_SAC_FrontLounge (economizer) | SAC_FrontLounge (economizer) | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb |  |  | 2021-05-06
CO_SH_SAC_MeetingRoom (economizer) | SAC_MeetingRoom (economizer) | No | No | No | No | No | No | No | No |  |  | 2021-05-06
CO_SH_SAC_Exc_EmpLge_RestRm (economizer) | SAC_Exc_EmpLge_RestRm (economizer) | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb |  |  | 2021-05-06
CO_SH_SAC_FRONTOFFICE Heating Capacity [kBtu/hr] | SAC_FRONTOFFICE Heating Capacity [kBtu/hr] | 34.8326 | 32.6696 | 34.3681 | 32.4497 | 33.9631 | 31.9278 | 33.1297 | 31.1643 |  |  | 2021-05-06
CO_SH_SAC_FRONTLOUNGE Heating Capacity [kBtu/hr] | SAC_FRONTLOUNGE Heating Capacity [kBtu/hr] | 95.3017 | 91.9559 | 95.3344 | 92.0056 | 96.6678 | 93.1763 | 97.1068 | 93.4119 |  |  | 2021-05-06
CO_SH_SAC_MEETINGROOM Heating Capacity [kBtu/hr] | SAC_MEETINGROOM Heating Capacity [kBtu/hr] | 47.3224 | 46.3325 | 47.387 | 46.3834 | 48.2999 | 47.2712 | 48.4802 | 47.6573 |  |  | 2021-05-06
CO_SH_SAC_EXC_EMPLGE_RESTRM Heating Capacity [kBtu/hr] | SAC_EXC_EMPLGE_RESTRM Heating Capacity [kBtu/hr] | 91.179 | 90.5067 | 91.2094 | 90.5436 | 91.8572 | 91.1029 | 92.1365 | 91.3106 |  |  | 2021-05-06
id | item | Zone4B(CO-Trinidad-CO) ASHRAE901-state_STD2016 | Zone4B(CO-Trinidad-CO) ASHRAE901-state_STD2019 | Zone5B(CO-ColoradoSprings-CO) ASHRAE901-state_STD2016 | Zone5B(CO-ColoradoSprings-CO) ASHRAE901-state_STD2019 | Zone6B(CO-EagleCounty-CO) ASHRAE901-state_STD2016 | Zone6B(CO-EagleCounty-CO) ASHRAE901-state_STD2019 | Zone7(CO-GunnisonCounty-CO) ASHRAE901-state_STD2016 | Zone7(CO-GunnisonCounty-CO) ASHRAE901-state_STD2019 |  |  | 2021-05-06
CO_MA_SPLIT GSW COOLING COIL Cooling Capacity [ton] | SPLIT GSW COOLING COIL Cooling Capacity [ton] | 0.78808 | 0.76956 | 0.79172 | 0.77269 | 0.74916 | 0.71217 | 0.73654 | 0.66411 |  |  | 2021-05-06
CO_MA_SPLIT GNW COOLING COIL Cooling Capacity [ton] | SPLIT GNW COOLING COIL Cooling Capacity [ton] | 0.76101 | 0.74271 | 0.75744 | 0.73878 | 0.71349 | 0.67817 | 0.70251 | 0.63564 |  |  | 2021-05-06
CO_MA_SPLIT OFFICE COOLING COIL Cooling Capacity [ton] | SPLIT OFFICE COOLING COIL Cooling Capacity [ton] | 1.7804 | 1.5845 | 1.8166 | 1.6173 | 1.6898 | 1.4728 | 1.7075 | 1.4372 |  |  | 2021-05-06
CO_MA_SPLIT GNE COOLING COIL Cooling Capacity [ton] | SPLIT GNE COOLING COIL Cooling Capacity [ton] | 0.60852 | 0.59309 | 0.6072 | 0.59142 | 0.56306 | 0.53532 | 0.53932 | 0.48869 |  |  | 2021-05-06
CO_MA_SPLIT GN1 COOLING COIL Cooling Capacity [ton] | SPLIT GN1 COOLING COIL Cooling Capacity [ton] | 0.51727 | 0.50495 | 0.51489 | 0.50238 | 0.47586 | 0.45856 | 0.46053 | 0.42846 |  |  | 2021-05-06
CO_MA_SPLIT GN2 COOLING COIL Cooling Capacity [ton] | SPLIT GN2 COOLING COIL Cooling Capacity [ton] | 0.51424 | 0.502 | 0.51176 | 0.49934 | 0.47297 | 0.45556 | 0.45677 | 0.4252 |  |  | 2021-05-06
CO_MA_SPLIT GS1 COOLING COIL Cooling Capacity [ton] | SPLIT GS1 COOLING COIL Cooling Capacity [ton] | 0.54188 | 0.5289 | 0.5481 | 0.53468 | 0.51359 | 0.49388 | 0.49394 | 0.4586 |  |  | 2021-05-06
CO_MA_SPLIT GS2 COOLING COIL Cooling Capacity [ton] | SPLIT GS2 COOLING COIL Cooling Capacity [ton] | 0.58606 | 0.56685 | 0.59297 | 0.57318 | 0.55782 | 0.5319 | 0.53898 | 0.49695 |  |  | 2021-05-06
CO_MA_SPLIT MSW COOLING COIL Cooling Capacity [ton] | SPLIT MSW COOLING COIL Cooling Capacity [ton] | 2.0686 | 2.0266 | 2.0764 | 2.0334 | 2.0115 | 1.9166 | 2.087 | 1.8994 |  |  | 2021-05-06
CO_MA_SPLIT MNW COOLING COIL Cooling Capacity [ton] | SPLIT MNW COOLING COIL Cooling Capacity [ton] | 2.0168 | 1.9754 | 2.0091 | 1.967 | 1.9454 | 1.8529 | 2.0281 | 1.8493 |  |  | 2021-05-06
CO_MA_SPLIT MSE COOLING COIL Cooling Capacity [ton] | SPLIT MSE COOLING COIL Cooling Capacity [ton] | 1.5939 | 1.5608 | 1.5997 | 1.5656 | 1.5128 | 1.4443 | 1.534 | 1.377 |  |  | 2021-05-06
CO_MA_SPLIT MNE COOLING COIL Cooling Capacity [ton] | SPLIT MNE COOLING COIL Cooling Capacity [ton] | 1.5163 | 1.4872 | 1.5095 | 1.4733 | 1.4151 | 1.3583 | 1.502 | 1.3371 |  |  | 2021-05-06
CO_MA_SPLIT MN1 COOLING COIL Cooling Capacity [ton] | SPLIT MN1 COOLING COIL Cooling Capacity [ton] | 1.2301 | 1.2067 | 1.2224 | 1.1986 | 1.1589 | 1.1206 | 1.1796 | 1.1085 |  |  | 2021-05-06
CO_MA_SPLIT MN2 COOLING COIL Cooling Capacity [ton] | SPLIT MN2 COOLING COIL Cooling Capacity [ton] | 1.2216 | 1.1983 | 1.2137 | 1.1901 | 1.1496 | 1.112 | 1.1685 | 1.0989 |  |  | 2021-05-06
CO_MA_SPLIT MS1 COOLING COIL Cooling Capacity [ton] | SPLIT MS1 COOLING COIL Cooling Capacity [ton] | 1.2664 | 1.2424 | 1.2744 | 1.2497 | 1.2154 | 1.1743 | 1.2167 | 1.1441 |  |  | 2021-05-06
CO_MA_SPLIT MS2 COOLING COIL Cooling Capacity [ton] | SPLIT MS2 COOLING COIL Cooling Capacity [ton] | 1.2582 | 1.2346 | 1.2659 | 1.2415 | 1.2071 | 1.1666 | 1.2067 | 1.1355 |  |  | 2021-05-06
CO_MA_SPLIT TSW COOLING COIL Cooling Capacity [ton] | SPLIT TSW COOLING COIL Cooling Capacity [ton] | 1.337 | 1.3142 | 1.3319 | 1.3086 | 1.2867 | 1.2329 | 1.2963 | 1.1866 |  |  | 2021-05-06
CO_MA_SPLIT TNW COOLING COIL Cooling Capacity [ton] | SPLIT TNW COOLING COIL Cooling Capacity [ton] | 1.3037 | 1.281 | 1.292 | 1.269 | 1.2467 | 1.1939 | 1.2604 | 1.1571 |  |  | 2021-05-06
CO_MA_SPLIT TSE COOLING COIL Cooling Capacity [ton] | SPLIT TSE COOLING COIL Cooling Capacity [ton] | 1.0915 | 1.0744 | 1.0871 | 1.0693 | 1.0262 | 0.9889 | 0.99575 | 0.90845 |  |  | 2021-05-06
CO_MA_SPLIT TNE COOLING COIL Cooling Capacity [ton] | SPLIT TNE COOLING COIL Cooling Capacity [ton] | 1.0184 | 1.0021 | 1.0031 | 0.98657 | 0.9456 | 0.91189 | 0.90582 | 0.84096 |  |  | 2021-05-06
CO_MA_SPLIT TN1 COOLING COIL Cooling Capacity [ton] | SPLIT TN1 COOLING COIL Cooling Capacity [ton] | 0.81352 | 0.80089 | 0.80101 | 0.78811 | 0.75775 | 0.73663 | 0.72703 | 0.6917 |  |  | 2021-05-06
CO_MA_SPLIT TN2 COOLING COIL Cooling Capacity [ton] | SPLIT TN2 COOLING COIL Cooling Capacity [ton] | 0.81302 | 0.80048 | 0.80052 | 0.78772 | 0.75322 | 0.73143 | 0.71494 | 0.68125 |  |  | 2021-05-06
CO_MA_SPLIT TS1 COOLING COIL Cooling Capacity [ton] | SPLIT TS1 COOLING COIL Cooling Capacity [ton] | 0.88861 | 0.87479 | 0.8845 | 0.87025 | 0.83541 | 0.80951 | 0.79606 | 0.7452 |  |  | 2021-05-06
CO_MA_SPLIT TS2 COOLING COIL Cooling Capacity [ton] | SPLIT TS2 COOLING COIL Cooling Capacity [ton] | 0.88854 | 0.87484 | 0.88436 | 0.87022 | 0.83516 | 0.80956 | 0.79754 | 0.74517 |  |  | 2021-05-06
CO_MA_Split GN1 Furnace with DX Cooling OA Rate [cfm] | Split GN1 Furnace with DX Cooling OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 |  |  | 2021-05-06
CO_MA_Split GN2 Furnace with DX Cooling OA Rate [cfm] | Split GN2 Furnace with DX Cooling OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 |  |  | 2021-05-06
CO_MA_Split GNE Furnace with DX Cooling OA Rate [cfm] | Split GNE Furnace with DX Cooling OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 |  |  | 2021-05-06
CO_MA_Split GNW Furnace with DX Cooling OA Rate [cfm] | Split GNW Furnace with DX Cooling OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 |  |  | 2021-05-06
CO_MA_Split GS1 Furnace with DX Cooling OA Rate [cfm] | Split GS1 Furnace with DX Cooling OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 |  |  | 2021-05-06
CO_MA_Split GS2 Furnace with DX Cooling OA Rate [cfm] | Split GS2 Furnace with DX Cooling OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 |  |  | 2021-05-06
CO_MA_Split GSW Furnace with DX Cooling OA Rate [cfm] | Split GSW Furnace with DX Cooling OA Rate [cfm] | 56.9945 | 56.9945 | 56.9945 | 56.9945 | 56.9945 | 56.9945 | 56.9945 | 56.9945 |  |  | 2021-05-06
CO_MA_Split MN1 Furnace with DX Cooling OA Rate [cfm] | Split MN1 Furnace with DX Cooling OA Rate [cfm] | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824 |  |  | 2021-05-06
CO_MA_Split MN2 Furnace with DX Cooling OA Rate [cfm] | Split MN2 Furnace with DX Cooling OA Rate [cfm] | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824 |  |  | 2021-05-06
CO_MA_Split MNE Furnace with DX Cooling OA Rate [cfm] | Split MNE Furnace with DX Cooling OA Rate [cfm] | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824 |  |  | 2021-05-06
CO_MA_Split MNW Furnace with DX Cooling OA Rate [cfm] | Split MNW Furnace with DX Cooling OA Rate [cfm] | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824 |  |  | 2021-05-06
CO_MA_Split MS1 Furnace with DX Cooling OA Rate [cfm] | Split MS1 Furnace with DX Cooling OA Rate [cfm] | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824 |  |  | 2021-05-06
CO_MA_Split MS2 Furnace with DX Cooling OA Rate [cfm] | Split MS2 Furnace with DX Cooling OA Rate [cfm] | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824 |  |  | 2021-05-06
CO_MA_Split MSE Furnace with DX Cooling OA Rate [cfm] | Split MSE Furnace with DX Cooling OA Rate [cfm] | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824 |  |  | 2021-05-06
CO_MA_Split MSW Furnace with DX Cooling OA Rate [cfm] | Split MSW Furnace with DX Cooling OA Rate [cfm] | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824 |  |  | 2021-05-06
CO_MA_Split Office Furnace with DX Cooling OA Rate [cfm] | Split Office Furnace with DX Cooling OA Rate [cfm] | 80.7372 | 80.7372 | 80.7372 | 80.7372 | 80.7372 | 80.7372 | 80.7372 | 80.7372 |  |  | 2021-05-06
CO_MA_Split TN1 Furnace with DX Cooling OA Rate [cfm] | Split TN1 Furnace with DX Cooling OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 |  |  | 2021-05-06
CO_MA_Split TN2 Furnace with DX Cooling OA Rate [cfm] | Split TN2 Furnace with DX Cooling OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 |  |  | 2021-05-06
CO_MA_Split TNE Furnace with DX Cooling OA Rate [cfm] | Split TNE Furnace with DX Cooling OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 |  |  | 2021-05-06
CO_MA_Split TNW Furnace with DX Cooling OA Rate [cfm] | Split TNW Furnace with DX Cooling OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 |  |  | 2021-05-06
CO_MA_Split TS1 Furnace with DX Cooling OA Rate [cfm] | Split TS1 Furnace with DX Cooling OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 |  |  | 2021-05-06
CO_MA_Split TS2 Furnace with DX Cooling OA Rate [cfm] | Split TS2 Furnace with DX Cooling OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 |  |  | 2021-05-06
CO_MA_Split TSE Furnace with DX Cooling OA Rate [cfm] | Split TSE Furnace with DX Cooling OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 |  |  | 2021-05-06
CO_MA_Split TSW Furnace with DX Cooling OA Rate [cfm] | Split TSW Furnace with DX Cooling OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 |  |  | 2021-05-06
CO_MA_SPLIT GSW HEATING COIL Heating Capacity [kBtu/hr] | SPLIT GSW HEATING COIL Heating Capacity [kBtu/hr] | 8.6725 | 8.7321 | 8.6051 | 8.665 | 8.9887 | 9.0491 | 9.3158 | 9.2013 |  |  | 2021-05-06
CO_MA_SPLIT GNW HEATING COIL Heating Capacity [kBtu/hr] | SPLIT GNW HEATING COIL Heating Capacity [kBtu/hr] | 8.584 | 8.6437 | 8.549 | 8.609 | 8.8716 | 8.9321 | 9.2296 | 9.1134 |  |  | 2021-05-06
CO_MA_SPLIT OFFICE HEATING COIL Heating Capacity [kBtu/hr] | SPLIT OFFICE HEATING COIL Heating Capacity [kBtu/hr] | 20.9205 | 21.0145 | 20.9034 | 21.0048 | 21.68 | 21.7753 | 22.2932 | 22.137 |  |  | 2021-05-06
CO_MA_SPLIT GNE HEATING COIL Heating Capacity [kBtu/hr] | SPLIT GNE HEATING COIL Heating Capacity [kBtu/hr] | 8.5623 | 8.622 | 8.5709 | 8.631 | 8.8849 | 8.9454 | 9.2411 | 9.1236 |  |  | 2021-05-06
CO_MA_SPLIT GN1 HEATING COIL Heating Capacity [kBtu/hr] | SPLIT GN1 HEATING COIL Heating Capacity [kBtu/hr] | 6.2196 | 6.2794 | 6.2368 | 6.2969 | 6.6164 | 6.677 | 6.9755 | 6.9188 |  |  | 2021-05-06
CO_MA_SPLIT GN2 HEATING COIL Heating Capacity [kBtu/hr] | SPLIT GN2 HEATING COIL Heating Capacity [kBtu/hr] | 6.2189 | 6.2788 | 6.2375 | 6.2976 | 6.6168 | 6.6774 | 6.9759 | 6.9191 |  |  | 2021-05-06
CO_MA_SPLIT GS1 HEATING COIL Heating Capacity [kBtu/hr] | SPLIT GS1 HEATING COIL Heating Capacity [kBtu/hr] | 6.2039 | 6.2635 | 6.1867 | 6.2467 | 6.6172 | 6.6776 | 6.9371 | 6.8819 |  |  | 2021-05-06
CO_MA_SPLIT GS2 HEATING COIL Heating Capacity [kBtu/hr] | SPLIT GS2 HEATING COIL Heating Capacity [kBtu/hr] | 6.7013 | 6.7625 | 6.6863 | 6.7479 | 7.1272 | 7.1892 | 7.4537 | 7.397 |  |  | 2021-05-06
CO_MA_SPLIT MSW HEATING COIL Heating Capacity [kBtu/hr] | SPLIT MSW HEATING COIL Heating Capacity [kBtu/hr] | 15.93 | 16.0576 | 15.3332 | 15.4614 | 14.2949 | 14.4269 | 14.427 | 14.205 |  |  | 2021-05-06
CO_MA_SPLIT MNW HEATING COIL Heating Capacity [kBtu/hr] | SPLIT MNW HEATING COIL Heating Capacity [kBtu/hr] | 15.9411 | 16.0687 | 15.4233 | 15.5513 | 14.2593 | 14.3908 | 14.4819 | 14.2549 |  |  | 2021-05-06
CO_MA_SPLIT MSE HEATING COIL Heating Capacity [kBtu/hr] | SPLIT MSE HEATING COIL Heating Capacity [kBtu/hr] | 15.8784 | 16.006 | 15.3854 | 15.5136 | 14.327 | 14.459 | 14.4549 | 14.2297 |  |  | 2021-05-06
CO_MA_SPLIT MNE HEATING COIL Heating Capacity [kBtu/hr] | SPLIT MNE HEATING COIL Heating Capacity [kBtu/hr] | 15.8895 | 16.0171 | 15.4755 | 15.6036 | 14.2914 | 14.423 | 14.5098 | 14.2796 |  |  | 2021-05-06
CO_MA_SPLIT MN1 HEATING COIL Heating Capacity [kBtu/hr] | SPLIT MN1 HEATING COIL Heating Capacity [kBtu/hr] | 10.8029 | 10.9295 | 10.5353 | 10.6619 | 10.519 | 10.519 | 10.8163 | 10.8163 |  |  | 2021-05-06
CO_MA_SPLIT MN2 HEATING COIL Heating Capacity [kBtu/hr] | SPLIT MN2 HEATING COIL Heating Capacity [kBtu/hr] | 10.8015 | 10.9281 | 10.5368 | 10.6634 | 10.519 | 10.519 | 10.8163 | 10.8163 |  |  | 2021-05-06
CO_MA_SPLIT MS1 HEATING COIL Heating Capacity [kBtu/hr] | SPLIT MS1 HEATING COIL Heating Capacity [kBtu/hr] | 10.8003 | 10.9269 | 10.4544 | 10.581 | 10.519 | 10.519 | 10.8163 | 10.8163 |  |  | 2021-05-06
CO_MA_SPLIT MS2 HEATING COIL Heating Capacity [kBtu/hr] | SPLIT MS2 HEATING COIL Heating Capacity [kBtu/hr] | 10.7989 | 10.9255 | 10.4559 | 10.5824 | 10.519 | 10.519 | 10.8163 | 10.8163 |  |  | 2021-05-06
CO_MA_SPLIT TSW HEATING COIL Heating Capacity [kBtu/hr] | SPLIT TSW HEATING COIL Heating Capacity [kBtu/hr] | 11.4454 | 11.5072 | 11.2113 | 11.2732 | 10.7729 | 10.8351 | 10.6938 | 10.5845 |  |  | 2021-05-06
CO_MA_SPLIT TNW HEATING COIL Heating Capacity [kBtu/hr] | SPLIT TNW HEATING COIL Heating Capacity [kBtu/hr] | 11.4572 | 11.519 | 11.2655 | 11.3275 | 10.7604 | 10.8227 | 10.7307 | 10.6192 |  |  | 2021-05-06
CO_MA_SPLIT TSE HEATING COIL Heating Capacity [kBtu/hr] | SPLIT TSE HEATING COIL Heating Capacity [kBtu/hr] | 11.4181 | 11.4799 | 11.2391 | 11.301 | 10.7903 | 10.8525 | 10.709 | 10.598 |  |  | 2021-05-06
CO_MA_SPLIT TNE HEATING COIL Heating Capacity [kBtu/hr] | SPLIT TNE HEATING COIL Heating Capacity [kBtu/hr] | 11.4298 | 11.4917 | 11.2932 | 11.3553 | 10.7779 | 10.8402 | 10.746 | 10.6328 |  |  | 2021-05-06
CO_MA_SPLIT TN1 HEATING COIL Heating Capacity [kBtu/hr] | SPLIT TN1 HEATING COIL Heating Capacity [kBtu/hr] | 8.7707 | 8.8326 | 8.7083 | 8.7702 | 8.6505 | 8.7128 | 8.672 | 8.6212 |  |  | 2021-05-06
CO_MA_SPLIT TN2 HEATING COIL Heating Capacity [kBtu/hr] | SPLIT TN2 HEATING COIL Heating Capacity [kBtu/hr] | 8.7699 | 8.8317 | 8.7091 | 8.7711 | 8.651 | 8.7133 | 8.6724 | 8.6216 |  |  | 2021-05-06
CO_MA_SPLIT TS1 HEATING COIL Heating Capacity [kBtu/hr] | SPLIT TS1 HEATING COIL Heating Capacity [kBtu/hr] | 8.7529 | 8.8146 | 8.6476 | 8.7095 | 8.6571 | 8.7193 | 8.6288 | 8.58 |  |  | 2021-05-06
CO_MA_SPLIT TS2 HEATING COIL Heating Capacity [kBtu/hr] | SPLIT TS2 HEATING COIL Heating Capacity [kBtu/hr] | 8.752 | 8.8138 | 8.6484 | 8.7103 | 8.6576 | 8.7198 | 8.6293 | 8.5804 |  |  | 2021-05-06
CO_MA_Split_GSW ERV Flag | Split_GSW ERV Flag | No | Yes | No | Yes | Yes | Yes | Yes | Yes |  |  | 2021-05-06
CO_MA_Split_GNW ERV Flag | Split_GNW ERV Flag | No | Yes | No | Yes | Yes | Yes | Yes | Yes |  |  | 2021-05-06
CO_MA_Split_GNE ERV Flag | Split_GNE ERV Flag | No | Yes | No | Yes | Yes | Yes | Yes | Yes |  |  | 2021-05-06
CO_MA_Split_GN1 ERV Flag | Split_GN1 ERV Flag | No | Yes | No | Yes | Yes | Yes | Yes | Yes |  |  | 2021-05-06
CO_MA_Split_GN2 ERV Flag | Split_GN2 ERV Flag | No | Yes | No | Yes | Yes | Yes | Yes | Yes |  |  | 2021-05-06
CO_MA_Split_GS1 ERV Flag | Split_GS1 ERV Flag | No | Yes | No | Yes | Yes | Yes | Yes | Yes |  |  | 2021-05-06
CO_MA_Split_GS2 ERV Flag | Split_GS2 ERV Flag | No | Yes | No | Yes | Yes | Yes | Yes | Yes |  |  | 2021-05-06
CO_MA_Split_MSW ERV Flag | Split_MSW ERV Flag | No | Yes | No | Yes | Yes | Yes | Yes | Yes |  |  | 2021-05-06
CO_MA_Split_MNW ERV Flag | Split_MNW ERV Flag | No | Yes | No | Yes | Yes | Yes | Yes | Yes |  |  | 2021-05-06
CO_MA_Split_MSE ERV Flag | Split_MSE ERV Flag | No | Yes | No | Yes | Yes | Yes | Yes | Yes |  |  | 2021-05-06
CO_MA_Split_MNE ERV Flag | Split_MNE ERV Flag | No | Yes | No | Yes | Yes | Yes | Yes | Yes |  |  | 2021-05-06
CO_MA_Split_MN1 ERV Flag | Split_MN1 ERV Flag | No | Yes | No | Yes | Yes | Yes | Yes | Yes |  |  | 2021-05-06
CO_MA_Split_MN2 ERV Flag | Split_MN2 ERV Flag | No | Yes | No | Yes | Yes | Yes | Yes | Yes |  |  | 2021-05-06
CO_MA_Split_MS1 ERV Flag | Split_MS1 ERV Flag | No | Yes | No | Yes | Yes | Yes | Yes | Yes |  |  | 2021-05-06
CO_MA_Split_MS2 ERV Flag | Split_MS2 ERV Flag | No | Yes | No | Yes | Yes | Yes | Yes | Yes |  |  | 2021-05-06
CO_MA_Split_TSW ERV Flag | Split_TSW ERV Flag | No | No | No | No | No | No | No | Yes |  |  | 2021-05-06
CO_MA_Split_TNW ERV Flag | Split_TNW ERV Flag | No | No | No | No | No | Yes | No | Yes |  |  | 2021-05-06
CO_MA_Split_TSE ERV Flag | Split_TSE ERV Flag | No | Yes | No | Yes | Yes | Yes | Yes | Yes |  |  | 2021-05-06
CO_MA_Split_TNE ERV Flag | Split_TNE ERV Flag | No | Yes | No | Yes | Yes | Yes | Yes | Yes |  |  | 2021-05-06
CO_MA_Split_TN1 ERV Flag | Split_TN1 ERV Flag | No | Yes | No | Yes | Yes | Yes | Yes | Yes |  |  | 2021-05-06
CO_MA_Split_TN2 ERV Flag | Split_TN2 ERV Flag | No | Yes | No | Yes | Yes | Yes | Yes | Yes |  |  | 2021-05-06
CO_MA_Split_TS1 ERV Flag | Split_TS1 ERV Flag | No | Yes | No | Yes | Yes | Yes | Yes | Yes |  |  | 2021-05-06
CO_MA_Split_TS2 ERV Flag | Split_TS2 ERV Flag | No | Yes | No | Yes | Yes | Yes | Yes | Yes |  |  | 2021-05-06
id | item | Zone5A(CT-HartfordBradley-CT) ASHRAE901-state_STD2016 | Zone5A(CT-HartfordBradley-CT) ASHRAE901-state_STD2019 | [8 empty] | 2021-05-06
CT_SO_PSZ-AC:1 Cooling Capacity [ton] | PSZ-AC:1 Cooling Capacity [ton] | 1.8077 | 1.7105 | [8 empty] | 2021-05-06
CT_SO_PSZ-AC:2 Cooling Capacity [ton] | PSZ-AC:2 Cooling Capacity [ton] | 1.5634 | 1.501 | [8 empty] | 2021-05-06
CT_SO_PSZ-AC:3 Cooling Capacity [ton] | PSZ-AC:3 Cooling Capacity [ton] | 1.0624 | 1.0246 | [8 empty] | 2021-05-06
CT_SO_PSZ-AC:4 Cooling Capacity [ton] | PSZ-AC:4 Cooling Capacity [ton] | 1.4914 | 1.4109 | [8 empty] | 2021-05-06
CT_SO_PSZ-AC:5 Cooling Capacity [ton] | PSZ-AC:5 Cooling Capacity [ton] | 1.2907 | 1.251 | [8 empty] | 2021-05-06
CT_SO_PSZ-AC:1 Supply Flow Rate [cfm] | PSZ-AC:1 Supply Flow Rate [cfm] | 635.664 | 593.2864 | [8 empty] | 2021-05-06
CT_SO_PSZ-AC:2 Supply Flow Rate [cfm] | PSZ-AC:2 Supply Flow Rate [cfm] | 572.0976 | 529.72 | [8 empty] | 2021-05-06
CT_SO_PSZ-AC:3 Supply Flow Rate [cfm] | PSZ-AC:3 Supply Flow Rate [cfm] | 444.9648 | 423.776 | [8 empty] | 2021-05-06
CT_SO_PSZ-AC:4 Supply Flow Rate [cfm] | PSZ-AC:4 Supply Flow Rate [cfm] | 529.72 | 508.5312 | [8 empty] | 2021-05-06
CT_SO_PSZ-AC:5 Supply Flow Rate [cfm] | PSZ-AC:5 Supply Flow Rate [cfm] | 529.72 | 508.5312 | [8 empty] | 2021-05-06
CT_SO_PSZ-AC:1 OA Rate [cfm] | PSZ-AC:1 OA Rate [cfm] | 136.9178 | 136.9178 | [8 empty] | 2021-05-06
CT_SO_PSZ-AC:2 OA Rate [cfm] | PSZ-AC:2 OA Rate [cfm] | 103.7925 | 103.7925 | [8 empty] | 2021-05-06
CT_SO_PSZ-AC:3 OA Rate [cfm] | PSZ-AC:3 OA Rate [cfm] | 61.5711 | 61.5711 | [8 empty] | 2021-05-06
CT_SO_PSZ-AC:4 OA Rate [cfm] | PSZ-AC:4 OA Rate [cfm] | 103.7925 | 103.7925 | [8 empty] | 2021-05-06
CT_SO_PSZ-AC:5 OA Rate [cfm] | PSZ-AC:5 OA Rate [cfm] | 61.5711 | 61.5711 | [8 empty] | 2021-05-06
CT_SO_PSZ-AC:1 heating Capacity [kBtu/hr] | PSZ-AC:1 heating Capacity [kBtu/hr] | 14.8555 | 14.8555 | [8 empty] | 2021-05-06
CT_SO_PSZ-AC:2 heating Capacity [kBtu/hr] | PSZ-AC:2 heating Capacity [kBtu/hr] | 19.8643 | 19.6445 | [8 empty] | 2021-05-06
CT_SO_PSZ-AC:3 heating Capacity [kBtu/hr] | PSZ-AC:3 heating Capacity [kBtu/hr] | 12.0814 | 11.9598 | [8 empty] | 2021-05-06
CT_SO_PSZ-AC:4 heating Capacity [kBtu/hr] | PSZ-AC:4 heating Capacity [kBtu/hr] | 19.7615 | 19.5741 | [8 empty] | 2021-05-06
CT_SO_PSZ-AC:5 heating Capacity [kBtu/hr] | PSZ-AC:5 heating Capacity [kBtu/hr] | 12.1333 | 12.0066 | [8 empty] | 2021-05-06
id | item | Zone5A(CT-HartfordBradley-CT) ASHRAE901-state_STD2016 | Zone5A(CT-HartfordBradley-CT) ASHRAE901-state_STD2019 | [8 empty] | 2021-05-06
CT_LO_CAV_BAS Supply Flow Rate [cfm] | CAV_BAS Supply Flow Rate [cfm] | 11632.6512 | 10763.9104 | [8 empty] | 2021-05-06
CT_LO_VAV_BOT WITH REHEAT Supply Flow Rate [cfm] | VAV_BOT WITH REHEAT Supply Flow Rate [cfm] | 19705.584 | 18794.4656 | [8 empty] | 2021-05-06
CT_LO_VAV_MID WITH REHEAT Supply Flow Rate [cfm] | VAV_MID WITH REHEAT Supply Flow Rate [cfm] | 183728.0851 | 174913.5443 | [8 empty] | 2021-05-06
CT_LO_VAV_TOP WITH REHEAT Supply Flow Rate [cfm] | VAV_TOP WITH REHEAT Supply Flow Rate [cfm] | 19366.5632 | 18582.5776 | [8 empty] | 2021-05-06
CT_LO_Supply Air Temp. Reset Flag | Supply Air Temp. Reset Flag | Yes | Yes | [8 empty] | 2021-05-06
CT_LO_CAV_BAS OA Rate [cfm] | CAV_BAS OA Rate [cfm] | 2542.8255 | 2542.8255 | [8 empty] | 2021-05-06
CT_LO_VAV_BOT WITH REHEAT OA Rate [cfm] | VAV_BOT WITH REHEAT OA Rate [cfm] | 5377.8022 | 4302.174 | [8 empty] | 2021-05-06
CT_LO_VAV_MID WITH REHEAT OA Rate [cfm] | VAV_MID WITH REHEAT OA Rate [cfm] | 53777.9373 | 43021.7396 | [8 empty] | 2021-05-06
CT_LO_VAV_TOP WITH REHEAT OA Rate [cfm] | VAV_TOP WITH REHEAT OA Rate [cfm] | 5377.8022 | 4302.174 | [8 empty] | 2021-05-06
CT_LO_AIRLOOP DATACENTER BASEMENT OA Rate [cfm] | AIRLOOP DATACENTER BASEMENT OA Rate [cfm] | 716.9654 | 716.9654 | [8 empty] | 2021-05-06
CT_LO_VAV_bot_WITH_REHEAT ERV Flag | VAV_bot_WITH_REHEAT ERV Flag | Yes | Yes | [8 empty] | 2021-05-06
CT_LO_VAV_mid_WITH_REHEAT ERV Flag | VAV_mid_WITH_REHEAT ERV Flag | Yes | Yes | [8 empty] | 2021-05-06
CT_LO_VAV_top_WITH_REHEAT ERV Flag | VAV_top_WITH_REHEAT ERV Flag | Yes | Yes | [8 empty] | 2021-05-06
CT_LO_COOLSYS1 CHILLER1 Capacity [ton] | COOLSYS1 CHILLER1 Capacity [ton] | 401.0401 | 363.3497 | [8 empty] | 2021-05-06
CT_LO_COOLSYS1 CHILLER2 Capacity [ton] | COOLSYS1 CHILLER2 Capacity [ton] | 401.0401 | 363.3497 | [8 empty] | 2021-05-06
CT_LO_TOWERWATERSYS COOLTOWER 1 Capacity [ton] | TOWERWATERSYS COOLTOWER 1 Capacity [ton] | 380.6572 | 344.886 | [8 empty] | 2021-05-06
CT_LO_TOWERWATERSYS COOLTOWER 2 Capacity [ton] | TOWERWATERSYS COOLTOWER 2 Capacity [ton] | 380.6572 | 344.886 | [8 empty] | 2021-05-06
CT_LO_HEATSYS1 BOILER Capacity [MMBTU/h] | HEATSYS1 BOILER Capacity [MMBTU/h] | 4564.4674 | 4031.0956 | [8 empty] | 2021-05-06
CT_LO_COOLSYS1 PUMP Flow Rate [gal/min] | COOLSYS1 PUMP Flow Rate [gal/min] | 0 | 0 | [8 empty] | 2021-05-06
CT_LO_COOLSYS1 CHILLER1 PUMP Flow Rate [gal/min] | COOLSYS1 CHILLER1 PUMP Flow Rate [gal/min] | 631.8763 | 572.3789 | [8 empty] | 2021-05-06
CT_LO_COOLSYS1 CHILLER2 PUMP Flow Rate [gal/min] | COOLSYS1 CHILLER2 PUMP Flow Rate [gal/min] | 631.8763 | 572.3789 | [8 empty] | 2021-05-06
CT_LO_COOLSYS1 PUMP SECONDARY Flow Rate [gal/min] | COOLSYS1 PUMP SECONDARY Flow Rate [gal/min] | 1263.7542 | 1144.7595 | [8 empty] | 2021-05-06
CT_LO_HEATSYS1 PUMP Flow Rate [gal/min] | HEATSYS1 PUMP Flow Rate [gal/min] | 936.9174 | 827.436 | [8 empty] | 2021-05-06
CT_LO_TOWERWATERSYS PUMP Flow Rate [gal/min] | TOWERWATERSYS PUMP Flow Rate [gal/min] | 2212.5466 | 2004.5904 | [8 empty] | 2021-05-06
CT_LO_PLANT CIRC PUMP Flow Rate [gal/min] | PLANT CIRC PUMP Flow Rate [gal/min] | 208.3192 | 207.4823 | [8 empty] | 2021-05-06
CT_LO_COOLSYS1 PUMP SECONDARY Pressure setpoint reset [yes,no] | COOLSYS1 PUMP SECONDARY Pressure setpoint reset [yes,no] | pump_ride_on_curve | pump_ride_on_curve | [8 empty] | 2021-05-06
CT_LO_COOLSYS1 CHILLER1 PUMP Pump Power [hp] | COOLSYS1 CHILLER1 PUMP Pump Power [hp] | 3.4088 | 3.0572 | [8 empty] | 2021-05-06
CT_LO_COOLSYS1 CHILLER2 PUMP Pump Power [hp] | COOLSYS1 CHILLER2 PUMP Pump Power [hp] | 3.4088 | 3.0572 | [8 empty] | 2021-05-06
CT_LO_COOLSYS1 PUMP SECONDARY Pump Power [hp] | COOLSYS1 PUMP SECONDARY Pump Power [hp] | 20.4525 | 18.3433 | [8 empty] | 2021-05-06
CT_LO_HEATSYS1 PUMP Pump Power [hp] | HEATSYS1 PUMP Pump Power [hp] | 20.252 | 17.7084 | [8 empty] | 2021-05-06
CT_LO_TOWERWATERSYS PUMP Pump Power [hp] | TOWERWATERSYS PUMP Pump Power [hp] | 39.6139 | 35.5356 | [8 empty] | 2021-05-06
CT_LO_PLANT CIRC PUMP Pump Power [hp] | PLANT CIRC PUMP Pump Power [hp] | 4.4952 | 4.4329 | [8 empty] | 2021-05-06
CT_LO_Datacenter PLANT CIRC PUMP Pump Power [hp] | Datacenter PLANT CIRC PUMP Pump Power [hp] | 4.4952 | 4.4329 | [8 empty] | 2021-05-06
CT_LO_ZN_VAV_BOXes_Max_Reheat_Water_Flow_GPM | ZN_VAV_BOXes_Max_Reheat_Water_Flow_GPM | 469.1063 | 451.6728 | [8 empty] | 2021-05-06
CT_LO_COOLSYS1 PUMP SECONDARY VSD | COOLSYS1 PUMP SECONDARY VSD | No | No | [8 empty] | 2021-05-06
CT_LO_HEATSYS1 PUMP VSD | HEATSYS1 PUMP VSD | No | No | [8 empty] | 2021-05-06
CT_LO_DATACENTER BASEMENT Cooling Capacity [ton] | DATACENTER BASEMENT Cooling Capacity [ton] | 121.6834 | 121.3225 | [8 empty] | 2021-05-06
CT_LO_DATACENTER BOT Cooling Capacity [ton] | DATACENTER BOT Cooling Capacity [ton] | 2.6754 | 2.6518 | [8 empty] | 2021-05-06
CT_LO_DATACENTER MID Cooling Capacity [ton] | DATACENTER MID Cooling Capacity [ton] | 25.6291 | 25.4208 | [8 empty] | 2021-05-06
CT_LO_DATACENTER TOP Cooling Capacity [ton] | DATACENTER TOP Cooling Capacity [ton] | 2.6105 | 2.5904 | [8 empty] | 2021-05-06
id | item | Zone5A(CT-HartfordBradley-CT) ASHRAE901-state_STD2016 | Zone5A(CT-HartfordBradley-CT) ASHRAE901-state_STD2019 | [8 empty] | 2021-05-06
CT_RS_PSZ-AC:1 Cooling Capacity [ton] | PSZ-AC:1 Cooling Capacity [ton] | 10.0174 | 9.6342 | [8 empty] | 2021-05-06
CT_RS_PSZ-AC:2 Cooling Capacity [ton] | PSZ-AC:2 Cooling Capacity [ton] | 47.6998 | 46.1141 | [8 empty] | 2021-05-06
CT_RS_PSZ-AC:3 Cooling Capacity [ton] | PSZ-AC:3 Cooling Capacity [ton] | 6.2514 | 6.0914 | [8 empty] | 2021-05-06
CT_RS_PSZ-AC:4 Cooling Capacity [ton] | PSZ-AC:4 Cooling Capacity [ton] | 5.0648 | 4.8958 | [8 empty] | 2021-05-06
CT_RS_PSZ-AC:1 Supply Flow Rate [cfm] | PSZ-AC:1 Supply Flow Rate [cfm] | 3898.7392 | 3602.096 | [8 empty] | 2021-05-06
CT_RS_PSZ-AC:2 Supply Flow Rate [cfm] | PSZ-AC:2 Supply Flow Rate [cfm] | 15234.7472 | 14429.5728 | [8 empty] | 2021-05-06
CT_RS_PSZ-AC:3 Supply Flow Rate [cfm] | PSZ-AC:3 Supply Flow Rate [cfm] | 2267.2016 | 2182.4464 | [8 empty] | 2021-05-06
CT_RS_PSZ-AC:4 Supply Flow Rate [cfm] | PSZ-AC:4 Supply Flow Rate [cfm] | 1716.2928 | 1652.7264 | [8 empty] | 2021-05-06
CT_RS_PSZ-AC:1 OA Rate [cfm] | PSZ-AC:1 OA Rate [cfm] | 490.669 | 490.669 | [8 empty] | 2021-05-06
CT_RS_PSZ-AC:2 OA Rate [cfm] | PSZ-AC:2 OA Rate [cfm] | 4005.1282 | 4005.1282 | [8 empty] | 2021-05-06
CT_RS_PSZ-AC:3 OA Rate [cfm] | PSZ-AC:3 OA Rate [cfm] | 377.3937 | 377.3937 | [8 empty] | 2021-05-06
CT_RS_PSZ-AC:4 OA Rate [cfm] | PSZ-AC:4 OA Rate [cfm] | 377.3937 | 377.3937 | [8 empty] | 2021-05-06
CT_RS_PSZ-AC:1 OA Damper [gravity, motorized] | PSZ-AC:1 OA Damper [gravity, motorized] | motorized | motorized | [8 empty] | 2021-05-06
CT_RS_PSZ-AC:2 OA Damper [gravity, motorized] | PSZ-AC:2 OA Damper [gravity, motorized] | motorized | motorized | [8 empty] | 2021-05-06
CT_RS_PSZ-AC:3 OA Damper [gravity, motorized] | PSZ-AC:3 OA Damper [gravity, motorized] | motorized | motorized | [8 empty] | 2021-05-06
CT_RS_PSZ-AC:4 OA Damper [gravity, motorized] | PSZ-AC:4 OA Damper [gravity, motorized] | motorized | motorized | [8 empty] | 2021-05-06
CT_RS_PSZ-AC:1 Heating Capacity [kBtu/hr] | PSZ-AC:1 Heating Capacity [kBtu/hr] | 177.1894 | 165.6297 | [8 empty] | 2021-05-06
CT_RS_PSZ-AC:2 Heating Capacity [kBtu/hr] | PSZ-AC:2 Heating Capacity [kBtu/hr] | 833.8607 | 799.543 | [8 empty] | 2021-05-06
CT_RS_PSZ-AC:3 Heating Capacity [kBtu/hr] | PSZ-AC:3 Heating Capacity [kBtu/hr] | 110.3618 | 107.657 | [8 empty] | 2021-05-06
CT_RS_PSZ-AC:4 Heating Capacity [kBtu/hr] | PSZ-AC:4 Heating Capacity [kBtu/hr] | 90.1383 | 87.031 | [8 empty] | 2021-05-06
id | item | Zone5A(CT-HartfordBradley-CT) ASHRAE901-state_STD2016 | Zone5A(CT-HartfordBradley-CT) ASHRAE901-state_STD2019 | [8 empty] | 2021-05-06
CT_PS_VAV_POD_1 Cooling Capacity [ton] | VAV_POD_1 Cooling Capacity [ton] | 19.0903 | 18.43 | [8 empty] | 2021-05-06
CT_PS_VAV_POD_2 Cooling Capacity [ton] | VAV_POD_2 Cooling Capacity [ton] | 18.8243 | 18.3788 | [8 empty] | 2021-05-06
CT_PS_VAV_POD_3 Cooling Capacity [ton] | VAV_POD_3 Cooling Capacity [ton] | 17.3615 | 16.5527 | [8 empty] | 2021-05-06
CT_PS_VAV_OTHER Cooling Capacity [ton] | VAV_OTHER Cooling Capacity [ton] | 26.4536 | 24.8862 | [8 empty] | 2021-05-06
CT_PS_PSZ-AC_1:6 Cooling Capacity [ton] | PSZ-AC_1:6 Cooling Capacity [ton] | 8.145 | 7.8819 | [8 empty] | 2021-05-06
CT_PS_PSZ-AC_2:5 Cooling Capacity [ton] | PSZ-AC_2:5 Cooling Capacity [ton] | 5.3948 | 5.3686 | [8 empty] | 2021-05-06
CT_PS_PSZ-AC_2:7 Cooling Capacity [ton] | PSZ-AC_2:7 Cooling Capacity [ton] | 10.5074 | 10.5074 | [8 empty] | 2021-05-06
CT_PS_VAV_POD_1 Supply Flow Rate [cfm] | VAV_POD_1 Supply Flow Rate [cfm] | 5720.976 | 5530.2768 | [8 empty] | 2021-05-06
CT_PS_VAV_POD_2 Supply Flow Rate [cfm] | VAV_POD_2 Supply Flow Rate [cfm] | 5657.4096 | 5509.088 | [8 empty] | 2021-05-06
CT_PS_VAV_POD_3 Supply Flow Rate [cfm] | VAV_POD_3 Supply Flow Rate [cfm] | 5212.4448 | 4958.1792 | [8 empty] | 2021-05-06
CT_PS_VAV_OTHER Supply Flow Rate [cfm] | VAV_OTHER Supply Flow Rate [cfm] | 7945.8 | 7458.4576 | [8 empty] | 2021-05-06
CT_PS_PSZ-AC_2:5 Supply Flow Rate [cfm] | PSZ-AC_2:5 Supply Flow Rate [cfm] | 1610.3488 | 1610.3488 | [8 empty] | 2021-05-06
CT_PS_PSZ-AC_1:6 Supply Flow Rate [cfm] | PSZ-AC_1:6 Supply Flow Rate [cfm] | 2542.656 | 2436.712 | [8 empty] | 2021-05-06
CT_PS_PSZ-AC_2:7 Supply Flow Rate [cfm] | PSZ-AC_2:7 Supply Flow Rate [cfm] | 3157.1312 | 3157.1312 | [8 empty] | 2021-05-06
CT_PS_Supply Air Temp. Reset Flag | Supply Air Temp. Reset Flag | Yes | Yes | [8 empty] | 2021-05-06
CT_PS_VAV_POD_1 OA Rate [cfm] | VAV_POD_1 OA Rate [cfm] | 5726.4003 | 5530.5311 | [8 empty] | 2021-05-06
CT_PS_VAV_POD_2 OA Rate [cfm] | VAV_POD_2 OA Rate [cfm] | 5648.8493 | 5515.1904 | [8 empty] | 2021-05-06
CT_PS_VAV_POD_3 OA Rate [cfm] | VAV_POD_3 OA Rate [cfm] | 5209.9233 | 4967.1844 | [8 empty] | 2021-05-06
CT_PS_VAV_OTHER OA Rate [cfm] | VAV_OTHER OA Rate [cfm] | 3736.1787 | 2988.8921 | [8 empty] | 2021-05-06
CT_PS_PSZ-AC_2:5 OA Rate [cfm] | PSZ-AC_2:5 OA Rate [cfm] | 1152.7343 | 1152.7343 | [8 empty] | 2021-05-06
CT_PS_PSZ-AC_1:6 OA Rate [cfm] | PSZ-AC_1:6 OA Rate [cfm] | 539.9118 | 539.9118 | [8 empty] | 2021-05-06
CT_PS_PSZ-AC_2:7 OA Rate [cfm] | PSZ-AC_2:7 OA Rate [cfm] | 3153.0841 | 3153.0841 | [8 empty] | 2021-05-06
CT_PS_VAV_POD_1 OA Damper [gravity, motorized] | VAV_POD_1 OA Damper [gravity, motorized] | motorized | motorized | [8 empty] | 2021-05-06
CT_PS_VAV_POD_2 OA Damper [gravity, motorized] | VAV_POD_2 OA Damper [gravity, motorized] | motorized | motorized | [8 empty] | 2021-05-06
CT_PS_VAV_POD_3 OA Damper [gravity, motorized] | VAV_POD_3 OA Damper [gravity, motorized] | motorized | motorized | [8 empty] | 2021-05-06
CT_PS_VAV_OTHER OA Damper [gravity, motorized] | VAV_OTHER OA Damper [gravity, motorized] | motorized | motorized | [8 empty] | 2021-05-06
CT_PS_PSZ-AC_2:5 OA Damper [gravity, motorized] | PSZ-AC_2:5 OA Damper [gravity, motorized] | motorized | motorized | [8 empty] | 2021-05-06
CT_PS_PSZ-AC_1:6 OA Damper [gravity, motorized] | PSZ-AC_1:6 OA Damper [gravity, motorized] | motorized | motorized | [8 empty] | 2021-05-06
CT_PS_PSZ-AC_2:7 OA Damper [gravity, motorized] | PSZ-AC_2:7 OA Damper [gravity, motorized] | motorized | motorized | [8 empty] | 2021-05-06
CT_PS_VAV_POD_1 (economizer) | VAV_POD_1 (economizer) | DifferentialDryBulb | DifferentialDryBulb | [8 empty] | 2021-05-06
CT_PS_VAV_POD_2 (economizer) | VAV_POD_2 (economizer) | DifferentialDryBulb | DifferentialDryBulb | [8 empty] | 2021-05-06
CT_PS_VAV_POD_3 (economizer) | VAV_POD_3 (economizer) | DifferentialDryBulb | DifferentialDryBulb | [8 empty] | 2021-05-06
CT_PS_VAV_OTHER (economizer) | VAV_OTHER (economizer) | DifferentialDryBulb | DifferentialDryBulb | [8 empty] | 2021-05-06
CT_PS_PSZ-AC_2:5 (economizer) | PSZ-AC_2:5 (economizer) | DifferentialDryBulb | DifferentialDryBulb | [8 empty] | 2021-05-06
CT_PS_PSZ-AC_1:6 (economizer) | PSZ-AC_1:6 (economizer) | DifferentialDryBulb | DifferentialDryBulb | [8 empty] | 2021-05-06
CT_PS_PSZ-AC_2:7 (economizer) | PSZ-AC_2:7 (economizer) | DifferentialDryBulb | DifferentialDryBulb | [8 empty] | 2021-05-06
CT_PS_VAV_Pod_1_ERV Flag | VAV_Pod_1_ERV Flag | Yes | Yes | [8 empty] | 2021-05-06
CT_PS_VAV_Pod_2_ERV Flag | VAV_Pod_2_ERV Flag | Yes | Yes | [8 empty] | 2021-05-06
CT_PS_VAV_Pod_3_ERV Flag | VAV_Pod_3_ERV Flag | Yes | Yes | [8 empty] | 2021-05-06
CT_PS_VAV_OTHER_ERV Flag | VAV_OTHER_ERV Flag | Yes | Yes | [8 empty] | 2021-05-06
CT_PS_PSZ_AC_2_5_ERV Flag | PSZ_AC_2_5_ERV Flag | Yes | Yes | [8 empty] | 2021-05-06
CT_PS_PSZ_AC_2_7_ERV Flag | PSZ_AC_2_7_ERV Flag | Yes | Yes | [8 empty] | 2021-05-06
CT_PS_HEATSYS1 Capacity [MMBTU/h] | HEATSYS1 Capacity [MMBTU/h] | 1.1123 | 1.0664 | [8 empty] | 2021-05-06
CT_PS_HEATSYS1 Flow Rate [gal/min] | HEATSYS1 Flow Rate [gal/min] | 114.1521 | 109.4506 | [8 empty] | 2021-05-06
CT_PS_VAV_POD_1 Fan Power [hp] | VAV_POD_1 Fan Power [hp] | 8.4515 | 8.1592 | [8 empty] | 2021-05-06
CT_PS_VAV_POD_2 Fan Power [hp] | VAV_POD_2 Fan Power [hp] | 8.3338 | 8.1366 | [8 empty] | 2021-05-06
CT_PS_VAV_POD_3 Fan Power [hp] | VAV_POD_3 Fan Power [hp] | 7.6862 | 7.3281 | [8 empty] | 2021-05-06
CT_PS_VAV_OTHER Fan Power [hp] | VAV_OTHER Fan Power [hp] | 11.6226 | 10.934 | [8 empty] | 2021-05-06
CT_PS_HEATSYS1 Pump Power [hp] | HEATSYS1 Pump Power [hp] | 2.4675 | 2.3424 | [8 empty] | 2021-05-06
CT_PS_PSZ-AC_1:6 Heating Capacity [kBtu/hr] | PSZ-AC_1:6 Heating Capacity [kBtu/hr] | 213.7474 | 205.1657 | [8 empty] | 2021-05-06
CT_PS_PSZ-AC_2:5 Heating Capacity [kBtu/hr] | PSZ-AC_2:5 Heating Capacity [kBtu/hr] | 142.2317 | 141.9426 | [8 empty] | 2021-05-06
CT_PS_PSZ-AC_2:7 Heating Capacity [kBtu/hr] | PSZ-AC_2:7 Heating Capacity [kBtu/hr] | 342.1082 | 342.1082 | [8 empty] | 2021-05-06
CT_PS_ZN_VAV_BOXes_Max_Reheat_Water_Flow_GPM | ZN_VAV_BOXes_Max_Reheat_Water_Flow_GPM | 72.016 | 69.1094 | [8 empty] | 2021-05-06
id | item | Zone5A(CT-HartfordBradley-CT) ASHRAE901-state_STD2016 | Zone5A(CT-HartfordBradley-CT) ASHRAE901-state_STD2019 | [8 empty] | 2021-05-06
CT_SH_SAC_FRONTOFFICE Cooling Capacity [ton] | SAC_FRONTOFFICE Cooling Capacity [ton] | 2.2513 | 2.1405 | [8 empty] | 2021-05-06
CT_SH_SAC_FRONTLOUNGE Cooling Capacity [ton] | SAC_FRONTLOUNGE Cooling Capacity [ton] | 6.0031 | 5.6994 | [8 empty] | 2021-05-06
CT_SH_SAC_MEETINGROOM Cooling Capacity [ton] | SAC_MEETINGROOM Cooling Capacity [ton] | 2.8521 | 2.7702 | [8 empty] | 2021-05-06
CT_SH_SAC_EXC_EMPLGE_RESTRM Cooling Capacity [ton] | SAC_EXC_EMPLGE_RESTRM Cooling Capacity [ton] | 5.867 | 5.826 | [8 empty] | 2021-05-06
CT_SH_SAC_FO_ADDAQ SUPPLY FAN Supply Flow Rate [cfm] | SAC_FO_ADDAQ SUPPLY FAN Supply Flow Rate [cfm] | 762.7968 | 720.4192 | [8 empty] | 2021-05-06
CT_SH_SAC_FL_ADDAQ SUPPLY FAN Supply Flow Rate [cfm] | SAC_FL_ADDAQ SUPPLY FAN Supply Flow Rate [cfm] | 1801.048 | 1716.2928 | [8 empty] | 2021-05-06
CT_SH_SAC_MR_ADDAQ SUPPLY FAN Supply Flow Rate [cfm] | SAC_MR_ADDAQ SUPPLY FAN Supply Flow Rate [cfm] | 847.552 | 826.3632 | [8 empty] | 2021-05-06
CT_SH_SAC_EXC_ADDAQ SUPPLY FAN Supply Flow Rate [cfm] | SAC_EXC_ADDAQ SUPPLY FAN Supply Flow Rate [cfm] | 2182.4464 | 2161.2576 | [8 empty] | 2021-05-06
CT_SH_SAC_Exc_EmpLge_RestRm OA Rate [cfm] | SAC_Exc_EmpLge_RestRm OA Rate [cfm] | 199.9928 | 199.9928 | [8 empty] | 2021-05-06
CT_SH_SAC_FrontLounge OA Rate [cfm] | SAC_FrontLounge OA Rate [cfm] | 500.0133 | 500.0133 | [8 empty] | 2021-05-06
CT_SH_SAC_FrontOffice OA Rate [cfm] | SAC_FrontOffice OA Rate [cfm] | 119.2938 | 119.2938 | [8 empty] | 2021-05-06
CT_SH_SAC_MeetingRoom OA Rate [cfm] | SAC_MeetingRoom OA Rate [cfm] | 267.7629 | 267.7629 | [8 empty] | 2021-05-06
CT_SH_SAC_FrontLounge OA Damper [gravity, motorized] | SAC_FrontLounge OA Damper [gravity, motorized] | motorized | motorized | [8 empty] | 2021-05-06
CT_SH_SAC_FrontOffice (economizer) | SAC_FrontOffice (economizer) | No | No | [8 empty] | 2021-05-06
CT_SH_SAC_FrontLounge (economizer) | SAC_FrontLounge (economizer) | DifferentialDryBulb | DifferentialDryBulb | [8 empty] | 2021-05-06
CT_SH_SAC_MeetingRoom (economizer) | SAC_MeetingRoom (economizer) | No | No | [8 empty] | 2021-05-06
CT_SH_SAC_Exc_EmpLge_RestRm (economizer) | SAC_Exc_EmpLge_RestRm (economizer) | DifferentialDryBulb | DifferentialDryBulb | [8 empty] | 2021-05-06
CT_SH_SAC_FRONTOFFICE Heating Capacity [kBtu/hr] | SAC_FRONTOFFICE Heating Capacity [kBtu/hr] | 36.4085 | 34.6368 | [8 empty] | 2021-05-06
CT_SH_SAC_FRONTLOUNGE Heating Capacity [kBtu/hr] | SAC_FRONTLOUNGE Heating Capacity [kBtu/hr] | 101.8795 | 98.5447 | [8 empty] | 2021-05-06
CT_SH_SAC_MEETINGROOM Heating Capacity [kBtu/hr] | SAC_MEETINGROOM Heating Capacity [kBtu/hr] | 50.5747 | 49.6753 | [8 empty] | 2021-05-06
CT_SH_SAC_EXC_EMPLGE_RESTRM Heating Capacity [kBtu/hr] | SAC_EXC_EMPLGE_RESTRM Heating Capacity [kBtu/hr] | 94.0392 | 93.3801 | [8 empty] | 2021-05-06
id | item | Zone5A(CT-HartfordBradley-CT) ASHRAE901-state_STD2016 | Zone5A(CT-HartfordBradley-CT) ASHRAE901-state_STD2019 | [8 empty] | 2021-05-06
CT_MA_SPLIT GSW COOLING COIL Cooling Capacity [ton] | SPLIT GSW COOLING COIL Cooling Capacity [ton] | 0.81849 | 0.80226 | [8 empty] | 2021-05-06
CT_MA_SPLIT GNW COOLING COIL Cooling Capacity [ton] | SPLIT GNW COOLING COIL Cooling Capacity [ton] | 0.77595 | 0.76238 | [8 empty] | 2021-05-06
CT_MA_SPLIT OFFICE COOLING COIL Cooling Capacity [ton] | SPLIT OFFICE COOLING COIL Cooling Capacity [ton] | 1.7003 | 1.5718 | [8 empty] | 2021-05-06
CT_MA_SPLIT GNE COOLING COIL Cooling Capacity [ton] | SPLIT GNE COOLING COIL Cooling Capacity [ton] | 0.67235 | 0.66053 | [8 empty] | 2021-05-06
CT_MA_SPLIT GN1 COOLING COIL Cooling Capacity [ton] | SPLIT GN1 COOLING COIL Cooling Capacity [ton] | 0.57023 | 0.56119 | [8 empty] | 2021-05-06
CT_MA_SPLIT GN2 COOLING COIL Cooling Capacity [ton] | SPLIT GN2 COOLING COIL Cooling Capacity [ton] | 0.56816 | 0.55917 | [8 empty] | 2021-05-06
CT_MA_SPLIT GS1 COOLING COIL Cooling Capacity [ton] | SPLIT GS1 COOLING COIL Cooling Capacity [ton] | 0.61847 | 0.60805 | [8 empty] | 2021-05-06
CT_MA_SPLIT GS2 COOLING COIL Cooling Capacity [ton] | SPLIT GS2 COOLING COIL Cooling Capacity [ton] | 0.64963 | 0.63425 | [8 empty] | 2021-05-06
CT_MA_SPLIT MSW COOLING COIL Cooling Capacity [ton] | SPLIT MSW COOLING COIL Cooling Capacity [ton] | 1.9935 | 1.9616 | [8 empty] | 2021-05-06
CT_MA_SPLIT MNW COOLING COIL Cooling Capacity [ton] | SPLIT MNW COOLING COIL Cooling Capacity [ton] | 1.9144 | 1.8796 | [8 empty] | 2021-05-06
CT_MA_SPLIT MSE COOLING COIL Cooling Capacity [ton] | SPLIT MSE COOLING COIL Cooling Capacity [ton] | 1.7383 | 1.7103 | [8 empty] | 2021-05-06
CT_MA_SPLIT MNE COOLING COIL Cooling Capacity [ton] | SPLIT MNE COOLING COIL Cooling Capacity [ton] | 1.5341 | 1.505 | [8 empty] | 2021-05-06
CT_MA_SPLIT MN1 COOLING COIL Cooling Capacity [ton] | SPLIT MN1 COOLING COIL Cooling Capacity [ton] | 1.2828 | 1.2606 | [8 empty] | 2021-05-06
CT_MA_SPLIT MN2 COOLING COIL Cooling Capacity [ton] | SPLIT MN2 COOLING COIL Cooling Capacity [ton] | 1.2722 | 1.255 | [8 empty] | 2021-05-06
CT_MA_SPLIT MS1 COOLING COIL Cooling Capacity [ton] | SPLIT MS1 COOLING COIL Cooling Capacity [ton] | 1.3664 | 1.3469 | [8 empty] | 2021-05-06
CT_MA_SPLIT MS2 COOLING COIL Cooling Capacity [ton] | SPLIT MS2 COOLING COIL Cooling Capacity [ton] | 1.3605 | 1.3412 | [8 empty] | 2021-05-06
CT_MA_SPLIT TSW COOLING COIL Cooling Capacity [ton] | SPLIT TSW COOLING COIL Cooling Capacity [ton] | 1.2519 | 1.2346 | [8 empty] | 2021-05-06
CT_MA_SPLIT TNW COOLING COIL Cooling Capacity [ton] | SPLIT TNW COOLING COIL Cooling Capacity [ton] | 1.1943 | 1.1779 | [8 empty] | 2021-05-06
CT_MA_SPLIT TSE COOLING COIL Cooling Capacity [ton] | SPLIT TSE COOLING COIL Cooling Capacity [ton] | 1.1161 | 1.1029 | [8 empty] | 2021-05-06
CT_MA_SPLIT TNE COOLING COIL Cooling Capacity [ton] | SPLIT TNE COOLING COIL Cooling Capacity [ton] | 1.0332 | 1.0206 | [8 empty] | 2021-05-06
CT_MA_SPLIT TN1 COOLING COIL Cooling Capacity [ton] | SPLIT TN1 COOLING COIL Cooling Capacity [ton] | 0.84525 | 0.83541 | [8 empty] | 2021-05-06
CT_MA_SPLIT TN2 COOLING COIL Cooling Capacity [ton] | SPLIT TN2 COOLING COIL Cooling Capacity [ton] | 0.8465 | 0.83672 | [8 empty] | 2021-05-06
CT_MA_SPLIT TS1 COOLING COIL Cooling Capacity [ton] | SPLIT TS1 COOLING COIL Cooling Capacity [ton] | 0.92654 | 0.91516 | [8 empty] | 2021-05-06
CT_MA_SPLIT TS2 COOLING COIL Cooling Capacity [ton] | SPLIT TS2 COOLING COIL Cooling Capacity [ton] | 0.92894 | 0.91753 | [8 empty] | 2021-05-06
CT_MA_Split GN1 Furnace with DX Cooling OA Rate [cfm] | Split GN1 Furnace with DX Cooling OA Rate [cfm] | 54.9913 | 54.9913 | [8 empty] | 2021-05-06
CT_MA_Split GN2 Furnace with DX Cooling OA Rate [cfm] | Split GN2 Furnace with DX Cooling OA Rate [cfm] | 54.9913 | 54.9913 | [8 empty] | 2021-05-06
CT_MA_Split GNE Furnace with DX Cooling OA Rate [cfm] | Split GNE Furnace with DX Cooling OA Rate [cfm] | 54.9913 | 54.9913 | [8 empty] | 2021-05-06
CT_MA_Split GNW Furnace with DX Cooling OA Rate [cfm] | Split GNW Furnace with DX Cooling OA Rate [cfm] | 54.9913 | 54.9913 | [8 empty] | 2021-05-06
CT_MA_Split GS1 Furnace with DX Cooling OA Rate [cfm] | Split GS1 Furnace with DX Cooling OA Rate [cfm] | 54.9913 | 54.9913 | [8 empty] | 2021-05-06
CT_MA_Split GS2 Furnace with DX Cooling OA Rate [cfm] | Split GS2 Furnace with DX Cooling OA Rate [cfm] | 54.9913 | 54.9913 | [8 empty] | 2021-05-06
CT_MA_Split GSW Furnace with DX Cooling OA Rate [cfm] | Split GSW Furnace with DX Cooling OA Rate [cfm] | 56.9945 | 56.9945 | [8 empty] | 2021-05-06
CT_MA_Split MN1 Furnace with DX Cooling OA Rate [cfm] | Split MN1 Furnace with DX Cooling OA Rate [cfm] | 109.9824 | 109.9824 | [8 empty] | 2021-05-06
CT_MA_Split MN2 Furnace with DX Cooling OA Rate [cfm] | Split MN2 Furnace with DX Cooling OA Rate [cfm] | 109.9824 | 109.9824 | [8 empty] | 2021-05-06
CT_MA_Split MNE Furnace with DX Cooling OA Rate [cfm] | Split MNE Furnace with DX Cooling OA Rate [cfm] | 109.9824 | 109.9824 | [8 empty] | 2021-05-06
CT_MA_Split MNW Furnace with DX Cooling OA Rate [cfm] | Split MNW Furnace with DX Cooling OA Rate [cfm] | 109.9824 | 109.9824 | [8 empty] | 2021-05-06
CT_MA_Split MS1 Furnace with DX Cooling OA Rate [cfm] | Split MS1 Furnace with DX Cooling OA Rate [cfm] | 109.9824 | 109.9824 | [8 empty] | 2021-05-06
CT_MA_Split MS2 Furnace with DX Cooling OA Rate [cfm] | Split MS2 Furnace with DX Cooling OA Rate [cfm] | 109.9824 | 109.9824 | [8 empty] | 2021-05-06
CT_MA_Split MSE Furnace with DX Cooling OA Rate [cfm] | Split MSE Furnace with DX Cooling OA Rate [cfm] | 109.9824 | 109.9824 | [8 empty] | 2021-05-06
CT_MA_Split MSW Furnace with DX Cooling OA Rate [cfm] | Split MSW Furnace with DX Cooling OA Rate [cfm] | 109.9824 | 109.9824 | [8 empty] | 2021-05-06
CT_MA_Split Office Furnace with DX Cooling OA Rate [cfm] | Split Office Furnace with DX Cooling OA Rate [cfm] | 80.7372 | 80.7372 | [8 empty] | 2021-05-06
CT_MA_Split TN1 Furnace with DX Cooling OA Rate [cfm] | Split TN1 Furnace with DX Cooling OA Rate [cfm] | 54.9913 | 54.9913 | [8 empty] | 2021-05-06
CT_MA_Split TN2 Furnace with DX Cooling OA Rate [cfm] | Split TN2 Furnace with DX Cooling OA Rate [cfm] | 54.9913 | 54.9913 | [8 empty] | 2021-05-06
CT_MA_Split TNE Furnace with DX Cooling OA Rate [cfm] | Split TNE Furnace with DX Cooling OA Rate [cfm] | 54.9913 | 54.9913 | [8 empty] | 2021-05-06
CT_MA_Split TNW Furnace with DX Cooling OA Rate [cfm] | Split TNW Furnace with DX Cooling OA Rate [cfm] | 54.9913 | 54.9913 | [8 empty] | 2021-05-06
CT_MA_Split TS1 Furnace with DX Cooling OA Rate [cfm] | Split TS1 Furnace with DX Cooling OA Rate [cfm] | 54.9913 | 54.9913 | [8 empty] | 2021-05-06
CT_MA_Split TS2 Furnace with DX Cooling OA Rate [cfm] | Split TS2 Furnace with DX Cooling OA Rate [cfm] | 54.9913 | 54.9913 | [8 empty] | 2021-05-06
CT_MA_Split TSE Furnace with DX Cooling OA Rate [cfm] | Split TSE Furnace with DX Cooling OA Rate [cfm] | 54.9913 | 54.9913 | [8 empty] | 2021-05-06
CT_MA_Split TSW Furnace with DX Cooling OA Rate [cfm] | Split TSW Furnace with DX Cooling OA Rate [cfm] | 54.9913 | 54.9913 | [8 empty] | 2021-05-06
CT_MA_SPLIT GSW HEATING COIL Heating Capacity [kBtu/hr] | SPLIT GSW HEATING COIL Heating Capacity [kBtu/hr] | 9.7657 | 9.8246 | [8 empty] | 2021-05-06
CT_MA_SPLIT GNW HEATING COIL Heating Capacity [kBtu/hr] | SPLIT GNW HEATING COIL Heating Capacity [kBtu/hr] | 9.6893 | 9.7483 | [8 empty] | 2021-05-06
CT_MA_SPLIT OFFICE HEATING COIL Heating Capacity [kBtu/hr] | SPLIT OFFICE HEATING COIL Heating Capacity [kBtu/hr] | 22.6634 | 22.7483 | [8 empty] | 2021-05-06
CT_MA_SPLIT GNE HEATING COIL Heating Capacity [kBtu/hr] | SPLIT GNE HEATING COIL Heating Capacity [kBtu/hr] | 9.6676 | 9.7266 | [8 empty] | 2021-05-06
CT_MA_SPLIT GN1 HEATING COIL Heating Capacity [kBtu/hr] | SPLIT GN1 HEATING COIL Heating Capacity [kBtu/hr] | 7.1978 | 7.2568 | [8 empty] | 2021-05-06
CT_MA_SPLIT GN2 HEATING COIL Heating Capacity [kBtu/hr] | SPLIT GN2 HEATING COIL Heating Capacity [kBtu/hr] | 7.1971 | 7.2562 | [8 empty] | 2021-05-06
CT_MA_SPLIT GS1 HEATING COIL Heating Capacity [kBtu/hr] | SPLIT GS1 HEATING COIL Heating Capacity [kBtu/hr] | 7.1463 | 7.2052 | [8 empty] | 2021-05-06
CT_MA_SPLIT GS2 HEATING COIL Heating Capacity [kBtu/hr] | SPLIT GS2 HEATING COIL Heating Capacity [kBtu/hr] | 7.6502 | 7.7102 | [8 empty] | 2021-05-06
CT_MA_SPLIT MSW HEATING COIL Heating Capacity [kBtu/hr] | SPLIT MSW HEATING COIL Heating Capacity [kBtu/hr] | 17.0427 | 17.1715 | [8 empty] | 2021-05-06
CT_MA_SPLIT MNW HEATING COIL Heating Capacity [kBtu/hr] | SPLIT MNW HEATING COIL Heating Capacity [kBtu/hr] | 17.1312 | 17.2601 | [8 empty] | 2021-05-06
CT_MA_SPLIT MSE HEATING COIL Heating Capacity [kBtu/hr] | SPLIT MSE HEATING COIL Heating Capacity [kBtu/hr] | 16.9912 | 17.12 | [8 empty] | 2021-05-06
CT_MA_SPLIT MNE HEATING COIL Heating Capacity [kBtu/hr] | SPLIT MNE HEATING COIL Heating Capacity [kBtu/hr] | 17.0797 | 17.2086 | [8 empty] | 2021-05-06
CT_MA_SPLIT MN1 HEATING COIL Heating Capacity [kBtu/hr] | SPLIT MN1 HEATING COIL Heating Capacity [kBtu/hr] | 11.9914 | 12.1171 | [8 empty] | 2021-05-06
CT_MA_SPLIT MN2 HEATING COIL Heating Capacity [kBtu/hr] | SPLIT MN2 HEATING COIL Heating Capacity [kBtu/hr] | 11.99 | 12.1158 | [8 empty] | 2021-05-06
CT_MA_SPLIT MS1 HEATING COIL Heating Capacity [kBtu/hr] | SPLIT MS1 HEATING COIL Heating Capacity [kBtu/hr] | 11.933 | 12.0376 | [8 empty] | 2021-05-06
CT_MA_SPLIT MS2 HEATING COIL Heating Capacity [kBtu/hr] | SPLIT MS2 HEATING COIL Heating Capacity [kBtu/hr] | 11.933 | 12.0362 | [8 empty] | 2021-05-06
CT_MA_SPLIT TSW HEATING COIL Heating Capacity [kBtu/hr] | SPLIT TSW HEATING COIL Heating Capacity [kBtu/hr] | 12.0729 | 12.1348 | [8 empty] | 2021-05-06
CT_MA_SPLIT TNW HEATING COIL Heating Capacity [kBtu/hr] | SPLIT TNW HEATING COIL Heating Capacity [kBtu/hr] | 12.1263 | 12.1883 | [8 empty] | 2021-05-06
CT_MA_SPLIT TSE HEATING COIL Heating Capacity [kBtu/hr] | SPLIT TSE HEATING COIL Heating Capacity [kBtu/hr] | 12.0456 | 12.1074 | [8 empty] | 2021-05-06
CT_MA_SPLIT TNE HEATING COIL Heating Capacity [kBtu/hr] | SPLIT TNE HEATING COIL Heating Capacity [kBtu/hr] | 12.099 | 12.1609 | [8 empty] | 2021-05-06
CT_MA_SPLIT TN1 HEATING COIL Heating Capacity [kBtu/hr] | SPLIT TN1 HEATING COIL Heating Capacity [kBtu/hr] | 9.3723 | 9.4341 | [8 empty] | 2021-05-06
CT_MA_SPLIT TN2 HEATING COIL Heating Capacity [kBtu/hr] | SPLIT TN2 HEATING COIL Heating Capacity [kBtu/hr] | 9.3715 | 9.4333 | [8 empty] | 2021-05-06
CT_MA_SPLIT TS1 HEATING COIL Heating Capacity [kBtu/hr] | SPLIT TS1 HEATING COIL Heating Capacity [kBtu/hr] | 9.312 | 9.3738 | [8 empty] | 2021-05-06
CT_MA_SPLIT TS2 HEATING COIL Heating Capacity [kBtu/hr] | SPLIT TS2 HEATING COIL Heating Capacity [kBtu/hr] | 9.3112 | 9.373 | [8 empty] | 2021-05-06
CT_MA_Split_GSW ERV Flag | Split_GSW ERV Flag | Yes | Yes | [8 empty] | 2021-05-06
CT_MA_Split_GNW ERV Flag | Split_GNW ERV Flag | Yes | Yes | [8 empty] | 2021-05-06
CT_MA_Split_GNE ERV Flag | Split_GNE ERV Flag | Yes | Yes | [8 empty] | 2021-05-06
CT_MA_Split_GN1 ERV Flag | Split_GN1 ERV Flag | Yes | Yes | [8 empty] | 2021-05-06
CT_MA_Split_GN2 ERV Flag | Split_GN2 ERV Flag | Yes | Yes | [8 empty] | 2021-05-06
CT_MA_Split_GS1 ERV Flag | Split_GS1 ERV Flag | Yes | Yes | [8 empty] | 2021-05-06
CT_MA_Split_GS2 ERV Flag | Split_GS2 ERV Flag | Yes | Yes | [8 empty] | 2021-05-06
CT_MA_Split_MSW ERV Flag | Split_MSW ERV Flag | Yes | Yes | [8 empty] | 2021-05-06
CT_MA_Split_MNW ERV Flag | Split_MNW ERV Flag | Yes | Yes | [8 empty] | 2021-05-06
CT_MA_Split_MSE ERV Flag | Split_MSE ERV Flag | Yes | Yes | [8 empty] | 2021-05-06
CT_MA_Split_MNE ERV Flag | Split_MNE ERV Flag | Yes | Yes | [8 empty] | 2021-05-06
CT_MA_Split_MN1 ERV Flag | Split_MN1 ERV Flag | Yes | Yes | [8 empty] | 2021-05-06
CT_MA_Split_MN2 ERV Flag | Split_MN2 ERV Flag | Yes | Yes | [8 empty] | 2021-05-06
CT_MA_Split_MS1 ERV Flag | Split_MS1 ERV Flag | Yes | Yes | [8 empty] | 2021-05-06
CT_MA_Split_MS2 ERV Flag | Split_MS2 ERV Flag | Yes | Yes | [8 empty] | 2021-05-06
CT_MA_Split_TSW ERV Flag | Split_TSW ERV Flag | Yes | Yes | [8 empty] | 2021-05-06
CT_MA_Split_TNW ERV Flag | Split_TNW ERV Flag | Yes | Yes | [8 empty] | 2021-05-06
CT_MA_Split_TSE ERV Flag | Split_TSE ERV Flag | Yes | Yes | [8 empty] | 2021-05-06
CT_MA_Split_TNE ERV Flag | Split_TNE ERV Flag | Yes | Yes | [8 empty] | 2021-05-06
CT_MA_Split_TN1 ERV Flag | Split_TN1 ERV Flag | Yes | Yes | [8 empty] | 2021-05-06
CT_MA_Split_TN2 ERV Flag | Split_TN2 ERV Flag | Yes | Yes | [8 empty] | 2021-05-06
CT_MA_Split_TS1 ERV Flag | Split_TS1 ERV Flag | Yes | Yes | [8 empty] | 2021-05-06
CT_MA_Split_TS2 ERV Flag | Split_TS2 ERV Flag | Yes | Yes | [8 empty] | 2021-05-06
id | item | Zone4A(DC-Baltimore-MD) ASHRAE901-state_STD2016 | Zone4A(DC-Baltimore-MD) ASHRAE901-state_STD2019 | [8 empty] | 2021-05-06
DC_SO_PSZ-AC:1 Cooling Capacity [ton] | PSZ-AC:1 Cooling Capacity [ton] | 1.9002 | 1.8024 | [8 empty] | 2021-05-06
DC_SO_PSZ-AC:2 Cooling Capacity [ton] | PSZ-AC:2 Cooling Capacity [ton] | 1.6912 | 1.625 | [8 empty] | 2021-05-06
DC_SO_PSZ-AC:3 Cooling Capacity [ton] | PSZ-AC:3 Cooling Capacity [ton] | 1.1296 | 1.091 | [8 empty] | 2021-05-06
DC_SO_PSZ-AC:4 Cooling Capacity [ton] | PSZ-AC:4 Cooling Capacity [ton] | 1.6237 | 1.5542 | [8 empty] | 2021-05-06
DC_SO_PSZ-AC:5 Cooling Capacity [ton] | PSZ-AC:5 Cooling Capacity [ton] | 1.3376 | 1.2979 | [8 empty] | 2021-05-06
DC_SO_PSZ-AC:1 Supply Flow Rate [cfm] | PSZ-AC:1 Supply Flow Rate [cfm] | 656.8528 | 614.4752 | [8 empty] | 2021-05-06
DC_SO_PSZ-AC:2 Supply Flow Rate [cfm] | PSZ-AC:2 Supply Flow Rate [cfm] | 593.2864 | 572.0976 | [8 empty] | 2021-05-06
DC_SO_PSZ-AC:3 Supply Flow Rate [cfm] | PSZ-AC:3 Supply Flow Rate [cfm] | 444.9648 | 423.776 | [8 empty] | 2021-05-06
DC_SO_PSZ-AC:4 Supply Flow Rate [cfm] | PSZ-AC:4 Supply Flow Rate [cfm] | 572.0976 | 529.72 | [8 empty] | 2021-05-06
DC_SO_PSZ-AC:5 Supply Flow Rate [cfm] | PSZ-AC:5 Supply Flow Rate [cfm] | 529.72 | 508.5312 | [8 empty] | 2021-05-06
DC_SO_PSZ-AC:1 OA Rate [cfm] | PSZ-AC:1 OA Rate [cfm] | 136.9178 | 136.9178 | [8 empty] | 2021-05-06
DC_SO_PSZ-AC:2 OA Rate [cfm] | PSZ-AC:2 OA Rate [cfm] | 103.7925 | 103.7925 | [8 empty] | 2021-05-06
DC_SO_PSZ-AC:3 OA Rate [cfm] | PSZ-AC:3 OA Rate [cfm] | 61.5711 | 61.5711 | [8 empty] | 2021-05-06
DC_SO_PSZ-AC:4 OA Rate [cfm] | PSZ-AC:4 OA Rate [cfm] | 103.7925 | 103.7925 | [8 empty] | 2021-05-06
DC_SO_PSZ-AC:5 OA Rate [cfm] | PSZ-AC:5 OA Rate [cfm] | 61.5711 | 61.5711 | [8 empty] | 2021-05-06
DC_SO_PSZ-AC:1 heating Capacity [kBtu/hr] | PSZ-AC:1 heating Capacity [kBtu/hr] | 13.4294 | 13.4294 | [8 empty] | 2021-05-06
DC_SO_PSZ-AC:2 heating Capacity [kBtu/hr] | PSZ-AC:2 heating Capacity [kBtu/hr] | 17.7984 | 17.6098 | [8 empty] | 2021-05-06
DC_SO_PSZ-AC:3 heating Capacity [kBtu/hr] | PSZ-AC:3 heating Capacity [kBtu/hr] | 10.8894 | 10.7851 | [8 empty] | 2021-05-06
DC_SO_PSZ-AC:4 heating Capacity [kBtu/hr] | PSZ-AC:4 heating Capacity [kBtu/hr] | 17.7032 | 17.5421 | [8 empty] | 2021-05-06
DC_SO_PSZ-AC:5 heating Capacity [kBtu/hr] | PSZ-AC:5 heating Capacity [kBtu/hr] | 10.9318 | 10.8228 | [8 empty] | 2021-05-06
id | item | Zone4A(DC-Baltimore-MD) ASHRAE901-state_STD2016 | Zone4A(DC-Baltimore-MD) ASHRAE901-state_STD2019 | [8 empty] | 2021-05-06
DC_LO_CAV_BAS Supply Flow Rate [cfm] | CAV_BAS Supply Flow Rate [cfm] | 11717.4064 | 10848.6656 | [8 empty] | 2021-05-06
DC_LO_VAV_BOT WITH REHEAT Supply Flow Rate [cfm] | VAV_BOT WITH REHEAT Supply Flow Rate [cfm] | 19620.8288 | 18688.5216 | [8 empty] | 2021-05-06
DC_LO_VAV_MID WITH REHEAT Supply Flow Rate [cfm] | VAV_MID WITH REHEAT Supply Flow Rate [cfm] | 182605.0787 | 173684.5939 | [8 empty] | 2021-05-06
DC_LO_VAV_TOP WITH REHEAT Supply Flow Rate [cfm] | VAV_TOP WITH REHEAT Supply Flow Rate [cfm] | 19451.3184 | 18667.3328 | [8 empty] | 2021-05-06
DC_LO_Supply Air Temp. Reset Flag | Supply Air Temp. Reset Flag | Yes | Yes | [8 empty] | 2021-05-06
DC_LO_CAV_BAS OA Rate [cfm] | CAV_BAS OA Rate [cfm] | 2542.8255 | 2542.8255 | [8 empty] | 2021-05-06
DC_LO_VAV_BOT WITH REHEAT OA Rate [cfm] | VAV_BOT WITH REHEAT OA Rate [cfm] | 5377.8022 | 4302.174 | [8 empty] | 2021-05-06
DC_LO_VAV_MID WITH REHEAT OA Rate [cfm] | VAV_MID WITH REHEAT OA Rate [cfm] | 53777.9373 | 43021.7396 | [8 empty] | 2021-05-06
DC_LO_VAV_TOP WITH REHEAT OA Rate [cfm] | VAV_TOP WITH REHEAT OA Rate [cfm] | 5377.8022 | 4302.174 | [8 empty] | 2021-05-06
DC_LO_AIRLOOP DATACENTER BASEMENT OA Rate [cfm] | AIRLOOP DATACENTER BASEMENT OA Rate [cfm] | 716.9654 | 716.9654 | [8 empty] | 2021-05-06
DC_LO_VAV_bot_WITH_REHEAT ERV Flag | VAV_bot_WITH_REHEAT ERV Flag | Yes | Yes | [8 empty] | 2021-05-06
DC_LO_VAV_mid_WITH_REHEAT ERV Flag | VAV_mid_WITH_REHEAT ERV Flag | Yes | Yes | [8 empty] | 2021-05-06
DC_LO_VAV_top_WITH_REHEAT ERV Flag | VAV_top_WITH_REHEAT ERV Flag | Yes | Yes | [8 empty] | 2021-05-06
DC_LO_COOLSYS1 CHILLER1 Capacity [ton] | COOLSYS1 CHILLER1 Capacity [ton] | 419.3885 | 377.8111 | [8 empty] | 2021-05-06
DC_LO_COOLSYS1 CHILLER2 Capacity [ton] | COOLSYS1 CHILLER2 Capacity [ton] | 419.3885 | 377.8111 | [8 empty] | 2021-05-06
DC_LO_TOWERWATERSYS COOLTOWER 1 Capacity [ton] | TOWERWATERSYS COOLTOWER 1 Capacity [ton] | 398.0767 | 358.6169 | [8 empty] | 2021-05-06
DC_LO_TOWERWATERSYS COOLTOWER 2 Capacity [ton] | TOWERWATERSYS COOLTOWER 2 Capacity [ton] | 398.0767 | 358.6169 | [8 empty] | 2021-05-06
DC_LO_HEATSYS1 BOILER Capacity [MMBTU/h] | HEATSYS1 BOILER Capacity [MMBTU/h] | 4070.838 | 3599.392 | [8 empty] | 2021-05-06
DC_LO_COOLSYS1 PUMP Flow Rate [gal/min] | COOLSYS1 PUMP Flow Rate [gal/min] | 0 | 0 | [8 empty] | 2021-05-06
DC_LO_COOLSYS1 CHILLER1 PUMP Flow Rate [gal/min] | COOLSYS1 CHILLER1 PUMP Flow Rate [gal/min] | 660.9236 | 592.5025 | [8 empty] | 2021-05-06
DC_LO_COOLSYS1 CHILLER2 PUMP Flow Rate [gal/min] | COOLSYS1 CHILLER2 PUMP Flow Rate [gal/min] | 660.9236 | 592.5025 | [8 empty] | 2021-05-06
DC_LO_COOLSYS1 PUMP SECONDARY Flow Rate [gal/min] | COOLSYS1 PUMP SECONDARY Flow Rate [gal/min] | 1321.8472 | 1185.005 | [8 empty] | 2021-05-06
DC_LO_HEATSYS1 PUMP Flow Rate [gal/min] | HEATSYS1 PUMP Flow Rate [gal/min] | 835.5926 | 738.8232 | [8 empty] | 2021-05-06
DC_LO_TOWERWATERSYS PUMP Flow Rate [gal/min] | TOWERWATERSYS PUMP Flow Rate [gal/min] | 2313.8302 | 2084.476 | [8 empty] | 2021-05-06
DC_LO_PLANT CIRC PUMP Flow Rate [gal/min] | PLANT CIRC PUMP Flow Rate [gal/min] | 208.4096 | 207.5632 | [8 empty] | 2021-05-06
DC_LO_COOLSYS1 PUMP SECONDARY Pressure setpoint reset [yes,no] | COOLSYS1 PUMP SECONDARY Pressure setpoint reset [yes,no] | pump_ride_on_curve | pump_ride_on_curve | [8 empty] | 2021-05-06
DC_LO_COOLSYS1 CHILLER1 PUMP Pump Power [hp] | COOLSYS1 CHILLER1 PUMP Pump Power [hp] | 3.5655 | 3.1647 | [8 empty] | 2021-05-06
DC_LO_COOLSYS1 CHILLER2 PUMP Pump Power [hp] | COOLSYS1 CHILLER2 PUMP Pump Power [hp] | 3.5655 | 3.1647 | [8 empty] | 2021-05-06
DC_LO_COOLSYS1 PUMP SECONDARY Pump Power [hp] | COOLSYS1 PUMP SECONDARY Pump Power [hp] | 21.3927 | 18.9882 | [8 empty] | 2021-05-06
DC_LO_HEATSYS1 PUMP Pump Power [hp] | HEATSYS1 PUMP Pump Power [hp] | 18.0618 | 15.812 | [8 empty] | 2021-05-06
DC_LO_TOWERWATERSYS PUMP Pump Power [hp] | TOWERWATERSYS PUMP Pump Power [hp] | 41.4263 | 36.9499 | [8 empty] | 2021-05-06
DC_LO_PLANT CIRC PUMP Pump Power [hp] | PLANT CIRC PUMP Pump Power [hp] | 4.4972 | 4.4346 | [8 empty] | 2021-05-06
DC_LO_Datacenter PLANT CIRC PUMP Pump Power [hp] | Datacenter PLANT CIRC PUMP Pump Power [hp] | 4.4972 | 4.4346 | [8 empty] | 2021-05-06
DC_LO_ZN_VAV_BOXes_Max_Reheat_Water_Flow_GPM | ZN_VAV_BOXes_Max_Reheat_Water_Flow_GPM | 438.3628 | 419.0812 | [8 empty] | 2021-05-06
DC_LO_COOLSYS1 PUMP SECONDARY VSD | COOLSYS1 PUMP SECONDARY VSD | No | No | [8 empty] | 2021-05-06
DC_LO_HEATSYS1 PUMP VSD | HEATSYS1 PUMP VSD | No | No | [8 empty] | 2021-05-06
DC_LO_DATACENTER BASEMENT Cooling Capacity [ton] | DATACENTER BASEMENT Cooling Capacity [ton] | 122.0782 | 121.7171 | [8 empty] | 2021-05-06
DC_LO_DATACENTER BOT Cooling Capacity [ton] | DATACENTER BOT Cooling Capacity [ton] | 2.6505 | 2.6272 | [8 empty] | 2021-05-06
DC_LO_DATACENTER MID Cooling Capacity [ton] | DATACENTER MID Cooling Capacity [ton] | 25.352 | 25.1355 | [8 empty] | 2021-05-06
DC_LO_DATACENTER TOP Cooling Capacity [ton] | DATACENTER TOP Cooling Capacity [ton] | 2.5842 | 2.5643 | [8 empty] | 2021-05-06
id | item | Zone4A(DC-Baltimore-MD) ASHRAE901-state_STD2016 | Zone4A(DC-Baltimore-MD) ASHRAE901-state_STD2019 | [8 empty] | 2021-05-06
DC_RS_PSZ-AC:1 Cooling Capacity [ton] | PSZ-AC:1 Cooling Capacity [ton] | 10.5815 | 10.2464 | [8 empty] | 2021-05-06
DC_RS_PSZ-AC:2 Cooling Capacity [ton] | PSZ-AC:2 Cooling Capacity [ton] | 50.5021 | 48.4923 | [8 empty] | 2021-05-06
DC_RS_PSZ-AC:3 Cooling Capacity [ton] | PSZ-AC:3 Cooling Capacity [ton] | 6.6414 | 6.4807 | [8 empty] | 2021-05-06
DC_RS_PSZ-AC:4 Cooling Capacity [ton] | PSZ-AC:4 Cooling Capacity [ton] | 5.427 | 5.2702 | [8 empty] | 2021-05-06
DC_RS_PSZ-AC:1 Supply Flow Rate [cfm] | PSZ-AC:1 Supply Flow Rate [cfm] | 4025.872 | 3771.6064 | [8 empty] | 2021-05-06
DC_RS_PSZ-AC:2 Supply Flow Rate [cfm] | PSZ-AC:2 Supply Flow Rate [cfm] | 15340.6912 | 14556.7056 | [8 empty] | 2021-05-06
DC_RS_PSZ-AC:3 Supply Flow Rate [cfm] | PSZ-AC:3 Supply Flow Rate [cfm] | 2330.768 | 2246.0128 | [8 empty] | 2021-05-06
DC_RS_PSZ-AC:4 Supply Flow Rate [cfm] | PSZ-AC:4 Supply Flow Rate [cfm] | 1779.8592 | 1716.2928 | [8 empty] | 2021-05-06
DC_RS_PSZ-AC:1 OA Rate [cfm] | PSZ-AC:1 OA Rate [cfm] | 490.669 | 490.669 | [8 empty] | 2021-05-06
DC_RS_PSZ-AC:2 OA Rate [cfm] | PSZ-AC:2 OA Rate [cfm] | 4005.1282 | 4005.1282 | [8 empty] | 2021-05-06
DC_RS_PSZ-AC:3 OA Rate [cfm] | PSZ-AC:3 OA Rate [cfm] | 377.3937 | 377.3937 | [8 empty] | 2021-05-06
DC_RS_PSZ-AC:4 OA Rate [cfm] | PSZ-AC:4 OA Rate [cfm] | 377.3937 | 377.3937 | [8 empty] | 2021-05-06
DC_RS_PSZ-AC:1 OA Damper [gravity, motorized] | PSZ-AC:1 OA Damper [gravity, motorized] | motorized | motorized | [8 empty] | 2021-05-06
DC_RS_PSZ-AC:2 OA Damper [gravity, motorized] | PSZ-AC:2 OA Damper [gravity, motorized] | motorized | motorized | [8 empty] | 2021-05-06
DC_RS_PSZ-AC:3 OA Damper [gravity, motorized] | PSZ-AC:3 OA Damper [gravity, motorized] | motorized | motorized | [8 empty] | 2021-05-06
DC_RS_PSZ-AC:4 OA Damper [gravity, motorized] | PSZ-AC:4 OA Damper [gravity, motorized] | motorized | motorized | [8 empty] | 2021-05-06
DC_RS_PSZ-AC:1 Heating Capacity [kBtu/hr] | PSZ-AC:1 Heating Capacity [kBtu/hr] | 177.8179 | 167.5076 | [8 empty] | 2021-05-06
DC_RS_PSZ-AC:2 Heating Capacity [kBtu/hr] | PSZ-AC:2 Heating Capacity [kBtu/hr] | 798.1653 | 764.8143 | [8 empty] | 2021-05-06
DC_RS_PSZ-AC:3 Heating Capacity [kBtu/hr] | PSZ-AC:3 Heating Capacity [kBtu/hr] | 108.941 | 106.2685 | [8 empty] | 2021-05-06
DC_RS_PSZ-AC:4 Heating Capacity [kBtu/hr] | PSZ-AC:4 Heating Capacity [kBtu/hr] | 88.9721 | 86.1477 | [8 empty] | 2021-05-06
id | item | Zone4A(DC-Baltimore-MD) ASHRAE901-state_STD2016 | Zone4A(DC-Baltimore-MD) ASHRAE901-state_STD2019 | [8 empty] | 2021-05-06
DC_PS_VAV_POD_1 Cooling Capacity [ton] | VAV_POD_1 Cooling Capacity [ton] | 19.2855 | 18.6268 | [8 empty] | 2021-05-06
DC_PS_VAV_POD_2 Cooling Capacity [ton] | VAV_POD_2 Cooling Capacity [ton] | 18.9849 | 18.4274 | [8 empty] | 2021-05-06
DC_PS_VAV_POD_3 Cooling Capacity [ton] | VAV_POD_3 Cooling Capacity [ton] | 17.5233 | 16.7415 | [8 empty] | 2021-05-06
DC_PS_VAV_OTHER Cooling Capacity [ton] | VAV_OTHER Cooling Capacity [ton] | 26.8056 | 25.2864 | [8 empty] | 2021-05-06
DC_PS_PSZ-AC_1:6 Cooling Capacity [ton] | PSZ-AC_1:6 Cooling Capacity [ton] | 8.4875 | 8.1383 | [8 empty] | 2021-05-06
DC_PS_PSZ-AC_2:5 Cooling Capacity [ton] | PSZ-AC_2:5 Cooling Capacity [ton] | 5.3757 | 5.4614 | [8 empty] | 2021-05-06
DC_PS_PSZ-AC_2:7 Cooling Capacity [ton] | PSZ-AC_2:7 Cooling Capacity [ton] | 10.5074 | 10.5074 | [8 empty] | 2021-05-06
DC_PS_VAV_POD_1 Supply Flow Rate [cfm] | VAV_POD_1 Supply Flow Rate [cfm] | 5784.5424 | 5593.8432 | [8 empty] | 2021-05-06
DC_PS_VAV_POD_2 Supply Flow Rate [cfm] | VAV_POD_2 Supply Flow Rate [cfm] | 5699.7872 | 5530.2768 | [8 empty] | 2021-05-06
DC_PS_VAV_POD_3 Supply Flow Rate [cfm] | VAV_POD_3 Supply Flow Rate [cfm] | 5254.8224 | 5021.7456 | [8 empty] | 2021-05-06
DC_PS_VAV_OTHER Supply Flow Rate [cfm] | VAV_OTHER Supply Flow Rate [cfm] | 8051.744 | 7585.5904 | [8 empty] | 2021-05-06
DC_PS_PSZ-AC_2:5 Supply Flow Rate [cfm] | PSZ-AC_2:5 Supply Flow Rate [cfm] | 1610.3488 | 1631.5376 | [8 empty] | 2021-05-06
DC_PS_PSZ-AC_1:6 Supply Flow Rate [cfm] | PSZ-AC_1:6 Supply Flow Rate [cfm] | 2542.656 | 2436.712 | [8 empty] | 2021-05-06
DC_PS_PSZ-AC_2:7 Supply Flow Rate [cfm] | PSZ-AC_2:7 Supply Flow Rate [cfm] | 3157.1312 | 3157.1312 | [8 empty] | 2021-05-06
DC_PS_Supply Air Temp. Reset Flag | Supply Air Temp. Reset Flag | Yes | Yes | [8 empty] | 2021-05-06
DC_PS_VAV_POD_1 OA Rate [cfm] | VAV_POD_1 OA Rate [cfm] | 5787.2758 | 5589.5843 | [8 empty] | 2021-05-06
DC_PS_VAV_POD_2 OA Rate [cfm] | VAV_POD_2 OA Rate [cfm] | 5696.4606 | 5529.7471 | [8 empty] | 2021-05-06
DC_PS_VAV_POD_3 OA Rate [cfm] | VAV_POD_3 OA Rate [cfm] | 5257.7465 | 5023.8645 | [8 empty] | 2021-05-06
DC_PS_VAV_OTHER OA Rate [cfm] | VAV_OTHER OA Rate [cfm] | 3736.1787 | 2988.8921 | [8 empty] | 2021-05-06
DC_PS_PSZ-AC_2:5 OA Rate [cfm] | PSZ-AC_2:5 OA Rate [cfm] | 1152.7343 | 1152.7343 | [8 empty] | 2021-05-06
DC_PS_PSZ-AC_1:6 OA Rate [cfm] | PSZ-AC_1:6 OA Rate [cfm] | 539.9118 | 539.9118 | [8 empty] | 2021-05-06
DC_PS_PSZ-AC_2:7 OA Rate [cfm] | PSZ-AC_2:7 OA Rate [cfm] | 3153.0841 | 3153.0841 | [8 empty] | 2021-05-06
DC_PS_VAV_POD_1 OA Damper [gravity, motorized] | VAV_POD_1 OA Damper [gravity, motorized] | motorized | motorized | [8 empty] | 2021-05-06
DC_PS_VAV_POD_2 OA Damper [gravity, motorized] | VAV_POD_2 OA Damper [gravity, motorized] | motorized | motorized | [8 empty] | 2021-05-06
DC_PS_VAV_POD_3 OA Damper [gravity, motorized] | VAV_POD_3 OA Damper [gravity, motorized] | motorized | motorized | [8 empty] | 2021-05-06
DC_PS_VAV_OTHER OA Damper [gravity, motorized] | VAV_OTHER OA Damper [gravity, motorized] | motorized | motorized | [8 empty] | 2021-05-06
DC_PS_PSZ-AC_2:5 OA Damper [gravity, motorized] | PSZ-AC_2:5 OA Damper [gravity, motorized] | motorized | motorized | [8 empty] | 2021-05-06
DC_PS_PSZ-AC_1:6 OA Damper [gravity, motorized] | PSZ-AC_1:6 OA Damper [gravity, motorized] | motorized | motorized | [8 empty] | 2021-05-06
DC_PS_PSZ-AC_2:7 OA Damper [gravity, motorized] | PSZ-AC_2:7 OA Damper [gravity, motorized] | motorized | motorized | [8 empty] | 2021-05-06
DC_PS_VAV_POD_1 (economizer) | VAV_POD_1 (economizer) | DifferentialEnthalpy | DifferentialEnthalpy | [8 empty] | 2021-05-06
DC_PS_VAV_POD_2 (economizer) | VAV_POD_2 (economizer) | DifferentialEnthalpy | DifferentialEnthalpy | [8 empty] | 2021-05-06
DC_PS_VAV_POD_3 (economizer) | VAV_POD_3 (economizer) | DifferentialEnthalpy | DifferentialEnthalpy | [8 empty] | 2021-05-06
DC_PS_VAV_OTHER (economizer) | VAV_OTHER (economizer) | DifferentialEnthalpy | DifferentialEnthalpy | [8 empty] | 2021-05-06
DC_PS_PSZ-AC_2:5 (economizer) | PSZ-AC_2:5 (economizer) | DifferentialEnthalpy | DifferentialEnthalpy | [8 empty] | 2021-05-06
DC_PS_PSZ-AC_1:6 (economizer) | PSZ-AC_1:6 (economizer) | DifferentialEnthalpy | DifferentialEnthalpy | [8 empty] | 2021-05-06
DC_PS_PSZ-AC_2:7 (economizer) | PSZ-AC_2:7 (economizer) | DifferentialEnthalpy | DifferentialEnthalpy | [8 empty] | 2021-05-06
DC_PS_VAV_Pod_1_ERV Flag | VAV_Pod_1_ERV Flag | Yes | Yes | [8 empty] | 2021-05-06
DC_PS_VAV_Pod_2_ERV Flag | VAV_Pod_2_ERV Flag | Yes | Yes | [8 empty] | 2021-05-06
DC_PS_VAV_Pod_3_ERV Flag | VAV_Pod_3_ERV Flag | Yes | Yes | [8 empty] | 2021-05-06
DC_PS_VAV_OTHER_ERV Flag | VAV_OTHER_ERV Flag | Yes | Yes | [8 empty] | 2021-05-06
DC_PS_PSZ_AC_2_5_ERV Flag | PSZ_AC_2_5_ERV Flag | Yes | Yes | [8 empty] | 2021-05-06
DC_PS_PSZ_AC_2_7_ERV Flag | PSZ_AC_2_7_ERV Flag | Yes | Yes | [8 empty] | 2021-05-06
DC_PS_HEATSYS1 Capacity [MMBTU/h] | HEATSYS1 Capacity [MMBTU/h] | 0.99182 | 0.94583 | [8 empty] | 2021-05-06
DC_PS_HEATSYS1 Flow Rate [gal/min] | HEATSYS1 Flow Rate [gal/min] | 101.7924 | 97.0723 | [8 empty] | 2021-05-06
DC_PS_VAV_POD_1 Fan Power [hp] | VAV_POD_1 Fan Power [hp] | 8.538 | 8.2463 | [8 empty] | 2021-05-06
DC_PS_VAV_POD_2 Fan Power [hp] | VAV_POD_2 Fan Power [hp] | 8.4049 | 8.158 | [8 empty] | 2021-05-06
DC_PS_VAV_POD_3 Fan Power [hp] | VAV_POD_3 Fan Power [hp] | 7.7578 | 7.4117 | [8 empty] | 2021-05-06
DC_PS_VAV_OTHER Fan Power [hp] | VAV_OTHER Fan Power [hp] | 11.7773 | 11.1098 | [8 empty] | 2021-05-06
DC_PS_HEATSYS1 Pump Power [hp] | HEATSYS1 Pump Power [hp] | 2.2003 | 2.0775 | [8 empty] | 2021-05-06
DC_PS_PSZ-AC_1:6 Heating Capacity [kBtu/hr] | PSZ-AC_1:6 Heating Capacity [kBtu/hr] | 209.0182 | 200.4499 | [8 empty] | 2021-05-06
DC_PS_PSZ-AC_2:5 Heating Capacity [kBtu/hr] | PSZ-AC_2:5 Heating Capacity [kBtu/hr] | 130.0227 | 130.969 | [8 empty] | 2021-05-06
DC_PS_PSZ-AC_2:7 Heating Capacity [kBtu/hr] | PSZ-AC_2:7 Heating Capacity [kBtu/hr] | 309.2659 | 309.2659 | [8 empty] | 2021-05-06
DC_PS_ZN_VAV_BOXes_Max_Reheat_Water_Flow_GPM | ZN_VAV_BOXes_Max_Reheat_Water_Flow_GPM | 67.176 | 63.9299 | [8 empty] | 2021-05-06
id | item | Zone4A(DC-Baltimore-MD) ASHRAE901-state_STD2016 | Zone4A(DC-Baltimore-MD) ASHRAE901-state_STD2019 | [8 empty] | 2021-05-06
DC_SH_SAC_FRONTOFFICE Cooling Capacity [ton] | SAC_FRONTOFFICE Cooling Capacity [ton] | 2.403 | 2.2861 | [8 empty] | 2021-05-06
DC_SH_SAC_FRONTLOUNGE Cooling Capacity [ton] | SAC_FRONTLOUNGE Cooling Capacity [ton] | 6.152 | 5.8438 | [8 empty] | 2021-05-06
DC_SH_SAC_MEETINGROOM Cooling Capacity [ton] | SAC_MEETINGROOM Cooling Capacity [ton] | 2.8896 | 2.8184 | [8 empty] | 2021-05-06
DC_SH_SAC_EXC_EMPLGE_RESTRM Cooling Capacity [ton] | SAC_EXC_EMPLGE_RESTRM Cooling Capacity [ton] | 6.087 | 6.0449 | [8 empty] | 2021-05-06
DC_SH_SAC_FO_ADDAQ SUPPLY FAN Supply Flow Rate [cfm] | SAC_FO_ADDAQ SUPPLY FAN Supply Flow Rate [cfm] | 783.9856 | 741.608 | [8 empty] | 2021-05-06
DC_SH_SAC_FL_ADDAQ SUPPLY FAN Supply Flow Rate [cfm] | SAC_FL_ADDAQ SUPPLY FAN Supply Flow Rate [cfm] | 1843.4256 | 1758.6704 | [8 empty] | 2021-05-06
DC_SH_SAC_MR_ADDAQ SUPPLY FAN Supply Flow Rate [cfm] | SAC_MR_ADDAQ SUPPLY FAN Supply Flow Rate [cfm] | 868.7408 | 847.552 | [8 empty] | 2021-05-06
DC_SH_SAC_EXC_ADDAQ SUPPLY FAN Supply Flow Rate [cfm] | SAC_EXC_ADDAQ SUPPLY FAN Supply Flow Rate [cfm] | 2182.4464 | 2161.2576 | [8 empty] | 2021-05-06
DC_SH_SAC_Exc_EmpLge_RestRm OA Rate [cfm] | SAC_Exc_EmpLge_RestRm OA Rate [cfm] | 199.9928 | 199.9928 | [8 empty] | 2021-05-06
DC_SH_SAC_FrontLounge OA Rate [cfm] | SAC_FrontLounge OA Rate [cfm] | 500.0133 | 500.0133 | [8 empty] | 2021-05-06
DC_SH_SAC_FrontOffice OA Rate [cfm] | SAC_FrontOffice OA Rate [cfm] | 119.2938 | 119.2938 | [8 empty] | 2021-05-06
DC_SH_SAC_MeetingRoom OA Rate [cfm] | SAC_MeetingRoom OA Rate [cfm] | 267.7629 | 267.7629 | [8 empty] | 2021-05-06
DC_SH_SAC_FrontLounge OA Damper [gravity, motorized] | SAC_FrontLounge OA Damper [gravity, motorized] | motorized | motorized | [8 empty] | 2021-05-06
DC_SH_SAC_FrontOffice (economizer) | SAC_FrontOffice (economizer) | No | No | [8 empty] | 2021-05-06
DC_SH_SAC_FrontLounge (economizer) | SAC_FrontLounge (economizer) | DifferentialEnthalpy | DifferentialEnthalpy | [8 empty] | 2021-05-06
DC_SH_SAC_MeetingRoom (economizer) | SAC_MeetingRoom (economizer) | No | No | [8 empty] | 2021-05-06
DC_SH_SAC_Exc_EmpLge_RestRm (economizer) | SAC_Exc_EmpLge_RestRm (economizer) | DifferentialEnthalpy | DifferentialEnthalpy | [8 empty] | 2021-05-06
DC_SH_SAC_FRONTOFFICE Heating Capacity [kBtu/hr] | SAC_FRONTOFFICE Heating Capacity [kBtu/hr] | 36.078 | 34.3251 | [8 empty] | 2021-05-06
DC_SH_SAC_FRONTLOUNGE Heating Capacity [kBtu/hr] | SAC_FRONTLOUNGE Heating Capacity [kBtu/hr] | 98.3301 | 94.9441 | [8 empty] | 2021-05-06
DC_SH_SAC_MEETINGROOM Heating Capacity [kBtu/hr] | SAC_MEETINGROOM Heating Capacity [kBtu/hr] | 48.2083 | 47.4257 | [8 empty] | 2021-05-06
DC_SH_SAC_EXC_EMPLGE_RESTRM Heating Capacity [kBtu/hr] | SAC_EXC_EMPLGE_RESTRM Heating Capacity [kBtu/hr] | 92.4562 | 91.8045 | [8 empty] | 2021-05-06
id | item | Zone4A(DC-Baltimore-MD) ASHRAE901-state_STD2016 | Zone4A(DC-Baltimore-MD) ASHRAE901-state_STD2019 | [8 empty] | 2021-05-06
DC_MA_SPLIT GSW COOLING COIL Cooling Capacity [ton] | SPLIT GSW COOLING COIL Cooling Capacity [ton] | 0.89896 | 0.88507 | [8 empty] | 2021-05-06
DC_MA_SPLIT GNW COOLING COIL Cooling Capacity [ton] | SPLIT GNW COOLING COIL Cooling Capacity [ton] | 0.86337 | 0.8499 | [8 empty] | 2021-05-06
DC_MA_SPLIT OFFICE COOLING COIL Cooling Capacity [ton] | SPLIT OFFICE COOLING COIL Cooling Capacity [ton] | 1.701 | 1.6099 | [8 empty] | 2021-05-06
DC_MA_SPLIT GNE COOLING COIL Cooling Capacity [ton] | SPLIT GNE COOLING COIL Cooling Capacity [ton] | 0.76485 | 0.75291 | [8 empty] | 2021-05-06
DC_MA_SPLIT GN1 COOLING COIL Cooling Capacity [ton] | SPLIT GN1 COOLING COIL Cooling Capacity [ton] | 0.64449 | 0.63483 | [8 empty] | 2021-05-06
DC_MA_SPLIT GN2 COOLING COIL Cooling Capacity [ton] | SPLIT GN2 COOLING COIL Cooling Capacity [ton] | 0.64259 | 0.63297 | [8 empty] | 2021-05-06
DC_MA_SPLIT GS1 COOLING COIL Cooling Capacity [ton] | SPLIT GS1 COOLING COIL Cooling Capacity [ton] | 0.68794 | 0.67759 | [8 empty] | 2021-05-06
DC_MA_SPLIT GS2 COOLING COIL Cooling Capacity [ton] | SPLIT GS2 COOLING COIL Cooling Capacity [ton] | 0.71843 | 0.70434 | [8 empty] | 2021-05-06
DC_MA_SPLIT MSW COOLING COIL Cooling Capacity [ton] | SPLIT MSW COOLING COIL Cooling Capacity [ton] | 2.104 | 2.0732 | [8 empty] | 2021-05-06
DC_MA_SPLIT MNW COOLING COIL Cooling Capacity [ton] | SPLIT MNW COOLING COIL Cooling Capacity [ton] | 2.034 | 2.0043 | [8 empty] | 2021-05-06
DC_MA_SPLIT MSE COOLING COIL Cooling Capacity [ton] | SPLIT MSE COOLING COIL Cooling Capacity [ton] | 1.8679 | 1.8411 | [8 empty] | 2021-05-06
DC_MA_SPLIT MNE COOLING COIL Cooling Capacity [ton] | SPLIT MNE COOLING COIL Cooling Capacity [ton] | 1.7241 | 1.7011 | [8 empty] | 2021-05-06
DC_MA_SPLIT MN1 COOLING COIL Cooling Capacity [ton] | SPLIT MN1 COOLING COIL Cooling Capacity [ton] | 1.404 | 1.3854 | [8 empty] | 2021-05-06
DC_MA_SPLIT MN2 COOLING COIL Cooling Capacity [ton] | SPLIT MN2 COOLING COIL Cooling Capacity [ton] | 1.3987 | 1.3803 | [8 empty] | 2021-05-06
DC_MA_SPLIT MS1 COOLING COIL Cooling Capacity [ton] | SPLIT MS1 COOLING COIL Cooling Capacity [ton] | 1.4831 | 1.4635 | [8 empty] | 2021-05-06
DC_MA_SPLIT MS2 COOLING COIL Cooling Capacity [ton] | SPLIT MS2 COOLING COIL Cooling Capacity [ton] | 1.4779 | 1.4585 | [8 empty] | 2021-05-06
DC_MA_SPLIT TSW COOLING COIL Cooling Capacity [ton] | SPLIT TSW COOLING COIL Cooling Capacity [ton] | 1.3201 | 1.3031 | [8 empty] | 2021-05-06
DC_MA_SPLIT TNW COOLING COIL Cooling Capacity [ton] | SPLIT TNW COOLING COIL Cooling Capacity [ton] | 1.2709 | 1.2548 | [8 empty] | 2021-05-06
DC_MA_SPLIT TSE COOLING COIL Cooling Capacity [ton] | SPLIT TSE COOLING COIL Cooling Capacity [ton] | 1.1993 | 1.1854 | [8 empty] | 2021-05-06
DC_MA_SPLIT TNE COOLING COIL Cooling Capacity [ton] | SPLIT TNE COOLING COIL Cooling Capacity [ton] | 1.1256 | 1.1128 | [8 empty] | 2021-05-06
DC_MA_SPLIT TN1 COOLING COIL Cooling Capacity [ton] | SPLIT TN1 COOLING COIL Cooling Capacity [ton] | 0.89139 | 0.88184 | [8 empty] | 2021-05-06
DC_MA_SPLIT TN2 COOLING COIL Cooling Capacity [ton] | SPLIT TN2 COOLING COIL Cooling Capacity [ton] | 0.92 | 0.91007 | [8 empty] | 2021-05-06
DC_MA_SPLIT TS1 COOLING COIL Cooling Capacity [ton] | SPLIT TS1 COOLING COIL Cooling Capacity [ton] | 0.9933 | 0.98226 | [8 empty] | 2021-05-06
DC_MA_SPLIT TS2 COOLING COIL Cooling Capacity [ton] | SPLIT TS2 COOLING COIL Cooling Capacity [ton] | 0.99478 | 0.98373 | [8 empty] | 2021-05-06
DC_MA_Split GN1 Furnace with DX Cooling OA Rate [cfm] | Split GN1 Furnace with DX Cooling OA Rate [cfm] | 54.9913 | 54.9913 | [8 empty] | 2021-05-06
DC_MA_Split GN2 Furnace with DX Cooling OA Rate [cfm] | Split GN2 Furnace with DX Cooling OA Rate [cfm] | 54.9913 | 54.9913 | [8 empty] | 2021-05-06
DC_MA_Split GNE Furnace with DX Cooling OA Rate [cfm] | Split GNE Furnace with DX Cooling OA Rate [cfm] | 54.9913 | 54.9913 | [8 empty] | 2021-05-06
DC_MA_Split GNW Furnace with DX Cooling OA Rate [cfm] | Split GNW Furnace with DX Cooling OA Rate [cfm] | 54.9913 | 54.9913 | [8 empty] | 2021-05-06
DC_MA_Split GS1 Furnace with DX Cooling OA Rate [cfm] | Split GS1 Furnace with DX Cooling OA Rate [cfm] | 54.9913 | 54.9913 | [8 empty] | 2021-05-06
DC_MA_Split GS2 Furnace with DX Cooling OA Rate [cfm] | Split GS2 Furnace with DX Cooling OA Rate [cfm] | 54.9913 | 54.9913 | [8 empty] | 2021-05-06
DC_MA_Split GSW Furnace with DX Cooling OA Rate [cfm] | Split GSW Furnace with DX Cooling OA Rate [cfm] | 56.9945 | 56.9945 | [8 empty] | 2021-05-06
DC_MA_Split MN1 Furnace with DX Cooling OA Rate [cfm] | Split MN1 Furnace with DX Cooling OA Rate [cfm] | 109.9824 | 109.9824 | [8 empty] | 2021-05-06
DC_MA_Split MN2 Furnace with DX Cooling OA Rate [cfm] | Split MN2 Furnace with DX Cooling OA Rate [cfm] | 109.9824 | 109.9824 | [8 empty] | 2021-05-06
DC_MA_Split MNE Furnace with DX Cooling OA Rate [cfm] | Split MNE Furnace with DX Cooling OA Rate [cfm] | 109.9824 | 109.9824 | [8 empty] | 2021-05-06
DC_MA_Split MNW Furnace with DX Cooling OA Rate [cfm] | Split MNW Furnace with DX Cooling OA Rate [cfm] | 109.9824 | 109.9824 | [8 empty] | 2021-05-06
DC_MA_Split MS1 Furnace with DX Cooling OA Rate [cfm] | Split MS1 Furnace with DX Cooling OA Rate [cfm] | 109.9824 | 109.9824 | [8 empty] | 2021-05-06
DC_MA_Split MS2 Furnace with DX Cooling OA Rate [cfm] | Split MS2 Furnace with DX Cooling OA Rate [cfm] | 109.9824 | 109.9824 | [8 empty] | 2021-05-06
DC_MA_Split MSE Furnace with DX Cooling OA Rate [cfm] | Split MSE Furnace with DX Cooling OA Rate [cfm] | 109.9824 | 109.9824 | [8 empty] | 2021-05-06
DC_MA_Split MSW Furnace with DX Cooling OA Rate [cfm] | Split MSW Furnace with DX Cooling OA Rate [cfm] | 109.9824 | 109.9824 | [8 empty] | 2021-05-06
DC_MA_Split Office Furnace with DX Cooling OA Rate [cfm] | Split Office Furnace with DX Cooling OA Rate [cfm] | 80.7372 | 80.7372 | [8 empty] | 2021-05-06
DC_MA_Split TN1 Furnace with DX Cooling OA Rate [cfm] | Split TN1 Furnace with DX Cooling OA Rate [cfm] | 54.9913 | 54.9913 | [8 empty] | 2021-05-06
DC_MA_Split TN2 Furnace with DX Cooling OA Rate [cfm] | Split TN2 Furnace with DX Cooling OA Rate [cfm] | 54.9913 | 54.9913 | [8 empty] | 2021-05-06
DC_MA_Split TNE Furnace with DX Cooling OA Rate [cfm] | Split TNE Furnace with DX Cooling OA Rate [cfm] | 54.9913 | 54.9913 | [8 empty] | 2021-05-06
DC_MA_Split TNW Furnace with DX Cooling OA Rate [cfm] | Split TNW Furnace with DX Cooling OA Rate [cfm] | 54.9913 | 54.9913 | [8 empty] | 2021-05-06
DC_MA_Split TS1 Furnace with DX Cooling OA Rate [cfm] | Split TS1 Furnace with DX Cooling OA Rate [cfm] | 54.9913 | 54.9913 | [8 empty] | 2021-05-06
DC_MA_Split TS2 Furnace with DX Cooling OA Rate [cfm] | Split TS2 Furnace with DX Cooling OA Rate [cfm] | 54.9913 | 54.9913 | [8 empty] | 2021-05-06
DC_MA_Split TSE Furnace with DX Cooling OA Rate [cfm] | Split TSE Furnace with DX Cooling OA Rate [cfm] | 54.9913 | 54.9913 | [8 empty] | 2021-05-06
DC_MA_Split TSW Furnace with DX Cooling OA Rate [cfm] | Split TSW Furnace with DX Cooling OA Rate [cfm] | 54.9913 | 54.9913 | [8 empty] | 2021-05-06
DC_MA_SPLIT GSW HEATING COIL Heating Capacity [kBtu/hr] | SPLIT GSW HEATING COIL Heating Capacity [kBtu/hr] | 8.3973 | 8.4561 | [8 empty] | 2021-05-06
DC_MA_SPLIT GNW HEATING COIL Heating Capacity [kBtu/hr] | SPLIT GNW HEATING COIL Heating Capacity [kBtu/hr] | 8.3321 | 8.391 | [8 empty] | 2021-05-06
DC_MA_SPLIT OFFICE HEATING COIL Heating Capacity [kBtu/hr] | SPLIT OFFICE HEATING COIL Heating Capacity [kBtu/hr] | 20.5861 | 20.6925 | [8 empty] | 2021-05-06
DC_MA_SPLIT GNE HEATING COIL Heating Capacity [kBtu/hr] | SPLIT GNE HEATING COIL Heating Capacity [kBtu/hr] | 8.3152 | 8.374 | [8 empty] | 2021-05-06
DC_MA_SPLIT GN1 HEATING COIL Heating Capacity [kBtu/hr] | SPLIT GN1 HEATING COIL Heating Capacity [kBtu/hr] | 6.0399 | 6.0989 | [8 empty] | 2021-05-06
DC_MA_SPLIT GN2 HEATING COIL Heating Capacity [kBtu/hr] | SPLIT GN2 HEATING COIL Heating Capacity [kBtu/hr] | 6.0394 | 6.0984 | [8 empty] | 2021-05-06
DC_MA_SPLIT GS1 HEATING COIL Heating Capacity [kBtu/hr] | SPLIT GS1 HEATING COIL Heating Capacity [kBtu/hr] | 5.9974 | 6.0562 | [8 empty] | 2021-05-06
DC_MA_SPLIT GS2 HEATING COIL Heating Capacity [kBtu/hr] | SPLIT GS2 HEATING COIL Heating Capacity [kBtu/hr] | 6.4799 | 6.5408 | [8 empty] | 2021-05-06
DC_MA_SPLIT MSW HEATING COIL Heating Capacity [kBtu/hr] | SPLIT MSW HEATING COIL Heating Capacity [kBtu/hr] | 14.978 | 15.1067 | [8 empty] | 2021-05-06
DC_MA_SPLIT MNW HEATING COIL Heating Capacity [kBtu/hr] | SPLIT MNW HEATING COIL Heating Capacity [kBtu/hr] | 15.0488 | 15.1774 | [8 empty] | 2021-05-06
DC_MA_SPLIT MSE HEATING COIL Heating Capacity [kBtu/hr] | SPLIT MSE HEATING COIL Heating Capacity [kBtu/hr] | 14.9376 | 15.0663 | [8 empty] | 2021-05-06
DC_MA_SPLIT MNE HEATING COIL Heating Capacity [kBtu/hr] | SPLIT MNE HEATING COIL Heating Capacity [kBtu/hr] | 15.0084 | 15.1371 | [8 empty] | 2021-05-06
DC_MA_SPLIT MN1 HEATING COIL Heating Capacity [kBtu/hr] | SPLIT MN1 HEATING COIL Heating Capacity [kBtu/hr] | 10.7875 | 10.7875 | [8 empty] | 2021-05-06
DC_MA_SPLIT MN2 HEATING COIL Heating Capacity [kBtu/hr] | SPLIT MN2 HEATING COIL Heating Capacity [kBtu/hr] | 10.7875 | 10.7875 | [8 empty] | 2021-05-06
DC_MA_SPLIT MS1 HEATING COIL Heating Capacity [kBtu/hr] | SPLIT MS1 HEATING COIL Heating Capacity [kBtu/hr] | 10.7875 | 10.7875 | [8 empty] | 2021-05-06
DC_MA_SPLIT MS2 HEATING COIL Heating Capacity [kBtu/hr] | SPLIT MS2 HEATING COIL Heating Capacity [kBtu/hr] | 10.7875 | 10.7875 | [8 empty] | 2021-05-06
DC_MA_SPLIT TSW HEATING COIL Heating Capacity [kBtu/hr] | SPLIT TSW HEATING COIL Heating Capacity [kBtu/hr] | 10.6517 | 10.7132 | [8 empty] | 2021-05-06
DC_MA_SPLIT TNW HEATING COIL Heating Capacity [kBtu/hr] | SPLIT TNW HEATING COIL Heating Capacity [kBtu/hr] | 10.6948 | 10.7564 | [8 empty] | 2021-05-06
DC_MA_SPLIT TSE HEATING COIL Heating Capacity [kBtu/hr] | SPLIT TSE HEATING COIL Heating Capacity [kBtu/hr] | 10.6304 | 10.692 | [8 empty] | 2021-05-06
DC_MA_SPLIT TNE HEATING COIL Heating Capacity [kBtu/hr] | SPLIT TNE HEATING COIL Heating Capacity [kBtu/hr] | 10.6735 | 10.7352 | [8 empty] | 2021-05-06
DC_MA_SPLIT TN1 HEATING COIL Heating Capacity [kBtu/hr] | SPLIT TN1 HEATING COIL Heating Capacity [kBtu/hr] | 8.1153 | 8.1768 | [8 empty] | 2021-05-06
DC_MA_SPLIT TN2 HEATING COIL Heating Capacity [kBtu/hr] | SPLIT TN2 HEATING COIL Heating Capacity [kBtu/hr] | 8.1147 | 8.1761 | [8 empty] | 2021-05-06
DC_MA_SPLIT TS1 HEATING COIL Heating Capacity [kBtu/hr] | SPLIT TS1 HEATING COIL Heating Capacity [kBtu/hr] | 8.0648 | 8.1262 | [8 empty] | 2021-05-06
DC_MA_SPLIT TS2 HEATING COIL Heating Capacity [kBtu/hr] | SPLIT TS2 HEATING COIL Heating Capacity [kBtu/hr] | 8.0642 | 8.1256 | [8 empty] | 2021-05-06
DC_MA_Split_GSW ERV Flag | Split_GSW ERV Flag | Yes | Yes | [8 empty] | 2021-05-06
DC_MA_Split_GNW ERV Flag | Split_GNW ERV Flag | Yes | Yes | [8 empty] | 2021-05-06
DC_MA_Split_GNE ERV Flag | Split_GNE ERV Flag | Yes | Yes | [8 empty] | 2021-05-06
DC_MA_Split_GN1 ERV Flag | Split_GN1 ERV Flag | Yes | Yes | [8 empty] | 2021-05-06
DC_MA_Split_GN2 ERV Flag | Split_GN2 ERV Flag | Yes | Yes | [8 empty] | 2021-05-06
DC_MA_Split_GS1 ERV Flag | Split_GS1 ERV Flag | Yes | Yes | [8 empty] | 2021-05-06
DC_MA_Split_GS2 ERV Flag | Split_GS2 ERV Flag | Yes | Yes | [8 empty] | 2021-05-06
DC_MA_Split_MSW ERV Flag | Split_MSW ERV Flag | Yes | Yes | [8 empty] | 2021-05-06
DC_MA_Split_MNW ERV Flag | Split_MNW ERV Flag | Yes | Yes | [8 empty] | 2021-05-06
DC_MA_Split_MSE ERV Flag | Split_MSE ERV Flag | Yes | Yes | [8 empty] | 2021-05-06
DC_MA_Split_MNE ERV Flag | Split_MNE ERV Flag | Yes | Yes | [8 empty] | 2021-05-06
DC_MA_Split_MN1 ERV Flag | Split_MN1 ERV Flag | Yes | Yes | [8 empty] | 2021-05-06
DC_MA_Split_MN2 ERV Flag | Split_MN2 ERV Flag | Yes | Yes | [8 empty] | 2021-05-06
DC_MA_Split_MS1 ERV Flag | Split_MS1 ERV Flag | Yes | Yes | [8 empty] | 2021-05-06
DC_MA_Split_MS2 ERV Flag | Split_MS2 ERV Flag | Yes | Yes | [8 empty] | 2021-05-06
DC_MA_Split_TSW ERV Flag | Split_TSW ERV Flag | Yes | Yes | [8 empty] | 2021-05-06
DC_MA_Split_TNW ERV Flag | Split_TNW ERV Flag | Yes | Yes | [8 empty] | 2021-05-06
DC_MA_Split_TSE ERV Flag | Split_TSE ERV Flag | Yes | Yes | [8 empty] | 2021-05-06
DC_MA_Split_TNE ERV Flag | Split_TNE ERV Flag | Yes | Yes | [8 empty] | 2021-05-06
DC_MA_Split_TN1 ERV Flag | Split_TN1 ERV Flag | Yes | Yes | [8 empty] | 2021-05-06
DC_MA_Split_TN2 ERV Flag | Split_TN2 ERV Flag | Yes | Yes | [8 empty] | 2021-05-06
DC_MA_Split_TS1 ERV Flag | Split_TS1 ERV Flag | Yes | Yes | [8 empty] | 2021-05-06
DC_MA_Split_TS2 ERV Flag | Split_TS2 ERV Flag | Yes | Yes | [8 empty] | 2021-05-06
id | item | Zone4A(DE-Wilmington-DE) ASHRAE901-state_STD2016 | Zone4A(DE-Wilmington-DE) ASHRAE901-state_STD2019 | [8 empty] | 2021-05-06
DE_SO_PSZ-AC:1 Cooling Capacity [ton] | PSZ-AC:1 Cooling Capacity [ton] | 1.8802 | 1.7876 | [8 empty] | 2021-05-06
DE_SO_PSZ-AC:2 Cooling Capacity [ton] | PSZ-AC:2 Cooling Capacity [ton] | 1.649 | 1.5868 | [8 empty] | 2021-05-06
DE_SO_PSZ-AC:3 Cooling Capacity [ton] | PSZ-AC:3 Cooling Capacity [ton] | 1.1104 | 1.0721 | [8 empty] | 2021-05-06
DE_SO_PSZ-AC:4 Cooling Capacity [ton] | PSZ-AC:4 Cooling Capacity [ton] | 1.5804 | 1.5127 | [8 empty] | 2021-05-06
DE_SO_PSZ-AC:5 Cooling Capacity [ton] | PSZ-AC:5 Cooling Capacity [ton] | 1.3067 | 1.2675 | [8 empty] | 2021-05-06
DE_SO_PSZ-AC:1 Supply Flow Rate [cfm] | PSZ-AC:1 Supply Flow Rate [cfm] | 635.664 | 593.2864 | [8 empty] | 2021-05-06
DE_SO_PSZ-AC:2 Supply Flow Rate [cfm] | PSZ-AC:2 Supply Flow Rate [cfm] | 572.0976 | 550.9088 | [8 empty] | 2021-05-06
DE_SO_PSZ-AC:3 Supply Flow Rate [cfm] | PSZ-AC:3 Supply Flow Rate [cfm] | 444.9648 | 423.776 | [8 empty] | 2021-05-06
DE_SO_PSZ-AC:4 Supply Flow Rate [cfm] | PSZ-AC:4 Supply Flow Rate [cfm] | 550.9088 | 529.72 | [8 empty] | 2021-05-06
DE_SO_PSZ-AC:5 Supply Flow Rate [cfm] | PSZ-AC:5 Supply Flow Rate [cfm] | 508.5312 | 508.5312 | [8 empty] | 2021-05-06
DE_SO_PSZ-AC:1 OA Rate [cfm] | PSZ-AC:1 OA Rate [cfm] | 136.9178 | 136.9178 | [8 empty] | 2021-05-06
DE_SO_PSZ-AC:2 OA Rate [cfm] | PSZ-AC:2 OA Rate [cfm] | 103.7925 | 103.7925 | [8 empty] | 2021-05-06
DE_SO_PSZ-AC:3 OA Rate [cfm] | PSZ-AC:3 OA Rate [cfm] | 61.5711 | 61.5711 | [8 empty] | 2021-05-06
DE_SO_PSZ-AC:4 OA Rate [cfm] | PSZ-AC:4 OA Rate [cfm] | 103.7925 | 103.7925 | [8 empty] | 2021-05-06
DE_SO_PSZ-AC:5 OA Rate [cfm] | PSZ-AC:5 OA Rate [cfm] | 61.5711 | 61.5711 | [8 empty] | 2021-05-06
DE_SO_PSZ-AC:1 heating Capacity [kBtu/hr] | PSZ-AC:1 heating Capacity [kBtu/hr] | 13.6508 | 13.6508 | [8 empty] | 2021-05-06
DE_SO_PSZ-AC:2 heating Capacity [kBtu/hr] | PSZ-AC:2 heating Capacity [kBtu/hr] | 18.5316 | 18.3379 | [8 empty] | 2021-05-06
DE_SO_PSZ-AC:3 heating Capacity [kBtu/hr] | PSZ-AC:3 heating Capacity [kBtu/hr] | 11.3554 | 11.2483 | [8 empty] | 2021-05-06
DE_SO_PSZ-AC:4 heating Capacity [kBtu/hr] | PSZ-AC:4 heating Capacity [kBtu/hr] | 18.44 | 18.2741 | [8 empty] | 2021-05-06
DE_SO_PSZ-AC:5 heating Capacity [kBtu/hr] | PSZ-AC:5 heating Capacity [kBtu/hr] | 11.4024 | 11.2902 | [8 empty] | 2021-05-06
id | item | Zone4A(DE-Wilmington-DE) ASHRAE901-state_STD2016 | Zone4A(DE-Wilmington-DE) ASHRAE901-state_STD2019 | [8 empty] | 2021-05-06
DE_LO_CAV_BAS Supply Flow Rate [cfm] | CAV_BAS Supply Flow Rate [cfm] | 11653.84 | 10785.0992 | [8 empty] | 2021-05-06
DE_LO_VAV_BOT WITH REHEAT Supply Flow Rate [cfm] | VAV_BOT WITH REHEAT Supply Flow Rate [cfm] | 19514.8848 | 18603.7664 | [8 empty] | 2021-05-06
DE_LO_VAV_MID WITH REHEAT Supply Flow Rate [cfm] | VAV_MID WITH REHEAT Supply Flow Rate [cfm] | 181630.3939 | 172752.2867 | [8 empty] | 2021-05-06
DE_LO_VAV_TOP WITH REHEAT Supply Flow Rate [cfm] | VAV_TOP WITH REHEAT Supply Flow Rate [cfm] | 19197.0528 | 18413.0672 | [8 empty] | 2021-05-06
DE_LO_Supply Air Temp. Reset Flag | Supply Air Temp. Reset Flag | Yes | Yes | [8 empty] | 2021-05-06
DE_LO_CAV_BAS OA Rate [cfm] | CAV_BAS OA Rate [cfm] | 2542.8255 | 2542.8255 | [8 empty] | 2021-05-06
DE_LO_VAV_BOT WITH REHEAT OA Rate [cfm] | VAV_BOT WITH REHEAT OA Rate [cfm] | 5377.8022 | 4302.174 | [8 empty] | 2021-05-06
DE_LO_VAV_MID WITH REHEAT OA Rate [cfm] | VAV_MID WITH REHEAT OA Rate [cfm] | 53777.9373 | 43021.7396 | [8 empty] | 2021-05-06
DE_LO_VAV_TOP WITH REHEAT OA Rate [cfm] | VAV_TOP WITH REHEAT OA Rate [cfm] | 5377.8022 | 4302.174 | [8 empty] | 2021-05-06
DE_LO_AIRLOOP DATACENTER BASEMENT OA Rate [cfm] | AIRLOOP DATACENTER BASEMENT OA Rate [cfm] | 716.9654 | 716.9654 | [8 empty] | 2021-05-06
DE_LO_VAV_bot_WITH_REHEAT ERV Flag | VAV_bot_WITH_REHEAT ERV Flag | Yes | Yes | [8 empty] | 2021-05-06
DE_LO_VAV_mid_WITH_REHEAT ERV Flag | VAV_mid_WITH_REHEAT ERV Flag | Yes | Yes | [8 empty] | 2021-05-06
DE_LO_VAV_top_WITH_REHEAT ERV Flag | VAV_top_WITH_REHEAT ERV Flag | Yes | Yes | [8 empty] | 2021-05-06
DE_LO_COOLSYS1 CHILLER1 Capacity [ton] | COOLSYS1 CHILLER1 Capacity [ton] | 418.7019 | 377.5322 | [8 empty] | 2021-05-06
DE_LO_COOLSYS1 CHILLER2 Capacity [ton] | COOLSYS1 CHILLER2 Capacity [ton] | 418.7019 | 377.5322 | [8 empty] | 2021-05-06
DE_LO_TOWERWATERSYS COOLTOWER 1 Capacity [ton] | TOWERWATERSYS COOLTOWER 1 Capacity [ton] | 397.4204 | 358.3412 | [8 empty] | 2021-05-06
DE_LO_TOWERWATERSYS COOLTOWER 2 Capacity [ton] | TOWERWATERSYS COOLTOWER 2 Capacity [ton] | 397.4204 | 358.3412 | [8 empty] | 2021-05-06
DE_LO_HEATSYS1 BOILER Capacity [MMBTU/h] | HEATSYS1 BOILER Capacity [MMBTU/h] | 4182.9698 | 3707.27 | [8 empty] | 2021-05-06
DE_LO_COOLSYS1 PUMP Flow Rate [gal/min] | COOLSYS1 PUMP Flow Rate [gal/min] | 0 | 0 | [8 empty] | 2021-05-06
DE_LO_COOLSYS1 CHILLER1 PUMP Flow Rate [gal/min] | COOLSYS1 CHILLER1 PUMP Flow Rate [gal/min] | 659.8553 | 592.0952 | [8 empty] | 2021-05-06
DE_LO_COOLSYS1 CHILLER2 PUMP Flow Rate [gal/min] | COOLSYS1 CHILLER2 PUMP Flow Rate [gal/min] | 659.8553 | 592.0952 | [8 empty] | 2021-05-06
DE_LO_COOLSYS1 PUMP SECONDARY Flow Rate [gal/min] | COOLSYS1 PUMP SECONDARY Flow Rate [gal/min] | 1319.709 | 1184.1903 | [8 empty] | 2021-05-06
DE_LO_HEATSYS1 PUMP Flow Rate [gal/min] | HEATSYS1 PUMP Flow Rate [gal/min] | 858.6104 | 760.9661 | [8 empty] | 2021-05-06
DE_LO_TOWERWATERSYS PUMP Flow Rate [gal/min] | TOWERWATERSYS PUMP Flow Rate [gal/min] | 2310.0261 | 2082.891 | [8 empty] | 2021-05-06
DE_LO_PLANT CIRC PUMP Flow Rate [gal/min] | PLANT CIRC PUMP Flow Rate [gal/min] | 208.1369 | 207.308 | [8 empty] | 2021-05-06
DE_LO_COOLSYS1 PUMP SECONDARY Pressure setpoint reset [yes,no] | COOLSYS1 PUMP SECONDARY Pressure setpoint reset [yes,no] | pump_ride_on_curve | pump_ride_on_curve | [8 empty] | 2021-05-06
DE_LO_COOLSYS1 CHILLER1 PUMP Pump Power [hp] | COOLSYS1 CHILLER1 PUMP Pump Power [hp] | 3.5597 | 3.1625 | [8 empty] | 2021-05-06
DE_LO_COOLSYS1 CHILLER2 PUMP Pump Power [hp] | COOLSYS1 CHILLER2 PUMP Pump Power [hp] | 3.5597 | 3.1625 | [8 empty] | 2021-05-06
DE_LO_COOLSYS1 PUMP SECONDARY Pump Power [hp] | COOLSYS1 PUMP SECONDARY Pump Power [hp] | 21.3581 | 18.9751 | [8 empty] | 2021-05-06
DE_LO_HEATSYS1 PUMP Pump Power [hp] | HEATSYS1 PUMP Pump Power [hp] | 18.5593 | 16.2859 | [8 empty] | 2021-05-06
DE_LO_TOWERWATERSYS PUMP Pump Power [hp] | TOWERWATERSYS PUMP Pump Power [hp] | 41.3585 | 36.9226 | [8 empty] | 2021-05-06
DE_LO_PLANT CIRC PUMP Pump Power [hp] | PLANT CIRC PUMP Pump Power [hp] | 4.4913 | 4.4291 | [8 empty] | 2021-05-06
DE_LO_Datacenter PLANT CIRC PUMP Pump Power [hp] | Datacenter PLANT CIRC PUMP Pump Power [hp] | 4.4913 | 4.4291 | [8 empty] | 2021-05-06
DE_LO_ZN_VAV_BOXes_Max_Reheat_Water_Flow_GPM | ZN_VAV_BOXes_Max_Reheat_Water_Flow_GPM | 451.0121 | 433.0955 | [8 empty] | 2021-05-06
DE_LO_COOLSYS1 PUMP SECONDARY VSD | COOLSYS1 PUMP SECONDARY VSD | No | No | [8 empty] | 2021-05-06
DE_LO_HEATSYS1 PUMP VSD | HEATSYS1 PUMP VSD | No | No | [8 empty] | 2021-05-06
DE_LO_DATACENTER BASEMENT Cooling Capacity [ton] | DATACENTER BASEMENT Cooling Capacity [ton] | 121.9322 | 121.5716 | [8 empty] | 2021-05-06
DE_LO_DATACENTER BOT Cooling Capacity [ton] | DATACENTER BOT Cooling Capacity [ton] | 2.6463 | 2.6231 | [8 empty] | 2021-05-06
DE_LO_DATACENTER MID Cooling Capacity [ton] | DATACENTER MID Cooling Capacity [ton] | 25.3076 | 25.1042 | [8 empty] | 2021-05-06
DE_LO_DATACENTER TOP Cooling Capacity [ton] | DATACENTER TOP Cooling Capacity [ton] | 2.5788 | 2.5591 | [8 empty] | 2021-05-06
id | item | Zone4A(DE-Wilmington-DE) ASHRAE901-state_STD2016 | Zone4A(DE-Wilmington-DE) ASHRAE901-state_STD2019 | [8 empty] | 2021-05-06
DE_RS_PSZ-AC:1 Cooling Capacity [ton] | PSZ-AC:1 Cooling Capacity [ton] | 10.566 | 10.2427 | [8 empty] | 2021-05-06
DE_RS_PSZ-AC:2 Cooling Capacity [ton] | PSZ-AC:2 Cooling Capacity [ton] | 50.0428 | 48.1494 | [8 empty] | 2021-05-06
DE_RS_PSZ-AC:3 Cooling Capacity [ton] | PSZ-AC:3 Cooling Capacity [ton] | 6.5452 | 6.3855 | [8 empty] | 2021-05-06
DE_RS_PSZ-AC:4 Cooling Capacity [ton] | PSZ-AC:4 Cooling Capacity [ton] | 5.3487 | 5.1914 | [8 empty] | 2021-05-06
DE_RS_PSZ-AC:1 Supply Flow Rate [cfm] | PSZ-AC:1 Supply Flow Rate [cfm] | 3983.4944 | 3729.2288 | [8 empty] | 2021-05-06
DE_RS_PSZ-AC:2 Supply Flow Rate [cfm] | PSZ-AC:2 Supply Flow Rate [cfm] | 15234.7472 | 14450.7616 | [8 empty] | 2021-05-06
DE_RS_PSZ-AC:3 Supply Flow Rate [cfm] | PSZ-AC:3 Supply Flow Rate [cfm] | 2288.3904 | 2224.824 | [8 empty] | 2021-05-06
DE_RS_PSZ-AC:4 Supply Flow Rate [cfm] | PSZ-AC:4 Supply Flow Rate [cfm] | 1758.6704 | 1695.104 | [8 empty] | 2021-05-06
DE_RS_PSZ-AC:1 OA Rate [cfm] | PSZ-AC:1 OA Rate [cfm] | 490.669 | 490.669 | [8 empty] | 2021-05-06
DE_RS_PSZ-AC:2 OA Rate [cfm] | PSZ-AC:2 OA Rate [cfm] | 4005.1282 | 4005.1282 | [8 empty] | 2021-05-06
DE_RS_PSZ-AC:3 OA Rate [cfm] | PSZ-AC:3 OA Rate [cfm] | 377.3937 | 377.3937 | [8 empty] | 2021-05-06
DE_RS_PSZ-AC:4 OA Rate [cfm] | PSZ-AC:4 OA Rate [cfm] | 377.3937 | 377.3937 | [8 empty] | 2021-05-06
DE_RS_PSZ-AC:1 OA Damper [gravity, motorized] | PSZ-AC:1 OA Damper [gravity, motorized] | motorized | motorized | [8 empty] | 2021-05-06
DE_RS_PSZ-AC:2 OA Damper [gravity, motorized] | PSZ-AC:2 OA Damper [gravity, motorized] | motorized | motorized | [8 empty] | 2021-05-06
DE_RS_PSZ-AC:3 OA Damper [gravity, motorized] | PSZ-AC:3 OA Damper [gravity, motorized] | motorized | motorized | [8 empty] | 2021-05-06
DE_RS_PSZ-AC:4 OA Damper [gravity, motorized] | PSZ-AC:4 OA Damper [gravity, motorized] | motorized | motorized | [8 empty] | 2021-05-06
DE_RS_PSZ-AC:1 Heating Capacity [kBtu/hr] | PSZ-AC:1 Heating Capacity [kBtu/hr] | 177.2932 | 166.8108 | [8 empty] | 2021-05-06
DE_RS_PSZ-AC:2 Heating Capacity [kBtu/hr] | PSZ-AC:2 Heating Capacity [kBtu/hr] | 800.1617 | 767.0681 | [8 empty] | 2021-05-06
DE_RS_PSZ-AC:3 Heating Capacity [kBtu/hr] | PSZ-AC:3 Heating Capacity [kBtu/hr] | 108.7551 | 106.0724 | [8 empty] | 2021-05-06
DE_RS_PSZ-AC:4 Heating Capacity [kBtu/hr] | PSZ-AC:4 Heating Capacity [kBtu/hr] | 88.7404 | 85.8531 | [8 empty] | 2021-05-06
id | item | Zone4A(DE-Wilmington-DE) ASHRAE901-state_STD2016 | Zone4A(DE-Wilmington-DE) ASHRAE901-state_STD2019 | [8 empty] | 2021-05-06
DE_PS_VAV_POD_1 Cooling Capacity [ton] | VAV_POD_1 Cooling Capacity [ton] | 18.9909 | 18.3364 | [8 empty] | 2021-05-06
DE_PS_VAV_POD_2 Cooling Capacity [ton] | VAV_POD_2 Cooling Capacity [ton] | 18.6868 | 18.2766 | [8 empty] | 2021-05-06
DE_PS_VAV_POD_3 Cooling Capacity [ton] | VAV_POD_3 Cooling Capacity [ton] | 17.2273 | 16.4491 | [8 empty] | 2021-05-06
DE_PS_VAV_OTHER Cooling Capacity [ton] | VAV_OTHER Cooling Capacity [ton] | 26.267 | 24.7552 | [8 empty] | 2021-05-06
DE_PS_PSZ-AC_1:6 Cooling Capacity [ton] | PSZ-AC_1:6 Cooling Capacity [ton] | 8.4089 | 8.0854 | [8 empty] | 2021-05-06
DE_PS_PSZ-AC_2:5 Cooling Capacity [ton] | PSZ-AC_2:5 Cooling Capacity [ton] | 5.2821 | 5.3661 | [8 empty] | 2021-05-06
DE_PS_PSZ-AC_2:7 Cooling Capacity [ton] | PSZ-AC_2:7 Cooling Capacity [ton] | 10.5074 | 10.5074 | [8 empty] | 2021-05-06
DE_PS_VAV_POD_1 Supply Flow Rate [cfm] | VAV_POD_1 Supply Flow Rate [cfm] | 5699.7872 | 5509.088 | [8 empty] | 2021-05-06
DE_PS_VAV_POD_2 Supply Flow Rate [cfm] | VAV_POD_2 Supply Flow Rate [cfm] | 5615.032 | 5487.8992 | [8 empty] | 2021-05-06
DE_PS_VAV_POD_3 Supply Flow Rate [cfm] | VAV_POD_3 Supply Flow Rate [cfm] | 5170.0672 | 4936.9904 | [8 empty] | 2021-05-06
DE_PS_VAV_OTHER Supply Flow Rate [cfm] | VAV_OTHER Supply Flow Rate [cfm] | 7882.2336 | 7437.2688 | [8 empty] | 2021-05-06
DE_PS_PSZ-AC_2:5 Supply Flow Rate [cfm] | PSZ-AC_2:5 Supply Flow Rate [cfm] | 1589.16 | 1610.3488 | [8 empty] | 2021-05-06
DE_PS_PSZ-AC_1:6 Supply Flow Rate [cfm] | PSZ-AC_1:6 Supply Flow Rate [cfm] | 2542.656 | 2436.712 | [8 empty] | 2021-05-06
DE_PS_PSZ-AC_2:7 Supply Flow Rate [cfm] | PSZ-AC_2:7 Supply Flow Rate [cfm] | 3157.1312 | 3157.1312 | [8 empty] | 2021-05-06
DE_PS_Supply Air Temp. Reset Flag | Supply Air Temp. Reset Flag | Yes | Yes | [8 empty] | 2021-05-06
DE_PS_VAV_POD_1 OA Rate [cfm] | VAV_POD_1 OA Rate [cfm] | 5698.8549 | 5502.4559 | [8 empty] | 2021-05-06
DE_PS_VAV_POD_2 OA Rate [cfm] | VAV_POD_2 OA Rate [cfm] | 5607.5947 | 5484.509 | [8 empty] | 2021-05-06
DE_PS_VAV_POD_3 OA Rate [cfm] | VAV_POD_3 OA Rate [cfm] | 5168.5416 | 4936.1005 | [8 empty] | 2021-05-06
DE_PS_VAV_OTHER OA Rate [cfm] | VAV_OTHER OA Rate [cfm] | 3736.1787 | 2988.8921 | [8 empty] | 2021-05-06
DE_PS_PSZ-AC_2:5 OA Rate [cfm] | PSZ-AC_2:5 OA Rate [cfm] | 1152.7343 | 1152.7343 | [8 empty] | 2021-05-06
DE_PS_PSZ-AC_1:6 OA Rate [cfm] | PSZ-AC_1:6 OA Rate [cfm] | 539.9118 | 539.9118 | [8 empty] | 2021-05-06
DE_PS_PSZ-AC_2:7 OA Rate [cfm] | PSZ-AC_2:7 OA Rate [cfm] | 3153.0841 | 3153.0841 | [8 empty] | 2021-05-06
DE_PS_VAV_POD_1 OA Damper [gravity, motorized] | VAV_POD_1 OA Damper [gravity, motorized] | motorized | motorized | [8 empty] | 2021-05-06
DE_PS_VAV_POD_2 OA Damper [gravity, motorized] | VAV_POD_2 OA Damper [gravity, motorized] | motorized | motorized | [8 empty] | 2021-05-06
DE_PS_VAV_POD_3 OA Damper [gravity, motorized] | VAV_POD_3 OA Damper [gravity, motorized] | motorized | motorized | [8 empty] | 2021-05-06
DE_PS_VAV_OTHER OA Damper [gravity, motorized] | VAV_OTHER OA Damper [gravity, motorized] | motorized | motorized | [8 empty] | 2021-05-06
DE_PS_PSZ-AC_2:5 OA Damper [gravity, motorized] | PSZ-AC_2:5 OA Damper [gravity, motorized] | motorized | motorized | [8 empty] | 2021-05-06
DE_PS_PSZ-AC_1:6 OA Damper [gravity, motorized] | PSZ-AC_1:6 OA Damper [gravity, motorized] | motorized | motorized | [8 empty] | 2021-05-06
DE_PS_PSZ-AC_2:7 OA Damper [gravity, motorized] | PSZ-AC_2:7 OA Damper [gravity, motorized] | motorized | motorized | [8 empty] | 2021-05-06
DE_PS_VAV_POD_1 (economizer) | VAV_POD_1 (economizer) | DifferentialEnthalpy | DifferentialEnthalpy | [8 empty] | 2021-05-06
DE_PS_VAV_POD_2 (economizer) | VAV_POD_2 (economizer) | DifferentialEnthalpy | DifferentialEnthalpy | [8 empty] | 2021-05-06
DE_PS_VAV_POD_3 (economizer) | VAV_POD_3 (economizer) | DifferentialEnthalpy | DifferentialEnthalpy | [8 empty] | 2021-05-06
DE_PS_VAV_OTHER (economizer) | VAV_OTHER (economizer) | DifferentialEnthalpy | DifferentialEnthalpy | [8 empty] | 2021-05-06
DE_PS_PSZ-AC_2:5 (economizer) | PSZ-AC_2:5 (economizer) | DifferentialEnthalpy | DifferentialEnthalpy | [8 empty] | 2021-05-06
DE_PS_PSZ-AC_1:6 (economizer) | PSZ-AC_1:6 (economizer) | DifferentialEnthalpy | DifferentialEnthalpy | [8 empty] | 2021-05-06
DE_PS_PSZ-AC_2:7 (economizer) | PSZ-AC_2:7 (economizer) | DifferentialEnthalpy | DifferentialEnthalpy | [8 empty] | 2021-05-06
DE_PS_VAV_Pod_1_ERV Flag | VAV_Pod_1_ERV Flag | Yes | Yes | [8 empty] | 2021-05-06
DE_PS_VAV_Pod_2_ERV Flag | VAV_Pod_2_ERV Flag | Yes | Yes | [8 empty] | 2021-05-06
DE_PS_VAV_Pod_3_ERV Flag | VAV_Pod_3_ERV Flag | Yes | Yes | [8 empty] | 2021-05-06
DE_PS_VAV_OTHER_ERV Flag | VAV_OTHER_ERV Flag | Yes | Yes | [8 empty] | 2021-05-06
DE_PS_PSZ_AC_2_5_ERV Flag | PSZ_AC_2_5_ERV Flag | Yes | Yes | [8 empty] | 2021-05-06
DE_PS_PSZ_AC_2_7_ERV Flag | PSZ_AC_2_7_ERV Flag | Yes | Yes | [8 empty] | 2021-05-06
DE_PS_HEATSYS1 Capacity [MMBTU/h] | HEATSYS1 Capacity [MMBTU/h] | 1.01 | 0.96622 | [8 empty] | 2021-05-06
DE_PS_HEATSYS1 Flow Rate [gal/min] | HEATSYS1 Flow Rate [gal/min] | 103.6546 | 99.1652 | [8 empty] | 2021-05-06
DE_PS_VAV_POD_1 Fan Power [hp] | VAV_POD_1 Fan Power [hp] | 8.4075 | 8.1178 | [8 empty] | 2021-05-06
DE_PS_VAV_POD_2 Fan Power [hp] | VAV_POD_2 Fan Power [hp] | 8.2729 | 8.0913 | [8 empty] | 2021-05-06
DE_PS_VAV_POD_3 Fan Power [hp] | VAV_POD_3 Fan Power [hp] | 7.6268 | 7.2822 | [8 empty] | 2021-05-06
DE_PS_VAV_OTHER Fan Power [hp] | VAV_OTHER Fan Power [hp] | 11.5406 | 10.8764 | [8 empty] | 2021-05-06
DE_PS_HEATSYS1 Pump Power [hp] | HEATSYS1 Pump Power [hp] | 2.2406 | 2.1223 | [8 empty] | 2021-05-06
DE_PS_PSZ-AC_1:6 Heating Capacity [kBtu/hr] | PSZ-AC_1:6 Heating Capacity [kBtu/hr] | 209.0436 | 200.4757 | [8 empty] | 2021-05-06
DE_PS_PSZ-AC_2:5 Heating Capacity [kBtu/hr] | PSZ-AC_2:5 Heating Capacity [kBtu/hr] | 130.8937 | 131.8245 | [8 empty] | 2021-05-06
DE_PS_PSZ-AC_2:7 Heating Capacity [kBtu/hr] | PSZ-AC_2:7 Heating Capacity [kBtu/hr] | 314.3639 | 314.3639 | [8 empty] | 2021-05-06
DE_PS_ZN_VAV_BOXes_Max_Reheat_Water_Flow_GPM | ZN_VAV_BOXes_Max_Reheat_Water_Flow_GPM | 68.5272 | 65.4895 | [8 empty] | 2021-05-06
id | item | Zone4A(DE-Wilmington-DE) ASHRAE901-state_STD2016 | Zone4A(DE-Wilmington-DE) ASHRAE901-state_STD2019 | [8 empty] | 2021-05-06
DE_SH_SAC_FRONTOFFICE Cooling Capacity [ton] | SAC_FRONTOFFICE Cooling Capacity [ton] | 2.3464 | 2.236 | [8 empty] | 2021-05-06
DE_SH_SAC_FRONTLOUNGE Cooling Capacity [ton] | SAC_FRONTLOUNGE Cooling Capacity [ton] | 6.0674 | 5.7622 | [8 empty] | 2021-05-06
DE_SH_SAC_MEETINGROOM Cooling Capacity [ton] | SAC_MEETINGROOM Cooling Capacity [ton] | 2.8582 | 2.7872 | [8 empty] | 2021-05-06
DE_SH_SAC_EXC_EMPLGE_RESTRM Cooling Capacity [ton] | SAC_EXC_EMPLGE_RESTRM Cooling Capacity [ton] | 5.9933 | 5.952 | [8 empty] | 2021-05-06
DE_SH_SAC_FO_ADDAQ SUPPLY FAN Supply Flow Rate [cfm] | SAC_FO_ADDAQ SUPPLY FAN Supply Flow Rate [cfm] | 762.7968 | 720.4192 | [8 empty] | 2021-05-06
DE_SH_SAC_FL_ADDAQ SUPPLY FAN Supply Flow Rate [cfm] | SAC_FL_ADDAQ SUPPLY FAN Supply Flow Rate [cfm] | 1822.2368 | 1737.4816 | [8 empty] | 2021-05-06
DE_SH_SAC_MR_ADDAQ SUPPLY FAN Supply Flow Rate [cfm] | SAC_MR_ADDAQ SUPPLY FAN Supply Flow Rate [cfm] | 847.552 | 826.3632 | [8 empty] | 2021-05-06
DE_SH_SAC_EXC_ADDAQ SUPPLY FAN Supply Flow Rate [cfm] | SAC_EXC_ADDAQ SUPPLY FAN Supply Flow Rate [cfm] | 2182.4464 | 2161.2576 | [8 empty] | 2021-05-06
DE_SH_SAC_Exc_EmpLge_RestRm OA Rate [cfm] | SAC_Exc_EmpLge_RestRm OA Rate [cfm] | 199.9928 | 199.9928 | [8 empty] | 2021-05-06
DE_SH_SAC_FrontLounge OA Rate [cfm] | SAC_FrontLounge OA Rate [cfm] | 500.0133 | 500.0133 | [8 empty] | 2021-05-06
DE_SH_SAC_FrontOffice OA Rate [cfm] | SAC_FrontOffice OA Rate [cfm] | 119.2938 | 119.2938 | [8 empty] | 2021-05-06
DE_SH_SAC_MeetingRoom OA Rate [cfm] | SAC_MeetingRoom OA Rate [cfm] | 267.7629 | 267.7629 | [8 empty] | 2021-05-06
DE_SH_SAC_FrontLounge OA Damper [gravity, motorized] | SAC_FrontLounge OA Damper [gravity, motorized] | motorized | motorized | [8 empty] | 2021-05-06
DE_SH_SAC_FrontOffice (economizer) | SAC_FrontOffice (economizer) | No | No | [8 empty] | 2021-05-06
DE_SH_SAC_FrontLounge (economizer) | SAC_FrontLounge (economizer) | DifferentialEnthalpy | DifferentialEnthalpy | [8 empty] | 2021-05-06
DE_SH_SAC_MeetingRoom (economizer) | SAC_MeetingRoom (economizer) | No | No | [8 empty] | 2021-05-06
DE_SH_SAC_Exc_EmpLge_RestRm (economizer) | SAC_Exc_EmpLge_RestRm (economizer) | DifferentialEnthalpy | DifferentialEnthalpy | [8 empty] | 2021-05-06
DE_SH_SAC_FRONTOFFICE Heating Capacity [kBtu/hr] | SAC_FRONTOFFICE Heating Capacity [kBtu/hr] | 35.7974 | 34.0558 | [8 empty] | 2021-05-06
DE_SH_SAC_FRONTLOUNGE Heating Capacity [kBtu/hr] | SAC_FRONTLOUNGE Heating Capacity [kBtu/hr] | 98.3356 | 94.9733 | [8 empty] | 2021-05-06
DE_SH_SAC_MEETINGROOM Heating Capacity [kBtu/hr] | SAC_MEETINGROOM Heating Capacity [kBtu/hr] | 48.3527 | 47.5697 | [8 empty] | 2021-05-06
DE_SH_SAC_EXC_EMPLGE_RESTRM Heating Capacity [kBtu/hr] | SAC_EXC_EMPLGE_RESTRM Heating Capacity [kBtu/hr] | 92.423 | 91.7743 | [8 empty] | 2021-05-06
id | item | Zone4A(DE-Wilmington-DE) ASHRAE901-state_STD2016 | Zone4A(DE-Wilmington-DE) ASHRAE901-state_STD2019 | [8 empty] | 2021-05-06
DE_MA_SPLIT GSW COOLING COIL Cooling Capacity [ton] | SPLIT GSW COOLING COIL Cooling Capacity [ton] | 0.87058 | 0.85671 | [8 empty] | 2021-05-06
DE_MA_SPLIT GNW COOLING COIL Cooling Capacity [ton] | SPLIT GNW COOLING COIL Cooling Capacity [ton] | 0.83439 | 0.82098 | [8 empty] | 2021-05-06
DE_MA_SPLIT OFFICE COOLING COIL Cooling Capacity [ton] | SPLIT OFFICE COOLING COIL Cooling Capacity [ton] | 1.6775 | 1.5771 | [8 empty] | 2021-05-06
DE_MA_SPLIT GNE COOLING COIL Cooling Capacity [ton] | SPLIT GNE COOLING COIL Cooling Capacity [ton] | 0.73814 | 0.72625 | [8 empty] | 2021-05-06
DE_MA_SPLIT GN1 COOLING COIL Cooling Capacity [ton] | SPLIT GN1 COOLING COIL Cooling Capacity [ton] | 0.6285 | 0.61884 | [8 empty] | 2021-05-06
DE_MA_SPLIT GN2 COOLING COIL Cooling Capacity [ton] | SPLIT GN2 COOLING COIL Cooling Capacity [ton] | 0.62663 | 0.61702 | [8 empty] | 2021-05-06
DE_MA_SPLIT GS1 COOLING COIL Cooling Capacity [ton] | SPLIT GS1 COOLING COIL Cooling Capacity [ton] | 0.67037 | 0.66 | [8 empty] | 2021-05-06
DE_MA_SPLIT GS2 COOLING COIL Cooling Capacity [ton] | SPLIT GS2 COOLING COIL Cooling Capacity [ton] | 0.70345 | 0.68679 | [8 empty] | 2021-05-06
DE_MA_SPLIT MSW COOLING COIL Cooling Capacity [ton] | SPLIT MSW COOLING COIL Cooling Capacity [ton] | 2.0613 | 2.0308 | [8 empty] | 2021-05-06
DE_MA_SPLIT MNW COOLING COIL Cooling Capacity [ton] | SPLIT MNW COOLING COIL Cooling Capacity [ton] | 1.9948 | 1.9651 | [8 empty] | 2021-05-06
DE_MA_SPLIT MSE COOLING COIL Cooling Capacity [ton] | SPLIT MSE COOLING COIL Cooling Capacity [ton] | 1.8239 | 1.797 | [8 empty] | 2021-05-06
DE_MA_SPLIT MNE COOLING COIL Cooling Capacity [ton] | SPLIT MNE COOLING COIL Cooling Capacity [ton] | 1.6879 | 1.6651 | [8 empty] | 2021-05-06
DE_MA_SPLIT MN1 COOLING COIL Cooling Capacity [ton] | SPLIT MN1 COOLING COIL Cooling Capacity [ton] | 1.3856 | 1.3671 | [8 empty] | 2021-05-06
DE_MA_SPLIT MN2 COOLING COIL Cooling Capacity [ton] | SPLIT MN2 COOLING COIL Cooling Capacity [ton] | 1.3804 | 1.3621 | [8 empty] | 2021-05-06
DE_MA_SPLIT MS1 COOLING COIL Cooling Capacity [ton] | SPLIT MS1 COOLING COIL Cooling Capacity [ton] | 1.4607 | 1.4412 | [8 empty] | 2021-05-06
DE_MA_SPLIT MS2 COOLING COIL Cooling Capacity [ton] | SPLIT MS2 COOLING COIL Cooling Capacity [ton] | 1.4555 | 1.4362 | [8 empty] | 2021-05-06
DE_MA_SPLIT TSW COOLING COIL Cooling Capacity [ton] | SPLIT TSW COOLING COIL Cooling Capacity [ton] | 1.2903 | 1.2734 | [8 empty] | 2021-05-06
DE_MA_SPLIT TNW COOLING COIL Cooling Capacity [ton] | SPLIT TNW COOLING COIL Cooling Capacity [ton] | 1.2388 | 1.2228 | [8 empty] | 2021-05-06
DE_MA_SPLIT TSE COOLING COIL Cooling Capacity [ton] | SPLIT TSE COOLING COIL Cooling Capacity [ton] | 1.1686 | 1.1546 | [8 empty] | 2021-05-06
DE_MA_SPLIT TNE COOLING COIL Cooling Capacity [ton] | SPLIT TNE COOLING COIL Cooling Capacity [ton] | 1.0937 | 1.081 | [8 empty] | 2021-05-06
DE_MA_SPLIT TN1 COOLING COIL Cooling Capacity [ton] | SPLIT TN1 COOLING COIL Cooling Capacity [ton] | 0.87059 | 0.86113 | [8 empty] | 2021-05-06
DE_MA_SPLIT TN2 COOLING COIL Cooling Capacity [ton] | SPLIT TN2 COOLING COIL Cooling Capacity [ton] | 0.89751 | 0.88761 | [8 empty] | 2021-05-06
DE_MA_SPLIT TS1 COOLING COIL Cooling Capacity [ton] | SPLIT TS1 COOLING COIL Cooling Capacity [ton] | 0.9707 | 0.95967 | [8 empty] | 2021-05-06
DE_MA_SPLIT TS2 COOLING COIL Cooling Capacity [ton] | SPLIT TS2 COOLING COIL Cooling Capacity [ton] | 0.97232 | 0.96126 | [8 empty] | 2021-05-06
DE_MA_Split GN1 Furnace with DX Cooling OA Rate [cfm] | Split GN1 Furnace with DX Cooling OA Rate [cfm] | 54.9913 | 54.9913 | [8 empty] | 2021-05-06
DE_MA_Split GN2 Furnace with DX Cooling OA Rate [cfm] | Split GN2 Furnace with DX Cooling OA Rate [cfm] | 54.9913 | 54.9913 | [8 empty] | 2021-05-06
DE_MA_Split GNE Furnace with DX Cooling OA Rate [cfm] | Split GNE Furnace with DX Cooling OA Rate [cfm] | 54.9913 | 54.9913 | [8 empty] | 2021-05-06
DE_MA_Split GNW Furnace with DX Cooling OA Rate [cfm] | Split GNW Furnace with DX Cooling OA Rate [cfm] | 54.9913 | 54.9913 | [8 empty] | 2021-05-06
DE_MA_Split GS1 Furnace with DX Cooling OA Rate [cfm] | Split GS1 Furnace with DX Cooling OA Rate [cfm] | 54.9913 | 54.9913 | [8 empty] | 2021-05-06
DE_MA_Split GS2 Furnace with DX Cooling OA Rate [cfm] | Split GS2 Furnace with DX Cooling OA Rate [cfm] | 54.9913 | 54.9913 | [8 empty] | 2021-05-06
DE_MA_Split GSW Furnace with DX Cooling OA Rate [cfm] | Split GSW Furnace with DX Cooling OA Rate [cfm] | 56.9945 | 56.9945 | [8 empty] | 2021-05-06
DE_MA_Split MN1 Furnace with DX Cooling OA Rate [cfm] | Split MN1 Furnace with DX Cooling OA Rate [cfm] | 109.9824 | 109.9824 | [8 empty] | 2021-05-06
DE_MA_Split MN2 Furnace with DX Cooling OA Rate [cfm] | Split MN2 Furnace with DX Cooling OA Rate [cfm] | 109.9824 | 109.9824 | [8 empty] | 2021-05-06
DE_MA_Split MNE Furnace with DX Cooling OA Rate [cfm] | Split MNE Furnace with DX Cooling OA Rate [cfm] | 109.9824 | 109.9824 | [8 empty] | 2021-05-06
DE_MA_Split MNW Furnace with DX Cooling OA Rate [cfm] | Split MNW Furnace with DX Cooling OA Rate [cfm] | 109.9824 | 109.9824 | [8 empty] | 2021-05-06
DE_MA_Split MS1 Furnace with DX Cooling OA Rate [cfm] | Split MS1 Furnace with DX Cooling OA Rate [cfm] | 109.9824 | 109.9824 | [8 empty] | 2021-05-06
DE_MA_Split MS2 Furnace with DX Cooling OA Rate [cfm] | Split MS2 Furnace with DX Cooling OA Rate [cfm] | 109.9824 | 109.9824 | [8 empty] | 2021-05-06
DE_MA_Split MSE Furnace with DX Cooling OA Rate [cfm] | Split MSE Furnace with DX Cooling OA Rate [cfm] | 109.9824 | 109.9824 | [8 empty] | 2021-05-06
DE_MA_Split MSW Furnace with DX Cooling OA Rate [cfm] | Split MSW Furnace with DX Cooling OA Rate [cfm] | 109.9824 | 109.9824 | [8 empty] | 2021-05-06
DE_MA_Split Office Furnace with DX Cooling OA Rate [cfm] | Split Office Furnace with DX Cooling OA Rate [cfm] | 80.7372 | 80.7372 | [8 empty] | 2021-05-06
DE_MA_Split TN1 Furnace with DX Cooling OA Rate [cfm] | Split TN1 Furnace with DX Cooling OA Rate [cfm] | 54.9913 | 54.9913 | [8 empty] | 2021-05-06
DE_MA_Split TN2 Furnace with DX Cooling OA Rate [cfm] | Split TN2 Furnace with DX Cooling OA Rate [cfm] | 54.9913 | 54.9913 | [8 empty] | 2021-05-06
DE_MA_Split TNE Furnace with DX Cooling OA Rate [cfm] | Split TNE Furnace with DX Cooling OA Rate [cfm] | 54.9913 | 54.9913 | [8 empty] | 2021-05-06
DE_MA_Split TNW Furnace with DX Cooling OA Rate [cfm] | Split TNW Furnace with DX Cooling OA Rate [cfm] | 54.9913 | 54.9913 | [8 empty] | 2021-05-06
DE_MA_Split TS1 Furnace with DX Cooling OA Rate [cfm] | Split TS1 Furnace with DX Cooling OA Rate [cfm] | 54.9913 | 54.9913 | [8 empty] | 2021-05-06
DE_MA_Split TS2 Furnace with DX Cooling OA Rate [cfm] | Split TS2 Furnace with DX Cooling OA Rate [cfm] | 54.9913 | 54.9913 | [8 empty] | 2021-05-06
DE_MA_Split TSE Furnace with DX Cooling OA Rate [cfm] | Split TSE Furnace with DX Cooling OA Rate [cfm] | 54.9913 | 54.9913 | [8 empty] | 2021-05-06
DE_MA_Split TSW Furnace with DX Cooling OA Rate [cfm] | Split TSW Furnace with DX Cooling OA Rate [cfm] | 54.9913 | 54.9913 | [8 empty] | 2021-05-06
DE_MA_SPLIT GSW HEATING COIL Heating Capacity [kBtu/hr] | SPLIT GSW HEATING COIL Heating Capacity [kBtu/hr] | 8.8976 | 8.9562 | [8 empty] | 2021-05-06
DE_MA_SPLIT GNW HEATING COIL Heating Capacity [kBtu/hr] | SPLIT GNW HEATING COIL Heating Capacity [kBtu/hr] | 8.8328 | 8.8915 | [8 empty] | 2021-05-06
DE_MA_SPLIT OFFICE HEATING COIL Heating Capacity [kBtu/hr] | SPLIT OFFICE HEATING COIL Heating Capacity [kBtu/hr] | 21.3253 | 21.4203 | [8 empty] | 2021-05-06
DE_MA_SPLIT GNE HEATING COIL Heating Capacity [kBtu/hr] | SPLIT GNE HEATING COIL Heating Capacity [kBtu/hr] | 8.814 | 8.8726 | [8 empty] | 2021-05-06
DE_MA_SPLIT GN1 HEATING COIL Heating Capacity [kBtu/hr] | SPLIT GN1 HEATING COIL Heating Capacity [kBtu/hr] | 6.3962 | 6.4549 | [8 empty] | 2021-05-06
DE_MA_SPLIT GN2 HEATING COIL Heating Capacity [kBtu/hr] | SPLIT GN2 HEATING COIL Heating Capacity [kBtu/hr] | 6.3956 | 6.4543 | [8 empty] | 2021-05-06
DE_MA_SPLIT GS1 HEATING COIL Heating Capacity [kBtu/hr] | SPLIT GS1 HEATING COIL Heating Capacity [kBtu/hr] | 6.3505 | 6.4091 | [8 empty] | 2021-05-06
DE_MA_SPLIT GS2 HEATING COIL Heating Capacity [kBtu/hr] | SPLIT GS2 HEATING COIL Heating Capacity [kBtu/hr] | 6.8425 | 6.9027 | [8 empty] | 2021-05-06
DE_MA_SPLIT MSW HEATING COIL Heating Capacity [kBtu/hr] | SPLIT MSW HEATING COIL Heating Capacity [kBtu/hr] | 16.1175 | 16.2465 | [8 empty] | 2021-05-06
DE_MA_SPLIT MNW HEATING COIL Heating Capacity [kBtu/hr] | SPLIT MNW HEATING COIL Heating Capacity [kBtu/hr] | 16.1952 | 16.3242 | [8 empty] | 2021-05-06
DE_MA_SPLIT MSE HEATING COIL Heating Capacity [kBtu/hr] | SPLIT MSE HEATING COIL Heating Capacity [kBtu/hr] | 16.0728 | 16.2018 | [8 empty] | 2021-05-06
DE_MA_SPLIT MNE HEATING COIL Heating Capacity [kBtu/hr] | SPLIT MNE HEATING COIL Heating Capacity [kBtu/hr] | 16.1505 | 16.2795 | [8 empty] | 2021-05-06
DE_MA_SPLIT MN1 HEATING COIL Heating Capacity [kBtu/hr] | SPLIT MN1 HEATING COIL Heating Capacity [kBtu/hr] | 11.0302 | 11.1548 | [8 empty] | 2021-05-06
DE_MA_SPLIT MN2 HEATING COIL Heating Capacity [kBtu/hr] | SPLIT MN2 HEATING COIL Heating Capacity [kBtu/hr] | 11.029 | 11.1536 | [8 empty] | 2021-05-06
DE_MA_SPLIT MS1 HEATING COIL Heating Capacity [kBtu/hr] | SPLIT MS1 HEATING COIL Heating Capacity [kBtu/hr] | 10.9653 | 11.0852 | [8 empty] | 2021-05-06
DE_MA_SPLIT MS2 HEATING COIL Heating Capacity [kBtu/hr] | SPLIT MS2 HEATING COIL Heating Capacity [kBtu/hr] | 10.9653 | 11.084 | [8 empty] | 2021-05-06
DE_MA_SPLIT TSW HEATING COIL Heating Capacity [kBtu/hr] | SPLIT TSW HEATING COIL Heating Capacity [kBtu/hr] | 11.3769 | 11.4385 | [8 empty] | 2021-05-06
DE_MA_SPLIT TNW HEATING COIL Heating Capacity [kBtu/hr] | SPLIT TNW HEATING COIL Heating Capacity [kBtu/hr] | 11.4235 | 11.4852 | [8 empty] | 2021-05-06
DE_MA_SPLIT TSE HEATING COIL Heating Capacity [kBtu/hr] | SPLIT TSE HEATING COIL Heating Capacity [kBtu/hr] | 11.3534 | 11.415 | [8 empty] | 2021-05-06
DE_MA_SPLIT TNE HEATING COIL Heating Capacity [kBtu/hr] | SPLIT TNE HEATING COIL Heating Capacity [kBtu/hr] | 11.4 | 11.4617 | [8 empty] | 2021-05-06
DE_MA_SPLIT TN1 HEATING COIL Heating Capacity [kBtu/hr] | SPLIT TN1 HEATING COIL Heating Capacity [kBtu/hr] | 8.6103 | 8.6717 | [8 empty] | 2021-05-06
DE_MA_SPLIT TN2 HEATING COIL Heating Capacity [kBtu/hr] | SPLIT TN2 HEATING COIL Heating Capacity [kBtu/hr] | 8.6096 | 8.671 | [8 empty] | 2021-05-06
DE_MA_SPLIT TS1 HEATING COIL Heating Capacity [kBtu/hr] | SPLIT TS1 HEATING COIL Heating Capacity [kBtu/hr] | 8.5564 | 8.6178 | [8 empty] | 2021-05-06
DE_MA_SPLIT TS2 HEATING COIL Heating Capacity [kBtu/hr] | SPLIT TS2 HEATING COIL Heating Capacity [kBtu/hr] | 8.5557 | 8.6171 | [8 empty] | 2021-05-06
DE_MA_Split_GSW ERV Flag | Split_GSW ERV Flag | Yes | Yes | [8 empty] | 2021-05-06
DE_MA_Split_GNW ERV Flag | Split_GNW ERV Flag | Yes | Yes | [8 empty] | 2021-05-06
DE_MA_Split_GNE ERV Flag | Split_GNE ERV Flag | Yes | Yes | [8 empty] | 2021-05-06
DE_MA_Split_GN1 ERV Flag | Split_GN1 ERV Flag | Yes | Yes | [8 empty] | 2021-05-06
DE_MA_Split_GN2 ERV Flag | Split_GN2 ERV Flag | Yes | Yes | [8 empty] | 2021-05-06
DE_MA_Split_GS1 ERV Flag | Split_GS1 ERV Flag | Yes | Yes | [8 empty] | 2021-05-06
DE_MA_Split_GS2 ERV Flag | Split_GS2 ERV Flag | Yes | Yes | [8 empty] | 2021-05-06
DE_MA_Split_MSW ERV Flag | Split_MSW ERV Flag | Yes | Yes | [8 empty] | 2021-05-06
DE_MA_Split_MNW ERV Flag | Split_MNW ERV Flag | Yes | Yes | [8 empty] | 2021-05-06
DE_MA_Split_MSE ERV Flag | Split_MSE ERV Flag | Yes | Yes | [8 empty] | 2021-05-06
DE_MA_Split_MNE ERV Flag | Split_MNE ERV Flag | Yes | Yes | [8 empty] | 2021-05-06
DE_MA_Split_MN1 ERV Flag | Split_MN1 ERV Flag | Yes | Yes | [8 empty] | 2021-05-06
DE_MA_Split_MN2 ERV Flag | Split_MN2 ERV Flag | Yes | Yes | [8 empty] | 2021-05-06
DE_MA_Split_MS1 ERV Flag | Split_MS1 ERV Flag | Yes | Yes | [8 empty] | 2021-05-06
DE_MA_Split_MS2 ERV Flag | Split_MS2 ERV Flag | Yes | Yes | [8 empty] | 2021-05-06
DE_MA_Split_TSW ERV Flag | Split_TSW ERV Flag | Yes | Yes | [8 empty] | 2021-05-06
DE_MA_Split_TNW ERV Flag | Split_TNW ERV Flag | Yes | Yes | [8 empty] | 2021-05-06
DE_MA_Split_TSE ERV Flag | Split_TSE ERV Flag | Yes | Yes | [8 empty] | 2021-05-06
DE_MA_Split_TNE ERV Flag | Split_TNE ERV Flag | Yes | Yes | [8 empty] | 2021-05-06
DE_MA_Split_TN1 ERV Flag | Split_TN1 ERV Flag | Yes | Yes | [8 empty] | 2021-05-06
DE_MA_Split_TN2 ERV Flag | Split_TN2 ERV Flag | Yes | Yes | [8 empty] | 2021-05-06
DE_MA_Split_TS1 ERV Flag | Split_TS1 ERV Flag | Yes | Yes | [8 empty] | 2021-05-06
DE_MA_Split_TS2 ERV Flag | Split_TS2 ERV Flag | Yes | Yes | [8 empty] | 2021-05-06
id | item | Zone1A(FL-Miami-FL) ASHRAE901-state_STD2016 | Zone1A(FL-Miami-FL) ASHRAE901-state_STD2019 | Zone2A(FL-Tampa-FL) ASHRAE901-state_STD2016 | Zone2A(FL-Tampa-FL) ASHRAE901-state_STD2019 | [6 empty] | 2021-05-06
FL_SO_PSZ-AC:1 Cooling Capacity [ton] | PSZ-AC:1 Cooling Capacity [ton] | 2.0602 | 1.9614 | 2.0483 | 1.9518 | [6 empty] | 2021-05-06
FL_SO_PSZ-AC:2 Cooling Capacity [ton] | PSZ-AC:2 Cooling Capacity [ton] | 1.8732 | 1.7751 | 1.9055 | 1.8143 | [6 empty] | 2021-05-06
FL_SO_PSZ-AC:3 Cooling Capacity [ton] | PSZ-AC:3 Cooling Capacity [ton] | 1.2715 | 1.2087 | 1.2946 | 1.2479 | [6 empty] | 2021-05-06
FL_SO_PSZ-AC:4 Cooling Capacity [ton] | PSZ-AC:4 Cooling Capacity [ton] | 1.8629 | 1.7766 | 1.8688 | 1.7775 | [6 empty] | 2021-05-06
FL_SO_PSZ-AC:5 Cooling Capacity [ton] | PSZ-AC:5 Cooling Capacity [ton] | 1.4565 | 1.3847 | 1.464 | 1.4142 | [6 empty] | 2021-05-06
FL_SO_PSZ-AC:1 Supply Flow Rate [cfm] | PSZ-AC:1 Supply Flow Rate [cfm] | 678.0416 | 635.664 | 678.0416 | 635.664 | [6 empty] | 2021-05-06
FL_SO_PSZ-AC:2 Supply Flow Rate [cfm] | PSZ-AC:2 Supply Flow Rate [cfm] | 656.8528 | 614.4752 | 656.8528 | 614.4752 | [6 empty] | 2021-05-06
FL_SO_PSZ-AC:3 Supply Flow Rate [cfm] | PSZ-AC:3 Supply Flow Rate [cfm] | 487.3424 | 444.9648 | 487.3424 | 466.1536 | [6 empty] | 2021-05-06
FL_SO_PSZ-AC:4 Supply Flow Rate [cfm] | PSZ-AC:4 Supply Flow Rate [cfm] | 635.664 | 593.2864 | 656.8528 | 614.4752 | [6 empty] | 2021-05-06
FL_SO_PSZ-AC:5 Supply Flow Rate [cfm] | PSZ-AC:5 Supply Flow Rate [cfm] | 550.9088 | 529.72 | 572.0976 | 550.9088 | [6 empty] | 2021-05-06
FL_SO_PSZ-AC:1 OA Rate [cfm] | PSZ-AC:1 OA Rate [cfm] | 136.9178 | 136.9178 | 136.9178 | 136.9178 | [6 empty] | 2021-05-06
FL_SO_PSZ-AC:2 OA Rate [cfm] | PSZ-AC:2 OA Rate [cfm] | 103.7925 | 103.7925 | 103.7925 | 103.7925 | [6 empty] | 2021-05-06
FL_SO_PSZ-AC:3 OA Rate [cfm] | PSZ-AC:3 OA Rate [cfm] | 61.5711 | 61.5711 | 61.5711 | 61.5711 | [6 empty] | 2021-05-06
FL_SO_PSZ-AC:4 OA Rate [cfm] | PSZ-AC:4 OA Rate [cfm] | 103.7925 | 103.7925 | 103.7925 | 103.7925 | [6 empty] | 2021-05-06
FL_SO_PSZ-AC:5 OA Rate [cfm] | PSZ-AC:5 OA Rate [cfm] | 61.5711 | 61.5711 | 61.5711 | 61.5711 | [6 empty] | 2021-05-06
FL_SO_PSZ-AC:1 heating Capacity [kBtu/hr] | PSZ-AC:1 heating Capacity [kBtu/hr] | 8.3407 | 8.3407 | 9.7055 | 9.7055 | [6 empty] | 2021-05-06
FL_SO_PSZ-AC:2 heating Capacity [kBtu/hr] | PSZ-AC:2 heating Capacity [kBtu/hr] | 7.5817 | 7.3543 | 10.6999 | 10.3303 | [6 empty] | 2021-05-06
FL_SO_PSZ-AC:3 heating Capacity [kBtu/hr] | PSZ-AC:3 heating Capacity [kBtu/hr] | 4.5793 | 4.453 | 6.5171 | 6.3031 | [6 empty] | 2021-05-06
FL_SO_PSZ-AC:4 heating Capacity [kBtu/hr] | PSZ-AC:4 heating Capacity [kBtu/hr] | 7.4051 | 7.209 | 10.4987 | 10.1819 | [6 empty] | 2021-05-06
FL_SO_PSZ-AC:5 heating Capacity [kBtu/hr] | PSZ-AC:5 heating Capacity [kBtu/hr] | 4.59 | 4.4574 | 6.5171 | 6.3031 | [6 empty] | 2021-05-06
id | item | Zone1A(FL-Miami-FL) ASHRAE901-state_STD2016 | Zone1A(FL-Miami-FL) ASHRAE901-state_STD2019 | Zone2A(FL-Tampa-FL) ASHRAE901-state_STD2016 | Zone2A(FL-Tampa-FL) ASHRAE901-state_STD2019 | [6 empty] | 2021-05-06
FL_LO_CAV_BAS Supply Flow Rate [cfm] | CAV_BAS Supply Flow Rate [cfm] | 11950.4832 | 11081.7424 | 11929.2944 | 11060.5536 | [6 empty] | 2021-05-06
FL_LO_VAV_BOT WITH REHEAT Supply Flow Rate [cfm] | VAV_BOT WITH REHEAT Supply Flow Rate [cfm] | 19726.7728 | 18688.5216 | 18858.032 | 17925.7248 | [6 empty] | 2021-05-06
FL_LO_VAV_MID WITH REHEAT Supply Flow Rate [cfm] | VAV_MID WITH REHEAT Supply Flow Rate [cfm] | 183812.8403 | 173811.7267 | 174002.4259 | 164933.6194 | [6 empty] | 2021-05-06
FL_LO_VAV_TOP WITH REHEAT Supply Flow Rate [cfm] | VAV_TOP WITH REHEAT Supply Flow Rate [cfm] | 19684.3952 | 18667.3328 | 18391.8784 | 17544.3264 | [6 empty] | 2021-05-06
FL_LO_Supply Air Temp. Reset Flag | Supply Air Temp. Reset Flag | No | Yes | No | No | [6 empty] | 2021-05-06
FL_LO_CAV_BAS OA Rate [cfm] | CAV_BAS OA Rate [cfm] | 2542.8255 | 2542.8255 | 2542.8255 | 2542.8255 | [6 empty] | 2021-05-06
FL_LO_VAV_BOT WITH REHEAT OA Rate [cfm] | VAV_BOT WITH REHEAT OA Rate [cfm] | 5377.8022 | 4302.174 | 5377.8022 | 4302.174 | [6 empty] | 2021-05-06
FL_LO_VAV_MID WITH REHEAT OA Rate [cfm] | VAV_MID WITH REHEAT OA Rate [cfm] | 53777.9373 | 43021.7396 | 53777.9373 | 43021.7396 | [6 empty] | 2021-05-06
FL_LO_VAV_TOP WITH REHEAT OA Rate [cfm] | VAV_TOP WITH REHEAT OA Rate [cfm] | 5377.8022 | 4302.174 | 5377.8022 | 4302.174 | [6 empty] | 2021-05-06
FL_LO_AIRLOOP DATACENTER BASEMENT OA Rate [cfm] | AIRLOOP DATACENTER BASEMENT OA Rate [cfm] | 716.9654 | 716.9654 | 716.9654 | 716.9654 | [6 empty] | 2021-05-06
FL_LO_VAV_bot_WITH_REHEAT ERV Flag | VAV_bot_WITH_REHEAT ERV Flag | Yes | Yes | Yes | Yes | [6 empty] | 2021-05-06
FL_LO_VAV_mid_WITH_REHEAT ERV Flag | VAV_mid_WITH_REHEAT ERV Flag | Yes | Yes | Yes | Yes | [6 empty] | 2021-05-06
FL_LO_VAV_top_WITH_REHEAT ERV Flag | VAV_top_WITH_REHEAT ERV Flag | Yes | Yes | Yes | Yes | [6 empty] | 2021-05-06
FL_LO_COOLSYS1 CHILLER1 Capacity [ton] | COOLSYS1 CHILLER1 Capacity [ton] | 452.7081 | 405.2219 | 440.2055 | 392.2507 | [6 empty] | 2021-05-06
FL_LO_COOLSYS1 CHILLER2 Capacity [ton] | COOLSYS1 CHILLER2 Capacity [ton] | 452.7081 | 405.2219 | 440.2055 | 392.2507 | [6 empty] | 2021-05-06
FL_LO_TOWERWATERSYS COOLTOWER 1 Capacity [ton] | TOWERWATERSYS COOLTOWER 1 Capacity [ton] | 429.6997 | 384.6346 | 417.8329 | 372.3215 | [6 empty] | 2021-05-06
FL_LO_TOWERWATERSYS COOLTOWER 2 Capacity [ton] | TOWERWATERSYS COOLTOWER 2 Capacity [ton] | 429.6997 | 384.6346 | 417.8329 | 372.3215 | [6 empty] | 2021-05-06
FL_LO_HEATSYS1 BOILER Capacity [MMBTU/h] | HEATSYS1 BOILER Capacity [MMBTU/h] | 2488.0249 | 2241.2646 | 2708.9154 | 2400.9005 | [6 empty] | 2021-05-06
FL_LO_COOLSYS1 PUMP Flow Rate [gal/min] | COOLSYS1 PUMP Flow Rate [gal/min] | 0 | 0 | 0 | 0 | [6 empty] | 2021-05-06
FL_LO_COOLSYS1 CHILLER1 PUMP Flow Rate [gal/min] | COOLSYS1 CHILLER1 PUMP Flow Rate [gal/min] | 710.7015 | 635.8706 | 691.1819 | 615.5822 | [6 empty] | 2021-05-06
FL_LO_COOLSYS1 CHILLER2 PUMP Flow Rate [gal/min] | COOLSYS1 CHILLER2 PUMP Flow Rate [gal/min] | 710.7015 | 635.8706 | 691.1819 | 615.5822 | [6 empty] | 2021-05-06
FL_LO_COOLSYS1 PUMP SECONDARY Flow Rate [gal/min] | COOLSYS1 PUMP SECONDARY Flow Rate [gal/min] | 1421.4031 | 1271.7412 | 1382.3622 | 1231.1628 | [6 empty] | 2021-05-06
FL_LO_HEATSYS1 PUMP Flow Rate [gal/min] | HEATSYS1 PUMP Flow Rate [gal/min] | 510.7006 | 460.0493 | 556.0404 | 492.8167 | [6 empty] | 2021-05-06
FL_LO_TOWERWATERSYS PUMP Flow Rate [gal/min] | TOWERWATERSYS PUMP Flow Rate [gal/min] | 2497.6939 | 2235.6881 | 2428.5865 | 2164.0446 | [6 empty] | 2021-05-06
FL_LO_PLANT CIRC PUMP Flow Rate [gal/min] | PLANT CIRC PUMP Flow Rate [gal/min] | 209.1514 | 207.9642 | 208.6457 | 207.7597 | [6 empty] | 2021-05-06
FL_LO_COOLSYS1 PUMP SECONDARY Pressure setpoint reset [yes,no] | COOLSYS1 PUMP SECONDARY Pressure setpoint reset [yes,no] | pump_ride_on_curve | pump_ride_on_curve | pump_ride_on_curve | pump_ride_on_curve | [6 empty] | 2021-05-06
FL_LO_COOLSYS1 CHILLER1 PUMP Pump Power [hp] | COOLSYS1 CHILLER1 PUMP Pump Power [hp] | 3.834 | 3.3963 | 3.7287 | 3.288 | [6 empty] | 2021-05-06
FL_LO_COOLSYS1 CHILLER2 PUMP Pump Power [hp] | COOLSYS1 CHILLER2 PUMP Pump Power [hp] | 3.834 | 3.3963 | 3.7287 | 3.288 | [6 empty] | 2021-05-06
FL_LO_COOLSYS1 PUMP SECONDARY Pump Power [hp] | COOLSYS1 PUMP SECONDARY Pump Power [hp] | 23.0039 | 20.378 | 22.3721 | 19.7278 | [6 empty] | 2021-05-06
FL_LO_HEATSYS1 PUMP Pump Power [hp] | HEATSYS1 PUMP Pump Power [hp] | 11.0391 | 9.8458 | 12.0191 | 10.547 | [6 empty] | 2021-05-06
FL_LO_TOWERWATERSYS PUMP Pump Power [hp] | TOWERWATERSYS PUMP Pump Power [hp] | 44.7176 | 39.6307 | 43.4826 | 38.3621 | [6 empty] | 2021-05-06
FL_LO_PLANT CIRC PUMP Pump Power [hp] | PLANT CIRC PUMP Pump Power [hp] | 4.5132 | 4.4432 | 4.5023 | 4.4388 | [6 empty] | 2021-05-06
FL_LO_Datacenter PLANT CIRC PUMP Pump Power [hp] | Datacenter PLANT CIRC PUMP Pump Power [hp] | 4.5132 | 4.4432 | 4.5023 | 4.4388 | [6 empty] | 2021-05-06
FL_LO_ZN_VAV_BOXes_Max_Reheat_Water_Flow_GPM | ZN_VAV_BOXes_Max_Reheat_Water_Flow_GPM | 369.3343 | 348.6867 | 346.651 | 322.0421 | [6 empty] | 2021-05-06
FL_LO_COOLSYS1 PUMP SECONDARY VSD | COOLSYS1 PUMP SECONDARY VSD | No | No | No | No | [6 empty] | 2021-05-06
FL_LO_HEATSYS1 PUMP VSD | HEATSYS1 PUMP VSD | No | No | No | No | [6 empty] | 2021-05-06
FL_LO_DATACENTER BASEMENT Cooling Capacity [ton] | DATACENTER BASEMENT Cooling Capacity [ton] | 122.4929 | 122.1311 | 122.4277 | 122.0715 | [6 empty] | 2021-05-06
FL_LO_DATACENTER BOT Cooling Capacity [ton] | DATACENTER BOT Cooling Capacity [ton] | 2.6535 | 2.6266 | 2.6496 | 2.6231 | [6 empty] | 2021-05-06
FL_LO_DATACENTER MID Cooling Capacity [ton] | DATACENTER MID Cooling Capacity [ton] | 25.4867 | 25.0404 | 25.2014 | 24.9567 | [6 empty] | 2021-05-06
FL_LO_DATACENTER TOP Cooling Capacity [ton] | DATACENTER TOP Cooling Capacity [ton] | 2.5744 | 2.5402 | 2.5583 | 2.5375 | [6 empty] | 2021-05-06
id | item | Zone1A(FL-Miami-FL) ASHRAE901-state_STD2016 | Zone1A(FL-Miami-FL) ASHRAE901-state_STD2019 | Zone2A(FL-Tampa-FL) ASHRAE901-state_STD2016 | Zone2A(FL-Tampa-FL) ASHRAE901-state_STD2019 | [6 empty] | 2021-05-06
FL_RS_PSZ-AC:1 Cooling Capacity [ton] | PSZ-AC:1 Cooling Capacity [ton] | 12.802 | 12.3713 | 11.255 | 10.8925 | [6 empty] | 2021-05-06
FL_RS_PSZ-AC:2 Cooling Capacity [ton] | PSZ-AC:2 Cooling Capacity [ton] | 54.0793 | 51.1266 | 50.95 | 47.7609 | [6 empty] | 2021-05-06
FL_RS_PSZ-AC:3 Cooling Capacity [ton] | PSZ-AC:3 Cooling Capacity [ton] | 7.053 | 6.9007 | 6.86 | 6.7319 | [6 empty] | 2021-05-06
FL_RS_PSZ-AC:4 Cooling Capacity [ton] | PSZ-AC:4 Cooling Capacity [ton] | 6.2553 | 6.0928 | 5.6458 | 5.5118 | [6 empty] | 2021-05-06
FL_RS_PSZ-AC:1 Supply Flow Rate [cfm] | PSZ-AC:1 Supply Flow Rate [cfm] | 4661.536 | 4470.8368 | 4110.6272 | 3877.5504 | [6 empty] | 2021-05-06
FL_RS_PSZ-AC:2 Supply Flow Rate [cfm] | PSZ-AC:2 Supply Flow Rate [cfm] | 16251.8096 | 15340.6912 | 15298.3136 | 14323.6288 | [6 empty] | 2021-05-06
FL_RS_PSZ-AC:3 Supply Flow Rate [cfm] | PSZ-AC:3 Supply Flow Rate [cfm] | 2436.712 | 2373.1456 | 2309.5792 | 2246.0128 | [6 empty] | 2021-05-06
FL_RS_PSZ-AC:4 Supply Flow Rate [cfm] | PSZ-AC:4 Supply Flow Rate [cfm] | 2055.3136 | 1991.7472 | 1779.8592 | 1716.2928 | [6 empty] | 2021-05-06
FL_RS_PSZ-AC:1 OA Rate [cfm] | PSZ-AC:1 OA Rate [cfm] | 490.669 | 490.669 | 490.669 | 490.669 | [6 empty] | 2021-05-06
FL_RS_PSZ-AC:2 OA Rate [cfm] | PSZ-AC:2 OA Rate [cfm] | 4005.1282 | 4005.1282 | 4005.1282 | 4005.1282 | [6 empty] | 2021-05-06
FL_RS_PSZ-AC:3 OA Rate [cfm] | PSZ-AC:3 OA Rate [cfm] | 377.3937 | 377.3937 | 377.3937 | 377.3937 | [6 empty] | 2021-05-06
FL_RS_PSZ-AC:4 OA Rate [cfm] | PSZ-AC:4 OA Rate [cfm] | 377.3937 | 377.3937 | 377.3937 | 377.3937 | [6 empty] | 2021-05-06
FL_RS_PSZ-AC:1 OA Damper [gravity, motorized] | PSZ-AC:1 OA Damper [gravity, motorized] | gravity | gravity | motorized | motorized | [6 empty] | 2021-05-06
FL_RS_PSZ-AC:2 OA Damper [gravity, motorized] | PSZ-AC:2 OA Damper [gravity, motorized] | gravity | gravity | motorized | motorized | [6 empty] | 2021-05-06
FL_RS_PSZ-AC:3 OA Damper [gravity, motorized] | PSZ-AC:3 OA Damper [gravity, motorized] | gravity | gravity | motorized | motorized | [6 empty] | 2021-05-06
FL_RS_PSZ-AC:4 OA Damper [gravity, motorized] | PSZ-AC:4 OA Damper [gravity, motorized] | gravity | gravity | motorized | motorized | [6 empty] | 2021-05-06
FL_RS_PSZ-AC:1 Heating Capacity [kBtu/hr] | PSZ-AC:1 Heating Capacity [kBtu/hr] | 182.4455 | 173.5394 | 168.8934 | 159.0236 | [6 empty] | 2021-05-06
FL_RS_PSZ-AC:2 Heating Capacity [kBtu/hr] | PSZ-AC:2 Heating Capacity [kBtu/hr] | 686.6962 | 648.2479 | 690.8604 | 652.7634 | [6 empty] | 2021-05-06
FL_RS_PSZ-AC:3 Heating Capacity [kBtu/hr] | PSZ-AC:3 Heating Capacity [kBtu/hr] | 97.6103 | 95.1071 | 98.7532 | 96.3492 | [6 empty] | 2021-05-06
FL_RS_PSZ-AC:4 Heating Capacity [kBtu/hr] | PSZ-AC:4 Heating Capacity [kBtu/hr] | 85.5302 | 82.7506 | 79.1632 | 76.618 | [6 empty] | 2021-05-06
id | item | Zone1A(FL-Miami-FL) ASHRAE901-state_STD2016 | Zone1A(FL-Miami-FL) ASHRAE901-state_STD2019 | Zone2A(FL-Tampa-FL) ASHRAE901-state_STD2016 | Zone2A(FL-Tampa-FL) ASHRAE901-state_STD2019 | [6 empty] | 2021-05-06
FL_PS_VAV_POD_1 Cooling Capacity [ton] | VAV_POD_1 Cooling Capacity [ton] | 19.7695 | 18.5316 | 19.0769 | 18.2921 | [6 empty] | 2021-05-06
FL_PS_VAV_POD_2 Cooling Capacity [ton] | VAV_POD_2 Cooling Capacity [ton] | 19.8611 | 18.5115 | 19.0943 | 18.2662 | [6 empty] | 2021-05-06
FL_PS_VAV_POD_3 Cooling Capacity [ton] | VAV_POD_3 Cooling Capacity [ton] | 18.0522 | 16.7353 | 17.4476 | 16.4377 | [6 empty] | 2021-05-06
FL_PS_VAV_OTHER Cooling Capacity [ton] | VAV_OTHER Cooling Capacity [ton] | 27.7392 | 25.862 | 26.3197 | 24.5881 | [6 empty] | 2021-05-06
FL_PS_PSZ-AC_1:6 Cooling Capacity [ton] | PSZ-AC_1:6 Cooling Capacity [ton] | 8.4987 | 8.0928 | 8.3546 | 7.9781 | [6 empty] | 2021-05-06
FL_PS_PSZ-AC_2:5 Cooling Capacity [ton] | PSZ-AC_2:5 Cooling Capacity [ton] | 5.6402 | 5.362 | 5.2265 | 5.0664 | [6 empty] | 2021-05-06
FL_PS_PSZ-AC_2:7 Cooling Capacity [ton] | PSZ-AC_2:7 Cooling Capacity [ton] | 10.5074 | 10.5074 | 10.5074 | 10.5074 | [6 empty] | 2021-05-06
FL_PS_VAV_POD_1 Supply Flow Rate [cfm] | VAV_POD_1 Supply Flow Rate [cfm] | 5932.864 | 5551.4656 | 5720.976 | 5487.8992 | [6 empty] | 2021-05-06
FL_PS_VAV_POD_2 Supply Flow Rate [cfm] | VAV_POD_2 Supply Flow Rate [cfm] | 5954.0528 | 5551.4656 | 5720.976 | 5487.8992 | [6 empty] | 2021-05-06
FL_PS_VAV_POD_3 Supply Flow Rate [cfm] | VAV_POD_3 Supply Flow Rate [cfm] | 5424.3328 | 5021.7456 | 5233.6336 | 4936.9904 | [6 empty] | 2021-05-06
FL_PS_VAV_OTHER Supply Flow Rate [cfm] | VAV_OTHER Supply Flow Rate [cfm] | 8327.1984 | 7755.1008 | 7903.4224 | 7373.7024 | [6 empty] | 2021-05-06
FL_PS_PSZ-AC_2:5 Supply Flow Rate [cfm] | PSZ-AC_2:5 Supply Flow Rate [cfm] | 1695.104 | 1610.3488 | 1567.9712 | 1525.5936 | [6 empty] | 2021-05-06
FL_PS_PSZ-AC_1:6 Supply Flow Rate [cfm] | PSZ-AC_1:6 Supply Flow Rate [cfm] | 2542.656 | 2436.712 | 2500.2784 | 2394.3344 | [6 empty] | 2021-05-06
FL_PS_PSZ-AC_2:7 Supply Flow Rate [cfm] | PSZ-AC_2:7 Supply Flow Rate [cfm] | 3157.1312 | 3157.1312 | 3157.1312 | 3157.1312 | [6 empty] | 2021-05-06
FL_PS_Supply Air Temp. Reset Flag | Supply Air Temp. Reset Flag | No | No | No | No | [6 empty] | 2021-05-06
FL_PS_VAV_POD_1 OA Rate [cfm] | VAV_POD_1 OA Rate [cfm] | 5932.5038 | 5561.0218 | 5724.6417 | 5489.1705 | [6 empty] | 2021-05-06
FL_PS_VAV_POD_2 OA Rate [cfm] | VAV_POD_2 OA Rate [cfm] | 5957.888 | 5554.9829 | 5729.0913 | 5481.3942 | [6 empty] | 2021-05-06
FL_PS_VAV_POD_3 OA Rate [cfm] | VAV_POD_3 OA Rate [cfm] | 5417.171 | 5021.9787 | 5235.7313 | 4932.6679 | [6 empty] | 2021-05-06
FL_PS_VAV_OTHER OA Rate [cfm] | VAV_OTHER OA Rate [cfm] | 3736.1787 | 2988.8921 | 3736.1787 | 2988.8921 | [6 empty] | 2021-05-06
FL_PS_PSZ-AC_2:5 OA Rate [cfm] | PSZ-AC_2:5 OA Rate [cfm] | 1152.7343 | 1152.7343 | 1152.7343 | 1152.7343 | [6 empty] | 2021-05-06
FL_PS_PSZ-AC_1:6 OA Rate [cfm] | PSZ-AC_1:6 OA Rate [cfm] | 539.9118 | 539.9118 | 539.9118 | 539.9118 | [6 empty] | 2021-05-06
FL_PS_PSZ-AC_2:7 OA Rate [cfm] | PSZ-AC_2:7 OA Rate [cfm] | 3153.0841 | 3153.0841 | 3153.0841 | 3153.0841 | [6 empty] | 2021-05-06
FL_PS_VAV_POD_1 OA Damper [gravity, motorized] | VAV_POD_1 OA Damper [gravity, motorized] | gravity | gravity | motorized | motorized | [6 empty] | 2021-05-06
FL_PS_VAV_POD_2 OA Damper [gravity, motorized] | VAV_POD_2 OA Damper [gravity, motorized] | gravity | gravity | motorized | motorized | [6 empty] | 2021-05-06
FL_PS_VAV_POD_3 OA Damper [gravity, motorized] | VAV_POD_3 OA Damper [gravity, motorized] | gravity | gravity | motorized | motorized | [6 empty] | 2021-05-06
FL_PS_VAV_OTHER OA Damper [gravity, motorized] | VAV_OTHER OA Damper [gravity, motorized] | gravity | gravity | motorized | motorized | [6 empty] | 2021-05-06
FL_PS_PSZ-AC_2:5 OA Damper [gravity, motorized] | PSZ-AC_2:5 OA Damper [gravity, motorized] | gravity | gravity | motorized | motorized | [6 empty] | 2021-05-06
FL_PS_PSZ-AC_1:6 OA Damper [gravity, motorized] | PSZ-AC_1:6 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2021-05-06
FL_PS_PSZ-AC_2:7 OA Damper [gravity, motorized] | PSZ-AC_2:7 OA Damper [gravity, motorized] | gravity | gravity | motorized | motorized | [6 empty] | 2021-05-06
FL_PS_VAV_POD_1 (economizer) | VAV_POD_1 (economizer) | No | No | DifferentialEnthalpy | DifferentialEnthalpy | [6 empty] | 2021-05-06
FL_PS_VAV_POD_2 (economizer) | VAV_POD_2 (economizer) | No | No | DifferentialEnthalpy | DifferentialEnthalpy | [6 empty] | 2021-05-06
FL_PS_VAV_POD_3 (economizer) | VAV_POD_3 (economizer) | No | No | DifferentialEnthalpy | DifferentialEnthalpy | [6 empty] | 2021-05-06
FL_PS_VAV_OTHER (economizer) | VAV_OTHER (economizer) | No | No | DifferentialEnthalpy | DifferentialEnthalpy | [6 empty] | 2021-05-06
FL_PS_PSZ-AC_2:5 (economizer) | PSZ-AC_2:5 (economizer) | No | No | DifferentialEnthalpy | DifferentialEnthalpy | [6 empty] | 2021-05-06
FL_PS_PSZ-AC_1:6 (economizer) | PSZ-AC_1:6 (economizer) | No | No | DifferentialEnthalpy | DifferentialEnthalpy | [6 empty] | 2021-05-06
FL_PS_PSZ-AC_2:7 (economizer) | PSZ-AC_2:7 (economizer) | No | No | DifferentialEnthalpy | DifferentialEnthalpy | [6 empty] | 2021-05-06
FL_PS_VAV_Pod_1_ERV Flag | VAV_Pod_1_ERV Flag | Yes | Yes | Yes | Yes | [6 empty] | 2021-05-06
FL_PS_VAV_Pod_2_ERV Flag | VAV_Pod_2_ERV Flag | Yes | Yes | Yes | Yes | [6 empty] | 2021-05-06
FL_PS_VAV_Pod_3_ERV Flag | VAV_Pod_3_ERV Flag | Yes | Yes | Yes | Yes | [6 empty] | 2021-05-06
FL_PS_VAV_OTHER_ERV Flag | VAV_OTHER_ERV Flag | Yes | Yes | Yes | Yes | [6 empty] | 2021-05-06
FL_PS_PSZ_AC_2_5_ERV Flag | PSZ_AC_2_5_ERV Flag | No | Yes | Yes | Yes | [6 empty] | 2021-05-06
FL_PS_PSZ_AC_2_7_ERV Flag | PSZ_AC_2_7_ERV Flag | Yes | Yes | Yes | Yes | [6 empty] | 2021-05-06
FL_PS_HEATSYS1 Capacity [MMBTU/h] | HEATSYS1 Capacity [MMBTU/h] | 0.58075 | 0.52665 | 0.67777 | 0.63346 | [6 empty] | 2021-05-06
FL_PS_HEATSYS1 Flow Rate [gal/min] | HEATSYS1 Flow Rate [gal/min] | 59.6032 | 54.0512 | 69.561 | 65.0128 | [6 empty] | 2021-05-06
FL_PS_VAV_POD_1 Fan Power [hp] | VAV_POD_1 Fan Power [hp] | 8.7522 | 8.2042 | 8.4456 | 8.0982 | [6 empty] | 2021-05-06
FL_PS_VAV_POD_2 Fan Power [hp] | VAV_POD_2 Fan Power [hp] | 8.7928 | 8.1953 | 8.4533 | 8.0867 | [6 empty] | 2021-05-06
FL_PS_VAV_POD_3 Fan Power [hp] | VAV_POD_3 Fan Power [hp] | 7.992 | 7.4089 | 7.7243 | 7.2772 | [6 empty] | 2021-05-06
FL_PS_VAV_OTHER Fan Power [hp] | VAV_OTHER Fan Power [hp] | 11.5323 | 10.7518 | 11.5638 | 10.803 | [6 empty] | 2021-05-06
FL_PS_HEATSYS1 Pump Power [hp] | HEATSYS1 Pump Power [hp] | 1.2884 | 1.1568 | 1.5036 | 1.3914 | [6 empty] | 2021-05-06
FL_PS_PSZ-AC_1:6 Heating Capacity [kBtu/hr] | PSZ-AC_1:6 Heating Capacity [kBtu/hr] | 189.3994 | 179.9172 | 191.5066 | 182.7045 | [6 empty] | 2021-05-06
FL_PS_PSZ-AC_2:5 Heating Capacity [kBtu/hr] | PSZ-AC_2:5 Heating Capacity [kBtu/hr] | 90.183 | 87.0951 | 97.0918 | 95.3136 | [6 empty] | 2021-05-06
FL_PS_PSZ-AC_2:7 Heating Capacity [kBtu/hr] | PSZ-AC_2:7 Heating Capacity [kBtu/hr] | 192.0781 | 192.0781 | 223.5076 | 223.5076 | [6 empty] | 2021-05-06
FL_PS_ZN_VAV_BOXes_Max_Reheat_Water_Flow_GPM | ZN_VAV_BOXes_Max_Reheat_Water_Flow_GPM | 53.3054 | 48.1795 | 55.9974 | 52.1699 | [6 empty] | 2021-05-06
id | item | Zone1A(FL-Miami-FL) ASHRAE901-state_STD2016 | Zone1A(FL-Miami-FL) ASHRAE901-state_STD2019 | Zone2A(FL-Tampa-FL) ASHRAE901-state_STD2016 | Zone2A(FL-Tampa-FL) ASHRAE901-state_STD2019 | [6 empty] | 2021-05-06
FL_SH_SAC_FRONTOFFICE Cooling Capacity [ton] | SAC_FRONTOFFICE Cooling Capacity [ton] | 2.59 | 2.4573 | 2.5815 | 2.4543 | [6 empty] | 2021-05-06
FL_SH_SAC_FRONTLOUNGE Cooling Capacity [ton] | SAC_FRONTLOUNGE Cooling Capacity [ton] | 6.3461 | 6.0226 | 6.2379 | 5.9162 | [6 empty] | 2021-05-06
FL_SH_SAC_MEETINGROOM Cooling Capacity [ton] | SAC_MEETINGROOM Cooling Capacity [ton] | 3.0045 | 2.9022 | 2.9731 | 2.8781 | [6 empty] | 2021-05-06
FL_SH_SAC_EXC_EMPLGE_RESTRM Cooling Capacity [ton] | SAC_EXC_EMPLGE_RESTRM Cooling Capacity [ton] | 6.0876 | 6.0498 | 6.1742 | 6.1359 | [6 empty] | 2021-05-06
FL_SH_SAC_FO_ADDAQ SUPPLY FAN Supply Flow Rate [cfm] | SAC_FO_ADDAQ SUPPLY FAN Supply Flow Rate [cfm] | 826.3632 | 783.9856 | 826.3632 | 783.9856 | [6 empty] | 2021-05-06
FL_SH_SAC_FL_ADDAQ SUPPLY FAN Supply Flow Rate [cfm] | SAC_FL_ADDAQ SUPPLY FAN Supply Flow Rate [cfm] | 1906.992 | 1801.048 | 1864.6144 | 1779.8592 | [6 empty] | 2021-05-06
FL_SH_SAC_MR_ADDAQ SUPPLY FAN Supply Flow Rate [cfm] | SAC_MR_ADDAQ SUPPLY FAN Supply Flow Rate [cfm] | 911.1184 | 868.7408 | 889.9296 | 868.7408 | [6 empty] | 2021-05-06
FL_SH_SAC_EXC_ADDAQ SUPPLY FAN Supply Flow Rate [cfm] | SAC_EXC_ADDAQ SUPPLY FAN Supply Flow Rate [cfm] | 2140.0688 | 2118.88 | 2182.4464 | 2161.2576 | [6 empty] | 2021-05-06
FL_SH_SAC_Exc_EmpLge_RestRm OA Rate [cfm] | SAC_Exc_EmpLge_RestRm OA Rate [cfm] | 199.9928 | 199.9928 | 199.9928 | 199.9928 | [6 empty] | 2021-05-06
FL_SH_SAC_FrontLounge OA Rate [cfm] | SAC_FrontLounge OA Rate [cfm] | 500.0133 | 500.0133 | 500.0133 | 500.0133 | [6 empty] | 2021-05-06
FL_SH_SAC_FrontOffice OA Rate [cfm] | SAC_FrontOffice OA Rate [cfm] | 119.2938 | 119.2938 | 119.2938 | 119.2938 | [6 empty] | 2021-05-06
FL_SH_SAC_MeetingRoom OA Rate [cfm] | SAC_MeetingRoom OA Rate [cfm] | 267.7629 | 267.7629 | 267.7629 | 267.7629 | [6 empty] | 2021-05-06
FL_SH_SAC_FrontLounge OA Damper [gravity, motorized] | SAC_FrontLounge OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2021-05-06
FL_SH_SAC_FrontOffice (economizer) | SAC_FrontOffice (economizer) | No | No | No | No | [6 empty] | 2021-05-06
FL_SH_SAC_FrontLounge (economizer) | SAC_FrontLounge (economizer) | No | No | DifferentialEnthalpy | DifferentialEnthalpy | [6 empty] | 2021-05-06
FL_SH_SAC_MeetingRoom (economizer) | SAC_MeetingRoom (economizer) | No | No | No | No | [6 empty] | 2021-05-06
FL_SH_SAC_Exc_EmpLge_RestRm (economizer) | SAC_Exc_EmpLge_RestRm (economizer) | No | No | DifferentialEnthalpy | DifferentialEnthalpy | [6 empty] | 2021-05-06
FL_SH_SAC_FRONTOFFICE Heating Capacity [kBtu/hr] | SAC_FRONTOFFICE Heating Capacity [kBtu/hr] | 33.4238 | 31.3583 | 34.6276 | 32.6416 | [6 empty] | 2021-05-06
FL_SH_SAC_FRONTLOUNGE Heating Capacity [kBtu/hr] | SAC_FRONTLOUNGE Heating Capacity [kBtu/hr] | 82.0869 | 78.5187 | 85.9075 | 82.3562 | [6 empty] | 2021-05-06
FL_SH_SAC_MEETINGROOM Heating Capacity [kBtu/hr] | SAC_MEETINGROOM Heating Capacity [kBtu/hr] | 39.6123 | 38.4841 | 41.9486 | 40.9003 | [6 empty] | 2021-05-06
FL_SH_SAC_EXC_EMPLGE_RESTRM Heating Capacity [kBtu/hr] | SAC_EXC_EMPLGE_RESTRM Heating Capacity [kBtu/hr] | 83.6045 | 82.9862 | 86.7118 | 86.1913 | [6 empty] | 2021-05-06
id | item | Zone1A(FL-Miami-FL) ASHRAE901-state_STD2016 | Zone1A(FL-Miami-FL) ASHRAE901-state_STD2019 | Zone2A(FL-Tampa-FL) ASHRAE901-state_STD2016 | Zone2A(FL-Tampa-FL) ASHRAE901-state_STD2019 | [6 empty] | 2021-05-06
FL_MA_SPLIT GSW COOLING COIL Cooling Capacity [ton] | SPLIT GSW COOLING COIL Cooling Capacity [ton] | 1.061 | 1.0389 | 0.98272 | 0.97232 | [6 empty] | 2021-05-06
FL_MA_SPLIT GNW COOLING COIL Cooling Capacity [ton] | SPLIT GNW COOLING COIL Cooling Capacity [ton] | 1.0702 | 1.0451 | 0.94662 | 0.93628 | [6 empty] | 2021-05-06
FL_MA_SPLIT OFFICE COOLING COIL Cooling Capacity [ton] | SPLIT OFFICE COOLING COIL Cooling Capacity [ton] | 1.911 | 1.8054 | 1.8273 | 1.7703 | [6 empty] | 2021-05-06
FL_MA_SPLIT GNE COOLING COIL Cooling Capacity [ton] | SPLIT GNE COOLING COIL Cooling Capacity [ton] | 0.93958 | 0.92064 | 0.84929 | 0.83999 | [6 empty] | 2021-05-06
FL_MA_SPLIT GN1 COOLING COIL Cooling Capacity [ton] | SPLIT GN1 COOLING COIL Cooling Capacity [ton] | 0.79933 | 0.78569 | 0.72523 | 0.717 | [6 empty] | 2021-05-06
FL_MA_SPLIT GN2 COOLING COIL Cooling Capacity [ton] | SPLIT GN2 COOLING COIL Cooling Capacity [ton] | 0.7972 | 0.78367 | 0.72357 | 0.71534 | [6 empty] | 2021-05-06
FL_MA_SPLIT GS1 COOLING COIL Cooling Capacity [ton] | SPLIT GS1 COOLING COIL Cooling Capacity [ton] | 0.78093 | 0.76833 | 0.76172 | 0.75314 | [6 empty] | 2021-05-06
FL_MA_SPLIT GS2 COOLING COIL Cooling Capacity [ton] | SPLIT GS2 COOLING COIL Cooling Capacity [ton] | 0.81698 | 0.80117 | 0.79517 | 0.78394 | [6 empty] | 2021-05-06
FL_MA_SPLIT MSW COOLING COIL Cooling Capacity [ton] | SPLIT MSW COOLING COIL Cooling Capacity [ton] | 2.2639 | 2.2106 | 2.0624 | 2.0396 | [6 empty] | 2021-05-06
FL_MA_SPLIT MNW COOLING COIL Cooling Capacity [ton] | SPLIT MNW COOLING COIL Cooling Capacity [ton] | 2.3052 | 2.249 | 1.9951 | 1.973 | [6 empty] | 2021-05-06
FL_MA_SPLIT MSE COOLING COIL Cooling Capacity [ton] | SPLIT MSE COOLING COIL Cooling Capacity [ton] | 1.9308 | 1.8797 | 1.8476 | 1.8229 | [6 empty] | 2021-05-06
FL_MA_SPLIT MNE COOLING COIL Cooling Capacity [ton] | SPLIT MNE COOLING COIL Cooling Capacity [ton] | 1.9703 | 1.9182 | 1.7429 | 1.7222 | [6 empty] | 2021-05-06
FL_MA_SPLIT MN1 COOLING COIL Cooling Capacity [ton] | SPLIT MN1 COOLING COIL Cooling Capacity [ton] | 1.6289 | 1.5967 | 1.4416 | 1.4252 | [6 empty] | 2021-05-06
FL_MA_SPLIT MN2 COOLING COIL Cooling Capacity [ton] | SPLIT MN2 COOLING COIL Cooling Capacity [ton] | 1.6237 | 1.5918 | 1.4373 | 1.4209 | [6 empty] | 2021-05-06
FL_MA_SPLIT MS1 COOLING COIL Cooling Capacity [ton] | SPLIT MS1 COOLING COIL Cooling Capacity [ton] | 1.5859 | 1.5588 | 1.5147 | 1.4969 | [6 empty] | 2021-05-06
FL_MA_SPLIT MS2 COOLING COIL Cooling Capacity [ton] | SPLIT MS2 COOLING COIL Cooling Capacity [ton] | 1.5811 | 1.5544 | 1.5107 | 1.4928 | [6 empty] | 2021-05-06
FL_MA_SPLIT TSW COOLING COIL Cooling Capacity [ton] | SPLIT TSW COOLING COIL Cooling Capacity [ton] | 1.3542 | 1.3236 | 1.2499 | 1.2385 | [6 empty] | 2021-05-06
FL_MA_SPLIT TNW COOLING COIL Cooling Capacity [ton] | SPLIT TNW COOLING COIL Cooling Capacity [ton] | 1.3668 | 1.3361 | 1.2111 | 1.1997 | [6 empty] | 2021-05-06
FL_MA_SPLIT TSE COOLING COIL Cooling Capacity [ton] | SPLIT TSE COOLING COIL Cooling Capacity [ton] | 1.1955 | 1.1736 | 1.1502 | 1.1388 | [6 empty] | 2021-05-06
FL_MA_SPLIT TNE COOLING COIL Cooling Capacity [ton] | SPLIT TNE COOLING COIL Cooling Capacity [ton] | 1.1853 | 1.1629 | 1.0811 | 1.0705 | [6 empty] | 2021-05-06
FL_MA_SPLIT TN1 COOLING COIL Cooling Capacity [ton] | SPLIT TN1 COOLING COIL Cooling Capacity [ton] | 0.97513 | 0.95969 | 0.88002 | 0.87134 | [6 empty] | 2021-05-06
FL_MA_SPLIT TN2 COOLING COIL Cooling Capacity [ton] | SPLIT TN2 COOLING COIL Cooling Capacity [ton] | 0.96955 | 0.95446 | 0.87517 | 0.86651 | [6 empty] | 2021-05-06
FL_MA_SPLIT TS1 COOLING COIL Cooling Capacity [ton] | SPLIT TS1 COOLING COIL Cooling Capacity [ton] | 0.97299 | 0.9574 | 0.9605 | 0.95057 | [6 empty] | 2021-05-06
FL_MA_SPLIT TS2 COOLING COIL Cooling Capacity [ton] | SPLIT TS2 COOLING COIL Cooling Capacity [ton] | 0.97423 | 0.95877 | 0.96262 | 0.95265 | [6 empty] | 2021-05-06
FL_MA_Split GN1 Furnace with DX Cooling OA Rate [cfm] | Split GN1 Furnace with DX Cooling OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | [6 empty] | 2021-05-06
FL_MA_Split GN2 Furnace with DX Cooling OA Rate [cfm] | Split GN2 Furnace with DX Cooling OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | [6 empty] | 2021-05-06
FL_MA_Split GNE Furnace with DX Cooling OA Rate [cfm] | Split GNE Furnace with DX Cooling OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | [6 empty] | 2021-05-06
FL_MA_Split GNW Furnace with DX Cooling OA Rate [cfm] | Split GNW Furnace with DX Cooling OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | [6 empty] | 2021-05-06
FL_MA_Split GS1 Furnace with DX Cooling OA Rate [cfm] | Split GS1 Furnace with DX Cooling OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | [6 empty] | 2021-05-06
FL_MA_Split GS2 Furnace with DX Cooling OA Rate [cfm] | Split GS2 Furnace with DX Cooling OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | [6 empty] | 2021-05-06
FL_MA_Split GSW Furnace with DX Cooling OA Rate [cfm] | Split GSW Furnace with DX Cooling OA Rate [cfm] | 56.9945 | 56.9945 | 56.9945 | 56.9945 | [6 empty] | 2021-05-06
FL_MA_Split MN1 Furnace with DX Cooling OA Rate [cfm] | Split MN1 Furnace with DX Cooling OA Rate [cfm] | 109.9824 | 109.9824 | 109.9824 | 109.9824 | [6 empty] | 2021-05-06
FL_MA_Split MN2 Furnace with DX Cooling OA Rate [cfm] | Split MN2 Furnace with DX Cooling OA Rate [cfm] | 109.9824 | 109.9824 | 109.9824 | 109.9824 | [6 empty] | 2021-05-06
FL_MA_Split MNE Furnace with DX Cooling OA Rate [cfm] | Split MNE Furnace with DX Cooling OA Rate [cfm] | 109.9824 | 109.9824 | 109.9824 | 109.9824 | [6 empty] | 2021-05-06
FL_MA_Split MNW Furnace with DX Cooling OA Rate [cfm] | Split MNW Furnace with DX Cooling OA Rate [cfm] | 109.9824 | 109.9824 | 109.9824 | 109.9824 | [6 empty] | 2021-05-06
FL_MA_Split MS1 Furnace with DX Cooling OA Rate [cfm] | Split MS1 Furnace with DX Cooling OA Rate [cfm] | 109.9824 | 109.9824 | 109.9824 | 109.9824 | [6 empty] | 2021-05-06
FL_MA_Split MS2 Furnace with DX Cooling OA Rate [cfm] | Split MS2 Furnace with DX Cooling OA Rate [cfm] | 109.9824 | 109.9824 | 109.9824 | 109.9824 | [6 empty] | 2021-05-06
FL_MA_Split MSE Furnace with DX Cooling OA Rate [cfm] | Split MSE Furnace with DX Cooling OA Rate [cfm] | 109.9824 | 109.9824 | 109.9824 | 109.9824 | [6 empty] | 2021-05-06
FL_MA_Split MSW Furnace with DX Cooling OA Rate [cfm] | Split MSW Furnace with DX Cooling OA Rate [cfm] | 109.9824 | 109.9824 | 109.9824 | 109.9824 | [6 empty] | 2021-05-06
FL_MA_Split Office Furnace with DX Cooling OA Rate [cfm] | Split Office Furnace with DX Cooling OA Rate [cfm] | 80.7372 | 80.7372 | 80.7372 | 80.7372 | [6 empty] | 2021-05-06
FL_MA_Split TN1 Furnace with DX Cooling OA Rate [cfm] | Split TN1 Furnace with DX Cooling OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | [6 empty] | 2021-05-06
FL_MA_Split TN2 Furnace with DX Cooling OA Rate [cfm] | Split TN2 Furnace with DX Cooling OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | [6 empty] | 2021-05-06
FL_MA_Split TNE Furnace with DX Cooling OA Rate [cfm] | Split TNE Furnace with DX Cooling OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | [6 empty] | 2021-05-06
FL_MA_Split TNW Furnace with DX Cooling OA Rate [cfm] | Split TNW Furnace with DX Cooling OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | [6 empty] | 2021-05-06
FL_MA_Split TS1 Furnace with DX Cooling OA Rate [cfm] | Split TS1 Furnace with DX Cooling OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | [6 empty] | 2021-05-06
FL_MA_Split TS2 Furnace with DX Cooling OA Rate [cfm] | Split TS2 Furnace with DX Cooling OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | [6 empty] | 2021-05-06
FL_MA_Split TSE Furnace with DX Cooling OA Rate [cfm] | Split TSE Furnace with DX Cooling OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | [6 empty] | 2021-05-06
FL_MA_Split TSW Furnace with DX Cooling OA Rate [cfm] | Split TSW Furnace with DX Cooling OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | [6 empty] | 2021-05-06
FL_MA_SPLIT GSW HEATING COIL Heating Capacity [kBtu/hr] | SPLIT GSW HEATING COIL Heating Capacity [kBtu/hr] | 3.472 | 3.472 | 4.0401 | 4.0401 | [6 empty] | 2021-05-06
FL_MA_SPLIT GNW HEATING COIL Heating Capacity [kBtu/hr] | SPLIT GNW HEATING COIL Heating Capacity [kBtu/hr] | 3.3499 | 3.3499 | 3.8981 | 3.8981 | [6 empty] | 2021-05-06
FL_MA_SPLIT OFFICE HEATING COIL Heating Capacity [kBtu/hr] | SPLIT OFFICE HEATING COIL Heating Capacity [kBtu/hr] | 9.2774 | 9.223 | 11.3432 | 11.2156 | [6 empty] | 2021-05-06
FL_MA_SPLIT GNE HEATING COIL Heating Capacity [kBtu/hr] | SPLIT GNE HEATING COIL Heating Capacity [kBtu/hr] | 3.3499 | 3.3499 | 3.8981 | 3.8981 | [6 empty] | 2021-05-06
FL_MA_SPLIT GN1 HEATING COIL Heating Capacity [kBtu/hr] | SPLIT GN1 HEATING COIL Heating Capacity [kBtu/hr] | 3.3499 | 3.3499 | 3.8981 | 3.8981 | [6 empty] | 2021-05-06
FL_MA_SPLIT GN2 HEATING COIL Heating Capacity [kBtu/hr] | SPLIT GN2 HEATING COIL Heating Capacity [kBtu/hr] | 3.3499 | 3.3499 | 3.8981 | 3.8981 | [6 empty] | 2021-05-06
FL_MA_SPLIT GS1 HEATING COIL Heating Capacity [kBtu/hr] | SPLIT GS1 HEATING COIL Heating Capacity [kBtu/hr] | 3.3499 | 3.3499 | 3.8981 | 3.8981 | [6 empty] | 2021-05-06
FL_MA_SPLIT GS2 HEATING COIL Heating Capacity [kBtu/hr] | SPLIT GS2 HEATING COIL Heating Capacity [kBtu/hr] | 3.3499 | 3.3499 | 3.8981 | 3.8981 | [6 empty] | 2021-05-06
FL_MA_SPLIT MSW HEATING COIL Heating Capacity [kBtu/hr] | SPLIT MSW HEATING COIL Heating Capacity [kBtu/hr] | 6.6998 | 6.6998 | 7.7961 | 7.7961 | [6 empty] | 2021-05-06
FL_MA_SPLIT MNW HEATING COIL Heating Capacity [kBtu/hr] | SPLIT MNW HEATING COIL Heating Capacity [kBtu/hr] | 6.6998 | 6.6998 | 7.7961 | 7.7961 | [6 empty] | 2021-05-06
FL_MA_SPLIT MSE HEATING COIL Heating Capacity [kBtu/hr] | SPLIT MSE HEATING COIL Heating Capacity [kBtu/hr] | 6.6998 | 6.6998 | 7.7961 | 7.7961 | [6 empty] | 2021-05-06
FL_MA_SPLIT MNE HEATING COIL Heating Capacity [kBtu/hr] | SPLIT MNE HEATING COIL Heating Capacity [kBtu/hr] | 6.6998 | 6.6998 | 7.7961 | 7.7961 | [6 empty] | 2021-05-06
FL_MA_SPLIT MN1 HEATING COIL Heating Capacity [kBtu/hr] | SPLIT MN1 HEATING COIL Heating Capacity [kBtu/hr] | 6.6998 | 6.6998 | 7.7961 | 7.7961 | [6 empty] | 2021-05-06
FL_MA_SPLIT MN2 HEATING COIL Heating Capacity [kBtu/hr] | SPLIT MN2 HEATING COIL Heating Capacity [kBtu/hr] | 6.6998 | 6.6998 | 7.7961 | 7.7961 | [6 empty] | 2021-05-06
FL_MA_SPLIT MS1 HEATING COIL Heating Capacity [kBtu/hr] | SPLIT MS1 HEATING COIL Heating Capacity [kBtu/hr] | 6.6998 | 6.6998 | 7.7961 | 7.7961 | [6 empty] | 2021-05-06
FL_MA_SPLIT MS2 HEATING COIL Heating Capacity [kBtu/hr] | SPLIT MS2 HEATING COIL Heating Capacity [kBtu/hr] | 6.6998 | 6.6998 | 7.7961 | 7.7961 | [6 empty] | 2021-05-06
FL_MA_SPLIT TSW HEATING COIL Heating Capacity [kBtu/hr] | SPLIT TSW HEATING COIL Heating Capacity [kBtu/hr] | 4.4389 | 4.4135 | 5.4858 | 5.4261 | [6 empty] | 2021-05-06
FL_MA_SPLIT TNW HEATING COIL Heating Capacity [kBtu/hr] | SPLIT TNW HEATING COIL Heating Capacity [kBtu/hr] | 4.4471 | 4.419 | 5.5118 | 5.4483 | [6 empty] | 2021-05-06
FL_MA_SPLIT TSE HEATING COIL Heating Capacity [kBtu/hr] | SPLIT TSE HEATING COIL Heating Capacity [kBtu/hr] | 4.4368 | 4.4136 | 5.4858 | 5.4261 | [6 empty] | 2021-05-06
FL_MA_SPLIT TNE HEATING COIL Heating Capacity [kBtu/hr] | SPLIT TNE HEATING COIL Heating Capacity [kBtu/hr] | 4.4451 | 4.4191 | 5.5118 | 5.4483 | [6 empty] | 2021-05-06
FL_MA_SPLIT TN1 HEATING COIL Heating Capacity [kBtu/hr] | SPLIT TN1 HEATING COIL Heating Capacity [kBtu/hr] | 3.3499 | 3.3499 | 4.0713 | 4.0509 | [6 empty] | 2021-05-06
FL_MA_SPLIT TN2 HEATING COIL Heating Capacity [kBtu/hr] | SPLIT TN2 HEATING COIL Heating Capacity [kBtu/hr] | 3.3499 | 3.3499 | 4.0713 | 4.0509 | [6 empty] | 2021-05-06
FL_MA_SPLIT TS1 HEATING COIL Heating Capacity [kBtu/hr] | SPLIT TS1 HEATING COIL Heating Capacity [kBtu/hr] | 3.3499 | 3.3499 | 4.0379 | 4.021 | [6 empty] | 2021-05-06
FL_MA_SPLIT TS2 HEATING COIL Heating Capacity [kBtu/hr] | SPLIT TS2 HEATING COIL Heating Capacity [kBtu/hr] | 3.3499 | 3.3499 | 4.0379 | 4.021 | [6 empty] | 2021-05-06
FL_MA_Split_GSW ERV Flag | Split_GSW ERV Flag | No | Yes | No | Yes | [6 empty] | 2021-05-06
FL_MA_Split_GNW ERV Flag | Split_GNW ERV Flag | No | Yes | No | Yes | [6 empty] | 2021-05-06
FL_MA_Split_GNE ERV Flag | Split_GNE ERV Flag | No | Yes | No | Yes | [6 empty] | 2021-05-06
FL_MA_Split_GN1 ERV Flag | Split_GN1 ERV Flag | No | Yes | No | Yes | [6 empty] | 2021-05-06
FL_MA_Split_GN2 ERV Flag | Split_GN2 ERV Flag | No | Yes | No | Yes | [6 empty] | 2021-05-06
FL_MA_Split_GS1 ERV Flag | Split_GS1 ERV Flag | No | Yes | No | Yes | [6 empty] | 2021-05-06
FL_MA_Split_GS2 ERV Flag | Split_GS2 ERV Flag | No | Yes | No | Yes | [6 empty] | 2021-05-06
FL_MA_Split_MSW ERV Flag | Split_MSW ERV Flag | No | Yes | No | Yes | [6 empty] | 2021-05-06
FL_MA_Split_MNW ERV Flag | Split_MNW ERV Flag | No | Yes | No | Yes | [6 empty] | 2021-05-06
FL_MA_Split_MSE ERV Flag | Split_MSE ERV Flag | No | Yes | No | Yes | [6 empty] | 2021-05-06
FL_MA_Split_MNE ERV Flag | Split_MNE ERV Flag | No | Yes | No | Yes | [6 empty] | 2021-05-06
FL_MA_Split_MN1 ERV Flag | Split_MN1 ERV Flag | No | Yes | No | Yes | [6 empty] | 2021-05-06
FL_MA_Split_MN2 ERV Flag | Split_MN2 ERV Flag | No | Yes | No | Yes | [6 empty] | 2021-05-06
FL_MA_Split_MS1 ERV Flag | Split_MS1 ERV Flag | No | Yes | No | Yes | [6 empty] | 2021-05-06
FL_MA_Split_MS2 ERV Flag | Split_MS2 ERV Flag | No | Yes | No | Yes | [6 empty] | 2021-05-06
FL_MA_Split_TSW ERV Flag | Split_TSW ERV Flag | No | Yes | No | Yes | [6 empty] | 2021-05-06
FL_MA_Split_TNW ERV Flag | Split_TNW ERV Flag | No | Yes | No | Yes | [6 empty] | 2021-05-06
FL_MA_Split_TSE ERV Flag | Split_TSE ERV Flag | No | Yes | No | Yes | [6 empty] | 2021-05-06
FL_MA_Split_TNE ERV Flag | Split_TNE ERV Flag | No | Yes | No | Yes | [6 empty] | 2021-05-06
FL_MA_Split_TN1 ERV Flag | Split_TN1 ERV Flag | No | Yes | No | Yes | [6 empty] | 2021-05-06
FL_MA_Split_TN2 ERV Flag | Split_TN2 ERV Flag | No | Yes | No | Yes | [6 empty] | 2021-05-06
FL_MA_Split_TS1 ERV Flag | Split_TS1 ERV Flag | No | Yes | No | Yes | [6 empty] | 2021-05-06
FL_MA_Split_TS2 ERV Flag | Split_TS2 ERV Flag | No | Yes | No | Yes | [6 empty] | 2021-05-06
id | item | Zone2A(GA-Savannah-GA) ASHRAE901-state_STD2016 | Zone2A(GA-Savannah-GA) ASHRAE901-state_STD2019 | Zone3A(GA-Atlanta-GA) ASHRAE901-state_STD2016 | Zone3A(GA-Atlanta-GA) ASHRAE901-state_STD2019 | [6 empty] | 2021-05-06
GA_SO_PSZ-AC:1 Cooling Capacity [ton] | PSZ-AC:1 Cooling Capacity [ton] | 2.0624 | 1.9692 | 1.9516 | 1.8603 | [6 empty] | 2021-05-06
GA_SO_PSZ-AC:2 Cooling Capacity [ton] | PSZ-AC:2 Cooling Capacity [ton] | 1.8437 | 1.7667 | 1.7053 | 1.6446 | [6 empty] | 2021-05-06
GA_SO_PSZ-AC:3 Cooling Capacity [ton] | PSZ-AC:3 Cooling Capacity [ton] | 1.227 | 1.1796 | 1.1621 | 1.121 | [6 empty] | 2021-05-06
GA_SO_PSZ-AC:4 Cooling Capacity [ton] | PSZ-AC:4 Cooling Capacity [ton] | 1.8435 | 1.7588 | 1.7051 | 1.6295 | [6 empty] | 2021-05-06
GA_SO_PSZ-AC:5 Cooling Capacity [ton] | PSZ-AC:5 Cooling Capacity [ton] | 1.4168 | 1.365 | 1.3217 | 1.2796 | [6 empty] | 2021-05-06
GA_SO_PSZ-AC:1 Supply Flow Rate [cfm] | PSZ-AC:1 Supply Flow Rate [cfm] | 678.0416 | 635.664 | 699.2304 | 656.8528 | [6 empty] | 2021-05-06
GA_SO_PSZ-AC:2 Supply Flow Rate [cfm] | PSZ-AC:2 Supply Flow Rate [cfm] | 635.664 | 593.2864 | 635.664 | 593.2864 | [6 empty] | 2021-05-06
GA_SO_PSZ-AC:3 Supply Flow Rate [cfm] | PSZ-AC:3 Supply Flow Rate [cfm] | 466.1536 | 444.9648 | 466.1536 | 444.9648 | [6 empty] | 2021-05-06
GA_SO_PSZ-AC:4 Supply Flow Rate [cfm] | PSZ-AC:4 Supply Flow Rate [cfm] | 635.664 | 593.2864 | 635.664 | 593.2864 | [6 empty] | 2021-05-06
GA_SO_PSZ-AC:5 Supply Flow Rate [cfm] | PSZ-AC:5 Supply Flow Rate [cfm] | 550.9088 | 508.5312 | 529.72 | 508.5312 | [6 empty] | 2021-05-06
GA_SO_PSZ-AC:1 OA Rate [cfm] | PSZ-AC:1 OA Rate [cfm] | 136.9178 | 136.9178 | 136.9178 | 136.9178 | [6 empty] | 2021-05-06
GA_SO_PSZ-AC:2 OA Rate [cfm] | PSZ-AC:2 OA Rate [cfm] | 103.7925 | 103.7925 | 103.7925 | 103.7925 | [6 empty] | 2021-05-06
GA_SO_PSZ-AC:3 OA Rate [cfm] | PSZ-AC:3 OA Rate [cfm] | 61.5711 | 61.5711 | 61.5711 | 61.5711 | [6 empty] | 2021-05-06
GA_SO_PSZ-AC:4 OA Rate [cfm] | PSZ-AC:4 OA Rate [cfm] | 103.7925 | 103.7925 | 103.7925 | 103.7925 | [6 empty] | 2021-05-06
GA_SO_PSZ-AC:5 OA Rate [cfm] | PSZ-AC:5 OA Rate [cfm] | 61.5711 | 61.5711 | 61.5711 | 61.5711 | [6 empty] | 2021-05-06
GA_SO_PSZ-AC:1 heating Capacity [kBtu/hr] | PSZ-AC:1 heating Capacity [kBtu/hr] | 11.3744 | 11.3744 | 11.9094 | 11.9094 | [6 empty] | 2021-05-06
GA_SO_PSZ-AC:2 heating Capacity [kBtu/hr] | PSZ-AC:2 heating Capacity [kBtu/hr] | 14.6987 | 14.2033 | 17.473 | 17.2426 | [6 empty] | 2021-05-06
GA_SO_PSZ-AC:3 heating Capacity [kBtu/hr] | PSZ-AC:3 heating Capacity [kBtu/hr] | 8.9417 | 8.6676 | 10.7536 | 10.6262 | [6 empty] | 2021-05-06
GA_SO_PSZ-AC:4 heating Capacity [kBtu/hr] | PSZ-AC:4 heating Capacity [kBtu/hr] | 14.4469 | 14.0241 | 17.3126 | 17.1137 | [6 empty] | 2021-05-06
GA_SO_PSZ-AC:5 heating Capacity [kBtu/hr] | PSZ-AC:5 heating Capacity [kBtu/hr] | 8.9824 | 8.6967 | 10.8067 | 10.6723 | [6 empty] | 2021-05-06
id | item | Zone2A(GA-Savannah-GA) ASHRAE901-state_STD2016 | Zone2A(GA-Savannah-GA) ASHRAE901-state_STD2019 | Zone3A(GA-Atlanta-GA) ASHRAE901-state_STD2016 | Zone3A(GA-Atlanta-GA) ASHRAE901-state_STD2019 | [6 empty] | 2021-05-06
GA_LO_CAV_BAS Supply Flow Rate [cfm] | CAV_BAS Supply Flow Rate [cfm] | 11590.2736 | 10742.7216 | 11886.9168 | 10996.9872 | [6 empty] | 2021-05-06
GA_LO_VAV_BOT WITH REHEAT Supply Flow Rate [cfm] | VAV_BOT WITH REHEAT Supply Flow Rate [cfm] | 19006.3536 | 18074.0464 | 19387.752 | 18413.0672 | [6 empty] | 2021-05-06
GA_LO_VAV_MID WITH REHEAT Supply Flow Rate [cfm] | VAV_MID WITH REHEAT Supply Flow Rate [cfm] | 176396.7603 | 167455.0867 | 179638.6467 | 170273.1971 | [6 empty] | 2021-05-06
GA_LO_VAV_TOP WITH REHEAT Supply Flow Rate [cfm] | VAV_TOP WITH REHEAT Supply Flow Rate [cfm] | 18752.088 | 17883.3472 | 18963.976 | 18137.6128 | [6 empty] | 2021-05-06
GA_LO_Supply Air Temp. Reset Flag | Supply Air Temp. Reset Flag | No | No | No | Yes | [6 empty] | 2021-05-06
GA_LO_CAV_BAS OA Rate [cfm] | CAV_BAS OA Rate [cfm] | 2542.8255 | 2542.8255 | 2542.8255 | 2542.8255 | [6 empty] | 2021-05-06
GA_LO_VAV_BOT WITH REHEAT OA Rate [cfm] | VAV_BOT WITH REHEAT OA Rate [cfm] | 5377.8022 | 4302.174 | 5377.8022 | 4302.174 | [6 empty] | 2021-05-06
GA_LO_VAV_MID WITH REHEAT OA Rate [cfm] | VAV_MID WITH REHEAT OA Rate [cfm] | 53777.9373 | 43021.7396 | 53777.9373 | 43021.7396 | [6 empty] | 2021-05-06
GA_LO_VAV_TOP WITH REHEAT OA Rate [cfm] | VAV_TOP WITH REHEAT OA Rate [cfm] | 5377.8022 | 4302.174 | 5377.8022 | 4302.174 | [6 empty] | 2021-05-06
GA_LO_AIRLOOP DATACENTER BASEMENT OA Rate [cfm] | AIRLOOP DATACENTER BASEMENT OA Rate [cfm] | 716.9654 | 716.9654 | 716.9654 | 716.9654 | [6 empty] | 2021-05-06
GA_LO_VAV_bot_WITH_REHEAT ERV Flag | VAV_bot_WITH_REHEAT ERV Flag | Yes | Yes | Yes | Yes | [6 empty] | 2021-05-06
GA_LO_VAV_mid_WITH_REHEAT ERV Flag | VAV_mid_WITH_REHEAT ERV Flag | Yes | Yes | Yes | Yes | [6 empty] | 2021-05-06
GA_LO_VAV_top_WITH_REHEAT ERV Flag | VAV_top_WITH_REHEAT ERV Flag | Yes | Yes | Yes | Yes | [6 empty] | 2021-05-06
GA_LO_COOLSYS1 CHILLER1 Capacity [ton] | COOLSYS1 CHILLER1 Capacity [ton] | 441.7981 | 395.9067 | 405.9587 | 365.7786 | [6 empty] | 2021-05-06
GA_LO_COOLSYS1 CHILLER2 Capacity [ton] | COOLSYS1 CHILLER2 Capacity [ton] | 441.7981 | 395.9067 | 405.9587 | 365.7786 | [6 empty] | 2021-05-06
GA_LO_TOWERWATERSYS COOLTOWER 1 Capacity [ton] | TOWERWATERSYS COOLTOWER 1 Capacity [ton] | 419.3425 | 375.787 | 385.3304 | 347.1964 | [6 empty] | 2021-05-06
GA_LO_TOWERWATERSYS COOLTOWER 2 Capacity [ton] | TOWERWATERSYS COOLTOWER 2 Capacity [ton] | 419.3425 | 375.787 | 385.3304 | 347.1964 | [6 empty] | 2021-05-06
GA_LO_HEATSYS1 BOILER Capacity [MMBTU/h] | HEATSYS1 BOILER Capacity [MMBTU/h] | 3441.8231 | 3058.0303 | 3754.3171 | 3351.1624 | [6 empty] | 2021-05-06
GA_LO_COOLSYS1 PUMP Flow Rate [gal/min] | COOLSYS1 PUMP Flow Rate [gal/min] | 0 | 0 | 0 | 0 | [6 empty] | 2021-05-06
GA_LO_COOLSYS1 CHILLER1 PUMP Flow Rate [gal/min] | COOLSYS1 CHILLER1 PUMP Flow Rate [gal/min] | 693.6609 | 621.3247 | 639.6889 | 573.5424 | [6 empty] | 2021-05-06
GA_LO_COOLSYS1 CHILLER2 PUMP Flow Rate [gal/min] | COOLSYS1 CHILLER2 PUMP Flow Rate [gal/min] | 693.6609 | 621.3247 | 639.6889 | 573.5424 | [6 empty] | 2021-05-06
GA_LO_COOLSYS1 PUMP SECONDARY Flow Rate [gal/min] | COOLSYS1 PUMP SECONDARY Flow Rate [gal/min] | 1387.3217 | 1242.6495 | 1279.3794 | 1147.0847 | [6 empty] | 2021-05-06
GA_LO_HEATSYS1 PUMP Flow Rate [gal/min] | HEATSYS1 PUMP Flow Rate [gal/min] | 706.479 | 627.7013 | 770.6237 | 687.8707 | [6 empty] | 2021-05-06
GA_LO_TOWERWATERSYS PUMP Flow Rate [gal/min] | TOWERWATERSYS PUMP Flow Rate [gal/min] | 2437.4627 | 2184.1745 | 2239.6507 | 2018.0631 | [6 empty] | 2021-05-06
GA_LO_PLANT CIRC PUMP Flow Rate [gal/min] | PLANT CIRC PUMP Flow Rate [gal/min] | 208.1496 | 207.2668 | 209.3099 | 208.4444 | [6 empty] | 2021-05-06
GA_LO_COOLSYS1 PUMP SECONDARY Pressure setpoint reset [yes,no] | COOLSYS1 PUMP SECONDARY Pressure setpoint reset [yes,no] | pump_ride_on_curve | pump_ride_on_curve | pump_ride_on_curve | pump_ride_on_curve | [6 empty] | 2021-05-06
GA_LO_COOLSYS1 CHILLER1 PUMP Pump Power [hp] | COOLSYS1 CHILLER1 PUMP Pump Power [hp] | 3.7421 | 3.3186 | 3.4509 | 3.0634 | [6 empty] | 2021-05-06
GA_LO_COOLSYS1 CHILLER2 PUMP Pump Power [hp] | COOLSYS1 CHILLER2 PUMP Pump Power [hp] | 3.7421 | 3.3186 | 3.4509 | 3.0634 | [6 empty] | 2021-05-06
GA_LO_COOLSYS1 PUMP SECONDARY Pump Power [hp] | COOLSYS1 PUMP SECONDARY Pump Power [hp] | 22.4523 | 19.9119 | 20.7054 | 18.3806 | [6 empty] | 2021-05-06
GA_LO_HEATSYS1 PUMP Pump Power [hp] | HEATSYS1 PUMP Pump Power [hp] | 15.271 | 13.4338 | 16.6575 | 14.7215 | [6 empty] | 2021-05-06
GA_LO_TOWERWATERSYS PUMP Pump Power [hp] | TOWERWATERSYS PUMP Pump Power [hp] | 43.6399 | 38.7197 | 40.0998 | 35.7731 | [6 empty] | 2021-05-06
GA_LO_PLANT CIRC PUMP Pump Power [hp] | PLANT CIRC PUMP Pump Power [hp] | 4.4916 | 4.4282 | 4.5166 | 4.4534 | [6 empty] | 2021-05-06
GA_LO_Datacenter PLANT CIRC PUMP Pump Power [hp] | Datacenter PLANT CIRC PUMP Pump Power [hp] | 4.4916 | 4.4282 | 4.5166 | 4.4534 | [6 empty] | 2021-05-06
GA_LO_ZN_VAV_BOXes_Max_Reheat_Water_Flow_GPM | ZN_VAV_BOXes_Max_Reheat_Water_Flow_GPM | 415.515 | 390.3976 | 438.5444 | 420.634 | [6 empty] | 2021-05-06
GA_LO_COOLSYS1 PUMP SECONDARY VSD | COOLSYS1 PUMP SECONDARY VSD | No | No | No | No | [6 empty] | 2021-05-06
GA_LO_HEATSYS1 PUMP VSD | HEATSYS1 PUMP VSD | No | No | No | No | [6 empty] | 2021-05-06
GA_LO_DATACENTER BASEMENT Cooling Capacity [ton] | DATACENTER BASEMENT Cooling Capacity [ton] | 122.132 | 121.776 | 123.0041 | 122.6436 | [6 empty] | 2021-05-06
GA_LO_DATACENTER BOT Cooling Capacity [ton] | DATACENTER BOT Cooling Capacity [ton] | 2.643 | 2.6165 | 2.6192 | 2.6184 | [6 empty] | 2021-05-06
GA_LO_DATACENTER MID Cooling Capacity [ton] | DATACENTER MID Cooling Capacity [ton] | 25.1618 | 24.9182 | 25.1687 | 24.9154 | [6 empty] | 2021-05-06
GA_LO_DATACENTER TOP Cooling Capacity [ton] | DATACENTER TOP Cooling Capacity [ton] | 2.5369 | 2.5161 | 2.5324 | 2.5127 | [6 empty] | 2021-05-06
id | item | Zone2A(GA-Savannah-GA) ASHRAE901-state_STD2016 | Zone2A(GA-Savannah-GA) ASHRAE901-state_STD2019 | Zone3A(GA-Atlanta-GA) ASHRAE901-state_STD2016 | Zone3A(GA-Atlanta-GA) ASHRAE901-state_STD2019 | [6 empty] | 2021-05-06
GA_RS_PSZ-AC:1 Cooling Capacity [ton] | PSZ-AC:1 Cooling Capacity [ton] | 11.1428 | 10.7827 | 10.5775 | 10.2395 | [6 empty] | 2021-05-06
GA_RS_PSZ-AC:2 Cooling Capacity [ton] | PSZ-AC:2 Cooling Capacity [ton] | 50.7624 | 47.8238 | 49.7817 | 47.699 | [6 empty] | 2021-05-06
GA_RS_PSZ-AC:3 Cooling Capacity [ton] | PSZ-AC:3 Cooling Capacity [ton] | 6.8862 | 6.7456 | 6.4918 | 6.3323 | [6 empty] | 2021-05-06
GA_RS_PSZ-AC:4 Cooling Capacity [ton] | PSZ-AC:4 Cooling Capacity [ton] | 5.6612 | 5.5205 | 5.2649 | 5.11 | [6 empty] | 2021-05-06
GA_RS_PSZ-AC:1 Supply Flow Rate [cfm] | PSZ-AC:1 Supply Flow Rate [cfm] | 4131.816 | 3877.5504 | 4110.6272 | 3856.3616 | [6 empty] | 2021-05-06
GA_RS_PSZ-AC:2 Supply Flow Rate [cfm] | PSZ-AC:2 Supply Flow Rate [cfm] | 15234.7472 | 14344.8176 | 15446.6352 | 14535.5168 | [6 empty] | 2021-05-06
GA_RS_PSZ-AC:3 Supply Flow Rate [cfm] | PSZ-AC:3 Supply Flow Rate [cfm] | 2288.3904 | 2224.824 | 2309.5792 | 2246.0128 | [6 empty] | 2021-05-06
GA_RS_PSZ-AC:4 Supply Flow Rate [cfm] | PSZ-AC:4 Supply Flow Rate [cfm] | 1758.6704 | 1695.104 | 1758.6704 | 1695.104 | [6 empty] | 2021-05-06
GA_RS_PSZ-AC:1 OA Rate [cfm] | PSZ-AC:1 OA Rate [cfm] | 490.669 | 490.669 | 490.669 | 490.669 | [6 empty] | 2021-05-06
GA_RS_PSZ-AC:2 OA Rate [cfm] | PSZ-AC:2 OA Rate [cfm] | 4005.1282 | 4005.1282 | 4005.1282 | 4005.1282 | [6 empty] | 2021-05-06
GA_RS_PSZ-AC:3 OA Rate [cfm] | PSZ-AC:3 OA Rate [cfm] | 377.3937 | 377.3937 | 377.3937 | 377.3937 | [6 empty] | 2021-05-06
GA_RS_PSZ-AC:4 OA Rate [cfm] | PSZ-AC:4 OA Rate [cfm] | 377.3937 | 377.3937 | 377.3937 | 377.3937 | [6 empty] | 2021-05-06
GA_RS_PSZ-AC:1 OA Damper [gravity, motorized] | PSZ-AC:1 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2021-05-06
GA_RS_PSZ-AC:2 OA Damper [gravity, motorized] | PSZ-AC:2 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2021-05-06
GA_RS_PSZ-AC:3 OA Damper [gravity, motorized] | PSZ-AC:3 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2021-05-06
GA_RS_PSZ-AC:4 OA Damper [gravity, motorized] | PSZ-AC:4 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2021-05-06
GA_RS_PSZ-AC:1 Heating Capacity [kBtu/hr] | PSZ-AC:1 Heating Capacity [kBtu/hr] | 174.9608 | 165.0239 | 171.6757 | 161.6632 | [6 empty] | 2021-05-06
GA_RS_PSZ-AC:2 Heating Capacity [kBtu/hr] | PSZ-AC:2 Heating Capacity [kBtu/hr] | 736.3578 | 699.0764 | 745.4557 | 708.3515 | [6 empty] | 2021-05-06
GA_RS_PSZ-AC:3 Heating Capacity [kBtu/hr] | PSZ-AC:3 Heating Capacity [kBtu/hr] | 102.4596 | 99.9652 | 102.2749 | 99.6129 | [6 empty] | 2021-05-06
GA_RS_PSZ-AC:4 Heating Capacity [kBtu/hr] | PSZ-AC:4 Heating Capacity [kBtu/hr] | 82.8391 | 80.1945 | 82.4512 | 79.6716 | [6 empty] | 2021-05-06
id | item | Zone2A(GA-Savannah-GA) ASHRAE901-state_STD2016 | Zone2A(GA-Savannah-GA) ASHRAE901-state_STD2019 | Zone3A(GA-Atlanta-GA) ASHRAE901-state_STD2016 | Zone3A(GA-Atlanta-GA) ASHRAE901-state_STD2019 | [6 empty] | 2021-05-06
GA_PS_VAV_POD_1 Cooling Capacity [ton] | VAV_POD_1 Cooling Capacity [ton] | 18.795 | 18.2241 | 18.7169 | 18.1742 | [6 empty] | 2021-05-06
GA_PS_VAV_POD_2 Cooling Capacity [ton] | VAV_POD_2 Cooling Capacity [ton] | 18.7825 | 18.192 | 18.668 | 18.1388 | [6 empty] | 2021-05-06
GA_PS_VAV_POD_3 Cooling Capacity [ton] | VAV_POD_3 Cooling Capacity [ton] | 17.1906 | 16.2435 | 17.0885 | 16.2056 | [6 empty] | 2021-05-06
GA_PS_VAV_OTHER Cooling Capacity [ton] | VAV_OTHER Cooling Capacity [ton] | 26.2489 | 24.5812 | 26.31 | 24.7006 | [6 empty] | 2021-05-06
GA_PS_PSZ-AC_1:6 Cooling Capacity [ton] | PSZ-AC_1:6 Cooling Capacity [ton] | 8.3664 | 7.9879 | 8.4227 | 8.1482 | [6 empty] | 2021-05-06
GA_PS_PSZ-AC_2:5 Cooling Capacity [ton] | PSZ-AC_2:5 Cooling Capacity [ton] | 5.2639 | 5.087 | 5.259 | 5.0918 | [6 empty] | 2021-05-06
GA_PS_PSZ-AC_2:7 Cooling Capacity [ton] | PSZ-AC_2:7 Cooling Capacity [ton] | 10.5074 | 10.5074 | 10.5074 | 10.5074 | [6 empty] | 2021-05-06
GA_PS_VAV_POD_1 Supply Flow Rate [cfm] | VAV_POD_1 Supply Flow Rate [cfm] | 5636.2208 | 5466.7104 | 5615.032 | 5445.5216 | [6 empty] | 2021-05-06
GA_PS_VAV_POD_2 Supply Flow Rate [cfm] | VAV_POD_2 Supply Flow Rate [cfm] | 5636.2208 | 5466.7104 | 5593.8432 | 5445.5216 | [6 empty] | 2021-05-06
GA_PS_VAV_POD_3 Supply Flow Rate [cfm] | VAV_POD_3 Supply Flow Rate [cfm] | 5148.8784 | 4873.424 | 5127.6896 | 4873.424 | [6 empty] | 2021-05-06
GA_PS_VAV_OTHER Supply Flow Rate [cfm] | VAV_OTHER Supply Flow Rate [cfm] | 7882.2336 | 7373.7024 | 7903.4224 | 7416.08 | [6 empty] | 2021-05-06
GA_PS_PSZ-AC_2:5 Supply Flow Rate [cfm] | PSZ-AC_2:5 Supply Flow Rate [cfm] | 1589.16 | 1525.5936 | 1567.9712 | 1525.5936 | [6 empty] | 2021-05-06
GA_PS_PSZ-AC_1:6 Supply Flow Rate [cfm] | PSZ-AC_1:6 Supply Flow Rate [cfm] | 2500.2784 | 2394.3344 | 2585.0336 | 2457.9008 | [6 empty] | 2021-05-06
GA_PS_PSZ-AC_2:7 Supply Flow Rate [cfm] | PSZ-AC_2:7 Supply Flow Rate [cfm] | 3157.1312 | 3157.1312 | 3157.1312 | 3157.1312 | [6 empty] | 2021-05-06
GA_PS_Supply Air Temp. Reset Flag | Supply Air Temp. Reset Flag | No | No | No | No | [6 empty] | 2021-05-06
GA_PS_VAV_POD_1 OA Rate [cfm] | VAV_POD_1 OA Rate [cfm] | 5639.6534 | 5468.7445 | 5614.4599 | 5453.7641 | [6 empty] | 2021-05-06
GA_PS_VAV_POD_2 OA Rate [cfm] | VAV_POD_2 OA Rate [cfm] | 5635.7123 | 5459.1248 | 5600.2422 | 5443.1485 | [6 empty] | 2021-05-06
GA_PS_VAV_POD_3 OA Rate [cfm] | VAV_POD_3 OA Rate [cfm] | 5157.3751 | 4874.4199 | 5127.9651 | 4863.0203 | [6 empty] | 2021-05-06
GA_PS_VAV_OTHER OA Rate [cfm] | VAV_OTHER OA Rate [cfm] | 3736.1787 | 2988.8921 | 3736.1787 | 2988.8921 | [6 empty] | 2021-05-06
GA_PS_PSZ-AC_2:5 OA Rate [cfm] | PSZ-AC_2:5 OA Rate [cfm] | 1152.7343 | 1152.7343 | 1152.7343 | 1152.7343 | [6 empty] | 2021-05-06
GA_PS_PSZ-AC_1:6 OA Rate [cfm] | PSZ-AC_1:6 OA Rate [cfm] | 539.9118 | 539.9118 | 539.9118 | 539.9118 | [6 empty] | 2021-05-06
GA_PS_PSZ-AC_2:7 OA Rate [cfm] | PSZ-AC_2:7 OA Rate [cfm] | 3153.0841 | 3153.0841 | 3153.0841 | 3153.0841 | [6 empty] | 2021-05-06
GA_PS_VAV_POD_1 OA Damper [gravity, motorized] | VAV_POD_1 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2021-05-06
GA_PS_VAV_POD_2 OA Damper [gravity, motorized] | VAV_POD_2 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2021-05-06
GA_PS_VAV_POD_3 OA Damper [gravity, motorized] | VAV_POD_3 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2021-05-06
GA_PS_VAV_OTHER OA Damper [gravity, motorized] | VAV_OTHER OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2021-05-06
GA_PS_PSZ-AC_2:5 OA Damper [gravity, motorized] | PSZ-AC_2:5 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2021-05-06
GA_PS_PSZ-AC_1:6 OA Damper [gravity, motorized] | PSZ-AC_1:6 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2021-05-06
GA_PS_PSZ-AC_2:7 OA Damper [gravity, motorized] | PSZ-AC_2:7 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2021-05-06
GA_PS_VAV_POD_1 (economizer) | VAV_POD_1 (economizer) | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialEnthalpy | [6 empty] | 2021-05-06
GA_PS_VAV_POD_2 (economizer) | VAV_POD_2 (economizer) | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialEnthalpy | [6 empty] | 2021-05-06
GA_PS_VAV_POD_3 (economizer) | VAV_POD_3 (economizer) | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialEnthalpy | [6 empty] | 2021-05-06
GA_PS_VAV_OTHER (economizer) | VAV_OTHER (economizer) | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialEnthalpy | [6 empty] | 2021-05-06
GA_PS_PSZ-AC_2:5 (economizer) | PSZ-AC_2:5 (economizer) | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialEnthalpy | [6 empty] | 2021-05-06
GA_PS_PSZ-AC_1:6 (economizer) | PSZ-AC_1:6 (economizer) | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialEnthalpy | [6 empty] | 2021-05-06
GA_PS_PSZ-AC_2:7 (economizer) | PSZ-AC_2:7 (economizer) | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialEnthalpy | [6 empty] | 2021-05-06
GA_PS_VAV_Pod_1_ERV Flag | VAV_Pod_1_ERV Flag | Yes | Yes | Yes | Yes | [6 empty] | 2021-05-06
GA_PS_VAV_Pod_2_ERV Flag | VAV_Pod_2_ERV Flag | Yes | Yes | Yes | Yes | [6 empty] | 2021-05-06
GA_PS_VAV_Pod_3_ERV Flag | VAV_Pod_3_ERV Flag | Yes | Yes | Yes | Yes | [6 empty] | 2021-05-06
GA_PS_VAV_OTHER_ERV Flag | VAV_OTHER_ERV Flag | Yes | Yes | Yes | Yes | [6 empty] | 2021-05-06
GA_PS_PSZ_AC_2_5_ERV Flag | PSZ_AC_2_5_ERV Flag | Yes | Yes | Yes | Yes | [6 empty] | 2021-05-06
GA_PS_PSZ_AC_2_7_ERV Flag | PSZ_AC_2_7_ERV Flag | Yes | Yes | Yes | Yes | [6 empty] | 2021-05-06
GA_PS_HEATSYS1 Capacity [MMBTU/h] | HEATSYS1 Capacity [MMBTU/h] | 0.82194 | 0.76723 | 0.90796 | 0.8659 | [6 empty] | 2021-05-06
GA_PS_HEATSYS1 Flow Rate [gal/min] | HEATSYS1 Flow Rate [gal/min] | 84.3573 | 78.7416 | 93.1858 | 88.869 | [6 empty] | 2021-05-06
GA_PS_VAV_POD_1 Fan Power [hp] | VAV_POD_1 Fan Power [hp] | 8.3208 | 8.068 | 8.2862 | 8.0459 | [6 empty] | 2021-05-06
GA_PS_VAV_POD_2 Fan Power [hp] | VAV_POD_2 Fan Power [hp] | 8.3153 | 8.0538 | 8.2646 | 8.0303 | [6 empty] | 2021-05-06
GA_PS_VAV_POD_3 Fan Power [hp] | VAV_POD_3 Fan Power [hp] | 7.6105 | 7.1912 | 7.5653 | 7.1744 | [6 empty] | 2021-05-06
GA_PS_VAV_OTHER Fan Power [hp] | VAV_OTHER Fan Power [hp] | 11.5327 | 10.8 | 11.5596 | 10.8524 | [6 empty] | 2021-05-06
GA_PS_HEATSYS1 Pump Power [hp] | HEATSYS1 Pump Power [hp] | 1.8234 | 1.6852 | 2.0143 | 1.9019 | [6 empty] | 2021-05-06
GA_PS_PSZ-AC_1:6 Heating Capacity [kBtu/hr] | PSZ-AC_1:6 Heating Capacity [kBtu/hr] | 198.2171 | 189.3793 | 200.3902 | 191.6892 | [6 empty] | 2021-05-06
GA_PS_PSZ-AC_2:5 Heating Capacity [kBtu/hr] | PSZ-AC_2:5 Heating Capacity [kBtu/hr] | 111.5436 | 109.5809 | 115.4529 | 113.6622 | [6 empty] | 2021-05-06
GA_PS_PSZ-AC_2:7 Heating Capacity [kBtu/hr] | PSZ-AC_2:7 Heating Capacity [kBtu/hr] | 261.9429 | 261.9429 | 274.2625 | 274.2625 | [6 empty] | 2021-05-06
GA_PS_ZN_VAV_BOXes_Max_Reheat_Water_Flow_GPM | ZN_VAV_BOXes_Max_Reheat_Water_Flow_GPM | 61.784 | 57.2205 | 66.4034 | 63.2682 | [6 empty] | 2021-05-06
id | item | Zone2A(GA-Savannah-GA) ASHRAE901-state_STD2016 | Zone2A(GA-Savannah-GA) ASHRAE901-state_STD2019 | Zone3A(GA-Atlanta-GA) ASHRAE901-state_STD2016 | Zone3A(GA-Atlanta-GA) ASHRAE901-state_STD2019 | [6 empty] | 2021-05-06
GA_SH_SAC_FRONTOFFICE Cooling Capacity [ton] | SAC_FRONTOFFICE Cooling Capacity [ton] | 2.5631 | 2.4298 | 2.4403 | 2.2997 | [6 empty] | 2021-05-06
GA_SH_SAC_FRONTLOUNGE Cooling Capacity [ton] | SAC_FRONTLOUNGE Cooling Capacity [ton] | 6.2036 | 5.8868 | 6.3227 | 6.0012 | [6 empty] | 2021-05-06
GA_SH_SAC_MEETINGROOM Cooling Capacity [ton] | SAC_MEETINGROOM Cooling Capacity [ton] | 2.9345 | 2.8451 | 2.9998 | 2.9106 | [6 empty] | 2021-05-06
GA_SH_SAC_EXC_EMPLGE_RESTRM Cooling Capacity [ton] | SAC_EXC_EMPLGE_RESTRM Cooling Capacity [ton] | 6.2232 | 6.1891 | 6.0747 | 6.0324 | [6 empty] | 2021-05-06
GA_SH_SAC_FO_ADDAQ SUPPLY FAN Supply Flow Rate [cfm] | SAC_FO_ADDAQ SUPPLY FAN Supply Flow Rate [cfm] | 805.1744 | 762.7968 | 826.3632 | 762.7968 | [6 empty] | 2021-05-06
GA_SH_SAC_FL_ADDAQ SUPPLY FAN Supply Flow Rate [cfm] | SAC_FL_ADDAQ SUPPLY FAN Supply Flow Rate [cfm] | 1864.6144 | 1758.6704 | 1906.992 | 1801.048 | [6 empty] | 2021-05-06
GA_SH_SAC_MR_ADDAQ SUPPLY FAN Supply Flow Rate [cfm] | SAC_MR_ADDAQ SUPPLY FAN Supply Flow Rate [cfm] | 889.9296 | 847.552 | 889.9296 | 868.7408 | [6 empty] | 2021-05-06
GA_SH_SAC_EXC_ADDAQ SUPPLY FAN Supply Flow Rate [cfm] | SAC_EXC_ADDAQ SUPPLY FAN Supply Flow Rate [cfm] | 2161.2576 | 2140.0688 | 2224.824 | 2224.824 | [6 empty] | 2021-05-06
GA_SH_SAC_Exc_EmpLge_RestRm OA Rate [cfm] | SAC_Exc_EmpLge_RestRm OA Rate [cfm] | 199.9928 | 199.9928 | 199.9928 | 199.9928 | [6 empty] | 2021-05-06
GA_SH_SAC_FrontLounge OA Rate [cfm] | SAC_FrontLounge OA Rate [cfm] | 500.0133 | 500.0133 | 500.0133 | 500.0133 | [6 empty] | 2021-05-06
GA_SH_SAC_FrontOffice OA Rate [cfm] | SAC_FrontOffice OA Rate [cfm] | 119.2938 | 119.2938 | 119.2938 | 119.2938 | [6 empty] | 2021-05-06
GA_SH_SAC_MeetingRoom OA Rate [cfm] | SAC_MeetingRoom OA Rate [cfm] | 267.7629 | 267.7629 | 267.7629 | 267.7629 | [6 empty] | 2021-05-06
GA_SH_SAC_FrontLounge OA Damper [gravity, motorized] | SAC_FrontLounge OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2021-05-06
GA_SH_SAC_FrontOffice (economizer) | SAC_FrontOffice (economizer) | No | No | No | No | [6 empty] | 2021-05-06
GA_SH_SAC_FrontLounge (economizer) | SAC_FrontLounge (economizer) | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialEnthalpy | [6 empty] | 2021-05-06
GA_SH_SAC_MeetingRoom (economizer) | SAC_MeetingRoom (economizer) | No | No | No | No | [6 empty] | 2021-05-06
GA_SH_SAC_Exc_EmpLge_RestRm (economizer) | SAC_Exc_EmpLge_RestRm (economizer) | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialEnthalpy | [6 empty] | 2021-05-06
GA_SH_SAC_FRONTOFFICE Heating Capacity [kBtu/hr] | SAC_FRONTOFFICE Heating Capacity [kBtu/hr] | 35.3049 | 33.2614 | 35.3169 | 33.1555 | [6 empty] | 2021-05-06
GA_SH_SAC_FRONTLOUNGE Heating Capacity [kBtu/hr] | SAC_FRONTLOUNGE Heating Capacity [kBtu/hr] | 91.5759 | 88.0823 | 93.0777 | 89.6547 | [6 empty] | 2021-05-06
GA_SH_SAC_MEETINGROOM Heating Capacity [kBtu/hr] | SAC_MEETINGROOM Heating Capacity [kBtu/hr] | 44.7655 | 43.7798 | 45.7321 | 44.7827 | [6 empty] | 2021-05-06
GA_SH_SAC_EXC_EMPLGE_RESTRM Heating Capacity [kBtu/hr] | SAC_EXC_EMPLGE_RESTRM Heating Capacity [kBtu/hr] | 88.7217 | 88.1874 | 89.5719 | 88.9199 | [6 empty] | 2021-05-06
id | item | Zone2A(GA-Savannah-GA) ASHRAE901-state_STD2016 | Zone2A(GA-Savannah-GA) ASHRAE901-state_STD2019 | Zone3A(GA-Atlanta-GA) ASHRAE901-state_STD2016 | Zone3A(GA-Atlanta-GA) ASHRAE901-state_STD2019 | [6 empty] | 2021-05-06
GA_MA_SPLIT GSW COOLING COIL Cooling Capacity [ton] | SPLIT GSW COOLING COIL Cooling Capacity [ton] | 0.93105 | 0.91976 | 0.8744 | 0.86427 | [6 empty] | 2021-05-06
GA_MA_SPLIT GNW COOLING COIL Cooling Capacity [ton] | SPLIT GNW COOLING COIL Cooling Capacity [ton] | 0.91533 | 0.90371 | 0.84979 | 0.83958 | [6 empty] | 2021-05-06
GA_MA_SPLIT OFFICE COOLING COIL Cooling Capacity [ton] | SPLIT OFFICE COOLING COIL Cooling Capacity [ton] | 1.7356 | 1.6597 | 1.7048 | 1.5847 | [6 empty] | 2021-05-06
GA_MA_SPLIT GNE COOLING COIL Cooling Capacity [ton] | SPLIT GNE COOLING COIL Cooling Capacity [ton] | 0.81985 | 0.80734 | 0.75831 | 0.74707 | [6 empty] | 2021-05-06
GA_MA_SPLIT GN1 COOLING COIL Cooling Capacity [ton] | SPLIT GN1 COOLING COIL Cooling Capacity [ton] | 0.71302 | 0.70381 | 0.65566 | 0.64691 | [6 empty] | 2021-05-06
GA_MA_SPLIT GN2 COOLING COIL Cooling Capacity [ton] | SPLIT GN2 COOLING COIL Cooling Capacity [ton] | 0.71144 | 0.70224 | 0.65408 | 0.64535 | [6 empty] | 2021-05-06
GA_MA_SPLIT GS1 COOLING COIL Cooling Capacity [ton] | SPLIT GS1 COOLING COIL Cooling Capacity [ton] | 0.72327 | 0.71472 | 0.67657 | 0.66621 | [6 empty] | 2021-05-06
GA_MA_SPLIT GS2 COOLING COIL Cooling Capacity [ton] | SPLIT GS2 COOLING COIL Cooling Capacity [ton] | 0.75861 | 0.74585 | 0.71039 | 0.6978 | [6 empty] | 2021-05-06
GA_MA_SPLIT MSW COOLING COIL Cooling Capacity [ton] | SPLIT MSW COOLING COIL Cooling Capacity [ton] | 2.0635 | 2.0397 | 1.9603 | 1.9399 | [6 empty] | 2021-05-06
GA_MA_SPLIT MNW COOLING COIL Cooling Capacity [ton] | SPLIT MNW COOLING COIL Cooling Capacity [ton] | 2.0467 | 2.0225 | 1.9249 | 1.9044 | [6 empty] | 2021-05-06
GA_MA_SPLIT MSE COOLING COIL Cooling Capacity [ton] | SPLIT MSE COOLING COIL Cooling Capacity [ton] | 1.8038 | 1.7824 | 1.7029 | 1.6843 | [6 empty] | 2021-05-06
GA_MA_SPLIT MNE COOLING COIL Cooling Capacity [ton] | SPLIT MNE COOLING COIL Cooling Capacity [ton] | 1.7867 | 1.7649 | 1.6676 | 1.6488 | [6 empty] | 2021-05-06
GA_MA_SPLIT MN1 COOLING COIL Cooling Capacity [ton] | SPLIT MN1 COOLING COIL Cooling Capacity [ton] | 1.4896 | 1.4708 | 1.3869 | 1.3699 | [6 empty] | 2021-05-06
GA_MA_SPLIT MN2 COOLING COIL Cooling Capacity [ton] | SPLIT MN2 COOLING COIL Cooling Capacity [ton] | 1.4855 | 1.4668 | 1.3828 | 1.3659 | [6 empty] | 2021-05-06
GA_MA_SPLIT MS1 COOLING COIL Cooling Capacity [ton] | SPLIT MS1 COOLING COIL Cooling Capacity [ton] | 1.5178 | 1.4994 | 1.4307 | 1.414 | [6 empty] | 2021-05-06
GA_MA_SPLIT MS2 COOLING COIL Cooling Capacity [ton] | SPLIT MS2 COOLING COIL Cooling Capacity [ton] | 1.5141 | 1.4957 | 1.4272 | 1.4105 | [6 empty] | 2021-05-06
GA_MA_SPLIT TSW COOLING COIL Cooling Capacity [ton] | SPLIT TSW COOLING COIL Cooling Capacity [ton] | 1.2666 | 1.2545 | 1.2023 | 1.1919 | [6 empty] | 2021-05-06
GA_MA_SPLIT TNW COOLING COIL Cooling Capacity [ton] | SPLIT TNW COOLING COIL Cooling Capacity [ton] | 1.2445 | 1.2324 | 1.1753 | 1.1651 | [6 empty] | 2021-05-06
GA_MA_SPLIT TSE COOLING COIL Cooling Capacity [ton] | SPLIT TSE COOLING COIL Cooling Capacity [ton] | 1.1642 | 1.1526 | 1.1007 | 1.0906 | [6 empty] | 2021-05-06
GA_MA_SPLIT TNE COOLING COIL Cooling Capacity [ton] | SPLIT TNE COOLING COIL Cooling Capacity [ton] | 1.1274 | 1.1156 | 1.0526 | 1.0426 | [6 empty] | 2021-05-06
GA_MA_SPLIT TN1 COOLING COIL Cooling Capacity [ton] | SPLIT TN1 COOLING COIL Cooling Capacity [ton] | 0.92177 | 0.91234 | 0.86542 | 0.85706 | [6 empty] | 2021-05-06
GA_MA_SPLIT TN2 COOLING COIL Cooling Capacity [ton] | SPLIT TN2 COOLING COIL Cooling Capacity [ton] | 0.91726 | 0.90786 | 0.86114 | 0.85279 | [6 empty] | 2021-05-06
GA_MA_SPLIT TS1 COOLING COIL Cooling Capacity [ton] | SPLIT TS1 COOLING COIL Cooling Capacity [ton] | 0.96814 | 0.9568 | 0.91201 | 0.90333 | [6 empty] | 2021-05-06
GA_MA_SPLIT TS2 COOLING COIL Cooling Capacity [ton] | SPLIT TS2 COOLING COIL Cooling Capacity [ton] | 0.96843 | 0.95873 | 0.91426 | 0.90555 | [6 empty] | 2021-05-06
GA_MA_Split GN1 Furnace with DX Cooling OA Rate [cfm] | Split GN1 Furnace with DX Cooling OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | [6 empty] | 2021-05-06
GA_MA_Split GN2 Furnace with DX Cooling OA Rate [cfm] | Split GN2 Furnace with DX Cooling OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | [6 empty] | 2021-05-06
GA_MA_Split GNE Furnace with DX Cooling OA Rate [cfm] | Split GNE Furnace with DX Cooling OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | [6 empty] | 2021-05-06
GA_MA_Split GNW Furnace with DX Cooling OA Rate [cfm] | Split GNW Furnace with DX Cooling OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | [6 empty] | 2021-05-06
GA_MA_Split GS1 Furnace with DX Cooling OA Rate [cfm] | Split GS1 Furnace with DX Cooling OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | [6 empty] | 2021-05-06
GA_MA_Split GS2 Furnace with DX Cooling OA Rate [cfm] | Split GS2 Furnace with DX Cooling OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | [6 empty] | 2021-05-06
GA_MA_Split GSW Furnace with DX Cooling OA Rate [cfm] | Split GSW Furnace with DX Cooling OA Rate [cfm] | 56.9945 | 56.9945 | 56.9945 | 56.9945 | [6 empty] | 2021-05-06
GA_MA_Split MN1 Furnace with DX Cooling OA Rate [cfm] | Split MN1 Furnace with DX Cooling OA Rate [cfm] | 109.9824 | 109.9824 | 109.9824 | 109.9824 | [6 empty] | 2021-05-06
GA_MA_Split MN2 Furnace with DX Cooling OA Rate [cfm] | Split MN2 Furnace with DX Cooling OA Rate [cfm] | 109.9824 | 109.9824 | 109.9824 | 109.9824 | [6 empty] | 2021-05-06
GA_MA_Split MNE Furnace with DX Cooling OA Rate [cfm] | Split MNE Furnace with DX Cooling OA Rate [cfm] | 109.9824 | 109.9824 | 109.9824 | 109.9824 | [6 empty] | 2021-05-06
GA_MA_Split MNW Furnace with DX Cooling OA Rate [cfm] | Split MNW Furnace with DX Cooling OA Rate [cfm] | 109.9824 | 109.9824 | 109.9824 | 109.9824 | [6 empty] | 2021-05-06
GA_MA_Split MS1 Furnace with DX Cooling OA Rate [cfm] | Split MS1 Furnace with DX Cooling OA Rate [cfm] | 109.9824 | 109.9824 | 109.9824 | 109.9824 | [6 empty] | 2021-05-06
GA_MA_Split MS2 Furnace with DX Cooling OA Rate [cfm] | Split MS2 Furnace with DX Cooling OA Rate [cfm] | 109.9824 | 109.9824 | 109.9824 | 109.9824 | [6 empty] | 2021-05-06
GA_MA_Split MSE Furnace with DX Cooling OA Rate [cfm] | Split MSE Furnace with DX Cooling OA Rate [cfm] | 109.9824 | 109.9824 | 109.9824 | 109.9824 | [6 empty] | 2021-05-06
GA_MA_Split MSW Furnace with DX Cooling OA Rate [cfm] | Split MSW Furnace with DX Cooling OA Rate [cfm] | 109.9824 | 109.9824 | 109.9824 | 109.9824 | [6 empty] | 2021-05-06
GA_MA_Split Office Furnace with DX Cooling OA Rate [cfm] | Split Office Furnace with DX Cooling OA Rate [cfm] | 80.7372 | 80.7372 | 80.7372 | 80.7372 | [6 empty] | 2021-05-06
GA_MA_Split TN1 Furnace with DX Cooling OA Rate [cfm] | Split TN1 Furnace with DX Cooling OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | [6 empty] | 2021-05-06
GA_MA_Split TN2 Furnace with DX Cooling OA Rate [cfm] | Split TN2 Furnace with DX Cooling OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | [6 empty] | 2021-05-06
GA_MA_Split TNE Furnace with DX Cooling OA Rate [cfm] | Split TNE Furnace with DX Cooling OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | [6 empty] | 2021-05-06
GA_MA_Split TNW Furnace with DX Cooling OA Rate [cfm] | Split TNW Furnace with DX Cooling OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | [6 empty] | 2021-05-06
GA_MA_Split TS1 Furnace with DX Cooling OA Rate [cfm] | Split TS1 Furnace with DX Cooling OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | [6 empty] | 2021-05-06
GA_MA_Split TS2 Furnace with DX Cooling OA Rate [cfm] | Split TS2 Furnace with DX Cooling OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | [6 empty] | 2021-05-06
GA_MA_Split TSE Furnace with DX Cooling OA Rate [cfm] | Split TSE Furnace with DX Cooling OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | [6 empty] | 2021-05-06
GA_MA_Split TSW Furnace with DX Cooling OA Rate [cfm] | Split TSW Furnace with DX Cooling OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | [6 empty] | 2021-05-06
GA_MA_SPLIT GSW HEATING COIL Heating Capacity [kBtu/hr] | SPLIT GSW HEATING COIL Heating Capacity [kBtu/hr] | 5.9135 | 5.8092 | 7.4828 | 7.4096 | [6 empty] | 2021-05-06
GA_MA_SPLIT GNW HEATING COIL Heating Capacity [kBtu/hr] | SPLIT GNW HEATING COIL Heating Capacity [kBtu/hr] | 5.8706 | 5.7625 | 7.4376 | 7.3598 | [6 empty] | 2021-05-06
GA_MA_SPLIT OFFICE HEATING COIL Heating Capacity [kBtu/hr] | SPLIT OFFICE HEATING COIL Heating Capacity [kBtu/hr] | 15.8854 | 15.7146 | 18.8467 | 18.7837 | [6 empty] | 2021-05-06
GA_MA_SPLIT GNE HEATING COIL Heating Capacity [kBtu/hr] | SPLIT GNE HEATING COIL Heating Capacity [kBtu/hr] | 5.8545 | 5.7491 | 7.4135 | 7.339 | [6 empty] | 2021-05-06
GA_MA_SPLIT GN1 HEATING COIL Heating Capacity [kBtu/hr] | SPLIT GN1 HEATING COIL Heating Capacity [kBtu/hr] | 4.5684 | 4.5684 | 5.2178 | 5.1958 | [6 empty] | 2021-05-06
GA_MA_SPLIT GN2 HEATING COIL Heating Capacity [kBtu/hr] | SPLIT GN2 HEATING COIL Heating Capacity [kBtu/hr] | 4.5684 | 4.5684 | 5.217 | 5.1952 | [6 empty] | 2021-05-06
GA_MA_SPLIT GS1 HEATING COIL Heating Capacity [kBtu/hr] | SPLIT GS1 HEATING COIL Heating Capacity [kBtu/hr] | 4.5684 | 4.5684 | 5.1735 | 5.1562 | [6 empty] | 2021-05-06
GA_MA_SPLIT GS2 HEATING COIL Heating Capacity [kBtu/hr] | SPLIT GS2 HEATING COIL Heating Capacity [kBtu/hr] | 4.5684 | 4.5684 | 5.6667 | 5.6512 | [6 empty] | 2021-05-06
GA_MA_SPLIT MSW HEATING COIL Heating Capacity [kBtu/hr] | SPLIT MSW HEATING COIL Heating Capacity [kBtu/hr] | 10.0942 | 9.8921 | 14.0881 | 13.9153 | [6 empty] | 2021-05-06
GA_MA_SPLIT MNW HEATING COIL Heating Capacity [kBtu/hr] | SPLIT MNW HEATING COIL Heating Capacity [kBtu/hr] | 10.1624 | 9.9502 | 14.1833 | 13.9988 | [6 empty] | 2021-05-06
GA_MA_SPLIT MSE HEATING COIL Heating Capacity [kBtu/hr] | SPLIT MSE HEATING COIL Heating Capacity [kBtu/hr] | 10.0548 | 9.8593 | 14.0306 | 13.8658 | [6 empty] | 2021-05-06
GA_MA_SPLIT MNE HEATING COIL Heating Capacity [kBtu/hr] | SPLIT MNE HEATING COIL Heating Capacity [kBtu/hr] | 10.123 | 9.9174 | 14.1259 | 13.9493 | [6 empty] | 2021-05-06
GA_MA_SPLIT MN1 HEATING COIL Heating Capacity [kBtu/hr] | SPLIT MN1 HEATING COIL Heating Capacity [kBtu/hr] | 9.1368 | 9.1368 | 9.5665 | 9.5665 | [6 empty] | 2021-05-06
GA_MA_SPLIT MN2 HEATING COIL Heating Capacity [kBtu/hr] | SPLIT MN2 HEATING COIL Heating Capacity [kBtu/hr] | 9.1368 | 9.1368 | 9.5665 | 9.5665 | [6 empty] | 2021-05-06
GA_MA_SPLIT MS1 HEATING COIL Heating Capacity [kBtu/hr] | SPLIT MS1 HEATING COIL Heating Capacity [kBtu/hr] | 9.1368 | 9.1368 | 9.5665 | 9.5665 | [6 empty] | 2021-05-06
GA_MA_SPLIT MS2 HEATING COIL Heating Capacity [kBtu/hr] | SPLIT MS2 HEATING COIL Heating Capacity [kBtu/hr] | 9.1368 | 9.1368 | 9.5665 | 9.5665 | [6 empty] | 2021-05-06
GA_MA_SPLIT TSW HEATING COIL Heating Capacity [kBtu/hr] | SPLIT TSW HEATING COIL Heating Capacity [kBtu/hr] | 7.8002 | 7.7023 | 10.4252 | 10.3395 | [6 empty] | 2021-05-06
GA_MA_SPLIT TNW HEATING COIL Heating Capacity [kBtu/hr] | SPLIT TNW HEATING COIL Heating Capacity [kBtu/hr] | 7.8407 | 7.738 | 10.4804 | 10.3888 | [6 empty] | 2021-05-06
GA_MA_SPLIT TSE HEATING COIL Heating Capacity [kBtu/hr] | SPLIT TSE HEATING COIL Heating Capacity [kBtu/hr] | 7.7793 | 7.685 | 10.3953 | 10.3137 | [6 empty] | 2021-05-06
GA_MA_SPLIT TNE HEATING COIL Heating Capacity [kBtu/hr] | SPLIT TNE HEATING COIL Heating Capacity [kBtu/hr] | 7.8197 | 7.7206 | 10.4504 | 10.363 | [6 empty] | 2021-05-06
GA_MA_SPLIT TN1 HEATING COIL Heating Capacity [kBtu/hr] | SPLIT TN1 HEATING COIL Heating Capacity [kBtu/hr] | 6.0084 | 5.9633 | 7.8317 | 7.7939 | [6 empty] | 2021-05-06
GA_MA_SPLIT TN2 HEATING COIL Heating Capacity [kBtu/hr] | SPLIT TN2 HEATING COIL Heating Capacity [kBtu/hr] | 6.0078 | 5.9628 | 7.8308 | 7.7932 | [6 empty] | 2021-05-06
GA_MA_SPLIT TS1 HEATING COIL Heating Capacity [kBtu/hr] | SPLIT TS1 HEATING COIL Heating Capacity [kBtu/hr] | 5.961 | 5.9204 | 7.7694 | 7.7374 | [6 empty] | 2021-05-06
GA_MA_SPLIT TS2 HEATING COIL Heating Capacity [kBtu/hr] | SPLIT TS2 HEATING COIL Heating Capacity [kBtu/hr] | 5.9603 | 5.9199 | 7.7686 | 7.7366 | [6 empty] | 2021-05-06
GA_MA_Split_GSW ERV Flag | Split_GSW ERV Flag | No | Yes | No | Yes | [6 empty] | 2021-05-06
GA_MA_Split_GNW ERV Flag | Split_GNW ERV Flag | No | Yes | No | Yes | [6 empty] | 2021-05-06
GA_MA_Split_GNE ERV Flag | Split_GNE ERV Flag | No | Yes | No | Yes | [6 empty] | 2021-05-06
GA_MA_Split_GN1 ERV Flag | Split_GN1 ERV Flag | No | Yes | No | Yes | [6 empty] | 2021-05-06
GA_MA_Split_GN2 ERV Flag | Split_GN2 ERV Flag | No | Yes | No | Yes | [6 empty] | 2021-05-06
GA_MA_Split_GS1 ERV Flag | Split_GS1 ERV Flag | No | Yes | No | Yes | [6 empty] | 2021-05-06
GA_MA_Split_GS2 ERV Flag | Split_GS2 ERV Flag | No | Yes | No | Yes | [6 empty] | 2021-05-06
GA_MA_Split_MSW ERV Flag | Split_MSW ERV Flag | No | Yes | No | Yes | [6 empty] | 2021-05-06
GA_MA_Split_MNW ERV Flag | Split_MNW ERV Flag | No | Yes | No | Yes | [6 empty] | 2021-05-06
GA_MA_Split_MSE ERV Flag | Split_MSE ERV Flag | No | Yes | No | Yes | [6 empty] | 2021-05-06
GA_MA_Split_MNE ERV Flag | Split_MNE ERV Flag | No | Yes | No | Yes | [6 empty] | 2021-05-06
GA_MA_Split_MN1 ERV Flag | Split_MN1 ERV Flag | No | Yes | No | Yes | [6 empty] | 2021-05-06
GA_MA_Split_MN2 ERV Flag | Split_MN2 ERV Flag | No | Yes | No | Yes | [6 empty] | 2021-05-06
GA_MA_Split_MS1 ERV Flag | Split_MS1 ERV Flag | No | Yes | No | Yes | [6 empty] | 2021-05-06
GA_MA_Split_MS2 ERV Flag | Split_MS2 ERV Flag | No | Yes | No | Yes | [6 empty] | 2021-05-06
GA_MA_Split_TSW ERV Flag | Split_TSW ERV Flag | No | Yes | No | Yes | [6 empty] | 2021-05-06
GA_MA_Split_TNW ERV Flag | Split_TNW ERV Flag | No | Yes | No | Yes | [6 empty] | 2021-05-06
GA_MA_Split_TSE ERV Flag | Split_TSE ERV Flag | No | Yes | No | Yes | [6 empty] | 2021-05-06
GA_MA_Split_TNE ERV Flag | Split_TNE ERV Flag | No | Yes | No | Yes | [6 empty] | 2021-05-06
GA_MA_Split_TN1 ERV Flag | Split_TN1 ERV Flag | No | Yes | No | Yes | [6 empty] | 2021-05-06
GA_MA_Split_TN2 ERV Flag | Split_TN2 ERV Flag | No | Yes | No | Yes | [6 empty] | 2021-05-06
GA_MA_Split_TS1 ERV Flag | Split_TS1 ERV Flag | No | Yes | No | Yes | [6 empty] | 2021-05-06
GA_MA_Split_TS2 ERV Flag | Split_TS2 ERV Flag | No | Yes | No | Yes | [6 empty] | 2021-05-06
id | item | Zone1A(HI-Honolulu-HI) ASHRAE901-state_STD2016 | Zone1A(HI-Honolulu-HI) ASHRAE901-state_STD2019 | [8 empty] | 2021-05-06
HI_SO_PSZ-AC:1 Cooling Capacity [ton] | PSZ-AC:1 Cooling Capacity [ton] | 1.8822 | 1.7854 | [8 empty] | 2021-05-06
HI_SO_PSZ-AC:2 Cooling Capacity [ton] | PSZ-AC:2 Cooling Capacity [ton] | 1.7122 | 1.6179 | [8 empty] | 2021-05-06
HI_SO_PSZ-AC:3 Cooling Capacity [ton] | PSZ-AC:3 Cooling Capacity [ton] | 1.2243 | 1.1617 | [8 empty] | 2021-05-06
HI_SO_PSZ-AC:4 Cooling Capacity [ton] | PSZ-AC:4 Cooling Capacity [ton] | 1.6967 | 1.6099 | [8 empty] | 2021-05-06
HI_SO_PSZ-AC:5 Cooling Capacity [ton] | PSZ-AC:5 Cooling Capacity [ton] | 1.4318 | 1.3579 | [8 empty] | 2021-05-06
HI_SO_PSZ-AC:1 Supply Flow Rate [cfm] | PSZ-AC:1 Supply Flow Rate [cfm] | 678.0416 | 614.4752 | [8 empty] | 2021-05-06
HI_SO_PSZ-AC:2 Supply Flow Rate [cfm] | PSZ-AC:2 Supply Flow Rate [cfm] | 635.664 | 593.2864 | [8 empty] | 2021-05-06
HI_SO_PSZ-AC:3 Supply Flow Rate [cfm] | PSZ-AC:3 Supply Flow Rate [cfm] | 487.3424 | 466.1536 | [8 empty] | 2021-05-06
HI_SO_PSZ-AC:4 Supply Flow Rate [cfm] | PSZ-AC:4 Supply Flow Rate [cfm] | 635.664 | 593.2864 | [8 empty] | 2021-05-06
HI_SO_PSZ-AC:5 Supply Flow Rate [cfm] | PSZ-AC:5 Supply Flow Rate [cfm] | 593.2864 | 550.9088 | [8 empty] | 2021-05-06
HI_SO_PSZ-AC:1 OA Rate [cfm] | PSZ-AC:1 OA Rate [cfm] | 136.9178 | 136.9178 | [8 empty] | 2021-05-06
HI_SO_PSZ-AC:2 OA Rate [cfm] | PSZ-AC:2 OA Rate [cfm] | 103.7925 | 103.7925 | [8 empty] | 2021-05-06
HI_SO_PSZ-AC:3 OA Rate [cfm] | PSZ-AC:3 OA Rate [cfm] | 61.5711 | 61.5711 | [8 empty] | 2021-05-06
HI_SO_PSZ-AC:4 OA Rate [cfm] | PSZ-AC:4 OA Rate [cfm] | 103.7925 | 103.7925 | [8 empty] | 2021-05-06
HI_SO_PSZ-AC:5 OA Rate [cfm] | PSZ-AC:5 OA Rate [cfm] | 61.5711 | 61.5711 | [8 empty] | 2021-05-06
HI_SO_PSZ-AC:1 heating Capacity [kBtu/hr] | PSZ-AC:1 heating Capacity [kBtu/hr] | 6.3489 | 6.3489 | [8 empty] | 2021-05-06
HI_SO_PSZ-AC:2 heating Capacity [kBtu/hr] | PSZ-AC:2 heating Capacity [kBtu/hr] | 4.8129 | 4.8129 | [8 empty] | 2021-05-06
HI_SO_PSZ-AC:3 heating Capacity [kBtu/hr] | PSZ-AC:3 heating Capacity [kBtu/hr] | 2.855 | 2.855 | [8 empty] | 2021-05-06
HI_SO_PSZ-AC:4 heating Capacity [kBtu/hr] | PSZ-AC:4 heating Capacity [kBtu/hr] | 4.8129 | 4.8129 | [8 empty] | 2021-05-06
HI_SO_PSZ-AC:5 heating Capacity [kBtu/hr] | PSZ-AC:5 heating Capacity [kBtu/hr] | 2.855 | 2.855 | [8 empty] | 2021-05-06
id | item | Zone1A(HI-Honolulu-HI) ASHRAE901-state_STD2016 | Zone1A(HI-Honolulu-HI) ASHRAE901-state_STD2019 | [8 empty] | 2021-05-06
HI_LO_CAV_BAS Supply Flow Rate [cfm] | CAV_BAS Supply Flow Rate [cfm] | 11950.4832 | 11081.7424 | [8 empty] | 2021-05-06
HI_LO_VAV_BOT WITH REHEAT Supply Flow Rate [cfm] | VAV_BOT WITH REHEAT Supply Flow Rate [cfm] | 19218.2416 | 18201.1792 | [8 empty] | 2021-05-06
HI_LO_VAV_MID WITH REHEAT Supply Flow Rate [cfm] | VAV_MID WITH REHEAT Supply Flow Rate [cfm] | 177858.7875 | 168027.1843 | [8 empty] | 2021-05-06
HI_LO_VAV_TOP WITH REHEAT Supply Flow Rate [cfm] | VAV_TOP WITH REHEAT Supply Flow Rate [cfm] | 19091.1088 | 18074.0464 | [8 empty] | 2021-05-06
HI_LO_Supply Air Temp. Reset Flag | Supply Air Temp. Reset Flag | No | Yes | [8 empty] | 2021-05-06
HI_LO_CAV_BAS OA Rate [cfm] | CAV_BAS OA Rate [cfm] | 2542.8255 | 2542.8255 | [8 empty] | 2021-05-06
HI_LO_VAV_BOT WITH REHEAT OA Rate [cfm] | VAV_BOT WITH REHEAT OA Rate [cfm] | 5377.8022 | 4302.174 | [8 empty] | 2021-05-06
HI_LO_VAV_MID WITH REHEAT OA Rate [cfm] | VAV_MID WITH REHEAT OA Rate [cfm] | 53777.9373 | 43021.7396 | [8 empty] | 2021-05-06
HI_LO_VAV_TOP WITH REHEAT OA Rate [cfm] | VAV_TOP WITH REHEAT OA Rate [cfm] | 5377.8022 | 4302.174 | [8 empty] | 2021-05-06
HI_LO_AIRLOOP DATACENTER BASEMENT OA Rate [cfm] | AIRLOOP DATACENTER BASEMENT OA Rate [cfm] | 716.9654 | 716.9654 | [8 empty] | 2021-05-06
HI_LO_VAV_bot_WITH_REHEAT ERV Flag | VAV_bot_WITH_REHEAT ERV Flag | Yes | Yes | [8 empty] | 2021-05-06
HI_LO_VAV_mid_WITH_REHEAT ERV Flag | VAV_mid_WITH_REHEAT ERV Flag | Yes | Yes | [8 empty] | 2021-05-06
HI_LO_VAV_top_WITH_REHEAT ERV Flag | VAV_top_WITH_REHEAT ERV Flag | Yes | Yes | [8 empty] | 2021-05-06
HI_LO_COOLSYS1 CHILLER1 Capacity [ton] | COOLSYS1 CHILLER1 Capacity [ton] | 396.2321 | 358.1305 | [8 empty] | 2021-05-06
HI_LO_COOLSYS1 CHILLER2 Capacity [ton] | COOLSYS1 CHILLER2 Capacity [ton] | 396.2321 | 358.1305 | [8 empty] | 2021-05-06
HI_LO_TOWERWATERSYS COOLTOWER 1 Capacity [ton] | TOWERWATERSYS COOLTOWER 1 Capacity [ton] | 376.1021 | 339.9372 | [8 empty] | 2021-05-06
HI_LO_TOWERWATERSYS COOLTOWER 2 Capacity [ton] | TOWERWATERSYS COOLTOWER 2 Capacity [ton] | 376.1021 | 339.9372 | [8 empty] | 2021-05-06
HI_LO_HEATSYS1 BOILER Capacity [MMBTU/h] | HEATSYS1 BOILER Capacity [MMBTU/h] | 2309.1551 | 2114.9048 | [8 empty] | 2021-05-06
HI_LO_COOLSYS1 PUMP Flow Rate [gal/min] | COOLSYS1 PUMP Flow Rate [gal/min] | 0 | 0 | [8 empty] | 2021-05-06
HI_LO_COOLSYS1 CHILLER1 PUMP Flow Rate [gal/min] | COOLSYS1 CHILLER1 PUMP Flow Rate [gal/min] | 621.4674 | 561.485 | [8 empty] | 2021-05-06
HI_LO_COOLSYS1 CHILLER2 PUMP Flow Rate [gal/min] | COOLSYS1 CHILLER2 PUMP Flow Rate [gal/min] | 621.4674 | 561.485 | [8 empty] | 2021-05-06
HI_LO_COOLSYS1 PUMP SECONDARY Flow Rate [gal/min] | COOLSYS1 PUMP SECONDARY Flow Rate [gal/min] | 1242.9332 | 1122.9716 | [8 empty] | 2021-05-06
HI_LO_HEATSYS1 PUMP Flow Rate [gal/min] | HEATSYS1 PUMP Flow Rate [gal/min] | 473.9849 | 434.1118 | [8 empty] | 2021-05-06
HI_LO_TOWERWATERSYS PUMP Flow Rate [gal/min] | TOWERWATERSYS PUMP Flow Rate [gal/min] | 2186.0766 | 1975.9013 | [8 empty] | 2021-05-06
HI_LO_PLANT CIRC PUMP Flow Rate [gal/min] | PLANT CIRC PUMP Flow Rate [gal/min] | 207.858 | 206.6803 | [8 empty] | 2021-05-06
HI_LO_COOLSYS1 PUMP SECONDARY Pressure setpoint reset [yes,no] | COOLSYS1 PUMP SECONDARY Pressure setpoint reset [yes,no] | pump_ride_on_curve | pump_ride_on_curve | [8 empty] | 2021-05-06
HI_LO_COOLSYS1 CHILLER1 PUMP Pump Power [hp] | COOLSYS1 CHILLER1 PUMP Pump Power [hp] | 3.3526 | 2.999 | [8 empty] | 2021-05-06
HI_LO_COOLSYS1 CHILLER2 PUMP Pump Power [hp] | COOLSYS1 CHILLER2 PUMP Pump Power [hp] | 3.3526 | 2.999 | [8 empty] | 2021-05-06
HI_LO_COOLSYS1 PUMP SECONDARY Pump Power [hp] | COOLSYS1 PUMP SECONDARY Pump Power [hp] | 20.1156 | 17.9942 | [8 empty] | 2021-05-06
HI_LO_HEATSYS1 PUMP Pump Power [hp] | HEATSYS1 PUMP Pump Power [hp] | 10.2454 | 9.2907 | [8 empty] | 2021-05-06
HI_LO_TOWERWATERSYS PUMP Pump Power [hp] | TOWERWATERSYS PUMP Pump Power [hp] | 39.139 | 35.0251 | [8 empty] | 2021-05-06
HI_LO_PLANT CIRC PUMP Pump Power [hp] | PLANT CIRC PUMP Pump Power [hp] | 4.4853 | 4.4157 | [8 empty] | 2021-05-06
HI_LO_Datacenter PLANT CIRC PUMP Pump Power [hp] | Datacenter PLANT CIRC PUMP Pump Power [hp] | 4.4853 | 4.4157 | [8 empty] | 2021-05-06
HI_LO_ZN_VAV_BOXes_Max_Reheat_Water_Flow_GPM | ZN_VAV_BOXes_Max_Reheat_Water_Flow_GPM | 220.7018 | 196.7949 | [8 empty] | 2021-05-06
HI_LO_COOLSYS1 PUMP SECONDARY VSD | COOLSYS1 PUMP SECONDARY VSD | No | No | [8 empty] | 2021-05-06
HI_LO_HEATSYS1 PUMP VSD | HEATSYS1 PUMP VSD | No | No | [8 empty] | 2021-05-06
HI_LO_DATACENTER BASEMENT Cooling Capacity [ton] | DATACENTER BASEMENT Cooling Capacity [ton] | 121.658 | 121.2963 | [8 empty] | 2021-05-06
HI_LO_DATACENTER BOT Cooling Capacity [ton] | DATACENTER BOT Cooling Capacity [ton] | 2.6565 | 2.6133 | [8 empty] | 2021-05-06
HI_LO_DATACENTER MID Cooling Capacity [ton] | DATACENTER MID Cooling Capacity [ton] | 25.3631 | 24.9459 | [8 empty] | 2021-05-06
HI_LO_DATACENTER TOP Cooling Capacity [ton] | DATACENTER TOP Cooling Capacity [ton] | 2.5828 | 2.5419 | [8 empty] | 2021-05-06
id | item | Zone1A(HI-Honolulu-HI) ASHRAE901-state_STD2016 | Zone1A(HI-Honolulu-HI) ASHRAE901-state_STD2019 | [8 empty] | 2021-05-06
HI_RS_PSZ-AC:1 Cooling Capacity [ton] | PSZ-AC:1 Cooling Capacity [ton] | 11.1784 | 10.7502 | [8 empty] | 2021-05-06
HI_RS_PSZ-AC:2 Cooling Capacity [ton] | PSZ-AC:2 Cooling Capacity [ton] | 48.3879 | 46.3563 | [8 empty] | 2021-05-06
HI_RS_PSZ-AC:3 Cooling Capacity [ton] | PSZ-AC:3 Cooling Capacity [ton] | 6.446 | 6.316 | [8 empty] | 2021-05-06
HI_RS_PSZ-AC:4 Cooling Capacity [ton] | PSZ-AC:4 Cooling Capacity [ton] | 5.6649 | 5.5202 | [8 empty] | 2021-05-06
HI_RS_PSZ-AC:1 Supply Flow Rate [cfm] | PSZ-AC:1 Supply Flow Rate [cfm] | 4195.3824 | 4004.6832 | [8 empty] | 2021-05-06
HI_RS_PSZ-AC:2 Supply Flow Rate [cfm] | PSZ-AC:2 Supply Flow Rate [cfm] | 15806.8448 | 14895.7264 | [8 empty] | 2021-05-06
HI_RS_PSZ-AC:3 Supply Flow Rate [cfm] | PSZ-AC:3 Supply Flow Rate [cfm] | 2394.3344 | 2330.768 | [8 empty] | 2021-05-06
HI_RS_PSZ-AC:4 Supply Flow Rate [cfm] | PSZ-AC:4 Supply Flow Rate [cfm] | 1991.7472 | 1928.1808 | [8 empty] | 2021-05-06
HI_RS_PSZ-AC:1 OA Rate [cfm] | PSZ-AC:1 OA Rate [cfm] | 490.669 | 490.669 | [8 empty] | 2021-05-06
HI_RS_PSZ-AC:2 OA Rate [cfm] | PSZ-AC:2 OA Rate [cfm] | 4005.1282 | 4005.1282 | [8 empty] | 2021-05-06
HI_RS_PSZ-AC:3 OA Rate [cfm] | PSZ-AC:3 OA Rate [cfm] | 377.3937 | 377.3937 | [8 empty] | 2021-05-06
HI_RS_PSZ-AC:4 OA Rate [cfm] | PSZ-AC:4 OA Rate [cfm] | 377.3937 | 377.3937 | [8 empty] | 2021-05-06
HI_RS_PSZ-AC:1 OA Damper [gravity, motorized] | PSZ-AC:1 OA Damper [gravity, motorized] | gravity | gravity | [8 empty] | 2021-05-06
HI_RS_PSZ-AC:2 OA Damper [gravity, motorized] | PSZ-AC:2 OA Damper [gravity, motorized] | gravity | gravity | [8 empty] | 2021-05-06
HI_RS_PSZ-AC:3 OA Damper [gravity, motorized] | PSZ-AC:3 OA Damper [gravity, motorized] | gravity | gravity | [8 empty] | 2021-05-06
HI_RS_PSZ-AC:4 OA Damper [gravity, motorized] | PSZ-AC:4 OA Damper [gravity, motorized] | gravity | gravity | [8 empty] | 2021-05-06
HI_RS_PSZ-AC:1 Heating Capacity [kBtu/hr] | PSZ-AC:1 Heating Capacity [kBtu/hr] | 157.985 | 149.3696 | [8 empty] | 2021-05-06
HI_RS_PSZ-AC:2 Heating Capacity [kBtu/hr] | PSZ-AC:2 Heating Capacity [kBtu/hr] | 607.7994 | 572.5679 | [8 empty] | 2021-05-06
HI_RS_PSZ-AC:3 Heating Capacity [kBtu/hr] | PSZ-AC:3 Heating Capacity [kBtu/hr] | 92.7686 | 90.2628 | [8 empty] | 2021-05-06
HI_RS_PSZ-AC:4 Heating Capacity [kBtu/hr] | PSZ-AC:4 Heating Capacity [kBtu/hr] | 78.2158 | 75.6845 | [8 empty] | 2021-05-06
id | item | Zone1A(HI-Honolulu-HI) ASHRAE901-state_STD2016 | Zone1A(HI-Honolulu-HI) ASHRAE901-state_STD2019 | [8 empty] | 2021-05-06
HI_PS_VAV_POD_1 Cooling Capacity [ton] | VAV_POD_1 Cooling Capacity [ton] | 19.6469 | 18.4448 | [8 empty] | 2021-05-06
HI_PS_VAV_POD_2 Cooling Capacity [ton] | VAV_POD_2 Cooling Capacity [ton] | 19.7509 | 18.4434 | [8 empty] | 2021-05-06
HI_PS_VAV_POD_3 Cooling Capacity [ton] | VAV_POD_3 Cooling Capacity [ton] | 17.7317 | 16.5331 | [8 empty] | 2021-05-06
HI_PS_VAV_OTHER Cooling Capacity [ton] | VAV_OTHER Cooling Capacity [ton] | 27.3349 | 25.3802 | [8 empty] | 2021-05-06
HI_PS_PSZ-AC_1:6 Cooling Capacity [ton] | PSZ-AC_1:6 Cooling Capacity [ton] | 8.2226 | 7.9332 | [8 empty] | 2021-05-06
HI_PS_PSZ-AC_2:5 Cooling Capacity [ton] | PSZ-AC_2:5 Cooling Capacity [ton] | 5.5786 | 5.3279 | [8 empty] | 2021-05-06
HI_PS_PSZ-AC_2:7 Cooling Capacity [ton] | PSZ-AC_2:7 Cooling Capacity [ton] | 10.5074 | 10.5074 | [8 empty] | 2021-05-06
HI_PS_VAV_POD_1 Supply Flow Rate [cfm] | VAV_POD_1 Supply Flow Rate [cfm] | 5890.4864 | 5530.2768 | [8 empty] | 2021-05-06
HI_PS_VAV_POD_2 Supply Flow Rate [cfm] | VAV_POD_2 Supply Flow Rate [cfm] | 5932.864 | 5530.2768 | [8 empty] | 2021-05-06
HI_PS_VAV_POD_3 Supply Flow Rate [cfm] | VAV_POD_3 Supply Flow Rate [cfm] | 5318.3888 | 4958.1792 | [8 empty] | 2021-05-06
HI_PS_VAV_OTHER Supply Flow Rate [cfm] | VAV_OTHER Supply Flow Rate [cfm] | 8200.0656 | 7606.7792 | [8 empty] | 2021-05-06
HI_PS_PSZ-AC_2:5 Supply Flow Rate [cfm] | PSZ-AC_2:5 Supply Flow Rate [cfm] | 1673.9152 | 1589.16 | [8 empty] | 2021-05-06
HI_PS_PSZ-AC_1:6 Supply Flow Rate [cfm] | PSZ-AC_1:6 Supply Flow Rate [cfm] | 2542.656 | 2415.5232 | [8 empty] | 2021-05-06
HI_PS_PSZ-AC_2:7 Supply Flow Rate [cfm] | PSZ-AC_2:7 Supply Flow Rate [cfm] | 3157.1312 | 3157.1312 | [8 empty] | 2021-05-06
HI_PS_Supply Air Temp. Reset Flag | Supply Air Temp. Reset Flag | No | No | [8 empty] | 2021-05-06
HI_PS_VAV_POD_1 OA Rate [cfm] | VAV_POD_1 OA Rate [cfm] | 5893.58 | 5535.0019 | [8 empty] | 2021-05-06
HI_PS_VAV_POD_2 OA Rate [cfm] | VAV_POD_2 OA Rate [cfm] | 5926.91 | 5534.5569 | [8 empty] | 2021-05-06
HI_PS_VAV_POD_3 OA Rate [cfm] | VAV_POD_3 OA Rate [cfm] | 5318.6643 | 4961.294 | [8 empty] | 2021-05-06
HI_PS_VAV_OTHER OA Rate [cfm] | VAV_OTHER OA Rate [cfm] | 3736.1787 | 2988.8921 | [8 empty] | 2021-05-06
HI_PS_PSZ-AC_2:5 OA Rate [cfm] | PSZ-AC_2:5 OA Rate [cfm] | 1152.7343 | 1152.7343 | [8 empty] | 2021-05-06
HI_PS_PSZ-AC_1:6 OA Rate [cfm] | PSZ-AC_1:6 OA Rate [cfm] | 539.9118 | 539.9118 | [8 empty] | 2021-05-06
HI_PS_PSZ-AC_2:7 OA Rate [cfm] | PSZ-AC_2:7 OA Rate [cfm] | 3153.0841 | 3153.0841 | [8 empty] | 2021-05-06
HI_PS_VAV_POD_1 OA Damper [gravity, motorized] | VAV_POD_1 OA Damper [gravity, motorized] | gravity | gravity | [8 empty] | 2021-05-06
HI_PS_VAV_POD_2 OA Damper [gravity, motorized] | VAV_POD_2 OA Damper [gravity, motorized] | gravity | gravity | [8 empty] | 2021-05-06
HI_PS_VAV_POD_3 OA Damper [gravity, motorized] | VAV_POD_3 OA Damper [gravity, motorized] | gravity | gravity | [8 empty] | 2021-05-06
HI_PS_VAV_OTHER OA Damper [gravity, motorized] | VAV_OTHER OA Damper [gravity, motorized] | gravity | gravity | [8 empty] | 2021-05-06
HI_PS_PSZ-AC_2:5 OA Damper [gravity, motorized] | PSZ-AC_2:5 OA Damper [gravity, motorized] | gravity | gravity | [8 empty] | 2021-05-06
HI_PS_PSZ-AC_1:6 OA Damper [gravity, motorized] | PSZ-AC_1:6 OA Damper [gravity, motorized] | motorized | motorized | [8 empty] | 2021-05-06
HI_PS_PSZ-AC_2:7 OA Damper [gravity, motorized] | PSZ-AC_2:7 OA Damper [gravity, motorized] | gravity | gravity | [8 empty] | 2021-05-06
HI_PS_VAV_POD_1 (economizer) | VAV_POD_1 (economizer) | No | No | [8 empty] | 2021-05-06
HI_PS_VAV_POD_2 (economizer) | VAV_POD_2 (economizer) | No | No | [8 empty] | 2021-05-06
HI_PS_VAV_POD_3 (economizer) | VAV_POD_3 (economizer) | No | No | [8 empty] | 2021-05-06
HI_PS_VAV_OTHER (economizer) | VAV_OTHER (economizer) | No | No | [8 empty] | 2021-05-06
HI_PS_PSZ-AC_2:5 (economizer) | PSZ-AC_2:5 (economizer) | No | No | [8 empty] | 2021-05-06
HI_PS_PSZ-AC_1:6 (economizer) | PSZ-AC_1:6 (economizer) | No | No | [8 empty] | 2021-05-06
HI_PS_PSZ-AC_2:7 (economizer) | PSZ-AC_2:7 (economizer) | No | No | [8 empty] | 2021-05-06
HI_PS_VAV_Pod_1_ERV Flag | VAV_Pod_1_ERV Flag | Yes | Yes | [8 empty] | 2021-05-06
HI_PS_VAV_Pod_2_ERV Flag | VAV_Pod_2_ERV Flag | Yes | Yes | [8 empty] | 2021-05-06
HI_PS_VAV_Pod_3_ERV Flag | VAV_Pod_3_ERV Flag | Yes | Yes | [8 empty] | 2021-05-06
HI_PS_VAV_OTHER_ERV Flag | VAV_OTHER_ERV Flag | Yes | Yes | [8 empty] | 2021-05-06
HI_PS_PSZ_AC_2_5_ERV Flag | PSZ_AC_2_5_ERV Flag | No | Yes | [8 empty] | 2021-05-06
HI_PS_PSZ_AC_2_7_ERV Flag | PSZ_AC_2_7_ERV Flag | Yes | Yes | [8 empty] | 2021-05-06
HI_PS_HEATSYS1 Capacity [MMBTU/h] | HEATSYS1 Capacity [MMBTU/h] | 0.57008 | 0.50643 | [8 empty] | 2021-05-06
HI_PS_HEATSYS1 Flow Rate [gal/min] | HEATSYS1 Flow Rate [gal/min] | 58.5083 | 51.9753 | [8 empty] | 2021-05-06
HI_PS_VAV_POD_1 Fan Power [hp] | VAV_POD_1 Fan Power [hp] | 8.698 | 8.1658 | [8 empty] | 2021-05-06
HI_PS_VAV_POD_2 Fan Power [hp] | VAV_POD_2 Fan Power [hp] | 8.744 | 8.1651 | [8 empty] | 2021-05-06
HI_PS_VAV_POD_3 Fan Power [hp] | VAV_POD_3 Fan Power [hp] | 7.8501 | 7.3194 | [8 empty] | 2021-05-06
HI_PS_VAV_OTHER Fan Power [hp] | VAV_OTHER Fan Power [hp] | 11.3642 | 10.5515 | [8 empty] | 2021-05-06
HI_PS_HEATSYS1 Pump Power [hp] | HEATSYS1 Pump Power [hp] | 1.2647 | 1.1124 | [8 empty] | 2021-05-06
HI_PS_PSZ-AC_1:6 Heating Capacity [kBtu/hr] | PSZ-AC_1:6 Heating Capacity [kBtu/hr] | 180.5036 | 171.0029 | [8 empty] | 2021-05-06
HI_PS_PSZ-AC_2:5 Heating Capacity [kBtu/hr] | PSZ-AC_2:5 Heating Capacity [kBtu/hr] | 72.7502 | 69.9656 | [8 empty] | 2021-05-06
HI_PS_PSZ-AC_2:7 Heating Capacity [kBtu/hr] | PSZ-AC_2:7 Heating Capacity [kBtu/hr] | 146.2089 | 146.2089 | [8 empty] | 2021-05-06
HI_PS_ZN_VAV_BOXes_Max_Reheat_Water_Flow_GPM | ZN_VAV_BOXes_Max_Reheat_Water_Flow_GPM | 39.0463 | 33.8181 | [8 empty] | 2021-05-06
id | item | Zone1A(HI-Honolulu-HI) ASHRAE901-state_STD2016 | Zone1A(HI-Honolulu-HI) ASHRAE901-state_STD2019 | [8 empty] | 2021-05-06
HI_SH_SAC_FRONTOFFICE Cooling Capacity [ton] | SAC_FRONTOFFICE Cooling Capacity [ton] | 2.492 | 2.3534 | [8 empty] | 2021-05-06
HI_SH_SAC_FRONTLOUNGE Cooling Capacity [ton] | SAC_FRONTLOUNGE Cooling Capacity [ton] | 6.3631 | 5.9933 | [8 empty] | 2021-05-06
HI_SH_SAC_MEETINGROOM Cooling Capacity [ton] | SAC_MEETINGROOM Cooling Capacity [ton] | 3.0425 | 2.9226 | [8 empty] | 2021-05-06
HI_SH_SAC_EXC_EMPLGE_RESTRM Cooling Capacity [ton] | SAC_EXC_EMPLGE_RESTRM Cooling Capacity [ton] | 5.7838 | 5.7423 | [8 empty] | 2021-05-06
HI_SH_SAC_FO_ADDAQ SUPPLY FAN Supply Flow Rate [cfm] | SAC_FO_ADDAQ SUPPLY FAN Supply Flow Rate [cfm] | 847.552 | 783.9856 | [8 empty] | 2021-05-06
HI_SH_SAC_FL_ADDAQ SUPPLY FAN Supply Flow Rate [cfm] | SAC_FL_ADDAQ SUPPLY FAN Supply Flow Rate [cfm] | 1906.992 | 1801.048 | [8 empty] | 2021-05-06
HI_SH_SAC_MR_ADDAQ SUPPLY FAN Supply Flow Rate [cfm] | SAC_MR_ADDAQ SUPPLY FAN Supply Flow Rate [cfm] | 911.1184 | 868.7408 | [8 empty] | 2021-05-06
HI_SH_SAC_EXC_ADDAQ SUPPLY FAN Supply Flow Rate [cfm] | SAC_EXC_ADDAQ SUPPLY FAN Supply Flow Rate [cfm] | 2118.88 | 2118.88 | [8 empty] | 2021-05-06
HI_SH_SAC_Exc_EmpLge_RestRm OA Rate [cfm] | SAC_Exc_EmpLge_RestRm OA Rate [cfm] | 199.9928 | 199.9928 | [8 empty] | 2021-05-06
HI_SH_SAC_FrontLounge OA Rate [cfm] | SAC_FrontLounge OA Rate [cfm] | 500.0133 | 500.0133 | [8 empty] | 2021-05-06
HI_SH_SAC_FrontOffice OA Rate [cfm] | SAC_FrontOffice OA Rate [cfm] | 119.2938 | 119.2938 | [8 empty] | 2021-05-06
HI_SH_SAC_MeetingRoom OA Rate [cfm] | SAC_MeetingRoom OA Rate [cfm] | 267.7629 | 267.7629 | [8 empty] | 2021-05-06
HI_SH_SAC_FrontLounge OA Damper [gravity, motorized] | SAC_FrontLounge OA Damper [gravity, motorized] | motorized | motorized | [8 empty] | 2021-05-06
HI_SH_SAC_FrontOffice (economizer) | SAC_FrontOffice (economizer) | No | No | [8 empty] | 2021-05-06
HI_SH_SAC_FrontLounge (economizer) | SAC_FrontLounge (economizer) | No | No | [8 empty] | 2021-05-06
HI_SH_SAC_MeetingRoom (economizer) | SAC_MeetingRoom (economizer) | No | No | [8 empty] | 2021-05-06
HI_SH_SAC_Exc_EmpLge_RestRm (economizer) | SAC_Exc_EmpLge_RestRm (economizer) | No | No | [8 empty] | 2021-05-06
HI_SH_SAC_FRONTOFFICE Heating Capacity [kBtu/hr] | SAC_FRONTOFFICE Heating Capacity [kBtu/hr] | 32.5495 | 30.3348 | [8 empty] | 2021-05-06
HI_SH_SAC_FRONTLOUNGE Heating Capacity [kBtu/hr] | SAC_FRONTLOUNGE Heating Capacity [kBtu/hr] | 75.0561 | 70.9723 | [8 empty] | 2021-05-06
HI_SH_SAC_MEETINGROOM Heating Capacity [kBtu/hr] | SAC_MEETINGROOM Heating Capacity [kBtu/hr] | 36.162 | 34.8384 | [8 empty] | 2021-05-06
HI_SH_SAC_EXC_EMPLGE_RESTRM Heating Capacity [kBtu/hr] | SAC_EXC_EMPLGE_RESTRM Heating Capacity [kBtu/hr] | 80.2406 | 79.5624 | [8 empty] | 2021-05-06
id | item | Zone1A(HI-Honolulu-HI) ASHRAE901-state_STD2016 | Zone1A(HI-Honolulu-HI) ASHRAE901-state_STD2019 | [8 empty] | 2021-05-06
HI_MA_SPLIT GSW COOLING COIL Cooling Capacity [ton] | SPLIT GSW COOLING COIL Cooling Capacity [ton] | 1.0064 | 0.98509 | [8 empty] | 2021-05-06
HI_MA_SPLIT GNW COOLING COIL Cooling Capacity [ton] | SPLIT GNW COOLING COIL Cooling Capacity [ton] | 0.98323 | 0.96212 | [8 empty] | 2021-05-06
HI_MA_SPLIT OFFICE COOLING COIL Cooling Capacity [ton] | SPLIT OFFICE COOLING COIL Cooling Capacity [ton] | 1.7854 | 1.6624 | [8 empty] | 2021-05-06
HI_MA_SPLIT GNE COOLING COIL Cooling Capacity [ton] | SPLIT GNE COOLING COIL Cooling Capacity [ton] | 0.84244 | 0.82108 | [8 empty] | 2021-05-06
HI_MA_SPLIT GN1 COOLING COIL Cooling Capacity [ton] | SPLIT GN1 COOLING COIL Cooling Capacity [ton] | 0.68914 | 0.67765 | [8 empty] | 2021-05-06
HI_MA_SPLIT GN2 COOLING COIL Cooling Capacity [ton] | SPLIT GN2 COOLING COIL Cooling Capacity [ton] | 0.68665 | 0.67528 | [8 empty] | 2021-05-06
HI_MA_SPLIT GS1 COOLING COIL Cooling Capacity [ton] | SPLIT GS1 COOLING COIL Cooling Capacity [ton] | 0.71127 | 0.69956 | [8 empty] | 2021-05-06
HI_MA_SPLIT GS2 COOLING COIL Cooling Capacity [ton] | SPLIT GS2 COOLING COIL Cooling Capacity [ton] | 0.74402 | 0.72893 | [8 empty] | 2021-05-06
HI_MA_SPLIT MSW COOLING COIL Cooling Capacity [ton] | SPLIT MSW COOLING COIL Cooling Capacity [ton] | 2.1728 | 2.1193 | [8 empty] | 2021-05-06
HI_MA_SPLIT MNW COOLING COIL Cooling Capacity [ton] | SPLIT MNW COOLING COIL Cooling Capacity [ton] | 2.1335 | 2.0805 | [8 empty] | 2021-05-06
HI_MA_SPLIT MSE COOLING COIL Cooling Capacity [ton] | SPLIT MSE COOLING COIL Cooling Capacity [ton] | 1.777 | 1.7633 | [8 empty] | 2021-05-06
HI_MA_SPLIT MNE COOLING COIL Cooling Capacity [ton] | SPLIT MNE COOLING COIL Cooling Capacity [ton] | 1.7797 | 1.7302 | [8 empty] | 2021-05-06
HI_MA_SPLIT MN1 COOLING COIL Cooling Capacity [ton] | SPLIT MN1 COOLING COIL Cooling Capacity [ton] | 1.3957 | 1.3718 | [8 empty] | 2021-05-06
HI_MA_SPLIT MN2 COOLING COIL Cooling Capacity [ton] | SPLIT MN2 COOLING COIL Cooling Capacity [ton] | 1.3896 | 1.366 | [8 empty] | 2021-05-06
HI_MA_SPLIT MS1 COOLING COIL Cooling Capacity [ton] | SPLIT MS1 COOLING COIL Cooling Capacity [ton] | 1.4412 | 1.4171 | [8 empty] | 2021-05-06
HI_MA_SPLIT MS2 COOLING COIL Cooling Capacity [ton] | SPLIT MS2 COOLING COIL Cooling Capacity [ton] | 1.4359 | 1.4121 | [8 empty] | 2021-05-06
HI_MA_SPLIT TSW COOLING COIL Cooling Capacity [ton] | SPLIT TSW COOLING COIL Cooling Capacity [ton] | 1.3026 | 1.2724 | [8 empty] | 2021-05-06
HI_MA_SPLIT TNW COOLING COIL Cooling Capacity [ton] | SPLIT TNW COOLING COIL Cooling Capacity [ton] | 1.2755 | 1.246 | [8 empty] | 2021-05-06
HI_MA_SPLIT TSE COOLING COIL Cooling Capacity [ton] | SPLIT TSE COOLING COIL Cooling Capacity [ton] | 1.1174 | 1.097 | [8 empty] | 2021-05-06
HI_MA_SPLIT TNE COOLING COIL Cooling Capacity [ton] | SPLIT TNE COOLING COIL Cooling Capacity [ton] | 1.0789 | 1.0578 | [8 empty] | 2021-05-06
HI_MA_SPLIT TN1 COOLING COIL Cooling Capacity [ton] | SPLIT TN1 COOLING COIL Cooling Capacity [ton] | 0.84883 | 0.83675 | [8 empty] | 2021-05-06
HI_MA_SPLIT TN2 COOLING COIL Cooling Capacity [ton] | SPLIT TN2 COOLING COIL Cooling Capacity [ton] | 0.84258 | 0.83089 | [8 empty] | 2021-05-06
HI_MA_SPLIT TS1 COOLING COIL Cooling Capacity [ton] | SPLIT TS1 COOLING COIL Cooling Capacity [ton] | 0.89773 | 0.88442 | [8 empty] | 2021-05-06
HI_MA_SPLIT TS2 COOLING COIL Cooling Capacity [ton] | SPLIT TS2 COOLING COIL Cooling Capacity [ton] | 0.89899 | 0.88581 | [8 empty] | 2021-05-06
HI_MA_Split GN1 Furnace with DX Cooling OA Rate [cfm] | Split GN1 Furnace with DX Cooling OA Rate [cfm] | 54.9913 | 54.9913 | [8 empty] | 2021-05-06
HI_MA_Split GN2 Furnace with DX Cooling OA Rate [cfm] | Split GN2 Furnace with DX Cooling OA Rate [cfm] | 54.9913 | 54.9913 | [8 empty] | 2021-05-06
HI_MA_Split GNE Furnace with DX Cooling OA Rate [cfm] | Split GNE Furnace with DX Cooling OA Rate [cfm] | 54.9913 | 54.9913 | [8 empty] | 2021-05-06
HI_MA_Split GNW Furnace with DX Cooling OA Rate [cfm] | Split GNW Furnace with DX Cooling OA Rate [cfm] | 54.9913 | 54.9913 | [8 empty] | 2021-05-06
HI_MA_Split GS1 Furnace with DX Cooling OA Rate [cfm] | Split GS1 Furnace with DX Cooling OA Rate [cfm] | 54.9913 | 54.9913 | [8 empty] | 2021-05-06
HI_MA_Split GS2 Furnace with DX Cooling OA Rate [cfm] | Split GS2 Furnace with DX Cooling OA Rate [cfm] | 54.9913 | 54.9913 | [8 empty] | 2021-05-06
HI_MA_Split GSW Furnace with DX Cooling OA Rate [cfm] | Split GSW Furnace with DX Cooling OA Rate [cfm] | 56.9945 | 56.9945 | [8 empty] | 2021-05-06
HI_MA_Split MN1 Furnace with DX Cooling OA Rate [cfm] | Split MN1 Furnace with DX Cooling OA Rate [cfm] | 109.9824 | 109.9824 | [8 empty] | 2021-05-06
HI_MA_Split MN2 Furnace with DX Cooling OA Rate [cfm] | Split MN2 Furnace with DX Cooling OA Rate [cfm] | 109.9824 | 109.9824 | [8 empty] | 2021-05-06
HI_MA_Split MNE Furnace with DX Cooling OA Rate [cfm] | Split MNE Furnace with DX Cooling OA Rate [cfm] | 109.9824 | 109.9824 | [8 empty] | 2021-05-06
HI_MA_Split MNW Furnace with DX Cooling OA Rate [cfm] | Split MNW Furnace with DX Cooling OA Rate [cfm] | 109.9824 | 109.9824 | [8 empty] | 2021-05-06
HI_MA_Split MS1 Furnace with DX Cooling OA Rate [cfm] | Split MS1 Furnace with DX Cooling OA Rate [cfm] | 109.9824 | 109.9824 | [8 empty] | 2021-05-06
HI_MA_Split MS2 Furnace with DX Cooling OA Rate [cfm] | Split MS2 Furnace with DX Cooling OA Rate [cfm] | 109.9824 | 109.9824 | [8 empty] | 2021-05-06
HI_MA_Split MSE Furnace with DX Cooling OA Rate [cfm] | Split MSE Furnace with DX Cooling OA Rate [cfm] | 109.9824 | 109.9824 | [8 empty] | 2021-05-06
HI_MA_Split MSW Furnace with DX Cooling OA Rate [cfm] | Split MSW Furnace with DX Cooling OA Rate [cfm] | 109.9824 | 109.9824 | [8 empty] | 2021-05-06
HI_MA_Split Office Furnace with DX Cooling OA Rate [cfm] | Split Office Furnace with DX Cooling OA Rate [cfm] | 80.7372 | 80.7372 | [8 empty] | 2021-05-06
HI_MA_Split TN1 Furnace with DX Cooling OA Rate [cfm] | Split TN1 Furnace with DX Cooling OA Rate [cfm] | 54.9913 | 54.9913 | [8 empty] | 2021-05-06
HI_MA_Split TN2 Furnace with DX Cooling OA Rate [cfm] | Split TN2 Furnace with DX Cooling OA Rate [cfm] | 54.9913 | 54.9913 | [8 empty] | 2021-05-06
HI_MA_Split TNE Furnace with DX Cooling OA Rate [cfm] | Split TNE Furnace with DX Cooling OA Rate [cfm] | 54.9913 | 54.9913 | [8 empty] | 2021-05-06
HI_MA_Split TNW Furnace with DX Cooling OA Rate [cfm] | Split TNW Furnace with DX Cooling OA Rate [cfm] | 54.9913 | 54.9913 | [8 empty] | 2021-05-06
HI_MA_Split TS1 Furnace with DX Cooling OA Rate [cfm] | Split TS1 Furnace with DX Cooling OA Rate [cfm] | 54.9913 | 54.9913 | [8 empty] | 2021-05-06
HI_MA_Split TS2 Furnace with DX Cooling OA Rate [cfm] | Split TS2 Furnace with DX Cooling OA Rate [cfm] | 54.9913 | 54.9913 | [8 empty] | 2021-05-06
HI_MA_Split TSE Furnace with DX Cooling OA Rate [cfm] | Split TSE Furnace with DX Cooling OA Rate [cfm] | 54.9913 | 54.9913 | [8 empty] | 2021-05-06
HI_MA_Split TSW Furnace with DX Cooling OA Rate [cfm] | Split TSW Furnace with DX Cooling OA Rate [cfm] | 54.9913 | 54.9913 | [8 empty] | 2021-05-06
HI_MA_SPLIT GSW HEATING COIL Heating Capacity [kBtu/hr] | SPLIT GSW HEATING COIL Heating Capacity [kBtu/hr] | 2.6428 | 2.6428 | [8 empty] | 2021-05-06
HI_MA_SPLIT GNW HEATING COIL Heating Capacity [kBtu/hr] | SPLIT GNW HEATING COIL Heating Capacity [kBtu/hr] | 2.55 | 2.55 | [8 empty] | 2021-05-06
HI_MA_SPLIT OFFICE HEATING COIL Heating Capacity [kBtu/hr] | SPLIT OFFICE HEATING COIL Heating Capacity [kBtu/hr] | 3.7438 | 3.7438 | [8 empty] | 2021-05-06
HI_MA_SPLIT GNE HEATING COIL Heating Capacity [kBtu/hr] | SPLIT GNE HEATING COIL Heating Capacity [kBtu/hr] | 2.55 | 2.55 | [8 empty] | 2021-05-06
HI_MA_SPLIT GN1 HEATING COIL Heating Capacity [kBtu/hr] | SPLIT GN1 HEATING COIL Heating Capacity [kBtu/hr] | 2.55 | 2.55 | [8 empty] | 2021-05-06
HI_MA_SPLIT GN2 HEATING COIL Heating Capacity [kBtu/hr] | SPLIT GN2 HEATING COIL Heating Capacity [kBtu/hr] | 2.55 | 2.55 | [8 empty] | 2021-05-06
HI_MA_SPLIT GS1 HEATING COIL Heating Capacity [kBtu/hr] | SPLIT GS1 HEATING COIL Heating Capacity [kBtu/hr] | 2.55 | 2.55 | [8 empty] | 2021-05-06
HI_MA_SPLIT GS2 HEATING COIL Heating Capacity [kBtu/hr] | SPLIT GS2 HEATING COIL Heating Capacity [kBtu/hr] | 2.55 | 2.55 | [8 empty] | 2021-05-06
HI_MA_SPLIT MSW HEATING COIL Heating Capacity [kBtu/hr] | SPLIT MSW HEATING COIL Heating Capacity [kBtu/hr] | 5.0999 | 5.0999 | [8 empty] | 2021-05-06
HI_MA_SPLIT MNW HEATING COIL Heating Capacity [kBtu/hr] | SPLIT MNW HEATING COIL Heating Capacity [kBtu/hr] | 5.0999 | 5.0999 | [8 empty] | 2021-05-06
HI_MA_SPLIT MSE HEATING COIL Heating Capacity [kBtu/hr] | SPLIT MSE HEATING COIL Heating Capacity [kBtu/hr] | 5.0999 | 5.0999 | [8 empty] | 2021-05-06
HI_MA_SPLIT MNE HEATING COIL Heating Capacity [kBtu/hr] | SPLIT MNE HEATING COIL Heating Capacity [kBtu/hr] | 5.0999 | 5.0999 | [8 empty] | 2021-05-06
HI_MA_SPLIT MN1 HEATING COIL Heating Capacity [kBtu/hr] | SPLIT MN1 HEATING COIL Heating Capacity [kBtu/hr] | 5.0999 | 5.0999 | [8 empty] | 2021-05-06
HI_MA_SPLIT MN2 HEATING COIL Heating Capacity [kBtu/hr] | SPLIT MN2 HEATING COIL Heating Capacity [kBtu/hr] | 5.0999 | 5.0999 | [8 empty] | 2021-05-06
HI_MA_SPLIT MS1 HEATING COIL Heating Capacity [kBtu/hr] | SPLIT MS1 HEATING COIL Heating Capacity [kBtu/hr] | 5.0999 | 5.0999 | [8 empty] | 2021-05-06
HI_MA_SPLIT MS2 HEATING COIL Heating Capacity [kBtu/hr] | SPLIT MS2 HEATING COIL Heating Capacity [kBtu/hr] | 5.0999 | 5.0999 | [8 empty] | 2021-05-06
HI_MA_SPLIT TSW HEATING COIL Heating Capacity [kBtu/hr] | SPLIT TSW HEATING COIL Heating Capacity [kBtu/hr] | 2.55 | 2.55 | [8 empty] | 2021-05-06
HI_MA_SPLIT TNW HEATING COIL Heating Capacity [kBtu/hr] | SPLIT TNW HEATING COIL Heating Capacity [kBtu/hr] | 2.55 | 2.55 | [8 empty] | 2021-05-06
HI_MA_SPLIT TSE HEATING COIL Heating Capacity [kBtu/hr] | SPLIT TSE HEATING COIL Heating Capacity [kBtu/hr] | 2.55 | 2.55 | [8 empty] | 2021-05-06
HI_MA_SPLIT TNE HEATING COIL Heating Capacity [kBtu/hr] | SPLIT TNE HEATING COIL Heating Capacity [kBtu/hr] | 2.55 | 2.55 | [8 empty] | 2021-05-06
HI_MA_SPLIT TN1 HEATING COIL Heating Capacity [kBtu/hr] | SPLIT TN1 HEATING COIL Heating Capacity [kBtu/hr] | 2.55 | 2.55 | [8 empty] | 2021-05-06
HI_MA_SPLIT TN2 HEATING COIL Heating Capacity [kBtu/hr] | SPLIT TN2 HEATING COIL Heating Capacity [kBtu/hr] | 2.55 | 2.55 | [8 empty] | 2021-05-06
HI_MA_SPLIT TS1 HEATING COIL Heating Capacity [kBtu/hr] | SPLIT TS1 HEATING COIL Heating Capacity [kBtu/hr] | 2.55 | 2.55 | [8 empty] | 2021-05-06
HI_MA_SPLIT TS2 HEATING COIL Heating Capacity [kBtu/hr] | SPLIT TS2 HEATING COIL Heating Capacity [kBtu/hr] | 2.55 | 2.55 | [8 empty] | 2021-05-06
HI_MA_Split_GSW ERV Flag | Split_GSW ERV Flag | No | Yes | [8 empty] | 2021-05-06
HI_MA_Split_GNW ERV Flag | Split_GNW ERV Flag | No | Yes | [8 empty] | 2021-05-06
HI_MA_Split_GNE ERV Flag | Split_GNE ERV Flag | No | Yes | [8 empty] | 2021-05-06
HI_MA_Split_GN1 ERV Flag | Split_GN1 ERV Flag | No | Yes | [8 empty] | 2021-05-06
HI_MA_Split_GN2 ERV Flag | Split_GN2 ERV Flag | No | Yes | [8 empty] | 2021-05-06
HI_MA_Split_GS1 ERV Flag | Split_GS1 ERV Flag | No | Yes | [8 empty] | 2021-05-06
HI_MA_Split_GS2 ERV Flag | Split_GS2 ERV Flag | No | Yes | [8 empty] | 2021-05-06
HI_MA_Split_MSW ERV Flag | Split_MSW ERV Flag | No | Yes | [8 empty] | 2021-05-06
HI_MA_Split_MNW ERV Flag | Split_MNW ERV Flag | No | Yes | [8 empty] | 2021-05-06
HI_MA_Split_MSE ERV Flag | Split_MSE ERV Flag | No | Yes | [8 empty] | 2021-05-06
HI_MA_Split_MNE ERV Flag | Split_MNE ERV Flag | No | Yes | [8 empty] | 2021-05-06
HI_MA_Split_MN1 ERV Flag | Split_MN1 ERV Flag | No | Yes | [8 empty] | 2021-05-06
HI_MA_Split_MN2 ERV Flag | Split_MN2 ERV Flag | No | Yes | [8 empty] | 2021-05-06
HI_MA_Split_MS1 ERV Flag | Split_MS1 ERV Flag | No | Yes | [8 empty] | 2021-05-06
HI_MA_Split_MS2 ERV Flag | Split_MS2 ERV Flag | No | Yes | [8 empty] | 2021-05-06
HI_MA_Split_TSW ERV Flag | Split_TSW ERV Flag | No | Yes | [8 empty] | 2021-05-06
HI_MA_Split_TNW ERV Flag | Split_TNW ERV Flag | No | Yes | [8 empty] | 2021-05-06
HI_MA_Split_TSE ERV Flag | Split_TSE ERV Flag | No | Yes | [8 empty] | 2021-05-06
HI_MA_Split_TNE ERV Flag | Split_TNE ERV Flag | No | Yes | [8 empty] | 2021-05-06
HI_MA_Split_TN1 ERV Flag | Split_TN1 ERV Flag | No | Yes | [8 empty] | 2021-05-06
HI_MA_Split_TN2 ERV Flag | Split_TN2 ERV Flag | No | Yes | [8 empty] | 2021-05-06
HI_MA_Split_TS1 ERV Flag | Split_TS1 ERV Flag | No | Yes | [8 empty] | 2021-05-06
HI_MA_Split_TS2 ERV Flag | Split_TS2 ERV Flag | No | Yes | [8 empty] | 2021-05-06
id | item | Zone5A(IA-DesMoines-IA) ASHRAE901-state_STD2016 | Zone5A(IA-DesMoines-IA) ASHRAE901-state_STD2019 | Zone6A(IA-MasonCity-IA) ASHRAE901-state_STD2016 | Zone6A(IA-MasonCity-IA) ASHRAE901-state_STD2019 | [6 empty] | 2021-05-06
IA_SO_PSZ-AC:1 Cooling Capacity [ton] | PSZ-AC:1 Cooling Capacity [ton] | 1.9752 | 1.8756 | 1.8858 | 1.7878 | [6 empty] | 2021-05-06
IA_SO_PSZ-AC:2 Cooling Capacity [ton] | PSZ-AC:2 Cooling Capacity [ton] | 1.7206 | 1.655 | 1.633 | 1.5536 | [6 empty] | 2021-05-06
IA_SO_PSZ-AC:3 Cooling Capacity [ton] | PSZ-AC:3 Cooling Capacity [ton] | 1.2219 | 1.1824 | 1.1808 | 1.1129 | [6 empty] | 2021-05-06
IA_SO_PSZ-AC:4 Cooling Capacity [ton] | PSZ-AC:4 Cooling Capacity [ton] | 1.6568 | 1.5752 | 1.5512 | 1.4613 | [6 empty] | 2021-05-06
IA_SO_PSZ-AC:5 Cooling Capacity [ton] | PSZ-AC:5 Cooling Capacity [ton] | 1.4369 | 1.3959 | 1.3955 | 1.3269 | [6 empty] | 2021-05-06
IA_SO_PSZ-AC:1 Supply Flow Rate [cfm] | PSZ-AC:1 Supply Flow Rate [cfm] | 656.8528 | 614.4752 | 656.8528 | 614.4752 | [6 empty] | 2021-05-06
IA_SO_PSZ-AC:2 Supply Flow Rate [cfm] | PSZ-AC:2 Supply Flow Rate [cfm] | 593.2864 | 572.0976 | 593.2864 | 550.9088 | [6 empty] | 2021-05-06
IA_SO_PSZ-AC:3 Supply Flow Rate [cfm] | PSZ-AC:3 Supply Flow Rate [cfm] | 487.3424 | 466.1536 | 487.3424 | 466.1536 | [6 empty] | 2021-05-06
IA_SO_PSZ-AC:4 Supply Flow Rate [cfm] | PSZ-AC:4 Supply Flow Rate [cfm] | 572.0976 | 529.72 | 550.9088 | 508.5312 | [6 empty] | 2021-05-06
IA_SO_PSZ-AC:5 Supply Flow Rate [cfm] | PSZ-AC:5 Supply Flow Rate [cfm] | 572.0976 | 550.9088 | 572.0976 | 550.9088 | [6 empty] | 2021-05-06
IA_SO_PSZ-AC:1 OA Rate [cfm] | PSZ-AC:1 OA Rate [cfm] | 136.9178 | 136.9178 | 136.9178 | 136.9178 | [6 empty] | 2021-05-06
IA_SO_PSZ-AC:2 OA Rate [cfm] | PSZ-AC:2 OA Rate [cfm] | 103.7925 | 103.7925 | 103.7925 | 103.7925 | [6 empty] | 2021-05-06
IA_SO_PSZ-AC:3 OA Rate [cfm] | PSZ-AC:3 OA Rate [cfm] | 61.5711 | 61.5711 | 61.5711 | 61.5711 | [6 empty] | 2021-05-06
IA_SO_PSZ-AC:4 OA Rate [cfm] | PSZ-AC:4 OA Rate [cfm] | 103.7925 | 103.7925 | 103.7925 | 103.7925 | [6 empty] | 2021-05-06
IA_SO_PSZ-AC:5 OA Rate [cfm] | PSZ-AC:5 OA Rate [cfm] | 61.5711 | 61.5711 | 61.5711 | 61.5711 | [6 empty] | 2021-05-06
IA_SO_PSZ-AC:1 heating Capacity [kBtu/hr] | PSZ-AC:1 heating Capacity [kBtu/hr] | 15.8752 | 15.8752 | 16.8384 | 16.8045 | [6 empty] | 2021-05-06
IA_SO_PSZ-AC:2 heating Capacity [kBtu/hr] | PSZ-AC:2 heating Capacity [kBtu/hr] | 23.2246 | 22.9708 | 25.2797 | 24.9983 | [6 empty] | 2021-05-06
IA_SO_PSZ-AC:3 heating Capacity [kBtu/hr] | PSZ-AC:3 heating Capacity [kBtu/hr] | 14.168 | 14.0278 | 15.4603 | 15.3048 | [6 empty] | 2021-05-06
IA_SO_PSZ-AC:4 heating Capacity [kBtu/hr] | PSZ-AC:4 heating Capacity [kBtu/hr] | 23.1311 | 22.9135 | 25.2306 | 24.9893 | [6 empty] | 2021-05-06
IA_SO_PSZ-AC:5 heating Capacity [kBtu/hr] | PSZ-AC:5 heating Capacity [kBtu/hr] | 14.2415 | 14.0944 | 15.54 | 15.3768 | [6 empty] | 2021-05-06
id | item | Zone5A(IA-DesMoines-IA) ASHRAE901-state_STD2016 | Zone5A(IA-DesMoines-IA) ASHRAE901-state_STD2019 | Zone6A(IA-MasonCity-IA) ASHRAE901-state_STD2016 | Zone6A(IA-MasonCity-IA) ASHRAE901-state_STD2019 | [6 empty] | 2021-05-06
IA_LO_CAV_BAS Supply Flow Rate [cfm] | CAV_BAS Supply Flow Rate [cfm] | 12014.0496 | 11124.12 | 12119.9936 | 11208.8752 | [6 empty] | 2021-05-06
IA_LO_VAV_BOT WITH REHEAT Supply Flow Rate [cfm] | VAV_BOT WITH REHEAT Supply Flow Rate [cfm] | 20595.5136 | 19642.0176 | 20659.08 | 19536.0736 | [6 empty] | 2021-05-06
IA_LO_VAV_MID WITH REHEAT Supply Flow Rate [cfm] | VAV_MID WITH REHEAT Supply Flow Rate [cfm] | 192373.1155 | 183219.5539 | 192351.9267 | 181397.3171 | [6 empty] | 2021-05-06
IA_LO_VAV_TOP WITH REHEAT Supply Flow Rate [cfm] | VAV_TOP WITH REHEAT Supply Flow Rate [cfm] | 20235.304 | 19430.1296 | 20256.4928 | 19197.0528 | [6 empty] | 2021-05-06
IA_LO_Supply Air Temp. Reset Flag | Supply Air Temp. Reset Flag | Yes | Yes | Yes | Yes | [6 empty] | 2021-05-06
IA_LO_CAV_BAS OA Rate [cfm] | CAV_BAS OA Rate [cfm] | 2542.8255 | 2542.8255 | 2542.8255 | 2542.8255 | [6 empty] | 2021-05-06
IA_LO_VAV_BOT WITH REHEAT OA Rate [cfm] | VAV_BOT WITH REHEAT OA Rate [cfm] | 5377.8022 | 4302.174 | 5377.8022 | 4302.174 | [6 empty] | 2021-05-06
IA_LO_VAV_MID WITH REHEAT OA Rate [cfm] | VAV_MID WITH REHEAT OA Rate [cfm] | 53777.9373 | 43021.7396 | 53777.9373 | 43021.7396 | [6 empty] | 2021-05-06
IA_LO_VAV_TOP WITH REHEAT OA Rate [cfm] | VAV_TOP WITH REHEAT OA Rate [cfm] | 5377.8022 | 4302.174 | 5377.8022 | 4302.174 | [6 empty] | 2021-05-06
IA_LO_AIRLOOP DATACENTER BASEMENT OA Rate [cfm] | AIRLOOP DATACENTER BASEMENT OA Rate [cfm] | 716.9654 | 716.9654 | 716.9654 | 716.9654 | [6 empty] | 2021-05-06
IA_LO_VAV_bot_WITH_REHEAT ERV Flag | VAV_bot_WITH_REHEAT ERV Flag | Yes | Yes | Yes | Yes | [6 empty] | 2021-05-06
IA_LO_VAV_mid_WITH_REHEAT ERV Flag | VAV_mid_WITH_REHEAT ERV Flag | Yes | Yes | Yes | Yes | [6 empty] | 2021-05-06
IA_LO_VAV_top_WITH_REHEAT ERV Flag | VAV_top_WITH_REHEAT ERV Flag | Yes | Yes | Yes | Yes | [6 empty] | 2021-05-06
IA_LO_COOLSYS1 CHILLER1 Capacity [ton] | COOLSYS1 CHILLER1 Capacity [ton] | 447.4683 | 402.6403 | 427.5437 | 384.011 | [6 empty] | 2021-05-06
IA_LO_COOLSYS1 CHILLER2 Capacity [ton] | COOLSYS1 CHILLER2 Capacity [ton] | 447.4683 | 402.6403 | 427.5437 | 384.011 | [6 empty] | 2021-05-06
IA_LO_TOWERWATERSYS COOLTOWER 1 Capacity [ton] | TOWERWATERSYS COOLTOWER 1 Capacity [ton] | 424.7245 | 382.1799 | 405.8216 | 364.4978 | [6 empty] | 2021-05-06
IA_LO_TOWERWATERSYS COOLTOWER 2 Capacity [ton] | TOWERWATERSYS COOLTOWER 2 Capacity [ton] | 424.7245 | 382.1799 | 405.8216 | 364.4978 | [6 empty] | 2021-05-06
IA_LO_HEATSYS1 BOILER Capacity [MMBTU/h] | HEATSYS1 BOILER Capacity [MMBTU/h] | 5140.2162 | 4545.8992 | 5442.6781 | 4808.5852 | [6 empty] | 2021-05-06
IA_LO_COOLSYS1 PUMP Flow Rate [gal/min] | COOLSYS1 PUMP Flow Rate [gal/min] | 0 | 0 | 0 | 0 | [6 empty] | 2021-05-06
IA_LO_COOLSYS1 CHILLER1 PUMP Flow Rate [gal/min] | COOLSYS1 CHILLER1 PUMP Flow Rate [gal/min] | 705.1888 | 634.4504 | 673.6435 | 604.9783 | [6 empty] | 2021-05-06
IA_LO_COOLSYS1 CHILLER2 PUMP Flow Rate [gal/min] | COOLSYS1 CHILLER2 PUMP Flow Rate [gal/min] | 705.1888 | 634.4504 | 673.6435 | 604.9783 | [6 empty] | 2021-05-06
IA_LO_COOLSYS1 PUMP SECONDARY Flow Rate [gal/min] | COOLSYS1 PUMP SECONDARY Flow Rate [gal/min] | 1410.376 | 1268.9024 | 1347.287 | 1209.9582 | [6 empty] | 2021-05-06
IA_LO_HEATSYS1 PUMP Flow Rate [gal/min] | HEATSYS1 PUMP Flow Rate [gal/min] | 1055.0974 | 933.1054 | 1117.1815 | 987.025 | [6 empty] | 2021-05-06
IA_LO_TOWERWATERSYS PUMP Flow Rate [gal/min] | TOWERWATERSYS PUMP Flow Rate [gal/min] | 2468.6878 | 2221.4228 | 2358.8451 | 2118.5542 | [6 empty] | 2021-05-06
IA_LO_PLANT CIRC PUMP Flow Rate [gal/min] | PLANT CIRC PUMP Flow Rate [gal/min] | 212.7415 | 211.8903 | 213.2201 | 212.0155 | [6 empty] | 2021-05-06
IA_LO_COOLSYS1 PUMP SECONDARY Pressure setpoint reset [yes,no] | COOLSYS1 PUMP SECONDARY Pressure setpoint reset [yes,no] | pump_ride_on_curve | pump_ride_on_curve | pump_ride_on_curve | pump_ride_on_curve | [6 empty] | 2021-05-06
IA_LO_COOLSYS1 CHILLER1 PUMP Pump Power [hp] | COOLSYS1 CHILLER1 PUMP Pump Power [hp] | 3.8042 | 3.3887 | 3.6341 | 3.2313 | [6 empty] | 2021-05-06
IA_LO_COOLSYS1 CHILLER2 PUMP Pump Power [hp] | COOLSYS1 CHILLER2 PUMP Pump Power [hp] | 3.8042 | 3.3887 | 3.6341 | 3.2313 | [6 empty] | 2021-05-06
IA_LO_COOLSYS1 PUMP SECONDARY Pump Power [hp] | COOLSYS1 PUMP SECONDARY Pump Power [hp] | 22.8255 | 20.3325 | 21.8044 | 19.388 | [6 empty] | 2021-05-06
IA_LO_HEATSYS1 PUMP Pump Power [hp] | HEATSYS1 PUMP Pump Power [hp] | 22.8065 | 19.9699 | 24.1485 | 21.1239 | [6 empty] | 2021-05-06
IA_LO_TOWERWATERSYS PUMP Pump Power [hp] | TOWERWATERSYS PUMP Pump Power [hp] | 44.2 | 39.3782 | 42.2319 | 37.5562 | [6 empty] | 2021-05-06
IA_LO_PLANT CIRC PUMP Pump Power [hp] | PLANT CIRC PUMP Pump Power [hp] | 4.5907 | 4.527 | 4.601 | 4.5297 | [6 empty] | 2021-05-06
IA_LO_Datacenter PLANT CIRC PUMP Pump Power [hp] | Datacenter PLANT CIRC PUMP Pump Power [hp] | 4.5907 | 4.527 | 4.601 | 4.5297 | [6 empty] | 2021-05-06
IA_LO_ZN_VAV_BOXes_Max_Reheat_Water_Flow_GPM | ZN_VAV_BOXes_Max_Reheat_Water_Flow_GPM | 527.9731 | 508.1615 | 544.9414 | 524.4579 | [6 empty] | 2021-05-06
IA_LO_COOLSYS1 PUMP SECONDARY VSD | COOLSYS1 PUMP SECONDARY VSD | No | No | No | No | [6 empty] | 2021-05-06
IA_LO_HEATSYS1 PUMP VSD | HEATSYS1 PUMP VSD | No | No | No | No | [6 empty] | 2021-05-06
IA_LO_DATACENTER BASEMENT Cooling Capacity [ton] | DATACENTER BASEMENT Cooling Capacity [ton] | 123.6983 | 123.3338 | 123.8215 | 123.4457 | [6 empty] | 2021-05-06
IA_LO_DATACENTER BOT Cooling Capacity [ton] | DATACENTER BOT Cooling Capacity [ton] | 2.7765 | 2.7523 | 2.7943 | 2.7512 | [6 empty] | 2021-05-06
IA_LO_DATACENTER MID Cooling Capacity [ton] | DATACENTER MID Cooling Capacity [ton] | 26.6486 | 26.4342 | 26.8406 | 26.4187 | [6 empty] | 2021-05-06
IA_LO_DATACENTER TOP Cooling Capacity [ton] | DATACENTER TOP Cooling Capacity [ton] | 2.7146 | 2.694 | 2.732 | 2.6903 | [6 empty] | 2021-05-06
id | item | Zone5A(IA-DesMoines-IA) ASHRAE901-state_STD2016 | Zone5A(IA-DesMoines-IA) ASHRAE901-state_STD2019 | Zone6A(IA-MasonCity-IA) ASHRAE901-state_STD2016 | Zone6A(IA-MasonCity-IA) ASHRAE901-state_STD2019 | [6 empty] | 2021-05-06
IA_RS_PSZ-AC:1 Cooling Capacity [ton] | PSZ-AC:1 Cooling Capacity [ton] | 10.9192 | 10.5678 | 10.307 | 9.8525 | [6 empty] | 2021-05-06
IA_RS_PSZ-AC:2 Cooling Capacity [ton] | PSZ-AC:2 Cooling Capacity [ton] | 53.094 | 50.0671 | 50.6841 | 48.8458 | [6 empty] | 2021-05-06
IA_RS_PSZ-AC:3 Cooling Capacity [ton] | PSZ-AC:3 Cooling Capacity [ton] | 6.8908 | 6.7235 | 6.4638 | 6.294 | [6 empty] | 2021-05-06
IA_RS_PSZ-AC:4 Cooling Capacity [ton] | PSZ-AC:4 Cooling Capacity [ton] | 5.6359 | 5.4679 | 5.221 | 5.0278 | [6 empty] | 2021-05-06
IA_RS_PSZ-AC:1 Supply Flow Rate [cfm] | PSZ-AC:1 Supply Flow Rate [cfm] | 4131.816 | 3856.3616 | 3962.3056 | 3644.4736 | [6 empty] | 2021-05-06
IA_RS_PSZ-AC:2 Supply Flow Rate [cfm] | PSZ-AC:2 Supply Flow Rate [cfm] | 15976.3552 | 15022.8592 | 15679.712 | 14853.3488 | [6 empty] | 2021-05-06
IA_RS_PSZ-AC:3 Supply Flow Rate [cfm] | PSZ-AC:3 Supply Flow Rate [cfm] | 2373.1456 | 2309.5792 | 2309.5792 | 2224.824 | [6 empty] | 2021-05-06
IA_RS_PSZ-AC:4 Supply Flow Rate [cfm] | PSZ-AC:4 Supply Flow Rate [cfm] | 1822.2368 | 1737.4816 | 1737.4816 | 1652.7264 | [6 empty] | 2021-05-06
IA_RS_PSZ-AC:1 OA Rate [cfm] | PSZ-AC:1 OA Rate [cfm] | 490.669 | 490.669 | 490.669 | 490.669 | [6 empty] | 2021-05-06
IA_RS_PSZ-AC:2 OA Rate [cfm] | PSZ-AC:2 OA Rate [cfm] | 4005.1282 | 4005.1282 | 4005.1282 | 4005.1282 | [6 empty] | 2021-05-06
IA_RS_PSZ-AC:3 OA Rate [cfm] | PSZ-AC:3 OA Rate [cfm] | 377.3937 | 377.3937 | 377.3937 | 377.3937 | [6 empty] | 2021-05-06
IA_RS_PSZ-AC:4 OA Rate [cfm] | PSZ-AC:4 OA Rate [cfm] | 377.3937 | 377.3937 | 377.3937 | 377.3937 | [6 empty] | 2021-05-06
IA_RS_PSZ-AC:1 OA Damper [gravity, motorized] | PSZ-AC:1 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2021-05-06
IA_RS_PSZ-AC:2 OA Damper [gravity, motorized] | PSZ-AC:2 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2021-05-06
IA_RS_PSZ-AC:3 OA Damper [gravity, motorized] | PSZ-AC:3 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2021-05-06
IA_RS_PSZ-AC:4 OA Damper [gravity, motorized] | PSZ-AC:4 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2021-05-06
IA_RS_PSZ-AC:1 Heating Capacity [kBtu/hr] | PSZ-AC:1 Heating Capacity [kBtu/hr] | 186.6114 | 175.9631 | 181.6454 | 169.4949 | [6 empty] | 2021-05-06
IA_RS_PSZ-AC:2 Heating Capacity [kBtu/hr] | PSZ-AC:2 Heating Capacity [kBtu/hr] | 879.3988 | 841.0497 | 887.4634 | 856.1073 | [6 empty] | 2021-05-06
IA_RS_PSZ-AC:3 Heating Capacity [kBtu/hr] | PSZ-AC:3 Heating Capacity [kBtu/hr] | 115.5249 | 112.7728 | 114.605 | 111.6595 | [6 empty] | 2021-05-06
IA_RS_PSZ-AC:4 Heating Capacity [kBtu/hr] | PSZ-AC:4 Heating Capacity [kBtu/hr] | 95.3562 | 92.4362 | 94.1027 | 90.5569 | [6 empty] | 2021-05-06
id | item | Zone5A(IA-DesMoines-IA) ASHRAE901-state_STD2016 | Zone5A(IA-DesMoines-IA) ASHRAE901-state_STD2019 | Zone6A(IA-MasonCity-IA) ASHRAE901-state_STD2016 | Zone6A(IA-MasonCity-IA) ASHRAE901-state_STD2019 | [6 empty] | 2021-05-06
IA_PS_VAV_POD_1 Cooling Capacity [ton] | VAV_POD_1 Cooling Capacity [ton] | 19.6719 | 18.992 | 19.5757 | 18.6413 | [6 empty] | 2021-05-06
IA_PS_VAV_POD_2 Cooling Capacity [ton] | VAV_POD_2 Cooling Capacity [ton] | 19.5528 | 18.7412 | 19.4338 | 18.562 | [6 empty] | 2021-05-06
IA_PS_VAV_POD_3 Cooling Capacity [ton] | VAV_POD_3 Cooling Capacity [ton] | 18.0278 | 17.166 | 17.9286 | 16.8362 | [6 empty] | 2021-05-06
IA_PS_VAV_OTHER Cooling Capacity [ton] | VAV_OTHER Cooling Capacity [ton] | 27.7479 | 26.1665 | 27.5884 | 25.6498 | [6 empty] | 2021-05-06
IA_PS_PSZ-AC_1:6 Cooling Capacity [ton] | PSZ-AC_1:6 Cooling Capacity [ton] | 8.7871 | 8.4079 | 8.5411 | 8.2539 | [6 empty] | 2021-05-06
IA_PS_PSZ-AC_2:5 Cooling Capacity [ton] | PSZ-AC_2:5 Cooling Capacity [ton] | 5.7423 | 5.7173 | 5.6818 | 5.5981 | [6 empty] | 2021-05-06
IA_PS_PSZ-AC_2:7 Cooling Capacity [ton] | PSZ-AC_2:7 Cooling Capacity [ton] | 10.5074 | 10.5074 | 10.5074 | 10.5074 | [6 empty] | 2021-05-06
IA_PS_VAV_POD_1 Supply Flow Rate [cfm] | VAV_POD_1 Supply Flow Rate [cfm] | 5911.6752 | 5699.7872 | 5869.2976 | 5593.8432 | [6 empty] | 2021-05-06
IA_PS_VAV_POD_2 Supply Flow Rate [cfm] | VAV_POD_2 Supply Flow Rate [cfm] | 5869.2976 | 5615.032 | 5826.92 | 5572.6544 | [6 empty] | 2021-05-06
IA_PS_VAV_POD_3 Supply Flow Rate [cfm] | VAV_POD_3 Supply Flow Rate [cfm] | 5403.144 | 5148.8784 | 5381.9552 | 5042.9344 | [6 empty] | 2021-05-06
IA_PS_VAV_OTHER Supply Flow Rate [cfm] | VAV_OTHER Supply Flow Rate [cfm] | 8327.1984 | 7861.0448 | 8284.8208 | 7691.5344 | [6 empty] | 2021-05-06
IA_PS_PSZ-AC_2:5 Supply Flow Rate [cfm] | PSZ-AC_2:5 Supply Flow Rate [cfm] | 1716.2928 | 1716.2928 | 1695.104 | 1673.9152 | [6 empty] | 2021-05-06
IA_PS_PSZ-AC_1:6 Supply Flow Rate [cfm] | PSZ-AC_1:6 Supply Flow Rate [cfm] | 2627.4112 | 2521.4672 | 2648.6 | 2521.4672 | [6 empty] | 2021-05-06
IA_PS_PSZ-AC_2:7 Supply Flow Rate [cfm] | PSZ-AC_2:7 Supply Flow Rate [cfm] | 3157.1312 | 3157.1312 | 3157.1312 | 3157.1312 | [6 empty] | 2021-05-06
IA_PS_Supply Air Temp. Reset Flag | Supply Air Temp. Reset Flag | Yes | Yes | Yes | Yes | [6 empty] | 2021-05-06
IA_PS_VAV_POD_1 OA Rate [cfm] | VAV_POD_1 OA Rate [cfm] | 5900.8689 | 5699.1939 | 5873.8956 | 5593.9492 | [6 empty] | 2021-05-06
IA_PS_VAV_POD_2 OA Rate [cfm] | VAV_POD_2 OA Rate [cfm] | 5867.4754 | 5623.9313 | 5830.9035 | 5570.1541 | [6 empty] | 2021-05-06
IA_PS_VAV_POD_3 OA Rate [cfm] | VAV_POD_3 OA Rate [cfm] | 5409.3735 | 5151.2304 | 5380.0694 | 5052.2575 | [6 empty] | 2021-05-06
IA_PS_VAV_OTHER OA Rate [cfm] | VAV_OTHER OA Rate [cfm] | 3736.1787 | 2988.8921 | 3736.1787 | 2988.8921 | [6 empty] | 2021-05-06
IA_PS_PSZ-AC_2:5 OA Rate [cfm] | PSZ-AC_2:5 OA Rate [cfm] | 1152.7343 | 1152.7343 | 1152.7343 | 1152.7343 | [6 empty] | 2021-05-06
IA_PS_PSZ-AC_1:6 OA Rate [cfm] | PSZ-AC_1:6 OA Rate [cfm] | 539.9118 | 539.9118 | 539.9118 | 539.9118 | [6 empty] | 2021-05-06
IA_PS_PSZ-AC_2:7 OA Rate [cfm] | PSZ-AC_2:7 OA Rate [cfm] | 3153.0841 | 3153.0841 | 3153.0841 | 3153.0841 | [6 empty] | 2021-05-06
IA_PS_VAV_POD_1 OA Damper [gravity, motorized] | VAV_POD_1 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2021-05-06
IA_PS_VAV_POD_2 OA Damper [gravity, motorized] | VAV_POD_2 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2021-05-06
IA_PS_VAV_POD_3 OA Damper [gravity, motorized] | VAV_POD_3 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2021-05-06
IA_PS_VAV_OTHER OA Damper [gravity, motorized] | VAV_OTHER OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2021-05-06
IA_PS_PSZ-AC_2:5 OA Damper [gravity, motorized] | PSZ-AC_2:5 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2021-05-06
IA_PS_PSZ-AC_1:6 OA Damper [gravity, motorized] | PSZ-AC_1:6 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2021-05-06
IA_PS_PSZ-AC_2:7 OA Damper [gravity, motorized] | PSZ-AC_2:7 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2021-05-06
IA_PS_VAV_POD_1 (economizer) | VAV_POD_1 (economizer) | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | [6 empty] | 2021-05-06
IA_PS_VAV_POD_2 (economizer) | VAV_POD_2 (economizer) | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | [6 empty] | 2021-05-06
IA_PS_VAV_POD_3 (economizer) | VAV_POD_3 (economizer) | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | [6 empty] | 2021-05-06
IA_PS_VAV_OTHER (economizer) | VAV_OTHER (economizer) | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | [6 empty] | 2021-05-06
IA_PS_PSZ-AC_2:5 (economizer) | PSZ-AC_2:5 (economizer) | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | [6 empty] | 2021-05-06
IA_PS_PSZ-AC_1:6 (economizer) | PSZ-AC_1:6 (economizer) | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | [6 empty] | 2021-05-06
IA_PS_PSZ-AC_2:7 (economizer) | PSZ-AC_2:7 (economizer) | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | [6 empty] | 2021-05-06
IA_PS_VAV_Pod_1_ERV Flag | VAV_Pod_1_ERV Flag | Yes | Yes | Yes | Yes | [6 empty] | 2021-05-06
IA_PS_VAV_Pod_2_ERV Flag | VAV_Pod_2_ERV Flag | Yes | Yes | Yes | Yes | [6 empty] | 2021-05-06
IA_PS_VAV_Pod_3_ERV Flag | VAV_Pod_3_ERV Flag | Yes | Yes | Yes | Yes | [6 empty] | 2021-05-06
IA_PS_VAV_OTHER_ERV Flag | VAV_OTHER_ERV Flag | Yes | Yes | Yes | Yes | [6 empty] | 2021-05-06
IA_PS_PSZ_AC_2_5_ERV Flag | PSZ_AC_2_5_ERV Flag | No | No | No | No | [6 empty] | 2021-05-06
IA_PS_PSZ_AC_2_7_ERV Flag | PSZ_AC_2_7_ERV Flag | Yes | Yes | Yes | Yes | [6 empty] | 2021-05-06
IA_PS_HEATSYS1 Capacity [MMBTU/h] | HEATSYS1 Capacity [MMBTU/h] | 1.2815 | 1.2304 | 1.3647 | 1.3049 | [6 empty] | 2021-05-06
IA_PS_HEATSYS1 Flow Rate [gal/min] | HEATSYS1 Flow Rate [gal/min] | 131.5206 | 126.2817 | 140.066 | 133.9281 | [6 empty] | 2021-05-06
IA_PS_VAV_POD_1 Fan Power [hp] | VAV_POD_1 Fan Power [hp] | 8.709 | 8.408 | 8.6664 | 8.2527 | [6 empty] | 2021-05-06
IA_PS_VAV_POD_2 Fan Power [hp] | VAV_POD_2 Fan Power [hp] | 8.6563 | 8.297 | 8.6036 | 8.2176 | [6 empty] | 2021-05-06
IA_PS_VAV_POD_3 Fan Power [hp] | VAV_POD_3 Fan Power [hp] | 7.9811 | 7.5996 | 7.9372 | 7.4536 | [6 empty] | 2021-05-06
IA_PS_VAV_OTHER Fan Power [hp] | VAV_OTHER Fan Power [hp] | 12.1913 | 11.4965 | 12.1212 | 11.2695 | [6 empty] | 2021-05-06
IA_PS_HEATSYS1 Pump Power [hp] | HEATSYS1 Pump Power [hp] | 2.8429 | 2.7026 | 3.0276 | 2.8663 | [6 empty] | 2021-05-06
IA_PS_PSZ-AC_1:6 Heating Capacity [kBtu/hr] | PSZ-AC_1:6 Heating Capacity [kBtu/hr] | 220.4807 | 211.9132 | 223.1193 | 213.86 | [6 empty] | 2021-05-06
IA_PS_PSZ-AC_2:5 Heating Capacity [kBtu/hr] | PSZ-AC_2:5 Heating Capacity [kBtu/hr] | 154.0576 | 153.7895 | 160.2694 | 159.3784 | [6 empty] | 2021-05-06
IA_PS_PSZ-AC_2:7 Heating Capacity [kBtu/hr] | PSZ-AC_2:7 Heating Capacity [kBtu/hr] | 365.5911 | 365.5911 | 384.8201 | 384.8201 | [6 empty] | 2021-05-06
IA_PS_ZN_VAV_BOXes_Max_Reheat_Water_Flow_GPM | ZN_VAV_BOXes_Max_Reheat_Water_Flow_GPM | 80.6692 | 77.7844 | 84.393 | 81.4411 | [6 empty] | 2021-05-06
id | item | Zone5A(IA-DesMoines-IA) ASHRAE901-state_STD2016 | Zone5A(IA-DesMoines-IA) ASHRAE901-state_STD2019 | Zone6A(IA-MasonCity-IA) ASHRAE901-state_STD2016 | Zone6A(IA-MasonCity-IA) ASHRAE901-state_STD2019 | [6 empty] | 2021-05-06
IA_SH_SAC_FRONTOFFICE Cooling Capacity [ton] | SAC_FRONTOFFICE Cooling Capacity [ton] | 2.4775 | 2.3646 | 2.4036 | 2.2586 | [6 empty] | 2021-05-06
IA_SH_SAC_FRONTLOUNGE Cooling Capacity [ton] | SAC_FRONTLOUNGE Cooling Capacity [ton] | 6.2813 | 5.9665 | 6.2538 | 5.9252 | [6 empty] | 2021-05-06
IA_SH_SAC_MEETINGROOM Cooling Capacity [ton] | SAC_MEETINGROOM Cooling Capacity [ton] | 2.9891 | 2.8967 | 2.9792 | 2.8827 | [6 empty] | 2021-05-06
IA_SH_SAC_EXC_EMPLGE_RESTRM Cooling Capacity [ton] | SAC_EXC_EMPLGE_RESTRM Cooling Capacity [ton] | 6.2283 | 6.1858 | 6.0411 | 5.9936 | [6 empty] | 2021-05-06
IA_SH_SAC_FO_ADDAQ SUPPLY FAN Supply Flow Rate [cfm] | SAC_FO_ADDAQ SUPPLY FAN Supply Flow Rate [cfm] | 805.1744 | 762.7968 | 805.1744 | 741.608 | [6 empty] | 2021-05-06
IA_SH_SAC_FL_ADDAQ SUPPLY FAN Supply Flow Rate [cfm] | SAC_FL_ADDAQ SUPPLY FAN Supply Flow Rate [cfm] | 1885.8032 | 1801.048 | 1885.8032 | 1779.8592 | [6 empty] | 2021-05-06
IA_SH_SAC_MR_ADDAQ SUPPLY FAN Supply Flow Rate [cfm] | SAC_MR_ADDAQ SUPPLY FAN Supply Flow Rate [cfm] | 889.9296 | 868.7408 | 889.9296 | 868.7408 | [6 empty] | 2021-05-06
IA_SH_SAC_EXC_ADDAQ SUPPLY FAN Supply Flow Rate [cfm] | SAC_EXC_ADDAQ SUPPLY FAN Supply Flow Rate [cfm] | 2246.0128 | 2224.824 | 2246.0128 | 2224.824 | [6 empty] | 2021-05-06
IA_SH_SAC_Exc_EmpLge_RestRm OA Rate [cfm] | SAC_Exc_EmpLge_RestRm OA Rate [cfm] | 199.9928 | 199.9928 | 199.9928 | 199.9928 | [6 empty] | 2021-05-06
IA_SH_SAC_FrontLounge OA Rate [cfm] | SAC_FrontLounge OA Rate [cfm] | 500.0133 | 500.0133 | 500.0133 | 500.0133 | [6 empty] | 2021-05-06
IA_SH_SAC_FrontOffice OA Rate [cfm] | SAC_FrontOffice OA Rate [cfm] | 119.2938 | 119.2938 | 119.2938 | 119.2938 | [6 empty] | 2021-05-06
IA_SH_SAC_MeetingRoom OA Rate [cfm] | SAC_MeetingRoom OA Rate [cfm] | 267.7629 | 267.7629 | 267.7629 | 267.7629 | [6 empty] | 2021-05-06
IA_SH_SAC_FrontLounge OA Damper [gravity, motorized] | SAC_FrontLounge OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2021-05-06
IA_SH_SAC_FrontOffice (economizer) | SAC_FrontOffice (economizer) | No | No | No | No | [6 empty] | 2021-05-06
IA_SH_SAC_FrontLounge (economizer) | SAC_FrontLounge (economizer) | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | [6 empty] | 2021-05-06
IA_SH_SAC_MeetingRoom (economizer) | SAC_MeetingRoom (economizer) | No | No | No | No | [6 empty] | 2021-05-06
IA_SH_SAC_Exc_EmpLge_RestRm (economizer) | SAC_Exc_EmpLge_RestRm (economizer) | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | [6 empty] | 2021-05-06
IA_SH_SAC_FRONTOFFICE Heating Capacity [kBtu/hr] | SAC_FRONTOFFICE Heating Capacity [kBtu/hr] | 38.4122 | 36.3961 | 38.4543 | 36.4302 | [6 empty] | 2021-05-06
IA_SH_SAC_FRONTLOUNGE Heating Capacity [kBtu/hr] | SAC_FRONTLOUNGE Heating Capacity [kBtu/hr] | 107.214 | 103.8557 | 109.5504 | 106.0746 | [6 empty] | 2021-05-06
IA_SH_SAC_MEETINGROOM Heating Capacity [kBtu/hr] | SAC_MEETINGROOM Heating Capacity [kBtu/hr] | 53.4173 | 52.4307 | 54.753 | 53.7325 | [6 empty] | 2021-05-06
IA_SH_SAC_EXC_EMPLGE_RESTRM Heating Capacity [kBtu/hr] | SAC_EXC_EMPLGE_RESTRM Heating Capacity [kBtu/hr] | 96.0213 | 95.354 | 96.6997 | 95.9449 | [6 empty] | 2021-05-06
id | item | Zone5A(IA-DesMoines-IA) ASHRAE901-state_STD2016 | Zone5A(IA-DesMoines-IA) ASHRAE901-state_STD2019 | Zone6A(IA-MasonCity-IA) ASHRAE901-state_STD2016 | Zone6A(IA-MasonCity-IA) ASHRAE901-state_STD2019 | [6 empty] | 2021-05-06
IA_MA_SPLIT GSW COOLING COIL Cooling Capacity [ton] | SPLIT GSW COOLING COIL Cooling Capacity [ton] | 0.9653 | 0.95074 | 0.91889 | 0.8886 | [6 empty] | 2021-05-06
IA_MA_SPLIT GNW COOLING COIL Cooling Capacity [ton] | SPLIT GNW COOLING COIL Cooling Capacity [ton] | 0.92325 | 0.90926 | 0.87242 | 0.84448 | [6 empty] | 2021-05-06
IA_MA_SPLIT OFFICE COOLING COIL Cooling Capacity [ton] | SPLIT OFFICE COOLING COIL Cooling Capacity [ton] | 1.7919 | 1.6643 | 1.8314 | 1.685 | [6 empty] | 2021-05-06
IA_MA_SPLIT GNE COOLING COIL Cooling Capacity [ton] | SPLIT GNE COOLING COIL Cooling Capacity [ton] | 0.80107 | 0.78869 | 0.75118 | 0.72819 | [6 empty] | 2021-05-06
IA_MA_SPLIT GN1 COOLING COIL Cooling Capacity [ton] | SPLIT GN1 COOLING COIL Cooling Capacity [ton] | 0.67165 | 0.66189 | 0.63629 | 0.60675 | [6 empty] | 2021-05-06
IA_MA_SPLIT GN2 COOLING COIL Cooling Capacity [ton] | SPLIT GN2 COOLING COIL Cooling Capacity [ton] | 0.66908 | 0.65938 | 0.63402 | 0.60432 | [6 empty] | 2021-05-06
IA_MA_SPLIT GS1 COOLING COIL Cooling Capacity [ton] | SPLIT GS1 COOLING COIL Cooling Capacity [ton] | 0.72033 | 0.70971 | 0.67885 | 0.66106 | [6 empty] | 2021-05-06
IA_MA_SPLIT GS2 COOLING COIL Cooling Capacity [ton] | SPLIT GS2 COOLING COIL Cooling Capacity [ton] | 0.75225 | 0.73774 | 0.71103 | 0.68898 | [6 empty] | 2021-05-06
IA_MA_SPLIT MSW COOLING COIL Cooling Capacity [ton] | SPLIT MSW COOLING COIL Cooling Capacity [ton] | 2.3066 | 2.2738 | 2.2322 | 2.1589 | [6 empty] | 2021-05-06
IA_MA_SPLIT MNW COOLING COIL Cooling Capacity [ton] | SPLIT MNW COOLING COIL Cooling Capacity [ton] | 2.2376 | 2.2059 | 2.1529 | 2.0839 | [6 empty] | 2021-05-06
IA_MA_SPLIT MSE COOLING COIL Cooling Capacity [ton] | SPLIT MSE COOLING COIL Cooling Capacity [ton] | 1.9865 | 1.9578 | 1.9386 | 1.8754 | [6 empty] | 2021-05-06
IA_MA_SPLIT MNE COOLING COIL Cooling Capacity [ton] | SPLIT MNE COOLING COIL Cooling Capacity [ton] | 1.8498 | 1.8192 | 1.7601 | 1.6926 | [6 empty] | 2021-05-06
IA_MA_SPLIT MN1 COOLING COIL Cooling Capacity [ton] | SPLIT MN1 COOLING COIL Cooling Capacity [ton] | 1.4875 | 1.4687 | 1.3972 | 1.368 | [6 empty] | 2021-05-06
IA_MA_SPLIT MN2 COOLING COIL Cooling Capacity [ton] | SPLIT MN2 COOLING COIL Cooling Capacity [ton] | 1.4804 | 1.4618 | 1.3899 | 1.3611 | [6 empty] | 2021-05-06
IA_MA_SPLIT MS1 COOLING COIL Cooling Capacity [ton] | SPLIT MS1 COOLING COIL Cooling Capacity [ton] | 1.5753 | 1.5553 | 1.4999 | 1.466 | [6 empty] | 2021-05-06
IA_MA_SPLIT MS2 COOLING COIL Cooling Capacity [ton] | SPLIT MS2 COOLING COIL Cooling Capacity [ton] | 1.569 | 1.5492 | 1.4935 | 1.4601 | [6 empty] | 2021-05-06
IA_MA_SPLIT TSW COOLING COIL Cooling Capacity [ton] | SPLIT TSW COOLING COIL Cooling Capacity [ton] | 1.4251 | 1.4073 | 1.3788 | 1.3378 | [6 empty] | 2021-05-06
IA_MA_SPLIT TNW COOLING COIL Cooling Capacity [ton] | SPLIT TNW COOLING COIL Cooling Capacity [ton] | 1.3826 | 1.3654 | 1.331 | 1.292 | [6 empty] | 2021-05-06
IA_MA_SPLIT TSE COOLING COIL Cooling Capacity [ton] | SPLIT TSE COOLING COIL Cooling Capacity [ton] | 1.2683 | 1.2535 | 1.2332 | 1.2006 | [6 empty] | 2021-05-06
IA_MA_SPLIT TNE COOLING COIL Cooling Capacity [ton] | SPLIT TNE COOLING COIL Cooling Capacity [ton] | 1.1882 | 1.1753 | 1.1366 | 1.1107 | [6 empty] | 2021-05-06
IA_MA_SPLIT TN1 COOLING COIL Cooling Capacity [ton] | SPLIT TN1 COOLING COIL Cooling Capacity [ton] | 0.94585 | 0.93623 | 0.89044 | 0.87473 | [6 empty] | 2021-05-06
IA_MA_SPLIT TN2 COOLING COIL Cooling Capacity [ton] | SPLIT TN2 COOLING COIL Cooling Capacity [ton] | 0.93843 | 0.92898 | 0.88274 | 0.86757 | [6 empty] | 2021-05-06
IA_MA_SPLIT TS1 COOLING COIL Cooling Capacity [ton] | SPLIT TS1 COOLING COIL Cooling Capacity [ton] | 1.0422 | 1.0309 | 1.0039 | 0.98091 | [6 empty] | 2021-05-06
IA_MA_SPLIT TS2 COOLING COIL Cooling Capacity [ton] | SPLIT TS2 COOLING COIL Cooling Capacity [ton] | 1.0448 | 1.0334 | 1.0075 | 0.98403 | [6 empty] | 2021-05-06
IA_MA_Split GN1 Furnace with DX Cooling OA Rate [cfm] | Split GN1 Furnace with DX Cooling OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | [6 empty] | 2021-05-06
IA_MA_Split GN2 Furnace with DX Cooling OA Rate [cfm] | Split GN2 Furnace with DX Cooling OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | [6 empty] | 2021-05-06
IA_MA_Split GNE Furnace with DX Cooling OA Rate [cfm] | Split GNE Furnace with DX Cooling OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | [6 empty] | 2021-05-06
IA_MA_Split GNW Furnace with DX Cooling OA Rate [cfm] | Split GNW Furnace with DX Cooling OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | [6 empty] | 2021-05-06
IA_MA_Split GS1 Furnace with DX Cooling OA Rate [cfm] | Split GS1 Furnace with DX Cooling OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | [6 empty] | 2021-05-06
IA_MA_Split GS2 Furnace with DX Cooling OA Rate [cfm] | Split GS2 Furnace with DX Cooling OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | [6 empty] | 2021-05-06
IA_MA_Split GSW Furnace with DX Cooling OA Rate [cfm] | Split GSW Furnace with DX Cooling OA Rate [cfm] | 56.9945 | 56.9945 | 56.9945 | 56.9945 | [6 empty] | 2021-05-06
IA_MA_Split MN1 Furnace with DX Cooling OA Rate [cfm] | Split MN1 Furnace with DX Cooling OA Rate [cfm] | 109.9824 | 109.9824 | 109.9824 | 109.9824 | [6 empty] | 2021-05-06
IA_MA_Split MN2 Furnace with DX Cooling OA Rate [cfm] | Split MN2 Furnace with DX Cooling OA Rate [cfm] | 109.9824 | 109.9824 | 109.9824 | 109.9824 | [6 empty] | 2021-05-06
IA_MA_Split MNE Furnace with DX Cooling OA Rate [cfm] | Split MNE Furnace with DX Cooling OA Rate [cfm] | 109.9824 | 109.9824 | 109.9824 | 109.9824 | [6 empty] | 2021-05-06
IA_MA_Split MNW Furnace with DX Cooling OA Rate [cfm] | Split MNW Furnace with DX Cooling OA Rate [cfm] | 109.9824 | 109.9824 | 109.9824 | 109.9824 | [6 empty] | 2021-05-06
IA_MA_Split MS1 Furnace with DX Cooling OA Rate [cfm] | Split MS1 Furnace with DX Cooling OA Rate [cfm] | 109.9824 | 109.9824 | 109.9824 | 109.9824 | [6 empty] | 2021-05-06
IA_MA_Split MS2 Furnace with DX Cooling OA Rate [cfm] | Split MS2 Furnace with DX Cooling OA Rate [cfm] | 109.9824 | 109.9824 | 109.9824 | 109.9824 | [6 empty] | 2021-05-06
IA_MA_Split MSE Furnace with DX Cooling OA Rate [cfm] | Split MSE Furnace with DX Cooling OA Rate [cfm] | 109.9824 | 109.9824 | 109.9824 | 109.9824 | [6 empty] | 2021-05-06
IA_MA_Split MSW Furnace with DX Cooling OA Rate [cfm] | Split MSW Furnace with DX Cooling OA Rate [cfm] | 109.9824 | 109.9824 | 109.9824 | 109.9824 | [6 empty] | 2021-05-06
IA_MA_Split Office Furnace with DX Cooling OA Rate [cfm] | Split Office Furnace with DX Cooling OA Rate [cfm] | 80.7372 | 80.7372 | 80.7372 | 80.7372 | [6 empty] | 2021-05-06
IA_MA_Split TN1 Furnace with DX Cooling OA Rate [cfm] | Split TN1 Furnace with DX Cooling OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | [6 empty] | 2021-05-06
IA_MA_Split TN2 Furnace with DX Cooling OA Rate [cfm] | Split TN2 Furnace with DX Cooling OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | [6 empty] | 2021-05-06
IA_MA_Split TNE Furnace with DX Cooling OA Rate [cfm] | Split TNE Furnace with DX Cooling OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | [6 empty] | 2021-05-06
IA_MA_Split TNW Furnace with DX Cooling OA Rate [cfm] | Split TNW Furnace with DX Cooling OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | [6 empty] | 2021-05-06
IA_MA_Split TS1 Furnace with DX Cooling OA Rate [cfm] | Split TS1 Furnace with DX Cooling OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | [6 empty] | 2021-05-06
IA_MA_Split TS2 Furnace with DX Cooling OA Rate [cfm] | Split TS2 Furnace with DX Cooling OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | [6 empty] | 2021-05-06
IA_MA_Split TSE Furnace with DX Cooling OA Rate [cfm] | Split TSE Furnace with DX Cooling OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | [6 empty] | 2021-05-06
IA_MA_Split TSW Furnace with DX Cooling OA Rate [cfm] | Split TSW Furnace with DX Cooling OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | [6 empty] | 2021-05-06
IA_MA_SPLIT GSW HEATING COIL Heating Capacity [kBtu/hr] | SPLIT GSW HEATING COIL Heating Capacity [kBtu/hr] | 11.9733 | 12.0323 | 12.9796 | 13.0391 | [6 empty] | 2021-05-06
IA_MA_SPLIT GNW HEATING COIL Heating Capacity [kBtu/hr] | SPLIT GNW HEATING COIL Heating Capacity [kBtu/hr] | 11.8964 | 11.9555 | 12.8954 | 12.9549 | [6 empty] | 2021-05-06
IA_MA_SPLIT OFFICE HEATING COIL Heating Capacity [kBtu/hr] | SPLIT OFFICE HEATING COIL Heating Capacity [kBtu/hr] | 25.498 | 25.5788 | 26.7782 | 26.8597 | [6 empty] | 2021-05-06
IA_MA_SPLIT GNE HEATING COIL Heating Capacity [kBtu/hr] | SPLIT GNE HEATING COIL Heating Capacity [kBtu/hr] | 11.8651 | 11.9243 | 12.8618 | 12.9213 | [6 empty] | 2021-05-06
IA_MA_SPLIT GN1 HEATING COIL Heating Capacity [kBtu/hr] | SPLIT GN1 HEATING COIL Heating Capacity [kBtu/hr] | 8.828 | 8.8872 | 9.6315 | 9.6911 | [6 empty] | 2021-05-06
IA_MA_SPLIT GN2 HEATING COIL Heating Capacity [kBtu/hr] | SPLIT GN2 HEATING COIL Heating Capacity [kBtu/hr] | 8.8271 | 8.8863 | 9.6305 | 9.6901 | [6 empty] | 2021-05-06
IA_MA_SPLIT GS1 HEATING COIL Heating Capacity [kBtu/hr] | SPLIT GS1 HEATING COIL Heating Capacity [kBtu/hr] | 8.7602 | 8.8193 | 9.5587 | 9.6182 | [6 empty] | 2021-05-06
IA_MA_SPLIT GS2 HEATING COIL Heating Capacity [kBtu/hr] | SPLIT GS2 HEATING COIL Heating Capacity [kBtu/hr] | 9.277 | 9.3369 | 10.0828 | 10.1431 | [6 empty] | 2021-05-06
IA_MA_SPLIT MSW HEATING COIL Heating Capacity [kBtu/hr] | SPLIT MSW HEATING COIL Heating Capacity [kBtu/hr] | 21.5438 | 21.673 | 23.592 | 23.7216 | [6 empty] | 2021-05-06
IA_MA_SPLIT MNW HEATING COIL Heating Capacity [kBtu/hr] | SPLIT MNW HEATING COIL Heating Capacity [kBtu/hr] | 21.6667 | 21.7958 | 23.7231 | 23.8526 | [6 empty] | 2021-05-06
IA_MA_SPLIT MSE HEATING COIL Heating Capacity [kBtu/hr] | SPLIT MSE HEATING COIL Heating Capacity [kBtu/hr] | 21.4707 | 21.5999 | 23.514 | 23.6436 | [6 empty] | 2021-05-06
IA_MA_SPLIT MNE HEATING COIL Heating Capacity [kBtu/hr] | SPLIT MNE HEATING COIL Heating Capacity [kBtu/hr] | 21.5935 | 21.7227 | 23.645 | 23.7746 | [6 empty] | 2021-05-06
IA_MA_SPLIT MN1 HEATING COIL Heating Capacity [kBtu/hr] | SPLIT MN1 HEATING COIL Heating Capacity [kBtu/hr] | 15.1627 | 15.2887 | 16.6905 | 16.8167 | [6 empty] | 2021-05-06
IA_MA_SPLIT MN2 HEATING COIL Heating Capacity [kBtu/hr] | SPLIT MN2 HEATING COIL Heating Capacity [kBtu/hr] | 15.1608 | 15.2869 | 16.6885 | 16.8147 | [6 empty] | 2021-05-06
IA_MA_SPLIT MS1 HEATING COIL Heating Capacity [kBtu/hr] | SPLIT MS1 HEATING COIL Heating Capacity [kBtu/hr] | 15.0499 | 15.176 | 16.5704 | 16.6966 | [6 empty] | 2021-05-06
IA_MA_SPLIT MS2 HEATING COIL Heating Capacity [kBtu/hr] | SPLIT MS2 HEATING COIL Heating Capacity [kBtu/hr] | 15.0481 | 15.1741 | 16.5684 | 16.6947 | [6 empty] | 2021-05-06
IA_MA_SPLIT TSW HEATING COIL Heating Capacity [kBtu/hr] | SPLIT TSW HEATING COIL Heating Capacity [kBtu/hr] | 14.9955 | 15.0575 | 16.4727 | 16.5348 | [6 empty] | 2021-05-06
IA_MA_SPLIT TNW HEATING COIL Heating Capacity [kBtu/hr] | SPLIT TNW HEATING COIL Heating Capacity [kBtu/hr] | 15.0669 | 15.129 | 16.5491 | 16.6113 | [6 empty] | 2021-05-06
IA_MA_SPLIT TSE HEATING COIL Heating Capacity [kBtu/hr] | SPLIT TSE HEATING COIL Heating Capacity [kBtu/hr] | 14.9569 | 15.0189 | 16.4315 | 16.4936 | [6 empty] | 2021-05-06
IA_MA_SPLIT TNE HEATING COIL Heating Capacity [kBtu/hr] | SPLIT TNE HEATING COIL Heating Capacity [kBtu/hr] | 15.0283 | 15.0903 | 16.5078 | 16.57 | [6 empty] | 2021-05-06
IA_MA_SPLIT TN1 HEATING COIL Heating Capacity [kBtu/hr] | SPLIT TN1 HEATING COIL Heating Capacity [kBtu/hr] | 11.5145 | 11.5764 | 12.6527 | 12.7147 | [6 empty] | 2021-05-06
IA_MA_SPLIT TN2 HEATING COIL Heating Capacity [kBtu/hr] | SPLIT TN2 HEATING COIL Heating Capacity [kBtu/hr] | 11.5134 | 11.5753 | 12.6516 | 12.7136 | [6 empty] | 2021-05-06
IA_MA_SPLIT TS1 HEATING COIL Heating Capacity [kBtu/hr] | SPLIT TS1 HEATING COIL Heating Capacity [kBtu/hr] | 11.4367 | 11.4985 | 12.5701 | 12.6321 | [6 empty] | 2021-05-06
IA_MA_SPLIT TS2 HEATING COIL Heating Capacity [kBtu/hr] | SPLIT TS2 HEATING COIL Heating Capacity [kBtu/hr] | 11.4356 | 11.4975 | 12.569 | 12.631 | [6 empty] | 2021-05-06
IA_MA_Split_GSW ERV Flag | Split_GSW ERV Flag | Yes | Yes | Yes | Yes | [6 empty] | 2021-05-06
IA_MA_Split_GNW ERV Flag | Split_GNW ERV Flag | Yes | Yes | Yes | Yes | [6 empty] | 2021-05-06
IA_MA_Split_GNE ERV Flag | Split_GNE ERV Flag | Yes | Yes | Yes | Yes | [6 empty] | 2021-05-06
IA_MA_Split_GN1 ERV Flag | Split_GN1 ERV Flag | Yes | Yes | Yes | Yes | [6 empty] | 2021-05-06
IA_MA_Split_GN2 ERV Flag | Split_GN2 ERV Flag | Yes | Yes | Yes | Yes | [6 empty] | 2021-05-06
IA_MA_Split_GS1 ERV Flag | Split_GS1 ERV Flag | Yes | Yes | Yes | Yes | [6 empty] | 2021-05-06
IA_MA_Split_GS2 ERV Flag | Split_GS2 ERV Flag | Yes | Yes | Yes | Yes | [6 empty] | 2021-05-06
IA_MA_Split_MSW ERV Flag | Split_MSW ERV Flag | Yes | Yes | Yes | Yes | [6 empty] | 2021-05-06
IA_MA_Split_MNW ERV Flag | Split_MNW ERV Flag | Yes | Yes | Yes | Yes | [6 empty] | 2021-05-06
IA_MA_Split_MSE ERV Flag | Split_MSE ERV Flag | Yes | Yes | Yes | Yes | [6 empty] | 2021-05-06
IA_MA_Split_MNE ERV Flag | Split_MNE ERV Flag | Yes | Yes | Yes | Yes | [6 empty] | 2021-05-06
IA_MA_Split_MN1 ERV Flag | Split_MN1 ERV Flag | Yes | Yes | Yes | Yes | [6 empty] | 2021-05-06
IA_MA_Split_MN2 ERV Flag | Split_MN2 ERV Flag | Yes | Yes | Yes | Yes | [6 empty] | 2021-05-06
IA_MA_Split_MS1 ERV Flag | Split_MS1 ERV Flag | Yes | Yes | Yes | Yes | [6 empty] | 2021-05-06
IA_MA_Split_MS2 ERV Flag | Split_MS2 ERV Flag | Yes | Yes | Yes | Yes | [6 empty] | 2021-05-06
IA_MA_Split_TSW ERV Flag | Split_TSW ERV Flag | Yes | Yes | Yes | Yes | [6 empty] | 2021-05-06
IA_MA_Split_TNW ERV Flag | Split_TNW ERV Flag | Yes | Yes | Yes | Yes | [6 empty] | 2021-05-06
IA_MA_Split_TSE ERV Flag | Split_TSE ERV Flag | Yes | Yes | Yes | Yes | [6 empty] | 2021-05-06
IA_MA_Split_TNE ERV Flag | Split_TNE ERV Flag | Yes | Yes | Yes | Yes | [6 empty] | 2021-05-06
IA_MA_Split_TN1 ERV Flag | Split_TN1 ERV Flag | Yes | Yes | Yes | Yes | [6 empty] | 2021-05-06
IA_MA_Split_TN2 ERV Flag | Split_TN2 ERV Flag | Yes | Yes | Yes | Yes | [6 empty] | 2021-05-06
IA_MA_Split_TS1 ERV Flag | Split_TS1 ERV Flag | Yes | Yes | Yes | Yes | [6 empty] | 2021-05-06
IA_MA_Split_TS2 ERV Flag | Split_TS2 ERV Flag | Yes | Yes | Yes | Yes | [6 empty] | 2021-05-06
id | item | Zone5B(ID-Boise-ID) ASHRAE901-state_STD2016 | Zone5B(ID-Boise-ID) ASHRAE901-state_STD2019 | Zone6B(ID-IdahoFalls-ID) ASHRAE901-state_STD2016 | Zone6B(ID-IdahoFalls-ID) ASHRAE901-state_STD2019 | [6 empty] | 2021-05-06
ID_SO_PSZ-AC:1 Cooling Capacity [ton] | PSZ-AC:1 Cooling Capacity [ton] | 1.5899 | 1.4935 | 1.6655 | 1.5433 | [6 empty] | 2021-05-06
ID_SO_PSZ-AC:2 Cooling Capacity [ton] | PSZ-AC:2 Cooling Capacity [ton] | 1.4717 | 1.4048 | 1.4582 | 1.3587 | [6 empty] | 2021-05-06
ID_SO_PSZ-AC:3 Cooling Capacity [ton] | PSZ-AC:3 Cooling Capacity [ton] | 1.1517 | 1.105 | 1.16 | 1.0762 | [6 empty] | 2021-05-06
ID_SO_PSZ-AC:4 Cooling Capacity [ton] | PSZ-AC:4 Cooling Capacity [ton] | 1.3767 | 1.2929 | 1.3442 | 1.2322 | [6 empty] | 2021-05-06
ID_SO_PSZ-AC:5 Cooling Capacity [ton] | PSZ-AC:5 Cooling Capacity [ton] | 1.3879 | 1.3397 | 1.4454 | 1.3562 | [6 empty] | 2021-05-06
ID_SO_PSZ-AC:1 Supply Flow Rate [cfm] | PSZ-AC:1 Supply Flow Rate [cfm] | 699.2304 | 656.8528 | 741.608 | 699.2304 | [6 empty] | 2021-05-06
ID_SO_PSZ-AC:2 Supply Flow Rate [cfm] | PSZ-AC:2 Supply Flow Rate [cfm] | 656.8528 | 635.664 | 656.8528 | 614.4752 | [6 empty] | 2021-05-06
ID_SO_PSZ-AC:3 Supply Flow Rate [cfm] | PSZ-AC:3 Supply Flow Rate [cfm] | 508.5312 | 487.3424 | 529.72 | 487.3424 | [6 empty] | 2021-05-06
ID_SO_PSZ-AC:4 Supply Flow Rate [cfm] | PSZ-AC:4 Supply Flow Rate [cfm] | 614.4752 | 572.0976 | 614.4752 | 550.9088 | [6 empty] | 2021-05-06
ID_SO_PSZ-AC:5 Supply Flow Rate [cfm] | PSZ-AC:5 Supply Flow Rate [cfm] | 614.4752 | 593.2864 | 656.8528 | 614.4752 | [6 empty] | 2021-05-06
ID_SO_PSZ-AC:1 OA Rate [cfm] | PSZ-AC:1 OA Rate [cfm] | 136.9178 | 136.9178 | 136.9178 | 136.9178 | [6 empty] | 2021-05-06
ID_SO_PSZ-AC:2 OA Rate [cfm] | PSZ-AC:2 OA Rate [cfm] | 103.7925 | 103.7925 | 103.7925 | 103.7925 | [6 empty] | 2021-05-06
ID_SO_PSZ-AC:3 OA Rate [cfm] | PSZ-AC:3 OA Rate [cfm] | 61.5711 | 61.5711 | 61.5711 | 61.5711 | [6 empty] | 2021-05-06
ID_SO_PSZ-AC:4 OA Rate [cfm] | PSZ-AC:4 OA Rate [cfm] | 103.7925 | 103.7925 | 103.7925 | 103.7925 | [6 empty] | 2021-05-06
ID_SO_PSZ-AC:5 OA Rate [cfm] | PSZ-AC:5 OA Rate [cfm] | 61.5711 | 61.5711 | 61.5711 | 61.5711 | [6 empty] | 2021-05-06
ID_SO_PSZ-AC:1 heating Capacity [kBtu/hr] | PSZ-AC:1 heating Capacity [kBtu/hr] | 13.8149 | 13.8149 | 14.5571 | 14.5246 | [6 empty] | 2021-05-06
ID_SO_PSZ-AC:2 heating Capacity [kBtu/hr] | PSZ-AC:2 heating Capacity [kBtu/hr] | 18.2944 | 18.0683 | 21.368 | 21.1103 | [6 empty] | 2021-05-06
ID_SO_PSZ-AC:3 heating Capacity [kBtu/hr] | PSZ-AC:3 heating Capacity [kBtu/hr] | 11.0599 | 10.9349 | 13.0777 | 12.9296 | [6 empty] | 2021-05-06
ID_SO_PSZ-AC:4 heating Capacity [kBtu/hr] | PSZ-AC:4 heating Capacity [kBtu/hr] | 18.0167 | 17.8384 | 21.3049 | 21.0857 | [6 empty] | 2021-05-06
ID_SO_PSZ-AC:5 heating Capacity [kBtu/hr] | PSZ-AC:5 heating Capacity [kBtu/hr] | 11.0147 | 10.8941 | 13.0777 | 12.9296 | [6 empty] | 2021-05-06
id | item | Zone5B(ID-Boise-ID) ASHRAE901-state_STD2016 | Zone5B(ID-Boise-ID) ASHRAE901-state_STD2019 | Zone6B(ID-IdahoFalls-ID) ASHRAE901-state_STD2016 | Zone6B(ID-IdahoFalls-ID) ASHRAE901-state_STD2019 | [6 empty] | 2021-05-06
ID_LO_CAV_BAS Supply Flow Rate [cfm] | CAV_BAS Supply Flow Rate [cfm] | 12670.9024 | 11738.5952 | 13772.72 | 12734.4688 | [6 empty] | 2021-05-06
ID_LO_VAV_BOT WITH REHEAT Supply Flow Rate [cfm] | VAV_BOT WITH REHEAT Supply Flow Rate [cfm] | 21104.0448 | 20108.1712 | 22629.6384 | 21358.3104 | [6 empty] | 2021-05-06
ID_LO_VAV_MID WITH REHEAT Supply Flow Rate [cfm] | VAV_MID WITH REHEAT Supply Flow Rate [cfm] | 195720.9459 | 186164.7971 | 208413.0371 | 196017.5891 | [6 empty] | 2021-05-06
ID_LO_VAV_TOP WITH REHEAT Supply Flow Rate [cfm] | VAV_TOP WITH REHEAT Supply Flow Rate [cfm] | 21591.3872 | 20722.6464 | 22862.7152 | 21633.7648 | [6 empty] | 2021-05-06
ID_LO_Supply Air Temp. Reset Flag | Supply Air Temp. Reset Flag | Yes | Yes | Yes | Yes | [6 empty] | 2021-05-06
ID_LO_CAV_BAS OA Rate [cfm] | CAV_BAS OA Rate [cfm] | 2542.8255 | 2542.8255 | 2542.8255 | 2542.8255 | [6 empty] | 2021-05-06
ID_LO_VAV_BOT WITH REHEAT OA Rate [cfm] | VAV_BOT WITH REHEAT OA Rate [cfm] | 5377.8022 | 4302.174 | 5377.8022 | 4302.174 | [6 empty] | 2021-05-06
ID_LO_VAV_MID WITH REHEAT OA Rate [cfm] | VAV_MID WITH REHEAT OA Rate [cfm] | 53777.9373 | 43021.7396 | 53777.9373 | 43021.7396 | [6 empty] | 2021-05-06
ID_LO_VAV_TOP WITH REHEAT OA Rate [cfm] | VAV_TOP WITH REHEAT OA Rate [cfm] | 5377.8022 | 4302.174 | 5377.8022 | 4302.174 | [6 empty] | 2021-05-06
ID_LO_AIRLOOP DATACENTER BASEMENT OA Rate [cfm] | AIRLOOP DATACENTER BASEMENT OA Rate [cfm] | 716.9654 | 716.9654 | 716.9654 | 716.9654 | [6 empty] | 2021-05-06
ID_LO_VAV_bot_WITH_REHEAT ERV Flag | VAV_bot_WITH_REHEAT ERV Flag | No | No | No | No | [6 empty] | 2021-05-06
ID_LO_VAV_mid_WITH_REHEAT ERV Flag | VAV_mid_WITH_REHEAT ERV Flag | No | No | No | No | [6 empty] | 2021-05-06
ID_LO_VAV_top_WITH_REHEAT ERV Flag | VAV_top_WITH_REHEAT ERV Flag | No | No | No | No | [6 empty] | 2021-05-06
ID_LO_COOLSYS1 CHILLER1 Capacity [ton] | COOLSYS1 CHILLER1 Capacity [ton] | 328.3705 | 300.1185 | 306.2447 | 283.5306 | [6 empty] | 2021-05-06
ID_LO_COOLSYS1 CHILLER2 Capacity [ton] | COOLSYS1 CHILLER2 Capacity [ton] | 328.3705 | 300.1185 | 306.2447 | 283.5306 | [6 empty] | 2021-05-06
ID_LO_TOWERWATERSYS COOLTOWER 1 Capacity [ton] | TOWERWATERSYS COOLTOWER 1 Capacity [ton] | 312.078 | 285.226 | 291.0485 | 269.4538 | [6 empty] | 2021-05-06
ID_LO_TOWERWATERSYS COOLTOWER 2 Capacity [ton] | TOWERWATERSYS COOLTOWER 2 Capacity [ton] | 312.078 | 285.226 | 291.0485 | 269.4538 | [6 empty] | 2021-05-06
ID_LO_HEATSYS1 BOILER Capacity [MMBTU/h] | HEATSYS1 BOILER Capacity [MMBTU/h] | 4357.3686 | 3846.0384 | 4701.65 | 4164.6379 | [6 empty] | 2021-05-06
ID_LO_COOLSYS1 PUMP Flow Rate [gal/min] | COOLSYS1 PUMP Flow Rate [gal/min] | 0 | 0 | 0 | 0 | [6 empty] | 2021-05-06
ID_LO_COOLSYS1 CHILLER1 PUMP Flow Rate [gal/min] | COOLSYS1 CHILLER1 PUMP Flow Rate [gal/min] | 516.5779 | 471.5535 | 481.0605 | 445.5938 | [6 empty] | 2021-05-06
ID_LO_COOLSYS1 CHILLER2 PUMP Flow Rate [gal/min] | COOLSYS1 CHILLER2 PUMP Flow Rate [gal/min] | 516.5779 | 471.5535 | 481.0605 | 445.5938 | [6 empty] | 2021-05-06
ID_LO_COOLSYS1 PUMP SECONDARY Flow Rate [gal/min] | COOLSYS1 PUMP SECONDARY Flow Rate [gal/min] | 1033.1573 | 943.1053 | 962.1194 | 891.1876 | [6 empty] | 2021-05-06
ID_LO_HEATSYS1 PUMP Flow Rate [gal/min] | HEATSYS1 PUMP Flow Rate [gal/min] | 894.4068 | 789.4507 | 965.0755 | 854.8476 | [6 empty] | 2021-05-06
ID_LO_TOWERWATERSYS PUMP Flow Rate [gal/min] | TOWERWATERSYS PUMP Flow Rate [gal/min] | 1811.6919 | 1655.7248 | 1689.6444 | 1602.6262 | [6 empty] | 2021-05-06
ID_LO_PLANT CIRC PUMP Flow Rate [gal/min] | PLANT CIRC PUMP Flow Rate [gal/min] | 220.9297 | 220.0294 | 227.8769 | 226.5724 | [6 empty] | 2021-05-06
ID_LO_COOLSYS1 PUMP SECONDARY Pressure setpoint reset [yes,no] | COOLSYS1 PUMP SECONDARY Pressure setpoint reset [yes,no] | pump_ride_on_curve | pump_ride_on_curve | pump_ride_on_curve | pump_ride_on_curve | [6 empty] | 2021-05-06
ID_LO_COOLSYS1 CHILLER1 PUMP Pump Power [hp] | COOLSYS1 CHILLER1 PUMP Pump Power [hp] | 2.7868 | 2.5187 | 2.5951 | 2.38 | [6 empty] | 2021-05-06
ID_LO_COOLSYS1 CHILLER2 PUMP Pump Power [hp] | COOLSYS1 CHILLER2 PUMP Pump Power [hp] | 2.7868 | 2.5187 | 2.5951 | 2.38 | [6 empty] | 2021-05-06
ID_LO_COOLSYS1 PUMP SECONDARY Pump Power [hp] | COOLSYS1 PUMP SECONDARY Pump Power [hp] | 16.7206 | 15.112 | 15.5709 | 14.2801 | [6 empty] | 2021-05-06
ID_LO_HEATSYS1 PUMP Pump Power [hp] | HEATSYS1 PUMP Pump Power [hp] | 19.3331 | 16.8955 | 20.8607 | 18.2951 | [6 empty] | 2021-05-06
ID_LO_TOWERWATERSYS PUMP Pump Power [hp] | TOWERWATERSYS PUMP Pump Power [hp] | 32.4358 | 29.3516 | 30.2502 | 28.4082 | [6 empty] | 2021-05-06
ID_LO_PLANT CIRC PUMP Pump Power [hp] | PLANT CIRC PUMP Pump Power [hp] | 4.7673 | 4.7009 | 4.9173 | 4.8407 | [6 empty] | 2021-05-06
ID_LO_Datacenter PLANT CIRC PUMP Pump Power [hp] | Datacenter PLANT CIRC PUMP Pump Power [hp] | 4.7673 | 4.7009 | 4.9173 | 4.8407 | [6 empty] | 2021-05-06
ID_LO_ZN_VAV_BOXes_Max_Reheat_Water_Flow_GPM | ZN_VAV_BOXes_Max_Reheat_Water_Flow_GPM | 454.7527 | 435.8175 | 488.9561 | 469.6776 | [6 empty] | 2021-05-06
ID_LO_COOLSYS1 PUMP SECONDARY VSD | COOLSYS1 PUMP SECONDARY VSD | No | No | No | No | [6 empty] | 2021-05-06
ID_LO_HEATSYS1 PUMP VSD | HEATSYS1 PUMP VSD | No | No | No | No | [6 empty] | 2021-05-06
ID_LO_DATACENTER BASEMENT Cooling Capacity [ton] | DATACENTER BASEMENT Cooling Capacity [ton] | 128.9348 | 128.5503 | 133.0648 | 132.6551 | [6 empty] | 2021-05-06
ID_LO_DATACENTER BOT Cooling Capacity [ton] | DATACENTER BOT Cooling Capacity [ton] | 2.8439 | 2.8183 | 2.9272 | 2.8806 | [6 empty] | 2021-05-06
ID_LO_DATACENTER MID Cooling Capacity [ton] | DATACENTER MID Cooling Capacity [ton] | 27.2744 | 27.0469 | 28.0748 | 27.6195 | [6 empty] | 2021-05-06
ID_LO_DATACENTER TOP Cooling Capacity [ton] | DATACENTER TOP Cooling Capacity [ton] | 2.7824 | 2.7605 | 2.8583 | 2.8133 | [6 empty] | 2021-05-06
id | item | Zone5B(ID-Boise-ID) ASHRAE901-state_STD2016 | Zone5B(ID-Boise-ID) ASHRAE901-state_STD2019 | Zone6B(ID-IdahoFalls-ID) ASHRAE901-state_STD2016 | Zone6B(ID-IdahoFalls-ID) ASHRAE901-state_STD2019 | [6 empty] | 2021-05-06
ID_RS_PSZ-AC:1 Cooling Capacity [ton] | PSZ-AC:1 Cooling Capacity [ton] | 10.571 | 9.9159 | 9.3144 | 8.5913 | [6 empty] | 2021-05-06
ID_RS_PSZ-AC:2 Cooling Capacity [ton] | PSZ-AC:2 Cooling Capacity [ton] | 44.1851 | 41.8795 | 40.9762 | 39.0356 | [6 empty] | 2021-05-06
ID_RS_PSZ-AC:3 Cooling Capacity [ton] | PSZ-AC:3 Cooling Capacity [ton] | 6.047 | 5.8908 | 5.5386 | 5.3449 | [6 empty] | 2021-05-06
ID_RS_PSZ-AC:4 Cooling Capacity [ton] | PSZ-AC:4 Cooling Capacity [ton] | 4.9506 | 4.7873 | 4.3823 | 4.1703 | [6 empty] | 2021-05-06
ID_RS_PSZ-AC:1 Supply Flow Rate [cfm] | PSZ-AC:1 Supply Flow Rate [cfm] | 4153.0048 | 3856.3616 | 4025.872 | 3665.6624 | [6 empty] | 2021-05-06
ID_RS_PSZ-AC:2 Supply Flow Rate [cfm] | PSZ-AC:2 Supply Flow Rate [cfm] | 16315.376 | 15298.3136 | 16929.8512 | 15997.544 | [6 empty] | 2021-05-06
ID_RS_PSZ-AC:3 Supply Flow Rate [cfm] | PSZ-AC:3 Supply Flow Rate [cfm] | 2415.5232 | 2351.9568 | 2479.0896 | 2373.1456 | [6 empty] | 2021-05-06
ID_RS_PSZ-AC:4 Supply Flow Rate [cfm] | PSZ-AC:4 Supply Flow Rate [cfm] | 1928.1808 | 1843.4256 | 1885.8032 | 1779.8592 | [6 empty] | 2021-05-06
ID_RS_PSZ-AC:1 OA Rate [cfm] | PSZ-AC:1 OA Rate [cfm] | 490.669 | 490.669 | 490.669 | 490.669 | [6 empty] | 2021-05-06
ID_RS_PSZ-AC:2 OA Rate [cfm] | PSZ-AC:2 OA Rate [cfm] | 4005.1282 | 4005.1282 | 4005.1282 | 4005.1282 | [6 empty] | 2021-05-06
ID_RS_PSZ-AC:3 OA Rate [cfm] | PSZ-AC:3 OA Rate [cfm] | 377.3937 | 377.3937 | 377.3937 | 377.3937 | [6 empty] | 2021-05-06
ID_RS_PSZ-AC:4 OA Rate [cfm] | PSZ-AC:4 OA Rate [cfm] | 377.3937 | 377.3937 | 377.3937 | 377.3937 | [6 empty] | 2021-05-06
ID_RS_PSZ-AC:1 OA Damper [gravity, motorized] | PSZ-AC:1 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2021-05-06
ID_RS_PSZ-AC:2 OA Damper [gravity, motorized] | PSZ-AC:2 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2021-05-06
ID_RS_PSZ-AC:3 OA Damper [gravity, motorized] | PSZ-AC:3 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2021-05-06
ID_RS_PSZ-AC:4 OA Damper [gravity, motorized] | PSZ-AC:4 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2021-05-06
ID_RS_PSZ-AC:1 Heating Capacity [kBtu/hr] | PSZ-AC:1 Heating Capacity [kBtu/hr] | 173.3108 | 161.9452 | 158.0945 | 144.8538 | [6 empty] | 2021-05-06
ID_RS_PSZ-AC:2 Heating Capacity [kBtu/hr] | PSZ-AC:2 Heating Capacity [kBtu/hr] | 809.8676 | 772.9249 | 800.2032 | 768.384 | [6 empty] | 2021-05-06
ID_RS_PSZ-AC:3 Heating Capacity [kBtu/hr] | PSZ-AC:3 Heating Capacity [kBtu/hr] | 107.5558 | 104.9254 | 102.2334 | 99.3879 | [6 empty] | 2021-05-06
ID_RS_PSZ-AC:4 Heating Capacity [kBtu/hr] | PSZ-AC:4 Heating Capacity [kBtu/hr] | 90.6477 | 88.0992 | 85.783 | 82.4589 | [6 empty] | 2021-05-06
id | item | Zone5B(ID-Boise-ID) ASHRAE901-state_STD2016 | Zone5B(ID-Boise-ID) ASHRAE901-state_STD2019 | Zone6B(ID-IdahoFalls-ID) ASHRAE901-state_STD2016 | Zone6B(ID-IdahoFalls-ID) ASHRAE901-state_STD2019 | [6 empty] | 2021-05-06
ID_PS_VAV_POD_1 Cooling Capacity [ton] | VAV_POD_1 Cooling Capacity [ton] | 21.4216 | 20.2505 | 20.1195 | 18.7483 | [6 empty] | 2021-05-06
ID_PS_VAV_POD_2 Cooling Capacity [ton] | VAV_POD_2 Cooling Capacity [ton] | 21.2346 | 19.9834 | 19.8153 | 18.4332 | [6 empty] | 2021-05-06
ID_PS_VAV_POD_3 Cooling Capacity [ton] | VAV_POD_3 Cooling Capacity [ton] | 19.6926 | 18.5657 | 18.5378 | 17.1203 | [6 empty] | 2021-05-06
ID_PS_VAV_OTHER Cooling Capacity [ton] | VAV_OTHER Cooling Capacity [ton] | 25.975 | 23.5094 | 22.5064 | 20.3596 | [6 empty] | 2021-05-06
ID_PS_PSZ-AC_1:6 Cooling Capacity [ton] | PSZ-AC_1:6 Cooling Capacity [ton] | 7.9862 | 7.705 | 7.7276 | 7.4269 | [6 empty] | 2021-05-06
ID_PS_PSZ-AC_2:5 Cooling Capacity [ton] | PSZ-AC_2:5 Cooling Capacity [ton] | 5.8258 | 5.8049 | 5.1644 | 5.1055 | [6 empty] | 2021-05-06
ID_PS_PSZ-AC_2:7 Cooling Capacity [ton] | PSZ-AC_2:7 Cooling Capacity [ton] | 10.5074 | 10.5074 | 9.5277 | 9.5277 | [6 empty] | 2021-05-06
ID_PS_VAV_POD_1 Supply Flow Rate [cfm] | VAV_POD_1 Supply Flow Rate [cfm] | 6420.2064 | 6081.1856 | 6462.584 | 6038.808 | [6 empty] | 2021-05-06
ID_PS_VAV_POD_2 Supply Flow Rate [cfm] | VAV_POD_2 Supply Flow Rate [cfm] | 6377.8288 | 5996.4304 | 6377.8288 | 5932.864 | [6 empty] | 2021-05-06
ID_PS_VAV_POD_3 Supply Flow Rate [cfm] | VAV_POD_3 Supply Flow Rate [cfm] | 5911.6752 | 5572.6544 | 5954.0528 | 5509.088 | [6 empty] | 2021-05-06
ID_PS_VAV_OTHER Supply Flow Rate [cfm] | VAV_OTHER Supply Flow Rate [cfm] | 9005.24 | 8496.7088 | 9259.5056 | 8581.464 | [6 empty] | 2021-05-06
ID_PS_PSZ-AC_2:5 Supply Flow Rate [cfm] | PSZ-AC_2:5 Supply Flow Rate [cfm] | 1843.4256 | 1822.2368 | 1906.992 | 1885.8032 | [6 empty] | 2021-05-06
ID_PS_PSZ-AC_1:6 Supply Flow Rate [cfm] | PSZ-AC_1:6 Supply Flow Rate [cfm] | 2775.7328 | 2648.6 | 2987.6208 | 2839.2992 | [6 empty] | 2021-05-06
ID_PS_PSZ-AC_2:7 Supply Flow Rate [cfm] | PSZ-AC_2:7 Supply Flow Rate [cfm] | 3157.1312 | 3157.1312 | 3157.1312 | 3157.1312 | [6 empty] | 2021-05-06
ID_PS_Supply Air Temp. Reset Flag | Supply Air Temp. Reset Flag | Yes | Yes | Yes | Yes | [6 empty] | 2021-05-06
ID_PS_VAV_POD_1 OA Rate [cfm] | VAV_POD_1 OA Rate [cfm] | 6428.2793 | 6076.8631 | 6470.7629 | 6029.7604 | [6 empty] | 2021-05-06
ID_PS_VAV_POD_2 OA Rate [cfm] | VAV_POD_2 OA Rate [cfm] | 6372.1502 | 5996.7059 | 6372.9342 | 5928.4355 | [6 empty] | 2021-05-06
ID_PS_VAV_POD_3 OA Rate [cfm] | VAV_POD_3 OA Rate [cfm] | 5909.4292 | 5422.002 | 5961.1934 | 5422.002 | [6 empty] | 2021-05-06
ID_PS_VAV_OTHER OA Rate [cfm] | VAV_OTHER OA Rate [cfm] | 3736.1787 | 2988.8921 | 3736.1787 | 2988.8921 | [6 empty] | 2021-05-06
ID_PS_PSZ-AC_2:5 OA Rate [cfm] | PSZ-AC_2:5 OA Rate [cfm] | 1152.7343 | 1152.7343 | 1152.7343 | 1152.7343 | [6 empty] | 2021-05-06
ID_PS_PSZ-AC_1:6 OA Rate [cfm] | PSZ-AC_1:6 OA Rate [cfm] | 539.9118 | 539.9118 | 539.9118 | 539.9118 | [6 empty] | 2021-05-06
ID_PS_PSZ-AC_2:7 OA Rate [cfm] | PSZ-AC_2:7 OA Rate [cfm] | 3153.0841 | 3153.0841 | 3153.0841 | 3153.0841 | [6 empty] | 2021-05-06
ID_PS_VAV_POD_1 OA Damper [gravity, motorized] | VAV_POD_1 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2021-05-06
ID_PS_VAV_POD_2 OA Damper [gravity, motorized] | VAV_POD_2 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2021-05-06
ID_PS_VAV_POD_3 OA Damper [gravity, motorized] | VAV_POD_3 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2021-05-06
ID_PS_VAV_OTHER OA Damper [gravity, motorized] | VAV_OTHER OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2021-05-06
ID_PS_PSZ-AC_2:5 OA Damper [gravity, motorized] | PSZ-AC_2:5 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2021-05-06
ID_PS_PSZ-AC_1:6 OA Damper [gravity, motorized] | PSZ-AC_1:6 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2021-05-06
ID_PS_PSZ-AC_2:7 OA Damper [gravity, motorized] | PSZ-AC_2:7 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2021-05-06
ID_PS_VAV_POD_1 (economizer) | VAV_POD_1 (economizer) | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | [6 empty] | 2021-05-06
ID_PS_VAV_POD_2 (economizer) | VAV_POD_2 (economizer) | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | [6 empty] | 2021-05-06
ID_PS_VAV_POD_3 (economizer) | VAV_POD_3 (economizer) | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | [6 empty] | 2021-05-06
ID_PS_VAV_OTHER (economizer) | VAV_OTHER (economizer) | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | [6 empty] | 2021-05-06
ID_PS_PSZ-AC_2:5 (economizer) | PSZ-AC_2:5 (economizer) | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | [6 empty] | 2021-05-06
ID_PS_PSZ-AC_1:6 (economizer) | PSZ-AC_1:6 (economizer) | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | [6 empty] | 2021-05-06
ID_PS_PSZ-AC_2:7 (economizer) | PSZ-AC_2:7 (economizer) | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | [6 empty] | 2021-05-06
ID_PS_VAV_Pod_1_ERV Flag | VAV_Pod_1_ERV Flag | No | No | Yes | Yes | [6 empty] | 2021-05-06
ID_PS_VAV_Pod_2_ERV Flag | VAV_Pod_2_ERV Flag | No | No | Yes | Yes | [6 empty] | 2021-05-06
ID_PS_VAV_Pod_3_ERV Flag | VAV_Pod_3_ERV Flag | No | No | Yes | Yes | [6 empty] | 2021-05-06
ID_PS_VAV_OTHER_ERV Flag | VAV_OTHER_ERV Flag | No | No | Yes | No | [6 empty] | 2021-05-06
ID_PS_PSZ_AC_2_5_ERV Flag | PSZ_AC_2_5_ERV Flag | No | No | No | No | [6 empty] | 2021-05-06
ID_PS_PSZ_AC_2_7_ERV Flag | PSZ_AC_2_7_ERV Flag | No | No | Yes | Yes | [6 empty] | 2021-05-06
ID_PS_HEATSYS1 Capacity [MMBTU/h] | HEATSYS1 Capacity [MMBTU/h] | 1.1244 | 1.055 | 1.2329 | 1.1547 | [6 empty] | 2021-05-06
ID_PS_HEATSYS1 Flow Rate [gal/min] | HEATSYS1 Flow Rate [gal/min] | 115.3942 | 108.2766 | 126.536 | 118.5087 | [6 empty] | 2021-05-06
ID_PS_VAV_POD_1 Fan Power [hp] | VAV_POD_1 Fan Power [hp] | 9.4836 | 8.9652 | 9.5463 | 8.8957 | [6 empty] | 2021-05-06
ID_PS_VAV_POD_2 Fan Power [hp] | VAV_POD_2 Fan Power [hp] | 9.4008 | 8.8469 | 9.402 | 8.7462 | [6 empty] | 2021-05-06
ID_PS_VAV_POD_3 Fan Power [hp] | VAV_POD_3 Fan Power [hp] | 8.7182 | 8.2193 | 8.7959 | 8.1233 | [6 empty] | 2021-05-06
ID_PS_VAV_OTHER Fan Power [hp] | VAV_OTHER Fan Power [hp] | 13.1971 | 12.4456 | 13.5631 | 12.56 | [6 empty] | 2021-05-06
ID_PS_HEATSYS1 Pump Power [hp] | HEATSYS1 Pump Power [hp] | 2.4943 | 2.3173 | 2.7351 | 2.5363 | [6 empty] | 2021-05-06
ID_PS_PSZ-AC_1:6 Heating Capacity [kBtu/hr] | PSZ-AC_1:6 Heating Capacity [kBtu/hr] | 214.3504 | 205.8808 | 215.6195 | 206.4685 | [6 empty] | 2021-05-06
ID_PS_PSZ-AC_2:5 Heating Capacity [kBtu/hr] | PSZ-AC_2:5 Heating Capacity [kBtu/hr] | 139.4953 | 139.1724 | 141.8246 | 140.976 | [6 empty] | 2021-05-06
ID_PS_PSZ-AC_2:7 Heating Capacity [kBtu/hr] | PSZ-AC_2:7 Heating Capacity [kBtu/hr] | 318.1449 | 318.1449 | 323.3284 | 323.3284 | [6 empty] | 2021-05-06
ID_PS_ZN_VAV_BOXes_Max_Reheat_Water_Flow_GPM | ZN_VAV_BOXes_Max_Reheat_Water_Flow_GPM | 70.8774 | 66.2942 | 76.4205 | 72.0114 | [6 empty] | 2021-05-06
id | item | Zone5B(ID-Boise-ID) ASHRAE901-state_STD2016 | Zone5B(ID-Boise-ID) ASHRAE901-state_STD2019 | Zone6B(ID-IdahoFalls-ID) ASHRAE901-state_STD2016 | Zone6B(ID-IdahoFalls-ID) ASHRAE901-state_STD2019 | [6 empty] | 2021-05-06
ID_SH_SAC_FRONTOFFICE Cooling Capacity [ton] | SAC_FRONTOFFICE Cooling Capacity [ton] | 2.1751 | 2.0441 | 1.9866 | 1.8696 | [6 empty] | 2021-05-06
ID_SH_SAC_FRONTLOUNGE Cooling Capacity [ton] | SAC_FRONTLOUNGE Cooling Capacity [ton] | 5.5677 | 5.3328 | 5.2468 | 5.0047 | [6 empty] | 2021-05-06
ID_SH_SAC_MEETINGROOM Cooling Capacity [ton] | SAC_MEETINGROOM Cooling Capacity [ton] | 2.899 | 2.8256 | 2.7636 | 2.6876 | [6 empty] | 2021-05-06
ID_SH_SAC_EXC_EMPLGE_RESTRM Cooling Capacity [ton] | SAC_EXC_EMPLGE_RESTRM Cooling Capacity [ton] | 5.772 | 5.7288 | 5.7073 | 5.6532 | [6 empty] | 2021-05-06
ID_SH_SAC_FO_ADDAQ SUPPLY FAN Supply Flow Rate [cfm] | SAC_FO_ADDAQ SUPPLY FAN Supply Flow Rate [cfm] | 868.7408 | 805.1744 | 868.7408 | 805.1744 | [6 empty] | 2021-05-06
ID_SH_SAC_FL_ADDAQ SUPPLY FAN Supply Flow Rate [cfm] | SAC_FL_ADDAQ SUPPLY FAN Supply Flow Rate [cfm] | 1991.7472 | 1885.8032 | 2097.6912 | 1970.5584 | [6 empty] | 2021-05-06
ID_SH_SAC_MR_ADDAQ SUPPLY FAN Supply Flow Rate [cfm] | SAC_MR_ADDAQ SUPPLY FAN Supply Flow Rate [cfm] | 932.3072 | 911.1184 | 995.8736 | 974.6848 | [6 empty] | 2021-05-06
ID_SH_SAC_EXC_ADDAQ SUPPLY FAN Supply Flow Rate [cfm] | SAC_EXC_ADDAQ SUPPLY FAN Supply Flow Rate [cfm] | 2394.3344 | 2373.1456 | 2563.8448 | 2542.656 | [6 empty] | 2021-05-06
ID_SH_SAC_Exc_EmpLge_RestRm OA Rate [cfm] | SAC_Exc_EmpLge_RestRm OA Rate [cfm] | 199.9928 | 199.9928 | 199.9928 | 199.9928 | [6 empty] | 2021-05-06
ID_SH_SAC_FrontLounge OA Rate [cfm] | SAC_FrontLounge OA Rate [cfm] | 500.0133 | 500.0133 | 500.0133 | 500.0133 | [6 empty] | 2021-05-06
ID_SH_SAC_FrontOffice OA Rate [cfm] | SAC_FrontOffice OA Rate [cfm] | 119.2938 | 119.2938 | 119.2938 | 119.2938 | [6 empty] | 2021-05-06
ID_SH_SAC_MeetingRoom OA Rate [cfm] | SAC_MeetingRoom OA Rate [cfm] | 267.7629 | 267.7629 | 267.7629 | 267.7629 | [6 empty] | 2021-05-06
ID_SH_SAC_FrontLounge OA Damper [gravity, motorized] | SAC_FrontLounge OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2021-05-06
ID_SH_SAC_FrontOffice (economizer) | SAC_FrontOffice (economizer) | No | No | No | No | [6 empty] | 2021-05-06
ID_SH_SAC_FrontLounge (economizer) | SAC_FrontLounge (economizer) | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | [6 empty] | 2021-05-06
ID_SH_SAC_MeetingRoom (economizer) | SAC_MeetingRoom (economizer) | No | No | No | No | [6 empty] | 2021-05-06
ID_SH_SAC_Exc_EmpLge_RestRm (economizer) | SAC_Exc_EmpLge_RestRm (economizer) | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | [6 empty] | 2021-05-06
ID_SH_SAC_FRONTOFFICE Heating Capacity [kBtu/hr] | SAC_FRONTOFFICE Heating Capacity [kBtu/hr] | 37.0875 | 35.1244 | 35.485 | 33.7021 | [6 empty] | 2021-05-06
ID_SH_SAC_FRONTLOUNGE Heating Capacity [kBtu/hr] | SAC_FRONTLOUNGE Heating Capacity [kBtu/hr] | 100.7232 | 97.3602 | 100.5741 | 97.0717 | [6 empty] | 2021-05-06
ID_SH_SAC_MEETINGROOM Heating Capacity [kBtu/hr] | SAC_MEETINGROOM Heating Capacity [kBtu/hr] | 49.8667 | 48.8777 | 50.1438 | 49.1072 | [6 empty] | 2021-05-06
ID_SH_SAC_EXC_EMPLGE_RESTRM Heating Capacity [kBtu/hr] | SAC_EXC_EMPLGE_RESTRM Heating Capacity [kBtu/hr] | 94.1871 | 93.5278 | 93.8098 | 93.057 | [6 empty] | 2021-05-06
id | item | Zone5B(ID-Boise-ID) ASHRAE901-state_STD2016 | Zone5B(ID-Boise-ID) ASHRAE901-state_STD2019 | Zone6B(ID-IdahoFalls-ID) ASHRAE901-state_STD2016 | Zone6B(ID-IdahoFalls-ID) ASHRAE901-state_STD2019 | [6 empty] | 2021-05-06
ID_MA_SPLIT GSW COOLING COIL Cooling Capacity [ton] | SPLIT GSW COOLING COIL Cooling Capacity [ton] | 0.82507 | 0.80809 | 0.7999 | 0.7608 | [6 empty] | 2021-05-06
ID_MA_SPLIT GNW COOLING COIL Cooling Capacity [ton] | SPLIT GNW COOLING COIL Cooling Capacity [ton] | 0.76962 | 0.75348 | 0.74023 | 0.70437 | [6 empty] | 2021-05-06
ID_MA_SPLIT OFFICE COOLING COIL Cooling Capacity [ton] | SPLIT OFFICE COOLING COIL Cooling Capacity [ton] | 1.7672 | 1.6011 | 1.7354 | 1.5157 | [6 empty] | 2021-05-06
ID_MA_SPLIT GNE COOLING COIL Cooling Capacity [ton] | SPLIT GNE COOLING COIL Cooling Capacity [ton] | 0.63545 | 0.62142 | 0.59829 | 0.5692 | [6 empty] | 2021-05-06
ID_MA_SPLIT GN1 COOLING COIL Cooling Capacity [ton] | SPLIT GN1 COOLING COIL Cooling Capacity [ton] | 0.51617 | 0.50516 | 0.49274 | 0.47331 | [6 empty] | 2021-05-06
ID_MA_SPLIT GN2 COOLING COIL Cooling Capacity [ton] | SPLIT GN2 COOLING COIL Cooling Capacity [ton] | 0.51373 | 0.50279 | 0.49011 | 0.47088 | [6 empty] | 2021-05-06
ID_MA_SPLIT GS1 COOLING COIL Cooling Capacity [ton] | SPLIT GS1 COOLING COIL Cooling Capacity [ton] | 0.57517 | 0.56428 | 0.55364 | 0.5306 | [6 empty] | 2021-05-06
ID_MA_SPLIT GS2 COOLING COIL Cooling Capacity [ton] | SPLIT GS2 COOLING COIL Cooling Capacity [ton] | 0.61723 | 0.5996 | 0.59753 | 0.56815 | [6 empty] | 2021-05-06
ID_MA_SPLIT MSW COOLING COIL Cooling Capacity [ton] | SPLIT MSW COOLING COIL Cooling Capacity [ton] | 2.0476 | 2.009 | 2.0697 | 1.9748 | [6 empty] | 2021-05-06
ID_MA_SPLIT MNW COOLING COIL Cooling Capacity [ton] | SPLIT MNW COOLING COIL Cooling Capacity [ton] | 1.9254 | 1.8887 | 1.9445 | 1.8563 | [6 empty] | 2021-05-06
ID_MA_SPLIT MSE COOLING COIL Cooling Capacity [ton] | SPLIT MSE COOLING COIL Cooling Capacity [ton] | 1.7139 | 1.6827 | 1.6344 | 1.5547 | [6 empty] | 2021-05-06
ID_MA_SPLIT MNE COOLING COIL Cooling Capacity [ton] | SPLIT MNE COOLING COIL Cooling Capacity [ton] | 1.504 | 1.4681 | 1.4532 | 1.3898 | [6 empty] | 2021-05-06
ID_MA_SPLIT MN1 COOLING COIL Cooling Capacity [ton] | SPLIT MN1 COOLING COIL Cooling Capacity [ton] | 1.1519 | 1.131 | 1.1499 | 1.1126 | [6 empty] | 2021-05-06
ID_MA_SPLIT MN2 COOLING COIL Cooling Capacity [ton] | SPLIT MN2 COOLING COIL Cooling Capacity [ton] | 1.1451 | 1.1244 | 1.142 | 1.1054 | [6 empty] | 2021-05-06
ID_MA_SPLIT MS1 COOLING COIL Cooling Capacity [ton] | SPLIT MS1 COOLING COIL Cooling Capacity [ton] | 1.2724 | 1.2493 | 1.2681 | 1.2243 | [6 empty] | 2021-05-06
ID_MA_SPLIT MS2 COOLING COIL Cooling Capacity [ton] | SPLIT MS2 COOLING COIL Cooling Capacity [ton] | 1.2668 | 1.2439 | 1.2609 | 1.2177 | [6 empty] | 2021-05-06
ID_MA_SPLIT TSW COOLING COIL Cooling Capacity [ton] | SPLIT TSW COOLING COIL Cooling Capacity [ton] | 1.3255 | 1.3048 | 1.325 | 1.2721 | [6 empty] | 2021-05-06
ID_MA_SPLIT TNW COOLING COIL Cooling Capacity [ton] | SPLIT TNW COOLING COIL Cooling Capacity [ton] | 1.2584 | 1.2386 | 1.26 | 1.21 | [6 empty] | 2021-05-06
ID_MA_SPLIT TSE COOLING COIL Cooling Capacity [ton] | SPLIT TSE COOLING COIL Cooling Capacity [ton] | 1.1314 | 1.1151 | 1.1047 | 1.0613 | [6 empty] | 2021-05-06
ID_MA_SPLIT TNE COOLING COIL Cooling Capacity [ton] | SPLIT TNE COOLING COIL Cooling Capacity [ton] | 1.0183 | 1.005 | 0.96837 | 0.93637 | [6 empty] | 2021-05-06
ID_MA_SPLIT TN1 COOLING COIL Cooling Capacity [ton] | SPLIT TN1 COOLING COIL Cooling Capacity [ton] | 0.7989 | 0.78813 | 0.77919 | 0.75899 | [6 empty] | 2021-05-06
ID_MA_SPLIT TN2 COOLING COIL Cooling Capacity [ton] | SPLIT TN2 COOLING COIL Cooling Capacity [ton] | 0.79171 | 0.78114 | 0.77028 | 0.75077 | [6 empty] | 2021-05-06
ID_MA_SPLIT TS1 COOLING COIL Cooling Capacity [ton] | SPLIT TS1 COOLING COIL Cooling Capacity [ton] | 0.92118 | 0.90542 | 0.88496 | 0.85489 | [6 empty] | 2021-05-06
ID_MA_SPLIT TS2 COOLING COIL Cooling Capacity [ton] | SPLIT TS2 COOLING COIL Cooling Capacity [ton] | 0.92458 | 0.9117 | 0.88935 | 0.85872 | [6 empty] | 2021-05-06
ID_MA_Split GN1 Furnace with DX Cooling OA Rate [cfm] | Split GN1 Furnace with DX Cooling OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | [6 empty] | 2021-05-06
ID_MA_Split GN2 Furnace with DX Cooling OA Rate [cfm] | Split GN2 Furnace with DX Cooling OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | [6 empty] | 2021-05-06
ID_MA_Split GNE Furnace with DX Cooling OA Rate [cfm] | Split GNE Furnace with DX Cooling OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | [6 empty] | 2021-05-06
ID_MA_Split GNW Furnace with DX Cooling OA Rate [cfm] | Split GNW Furnace with DX Cooling OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | [6 empty] | 2021-05-06
ID_MA_Split GS1 Furnace with DX Cooling OA Rate [cfm] | Split GS1 Furnace with DX Cooling OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | [6 empty] | 2021-05-06
ID_MA_Split GS2 Furnace with DX Cooling OA Rate [cfm] | Split GS2 Furnace with DX Cooling OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | [6 empty] | 2021-05-06
ID_MA_Split GSW Furnace with DX Cooling OA Rate [cfm] | Split GSW Furnace with DX Cooling OA Rate [cfm] | 56.9945 | 56.9945 | 56.9945 | 56.9945 | [6 empty] | 2021-05-06
ID_MA_Split MN1 Furnace with DX Cooling OA Rate [cfm] | Split MN1 Furnace with DX Cooling OA Rate [cfm] | 109.9824 | 109.9824 | 109.9824 | 109.9824 | [6 empty] | 2021-05-06
ID_MA_Split MN2 Furnace with DX Cooling OA Rate [cfm] | Split MN2 Furnace with DX Cooling OA Rate [cfm] | 109.9824 | 109.9824 | 109.9824 | 109.9824 | [6 empty] | 2021-05-06
ID_MA_Split MNE Furnace with DX Cooling OA Rate [cfm] | Split MNE Furnace with DX Cooling OA Rate [cfm] | 109.9824 | 109.9824 | 109.9824 | 109.9824 | [6 empty] | 2021-05-06
ID_MA_Split MNW Furnace with DX Cooling OA Rate [cfm] | Split MNW Furnace with DX Cooling OA Rate [cfm] | 109.9824 | 109.9824 | 109.9824 | 109.9824 | [6 empty] | 2021-05-06
ID_MA_Split MS1 Furnace with DX Cooling OA Rate [cfm] | Split MS1 Furnace with DX Cooling OA Rate [cfm] | 109.9824 | 109.9824 | 109.9824 | 109.9824 | [6 empty] | 2021-05-06
ID_MA_Split MS2 Furnace with DX Cooling OA Rate [cfm] | Split MS2 Furnace with DX Cooling OA Rate [cfm] | 109.9824 | 109.9824 | 109.9824 | 109.9824 | [6 empty] | 2021-05-06
ID_MA_Split MSE Furnace with DX Cooling OA Rate [cfm] | Split MSE Furnace with DX Cooling OA Rate [cfm] | 109.9824 | 109.9824 | 109.9824 | 109.9824 | [6 empty] | 2021-05-06
ID_MA_Split MSW Furnace with DX Cooling OA Rate [cfm] | Split MSW Furnace with DX Cooling OA Rate [cfm] | 109.9824 | 109.9824 | 109.9824 | 109.9824 | [6 empty] | 2021-05-06
ID_MA_Split Office Furnace with DX Cooling OA Rate [cfm] | Split Office Furnace with DX Cooling OA Rate [cfm] | 80.7372 | 80.7372 | 80.7372 | 80.7372 | [6 empty] | 2021-05-06
ID_MA_Split TN1 Furnace with DX Cooling OA Rate [cfm] | Split TN1 Furnace with DX Cooling OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | [6 empty] | 2021-05-06
ID_MA_Split TN2 Furnace with DX Cooling OA Rate [cfm] | Split TN2 Furnace with DX Cooling OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | [6 empty] | 2021-05-06
ID_MA_Split TNE Furnace with DX Cooling OA Rate [cfm] | Split TNE Furnace with DX Cooling OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | [6 empty] | 2021-05-06
ID_MA_Split TNW Furnace with DX Cooling OA Rate [cfm] | Split TNW Furnace with DX Cooling OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | [6 empty] | 2021-05-06
ID_MA_Split TS1 Furnace with DX Cooling OA Rate [cfm] | Split TS1 Furnace with DX Cooling OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | [6 empty] | 2021-05-06
ID_MA_Split TS2 Furnace with DX Cooling OA Rate [cfm] | Split TS2 Furnace with DX Cooling OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | [6 empty] | 2021-05-06
ID_MA_Split TSE Furnace with DX Cooling OA Rate [cfm] | Split TSE Furnace with DX Cooling OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | [6 empty] | 2021-05-06
ID_MA_Split TSW Furnace with DX Cooling OA Rate [cfm] | Split TSW Furnace with DX Cooling OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | [6 empty] | 2021-05-06
ID_MA_SPLIT GSW HEATING COIL Heating Capacity [kBtu/hr] | SPLIT GSW HEATING COIL Heating Capacity [kBtu/hr] | 8.5986 | 8.6582 | 10.3337 | 10.3937 | [6 empty] | 2021-05-06
ID_MA_SPLIT GNW HEATING COIL Heating Capacity [kBtu/hr] | SPLIT GNW HEATING COIL Heating Capacity [kBtu/hr] | 8.4684 | 8.5282 | 10.2644 | 10.3245 | [6 empty] | 2021-05-06
ID_MA_SPLIT OFFICE HEATING COIL Heating Capacity [kBtu/hr] | SPLIT OFFICE HEATING COIL Heating Capacity [kBtu/hr] | 20.9473 | 21.0584 | 23.4878 | 23.5703 | [6 empty] | 2021-05-06
ID_MA_SPLIT GNE HEATING COIL Heating Capacity [kBtu/hr] | SPLIT GNE HEATING COIL Heating Capacity [kBtu/hr] | 8.4874 | 8.5472 | 10.2644 | 10.3245 | [6 empty] | 2021-05-06
ID_MA_SPLIT GN1 HEATING COIL Heating Capacity [kBtu/hr] | SPLIT GN1 HEATING COIL Heating Capacity [kBtu/hr] | 6.3033 | 6.3632 | 7.6047 | 7.6647 | [6 empty] | 2021-05-06
ID_MA_SPLIT GN2 HEATING COIL Heating Capacity [kBtu/hr] | SPLIT GN2 HEATING COIL Heating Capacity [kBtu/hr] | 6.3039 | 6.3638 | 7.6047 | 7.6647 | [6 empty] | 2021-05-06
ID_MA_SPLIT GS1 HEATING COIL Heating Capacity [kBtu/hr] | SPLIT GS1 HEATING COIL Heating Capacity [kBtu/hr] | 6.3159 | 6.3756 | 7.5474 | 7.6073 | [6 empty] | 2021-05-06
ID_MA_SPLIT GS2 HEATING COIL Heating Capacity [kBtu/hr] | SPLIT GS2 HEATING COIL Heating Capacity [kBtu/hr] | 6.804 | 6.8661 | 8.0654 | 8.1263 | [6 empty] | 2021-05-06
ID_MA_SPLIT MSW HEATING COIL Heating Capacity [kBtu/hr] | SPLIT MSW HEATING COIL Heating Capacity [kBtu/hr] | 15.3045 | 15.4333 | 17.6256 | 17.7542 | [6 empty] | 2021-05-06
ID_MA_SPLIT MNW HEATING COIL Heating Capacity [kBtu/hr] | SPLIT MNW HEATING COIL Heating Capacity [kBtu/hr] | 15.2473 | 15.3758 | 17.7252 | 17.854 | [6 empty] | 2021-05-06
ID_MA_SPLIT MSE HEATING COIL Heating Capacity [kBtu/hr] | SPLIT MSE HEATING COIL Heating Capacity [kBtu/hr] | 15.3498 | 15.4786 | 17.6256 | 17.7542 | [6 empty] | 2021-05-06
ID_MA_SPLIT MNE HEATING COIL Heating Capacity [kBtu/hr] | SPLIT MNE HEATING COIL Heating Capacity [kBtu/hr] | 15.2926 | 15.4211 | 17.7252 | 17.854 | [6 empty] | 2021-05-06
ID_MA_SPLIT MN1 HEATING COIL Heating Capacity [kBtu/hr] | SPLIT MN1 HEATING COIL Heating Capacity [kBtu/hr] | 11.0972 | 11.0972 | 12.3639 | 12.4906 | [6 empty] | 2021-05-06
ID_MA_SPLIT MN2 HEATING COIL Heating Capacity [kBtu/hr] | SPLIT MN2 HEATING COIL Heating Capacity [kBtu/hr] | 11.0972 | 11.0972 | 12.3639 | 12.4906 | [6 empty] | 2021-05-06
ID_MA_SPLIT MS1 HEATING COIL Heating Capacity [kBtu/hr] | SPLIT MS1 HEATING COIL Heating Capacity [kBtu/hr] | 11.0972 | 11.0972 | 12.2743 | 12.401 | [6 empty] | 2021-05-06
ID_MA_SPLIT MS2 HEATING COIL Heating Capacity [kBtu/hr] | SPLIT MS2 HEATING COIL Heating Capacity [kBtu/hr] | 11.0972 | 11.0972 | 12.2743 | 12.401 | [6 empty] | 2021-05-06
ID_MA_SPLIT TSW HEATING COIL Heating Capacity [kBtu/hr] | SPLIT TSW HEATING COIL Heating Capacity [kBtu/hr] | 11.0466 | 11.1085 | 12.7771 | 12.8393 | [6 empty] | 2021-05-06
ID_MA_SPLIT TNW HEATING COIL Heating Capacity [kBtu/hr] | SPLIT TNW HEATING COIL Heating Capacity [kBtu/hr] | 11.0224 | 11.0844 | 12.8373 | 12.8995 | [6 empty] | 2021-05-06
ID_MA_SPLIT TSE HEATING COIL Heating Capacity [kBtu/hr] | SPLIT TSE HEATING COIL Heating Capacity [kBtu/hr] | 11.0708 | 11.1327 | 12.7771 | 12.8393 | [6 empty] | 2021-05-06
ID_MA_SPLIT TNE HEATING COIL Heating Capacity [kBtu/hr] | SPLIT TNE HEATING COIL Heating Capacity [kBtu/hr] | 11.0466 | 11.1086 | 12.8373 | 12.8995 | [6 empty] | 2021-05-06
ID_MA_SPLIT TN1 HEATING COIL Heating Capacity [kBtu/hr] | SPLIT TN1 HEATING COIL Heating Capacity [kBtu/hr] | 8.6148 | 8.6767 | 9.9936 | 10.0557 | [6 empty] | 2021-05-06
ID_MA_SPLIT TN2 HEATING COIL Heating Capacity [kBtu/hr] | SPLIT TN2 HEATING COIL Heating Capacity [kBtu/hr] | 8.6155 | 8.6774 | 9.9936 | 10.0557 | [6 empty] | 2021-05-06
ID_MA_SPLIT TS1 HEATING COIL Heating Capacity [kBtu/hr] | SPLIT TS1 HEATING COIL Heating Capacity [kBtu/hr] | 8.633 | 8.6949 | 9.927 | 9.9891 | [6 empty] | 2021-05-06
ID_MA_SPLIT TS2 HEATING COIL Heating Capacity [kBtu/hr] | SPLIT TS2 HEATING COIL Heating Capacity [kBtu/hr] | 8.6337 | 8.6955 | 9.927 | 9.9891 | [6 empty] | 2021-05-06
ID_MA_Split_GSW ERV Flag | Split_GSW ERV Flag | No | Yes | Yes | Yes | [6 empty] | 2021-05-06
ID_MA_Split_GNW ERV Flag | Split_GNW ERV Flag | No | Yes | Yes | Yes | [6 empty] | 2021-05-06
ID_MA_Split_GNE ERV Flag | Split_GNE ERV Flag | No | Yes | Yes | Yes | [6 empty] | 2021-05-06
ID_MA_Split_GN1 ERV Flag | Split_GN1 ERV Flag | No | Yes | Yes | Yes | [6 empty] | 2021-05-06
ID_MA_Split_GN2 ERV Flag | Split_GN2 ERV Flag | No | Yes | Yes | Yes | [6 empty] | 2021-05-06
ID_MA_Split_GS1 ERV Flag | Split_GS1 ERV Flag | No | Yes | Yes | Yes | [6 empty] | 2021-05-06
ID_MA_Split_GS2 ERV Flag | Split_GS2 ERV Flag | No | Yes | Yes | Yes | [6 empty] | 2021-05-06
ID_MA_Split_MSW ERV Flag | Split_MSW ERV Flag | No | Yes | Yes | Yes | [6 empty] | 2021-05-06
ID_MA_Split_MNW ERV Flag | Split_MNW ERV Flag | No | Yes | Yes | Yes | [6 empty] | 2021-05-06
ID_MA_Split_MSE ERV Flag | Split_MSE ERV Flag | No | Yes | Yes | Yes | [6 empty] | 2021-05-06
ID_MA_Split_MNE ERV Flag | Split_MNE ERV Flag | No | Yes | Yes | Yes | [6 empty] | 2021-05-06
ID_MA_Split_MN1 ERV Flag | Split_MN1 ERV Flag | No | Yes | Yes | Yes | [6 empty] | 2021-05-06
ID_MA_Split_MN2 ERV Flag | Split_MN2 ERV Flag | No | Yes | Yes | Yes | [6 empty] | 2021-05-06
ID_MA_Split_MS1 ERV Flag | Split_MS1 ERV Flag | No | Yes | Yes | Yes | [6 empty] | 2021-05-06
ID_MA_Split_MS2 ERV Flag | Split_MS2 ERV Flag | No | Yes | Yes | Yes | [6 empty] | 2021-05-06
ID_MA_Split_TSW ERV Flag | Split_TSW ERV Flag | No | No | No | No | [6 empty] | 2021-05-06
ID_MA_Split_TNW ERV Flag | Split_TNW ERV Flag | No | No | No | No | [6 empty] | 2021-05-06
ID_MA_Split_TSE ERV Flag | Split_TSE ERV Flag | No | Yes | Yes | Yes | [6 empty] | 2021-05-06
ID_MA_Split_TNE ERV Flag | Split_TNE ERV Flag | No | Yes | Yes | Yes | [6 empty] | 2021-05-06
ID_MA_Split_TN1 ERV Flag | Split_TN1 ERV Flag | No | Yes | Yes | Yes | [6 empty] | 2021-05-06
ID_MA_Split_TN2 ERV Flag | Split_TN2 ERV Flag | No | Yes | Yes | Yes | [6 empty] | 2021-05-06
ID_MA_Split_TS1 ERV Flag | Split_TS1 ERV Flag | No | Yes | Yes | Yes | [6 empty] | 2021-05-06
ID_MA_Split_TS2 ERV Flag | Split_TS2 ERV Flag | No | Yes | Yes | Yes | [6 empty] | 2021-05-06
id | item | Zone4A(IL-StLouis-MO) ASHRAE901-state_STD2016 | Zone4A(IL-StLouis-MO) ASHRAE901-state_STD2019 | Zone5A(IL-Peoria-IL) ASHRAE901-state_STD2016 | Zone5A(IL-Peoria-IL) ASHRAE901-state_STD2019 | [6 empty] | 2021-05-06
IL_SO_PSZ-AC:1 Cooling Capacity [ton] | PSZ-AC:1 Cooling Capacity [ton] | 2.0297 | 1.9336 | 1.9669 | 1.8723 | [6 empty] | 2021-05-06
IL_SO_PSZ-AC:2 Cooling Capacity [ton] | PSZ-AC:2 Cooling Capacity [ton] | 1.8157 | 1.7487 | 1.7066 | 1.6421 | [6 empty] | 2021-05-06
IL_SO_PSZ-AC:3 Cooling Capacity [ton] | PSZ-AC:3 Cooling Capacity [ton] | 1.2589 | 1.2191 | 1.1867 | 1.1478 | [6 empty] | 2021-05-06
IL_SO_PSZ-AC:4 Cooling Capacity [ton] | PSZ-AC:4 Cooling Capacity [ton] | 1.773 | 1.6842 | 1.6495 | 1.566 | [6 empty] | 2021-05-06
IL_SO_PSZ-AC:5 Cooling Capacity [ton] | PSZ-AC:5 Cooling Capacity [ton] | 1.4801 | 1.4385 | 1.4085 | 1.3681 | [6 empty] | 2021-05-06
IL_SO_PSZ-AC:1 Supply Flow Rate [cfm] | PSZ-AC:1 Supply Flow Rate [cfm] | 678.0416 | 614.4752 | 656.8528 | 614.4752 | [6 empty] | 2021-05-06
IL_SO_PSZ-AC:2 Supply Flow Rate [cfm] | PSZ-AC:2 Supply Flow Rate [cfm] | 614.4752 | 593.2864 | 593.2864 | 550.9088 | [6 empty] | 2021-05-06
IL_SO_PSZ-AC:3 Supply Flow Rate [cfm] | PSZ-AC:3 Supply Flow Rate [cfm] | 487.3424 | 466.1536 | 466.1536 | 444.9648 | [6 empty] | 2021-05-06
IL_SO_PSZ-AC:4 Supply Flow Rate [cfm] | PSZ-AC:4 Supply Flow Rate [cfm] | 593.2864 | 572.0976 | 550.9088 | 529.72 | [6 empty] | 2021-05-06
IL_SO_PSZ-AC:5 Supply Flow Rate [cfm] | PSZ-AC:5 Supply Flow Rate [cfm] | 572.0976 | 550.9088 | 550.9088 | 529.72 | [6 empty] | 2021-05-06
IL_SO_PSZ-AC:1 OA Rate [cfm] | PSZ-AC:1 OA Rate [cfm] | 136.9178 | 136.9178 | 136.9178 | 136.9178 | [6 empty] | 2021-05-06
IL_SO_PSZ-AC:2 OA Rate [cfm] | PSZ-AC:2 OA Rate [cfm] | 103.7925 | 103.7925 | 103.7925 | 103.7925 | [6 empty] | 2021-05-06
IL_SO_PSZ-AC:3 OA Rate [cfm] | PSZ-AC:3 OA Rate [cfm] | 61.5711 | 61.5711 | 61.5711 | 61.5711 | [6 empty] | 2021-05-06
IL_SO_PSZ-AC:4 OA Rate [cfm] | PSZ-AC:4 OA Rate [cfm] | 103.7925 | 103.7925 | 103.7925 | 103.7925 | [6 empty] | 2021-05-06
IL_SO_PSZ-AC:5 OA Rate [cfm] | PSZ-AC:5 OA Rate [cfm] | 61.5711 | 61.5711 | 61.5711 | 61.5711 | [6 empty] | 2021-05-06
IL_SO_PSZ-AC:1 heating Capacity [kBtu/hr] | PSZ-AC:1 heating Capacity [kBtu/hr] | 14.5075 | 14.5075 | 15.5831 | 15.5831 | [6 empty] | 2021-05-06
IL_SO_PSZ-AC:2 heating Capacity [kBtu/hr] | PSZ-AC:2 heating Capacity [kBtu/hr] | 20.6305 | 20.4123 | 22.1382 | 21.8841 | [6 empty] | 2021-05-06
IL_SO_PSZ-AC:3 heating Capacity [kBtu/hr] | PSZ-AC:3 heating Capacity [kBtu/hr] | 12.6384 | 12.5177 | 13.414 | 13.2796 | [6 empty] | 2021-05-06
IL_SO_PSZ-AC:4 heating Capacity [kBtu/hr] | PSZ-AC:4 heating Capacity [kBtu/hr] | 20.5381 | 20.351 | 21.9182 | 21.7104 | [6 empty] | 2021-05-06
IL_SO_PSZ-AC:5 heating Capacity [kBtu/hr] | PSZ-AC:5 heating Capacity [kBtu/hr] | 12.6977 | 12.5712 | 13.4796 | 13.339 | [6 empty] | 2021-05-06
id | item | Zone4A(IL-StLouis-MO) ASHRAE901-state_STD2016 | Zone4A(IL-StLouis-MO) ASHRAE901-state_STD2019 | Zone5A(IL-Peoria-IL) ASHRAE901-state_STD2016 | Zone5A(IL-Peoria-IL) ASHRAE901-state_STD2019 | [6 empty] | 2021-05-06
IL_LO_CAV_BAS Supply Flow Rate [cfm] | CAV_BAS Supply Flow Rate [cfm] | 11950.4832 | 11081.7424 | 11908.1056 | 11018.176 | [6 empty] | 2021-05-06
IL_LO_VAV_BOT WITH REHEAT Supply Flow Rate [cfm] | VAV_BOT WITH REHEAT Supply Flow Rate [cfm] | 20468.3808 | 19514.8848 | 20298.8704 | 19345.3744 | [6 empty] | 2021-05-06
IL_LO_VAV_MID WITH REHEAT Supply Flow Rate [cfm] | VAV_MID WITH REHEAT Supply Flow Rate [cfm] | 191440.8083 | 182372.0019 | 189406.6835 | 180380.2547 | [6 empty] | 2021-05-06
IL_LO_VAV_TOP WITH REHEAT Supply Flow Rate [cfm] | VAV_TOP WITH REHEAT Supply Flow Rate [cfm] | 20129.36 | 19324.1856 | 19917.472 | 19133.4864 | [6 empty] | 2021-05-06
IL_LO_Supply Air Temp. Reset Flag | Supply Air Temp. Reset Flag | Yes | Yes | Yes | Yes | [6 empty] | 2021-05-06
IL_LO_CAV_BAS OA Rate [cfm] | CAV_BAS OA Rate [cfm] | 2542.8255 | 2542.8255 | 2542.8255 | 2542.8255 | [6 empty] | 2021-05-06
IL_LO_VAV_BOT WITH REHEAT OA Rate [cfm] | VAV_BOT WITH REHEAT OA Rate [cfm] | 5377.8022 | 4302.174 | 5377.8022 | 4302.174 | [6 empty] | 2021-05-06
IL_LO_VAV_MID WITH REHEAT OA Rate [cfm] | VAV_MID WITH REHEAT OA Rate [cfm] | 53777.9373 | 43021.7396 | 53777.9373 | 43021.7396 | [6 empty] | 2021-05-06
IL_LO_VAV_TOP WITH REHEAT OA Rate [cfm] | VAV_TOP WITH REHEAT OA Rate [cfm] | 5377.8022 | 4302.174 | 5377.8022 | 4302.174 | [6 empty] | 2021-05-06
IL_LO_AIRLOOP DATACENTER BASEMENT OA Rate [cfm] | AIRLOOP DATACENTER BASEMENT OA Rate [cfm] | 716.9654 | 716.9654 | 716.9654 | 716.9654 | [6 empty] | 2021-05-06
IL_LO_VAV_bot_WITH_REHEAT ERV Flag | VAV_bot_WITH_REHEAT ERV Flag | Yes | Yes | Yes | Yes | [6 empty] | 2021-05-06
IL_LO_VAV_mid_WITH_REHEAT ERV Flag | VAV_mid_WITH_REHEAT ERV Flag | Yes | Yes | Yes | Yes | [6 empty] | 2021-05-06
IL_LO_VAV_top_WITH_REHEAT ERV Flag | VAV_top_WITH_REHEAT ERV Flag | Yes | Yes | Yes | Yes | [6 empty] | 2021-05-06
IL_LO_COOLSYS1 CHILLER1 Capacity [ton] | COOLSYS1 CHILLER1 Capacity [ton] | 456.1557 | 409.5927 | 448.7093 | 402.5962 | [6 empty] | 2021-05-06
IL_LO_COOLSYS1 CHILLER2 Capacity [ton] | COOLSYS1 CHILLER2 Capacity [ton] | 456.1557 | 409.5927 | 448.7093 | 402.5962 | [6 empty] | 2021-05-06
IL_LO_TOWERWATERSYS COOLTOWER 1 Capacity [ton] | TOWERWATERSYS COOLTOWER 1 Capacity [ton] | 432.9683 | 388.7828 | 425.906 | 382.1405 | [6 empty] | 2021-05-06
IL_LO_TOWERWATERSYS COOLTOWER 2 Capacity [ton] | TOWERWATERSYS COOLTOWER 2 Capacity [ton] | 432.9683 | 388.7828 | 425.906 | 382.1405 | [6 empty] | 2021-05-06
IL_LO_HEATSYS1 BOILER Capacity [MMBTU/h] | HEATSYS1 BOILER Capacity [MMBTU/h] | 4600.1432 | 4076.0788 | 4969.4943 | 4373.3747 | [6 empty] | 2021-05-06
IL_LO_COOLSYS1 PUMP Flow Rate [gal/min] | COOLSYS1 PUMP Flow Rate [gal/min] | 0 | 0 | 0 | 0 | [6 empty] | 2021-05-06
IL_LO_COOLSYS1 CHILLER1 PUMP Flow Rate [gal/min] | COOLSYS1 CHILLER1 PUMP Flow Rate [gal/min] | 718.9802 | 642.5642 | 707.2208 | 634.4219 | [6 empty] | 2021-05-06
IL_LO_COOLSYS1 CHILLER2 PUMP Flow Rate [gal/min] | COOLSYS1 CHILLER2 PUMP Flow Rate [gal/min] | 718.9802 | 642.5642 | 707.2208 | 634.4219 | [6 empty] | 2021-05-06
IL_LO_COOLSYS1 PUMP SECONDARY Flow Rate [gal/min] | COOLSYS1 PUMP SECONDARY Flow Rate [gal/min] | 1437.9619 | 1285.1283 | 1414.4432 | 1268.8437 | [6 empty] | 2021-05-06
IL_LO_HEATSYS1 PUMP Flow Rate [gal/min] | HEATSYS1 PUMP Flow Rate [gal/min] | 944.2402 | 836.6688 | 1020.0539 | 897.6926 | [6 empty] | 2021-05-06
IL_LO_TOWERWATERSYS PUMP Flow Rate [gal/min] | TOWERWATERSYS PUMP Flow Rate [gal/min] | 2516.7143 | 2259.7806 | 2475.5035 | 2221.1058 | [6 empty] | 2021-05-06
IL_LO_PLANT CIRC PUMP Flow Rate [gal/min] | PLANT CIRC PUMP Flow Rate [gal/min] | 211.223 | 210.4463 | 211.559 | 210.7808 | [6 empty] | 2021-05-06
IL_LO_COOLSYS1 PUMP SECONDARY Pressure setpoint reset [yes,no] | COOLSYS1 PUMP SECONDARY Pressure setpoint reset [yes,no] | pump_ride_on_curve | pump_ride_on_curve | pump_ride_on_curve | pump_ride_on_curve | [6 empty] | 2021-05-06
IL_LO_COOLSYS1 CHILLER1 PUMP Pump Power [hp] | COOLSYS1 CHILLER1 PUMP Pump Power [hp] | 3.8787 | 3.4321 | 3.8152 | 3.3886 | [6 empty] | 2021-05-06
IL_LO_COOLSYS1 CHILLER2 PUMP Pump Power [hp] | COOLSYS1 CHILLER2 PUMP Pump Power [hp] | 3.8787 | 3.4321 | 3.8152 | 3.3886 | [6 empty] | 2021-05-06
IL_LO_COOLSYS1 PUMP SECONDARY Pump Power [hp] | COOLSYS1 PUMP SECONDARY Pump Power [hp] | 23.2719 | 20.5925 | 22.8913 | 20.3316 | [6 empty] | 2021-05-06
IL_LO_HEATSYS1 PUMP Pump Power [hp] | HEATSYS1 PUMP Pump Power [hp] | 20.4103 | 17.906 | 22.0491 | 19.212 | [6 empty] | 2021-05-06
IL_LO_TOWERWATERSYS PUMP Pump Power [hp] | TOWERWATERSYS PUMP Pump Power [hp] | 45.0581 | 40.0581 | 44.3226 | 39.3739 | [6 empty] | 2021-05-06
IL_LO_PLANT CIRC PUMP Pump Power [hp] | PLANT CIRC PUMP Pump Power [hp] | 4.5579 | 4.4962 | 4.5651 | 4.5033 | [6 empty] | 2021-05-06
IL_LO_Datacenter PLANT CIRC PUMP Pump Power [hp] | Datacenter PLANT CIRC PUMP Pump Power [hp] | 4.5579 | 4.4962 | 4.5651 | 4.5033 | [6 empty] | 2021-05-06
IL_LO_ZN_VAV_BOXes_Max_Reheat_Water_Flow_GPM | ZN_VAV_BOXes_Max_Reheat_Water_Flow_GPM | 489.9475 | 471.1107 | 510.4969 | 491.055 | [6 empty] | 2021-05-06
IL_LO_COOLSYS1 PUMP SECONDARY VSD | COOLSYS1 PUMP SECONDARY VSD | No | No | No | No | [6 empty] | 2021-05-06
IL_LO_HEATSYS1 PUMP VSD | HEATSYS1 PUMP VSD | No | No | No | No | [6 empty] | 2021-05-06
IL_LO_DATACENTER BASEMENT Cooling Capacity [ton] | DATACENTER BASEMENT Cooling Capacity [ton] | 123.1994 | 122.8857 | 123.2102 | 122.8964 | [6 empty] | 2021-05-06
IL_LO_DATACENTER BOT Cooling Capacity [ton] | DATACENTER BOT Cooling Capacity [ton] | 2.7273 | 2.7034 | 2.7456 | 2.7216 | [6 empty] | 2021-05-06
IL_LO_DATACENTER MID Cooling Capacity [ton] | DATACENTER MID Cooling Capacity [ton] | 26.1324 | 25.922 | 26.333 | 26.1213 | [6 empty] | 2021-05-06
IL_LO_DATACENTER TOP Cooling Capacity [ton] | DATACENTER TOP Cooling Capacity [ton] | 2.666 | 2.6457 | 2.6828 | 2.6624 | [6 empty] | 2021-05-06
id | item | Zone4A(IL-StLouis-MO) ASHRAE901-state_STD2016 | Zone4A(IL-StLouis-MO) ASHRAE901-state_STD2019 | Zone5A(IL-Peoria-IL) ASHRAE901-state_STD2016 | Zone5A(IL-Peoria-IL) ASHRAE901-state_STD2019 | [6 empty] | 2021-05-06
IL_RS_PSZ-AC:1 Cooling Capacity [ton] | PSZ-AC:1 Cooling Capacity [ton] | 11.3604 | 10.9772 | 10.8187 | 10.4922 | [6 empty] | 2021-05-06
IL_RS_PSZ-AC:2 Cooling Capacity [ton] | PSZ-AC:2 Cooling Capacity [ton] | 53.6286 | 50.6436 | 52.3687 | 49.5185 | [6 empty] | 2021-05-06
IL_RS_PSZ-AC:3 Cooling Capacity [ton] | PSZ-AC:3 Cooling Capacity [ton] | 7.1931 | 7.0241 | 6.8232 | 6.6582 | [6 empty] | 2021-05-06
IL_RS_PSZ-AC:4 Cooling Capacity [ton] | PSZ-AC:4 Cooling Capacity [ton] | 5.9605 | 5.7725 | 5.5968 | 5.4313 | [6 empty] | 2021-05-06
IL_RS_PSZ-AC:1 Supply Flow Rate [cfm] | PSZ-AC:1 Supply Flow Rate [cfm] | 4280.1376 | 4025.872 | 4068.2496 | 3792.7952 | [6 empty] | 2021-05-06
IL_RS_PSZ-AC:2 Supply Flow Rate [cfm] | PSZ-AC:2 Supply Flow Rate [cfm] | 16103.488 | 15192.3696 | 15722.0896 | 14853.3488 | [6 empty] | 2021-05-06
IL_RS_PSZ-AC:3 Supply Flow Rate [cfm] | PSZ-AC:3 Supply Flow Rate [cfm] | 2436.712 | 2373.1456 | 2351.9568 | 2267.2016 | [6 empty] | 2021-05-06
IL_RS_PSZ-AC:4 Supply Flow Rate [cfm] | PSZ-AC:4 Supply Flow Rate [cfm] | 1906.992 | 1822.2368 | 1801.048 | 1716.2928 | [6 empty] | 2021-05-06
IL_RS_PSZ-AC:1 OA Rate [cfm] | PSZ-AC:1 OA Rate [cfm] | 490.669 | 490.669 | 490.669 | 490.669 | [6 empty] | 2021-05-06
IL_RS_PSZ-AC:2 OA Rate [cfm] | PSZ-AC:2 OA Rate [cfm] | 4005.1282 | 4005.1282 | 4005.1282 | 4005.1282 | [6 empty] | 2021-05-06
IL_RS_PSZ-AC:3 OA Rate [cfm] | PSZ-AC:3 OA Rate [cfm] | 377.3937 | 377.3937 | 377.3937 | 377.3937 | [6 empty] | 2021-05-06
IL_RS_PSZ-AC:4 OA Rate [cfm] | PSZ-AC:4 OA Rate [cfm] | 377.3937 | 377.3937 | 377.3937 | 377.3937 | [6 empty] | 2021-05-06
IL_RS_PSZ-AC:1 OA Damper [gravity, motorized] | PSZ-AC:1 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2021-05-06
IL_RS_PSZ-AC:2 OA Damper [gravity, motorized] | PSZ-AC:2 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2021-05-06
IL_RS_PSZ-AC:3 OA Damper [gravity, motorized] | PSZ-AC:3 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2021-05-06
IL_RS_PSZ-AC:4 OA Damper [gravity, motorized] | PSZ-AC:4 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2021-05-06
IL_RS_PSZ-AC:1 Heating Capacity [kBtu/hr] | PSZ-AC:1 Heating Capacity [kBtu/hr] | 189.8628 | 179.5287 | 184.4793 | 173.6433 | [6 empty] | 2021-05-06
IL_RS_PSZ-AC:2 Heating Capacity [kBtu/hr] | PSZ-AC:2 Heating Capacity [kBtu/hr] | 852.6338 | 814.6412 | 867.9555 | 831.6085 | [6 empty] | 2021-05-06
IL_RS_PSZ-AC:3 Heating Capacity [kBtu/hr] | PSZ-AC:3 Heating Capacity [kBtu/hr] | 115.0155 | 112.2588 | 114.1262 | 111.3918 | [6 empty] | 2021-05-06
IL_RS_PSZ-AC:4 Heating Capacity [kBtu/hr] | PSZ-AC:4 Heating Capacity [kBtu/hr] | 95.2672 | 92.3329 | 94.0899 | 91.1065 | [6 empty] | 2021-05-06
id | item | Zone4A(IL-StLouis-MO) ASHRAE901-state_STD2016 | Zone4A(IL-StLouis-MO) ASHRAE901-state_STD2019 | Zone5A(IL-Peoria-IL) ASHRAE901-state_STD2016 | Zone5A(IL-Peoria-IL) ASHRAE901-state_STD2019 | [6 empty] | 2021-05-06
IL_PS_VAV_POD_1 Cooling Capacity [ton] | VAV_POD_1 Cooling Capacity [ton] | 19.9864 | 19.1475 | 19.4828 | 18.8024 | [6 empty] | 2021-05-06
IL_PS_VAV_POD_2 Cooling Capacity [ton] | VAV_POD_2 Cooling Capacity [ton] | 19.7904 | 18.8772 | 19.2734 | 18.6208 | [6 empty] | 2021-05-06
IL_PS_VAV_POD_3 Cooling Capacity [ton] | VAV_POD_3 Cooling Capacity [ton] | 18.2881 | 17.3041 | 17.7834 | 16.9602 | [6 empty] | 2021-05-06
IL_PS_VAV_OTHER Cooling Capacity [ton] | VAV_OTHER Cooling Capacity [ton] | 28.0422 | 26.4424 | 27.4091 | 25.7852 | [6 empty] | 2021-05-06
IL_PS_PSZ-AC_1:6 Cooling Capacity [ton] | PSZ-AC_1:6 Cooling Capacity [ton] | 8.7122 | 8.3376 | 8.6751 | 8.2996 | [6 empty] | 2021-05-06
IL_PS_PSZ-AC_2:5 Cooling Capacity [ton] | PSZ-AC_2:5 Cooling Capacity [ton] | 5.7662 | 5.7396 | 5.6331 | 5.6061 | [6 empty] | 2021-05-06
IL_PS_PSZ-AC_2:7 Cooling Capacity [ton] | PSZ-AC_2:7 Cooling Capacity [ton] | 10.5074 | 10.5074 | 10.5074 | 10.5074 | [6 empty] | 2021-05-06
IL_PS_VAV_POD_1 Supply Flow Rate [cfm] | VAV_POD_1 Supply Flow Rate [cfm] | 5996.4304 | 5742.1648 | 5848.1088 | 5636.2208 | [6 empty] | 2021-05-06
IL_PS_VAV_POD_2 Supply Flow Rate [cfm] | VAV_POD_2 Supply Flow Rate [cfm] | 5932.864 | 5657.4096 | 5784.5424 | 5593.8432 | [6 empty] | 2021-05-06
IL_PS_VAV_POD_3 Supply Flow Rate [cfm] | VAV_POD_3 Supply Flow Rate [cfm] | 5487.8992 | 5191.256 | 5339.5776 | 5085.312 | [6 empty] | 2021-05-06
IL_PS_VAV_OTHER Supply Flow Rate [cfm] | VAV_OTHER Supply Flow Rate [cfm] | 8411.9536 | 7924.6112 | 8221.2544 | 7733.912 | [6 empty] | 2021-05-06
IL_PS_PSZ-AC_2:5 Supply Flow Rate [cfm] | PSZ-AC_2:5 Supply Flow Rate [cfm] | 1737.4816 | 1716.2928 | 1695.104 | 1673.9152 | [6 empty] | 2021-05-06
IL_PS_PSZ-AC_1:6 Supply Flow Rate [cfm] | PSZ-AC_1:6 Supply Flow Rate [cfm] | 2606.2224 | 2500.2784 | 2606.2224 | 2500.2784 | [6 empty] | 2021-05-06
IL_PS_PSZ-AC_2:7 Supply Flow Rate [cfm] | PSZ-AC_2:7 Supply Flow Rate [cfm] | 3157.1312 | 3157.1312 | 3157.1312 | 3157.1312 | [6 empty] | 2021-05-06
IL_PS_Supply Air Temp. Reset Flag | Supply Air Temp. Reset Flag | Yes | Yes | Yes | Yes | [6 empty] | 2021-05-06
IL_PS_VAV_POD_1 OA Rate [cfm] | VAV_POD_1 OA Rate [cfm] | 5994.9684 | 5745.8517 | 5846.4561 | 5642.2808 | [6 empty] | 2021-05-06
IL_PS_VAV_POD_2 OA Rate [cfm] | VAV_POD_2 OA Rate [cfm] | 5936.9111 | 5664.7197 | 5783.6313 | 5587.7832 | [6 empty] | 2021-05-06
IL_PS_VAV_POD_3 OA Rate [cfm] | VAV_POD_3 OA Rate [cfm] | 5487.9628 | 5192.6757 | 5335.7212 | 5089.4862 | [6 empty] | 2021-05-06
IL_PS_VAV_OTHER OA Rate [cfm] | VAV_OTHER OA Rate [cfm] | 3736.1787 | 2988.8921 | 3736.1787 | 2988.8921 | [6 empty] | 2021-05-06
IL_PS_PSZ-AC_2:5 OA Rate [cfm] | PSZ-AC_2:5 OA Rate [cfm] | 1152.7343 | 1152.7343 | 1152.7343 | 1152.7343 | [6 empty] | 2021-05-06
IL_PS_PSZ-AC_1:6 OA Rate [cfm] | PSZ-AC_1:6 OA Rate [cfm] | 539.9118 | 539.9118 | 539.9118 | 539.9118 | [6 empty] | 2021-05-06
IL_PS_PSZ-AC_2:7 OA Rate [cfm] | PSZ-AC_2:7 OA Rate [cfm] | 3153.0841 | 3153.0841 | 3153.0841 | 3153.0841 | [6 empty] | 2021-05-06
IL_PS_VAV_POD_1 OA Damper [gravity, motorized] | VAV_POD_1 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2021-05-06
IL_PS_VAV_POD_2 OA Damper [gravity, motorized] | VAV_POD_2 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2021-05-06
IL_PS_VAV_POD_3 OA Damper [gravity, motorized] | VAV_POD_3 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2021-05-06
IL_PS_VAV_OTHER OA Damper [gravity, motorized] | VAV_OTHER OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2021-05-06
IL_PS_PSZ-AC_2:5 OA Damper [gravity, motorized] | PSZ-AC_2:5 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2021-05-06
IL_PS_PSZ-AC_1:6 OA Damper [gravity, motorized] | PSZ-AC_1:6 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2021-05-06
IL_PS_PSZ-AC_2:7 OA Damper [gravity, motorized] | PSZ-AC_2:7 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2021-05-06
IL_PS_VAV_POD_1 (economizer) | VAV_POD_1 (economizer) | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialDryBulb | DifferentialDryBulb | [6 empty] | 2021-05-06
IL_PS_VAV_POD_2 (economizer) | VAV_POD_2 (economizer) | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialDryBulb | DifferentialDryBulb | [6 empty] | 2021-05-06
IL_PS_VAV_POD_3 (economizer) | VAV_POD_3 (economizer) | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialDryBulb | DifferentialDryBulb | [6 empty] | 2021-05-06
IL_PS_VAV_OTHER (economizer) | VAV_OTHER (economizer) | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialDryBulb | DifferentialDryBulb | [6 empty] | 2021-05-06
IL_PS_PSZ-AC_2:5 (economizer) | PSZ-AC_2:5 (economizer) | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialDryBulb | DifferentialDryBulb | [6 empty] | 2021-05-06
IL_PS_PSZ-AC_1:6 (economizer) | PSZ-AC_1:6 (economizer) | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialDryBulb | DifferentialDryBulb | [6 empty] | 2021-05-06
IL_PS_PSZ-AC_2:7 (economizer) | PSZ-AC_2:7 (economizer) | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialDryBulb | DifferentialDryBulb | [6 empty] | 2021-05-06
IL_PS_VAV_Pod_1_ERV Flag | VAV_Pod_1_ERV Flag | Yes | Yes | Yes | Yes | [6 empty] | 2021-05-06
IL_PS_VAV_Pod_2_ERV Flag | VAV_Pod_2_ERV Flag | Yes | Yes | Yes | Yes | [6 empty] | 2021-05-06
IL_PS_VAV_Pod_3_ERV Flag | VAV_Pod_3_ERV Flag | Yes | Yes | Yes | Yes | [6 empty] | 2021-05-06
IL_PS_VAV_OTHER_ERV Flag | VAV_OTHER_ERV Flag | Yes | Yes | Yes | Yes | [6 empty] | 2021-05-06
IL_PS_PSZ_AC_2_5_ERV Flag | PSZ_AC_2_5_ERV Flag | No | No | No | No | [6 empty] | 2021-05-06
IL_PS_PSZ_AC_2_7_ERV Flag | PSZ_AC_2_7_ERV Flag | Yes | Yes | Yes | Yes | [6 empty] | 2021-05-06
IL_PS_HEATSYS1 Capacity [MMBTU/h] | HEATSYS1 Capacity [MMBTU/h] | 1.1457 | 1.0918 | 1.2258 | 1.1777 | [6 empty] | 2021-05-06
IL_PS_HEATSYS1 Flow Rate [gal/min] | HEATSYS1 Flow Rate [gal/min] | 117.5856 | 112.0486 | 125.8075 | 120.8647 | [6 empty] | 2021-05-06
IL_PS_VAV_POD_1 Fan Power [hp] | VAV_POD_1 Fan Power [hp] | 8.8482 | 8.4769 | 8.6253 | 8.324 | [6 empty] | 2021-05-06
IL_PS_VAV_POD_2 Fan Power [hp] | VAV_POD_2 Fan Power [hp] | 8.7615 | 8.3572 | 8.5326 | 8.2437 | [6 empty] | 2021-05-06
IL_PS_VAV_POD_3 Fan Power [hp] | VAV_POD_3 Fan Power [hp] | 8.0964 | 7.6607 | 7.8729 | 7.5085 | [6 empty] | 2021-05-06
IL_PS_VAV_OTHER Fan Power [hp] | VAV_OTHER Fan Power [hp] | 12.3206 | 11.6177 | 12.0424 | 11.329 | [6 empty] | 2021-05-06
IL_PS_HEATSYS1 Pump Power [hp] | HEATSYS1 Pump Power [hp] | 2.5417 | 2.398 | 2.7194 | 2.5867 | [6 empty] | 2021-05-06
IL_PS_PSZ-AC_1:6 Heating Capacity [kBtu/hr] | PSZ-AC_1:6 Heating Capacity [kBtu/hr] | 215.6275 | 207.0427 | 218.531 | 209.9528 | [6 empty] | 2021-05-06
IL_PS_PSZ-AC_2:5 Heating Capacity [kBtu/hr] | PSZ-AC_2:5 Heating Capacity [kBtu/hr] | 143.0933 | 142.8043 | 150.6409 | 150.3479 | [6 empty] | 2021-05-06
IL_PS_PSZ-AC_2:7 Heating Capacity [kBtu/hr] | PSZ-AC_2:7 Heating Capacity [kBtu/hr] | 334.0931 | 334.0931 | 358.8652 | 358.8652 | [6 empty] | 2021-05-06
IL_PS_ZN_VAV_BOXes_Max_Reheat_Water_Flow_GPM | ZN_VAV_BOXes_Max_Reheat_Water_Flow_GPM | 74.6015 | 71.229 | 77.6827 | 74.9068 | [6 empty] | 2021-05-06
id | item | Zone4A(IL-StLouis-MO) ASHRAE901-state_STD2016 | Zone4A(IL-StLouis-MO) ASHRAE901-state_STD2019 | Zone5A(IL-Peoria-IL) ASHRAE901-state_STD2016 | Zone5A(IL-Peoria-IL) ASHRAE901-state_STD2019 | [6 empty] | 2021-05-06
IL_SH_SAC_FRONTOFFICE Cooling Capacity [ton] | SAC_FRONTOFFICE Cooling Capacity [ton] | 2.5713 | 2.4438 | 2.4515 | 2.3277 | [6 empty] | 2021-05-06
IL_SH_SAC_FRONTLOUNGE Cooling Capacity [ton] | SAC_FRONTLOUNGE Cooling Capacity [ton] | 6.3103 | 5.9991 | 6.1802 | 5.8697 | [6 empty] | 2021-05-06
IL_SH_SAC_MEETINGROOM Cooling Capacity [ton] | SAC_MEETINGROOM Cooling Capacity [ton] | 2.9907 | 2.897 | 2.9412 | 2.8482 | [6 empty] | 2021-05-06
IL_SH_SAC_EXC_EMPLGE_RESTRM Cooling Capacity [ton] | SAC_EXC_EMPLGE_RESTRM Cooling Capacity [ton] | 6.3538 | 6.3113 | 6.1818 | 6.1392 | [6 empty] | 2021-05-06
IL_SH_SAC_FO_ADDAQ SUPPLY FAN Supply Flow Rate [cfm] | SAC_FO_ADDAQ SUPPLY FAN Supply Flow Rate [cfm] | 805.1744 | 762.7968 | 783.9856 | 741.608 | [6 empty] | 2021-05-06
IL_SH_SAC_FL_ADDAQ SUPPLY FAN Supply Flow Rate [cfm] | SAC_FL_ADDAQ SUPPLY FAN Supply Flow Rate [cfm] | 1885.8032 | 1801.048 | 1864.6144 | 1758.6704 | [6 empty] | 2021-05-06
IL_SH_SAC_MR_ADDAQ SUPPLY FAN Supply Flow Rate [cfm] | SAC_MR_ADDAQ SUPPLY FAN Supply Flow Rate [cfm] | 889.9296 | 868.7408 | 889.9296 | 847.552 | [6 empty] | 2021-05-06
IL_SH_SAC_EXC_ADDAQ SUPPLY FAN Supply Flow Rate [cfm] | SAC_EXC_ADDAQ SUPPLY FAN Supply Flow Rate [cfm] | 2224.824 | 2224.824 | 2224.824 | 2203.6352 | [6 empty] | 2021-05-06
IL_SH_SAC_Exc_EmpLge_RestRm OA Rate [cfm] | SAC_Exc_EmpLge_RestRm OA Rate [cfm] | 199.9928 | 199.9928 | 199.9928 | 199.9928 | [6 empty] | 2021-05-06
IL_SH_SAC_FrontLounge OA Rate [cfm] | SAC_FrontLounge OA Rate [cfm] | 500.0133 | 500.0133 | 500.0133 | 500.0133 | [6 empty] | 2021-05-06
IL_SH_SAC_FrontOffice OA Rate [cfm] | SAC_FrontOffice OA Rate [cfm] | 119.2938 | 119.2938 | 119.2938 | 119.2938 | [6 empty] | 2021-05-06
IL_SH_SAC_MeetingRoom OA Rate [cfm] | SAC_MeetingRoom OA Rate [cfm] | 267.7629 | 267.7629 | 267.7629 | 267.7629 | [6 empty] | 2021-05-06
IL_SH_SAC_FrontLounge OA Damper [gravity, motorized] | SAC_FrontLounge OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2021-05-06
IL_SH_SAC_FrontOffice (economizer) | SAC_FrontOffice (economizer) | No | No | No | No | [6 empty] | 2021-05-06
IL_SH_SAC_FrontLounge (economizer) | SAC_FrontLounge (economizer) | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialDryBulb | DifferentialDryBulb | [6 empty] | 2021-05-06
IL_SH_SAC_MeetingRoom (economizer) | SAC_MeetingRoom (economizer) | No | No | No | No | [6 empty] | 2021-05-06
IL_SH_SAC_Exc_EmpLge_RestRm (economizer) | SAC_Exc_EmpLge_RestRm (economizer) | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialDryBulb | DifferentialDryBulb | [6 empty] | 2021-05-06
IL_SH_SAC_FRONTOFFICE Heating Capacity [kBtu/hr] | SAC_FRONTOFFICE Heating Capacity [kBtu/hr] | 37.7558 | 35.9329 | 37.5911 | 35.7838 | [6 empty] | 2021-05-06
IL_SH_SAC_FRONTLOUNGE Heating Capacity [kBtu/hr] | SAC_FRONTLOUNGE Heating Capacity [kBtu/hr] | 103.2367 | 99.8691 | 105.6053 | 102.256 | [6 empty] | 2021-05-06
IL_SH_SAC_MEETINGROOM Heating Capacity [kBtu/hr] | SAC_MEETINGROOM Heating Capacity [kBtu/hr] | 51.0788 | 50.0653 | 52.5786 | 51.5756 | [6 empty] | 2021-05-06
IL_SH_SAC_EXC_EMPLGE_RESTRM Heating Capacity [kBtu/hr] | SAC_EXC_EMPLGE_RESTRM Heating Capacity [kBtu/hr] | 94.549 | 93.8896 | 95.4671 | 94.806 | [6 empty] | 2021-05-06
id | item | Zone4A(IL-StLouis-MO) ASHRAE901-state_STD2016 | Zone4A(IL-StLouis-MO) ASHRAE901-state_STD2019 | Zone5A(IL-Peoria-IL) ASHRAE901-state_STD2016 | Zone5A(IL-Peoria-IL) ASHRAE901-state_STD2019 | [6 empty] | 2021-05-06
IL_MA_SPLIT GSW COOLING COIL Cooling Capacity [ton] | SPLIT GSW COOLING COIL Cooling Capacity [ton] | 0.99777 | 0.98378 | 0.93112 | 0.91673 | [6 empty] | 2021-05-06
IL_MA_SPLIT GNW COOLING COIL Cooling Capacity [ton] | SPLIT GNW COOLING COIL Cooling Capacity [ton] | 0.96349 | 0.94984 | 0.89225 | 0.87839 | [6 empty] | 2021-05-06
IL_MA_SPLIT OFFICE COOLING COIL Cooling Capacity [ton] | SPLIT OFFICE COOLING COIL Cooling Capacity [ton] | 1.8626 | 1.7479 | 1.7609 | 1.6297 | [6 empty] | 2021-05-06
IL_MA_SPLIT GNE COOLING COIL Cooling Capacity [ton] | SPLIT GNE COOLING COIL Cooling Capacity [ton] | 0.84857 | 0.83673 | 0.77816 | 0.76601 | [6 empty] | 2021-05-06
IL_MA_SPLIT GN1 COOLING COIL Cooling Capacity [ton] | SPLIT GN1 COOLING COIL Cooling Capacity [ton] | 0.71509 | 0.70543 | 0.65894 | 0.64917 | [6 empty] | 2021-05-06
IL_MA_SPLIT GN2 COOLING COIL Cooling Capacity [ton] | SPLIT GN2 COOLING COIL Cooling Capacity [ton] | 0.71286 | 0.70326 | 0.65663 | 0.64692 | [6 empty] | 2021-05-06
IL_MA_SPLIT GS1 COOLING COIL Cooling Capacity [ton] | SPLIT GS1 COOLING COIL Cooling Capacity [ton] | 0.75185 | 0.74177 | 0.70245 | 0.69195 | [6 empty] | 2021-05-06
IL_MA_SPLIT GS2 COOLING COIL Cooling Capacity [ton] | SPLIT GS2 COOLING COIL Cooling Capacity [ton] | 0.78258 | 0.76916 | 0.73295 | 0.71858 | [6 empty] | 2021-05-06
IL_MA_SPLIT MSW COOLING COIL Cooling Capacity [ton] | SPLIT MSW COOLING COIL Cooling Capacity [ton] | 2.3051 | 2.2732 | 2.2191 | 2.1869 | [6 empty] | 2021-05-06
IL_MA_SPLIT MNW COOLING COIL Cooling Capacity [ton] | SPLIT MNW COOLING COIL Cooling Capacity [ton] | 2.2431 | 2.2123 | 2.1516 | 2.1163 | [6 empty] | 2021-05-06
IL_MA_SPLIT MSE COOLING COIL Cooling Capacity [ton] | SPLIT MSE COOLING COIL Cooling Capacity [ton] | 2.0126 | 1.9856 | 1.9263 | 1.8983 | [6 empty] | 2021-05-06
IL_MA_SPLIT MNE COOLING COIL Cooling Capacity [ton] | SPLIT MNE COOLING COIL Cooling Capacity [ton] | 1.87 | 1.8396 | 1.7728 | 1.7377 | [6 empty] | 2021-05-06
IL_MA_SPLIT MN1 COOLING COIL Cooling Capacity [ton] | SPLIT MN1 COOLING COIL Cooling Capacity [ton] | 1.5324 | 1.5135 | 1.4524 | 1.4337 | [6 empty] | 2021-05-06
IL_MA_SPLIT MN2 COOLING COIL Cooling Capacity [ton] | SPLIT MN2 COOLING COIL Cooling Capacity [ton] | 1.5263 | 1.5077 | 1.4461 | 1.4275 | [6 empty] | 2021-05-06
IL_MA_SPLIT MS1 COOLING COIL Cooling Capacity [ton] | SPLIT MS1 COOLING COIL Cooling Capacity [ton] | 1.6004 | 1.5811 | 1.5302 | 1.5105 | [6 empty] | 2021-05-06
IL_MA_SPLIT MS2 COOLING COIL Cooling Capacity [ton] | SPLIT MS2 COOLING COIL Cooling Capacity [ton] | 1.5944 | 1.5753 | 1.524 | 1.5045 | [6 empty] | 2021-05-06
IL_MA_SPLIT TSW COOLING COIL Cooling Capacity [ton] | SPLIT TSW COOLING COIL Cooling Capacity [ton] | 1.4321 | 1.4148 | 1.3753 | 1.3579 | [6 empty] | 2021-05-06
IL_MA_SPLIT TNW COOLING COIL Cooling Capacity [ton] | SPLIT TNW COOLING COIL Cooling Capacity [ton] | 1.3942 | 1.3772 | 1.3332 | 1.3161 | [6 empty] | 2021-05-06
IL_MA_SPLIT TSE COOLING COIL Cooling Capacity [ton] | SPLIT TSE COOLING COIL Cooling Capacity [ton] | 1.2895 | 1.2756 | 1.2314 | 1.217 | [6 empty] | 2021-05-06
IL_MA_SPLIT TNE COOLING COIL Cooling Capacity [ton] | SPLIT TNE COOLING COIL Cooling Capacity [ton] | 1.2227 | 1.2097 | 1.1547 | 1.1432 | [6 empty] | 2021-05-06
IL_MA_SPLIT TN1 COOLING COIL Cooling Capacity [ton] | SPLIT TN1 COOLING COIL Cooling Capacity [ton] | 0.9682 | 0.95886 | 0.91535 | 0.90412 | [6 empty] | 2021-05-06
IL_MA_SPLIT TN2 COOLING COIL Cooling Capacity [ton] | SPLIT TN2 COOLING COIL Cooling Capacity [ton] | 0.99918 | 0.98915 | 0.94555 | 0.93561 | [6 empty] | 2021-05-06
IL_MA_SPLIT TS1 COOLING COIL Cooling Capacity [ton] | SPLIT TS1 COOLING COIL Cooling Capacity [ton] | 1.0638 | 1.0545 | 1.0178 | 1.0067 | [6 empty] | 2021-05-06
IL_MA_SPLIT TS2 COOLING COIL Cooling Capacity [ton] | SPLIT TS2 COOLING COIL Cooling Capacity [ton] | 1.0669 | 1.0561 | 1.02 | 1.0089 | [6 empty] | 2021-05-06
IL_MA_Split GN1 Furnace with DX Cooling OA Rate [cfm] | Split GN1 Furnace with DX Cooling OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | [6 empty] | 2021-05-06
IL_MA_Split GN2 Furnace with DX Cooling OA Rate [cfm] | Split GN2 Furnace with DX Cooling OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | [6 empty] | 2021-05-06
IL_MA_Split GNE Furnace with DX Cooling OA Rate [cfm] | Split GNE Furnace with DX Cooling OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | [6 empty] | 2021-05-06
IL_MA_Split GNW Furnace with DX Cooling OA Rate [cfm] | Split GNW Furnace with DX Cooling OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | [6 empty] | 2021-05-06
IL_MA_Split GS1 Furnace with DX Cooling OA Rate [cfm] | Split GS1 Furnace with DX Cooling OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | [6 empty] | 2021-05-06
IL_MA_Split GS2 Furnace with DX Cooling OA Rate [cfm] | Split GS2 Furnace with DX Cooling OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | [6 empty] | 2021-05-06
IL_MA_Split GSW Furnace with DX Cooling OA Rate [cfm] | Split GSW Furnace with DX Cooling OA Rate [cfm] | 56.9945 | 56.9945 | 56.9945 | 56.9945 | [6 empty] | 2021-05-06
IL_MA_Split MN1 Furnace with DX Cooling OA Rate [cfm] | Split MN1 Furnace with DX Cooling OA Rate [cfm] | 109.9824 | 109.9824 | 109.9824 | 109.9824 | [6 empty] | 2021-05-06
IL_MA_Split MN2 Furnace with DX Cooling OA Rate [cfm] | Split MN2 Furnace with DX Cooling OA Rate [cfm] | 109.9824 | 109.9824 | 109.9824 | 109.9824 | [6 empty] | 2021-05-06
IL_MA_Split MNE Furnace with DX Cooling OA Rate [cfm] | Split MNE Furnace with DX Cooling OA Rate [cfm] | 109.9824 | 109.9824 | 109.9824 | 109.9824 | [6 empty] | 2021-05-06
IL_MA_Split MNW Furnace with DX Cooling OA Rate [cfm] | Split MNW Furnace with DX Cooling OA Rate [cfm] | 109.9824 | 109.9824 | 109.9824 | 109.9824 | [6 empty] | 2021-05-06
IL_MA_Split MS1 Furnace with DX Cooling OA Rate [cfm] | Split MS1 Furnace with DX Cooling OA Rate [cfm] | 109.9824 | 109.9824 | 109.9824 | 109.9824 | [6 empty] | 2021-05-06
IL_MA_Split MS2 Furnace with DX Cooling OA Rate [cfm] | Split MS2 Furnace with DX Cooling OA Rate [cfm] | 109.9824 | 109.9824 | 109.9824 | 109.9824 | [6 empty] | 2021-05-06
IL_MA_Split MSE Furnace with DX Cooling OA Rate [cfm] | Split MSE Furnace with DX Cooling OA Rate [cfm] | 109.9824 | 109.9824 | 109.9824 | 109.9824 | [6 empty] | 2021-05-06
IL_MA_Split MSW Furnace with DX Cooling OA Rate [cfm] | Split MSW Furnace with DX Cooling OA Rate [cfm] | 109.9824 | 109.9824 | 109.9824 | 109.9824 | [6 empty] | 2021-05-06
IL_MA_Split Office Furnace with DX Cooling OA Rate [cfm] | Split Office Furnace with DX Cooling OA Rate [cfm] | 80.7372 | 80.7372 | 80.7372 | 80.7372 | [6 empty] | 2021-05-06
IL_MA_Split TN1 Furnace with DX Cooling OA Rate [cfm] | Split TN1 Furnace with DX Cooling OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | [6 empty] | 2021-05-06
IL_MA_Split TN2 Furnace with DX Cooling OA Rate [cfm] | Split TN2 Furnace with DX Cooling OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | [6 empty] | 2021-05-06
IL_MA_Split TNE Furnace with DX Cooling OA Rate [cfm] | Split TNE Furnace with DX Cooling OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | [6 empty] | 2021-05-06
IL_MA_Split TNW Furnace with DX Cooling OA Rate [cfm] | Split TNW Furnace with DX Cooling OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | [6 empty] | 2021-05-06
IL_MA_Split TS1 Furnace with DX Cooling OA Rate [cfm] | Split TS1 Furnace with DX Cooling OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | [6 empty] | 2021-05-06
IL_MA_Split TS2 Furnace with DX Cooling OA Rate [cfm] | Split TS2 Furnace with DX Cooling OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | [6 empty] | 2021-05-06
IL_MA_Split TSE Furnace with DX Cooling OA Rate [cfm] | Split TSE Furnace with DX Cooling OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | [6 empty] | 2021-05-06
IL_MA_Split TSW Furnace with DX Cooling OA Rate [cfm] | Split TSW Furnace with DX Cooling OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | [6 empty] | 2021-05-06
IL_MA_SPLIT GSW HEATING COIL Heating Capacity [kBtu/hr] | SPLIT GSW HEATING COIL Heating Capacity [kBtu/hr] | 10.2452 | 10.3039 | 11.2183 | 11.2773 | [6 empty] | 2021-05-06
IL_MA_SPLIT GNW HEATING COIL Heating Capacity [kBtu/hr] | SPLIT GNW HEATING COIL Heating Capacity [kBtu/hr] | 10.176 | 10.2348 | 11.0985 | 11.1576 | [6 empty] | 2021-05-06
IL_MA_SPLIT OFFICE HEATING COIL Heating Capacity [kBtu/hr] | SPLIT OFFICE HEATING COIL Heating Capacity [kBtu/hr] | 23.0975 | 23.1773 | 24.5791 | 24.6593 | [6 empty] | 2021-05-06
IL_MA_SPLIT GNE HEATING COIL Heating Capacity [kBtu/hr] | SPLIT GNE HEATING COIL Heating Capacity [kBtu/hr] | 10.1518 | 10.2106 | 11.0707 | 11.1298 | [6 empty] | 2021-05-06
IL_MA_SPLIT GN1 HEATING COIL Heating Capacity [kBtu/hr] | SPLIT GN1 HEATING COIL Heating Capacity [kBtu/hr] | 7.4479 | 7.5067 | 8.2483 | 8.3075 | [6 empty] | 2021-05-06
IL_MA_SPLIT GN2 HEATING COIL Heating Capacity [kBtu/hr] | SPLIT GN2 HEATING COIL Heating Capacity [kBtu/hr] | 7.4472 | 7.506 | 8.2475 | 8.3067 | [6 empty] | 2021-05-06
IL_MA_SPLIT GS1 HEATING COIL Heating Capacity [kBtu/hr] | SPLIT GS1 HEATING COIL Heating Capacity [kBtu/hr] | 7.3931 | 7.4517 | 8.2291 | 8.2881 | [6 empty] | 2021-05-06
IL_MA_SPLIT GS2 HEATING COIL Heating Capacity [kBtu/hr] | SPLIT GS2 HEATING COIL Heating Capacity [kBtu/hr] | 7.8991 | 7.9586 | 8.7413 | 8.8012 | [6 empty] | 2021-05-06
IL_MA_SPLIT MSW HEATING COIL Heating Capacity [kBtu/hr] | SPLIT MSW HEATING COIL Heating Capacity [kBtu/hr] | 18.7647 | 18.8935 | 20.0494 | 20.1785 | [6 empty] | 2021-05-06
IL_MA_SPLIT MNW HEATING COIL Heating Capacity [kBtu/hr] | SPLIT MNW HEATING COIL Heating Capacity [kBtu/hr] | 18.8621 | 18.9909 | 20.0612 | 20.1904 | [6 empty] | 2021-05-06
IL_MA_SPLIT MSE HEATING COIL Heating Capacity [kBtu/hr] | SPLIT MSE HEATING COIL Heating Capacity [kBtu/hr] | 18.7075 | 18.8364 | 19.9841 | 20.1132 | [6 empty] | 2021-05-06
IL_MA_SPLIT MNE HEATING COIL Heating Capacity [kBtu/hr] | SPLIT MNE HEATING COIL Heating Capacity [kBtu/hr] | 18.805 | 18.9337 | 19.9959 | 20.125 | [6 empty] | 2021-05-06
IL_MA_SPLIT MN1 HEATING COIL Heating Capacity [kBtu/hr] | SPLIT MN1 HEATING COIL Heating Capacity [kBtu/hr] | 12.985 | 13.1103 | 14.0617 | 14.1877 | [6 empty] | 2021-05-06
IL_MA_SPLIT MN2 HEATING COIL Heating Capacity [kBtu/hr] | SPLIT MN2 HEATING COIL Heating Capacity [kBtu/hr] | 12.9835 | 13.1087 | 14.06 | 14.186 | [6 empty] | 2021-05-06
IL_MA_SPLIT MS1 HEATING COIL Heating Capacity [kBtu/hr] | SPLIT MS1 HEATING COIL Heating Capacity [kBtu/hr] | 12.8964 | 13.0216 | 14.0591 | 14.1852 | [6 empty] | 2021-05-06
IL_MA_SPLIT MS2 HEATING COIL Heating Capacity [kBtu/hr] | SPLIT MS2 HEATING COIL Heating Capacity [kBtu/hr] | 12.8948 | 13.0201 | 14.0574 | 14.1835 | [6 empty] | 2021-05-06
IL_MA_SPLIT TSW HEATING COIL Heating Capacity [kBtu/hr] | SPLIT TSW HEATING COIL Heating Capacity [kBtu/hr] | 13.0824 | 13.144 | 14.0104 | 14.0723 | [6 empty] | 2021-05-06
IL_MA_SPLIT TNW HEATING COIL Heating Capacity [kBtu/hr] | SPLIT TNW HEATING COIL Heating Capacity [kBtu/hr] | 13.1395 | 13.2013 | 14.023 | 14.085 | [6 empty] | 2021-05-06
IL_MA_SPLIT TSE HEATING COIL Heating Capacity [kBtu/hr] | SPLIT TSE HEATING COIL Heating Capacity [kBtu/hr] | 13.0523 | 13.114 | 13.9758 | 14.0377 | [6 empty] | 2021-05-06
IL_MA_SPLIT TNE HEATING COIL Heating Capacity [kBtu/hr] | SPLIT TNE HEATING COIL Heating Capacity [kBtu/hr] | 13.1095 | 13.1712 | 13.9883 | 14.0504 | [6 empty] | 2021-05-06
IL_MA_SPLIT TN1 HEATING COIL Heating Capacity [kBtu/hr] | SPLIT TN1 HEATING COIL Heating Capacity [kBtu/hr] | 9.9378 | 9.9994 | 10.7711 | 10.833 | [6 empty] | 2021-05-06
IL_MA_SPLIT TN2 HEATING COIL Heating Capacity [kBtu/hr] | SPLIT TN2 HEATING COIL Heating Capacity [kBtu/hr] | 9.9369 | 9.9985 | 10.7702 | 10.832 | [6 empty] | 2021-05-06
IL_MA_SPLIT TS1 HEATING COIL Heating Capacity [kBtu/hr] | SPLIT TS1 HEATING COIL Heating Capacity [kBtu/hr] | 9.8736 | 9.9352 | 10.7525 | 10.8143 | [6 empty] | 2021-05-06
IL_MA_SPLIT TS2 HEATING COIL Heating Capacity [kBtu/hr] | SPLIT TS2 HEATING COIL Heating Capacity [kBtu/hr] | 9.8728 | 9.9343 | 10.7516 | 10.8133 | [6 empty] | 2021-05-06
IL_MA_Split_GSW ERV Flag | Split_GSW ERV Flag | Yes | Yes | Yes | Yes | [6 empty] | 2021-05-06
IL_MA_Split_GNW ERV Flag | Split_GNW ERV Flag | Yes | Yes | Yes | Yes | [6 empty] | 2021-05-06
IL_MA_Split_GNE ERV Flag | Split_GNE ERV Flag | Yes | Yes | Yes | Yes | [6 empty] | 2021-05-06
IL_MA_Split_GN1 ERV Flag | Split_GN1 ERV Flag | Yes | Yes | Yes | Yes | [6 empty] | 2021-05-06
IL_MA_Split_GN2 ERV Flag | Split_GN2 ERV Flag | Yes | Yes | Yes | Yes | [6 empty] | 2021-05-06
IL_MA_Split_GS1 ERV Flag | Split_GS1 ERV Flag | Yes | Yes | Yes | Yes | [6 empty] | 2021-05-06
IL_MA_Split_GS2 ERV Flag | Split_GS2 ERV Flag | Yes | Yes | Yes | Yes | [6 empty] | 2021-05-06
IL_MA_Split_MSW ERV Flag | Split_MSW ERV Flag | Yes | Yes | Yes | Yes | [6 empty] | 2021-05-06
IL_MA_Split_MNW ERV Flag | Split_MNW ERV Flag | Yes | Yes | Yes | Yes | [6 empty] | 2021-05-06
IL_MA_Split_MSE ERV Flag | Split_MSE ERV Flag | Yes | Yes | Yes | Yes | [6 empty] | 2021-05-06
IL_MA_Split_MNE ERV Flag | Split_MNE ERV Flag | Yes | Yes | Yes | Yes | [6 empty] | 2021-05-06
IL_MA_Split_MN1 ERV Flag | Split_MN1 ERV Flag | Yes | Yes | Yes | Yes | [6 empty] | 2021-05-06
IL_MA_Split_MN2 ERV Flag | Split_MN2 ERV Flag | Yes | Yes | Yes | Yes | [6 empty] | 2021-05-06
IL_MA_Split_MS1 ERV Flag | Split_MS1 ERV Flag | Yes | Yes | Yes | Yes | [6 empty] | 2021-05-06
IL_MA_Split_MS2 ERV Flag | Split_MS2 ERV Flag | Yes | Yes | Yes | Yes | [6 empty] | 2021-05-06
IL_MA_Split_TSW ERV Flag | Split_TSW ERV Flag | Yes | Yes | Yes | Yes | [6 empty] | 2021-05-06
IL_MA_Split_TNW ERV Flag | Split_TNW ERV Flag | Yes | Yes | Yes | Yes | [6 empty] | 2021-05-06
IL_MA_Split_TSE ERV Flag | Split_TSE ERV Flag | Yes | Yes | Yes | Yes | [6 empty] | 2021-05-06
IL_MA_Split_TNE ERV Flag | Split_TNE ERV Flag | Yes | Yes | Yes | Yes | [6 empty] | 2021-05-06
IL_MA_Split_TN1 ERV Flag | Split_TN1 ERV Flag | Yes | Yes | Yes | Yes | [6 empty] | 2021-05-06
IL_MA_Split_TN2 ERV Flag | Split_TN2 ERV Flag | Yes | Yes | Yes | Yes | [6 empty] | 2021-05-06
IL_MA_Split_TS1 ERV Flag | Split_TS1 ERV Flag | Yes | Yes | Yes | Yes | [6 empty] | 2021-05-06
IL_MA_Split_TS2 ERV Flag | Split_TS2 ERV Flag | Yes | Yes | Yes | Yes | [6 empty] | 2021-05-06
id | item | Zone4A(IN-Evansville-IN) ASHRAE901-state_STD2016 | Zone4A(IN-Evansville-IN) ASHRAE901-state_STD2019 | Zone5A(IN-FortWayne-IN) ASHRAE901-state_STD2016 | Zone5A(IN-FortWayne-IN) ASHRAE901-state_STD2019 | [6 empty] | 2021-05-06
IN_SO_PSZ-AC:1 Cooling Capacity [ton] | PSZ-AC:1 Cooling Capacity [ton] | 1.9753 | 1.8809 | 1.8476 | 1.7543 | [6 empty] | 2021-05-06
IN_SO_PSZ-AC:2 Cooling Capacity [ton] | PSZ-AC:2 Cooling Capacity [ton] | 1.7398 | 1.6757 | 1.5878 | 1.5247 | [6 empty] | 2021-05-06
IN_SO_PSZ-AC:3 Cooling Capacity [ton] | PSZ-AC:3 Cooling Capacity [ton] | 1.1733 | 1.1346 | 1.1443 | 1.1052 | [6 empty] | 2021-05-06
IN_SO_PSZ-AC:4 Cooling Capacity [ton] | PSZ-AC:4 Cooling Capacity [ton] | 1.6899 | 1.6188 | 1.5297 | 1.4451 | [6 empty] | 2021-05-06
IN_SO_PSZ-AC:5 Cooling Capacity [ton] | PSZ-AC:5 Cooling Capacity [ton] | 1.4096 | 1.3692 | 1.3147 | 1.2752 | [6 empty] | 2021-05-06
IN_SO_PSZ-AC:1 Supply Flow Rate [cfm] | PSZ-AC:1 Supply Flow Rate [cfm] | 656.8528 | 614.4752 | 656.8528 | 614.4752 | [6 empty] | 2021-05-06
IN_SO_PSZ-AC:2 Supply Flow Rate [cfm] | PSZ-AC:2 Supply Flow Rate [cfm] | 593.2864 | 572.0976 | 572.0976 | 550.9088 | [6 empty] | 2021-05-06
IN_SO_PSZ-AC:3 Supply Flow Rate [cfm] | PSZ-AC:3 Supply Flow Rate [cfm] | 466.1536 | 444.9648 | 466.1536 | 444.9648 | [6 empty] | 2021-05-06
IN_SO_PSZ-AC:4 Supply Flow Rate [cfm] | PSZ-AC:4 Supply Flow Rate [cfm] | 572.0976 | 550.9088 | 550.9088 | 508.5312 | [6 empty] | 2021-05-06
IN_SO_PSZ-AC:5 Supply Flow Rate [cfm] | PSZ-AC:5 Supply Flow Rate [cfm] | 550.9088 | 529.72 | 550.9088 | 529.72 | [6 empty] | 2021-05-06
IN_SO_PSZ-AC:1 OA Rate [cfm] | PSZ-AC:1 OA Rate [cfm] | 136.9178 | 136.9178 | 136.9178 | 136.9178 | [6 empty] | 2021-05-06
IN_SO_PSZ-AC:2 OA Rate [cfm] | PSZ-AC:2 OA Rate [cfm] | 103.7925 | 103.7925 | 103.7925 | 103.7925 | [6 empty] | 2021-05-06
IN_SO_PSZ-AC:3 OA Rate [cfm] | PSZ-AC:3 OA Rate [cfm] | 61.5711 | 61.5711 | 61.5711 | 61.5711 | [6 empty] | 2021-05-06
IN_SO_PSZ-AC:4 OA Rate [cfm] | PSZ-AC:4 OA Rate [cfm] | 103.7925 | 103.7925 | 103.7925 | 103.7925 | [6 empty] | 2021-05-06
IN_SO_PSZ-AC:5 OA Rate [cfm] | PSZ-AC:5 OA Rate [cfm] | 61.5711 | 61.5711 | 61.5711 | 61.5711 | [6 empty] | 2021-05-06
IN_SO_PSZ-AC:1 heating Capacity [kBtu/hr] | PSZ-AC:1 heating Capacity [kBtu/hr] | 14.3956 | 14.3956 | 15.3498 | 15.3498 | [6 empty] | 2021-05-06
IN_SO_PSZ-AC:2 heating Capacity [kBtu/hr] | PSZ-AC:2 heating Capacity [kBtu/hr] | 19.5355 | 19.3236 | 22.112 | 21.8603 | [6 empty] | 2021-05-06
IN_SO_PSZ-AC:3 heating Capacity [kBtu/hr] | PSZ-AC:3 heating Capacity [kBtu/hr] | 11.9293 | 11.8122 | 13.4152 | 13.2823 | [6 empty] | 2021-05-06
IN_SO_PSZ-AC:4 heating Capacity [kBtu/hr] | PSZ-AC:4 heating Capacity [kBtu/hr] | 19.4328 | 19.252 | 21.8943 | 21.6885 | [6 empty] | 2021-05-06
IN_SO_PSZ-AC:5 heating Capacity [kBtu/hr] | PSZ-AC:5 heating Capacity [kBtu/hr] | 11.9799 | 11.8577 | 13.4826 | 13.3432 | [6 empty] | 2021-05-06
id | item | Zone4A(IN-Evansville-IN) ASHRAE901-state_STD2016 | Zone4A(IN-Evansville-IN) ASHRAE901-state_STD2019 | Zone5A(IN-FortWayne-IN) ASHRAE901-state_STD2016 | Zone5A(IN-FortWayne-IN) ASHRAE901-state_STD2019 | [6 empty] | 2021-05-06
IN_LO_CAV_BAS Supply Flow Rate [cfm] | CAV_BAS Supply Flow Rate [cfm] | 11865.728 | 10996.9872 | 11886.9168 | 10996.9872 | [6 empty] | 2021-05-06
IN_LO_VAV_BOT WITH REHEAT Supply Flow Rate [cfm] | VAV_BOT WITH REHEAT Supply Flow Rate [cfm] | 20002.2272 | 19069.92 | 19790.3392 | 18836.8432 | [6 empty] | 2021-05-06
IN_LO_VAV_MID WITH REHEAT Supply Flow Rate [cfm] | VAV_MID WITH REHEAT Supply Flow Rate [cfm] | 186461.4403 | 177498.5779 | 183261.9315 | 174171.9363 | [6 empty] | 2021-05-06
IN_LO_VAV_TOP WITH REHEAT Supply Flow Rate [cfm] | VAV_TOP WITH REHEAT Supply Flow Rate [cfm] | 19684.3952 | 18879.2208 | 19642.0176 | 18858.032 | [6 empty] | 2021-05-06
IN_LO_Supply Air Temp. Reset Flag | Supply Air Temp. Reset Flag | Yes | Yes | Yes | Yes | [6 empty] | 2021-05-06
IN_LO_CAV_BAS OA Rate [cfm] | CAV_BAS OA Rate [cfm] | 2542.8255 | 2542.8255 | 2542.8255 | 2542.8255 | [6 empty] | 2021-05-06
IN_LO_VAV_BOT WITH REHEAT OA Rate [cfm] | VAV_BOT WITH REHEAT OA Rate [cfm] | 5377.8022 | 4302.174 | 5377.8022 | 4302.174 | [6 empty] | 2021-05-06
IN_LO_VAV_MID WITH REHEAT OA Rate [cfm] | VAV_MID WITH REHEAT OA Rate [cfm] | 53777.9373 | 43021.7396 | 53777.9373 | 43021.7396 | [6 empty] | 2021-05-06
IN_LO_VAV_TOP WITH REHEAT OA Rate [cfm] | VAV_TOP WITH REHEAT OA Rate [cfm] | 5377.8022 | 4302.174 | 5377.8022 | 4302.174 | [6 empty] | 2021-05-06
IN_LO_AIRLOOP DATACENTER BASEMENT OA Rate [cfm] | AIRLOOP DATACENTER BASEMENT OA Rate [cfm] | 716.9654 | 716.9654 | 716.9654 | 716.9654 | [6 empty] | 2021-05-06
IN_LO_VAV_bot_WITH_REHEAT ERV Flag | VAV_bot_WITH_REHEAT ERV Flag | Yes | Yes | Yes | Yes | [6 empty] | 2021-05-06
IN_LO_VAV_mid_WITH_REHEAT ERV Flag | VAV_mid_WITH_REHEAT ERV Flag | Yes | Yes | Yes | Yes | [6 empty] | 2021-05-06
IN_LO_VAV_top_WITH_REHEAT ERV Flag | VAV_top_WITH_REHEAT ERV Flag | Yes | Yes | Yes | Yes | [6 empty] | 2021-05-06
IN_LO_COOLSYS1 CHILLER1 Capacity [ton] | COOLSYS1 CHILLER1 Capacity [ton] | 443.2512 | 397.7786 | 407.4532 | 367.5624 | [6 empty] | 2021-05-06
IN_LO_COOLSYS1 CHILLER2 Capacity [ton] | COOLSYS1 CHILLER2 Capacity [ton] | 443.2512 | 397.7786 | 407.4532 | 367.5624 | [6 empty] | 2021-05-06
IN_LO_TOWERWATERSYS COOLTOWER 1 Capacity [ton] | TOWERWATERSYS COOLTOWER 1 Capacity [ton] | 420.7208 | 377.5592 | 386.7481 | 348.8898 | [6 empty] | 2021-05-06
IN_LO_TOWERWATERSYS COOLTOWER 2 Capacity [ton] | TOWERWATERSYS COOLTOWER 2 Capacity [ton] | 420.7208 | 377.5592 | 386.7481 | 348.8898 | [6 empty] | 2021-05-06
IN_LO_HEATSYS1 BOILER Capacity [MMBTU/h] | HEATSYS1 BOILER Capacity [MMBTU/h] | 4465.9185 | 3953.6495 | 4924.2271 | 4349.6735 | [6 empty] | 2021-05-06
IN_LO_COOLSYS1 PUMP Flow Rate [gal/min] | COOLSYS1 PUMP Flow Rate [gal/min] | 0 | 0 | 0 | 0 | [6 empty] | 2021-05-06
IN_LO_COOLSYS1 CHILLER1 PUMP Flow Rate [gal/min] | COOLSYS1 CHILLER1 PUMP Flow Rate [gal/min] | 698.6426 | 623.9987 | 642.011 | 579.0345 | [6 empty] | 2021-05-06
IN_LO_COOLSYS1 CHILLER2 PUMP Flow Rate [gal/min] | COOLSYS1 CHILLER2 PUMP Flow Rate [gal/min] | 698.6426 | 623.9987 | 642.011 | 579.0345 | [6 empty] | 2021-05-06
IN_LO_COOLSYS1 PUMP SECONDARY Flow Rate [gal/min] | COOLSYS1 PUMP SECONDARY Flow Rate [gal/min] | 1397.2852 | 1247.999 | 1284.0204 | 1158.069 | [6 empty] | 2021-05-06
IN_LO_HEATSYS1 PUMP Flow Rate [gal/min] | HEATSYS1 PUMP Flow Rate [gal/min] | 916.6892 | 811.5381 | 1010.7624 | 892.8281 | [6 empty] | 2021-05-06
IN_LO_TOWERWATERSYS PUMP Flow Rate [gal/min] | TOWERWATERSYS PUMP Flow Rate [gal/min] | 2445.3879 | 2194.6357 | 2247.8928 | 2027.8903 | [6 empty] | 2021-05-06
IN_LO_PLANT CIRC PUMP Flow Rate [gal/min] | PLANT CIRC PUMP Flow Rate [gal/min] | 210.0881 | 209.2496 | 210.7824 | 209.9391 | [6 empty] | 2021-05-06
IN_LO_COOLSYS1 PUMP SECONDARY Pressure setpoint reset [yes,no] | COOLSYS1 PUMP SECONDARY Pressure setpoint reset [yes,no] | pump_ride_on_curve | pump_ride_on_curve | pump_ride_on_curve | pump_ride_on_curve | [6 empty] | 2021-05-06
IN_LO_COOLSYS1 CHILLER1 PUMP Pump Power [hp] | COOLSYS1 CHILLER1 PUMP Pump Power [hp] | 3.7689 | 3.3329 | 3.4634 | 3.0928 | [6 empty] | 2021-05-06
IN_LO_COOLSYS1 CHILLER2 PUMP Pump Power [hp] | COOLSYS1 CHILLER2 PUMP Pump Power [hp] | 3.7689 | 3.3329 | 3.4634 | 3.0928 | [6 empty] | 2021-05-06
IN_LO_COOLSYS1 PUMP SECONDARY Pump Power [hp] | COOLSYS1 PUMP SECONDARY Pump Power [hp] | 22.6136 | 19.9976 | 20.7805 | 18.5566 | [6 empty] | 2021-05-06
IN_LO_HEATSYS1 PUMP Pump Power [hp] | HEATSYS1 PUMP Pump Power [hp] | 19.8148 | 17.3682 | 21.8482 | 19.1079 | [6 empty] | 2021-05-06
IN_LO_TOWERWATERSYS PUMP Pump Power [hp] | TOWERWATERSYS PUMP Pump Power [hp] | 43.7834 | 38.9027 | 40.2474 | 35.9476 | [6 empty] | 2021-05-06
IN_LO_PLANT CIRC PUMP Pump Power [hp] | PLANT CIRC PUMP Pump Power [hp] | 4.5334 | 4.4706 | 4.5484 | 4.4853 | [6 empty] | 2021-05-06
IN_LO_Datacenter PLANT CIRC PUMP Pump Power [hp] | Datacenter PLANT CIRC PUMP Pump Power [hp] | 4.5334 | 4.4706 | 4.5484 | 4.4853 | [6 empty] | 2021-05-06
IN_LO_ZN_VAV_BOXes_Max_Reheat_Water_Flow_GPM | ZN_VAV_BOXes_Max_Reheat_Water_Flow_GPM | 469.3364 | 451.2512 | 509.3114 | 491.7106 | [6 empty] | 2021-05-06
IN_LO_COOLSYS1 PUMP SECONDARY VSD | COOLSYS1 PUMP SECONDARY VSD | No | No | No | No | [6 empty] | 2021-05-06
IN_LO_HEATSYS1 PUMP VSD | HEATSYS1 PUMP VSD | No | No | No | No | [6 empty] | 2021-05-06
IN_LO_DATACENTER BASEMENT Cooling Capacity [ton] | DATACENTER BASEMENT Cooling Capacity [ton] | 122.8033 | 122.441 | 122.9372 | 122.5738 | [6 empty] | 2021-05-06
IN_LO_DATACENTER BOT Cooling Capacity [ton] | DATACENTER BOT Cooling Capacity [ton] | 2.6925 | 2.6689 | 2.7213 | 2.6975 | [6 empty] | 2021-05-06
IN_LO_DATACENTER MID Cooling Capacity [ton] | DATACENTER MID Cooling Capacity [ton] | 25.7692 | 25.5616 | 26.0879 | 25.8769 | [6 empty] | 2021-05-06
IN_LO_DATACENTER TOP Cooling Capacity [ton] | DATACENTER TOP Cooling Capacity [ton] | 2.6285 | 2.6084 | 2.6565 | 2.6362 | [6 empty] | 2021-05-06
id | item | Zone4A(IN-Evansville-IN) ASHRAE901-state_STD2016 | Zone4A(IN-Evansville-IN) ASHRAE901-state_STD2019 | Zone5A(IN-FortWayne-IN) ASHRAE901-state_STD2016 | Zone5A(IN-FortWayne-IN) ASHRAE901-state_STD2019 | [6 empty] | 2021-05-06
IN_RS_PSZ-AC:1 Cooling Capacity [ton] | PSZ-AC:1 Cooling Capacity [ton] | 10.9375 | 10.6001 | 10.1713 | 9.7753 | [6 empty] | 2021-05-06
IN_RS_PSZ-AC:2 Cooling Capacity [ton] | PSZ-AC:2 Cooling Capacity [ton] | 52.3438 | 49.6076 | 48.8654 | 46.7524 | [6 empty] | 2021-05-06
IN_RS_PSZ-AC:3 Cooling Capacity [ton] | PSZ-AC:3 Cooling Capacity [ton] | 6.8933 | 6.7305 | 6.2766 | 6.1164 | [6 empty] | 2021-05-06
IN_RS_PSZ-AC:4 Cooling Capacity [ton] | PSZ-AC:4 Cooling Capacity [ton] | 5.6703 | 5.5109 | 5.0573 | 4.8836 | [6 empty] | 2021-05-06
IN_RS_PSZ-AC:1 Supply Flow Rate [cfm] | PSZ-AC:1 Supply Flow Rate [cfm] | 4131.816 | 3898.7392 | 3919.928 | 3623.2848 | [6 empty] | 2021-05-06
IN_RS_PSZ-AC:2 Supply Flow Rate [cfm] | PSZ-AC:2 Supply Flow Rate [cfm] | 15700.9008 | 14895.7264 | 15404.2576 | 14429.5728 | [6 empty] | 2021-05-06
IN_RS_PSZ-AC:3 Supply Flow Rate [cfm] | PSZ-AC:3 Supply Flow Rate [cfm] | 2373.1456 | 2288.3904 | 2246.0128 | 2182.4464 | [6 empty] | 2021-05-06
IN_RS_PSZ-AC:4 Supply Flow Rate [cfm] | PSZ-AC:4 Supply Flow Rate [cfm] | 1822.2368 | 1758.6704 | 1695.104 | 1610.3488 | [6 empty] | 2021-05-06
IN_RS_PSZ-AC:1 OA Rate [cfm] | PSZ-AC:1 OA Rate [cfm] | 490.669 | 490.669 | 490.669 | 490.669 | [6 empty] | 2021-05-06
IN_RS_PSZ-AC:2 OA Rate [cfm] | PSZ-AC:2 OA Rate [cfm] | 4005.1282 | 4005.1282 | 4005.1282 | 4005.1282 | [6 empty] | 2021-05-06
IN_RS_PSZ-AC:3 OA Rate [cfm] | PSZ-AC:3 OA Rate [cfm] | 377.3937 | 377.3937 | 377.3937 | 377.3937 | [6 empty] | 2021-05-06
IN_RS_PSZ-AC:4 OA Rate [cfm] | PSZ-AC:4 OA Rate [cfm] | 377.3937 | 377.3937 | 377.3937 | 377.3937 | [6 empty] | 2021-05-06
IN_RS_PSZ-AC:1 OA Damper [gravity, motorized] | PSZ-AC:1 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2021-05-06
IN_RS_PSZ-AC:2 OA Damper [gravity, motorized] | PSZ-AC:2 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2021-05-06
IN_RS_PSZ-AC:3 OA Damper [gravity, motorized] | PSZ-AC:3 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2021-05-06
IN_RS_PSZ-AC:4 OA Damper [gravity, motorized] | PSZ-AC:4 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2021-05-06
IN_RS_PSZ-AC:1 Heating Capacity [kBtu/hr] | PSZ-AC:1 Heating Capacity [kBtu/hr] | 184.6341 | 174.3289 | 176.9715 | 165.4135 | [6 empty] | 2021-05-06
IN_RS_PSZ-AC:2 Heating Capacity [kBtu/hr] | PSZ-AC:2 Heating Capacity [kBtu/hr] | 835.3168 | 801.513 | 844.613 | 807.0453 | [6 empty] | 2021-05-06
IN_RS_PSZ-AC:3 Heating Capacity [kBtu/hr] | PSZ-AC:3 Heating Capacity [kBtu/hr] | 112.3666 | 109.6726 | 109.7466 | 107.0623 | [6 empty] | 2021-05-06
IN_RS_PSZ-AC:4 Heating Capacity [kBtu/hr] | PSZ-AC:4 Heating Capacity [kBtu/hr] | 92.4517 | 89.6038 | 89.4319 | 86.3294 | [6 empty] | 2021-05-06
id | item | Zone4A(IN-Evansville-IN) ASHRAE901-state_STD2016 | Zone4A(IN-Evansville-IN) ASHRAE901-state_STD2019 | Zone5A(IN-FortWayne-IN) ASHRAE901-state_STD2016 | Zone5A(IN-FortWayne-IN) ASHRAE901-state_STD2019 | [6 empty] | 2021-05-06
IN_PS_VAV_POD_1 Cooling Capacity [ton] | VAV_POD_1 Cooling Capacity [ton] | 19.4256 | 18.7601 | 19.2457 | 18.5461 | [6 empty] | 2021-05-06
IN_PS_VAV_POD_2 Cooling Capacity [ton] | VAV_POD_2 Cooling Capacity [ton] | 19.1956 | 18.571 | 19.0407 | 18.4588 | [6 empty] | 2021-05-06
IN_PS_VAV_POD_3 Cooling Capacity [ton] | VAV_POD_3 Cooling Capacity [ton] | 17.7421 | 16.9011 | 17.5507 | 16.7079 | [6 empty] | 2021-05-06
IN_PS_VAV_OTHER Cooling Capacity [ton] | VAV_OTHER Cooling Capacity [ton] | 27.2471 | 25.6968 | 27.0826 | 25.4005 | [6 empty] | 2021-05-06
IN_PS_PSZ-AC_1:6 Cooling Capacity [ton] | PSZ-AC_1:6 Cooling Capacity [ton] | 8.6033 | 8.2317 | 8.3802 | 8.1158 | [6 empty] | 2021-05-06
IN_PS_PSZ-AC_2:5 Cooling Capacity [ton] | PSZ-AC_2:5 Cooling Capacity [ton] | 5.6054 | 5.5839 | 5.5677 | 5.5429 | [6 empty] | 2021-05-06
IN_PS_PSZ-AC_2:7 Cooling Capacity [ton] | PSZ-AC_2:7 Cooling Capacity [ton] | 10.5074 | 10.5074 | 10.5074 | 10.5074 | [6 empty] | 2021-05-06
IN_PS_VAV_POD_1 Supply Flow Rate [cfm] | VAV_POD_1 Supply Flow Rate [cfm] | 5826.92 | 5636.2208 | 5784.5424 | 5572.6544 | [6 empty] | 2021-05-06
IN_PS_VAV_POD_2 Supply Flow Rate [cfm] | VAV_POD_2 Supply Flow Rate [cfm] | 5763.3536 | 5572.6544 | 5720.976 | 5530.2768 | [6 empty] | 2021-05-06
IN_PS_VAV_POD_3 Supply Flow Rate [cfm] | VAV_POD_3 Supply Flow Rate [cfm] | 5318.3888 | 5064.1232 | 5276.0112 | 5021.7456 | [6 empty] | 2021-05-06
IN_PS_VAV_OTHER Supply Flow Rate [cfm] | VAV_OTHER Supply Flow Rate [cfm] | 8178.8768 | 7712.7232 | 8136.4992 | 7627.968 | [6 empty] | 2021-05-06
IN_PS_PSZ-AC_2:5 Supply Flow Rate [cfm] | PSZ-AC_2:5 Supply Flow Rate [cfm] | 1673.9152 | 1673.9152 | 1673.9152 | 1673.9152 | [6 empty] | 2021-05-06
IN_PS_PSZ-AC_1:6 Supply Flow Rate [cfm] | PSZ-AC_1:6 Supply Flow Rate [cfm] | 2585.0336 | 2479.0896 | 2606.2224 | 2479.0896 | [6 empty] | 2021-05-06
IN_PS_PSZ-AC_2:7 Supply Flow Rate [cfm] | PSZ-AC_2:7 Supply Flow Rate [cfm] | 3157.1312 | 3157.1312 | 3157.1312 | 3157.1312 | [6 empty] | 2021-05-06
IN_PS_Supply Air Temp. Reset Flag | Supply Air Temp. Reset Flag | Yes | Yes | Yes | Yes | [6 empty] | 2021-05-06
IN_PS_VAV_POD_1 OA Rate [cfm] | VAV_POD_1 OA Rate [cfm] | 5828.4244 | 5629.5887 | 5775.3253 | 5565.3655 | [6 empty] | 2021-05-06
IN_PS_VAV_POD_2 OA Rate [cfm] | VAV_POD_2 OA Rate [cfm] | 5760.2812 | 5572.8663 | 5713.793 | 5539.1761 | [6 empty] | 2021-05-06
IN_PS_VAV_POD_3 OA Rate [cfm] | VAV_POD_3 OA Rate [cfm] | 5324.1098 | 5071.7512 | 5266.6669 | 5013.7786 | [6 empty] | 2021-05-06
IN_PS_VAV_OTHER OA Rate [cfm] | VAV_OTHER OA Rate [cfm] | 3736.1787 | 2988.8921 | 3736.1787 | 2988.8921 | [6 empty] | 2021-05-06
IN_PS_PSZ-AC_2:5 OA Rate [cfm] | PSZ-AC_2:5 OA Rate [cfm] | 1152.7343 | 1152.7343 | 1152.7343 | 1152.7343 | [6 empty] | 2021-05-06
IN_PS_PSZ-AC_1:6 OA Rate [cfm] | PSZ-AC_1:6 OA Rate [cfm] | 539.9118 | 539.9118 | 539.9118 | 539.9118 | [6 empty] | 2021-05-06
IN_PS_PSZ-AC_2:7 OA Rate [cfm] | PSZ-AC_2:7 OA Rate [cfm] | 3153.0841 | 3153.0841 | 3153.0841 | 3153.0841 | [6 empty] | 2021-05-06
IN_PS_VAV_POD_1 OA Damper [gravity, motorized] | VAV_POD_1 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2021-05-06
IN_PS_VAV_POD_2 OA Damper [gravity, motorized] | VAV_POD_2 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2021-05-06
IN_PS_VAV_POD_3 OA Damper [gravity, motorized] | VAV_POD_3 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2021-05-06
IN_PS_VAV_OTHER OA Damper [gravity, motorized] | VAV_OTHER OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2021-05-06
IN_PS_PSZ-AC_2:5 OA Damper [gravity, motorized] | PSZ-AC_2:5 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2021-05-06
IN_PS_PSZ-AC_1:6 OA Damper [gravity, motorized] | PSZ-AC_1:6 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2021-05-06
IN_PS_PSZ-AC_2:7 OA Damper [gravity, motorized] | PSZ-AC_2:7 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2021-05-06
IN_PS_VAV_POD_1 (economizer) | VAV_POD_1 (economizer) | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialDryBulb | DifferentialDryBulb | [6 empty] | 2021-05-06
IN_PS_VAV_POD_2 (economizer) | VAV_POD_2 (economizer) | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialDryBulb | DifferentialDryBulb | [6 empty] | 2021-05-06
IN_PS_VAV_POD_3 (economizer) | VAV_POD_3 (economizer) | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialDryBulb | DifferentialDryBulb | [6 empty] | 2021-05-06
IN_PS_VAV_OTHER (economizer) | VAV_OTHER (economizer) | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialDryBulb | DifferentialDryBulb | [6 empty] | 2021-05-06
IN_PS_PSZ-AC_2:5 (economizer) | PSZ-AC_2:5 (economizer) | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialDryBulb | DifferentialDryBulb | [6 empty] | 2021-05-06
IN_PS_PSZ-AC_1:6 (economizer) | PSZ-AC_1:6 (economizer) | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialDryBulb | DifferentialDryBulb | [6 empty] | 2021-05-06
IN_PS_PSZ-AC_2:7 (economizer) | PSZ-AC_2:7 (economizer) | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialDryBulb | DifferentialDryBulb | [6 empty] | 2021-05-06
IN_PS_VAV_Pod_1_ERV Flag | VAV_Pod_1_ERV Flag | Yes | Yes | Yes | Yes | [6 empty] | 2021-05-06
IN_PS_VAV_Pod_2_ERV Flag | VAV_Pod_2_ERV Flag | Yes | Yes | Yes | Yes | [6 empty] | 2021-05-06
IN_PS_VAV_Pod_3_ERV Flag | VAV_Pod_3_ERV Flag | Yes | Yes | Yes | Yes | [6 empty] | 2021-05-06
IN_PS_VAV_OTHER_ERV Flag | VAV_OTHER_ERV Flag | Yes | Yes | Yes | Yes | [6 empty] | 2021-05-06
IN_PS_PSZ_AC_2_5_ERV Flag | PSZ_AC_2_5_ERV Flag | No | No | No | No | [6 empty] | 2021-05-06
IN_PS_PSZ_AC_2_7_ERV Flag | PSZ_AC_2_7_ERV Flag | Yes | Yes | Yes | Yes | [6 empty] | 2021-05-06
IN_PS_HEATSYS1 Capacity [MMBTU/h] | HEATSYS1 Capacity [MMBTU/h] | 1.0921 | 1.0448 | 1.2054 | 1.1585 | [6 empty] | 2021-05-06
IN_PS_HEATSYS1 Flow Rate [gal/min] | HEATSYS1 Flow Rate [gal/min] | 112.081 | 107.2282 | 123.7154 | 118.8957 | [6 empty] | 2021-05-06
IN_PS_VAV_POD_1 Fan Power [hp] | VAV_POD_1 Fan Power [hp] | 8.6 | 8.3053 | 8.5203 | 8.2106 | [6 empty] | 2021-05-06
IN_PS_VAV_POD_2 Fan Power [hp] | VAV_POD_2 Fan Power [hp] | 8.4981 | 8.2216 | 8.4296 | 8.172 | [6 empty] | 2021-05-06
IN_PS_VAV_POD_3 Fan Power [hp] | VAV_POD_3 Fan Power [hp] | 7.8546 | 7.4824 | 7.7699 | 7.3968 | [6 empty] | 2021-05-06
IN_PS_VAV_OTHER Fan Power [hp] | VAV_OTHER Fan Power [hp] | 11.9713 | 11.2901 | 11.899 | 11.1599 | [6 empty] | 2021-05-06
IN_PS_HEATSYS1 Pump Power [hp] | HEATSYS1 Pump Power [hp] | 2.4227 | 2.2949 | 2.6742 | 2.5445 | [6 empty] | 2021-05-06
IN_PS_PSZ-AC_1:6 Heating Capacity [kBtu/hr] | PSZ-AC_1:6 Heating Capacity [kBtu/hr] | 213.751 | 205.177 | 216.7667 | 208.2115 | [6 empty] | 2021-05-06
IN_PS_PSZ-AC_2:5 Heating Capacity [kBtu/hr] | PSZ-AC_2:5 Heating Capacity [kBtu/hr] | 140.5319 | 140.2968 | 147.8726 | 147.6049 | [6 empty] | 2021-05-06
IN_PS_PSZ-AC_2:7 Heating Capacity [kBtu/hr] | PSZ-AC_2:7 Heating Capacity [kBtu/hr] | 331.5175 | 331.5175 | 353.4911 | 353.4911 | [6 empty] | 2021-05-06
IN_PS_ZN_VAV_BOXes_Max_Reheat_Water_Flow_GPM | ZN_VAV_BOXes_Max_Reheat_Water_Flow_GPM | 71.247 | 68.1924 | 77.2883 | 74.5996 | [6 empty] | 2021-05-06
id | item | Zone4A(IN-Evansville-IN) ASHRAE901-state_STD2016 | Zone4A(IN-Evansville-IN) ASHRAE901-state_STD2019 | Zone5A(IN-FortWayne-IN) ASHRAE901-state_STD2016 | Zone5A(IN-FortWayne-IN) ASHRAE901-state_STD2019 | [6 empty] | 2021-05-06
IN_SH_SAC_FRONTOFFICE Cooling Capacity [ton] | SAC_FRONTOFFICE Cooling Capacity [ton] | 2.4512 | 2.3268 | 2.3187 | 2.185 | [6 empty] | 2021-05-06
IN_SH_SAC_FRONTLOUNGE Cooling Capacity [ton] | SAC_FRONTLOUNGE Cooling Capacity [ton] | 6.1764 | 5.8671 | 6.1482 | 5.8351 | [6 empty] | 2021-05-06
IN_SH_SAC_MEETINGROOM Cooling Capacity [ton] | SAC_MEETINGROOM Cooling Capacity [ton] | 2.9181 | 2.8393 | 2.9301 | 2.8363 | [6 empty] | 2021-05-06
IN_SH_SAC_EXC_EMPLGE_RESTRM Cooling Capacity [ton] | SAC_EXC_EMPLGE_RESTRM Cooling Capacity [ton] | 6.2068 | 6.1636 | 5.9446 | 5.893 | [6 empty] | 2021-05-06
IN_SH_SAC_FO_ADDAQ SUPPLY FAN Supply Flow Rate [cfm] | SAC_FO_ADDAQ SUPPLY FAN Supply Flow Rate [cfm] | 783.9856 | 741.608 | 783.9856 | 720.4192 | [6 empty] | 2021-05-06
IN_SH_SAC_FL_ADDAQ SUPPLY FAN Supply Flow Rate [cfm] | SAC_FL_ADDAQ SUPPLY FAN Supply Flow Rate [cfm] | 1843.4256 | 1758.6704 | 1843.4256 | 1758.6704 | [6 empty] | 2021-05-06
IN_SH_SAC_MR_ADDAQ SUPPLY FAN Supply Flow Rate [cfm] | SAC_MR_ADDAQ SUPPLY FAN Supply Flow Rate [cfm] | 868.7408 | 847.552 | 868.7408 | 847.552 | [6 empty] | 2021-05-06
IN_SH_SAC_EXC_ADDAQ SUPPLY FAN Supply Flow Rate [cfm] | SAC_EXC_ADDAQ SUPPLY FAN Supply Flow Rate [cfm] | 2203.6352 | 2203.6352 | 2224.824 | 2203.6352 | [6 empty] | 2021-05-06
IN_SH_SAC_Exc_EmpLge_RestRm OA Rate [cfm] | SAC_Exc_EmpLge_RestRm OA Rate [cfm] | 199.9928 | 199.9928 | 199.9928 | 199.9928 | [6 empty] | 2021-05-06
IN_SH_SAC_FrontLounge OA Rate [cfm] | SAC_FrontLounge OA Rate [cfm] | 500.0133 | 500.0133 | 500.0133 | 500.0133 | [6 empty] | 2021-05-06
IN_SH_SAC_FrontOffice OA Rate [cfm] | SAC_FrontOffice OA Rate [cfm] | 119.2938 | 119.2938 | 119.2938 | 119.2938 | [6 empty] | 2021-05-06
IN_SH_SAC_MeetingRoom OA Rate [cfm] | SAC_MeetingRoom OA Rate [cfm] | 267.7629 | 267.7629 | 267.7629 | 267.7629 | [6 empty] | 2021-05-06
IN_SH_SAC_FrontLounge OA Damper [gravity, motorized] | SAC_FrontLounge OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2021-05-06
IN_SH_SAC_FrontOffice (economizer) | SAC_FrontOffice (economizer) | No | No | No | No | [6 empty] | 2021-05-06
IN_SH_SAC_FrontLounge (economizer) | SAC_FrontLounge (economizer) | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialDryBulb | DifferentialDryBulb | [6 empty] | 2021-05-06
IN_SH_SAC_MeetingRoom (economizer) | SAC_MeetingRoom (economizer) | No | No | No | No | [6 empty] | 2021-05-06
IN_SH_SAC_Exc_EmpLge_RestRm (economizer) | SAC_Exc_EmpLge_RestRm (economizer) | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialDryBulb | DifferentialDryBulb | [6 empty] | 2021-05-06
IN_SH_SAC_FRONTOFFICE Heating Capacity [kBtu/hr] | SAC_FRONTOFFICE Heating Capacity [kBtu/hr] | 36.8646 | 35.0385 | 36.8859 | 35.0997 | [6 empty] | 2021-05-06
IN_SH_SAC_FRONTLOUNGE Heating Capacity [kBtu/hr] | SAC_FRONTLOUNGE Heating Capacity [kBtu/hr] | 101.711 | 98.3412 | 104.1673 | 100.8063 | [6 empty] | 2021-05-06
IN_SH_SAC_MEETINGROOM Heating Capacity [kBtu/hr] | SAC_MEETINGROOM Heating Capacity [kBtu/hr] | 50.2241 | 49.3647 | 51.8928 | 50.8858 | [6 empty] | 2021-05-06
IN_SH_SAC_EXC_EMPLGE_RESTRM Heating Capacity [kBtu/hr] | SAC_EXC_EMPLGE_RESTRM Heating Capacity [kBtu/hr] | 94.1265 | 93.4621 | 94.7696 | 94.1128 | [6 empty] | 2021-05-06
id | item | Zone4A(IN-Evansville-IN) ASHRAE901-state_STD2016 | Zone4A(IN-Evansville-IN) ASHRAE901-state_STD2019 | Zone5A(IN-FortWayne-IN) ASHRAE901-state_STD2016 | Zone5A(IN-FortWayne-IN) ASHRAE901-state_STD2019 | [6 empty] | 2021-05-06
IN_MA_SPLIT GSW COOLING COIL Cooling Capacity [ton] | SPLIT GSW COOLING COIL Cooling Capacity [ton] | 0.92409 | 0.91011 | 0.8629 | 0.84876 | [6 empty] | 2021-05-06
IN_MA_SPLIT GNW COOLING COIL Cooling Capacity [ton] | SPLIT GNW COOLING COIL Cooling Capacity [ton] | 0.89163 | 0.87812 | 0.8201 | 0.80643 | [6 empty] | 2021-05-06
IN_MA_SPLIT OFFICE COOLING COIL Cooling Capacity [ton] | SPLIT OFFICE COOLING COIL Cooling Capacity [ton] | 1.7623 | 1.6393 | 1.7359 | 1.6072 | [6 empty] | 2021-05-06
IN_MA_SPLIT GNE COOLING COIL Cooling Capacity [ton] | SPLIT GNE COOLING COIL Cooling Capacity [ton] | 0.7881 | 0.77628 | 0.71499 | 0.70264 | [6 empty] | 2021-05-06
IN_MA_SPLIT GN1 COOLING COIL Cooling Capacity [ton] | SPLIT GN1 COOLING COIL Cooling Capacity [ton] | 0.66978 | 0.66013 | 0.60615 | 0.59651 | [6 empty] | 2021-05-06
IN_MA_SPLIT GN2 COOLING COIL Cooling Capacity [ton] | SPLIT GN2 COOLING COIL Cooling Capacity [ton] | 0.66783 | 0.65823 | 0.60654 | 0.59443 | [6 empty] | 2021-05-06
IN_MA_SPLIT GS1 COOLING COIL Cooling Capacity [ton] | SPLIT GS1 COOLING COIL Cooling Capacity [ton] | 0.70477 | 0.69462 | 0.65055 | 0.63998 | [6 empty] | 2021-05-06
IN_MA_SPLIT GS2 COOLING COIL Cooling Capacity [ton] | SPLIT GS2 COOLING COIL Cooling Capacity [ton] | 0.73568 | 0.7219 | 0.68083 | 0.66564 | [6 empty] | 2021-05-06
IN_MA_SPLIT MSW COOLING COIL Cooling Capacity [ton] | SPLIT MSW COOLING COIL Cooling Capacity [ton] | 2.1309 | 2.0995 | 2.1071 | 2.0751 | [6 empty] | 2021-05-06
IN_MA_SPLIT MNW COOLING COIL Cooling Capacity [ton] | SPLIT MNW COOLING COIL Cooling Capacity [ton] | 2.0747 | 2.0445 | 2.0258 | 1.995 | [6 empty] | 2021-05-06
IN_MA_SPLIT MSE COOLING COIL Cooling Capacity [ton] | SPLIT MSE COOLING COIL Cooling Capacity [ton] | 1.874 | 1.8476 | 1.815 | 1.7869 | [6 empty] | 2021-05-06
IN_MA_SPLIT MNE COOLING COIL Cooling Capacity [ton] | SPLIT MNE COOLING COIL Cooling Capacity [ton] | 1.6971 | 1.6682 | 1.6813 | 1.651 | [6 empty] | 2021-05-06
IN_MA_SPLIT MN1 COOLING COIL Cooling Capacity [ton] | SPLIT MN1 COOLING COIL Cooling Capacity [ton] | 1.4358 | 1.4173 | 1.3425 | 1.3245 | [6 empty] | 2021-05-06
IN_MA_SPLIT MN2 COOLING COIL Cooling Capacity [ton] | SPLIT MN2 COOLING COIL Cooling Capacity [ton] | 1.4303 | 1.4119 | 1.3361 | 1.3183 | [6 empty] | 2021-05-06
IN_MA_SPLIT MS1 COOLING COIL Cooling Capacity [ton] | SPLIT MS1 COOLING COIL Cooling Capacity [ton] | 1.4958 | 1.4766 | 1.4433 | 1.4234 | [6 empty] | 2021-05-06
IN_MA_SPLIT MS2 COOLING COIL Cooling Capacity [ton] | SPLIT MS2 COOLING COIL Cooling Capacity [ton] | 1.4902 | 1.4711 | 1.4382 | 1.4185 | [6 empty] | 2021-05-06
IN_MA_SPLIT TSW COOLING COIL Cooling Capacity [ton] | SPLIT TSW COOLING COIL Cooling Capacity [ton] | 1.3383 | 1.3212 | 1.3073 | 1.29 | [6 empty] | 2021-05-06
IN_MA_SPLIT TNW COOLING COIL Cooling Capacity [ton] | SPLIT TNW COOLING COIL Cooling Capacity [ton] | 1.295 | 1.2784 | 1.2664 | 1.2498 | [6 empty] | 2021-05-06
IN_MA_SPLIT TSE COOLING COIL Cooling Capacity [ton] | SPLIT TSE COOLING COIL Cooling Capacity [ton] | 1.2019 | 1.1884 | 1.1641 | 1.1496 | [6 empty] | 2021-05-06
IN_MA_SPLIT TNE COOLING COIL Cooling Capacity [ton] | SPLIT TNE COOLING COIL Cooling Capacity [ton] | 1.1377 | 1.1249 | 1.0835 | 1.0708 | [6 empty] | 2021-05-06
IN_MA_SPLIT TN1 COOLING COIL Cooling Capacity [ton] | SPLIT TN1 COOLING COIL Cooling Capacity [ton] | 0.93869 | 0.92871 | 0.87085 | 0.86123 | [6 empty] | 2021-05-06
IN_MA_SPLIT TN2 COOLING COIL Cooling Capacity [ton] | SPLIT TN2 COOLING COIL Cooling Capacity [ton] | 0.93999 | 0.93001 | 0.86461 | 0.85514 | [6 empty] | 2021-05-06
IN_MA_SPLIT TS1 COOLING COIL Cooling Capacity [ton] | SPLIT TS1 COOLING COIL Cooling Capacity [ton] | 1.0038 | 0.99301 | 0.94168 | 0.93083 | [6 empty] | 2021-05-06
IN_MA_SPLIT TS2 COOLING COIL Cooling Capacity [ton] | SPLIT TS2 COOLING COIL Cooling Capacity [ton] | 1.005 | 0.99414 | 0.95505 | 0.94405 | [6 empty] | 2021-05-06
IN_MA_Split GN1 Furnace with DX Cooling OA Rate [cfm] | Split GN1 Furnace with DX Cooling OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | [6 empty] | 2021-05-06
IN_MA_Split GN2 Furnace with DX Cooling OA Rate [cfm] | Split GN2 Furnace with DX Cooling OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | [6 empty] | 2021-05-06
IN_MA_Split GNE Furnace with DX Cooling OA Rate [cfm] | Split GNE Furnace with DX Cooling OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | [6 empty] | 2021-05-06
IN_MA_Split GNW Furnace with DX Cooling OA Rate [cfm] | Split GNW Furnace with DX Cooling OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | [6 empty] | 2021-05-06
IN_MA_Split GS1 Furnace with DX Cooling OA Rate [cfm] | Split GS1 Furnace with DX Cooling OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | [6 empty] | 2021-05-06
IN_MA_Split GS2 Furnace with DX Cooling OA Rate [cfm] | Split GS2 Furnace with DX Cooling OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | [6 empty] | 2021-05-06
IN_MA_Split GSW Furnace with DX Cooling OA Rate [cfm] | Split GSW Furnace with DX Cooling OA Rate [cfm] | 56.9945 | 56.9945 | 56.9945 | 56.9945 | [6 empty] | 2021-05-06
IN_MA_Split MN1 Furnace with DX Cooling OA Rate [cfm] | Split MN1 Furnace with DX Cooling OA Rate [cfm] | 109.9824 | 109.9824 | 109.9824 | 109.9824 | [6 empty] | 2021-05-06
IN_MA_Split MN2 Furnace with DX Cooling OA Rate [cfm] | Split MN2 Furnace with DX Cooling OA Rate [cfm] | 109.9824 | 109.9824 | 109.9824 | 109.9824 | [6 empty] | 2021-05-06
IN_MA_Split MNE Furnace with DX Cooling OA Rate [cfm] | Split MNE Furnace with DX Cooling OA Rate [cfm] | 109.9824 | 109.9824 | 109.9824 | 109.9824 | [6 empty] | 2021-05-06
IN_MA_Split MNW Furnace with DX Cooling OA Rate [cfm] | Split MNW Furnace with DX Cooling OA Rate [cfm] | 109.9824 | 109.9824 | 109.9824 | 109.9824 | [6 empty] | 2021-05-06
IN_MA_Split MS1 Furnace with DX Cooling OA Rate [cfm] | Split MS1 Furnace with DX Cooling OA Rate [cfm] | 109.9824 | 109.9824 | 109.9824 | 109.9824 | [6 empty] | 2021-05-06
IN_MA_Split MS2 Furnace with DX Cooling OA Rate [cfm] | Split MS2 Furnace with DX Cooling OA Rate [cfm] | 109.9824 | 109.9824 | 109.9824 | 109.9824 | [6 empty] | 2021-05-06
IN_MA_Split MSE Furnace with DX Cooling OA Rate [cfm] | Split MSE Furnace with DX Cooling OA Rate [cfm] | 109.9824 | 109.9824 | 109.9824 | 109.9824 | [6 empty] | 2021-05-06
IN_MA_Split MSW Furnace with DX Cooling OA Rate [cfm] | Split MSW Furnace with DX Cooling OA Rate [cfm] | 109.9824 | 109.9824 | 109.9824 | 109.9824 | [6 empty] | 2021-05-06
IN_MA_Split Office Furnace with DX Cooling OA Rate [cfm] | Split Office Furnace with DX Cooling OA Rate [cfm] | 80.7372 | 80.7372 | 80.7372 | 80.7372 | [6 empty] | 2021-05-06
IN_MA_Split TN1 Furnace with DX Cooling OA Rate [cfm] | Split TN1 Furnace with DX Cooling OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | [6 empty] | 2021-05-06
IN_MA_Split TN2 Furnace with DX Cooling OA Rate [cfm] | Split TN2 Furnace with DX Cooling OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | [6 empty] | 2021-05-06
IN_MA_Split TNE Furnace with DX Cooling OA Rate [cfm] | Split TNE Furnace with DX Cooling OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | [6 empty] | 2021-05-06
IN_MA_Split TNW Furnace with DX Cooling OA Rate [cfm] | Split TNW Furnace with DX Cooling OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | [6 empty] | 2021-05-06
IN_MA_Split TS1 Furnace with DX Cooling OA Rate [cfm] | Split TS1 Furnace with DX Cooling OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | [6 empty] | 2021-05-06
IN_MA_Split TS2 Furnace with DX Cooling OA Rate [cfm] | Split TS2 Furnace with DX Cooling OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | [6 empty] | 2021-05-06
IN_MA_Split TSE Furnace with DX Cooling OA Rate [cfm] | Split TSE Furnace with DX Cooling OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | [6 empty] | 2021-05-06
IN_MA_Split TSW Furnace with DX Cooling OA Rate [cfm] | Split TSW Furnace with DX Cooling OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | [6 empty] | 2021-05-06
IN_MA_SPLIT GSW HEATING COIL Heating Capacity [kBtu/hr] | SPLIT GSW HEATING COIL Heating Capacity [kBtu/hr] | 9.4848 | 9.5435 | 11.2212 | 11.2803 | [6 empty] | 2021-05-06
IN_MA_SPLIT GNW HEATING COIL Heating Capacity [kBtu/hr] | SPLIT GNW HEATING COIL Heating Capacity [kBtu/hr] | 9.4118 | 9.4706 | 11.1042 | 11.1634 | [6 empty] | 2021-05-06
IN_MA_SPLIT OFFICE HEATING COIL Heating Capacity [kBtu/hr] | SPLIT OFFICE HEATING COIL Heating Capacity [kBtu/hr] | 22.2361 | 22.3224 | 24.5118 | 24.5909 | [6 empty] | 2021-05-06
IN_MA_SPLIT GNE HEATING COIL Heating Capacity [kBtu/hr] | SPLIT GNE HEATING COIL Heating Capacity [kBtu/hr] | 9.3912 | 9.45 | 11.0757 | 11.1349 | [6 empty] | 2021-05-06
IN_MA_SPLIT GN1 HEATING COIL Heating Capacity [kBtu/hr] | SPLIT GN1 HEATING COIL Heating Capacity [kBtu/hr] | 6.9399 | 6.9987 | 8.204 | 8.2633 | [6 empty] | 2021-05-06
IN_MA_SPLIT GN2 HEATING COIL Heating Capacity [kBtu/hr] | SPLIT GN2 HEATING COIL Heating Capacity [kBtu/hr] | 6.9392 | 6.9981 | 8.2032 | 8.2625 | [6 empty] | 2021-05-06
IN_MA_SPLIT GS1 HEATING COIL Heating Capacity [kBtu/hr] | SPLIT GS1 HEATING COIL Heating Capacity [kBtu/hr] | 6.8908 | 6.9495 | 8.1851 | 8.2442 | [6 empty] | 2021-05-06
IN_MA_SPLIT GS2 HEATING COIL Heating Capacity [kBtu/hr] | SPLIT GS2 HEATING COIL Heating Capacity [kBtu/hr] | 7.391 | 7.451 | 8.6965 | 8.7564 | [6 empty] | 2021-05-06
IN_MA_SPLIT MSW HEATING COIL Heating Capacity [kBtu/hr] | SPLIT MSW HEATING COIL Heating Capacity [kBtu/hr] | 16.9473 | 17.0757 | 20.3303 | 20.4595 | [6 empty] | 2021-05-06
IN_MA_SPLIT MNW HEATING COIL Heating Capacity [kBtu/hr] | SPLIT MNW HEATING COIL Heating Capacity [kBtu/hr] | 17.0321 | 17.1605 | 20.342 | 20.4712 | [6 empty] | 2021-05-06
IN_MA_SPLIT MSE HEATING COIL Heating Capacity [kBtu/hr] | SPLIT MSE HEATING COIL Heating Capacity [kBtu/hr] | 16.8983 | 17.0267 | 20.2637 | 20.3929 | [6 empty] | 2021-05-06
IN_MA_SPLIT MNE HEATING COIL Heating Capacity [kBtu/hr] | SPLIT MNE HEATING COIL Heating Capacity [kBtu/hr] | 16.983 | 17.1114 | 20.2753 | 20.4045 | [6 empty] | 2021-05-06
IN_MA_SPLIT MN1 HEATING COIL Heating Capacity [kBtu/hr] | SPLIT MN1 HEATING COIL Heating Capacity [kBtu/hr] | 11.8139 | 11.9396 | 14.1649 | 14.2907 | [6 empty] | 2021-05-06
IN_MA_SPLIT MN2 HEATING COIL Heating Capacity [kBtu/hr] | SPLIT MN2 HEATING COIL Heating Capacity [kBtu/hr] | 11.8126 | 11.9383 | 14.1632 | 14.2889 | [6 empty] | 2021-05-06
IN_MA_SPLIT MS1 HEATING COIL Heating Capacity [kBtu/hr] | SPLIT MS1 HEATING COIL Heating Capacity [kBtu/hr] | 11.7376 | 11.8633 | 14.1624 | 14.2882 | [6 empty] | 2021-05-06
IN_MA_SPLIT MS2 HEATING COIL Heating Capacity [kBtu/hr] | SPLIT MS2 HEATING COIL Heating Capacity [kBtu/hr] | 11.7363 | 11.862 | 14.1606 | 14.2865 | [6 empty] | 2021-05-06
IN_MA_SPLIT TSW HEATING COIL Heating Capacity [kBtu/hr] | SPLIT TSW HEATING COIL Heating Capacity [kBtu/hr] | 11.9132 | 11.9749 | 14.1965 | 14.2583 | [6 empty] | 2021-05-06
IN_MA_SPLIT TNW HEATING COIL Heating Capacity [kBtu/hr] | SPLIT TNW HEATING COIL Heating Capacity [kBtu/hr] | 11.9641 | 12.0259 | 14.209 | 14.2709 | [6 empty] | 2021-05-06
IN_MA_SPLIT TSE HEATING COIL Heating Capacity [kBtu/hr] | SPLIT TSE HEATING COIL Heating Capacity [kBtu/hr] | 11.8872 | 11.9489 | 14.1613 | 14.2231 | [6 empty] | 2021-05-06
IN_MA_SPLIT TNE HEATING COIL Heating Capacity [kBtu/hr] | SPLIT TNE HEATING COIL Heating Capacity [kBtu/hr] | 11.9381 | 11.9999 | 14.1737 | 14.2357 | [6 empty] | 2021-05-06
IN_MA_SPLIT TN1 HEATING COIL Heating Capacity [kBtu/hr] | SPLIT TN1 HEATING COIL Heating Capacity [kBtu/hr] | 9.181 | 9.2427 | 10.8298 | 10.8916 | [6 empty] | 2021-05-06
IN_MA_SPLIT TN2 HEATING COIL Heating Capacity [kBtu/hr] | SPLIT TN2 HEATING COIL Heating Capacity [kBtu/hr] | 9.1803 | 9.242 | 10.8288 | 10.8906 | [6 empty] | 2021-05-06
IN_MA_SPLIT TS1 HEATING COIL Heating Capacity [kBtu/hr] | SPLIT TS1 HEATING COIL Heating Capacity [kBtu/hr] | 9.1231 | 9.1848 | 10.8113 | 10.873 | [6 empty] | 2021-05-06
IN_MA_SPLIT TS2 HEATING COIL Heating Capacity [kBtu/hr] | SPLIT TS2 HEATING COIL Heating Capacity [kBtu/hr] | 9.1224 | 9.184 | 10.8103 | 10.872 | [6 empty] | 2021-05-06
IN_MA_Split_GSW ERV Flag | Split_GSW ERV Flag | Yes | Yes | Yes | Yes | [6 empty] | 2021-05-06
IN_MA_Split_GNW ERV Flag | Split_GNW ERV Flag | Yes | Yes | Yes | Yes | [6 empty] | 2021-05-06
IN_MA_Split_GNE ERV Flag | Split_GNE ERV Flag | Yes | Yes | Yes | Yes | [6 empty] | 2021-05-06
IN_MA_Split_GN1 ERV Flag | Split_GN1 ERV Flag | Yes | Yes | Yes | Yes | [6 empty] | 2021-05-06
IN_MA_Split_GN2 ERV Flag | Split_GN2 ERV Flag | Yes | Yes | Yes | Yes | [6 empty] | 2021-05-06
IN_MA_Split_GS1 ERV Flag | Split_GS1 ERV Flag | Yes | Yes | Yes | Yes | [6 empty] | 2021-05-06
IN_MA_Split_GS2 ERV Flag | Split_GS2 ERV Flag | Yes | Yes | Yes | Yes | [6 empty] | 2021-05-06
IN_MA_Split_MSW ERV Flag | Split_MSW ERV Flag | Yes | Yes | Yes | Yes | [6 empty] | 2021-05-06
IN_MA_Split_MNW ERV Flag | Split_MNW ERV Flag | Yes | Yes | Yes | Yes | [6 empty] | 2021-05-06
IN_MA_Split_MSE ERV Flag | Split_MSE ERV Flag | Yes | Yes | Yes | Yes | [6 empty] | 2021-05-06
IN_MA_Split_MNE ERV Flag | Split_MNE ERV Flag | Yes | Yes | Yes | Yes | [6 empty] | 2021-05-06
IN_MA_Split_MN1 ERV Flag | Split_MN1 ERV Flag | Yes | Yes | Yes | Yes | [6 empty] | 2021-05-06
IN_MA_Split_MN2 ERV Flag | Split_MN2 ERV Flag | Yes | Yes | Yes | Yes | [6 empty] | 2021-05-06
IN_MA_Split_MS1 ERV Flag | Split_MS1 ERV Flag | Yes | Yes | Yes | Yes | [6 empty] | 2021-05-06
IN_MA_Split_MS2 ERV Flag | Split_MS2 ERV Flag | Yes | Yes | Yes | Yes | [6 empty] | 2021-05-06
IN_MA_Split_TSW ERV Flag | Split_TSW ERV Flag | Yes | Yes | Yes | Yes | [6 empty] | 2021-05-06
IN_MA_Split_TNW ERV Flag | Split_TNW ERV Flag | Yes | Yes | Yes | Yes | [6 empty] | 2021-05-06
IN_MA_Split_TSE ERV Flag | Split_TSE ERV Flag | Yes | Yes | Yes | Yes | [6 empty] | 2021-05-06
IN_MA_Split_TNE ERV Flag | Split_TNE ERV Flag | Yes | Yes | Yes | Yes | [6 empty] | 2021-05-06
IN_MA_Split_TN1 ERV Flag | Split_TN1 ERV Flag | Yes | Yes | Yes | Yes | [6 empty] | 2021-05-06
IN_MA_Split_TN2 ERV Flag | Split_TN2 ERV Flag | Yes | Yes | Yes | Yes | [6 empty] | 2021-05-06
IN_MA_Split_TS1 ERV Flag | Split_TS1 ERV Flag | Yes | Yes | Yes | Yes | [6 empty] | 2021-05-06
IN_MA_Split_TS2 ERV Flag | Split_TS2 ERV Flag | Yes | Yes | Yes | Yes | [6 empty] | 2021-05-06
id | item | Zone4A(KS-Topeka-KS) ASHRAE901-state_STD2016 | Zone4A(KS-Topeka-KS) ASHRAE901-state_STD2019 | Zone5A(KS-Goodland-KS) ASHRAE901-state_STD2016 | Zone5A(KS-Goodland-KS) ASHRAE901-state_STD2019 | [6 empty] | 2021-05-06
KS_SO_PSZ-AC:1 Cooling Capacity [ton] | PSZ-AC:1 Cooling Capacity [ton] | 2.0036 | 1.9068 | 1.7574 | 1.6586 | [6 empty] | 2021-05-06
KS_SO_PSZ-AC:2 Cooling Capacity [ton] | PSZ-AC:2 Cooling Capacity [ton] | 1.8013 | 1.7329 | 1.5754 | 1.5062 | [6 empty] | 2021-05-06
KS_SO_PSZ-AC:3 Cooling Capacity [ton] | PSZ-AC:3 Cooling Capacity [ton] | 1.2591 | 1.2187 | 1.1667 | 1.119 | [6 empty] | 2021-05-06
KS_SO_PSZ-AC:4 Cooling Capacity [ton] | PSZ-AC:4 Cooling Capacity [ton] | 1.7528 | 1.671 | 1.5257 | 1.4346 | [6 empty] | 2021-05-06
KS_SO_PSZ-AC:5 Cooling Capacity [ton] | PSZ-AC:5 Cooling Capacity [ton] | 1.4852 | 1.4431 | 1.4578 | 1.407 | [6 empty] | 2021-05-06
KS_SO_PSZ-AC:1 Supply Flow Rate [cfm] | PSZ-AC:1 Supply Flow Rate [cfm] | 678.0416 | 635.664 | 741.608 | 699.2304 | [6 empty] | 2021-05-06
KS_SO_PSZ-AC:2 Supply Flow Rate [cfm] | PSZ-AC:2 Supply Flow Rate [cfm] | 635.664 | 593.2864 | 678.0416 | 635.664 | [6 empty] | 2021-05-06
KS_SO_PSZ-AC:3 Supply Flow Rate [cfm] | PSZ-AC:3 Supply Flow Rate [cfm] | 508.5312 | 487.3424 | 529.72 | 508.5312 | [6 empty] | 2021-05-06
KS_SO_PSZ-AC:4 Supply Flow Rate [cfm] | PSZ-AC:4 Supply Flow Rate [cfm] | 614.4752 | 572.0976 | 656.8528 | 614.4752 | [6 empty] | 2021-05-06
KS_SO_PSZ-AC:5 Supply Flow Rate [cfm] | PSZ-AC:5 Supply Flow Rate [cfm] | 593.2864 | 572.0976 | 656.8528 | 635.664 | [6 empty] | 2021-05-06
KS_SO_PSZ-AC:1 OA Rate [cfm] | PSZ-AC:1 OA Rate [cfm] | 136.9178 | 136.9178 | 136.9178 | 136.9178 | [6 empty] | 2021-05-06
KS_SO_PSZ-AC:2 OA Rate [cfm] | PSZ-AC:2 OA Rate [cfm] | 103.7925 | 103.7925 | 103.7925 | 103.7925 | [6 empty] | 2021-05-06
KS_SO_PSZ-AC:3 OA Rate [cfm] | PSZ-AC:3 OA Rate [cfm] | 61.5711 | 61.5711 | 61.5711 | 61.5711 | [6 empty] | 2021-05-06
KS_SO_PSZ-AC:4 OA Rate [cfm] | PSZ-AC:4 OA Rate [cfm] | 103.7925 | 103.7925 | 103.7925 | 103.7925 | [6 empty] | 2021-05-06
KS_SO_PSZ-AC:5 OA Rate [cfm] | PSZ-AC:5 OA Rate [cfm] | 61.5711 | 61.5711 | 61.5711 | 61.5711 | [6 empty] | 2021-05-06
KS_SO_PSZ-AC:1 heating Capacity [kBtu/hr] | PSZ-AC:1 heating Capacity [kBtu/hr] | 14.8335 | 14.8335 | 13.7532 | 13.7532 | [6 empty] | 2021-05-06
KS_SO_PSZ-AC:2 heating Capacity [kBtu/hr] | PSZ-AC:2 heating Capacity [kBtu/hr] | 20.884 | 20.6565 | 21.0773 | 20.8296 | [6 empty] | 2021-05-06
KS_SO_PSZ-AC:3 heating Capacity [kBtu/hr] | PSZ-AC:3 heating Capacity [kBtu/hr] | 12.7584 | 12.6326 | 12.7965 | 12.6657 | [6 empty] | 2021-05-06
KS_SO_PSZ-AC:4 heating Capacity [kBtu/hr] | PSZ-AC:4 heating Capacity [kBtu/hr] | 20.7821 | 20.5878 | 20.8679 | 20.6653 | [6 empty] | 2021-05-06
KS_SO_PSZ-AC:5 heating Capacity [kBtu/hr] | PSZ-AC:5 heating Capacity [kBtu/hr] | 12.8173 | 12.6859 | 12.864 | 12.7268 | [6 empty] | 2021-05-06
id | item | Zone4A(KS-Topeka-KS) ASHRAE901-state_STD2016 | Zone4A(KS-Topeka-KS) ASHRAE901-state_STD2019 | Zone5A(KS-Goodland-KS) ASHRAE901-state_STD2016 | Zone5A(KS-Goodland-KS) ASHRAE901-state_STD2019 | [6 empty] | 2021-05-06
KS_LO_CAV_BAS Supply Flow Rate [cfm] | CAV_BAS Supply Flow Rate [cfm] | 12077.616 | 11187.6864 | 13306.5664 | 12310.6928 | [6 empty] | 2021-05-06
KS_LO_VAV_BOT WITH REHEAT Supply Flow Rate [cfm] | VAV_BOT WITH REHEAT Supply Flow Rate [cfm] | 20531.9472 | 19578.4512 | 22608.4496 | 21549.0096 | [6 empty] | 2021-05-06
KS_LO_VAV_MID WITH REHEAT Supply Flow Rate [cfm] | VAV_MID WITH REHEAT Supply Flow Rate [cfm] | 191610.3187 | 182435.5683 | 211061.6371 | 201124.0899 | [6 empty] | 2021-05-06
KS_LO_VAV_TOP WITH REHEAT Supply Flow Rate [cfm] | VAV_TOP WITH REHEAT Supply Flow Rate [cfm] | 20341.248 | 19514.8848 | 22735.5824 | 21824.464 | [6 empty] | 2021-05-06
KS_LO_Supply Air Temp. Reset Flag | Supply Air Temp. Reset Flag | Yes | Yes | Yes | Yes | [6 empty] | 2021-05-06
KS_LO_CAV_BAS OA Rate [cfm] | CAV_BAS OA Rate [cfm] | 2542.8255 | 2542.8255 | 2542.8255 | 2542.8255 | [6 empty] | 2021-05-06
KS_LO_VAV_BOT WITH REHEAT OA Rate [cfm] | VAV_BOT WITH REHEAT OA Rate [cfm] | 5377.8022 | 4302.174 | 5377.8022 | 4302.174 | [6 empty] | 2021-05-06
KS_LO_VAV_MID WITH REHEAT OA Rate [cfm] | VAV_MID WITH REHEAT OA Rate [cfm] | 53777.9373 | 43021.7396 | 53777.9373 | 43021.7396 | [6 empty] | 2021-05-06
KS_LO_VAV_TOP WITH REHEAT OA Rate [cfm] | VAV_TOP WITH REHEAT OA Rate [cfm] | 5377.8022 | 4302.174 | 5377.8022 | 4302.174 | [6 empty] | 2021-05-06
KS_LO_AIRLOOP DATACENTER BASEMENT OA Rate [cfm] | AIRLOOP DATACENTER BASEMENT OA Rate [cfm] | 716.9654 | 716.9654 | 716.9654 | 716.9654 | [6 empty] | 2021-05-06
KS_LO_VAV_bot_WITH_REHEAT ERV Flag | VAV_bot_WITH_REHEAT ERV Flag | Yes | Yes | Yes | No | [6 empty] | 2021-05-06
KS_LO_VAV_mid_WITH_REHEAT ERV Flag | VAV_mid_WITH_REHEAT ERV Flag | Yes | Yes | Yes | Yes | [6 empty] | 2021-05-06
KS_LO_VAV_top_WITH_REHEAT ERV Flag | VAV_top_WITH_REHEAT ERV Flag | Yes | Yes | Yes | No | [6 empty] | 2021-05-06
KS_LO_COOLSYS1 CHILLER1 Capacity [ton] | COOLSYS1 CHILLER1 Capacity [ton] | 440.6861 | 397.3315 | 348.2679 | 321.9784 | [6 empty] | 2021-05-06
KS_LO_COOLSYS1 CHILLER2 Capacity [ton] | COOLSYS1 CHILLER2 Capacity [ton] | 440.6861 | 397.3315 | 348.2679 | 321.9784 | [6 empty] | 2021-05-06
KS_LO_TOWERWATERSYS COOLTOWER 1 Capacity [ton] | TOWERWATERSYS COOLTOWER 1 Capacity [ton] | 418.2923 | 377.1391 | 330.7974 | 305.8254 | [6 empty] | 2021-05-06
KS_LO_TOWERWATERSYS COOLTOWER 2 Capacity [ton] | TOWERWATERSYS COOLTOWER 2 Capacity [ton] | 418.2923 | 377.1391 | 330.7974 | 305.8254 | [6 empty] | 2021-05-06
KS_LO_HEATSYS1 BOILER Capacity [MMBTU/h] | HEATSYS1 BOILER Capacity [MMBTU/h] | 4723.0837 | 4179.9031 | 4604.6945 | 4104.7723 | [6 empty] | 2021-05-06
KS_LO_COOLSYS1 PUMP Flow Rate [gal/min] | COOLSYS1 PUMP Flow Rate [gal/min] | 0 | 0 | 0 | 0 | [6 empty] | 2021-05-06
KS_LO_COOLSYS1 CHILLER1 PUMP Flow Rate [gal/min] | COOLSYS1 CHILLER1 PUMP Flow Rate [gal/min] | 694.455 | 623.1412 | 547.5843 | 506.4289 | [6 empty] | 2021-05-06
KS_LO_COOLSYS1 CHILLER2 PUMP Flow Rate [gal/min] | COOLSYS1 CHILLER2 PUMP Flow Rate [gal/min] | 694.455 | 623.1412 | 547.5843 | 506.4289 | [6 empty] | 2021-05-06
KS_LO_COOLSYS1 PUMP SECONDARY Flow Rate [gal/min] | COOLSYS1 PUMP SECONDARY Flow Rate [gal/min] | 1388.9099 | 1246.2824 | 1095.167 | 1012.8594 | [6 empty] | 2021-05-06
KS_LO_HEATSYS1 PUMP Flow Rate [gal/min] | HEATSYS1 PUMP Flow Rate [gal/min] | 969.4755 | 857.9796 | 945.1738 | 842.5588 | [6 empty] | 2021-05-06
KS_LO_TOWERWATERSYS PUMP Flow Rate [gal/min] | TOWERWATERSYS PUMP Flow Rate [gal/min] | 2431.2811 | 2192.0997 | 1921.3762 | 1776.3457 | [6 empty] | 2021-05-06
KS_LO_PLANT CIRC PUMP Flow Rate [gal/min] | PLANT CIRC PUMP Flow Rate [gal/min] | 212.025 | 211.1754 | 216.9037 | 216.0193 | [6 empty] | 2021-05-06
KS_LO_COOLSYS1 PUMP SECONDARY Pressure setpoint reset [yes,no] | COOLSYS1 PUMP SECONDARY Pressure setpoint reset [yes,no] | pump_ride_on_curve | pump_ride_on_curve | pump_ride_on_curve | pump_ride_on_curve | [6 empty] | 2021-05-06
KS_LO_COOLSYS1 CHILLER1 PUMP Pump Power [hp] | COOLSYS1 CHILLER1 PUMP Pump Power [hp] | 3.7463 | 3.3283 | 2.954 | 2.705 | [6 empty] | 2021-05-06
KS_LO_COOLSYS1 CHILLER2 PUMP Pump Power [hp] | COOLSYS1 CHILLER2 PUMP Pump Power [hp] | 3.7463 | 3.3283 | 2.954 | 2.705 | [6 empty] | 2021-05-06
KS_LO_COOLSYS1 PUMP SECONDARY Pump Power [hp] | COOLSYS1 PUMP SECONDARY Pump Power [hp] | 22.4781 | 19.9701 | 17.7241 | 16.2298 | [6 empty] | 2021-05-06
KS_LO_HEATSYS1 PUMP Pump Power [hp] | HEATSYS1 PUMP Pump Power [hp] | 20.9558 | 18.3621 | 20.4305 | 18.0321 | [6 empty] | 2021-05-06
KS_LO_TOWERWATERSYS PUMP Pump Power [hp] | TOWERWATERSYS PUMP Pump Power [hp] | 43.5301 | 38.859 | 34.4012 | 31.4895 | [6 empty] | 2021-05-06
KS_LO_PLANT CIRC PUMP Pump Power [hp] | PLANT CIRC PUMP Pump Power [hp] | 4.5752 | 4.5118 | 4.6805 | 4.6152 | [6 empty] | 2021-05-06
KS_LO_Datacenter PLANT CIRC PUMP Pump Power [hp] | Datacenter PLANT CIRC PUMP Pump Power [hp] | 4.5752 | 4.5118 | 4.6805 | 4.6152 | [6 empty] | 2021-05-06
KS_LO_ZN_VAV_BOXes_Max_Reheat_Water_Flow_GPM | ZN_VAV_BOXes_Max_Reheat_Water_Flow_GPM | 494.8352 | 475.9405 | 500.3756 | 480.9762 | [6 empty] | 2021-05-06
KS_LO_COOLSYS1 PUMP SECONDARY VSD | COOLSYS1 PUMP SECONDARY VSD | No | No | No | No | [6 empty] | 2021-05-06
KS_LO_HEATSYS1 PUMP VSD | HEATSYS1 PUMP VSD | No | No | No | No | [6 empty] | 2021-05-06
KS_LO_DATACENTER BASEMENT Cooling Capacity [ton] | DATACENTER BASEMENT Cooling Capacity [ton] | 123.5346 | 123.1703 | 126.6513 | 126.2731 | [6 empty] | 2021-05-06
KS_LO_DATACENTER BOT Cooling Capacity [ton] | DATACENTER BOT Cooling Capacity [ton] | 2.7475 | 2.7234 | 2.789 | 2.7639 | [6 empty] | 2021-05-06
KS_LO_DATACENTER MID Cooling Capacity [ton] | DATACENTER MID Cooling Capacity [ton] | 26.3439 | 26.1307 | 26.7184 | 26.4955 | [6 empty] | 2021-05-06
KS_LO_DATACENTER TOP Cooling Capacity [ton] | DATACENTER TOP Cooling Capacity [ton] | 2.6873 | 2.6666 | 2.7279 | 2.7063 | [6 empty] | 2021-05-06
id | item | Zone4A(KS-Topeka-KS) ASHRAE901-state_STD2016 | Zone4A(KS-Topeka-KS) ASHRAE901-state_STD2019 | Zone5A(KS-Goodland-KS) ASHRAE901-state_STD2016 | Zone5A(KS-Goodland-KS) ASHRAE901-state_STD2019 | [6 empty] | 2021-05-06
KS_RS_PSZ-AC:1 Cooling Capacity [ton] | PSZ-AC:1 Cooling Capacity [ton] | 11.0615 | 10.6731 | 9.9784 | 9.2945 | [6 empty] | 2021-05-06
KS_RS_PSZ-AC:2 Cooling Capacity [ton] | PSZ-AC:2 Cooling Capacity [ton] | 53.8539 | 50.6599 | 45.4183 | 43.5378 | [6 empty] | 2021-05-06
KS_RS_PSZ-AC:3 Cooling Capacity [ton] | PSZ-AC:3 Cooling Capacity [ton] | 7.0474 | 6.8804 | 6.1857 | 6.0167 | [6 empty] | 2021-05-06
KS_RS_PSZ-AC:4 Cooling Capacity [ton] | PSZ-AC:4 Cooling Capacity [ton] | 5.7884 | 5.607 | 4.8859 | 4.7024 | [6 empty] | 2021-05-06
KS_RS_PSZ-AC:1 Supply Flow Rate [cfm] | PSZ-AC:1 Supply Flow Rate [cfm] | 4280.1376 | 4004.6832 | 4492.0256 | 4174.1936 | [6 empty] | 2021-05-06
KS_RS_PSZ-AC:2 Supply Flow Rate [cfm] | PSZ-AC:2 Supply Flow Rate [cfm] | 16167.0544 | 15192.3696 | 17459.5712 | 16527.264 | [6 empty] | 2021-05-06
KS_RS_PSZ-AC:3 Supply Flow Rate [cfm] | PSZ-AC:3 Supply Flow Rate [cfm] | 2415.5232 | 2351.9568 | 2606.2224 | 2521.4672 | [6 empty] | 2021-05-06
KS_RS_PSZ-AC:4 Supply Flow Rate [cfm] | PSZ-AC:4 Supply Flow Rate [cfm] | 1864.6144 | 1801.048 | 1970.5584 | 1885.8032 | [6 empty] | 2021-05-06
KS_RS_PSZ-AC:1 OA Rate [cfm] | PSZ-AC:1 OA Rate [cfm] | 490.669 | 490.669 | 490.669 | 490.669 | [6 empty] | 2021-05-06
KS_RS_PSZ-AC:2 OA Rate [cfm] | PSZ-AC:2 OA Rate [cfm] | 4005.1282 | 4005.1282 | 4005.1282 | 4005.1282 | [6 empty] | 2021-05-06
KS_RS_PSZ-AC:3 OA Rate [cfm] | PSZ-AC:3 OA Rate [cfm] | 377.3937 | 377.3937 | 377.3937 | 377.3937 | [6 empty] | 2021-05-06
KS_RS_PSZ-AC:4 OA Rate [cfm] | PSZ-AC:4 OA Rate [cfm] | 377.3937 | 377.3937 | 377.3937 | 377.3937 | [6 empty] | 2021-05-06
KS_RS_PSZ-AC:1 OA Damper [gravity, motorized] | PSZ-AC:1 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2021-05-06
KS_RS_PSZ-AC:2 OA Damper [gravity, motorized] | PSZ-AC:2 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2021-05-06
KS_RS_PSZ-AC:3 OA Damper [gravity, motorized] | PSZ-AC:3 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2021-05-06
KS_RS_PSZ-AC:4 OA Damper [gravity, motorized] | PSZ-AC:4 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2021-05-06
KS_RS_PSZ-AC:1 Heating Capacity [kBtu/hr] | PSZ-AC:1 Heating Capacity [kBtu/hr] | 189.0288 | 178.7989 | 179.2161 | 167.6806 | [6 empty] | 2021-05-06
KS_RS_PSZ-AC:2 Heating Capacity [kBtu/hr] | PSZ-AC:2 Heating Capacity [kBtu/hr] | 858.8972 | 820.2648 | 829.2683 | 794.009 | [6 empty] | 2021-05-06
KS_RS_PSZ-AC:3 Heating Capacity [kBtu/hr] | PSZ-AC:3 Heating Capacity [kBtu/hr] | 114.3739 | 111.6784 | 109.9905 | 107.3081 | [6 empty] | 2021-05-06
KS_RS_PSZ-AC:4 Heating Capacity [kBtu/hr] | PSZ-AC:4 Heating Capacity [kBtu/hr] | 94.5332 | 91.7255 | 89.5869 | 86.4842 | [6 empty] | 2021-05-06
id | item | Zone4A(KS-Topeka-KS) ASHRAE901-state_STD2016 | Zone4A(KS-Topeka-KS) ASHRAE901-state_STD2019 | Zone5A(KS-Goodland-KS) ASHRAE901-state_STD2016 | Zone5A(KS-Goodland-KS) ASHRAE901-state_STD2019 | [6 empty] | 2021-05-06
KS_PS_VAV_POD_1 Cooling Capacity [ton] | VAV_POD_1 Cooling Capacity [ton] | 20.2271 | 19.2893 | 22.3165 | 21.0265 | [6 empty] | 2021-05-06
KS_PS_VAV_POD_2 Cooling Capacity [ton] | VAV_POD_2 Cooling Capacity [ton] | 20.1664 | 19.0693 | 22.0903 | 20.6644 | [6 empty] | 2021-05-06
KS_PS_VAV_POD_3 Cooling Capacity [ton] | VAV_POD_3 Cooling Capacity [ton] | 18.5675 | 17.4851 | 20.475 | 19.2899 | [6 empty] | 2021-05-06
KS_PS_VAV_OTHER Cooling Capacity [ton] | VAV_OTHER Cooling Capacity [ton] | 28.4235 | 26.8587 | 26.6313 | 24.1308 | [6 empty] | 2021-05-06
KS_PS_PSZ-AC_1:6 Cooling Capacity [ton] | PSZ-AC_1:6 Cooling Capacity [ton] | 8.8131 | 8.4346 | 8.0322 | 7.7545 | [6 empty] | 2021-05-06
KS_PS_PSZ-AC_2:5 Cooling Capacity [ton] | PSZ-AC_2:5 Cooling Capacity [ton] | 5.8616 | 5.8356 | 5.957 | 5.9359 | [6 empty] | 2021-05-06
KS_PS_PSZ-AC_2:7 Cooling Capacity [ton] | PSZ-AC_2:7 Cooling Capacity [ton] | 10.5074 | 10.5074 | 10.5074 | 10.5074 | [6 empty] | 2021-05-06
KS_PS_VAV_POD_1 Supply Flow Rate [cfm] | VAV_POD_1 Supply Flow Rate [cfm] | 6059.9968 | 5784.5424 | 6695.6608 | 6314.2624 | [6 empty] | 2021-05-06
KS_PS_VAV_POD_2 Supply Flow Rate [cfm] | VAV_POD_2 Supply Flow Rate [cfm] | 6059.9968 | 5720.976 | 6632.0944 | 6208.3184 | [6 empty] | 2021-05-06
KS_PS_VAV_POD_3 Supply Flow Rate [cfm] | VAV_POD_3 Supply Flow Rate [cfm] | 5572.6544 | 5254.8224 | 6144.752 | 5784.5424 | [6 empty] | 2021-05-06
KS_PS_VAV_OTHER Supply Flow Rate [cfm] | VAV_OTHER Supply Flow Rate [cfm] | 8539.0864 | 8051.744 | 9450.2048 | 8899.296 | [6 empty] | 2021-05-06
KS_PS_PSZ-AC_2:5 Supply Flow Rate [cfm] | PSZ-AC_2:5 Supply Flow Rate [cfm] | 1758.6704 | 1758.6704 | 1928.1808 | 1906.992 | [6 empty] | 2021-05-06
KS_PS_PSZ-AC_1:6 Supply Flow Rate [cfm] | PSZ-AC_1:6 Supply Flow Rate [cfm] | 2648.6 | 2521.4672 | 2902.8656 | 2775.7328 | [6 empty] | 2021-05-06
KS_PS_PSZ-AC_2:7 Supply Flow Rate [cfm] | PSZ-AC_2:7 Supply Flow Rate [cfm] | 3157.1312 | 3157.1312 | 3157.1312 | 3157.1312 | [6 empty] | 2021-05-06
KS_PS_Supply Air Temp. Reset Flag | Supply Air Temp. Reset Flag | Yes | Yes | Yes | Yes | [6 empty] | 2021-05-06
KS_PS_VAV_POD_1 OA Rate [cfm] | VAV_POD_1 OA Rate [cfm] | 6069.8072 | 5788.3988 | 6696.805 | 6282.2673 | [6 empty] | 2021-05-06
KS_PS_VAV_POD_2 OA Rate [cfm] | VAV_POD_2 OA Rate [cfm] | 6050.8432 | 5722.3957 | 6628.9585 | 6201.0507 | [6 empty] | 2021-05-06
KS_PS_VAV_POD_3 OA Rate [cfm] | VAV_POD_3 OA Rate [cfm] | 5570.9169 | 5246.9826 | 6143.3324 | 5422.002 | [6 empty] | 2021-05-06
KS_PS_VAV_OTHER OA Rate [cfm] | VAV_OTHER OA Rate [cfm] | 3736.1787 | 2988.8921 | 3736.1787 | 2988.8921 | [6 empty] | 2021-05-06
KS_PS_PSZ-AC_2:5 OA Rate [cfm] | PSZ-AC_2:5 OA Rate [cfm] | 1152.7343 | 1152.7343 | 1152.7343 | 1152.7343 | [6 empty] | 2021-05-06
KS_PS_PSZ-AC_1:6 OA Rate [cfm] | PSZ-AC_1:6 OA Rate [cfm] | 539.9118 | 539.9118 | 539.9118 | 539.9118 | [6 empty] | 2021-05-06
KS_PS_PSZ-AC_2:7 OA Rate [cfm] | PSZ-AC_2:7 OA Rate [cfm] | 3153.0841 | 3153.0841 | 3153.0841 | 3153.0841 | [6 empty] | 2021-05-06
KS_PS_VAV_POD_1 OA Damper [gravity, motorized] | VAV_POD_1 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2021-05-06
KS_PS_VAV_POD_2 OA Damper [gravity, motorized] | VAV_POD_2 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2021-05-06
KS_PS_VAV_POD_3 OA Damper [gravity, motorized] | VAV_POD_3 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2021-05-06
KS_PS_VAV_OTHER OA Damper [gravity, motorized] | VAV_OTHER OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2021-05-06
KS_PS_PSZ-AC_2:5 OA Damper [gravity, motorized] | PSZ-AC_2:5 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2021-05-06
KS_PS_PSZ-AC_1:6 OA Damper [gravity, motorized] | PSZ-AC_1:6 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2021-05-06
KS_PS_PSZ-AC_2:7 OA Damper [gravity, motorized] | PSZ-AC_2:7 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2021-05-06
KS_PS_VAV_POD_1 (economizer) | VAV_POD_1 (economizer) | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialDryBulb | DifferentialDryBulb | [6 empty] | 2021-05-06
KS_PS_VAV_POD_2 (economizer) | VAV_POD_2 (economizer) | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialDryBulb | DifferentialDryBulb | [6 empty] | 2021-05-06
KS_PS_VAV_POD_3 (economizer) | VAV_POD_3 (economizer) | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialDryBulb | DifferentialDryBulb | [6 empty] | 2021-05-06
KS_PS_VAV_OTHER (economizer) | VAV_OTHER (economizer) | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialDryBulb | DifferentialDryBulb | [6 empty] | 2021-05-06
KS_PS_PSZ-AC_2:5 (economizer) | PSZ-AC_2:5 (economizer) | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialDryBulb | DifferentialDryBulb | [6 empty] | 2021-05-06
KS_PS_PSZ-AC_1:6 (economizer) | PSZ-AC_1:6 (economizer) | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialDryBulb | DifferentialDryBulb | [6 empty] | 2021-05-06
KS_PS_PSZ-AC_2:7 (economizer) | PSZ-AC_2:7 (economizer) | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialDryBulb | DifferentialDryBulb | [6 empty] | 2021-05-06
KS_PS_VAV_Pod_1_ERV Flag | VAV_Pod_1_ERV Flag | Yes | Yes | Yes | Yes | [6 empty] | 2021-05-06
KS_PS_VAV_Pod_2_ERV Flag | VAV_Pod_2_ERV Flag | Yes | Yes | Yes | Yes | [6 empty] | 2021-05-06
KS_PS_VAV_Pod_3_ERV Flag | VAV_Pod_3_ERV Flag | Yes | Yes | Yes | Yes | [6 empty] | 2021-05-06
KS_PS_VAV_OTHER_ERV Flag | VAV_OTHER_ERV Flag | Yes | Yes | Yes | Yes | [6 empty] | 2021-05-06
KS_PS_PSZ_AC_2_5_ERV Flag | PSZ_AC_2_5_ERV Flag | No | No | No | No | [6 empty] | 2021-05-06
KS_PS_PSZ_AC_2_7_ERV Flag | PSZ_AC_2_7_ERV Flag | Yes | Yes | Yes | Yes | [6 empty] | 2021-05-06
KS_PS_HEATSYS1 Capacity [MMBTU/h] | HEATSYS1 Capacity [MMBTU/h] | 1.1823 | 1.1239 | 1.2322 | 1.1572 | [6 empty] | 2021-05-06
KS_PS_HEATSYS1 Flow Rate [gal/min] | HEATSYS1 Flow Rate [gal/min] | 121.3391 | 115.3482 | 126.4597 | 118.7693 | [6 empty] | 2021-05-06
KS_PS_VAV_POD_1 Fan Power [hp] | VAV_POD_1 Fan Power [hp] | 8.9548 | 8.5396 | 9.8798 | 9.3087 | [6 empty] | 2021-05-06
KS_PS_VAV_POD_2 Fan Power [hp] | VAV_POD_2 Fan Power [hp] | 8.9279 | 8.4422 | 9.7797 | 9.1484 | [6 empty] | 2021-05-06
KS_PS_VAV_POD_3 Fan Power [hp] | VAV_POD_3 Fan Power [hp] | 8.2201 | 7.7409 | 9.0645 | 8.5399 | [6 empty] | 2021-05-06
KS_PS_VAV_OTHER Fan Power [hp] | VAV_OTHER Fan Power [hp] | 12.4881 | 11.8006 | 13.8224 | 13.0149 | [6 empty] | 2021-05-06
KS_PS_HEATSYS1 Pump Power [hp] | HEATSYS1 Pump Power [hp] | 2.6228 | 2.4686 | 2.7335 | 2.5419 | [6 empty] | 2021-05-06
KS_PS_PSZ-AC_1:6 Heating Capacity [kBtu/hr] | PSZ-AC_1:6 Heating Capacity [kBtu/hr] | 217.3973 | 208.8218 | 215.7131 | 207.1897 | [6 empty] | 2021-05-06
KS_PS_PSZ-AC_2:5 Heating Capacity [kBtu/hr] | PSZ-AC_2:5 Heating Capacity [kBtu/hr] | 146.6268 | 146.3465 | 140.7972 | 140.4743 | [6 empty] | 2021-05-06
KS_PS_PSZ-AC_2:7 Heating Capacity [kBtu/hr] | PSZ-AC_2:7 Heating Capacity [kBtu/hr] | 341.6006 | 341.6006 | 316.7235 | 316.7235 | [6 empty] | 2021-05-06
KS_PS_ZN_VAV_BOXes_Max_Reheat_Water_Flow_GPM | ZN_VAV_BOXes_Max_Reheat_Water_Flow_GPM | 75.3181 | 71.793 | 78.3372 | 73.5133 | [6 empty] | 2021-05-06
id | item | Zone4A(KS-Topeka-KS) ASHRAE901-state_STD2016 | Zone4A(KS-Topeka-KS) ASHRAE901-state_STD2019 | Zone5A(KS-Goodland-KS) ASHRAE901-state_STD2016 | Zone5A(KS-Goodland-KS) ASHRAE901-state_STD2019 | [6 empty] | 2021-05-06
KS_SH_SAC_FRONTOFFICE Cooling Capacity [ton] | SAC_FRONTOFFICE Cooling Capacity [ton] | 2.5937 | 2.4538 | 2.3184 | 2.2069 | [6 empty] | 2021-05-06
KS_SH_SAC_FRONTLOUNGE Cooling Capacity [ton] | SAC_FRONTLOUNGE Cooling Capacity [ton] | 6.41 | 6.0939 | 6.1668 | 5.9262 | [6 empty] | 2021-05-06
KS_SH_SAC_MEETINGROOM Cooling Capacity [ton] | SAC_MEETINGROOM Cooling Capacity [ton] | 3.0483 | 2.9425 | 3.1855 | 3.1084 | [6 empty] | 2021-05-06
KS_SH_SAC_EXC_EMPLGE_RESTRM Cooling Capacity [ton] | SAC_EXC_EMPLGE_RESTRM Cooling Capacity [ton] | 6.3629 | 6.3191 | 6.1179 | 6.0727 | [6 empty] | 2021-05-06
KS_SH_SAC_FO_ADDAQ SUPPLY FAN Supply Flow Rate [cfm] | SAC_FO_ADDAQ SUPPLY FAN Supply Flow Rate [cfm] | 847.552 | 783.9856 | 911.1184 | 847.552 | [6 empty] | 2021-05-06
KS_SH_SAC_FL_ADDAQ SUPPLY FAN Supply Flow Rate [cfm] | SAC_FL_ADDAQ SUPPLY FAN Supply Flow Rate [cfm] | 1928.1808 | 1822.2368 | 2118.88 | 2012.936 | [6 empty] | 2021-05-06
KS_SH_SAC_MR_ADDAQ SUPPLY FAN Supply Flow Rate [cfm] | SAC_MR_ADDAQ SUPPLY FAN Supply Flow Rate [cfm] | 911.1184 | 889.9296 | 995.8736 | 974.6848 | [6 empty] | 2021-05-06
KS_SH_SAC_EXC_ADDAQ SUPPLY FAN Supply Flow Rate [cfm] | SAC_EXC_ADDAQ SUPPLY FAN Supply Flow Rate [cfm] | 2267.2016 | 2246.0128 | 2500.2784 | 2479.0896 | [6 empty] | 2021-05-06
KS_SH_SAC_Exc_EmpLge_RestRm OA Rate [cfm] | SAC_Exc_EmpLge_RestRm OA Rate [cfm] | 199.9928 | 199.9928 | 199.9928 | 199.9928 | [6 empty] | 2021-05-06
KS_SH_SAC_FrontLounge OA Rate [cfm] | SAC_FrontLounge OA Rate [cfm] | 500.0133 | 500.0133 | 500.0133 | 500.0133 | [6 empty] | 2021-05-06
KS_SH_SAC_FrontOffice OA Rate [cfm] | SAC_FrontOffice OA Rate [cfm] | 119.2938 | 119.2938 | 119.2938 | 119.2938 | [6 empty] | 2021-05-06
KS_SH_SAC_MeetingRoom OA Rate [cfm] | SAC_MeetingRoom OA Rate [cfm] | 267.7629 | 267.7629 | 267.7629 | 267.7629 | [6 empty] | 2021-05-06
KS_SH_SAC_FrontLounge OA Damper [gravity, motorized] | SAC_FrontLounge OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2021-05-06
KS_SH_SAC_FrontOffice (economizer) | SAC_FrontOffice (economizer) | No | No | No | No | [6 empty] | 2021-05-06
KS_SH_SAC_FrontLounge (economizer) | SAC_FrontLounge (economizer) | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialDryBulb | DifferentialDryBulb | [6 empty] | 2021-05-06
KS_SH_SAC_MeetingRoom (economizer) | SAC_MeetingRoom (economizer) | No | No | No | No | [6 empty] | 2021-05-06
KS_SH_SAC_Exc_EmpLge_RestRm (economizer) | SAC_Exc_EmpLge_RestRm (economizer) | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialDryBulb | DifferentialDryBulb | [6 empty] | 2021-05-06
KS_SH_SAC_FRONTOFFICE Heating Capacity [kBtu/hr] | SAC_FRONTOFFICE Heating Capacity [kBtu/hr] | 38.6636 | 36.4821 | 37.2876 | 35.3588 | [6 empty] | 2021-05-06
KS_SH_SAC_FRONTLOUNGE Heating Capacity [kBtu/hr] | SAC_FRONTLOUNGE Heating Capacity [kBtu/hr] | 104.9215 | 101.5396 | 102.0806 | 98.7336 | [6 empty] | 2021-05-06
KS_SH_SAC_MEETINGROOM Heating Capacity [kBtu/hr] | SAC_MEETINGROOM Heating Capacity [kBtu/hr] | 52.0741 | 50.9421 | 50.5001 | 49.4872 | [6 empty] | 2021-05-06
KS_SH_SAC_EXC_EMPLGE_RESTRM Heating Capacity [kBtu/hr] | SAC_EXC_EMPLGE_RESTRM Heating Capacity [kBtu/hr] | 95.1576 | 94.4839 | 93.8759 | 93.209 | [6 empty] | 2021-05-06
id | item | Zone4A(KS-Topeka-KS) ASHRAE901-state_STD2016 | Zone4A(KS-Topeka-KS) ASHRAE901-state_STD2019 | Zone5A(KS-Goodland-KS) ASHRAE901-state_STD2016 | Zone5A(KS-Goodland-KS) ASHRAE901-state_STD2019 | [6 empty] | 2021-05-06
KS_MA_SPLIT GSW COOLING COIL Cooling Capacity [ton] | SPLIT GSW COOLING COIL Cooling Capacity [ton] | 1.0003 | 0.9862 | 0.84203 | 0.82487 | [6 empty] | 2021-05-06
KS_MA_SPLIT GNW COOLING COIL Cooling Capacity [ton] | SPLIT GNW COOLING COIL Cooling Capacity [ton] | 0.96168 | 0.94784 | 0.80909 | 0.79249 | [6 empty] | 2021-05-06
KS_MA_SPLIT OFFICE COOLING COIL Cooling Capacity [ton] | SPLIT OFFICE COOLING COIL Cooling Capacity [ton] | 1.8167 | 1.6978 | 1.8781 | 1.7068 | [6 empty] | 2021-05-06
KS_MA_SPLIT GNE COOLING COIL Cooling Capacity [ton] | SPLIT GNE COOLING COIL Cooling Capacity [ton] | 0.84372 | 0.83161 | 0.66655 | 0.6532 | [6 empty] | 2021-05-06
KS_MA_SPLIT GN1 COOLING COIL Cooling Capacity [ton] | SPLIT GN1 COOLING COIL Cooling Capacity [ton] | 0.69786 | 0.68859 | 0.5499 | 0.53862 | [6 empty] | 2021-05-06
KS_MA_SPLIT GN2 COOLING COIL Cooling Capacity [ton] | SPLIT GN2 COOLING COIL Cooling Capacity [ton] | 0.69544 | 0.68623 | 0.54698 | 0.53575 | [6 empty] | 2021-05-06
KS_MA_SPLIT GS1 COOLING COIL Cooling Capacity [ton] | SPLIT GS1 COOLING COIL Cooling Capacity [ton] | 0.73972 | 0.72674 | 0.58788 | 0.57743 | [6 empty] | 2021-05-06
KS_MA_SPLIT GS2 COOLING COIL Cooling Capacity [ton] | SPLIT GS2 COOLING COIL Cooling Capacity [ton] | 0.77153 | 0.75744 | 0.62345 | 0.60599 | [6 empty] | 2021-05-06
KS_MA_SPLIT MSW COOLING COIL Cooling Capacity [ton] | SPLIT MSW COOLING COIL Cooling Capacity [ton] | 2.3221 | 2.2898 | 2.0888 | 2.05 | [6 empty] | 2021-05-06
KS_MA_SPLIT MNW COOLING COIL Cooling Capacity [ton] | SPLIT MNW COOLING COIL Cooling Capacity [ton] | 2.2651 | 2.2333 | 2.0217 | 1.984 | [6 empty] | 2021-05-06
KS_MA_SPLIT MSE COOLING COIL Cooling Capacity [ton] | SPLIT MSE COOLING COIL Cooling Capacity [ton] | 2.0149 | 1.9881 | 1.7238 | 1.6961 | [6 empty] | 2021-05-06
KS_MA_SPLIT MNE COOLING COIL Cooling Capacity [ton] | SPLIT MNE COOLING COIL Cooling Capacity [ton] | 1.8602 | 1.8293 | 1.5518 | 1.5253 | [6 empty] | 2021-05-06
KS_MA_SPLIT MN1 COOLING COIL Cooling Capacity [ton] | SPLIT MN1 COOLING COIL Cooling Capacity [ton] | 1.502 | 1.4837 | 1.2303 | 1.2089 | [6 empty] | 2021-05-06
KS_MA_SPLIT MN2 COOLING COIL Cooling Capacity [ton] | SPLIT MN2 COOLING COIL Cooling Capacity [ton] | 1.4954 | 1.4773 | 1.2222 | 1.2009 | [6 empty] | 2021-05-06
KS_MA_SPLIT MS1 COOLING COIL Cooling Capacity [ton] | SPLIT MS1 COOLING COIL Cooling Capacity [ton] | 1.5862 | 1.5669 | 1.2836 | 1.2643 | [6 empty] | 2021-05-06
KS_MA_SPLIT MS2 COOLING COIL Cooling Capacity [ton] | SPLIT MS2 COOLING COIL Cooling Capacity [ton] | 1.5806 | 1.5614 | 1.2766 | 1.2575 | [6 empty] | 2021-05-06
KS_MA_SPLIT TSW COOLING COIL Cooling Capacity [ton] | SPLIT TSW COOLING COIL Cooling Capacity [ton] | 1.444 | 1.4266 | 1.3533 | 1.3323 | [6 empty] | 2021-05-06
KS_MA_SPLIT TNW COOLING COIL Cooling Capacity [ton] | SPLIT TNW COOLING COIL Cooling Capacity [ton] | 1.4101 | 1.393 | 1.3117 | 1.291 | [6 empty] | 2021-05-06
KS_MA_SPLIT TSE COOLING COIL Cooling Capacity [ton] | SPLIT TSE COOLING COIL Cooling Capacity [ton] | 1.2952 | 1.2814 | 1.1316 | 1.1173 | [6 empty] | 2021-05-06
KS_MA_SPLIT TNE COOLING COIL Cooling Capacity [ton] | SPLIT TNE COOLING COIL Cooling Capacity [ton] | 1.2318 | 1.2189 | 1.061 | 1.0478 | [6 empty] | 2021-05-06
KS_MA_SPLIT TN1 COOLING COIL Cooling Capacity [ton] | SPLIT TN1 COOLING COIL Cooling Capacity [ton] | 0.97301 | 0.96353 | 0.85133 | 0.841 | [6 empty] | 2021-05-06
KS_MA_SPLIT TN2 COOLING COIL Cooling Capacity [ton] | SPLIT TN2 COOLING COIL Cooling Capacity [ton] | 0.96618 | 0.95688 | 0.85628 | 0.84595 | [6 empty] | 2021-05-06
KS_MA_SPLIT TS1 COOLING COIL Cooling Capacity [ton] | SPLIT TS1 COOLING COIL Cooling Capacity [ton] | 1.0583 | 1.0495 | 0.92379 | 0.91497 | [6 empty] | 2021-05-06
KS_MA_SPLIT TS2 COOLING COIL Cooling Capacity [ton] | SPLIT TS2 COOLING COIL Cooling Capacity [ton] | 1.0608 | 1.05 | 0.92709 | 0.91571 | [6 empty] | 2021-05-06
KS_MA_Split GN1 Furnace with DX Cooling OA Rate [cfm] | Split GN1 Furnace with DX Cooling OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | [6 empty] | 2021-05-06
KS_MA_Split GN2 Furnace with DX Cooling OA Rate [cfm] | Split GN2 Furnace with DX Cooling OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | [6 empty] | 2021-05-06
KS_MA_Split GNE Furnace with DX Cooling OA Rate [cfm] | Split GNE Furnace with DX Cooling OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | [6 empty] | 2021-05-06
KS_MA_Split GNW Furnace with DX Cooling OA Rate [cfm] | Split GNW Furnace with DX Cooling OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | [6 empty] | 2021-05-06
KS_MA_Split GS1 Furnace with DX Cooling OA Rate [cfm] | Split GS1 Furnace with DX Cooling OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | [6 empty] | 2021-05-06
KS_MA_Split GS2 Furnace with DX Cooling OA Rate [cfm] | Split GS2 Furnace with DX Cooling OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | [6 empty] | 2021-05-06
KS_MA_Split GSW Furnace with DX Cooling OA Rate [cfm] | Split GSW Furnace with DX Cooling OA Rate [cfm] | 56.9945 | 56.9945 | 56.9945 | 56.9945 | [6 empty] | 2021-05-06
KS_MA_Split MN1 Furnace with DX Cooling OA Rate [cfm] | Split MN1 Furnace with DX Cooling OA Rate [cfm] | 109.9824 | 109.9824 | 109.9824 | 109.9824 | [6 empty] | 2021-05-06
KS_MA_Split MN2 Furnace with DX Cooling OA Rate [cfm] | Split MN2 Furnace with DX Cooling OA Rate [cfm] | 109.9824 | 109.9824 | 109.9824 | 109.9824 | [6 empty] | 2021-05-06
KS_MA_Split MNE Furnace with DX Cooling OA Rate [cfm] | Split MNE Furnace with DX Cooling OA Rate [cfm] | 109.9824 | 109.9824 | 109.9824 | 109.9824 | [6 empty] | 2021-05-06
KS_MA_Split MNW Furnace with DX Cooling OA Rate [cfm] | Split MNW Furnace with DX Cooling OA Rate [cfm] | 109.9824 | 109.9824 | 109.9824 | 109.9824 | [6 empty] | 2021-05-06
KS_MA_Split MS1 Furnace with DX Cooling OA Rate [cfm] | Split MS1 Furnace with DX Cooling OA Rate [cfm] | 109.9824 | 109.9824 | 109.9824 | 109.9824 | [6 empty] | 2021-05-06
KS_MA_Split MS2 Furnace with DX Cooling OA Rate [cfm] | Split MS2 Furnace with DX Cooling OA Rate [cfm] | 109.9824 | 109.9824 | 109.9824 | 109.9824 | [6 empty] | 2021-05-06
KS_MA_Split MSE Furnace with DX Cooling OA Rate [cfm] | Split MSE Furnace with DX Cooling OA Rate [cfm] | 109.9824 | 109.9824 | 109.9824 | 109.9824 | [6 empty] | 2021-05-06
KS_MA_Split MSW Furnace with DX Cooling OA Rate [cfm] | Split MSW Furnace with DX Cooling OA Rate [cfm] | 109.9824 | 109.9824 | 109.9824 | 109.9824 | [6 empty] | 2021-05-06
KS_MA_Split Office Furnace with DX Cooling OA Rate [cfm] | Split Office Furnace with DX Cooling OA Rate [cfm] | 80.7372 | 80.7372 | 80.7372 | 80.7372 | [6 empty] | 2021-05-06
KS_MA_Split TN1 Furnace with DX Cooling OA Rate [cfm] | Split TN1 Furnace with DX Cooling OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | [6 empty] | 2021-05-06
KS_MA_Split TN2 Furnace with DX Cooling OA Rate [cfm] | Split TN2 Furnace with DX Cooling OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | [6 empty] | 2021-05-06
KS_MA_Split TNE Furnace with DX Cooling OA Rate [cfm] | Split TNE Furnace with DX Cooling OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | [6 empty] | 2021-05-06
KS_MA_Split TNW Furnace with DX Cooling OA Rate [cfm] | Split TNW Furnace with DX Cooling OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | [6 empty] | 2021-05-06
KS_MA_Split TS1 Furnace with DX Cooling OA Rate [cfm] | Split TS1 Furnace with DX Cooling OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | [6 empty] | 2021-05-06
KS_MA_Split TS2 Furnace with DX Cooling OA Rate [cfm] | Split TS2 Furnace with DX Cooling OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | [6 empty] | 2021-05-06
KS_MA_Split TSE Furnace with DX Cooling OA Rate [cfm] | Split TSE Furnace with DX Cooling OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | [6 empty] | 2021-05-06
KS_MA_Split TSW Furnace with DX Cooling OA Rate [cfm] | Split TSW Furnace with DX Cooling OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | [6 empty] | 2021-05-06
KS_MA_SPLIT GSW HEATING COIL Heating Capacity [kBtu/hr] | SPLIT GSW HEATING COIL Heating Capacity [kBtu/hr] | 10.3549 | 10.4139 | 10.5249 | 10.5846 | [6 empty] | 2021-05-06
KS_MA_SPLIT GNW HEATING COIL Heating Capacity [kBtu/hr] | SPLIT GNW HEATING COIL Heating Capacity [kBtu/hr] | 10.2804 | 10.3396 | 10.4233 | 10.4831 | [6 empty] | 2021-05-06
KS_MA_SPLIT OFFICE HEATING COIL Heating Capacity [kBtu/hr] | SPLIT OFFICE HEATING COIL Heating Capacity [kBtu/hr] | 23.3459 | 23.4205 | 23.3244 | 23.4053 | [6 empty] | 2021-05-06
KS_MA_SPLIT GNE HEATING COIL Heating Capacity [kBtu/hr] | SPLIT GNE HEATING COIL Heating Capacity [kBtu/hr] | 10.2562 | 10.3154 | 10.3948 | 10.4546 | [6 empty] | 2021-05-06
KS_MA_SPLIT GN1 HEATING COIL Heating Capacity [kBtu/hr] | SPLIT GN1 HEATING COIL Heating Capacity [kBtu/hr] | 7.6054 | 7.6646 | 7.5707 | 7.6305 | [6 empty] | 2021-05-06
KS_MA_SPLIT GN2 HEATING COIL Heating Capacity [kBtu/hr] | SPLIT GN2 HEATING COIL Heating Capacity [kBtu/hr] | 7.6047 | 7.6639 | 7.5698 | 7.6297 | [6 empty] | 2021-05-06
KS_MA_SPLIT GS1 HEATING COIL Heating Capacity [kBtu/hr] | SPLIT GS1 HEATING COIL Heating Capacity [kBtu/hr] | 7.5502 | 7.6093 | 7.5526 | 7.6123 | [6 empty] | 2021-05-06
KS_MA_SPLIT GS2 HEATING COIL Heating Capacity [kBtu/hr] | SPLIT GS2 HEATING COIL Heating Capacity [kBtu/hr] | 8.0594 | 8.1191 | 8.0624 | 8.123 | [6 empty] | 2021-05-06
KS_MA_SPLIT MSW HEATING COIL Heating Capacity [kBtu/hr] | SPLIT MSW HEATING COIL Heating Capacity [kBtu/hr] | 18.6167 | 18.7452 | 19.1697 | 19.2988 | [6 empty] | 2021-05-06
KS_MA_SPLIT MNW HEATING COIL Heating Capacity [kBtu/hr] | SPLIT MNW HEATING COIL Heating Capacity [kBtu/hr] | 18.7146 | 18.8431 | 19.1813 | 19.3104 | [6 empty] | 2021-05-06
KS_MA_SPLIT MSE HEATING COIL Heating Capacity [kBtu/hr] | SPLIT MSE HEATING COIL Heating Capacity [kBtu/hr] | 18.5594 | 18.688 | 19.103 | 19.2322 | [6 empty] | 2021-05-06
KS_MA_SPLIT MNE HEATING COIL Heating Capacity [kBtu/hr] | SPLIT MNE HEATING COIL Heating Capacity [kBtu/hr] | 18.6573 | 18.7859 | 19.1146 | 19.2437 | [6 empty] | 2021-05-06
KS_MA_SPLIT MN1 HEATING COIL Heating Capacity [kBtu/hr] | SPLIT MN1 HEATING COIL Heating Capacity [kBtu/hr] | 13.0269 | 13.1527 | 13.1109 | 13.2368 | [6 empty] | 2021-05-06
KS_MA_SPLIT MN2 HEATING COIL Heating Capacity [kBtu/hr] | SPLIT MN2 HEATING COIL Heating Capacity [kBtu/hr] | 13.0254 | 13.1512 | 13.1091 | 13.235 | [6 empty] | 2021-05-06
KS_MA_SPLIT MS1 HEATING COIL Heating Capacity [kBtu/hr] | SPLIT MS1 HEATING COIL Heating Capacity [kBtu/hr] | 12.938 | 13.0639 | 13.1084 | 13.2343 | [6 empty] | 2021-05-06
KS_MA_SPLIT MS2 HEATING COIL Heating Capacity [kBtu/hr] | SPLIT MS2 HEATING COIL Heating Capacity [kBtu/hr] | 12.9365 | 13.0624 | 13.1066 | 13.2325 | [6 empty] | 2021-05-06
KS_MA_SPLIT TSW HEATING COIL Heating Capacity [kBtu/hr] | SPLIT TSW HEATING COIL Heating Capacity [kBtu/hr] | 12.996 | 13.0578 | 13.5618 | 13.6237 | [6 empty] | 2021-05-06
KS_MA_SPLIT TNW HEATING COIL Heating Capacity [kBtu/hr] | SPLIT TNW HEATING COIL Heating Capacity [kBtu/hr] | 13.0539 | 13.1158 | 13.5741 | 13.636 | [6 empty] | 2021-05-06
KS_MA_SPLIT TSE HEATING COIL Heating Capacity [kBtu/hr] | SPLIT TSE HEATING COIL Heating Capacity [kBtu/hr] | 12.9657 | 13.0275 | 13.5268 | 13.5886 | [6 empty] | 2021-05-06
KS_MA_SPLIT TNE HEATING COIL Heating Capacity [kBtu/hr] | SPLIT TNE HEATING COIL Heating Capacity [kBtu/hr] | 13.0235 | 13.0854 | 13.539 | 13.601 | [6 empty] | 2021-05-06
KS_MA_SPLIT TN1 HEATING COIL Heating Capacity [kBtu/hr] | SPLIT TN1 HEATING COIL Heating Capacity [kBtu/hr] | 10.0122 | 10.074 | 10.2594 | 10.3211 | [6 empty] | 2021-05-06
KS_MA_SPLIT TN2 HEATING COIL Heating Capacity [kBtu/hr] | SPLIT TN2 HEATING COIL Heating Capacity [kBtu/hr] | 10.0114 | 10.0731 | 10.2583 | 10.3202 | [6 empty] | 2021-05-06
KS_MA_SPLIT TS1 HEATING COIL Heating Capacity [kBtu/hr] | SPLIT TS1 HEATING COIL Heating Capacity [kBtu/hr] | 9.9476 | 10.0092 | 10.2411 | 10.3028 | [6 empty] | 2021-05-06
KS_MA_SPLIT TS2 HEATING COIL Heating Capacity [kBtu/hr] | SPLIT TS2 HEATING COIL Heating Capacity [kBtu/hr] | 9.9467 | 10.0084 | 10.2401 | 10.3018 | [6 empty] | 2021-05-06
KS_MA_Split_GSW ERV Flag | Split_GSW ERV Flag | Yes | Yes | Yes | Yes | [6 empty] | 2021-05-06
KS_MA_Split_GNW ERV Flag | Split_GNW ERV Flag | Yes | Yes | Yes | Yes | [6 empty] | 2021-05-06
KS_MA_Split_GNE ERV Flag | Split_GNE ERV Flag | Yes | Yes | Yes | Yes | [6 empty] | 2021-05-06
KS_MA_Split_GN1 ERV Flag | Split_GN1 ERV Flag | Yes | Yes | Yes | Yes | [6 empty] | 2021-05-06
KS_MA_Split_GN2 ERV Flag | Split_GN2 ERV Flag | Yes | Yes | Yes | Yes | [6 empty] | 2021-05-06
KS_MA_Split_GS1 ERV Flag | Split_GS1 ERV Flag | Yes | Yes | Yes | Yes | [6 empty] | 2021-05-06
KS_MA_Split_GS2 ERV Flag | Split_GS2 ERV Flag | Yes | Yes | Yes | Yes | [6 empty] | 2021-05-06
KS_MA_Split_MSW ERV Flag | Split_MSW ERV Flag | Yes | Yes | Yes | Yes | [6 empty] | 2021-05-06
KS_MA_Split_MNW ERV Flag | Split_MNW ERV Flag | Yes | Yes | Yes | Yes | [6 empty] | 2021-05-06
KS_MA_Split_MSE ERV Flag | Split_MSE ERV Flag | Yes | Yes | Yes | Yes | [6 empty] | 2021-05-06
KS_MA_Split_MNE ERV Flag | Split_MNE ERV Flag | Yes | Yes | Yes | Yes | [6 empty] | 2021-05-06
KS_MA_Split_MN1 ERV Flag | Split_MN1 ERV Flag | Yes | Yes | Yes | Yes | [6 empty] | 2021-05-06
KS_MA_Split_MN2 ERV Flag | Split_MN2 ERV Flag | Yes | Yes | Yes | Yes | [6 empty] | 2021-05-06
KS_MA_Split_MS1 ERV Flag | Split_MS1 ERV Flag | Yes | Yes | Yes | Yes | [6 empty] | 2021-05-06
KS_MA_Split_MS2 ERV Flag | Split_MS2 ERV Flag | Yes | Yes | Yes | Yes | [6 empty] | 2021-05-06
KS_MA_Split_TSW ERV Flag | Split_TSW ERV Flag | No | No | No | No | [6 empty] | 2021-05-06
KS_MA_Split_TNW ERV Flag | Split_TNW ERV Flag | No | Yes | No | No | [6 empty] | 2021-05-06
KS_MA_Split_TSE ERV Flag | Split_TSE ERV Flag | Yes | Yes | Yes | Yes | [6 empty] | 2021-05-06
KS_MA_Split_TNE ERV Flag | Split_TNE ERV Flag | Yes | Yes | Yes | Yes | [6 empty] | 2021-05-06
KS_MA_Split_TN1 ERV Flag | Split_TN1 ERV Flag | Yes | Yes | Yes | Yes | [6 empty] | 2021-05-06
KS_MA_Split_TN2 ERV Flag | Split_TN2 ERV Flag | Yes | Yes | Yes | Yes | [6 empty] | 2021-05-06
KS_MA_Split_TS1 ERV Flag | Split_TS1 ERV Flag | Yes | Yes | Yes | Yes | [6 empty] | 2021-05-06
KS_MA_Split_TS2 ERV Flag | Split_TS2 ERV Flag | Yes | Yes | Yes | Yes | [6 empty] | 2021-05-06
id | item | Zone4A(KY-Lexington-KY) ASHRAE901-state_STD2016 | Zone4A(KY-Lexington-KY) ASHRAE901-state_STD2019 | [8 empty] | 2021-05-06
KY_SO_PSZ-AC:1 Cooling Capacity [ton] | PSZ-AC:1 Cooling Capacity [ton] | 1.86 | 1.7668 | [8 empty] | 2021-05-06
KY_SO_PSZ-AC:2 Cooling Capacity [ton] | PSZ-AC:2 Cooling Capacity [ton] | 1.6152 | 1.5524 | [8 empty] | 2021-05-06
KY_SO_PSZ-AC:3 Cooling Capacity [ton] | PSZ-AC:3 Cooling Capacity [ton] | 1.142 | 1.1029 | [8 empty] | 2021-05-06
KY_SO_PSZ-AC:4 Cooling Capacity [ton] | PSZ-AC:4 Cooling Capacity [ton] | 1.5772 | 1.4947 | [8 empty] | 2021-05-06
KY_SO_PSZ-AC:5 Cooling Capacity [ton] | PSZ-AC:5 Cooling Capacity [ton] | 1.3203 | 1.2806 | [8 empty] | 2021-05-06
KY_SO_PSZ-AC:1 Supply Flow Rate [cfm] | PSZ-AC:1 Supply Flow Rate [cfm] | 656.8528 | 614.4752 | [8 empty] | 2021-05-06
KY_SO_PSZ-AC:2 Supply Flow Rate [cfm] | PSZ-AC:2 Supply Flow Rate [cfm] | 593.2864 | 572.0976 | [8 empty] | 2021-05-06
KY_SO_PSZ-AC:3 Supply Flow Rate [cfm] | PSZ-AC:3 Supply Flow Rate [cfm] | 466.1536 | 444.9648 | [8 empty] | 2021-05-06
KY_SO_PSZ-AC:4 Supply Flow Rate [cfm] | PSZ-AC:4 Supply Flow Rate [cfm] | 572.0976 | 529.72 | [8 empty] | 2021-05-06
KY_SO_PSZ-AC:5 Supply Flow Rate [cfm] | PSZ-AC:5 Supply Flow Rate [cfm] | 550.9088 | 529.72 | [8 empty] | 2021-05-06
KY_SO_PSZ-AC:1 OA Rate [cfm] | PSZ-AC:1 OA Rate [cfm] | 136.9178 | 136.9178 | [8 empty] | 2021-05-06
KY_SO_PSZ-AC:2 OA Rate [cfm] | PSZ-AC:2 OA Rate [cfm] | 103.7925 | 103.7925 | [8 empty] | 2021-05-06
KY_SO_PSZ-AC:3 OA Rate [cfm] | PSZ-AC:3 OA Rate [cfm] | 61.5711 | 61.5711 | [8 empty] | 2021-05-06
KY_SO_PSZ-AC:4 OA Rate [cfm] | PSZ-AC:4 OA Rate [cfm] | 103.7925 | 103.7925 | [8 empty] | 2021-05-06
KY_SO_PSZ-AC:5 OA Rate [cfm] | PSZ-AC:5 OA Rate [cfm] | 61.5711 | 61.5711 | [8 empty] | 2021-05-06
KY_SO_PSZ-AC:1 heating Capacity [kBtu/hr] | PSZ-AC:1 heating Capacity [kBtu/hr] | 14.0163 | 14.0163 | [8 empty] | 2021-05-06
KY_SO_PSZ-AC:2 heating Capacity [kBtu/hr] | PSZ-AC:2 heating Capacity [kBtu/hr] | 19.3026 | 19.0929 | [8 empty] | 2021-05-06
KY_SO_PSZ-AC:3 heating Capacity [kBtu/hr] | PSZ-AC:3 heating Capacity [kBtu/hr] | 11.7948 | 11.6789 | [8 empty] | 2021-05-06
KY_SO_PSZ-AC:4 heating Capacity [kBtu/hr] | PSZ-AC:4 heating Capacity [kBtu/hr] | 19.2025 | 19.0235 | [8 empty] | 2021-05-06
KY_SO_PSZ-AC:5 heating Capacity [kBtu/hr] | PSZ-AC:5 heating Capacity [kBtu/hr] | 11.845 | 11.7241 | [8 empty] | 2021-05-06
id | item | Zone4A(KY-Lexington-KY) ASHRAE901-state_STD2016 | Zone4A(KY-Lexington-KY) ASHRAE901-state_STD2019 | [8 empty] | 2021-05-06
KY_LO_CAV_BAS Supply Flow Rate [cfm] | CAV_BAS Supply Flow Rate [cfm] | 12035.2384 | 11145.3088 | [8 empty] | 2021-05-06
KY_LO_VAV_BOT WITH REHEAT Supply Flow Rate [cfm] | VAV_BOT WITH REHEAT Supply Flow Rate [cfm] | 19790.3392 | 18836.8432 | [8 empty] | 2021-05-06
KY_LO_VAV_MID WITH REHEAT Supply Flow Rate [cfm] | VAV_MID WITH REHEAT Supply Flow Rate [cfm] | 183240.7427 | 174023.6147 | [8 empty] | 2021-05-06
KY_LO_VAV_TOP WITH REHEAT Supply Flow Rate [cfm] | VAV_TOP WITH REHEAT Supply Flow Rate [cfm] | 19705.584 | 18900.4096 | [8 empty] | 2021-05-06
KY_LO_Supply Air Temp. Reset Flag | Supply Air Temp. Reset Flag | Yes | Yes | [8 empty] | 2021-05-06
KY_LO_CAV_BAS OA Rate [cfm] | CAV_BAS OA Rate [cfm] | 2542.8255 | 2542.8255 | [8 empty] | 2021-05-06
KY_LO_VAV_BOT WITH REHEAT OA Rate [cfm] | VAV_BOT WITH REHEAT OA Rate [cfm] | 5377.8022 | 4302.174 | [8 empty] | 2021-05-06
KY_LO_VAV_MID WITH REHEAT OA Rate [cfm] | VAV_MID WITH REHEAT OA Rate [cfm] | 53777.9373 | 43021.7396 | [8 empty] | 2021-05-06
KY_LO_VAV_TOP WITH REHEAT OA Rate [cfm] | VAV_TOP WITH REHEAT OA Rate [cfm] | 5377.8022 | 4302.174 | [8 empty] | 2021-05-06
KY_LO_AIRLOOP DATACENTER BASEMENT OA Rate [cfm] | AIRLOOP DATACENTER BASEMENT OA Rate [cfm] | 716.9654 | 716.9654 | [8 empty] | 2021-05-06
KY_LO_VAV_bot_WITH_REHEAT ERV Flag | VAV_bot_WITH_REHEAT ERV Flag | Yes | Yes | [8 empty] | 2021-05-06
KY_LO_VAV_mid_WITH_REHEAT ERV Flag | VAV_mid_WITH_REHEAT ERV Flag | Yes | Yes | [8 empty] | 2021-05-06
KY_LO_VAV_top_WITH_REHEAT ERV Flag | VAV_top_WITH_REHEAT ERV Flag | Yes | Yes | [8 empty] | 2021-05-06
KY_LO_COOLSYS1 CHILLER1 Capacity [ton] | COOLSYS1 CHILLER1 Capacity [ton] | 402.2651 | 362.8161 | [8 empty] | 2021-05-06
KY_LO_COOLSYS1 CHILLER2 Capacity [ton] | COOLSYS1 CHILLER2 Capacity [ton] | 402.2651 | 362.8161 | [8 empty] | 2021-05-06
KY_LO_TOWERWATERSYS COOLTOWER 1 Capacity [ton] | TOWERWATERSYS COOLTOWER 1 Capacity [ton] | 381.8255 | 344.3741 | [8 empty] | 2021-05-06
KY_LO_TOWERWATERSYS COOLTOWER 2 Capacity [ton] | TOWERWATERSYS COOLTOWER 2 Capacity [ton] | 381.8255 | 344.3741 | [8 empty] | 2021-05-06
KY_LO_HEATSYS1 BOILER Capacity [MMBTU/h] | HEATSYS1 BOILER Capacity [MMBTU/h] | 4394.7878 | 3896.5011 | [8 empty] | 2021-05-06
KY_LO_COOLSYS1 PUMP Flow Rate [gal/min] | COOLSYS1 PUMP Flow Rate [gal/min] | 0 | 0 | [8 empty] | 2021-05-06
KY_LO_COOLSYS1 CHILLER1 PUMP Flow Rate [gal/min] | COOLSYS1 CHILLER1 PUMP Flow Rate [gal/min] | 633.7879 | 568.7302 | [8 empty] | 2021-05-06
KY_LO_COOLSYS1 CHILLER2 PUMP Flow Rate [gal/min] | COOLSYS1 CHILLER2 PUMP Flow Rate [gal/min] | 633.7879 | 568.7302 | [8 empty] | 2021-05-06
KY_LO_COOLSYS1 PUMP SECONDARY Flow Rate [gal/min] | COOLSYS1 PUMP SECONDARY Flow Rate [gal/min] | 1267.5757 | 1137.462 | [8 empty] | 2021-05-06
KY_LO_HEATSYS1 PUMP Flow Rate [gal/min] | HEATSYS1 PUMP Flow Rate [gal/min] | 902.0879 | 799.8089 | [8 empty] | 2021-05-06
KY_LO_TOWERWATERSYS PUMP Flow Rate [gal/min] | TOWERWATERSYS PUMP Flow Rate [gal/min] | 2219.3622 | 2001.7373 | [8 empty] | 2021-05-06
KY_LO_PLANT CIRC PUMP Flow Rate [gal/min] | PLANT CIRC PUMP Flow Rate [gal/min] | 210.4828 | 209.6427 | [8 empty] | 2021-05-06
KY_LO_COOLSYS1 PUMP SECONDARY Pressure setpoint reset [yes,no] | COOLSYS1 PUMP SECONDARY Pressure setpoint reset [yes,no] | pump_ride_on_curve | pump_ride_on_curve | [8 empty] | 2021-05-06
KY_LO_COOLSYS1 CHILLER1 PUMP Pump Power [hp] | COOLSYS1 CHILLER1 PUMP Pump Power [hp] | 3.4191 | 3.0377 | [8 empty] | 2021-05-06
KY_LO_COOLSYS1 CHILLER2 PUMP Pump Power [hp] | COOLSYS1 CHILLER2 PUMP Pump Power [hp] | 3.4191 | 3.0377 | [8 empty] | 2021-05-06
KY_LO_COOLSYS1 PUMP SECONDARY Pump Power [hp] | COOLSYS1 PUMP SECONDARY Pump Power [hp] | 20.5144 | 18.2264 | [8 empty] | 2021-05-06
KY_LO_HEATSYS1 PUMP Pump Power [hp] | HEATSYS1 PUMP Pump Power [hp] | 19.4992 | 17.1171 | [8 empty] | 2021-05-06
KY_LO_TOWERWATERSYS PUMP Pump Power [hp] | TOWERWATERSYS PUMP Pump Power [hp] | 39.7349 | 35.4834 | [8 empty] | 2021-05-06
KY_LO_PLANT CIRC PUMP Pump Power [hp] | PLANT CIRC PUMP Pump Power [hp] | 4.5419 | 4.479 | [8 empty] | 2021-05-06
KY_LO_Datacenter PLANT CIRC PUMP Pump Power [hp] | Datacenter PLANT CIRC PUMP Pump Power [hp] | 4.5419 | 4.479 | [8 empty] | 2021-05-06
KY_LO_ZN_VAV_BOXes_Max_Reheat_Water_Flow_GPM | ZN_VAV_BOXes_Max_Reheat_Water_Flow_GPM | 465.1806 | 447.6305 | [8 empty] | 2021-05-06
KY_LO_COOLSYS1 PUMP SECONDARY VSD | COOLSYS1 PUMP SECONDARY VSD | No | No | [8 empty] | 2021-05-06
KY_LO_HEATSYS1 PUMP VSD | HEATSYS1 PUMP VSD | No | No | [8 empty] | 2021-05-06
KY_LO_DATACENTER BASEMENT Cooling Capacity [ton] | DATACENTER BASEMENT Cooling Capacity [ton] | 123.2074 | 122.8428 | [8 empty] | 2021-05-06
KY_LO_DATACENTER BOT Cooling Capacity [ton] | DATACENTER BOT Cooling Capacity [ton] | 2.6836 | 2.66 | [8 empty] | 2021-05-06
KY_LO_DATACENTER MID Cooling Capacity [ton] | DATACENTER MID Cooling Capacity [ton] | 25.6756 | 25.4679 | [8 empty] | 2021-05-06
KY_LO_DATACENTER TOP Cooling Capacity [ton] | DATACENTER TOP Cooling Capacity [ton] | 2.6166 | 2.5965 | [8 empty] | 2021-05-06
id | item | Zone4A(KY-Lexington-KY) ASHRAE901-state_STD2016 | Zone4A(KY-Lexington-KY) ASHRAE901-state_STD2019 | [8 empty] | 2021-05-06
KY_RS_PSZ-AC:1 Cooling Capacity [ton] | PSZ-AC:1 Cooling Capacity [ton] | 10.3418 | 10.0157 | [8 empty] | 2021-05-06
KY_RS_PSZ-AC:2 Cooling Capacity [ton] | PSZ-AC:2 Cooling Capacity [ton] | 48.8867 | 46.904 | [8 empty] | 2021-05-06
KY_RS_PSZ-AC:3 Cooling Capacity [ton] | PSZ-AC:3 Cooling Capacity [ton] | 6.3675 | 6.2077 | [8 empty] | 2021-05-06
KY_RS_PSZ-AC:4 Cooling Capacity [ton] | PSZ-AC:4 Cooling Capacity [ton] | 5.1492 | 4.9904 | [8 empty] | 2021-05-06
KY_RS_PSZ-AC:1 Supply Flow Rate [cfm] | PSZ-AC:1 Supply Flow Rate [cfm] | 4047.0608 | 3792.7952 | [8 empty] | 2021-05-06
KY_RS_PSZ-AC:2 Supply Flow Rate [cfm] | PSZ-AC:2 Supply Flow Rate [cfm] | 15594.9568 | 14662.6496 | [8 empty] | 2021-05-06
KY_RS_PSZ-AC:3 Supply Flow Rate [cfm] | PSZ-AC:3 Supply Flow Rate [cfm] | 2309.5792 | 2224.824 | [8 empty] | 2021-05-06
KY_RS_PSZ-AC:4 Supply Flow Rate [cfm] | PSZ-AC:4 Supply Flow Rate [cfm] | 1758.6704 | 1673.9152 | [8 empty] | 2021-05-06
KY_RS_PSZ-AC:1 OA Rate [cfm] | PSZ-AC:1 OA Rate [cfm] | 490.669 | 490.669 | [8 empty] | 2021-05-06
KY_RS_PSZ-AC:2 OA Rate [cfm] | PSZ-AC:2 OA Rate [cfm] | 4005.1282 | 4005.1282 | [8 empty] | 2021-05-06
KY_RS_PSZ-AC:3 OA Rate [cfm] | PSZ-AC:3 OA Rate [cfm] | 377.3937 | 377.3937 | [8 empty] | 2021-05-06
KY_RS_PSZ-AC:4 OA Rate [cfm] | PSZ-AC:4 OA Rate [cfm] | 377.3937 | 377.3937 | [8 empty] | 2021-05-06
KY_RS_PSZ-AC:1 OA Damper [gravity, motorized] | PSZ-AC:1 OA Damper [gravity, motorized] | motorized | motorized | [8 empty] | 2021-05-06
KY_RS_PSZ-AC:2 OA Damper [gravity, motorized] | PSZ-AC:2 OA Damper [gravity, motorized] | motorized | motorized | [8 empty] | 2021-05-06
KY_RS_PSZ-AC:3 OA Damper [gravity, motorized] | PSZ-AC:3 OA Damper [gravity, motorized] | motorized | motorized | [8 empty] | 2021-05-06
KY_RS_PSZ-AC:4 OA Damper [gravity, motorized] | PSZ-AC:4 OA Damper [gravity, motorized] | motorized | motorized | [8 empty] | 2021-05-06
KY_RS_PSZ-AC:1 Heating Capacity [kBtu/hr] | PSZ-AC:1 Heating Capacity [kBtu/hr] | 176.8311 | 166.4163 | [8 empty] | 2021-05-06
KY_RS_PSZ-AC:2 Heating Capacity [kBtu/hr] | PSZ-AC:2 Heating Capacity [kBtu/hr] | 811.7908 | 774.8251 | [8 empty] | 2021-05-06
KY_RS_PSZ-AC:3 Heating Capacity [kBtu/hr] | PSZ-AC:3 Heating Capacity [kBtu/hr] | 107.6694 | 105.0102 | [8 empty] | 2021-05-06
KY_RS_PSZ-AC:4 Heating Capacity [kBtu/hr] | PSZ-AC:4 Heating Capacity [kBtu/hr] | 87.6314 | 84.7821 | [8 empty] | 2021-05-06
id | item | Zone4A(KY-Lexington-KY) ASHRAE901-state_STD2016 | Zone4A(KY-Lexington-KY) ASHRAE901-state_STD2019 | [8 empty] | 2021-05-06
KY_PS_VAV_POD_1 Cooling Capacity [ton] | VAV_POD_1 Cooling Capacity [ton] | 19.4059 | 18.7054 | [8 empty] | 2021-05-06
KY_PS_VAV_POD_2 Cooling Capacity [ton] | VAV_POD_2 Cooling Capacity [ton] | 19.1664 | 18.5177 | [8 empty] | 2021-05-06
KY_PS_VAV_POD_3 Cooling Capacity [ton] | VAV_POD_3 Cooling Capacity [ton] | 17.7383 | 16.858 | [8 empty] | 2021-05-06
KY_PS_VAV_OTHER Cooling Capacity [ton] | VAV_OTHER Cooling Capacity [ton] | 27.4253 | 25.8093 | [8 empty] | 2021-05-06
KY_PS_PSZ-AC_1:6 Cooling Capacity [ton] | PSZ-AC_1:6 Cooling Capacity [ton] | 8.3933 | 8.1278 | [8 empty] | 2021-05-06
KY_PS_PSZ-AC_2:5 Cooling Capacity [ton] | PSZ-AC_2:5 Cooling Capacity [ton] | 5.6369 | 5.6178 | [8 empty] | 2021-05-06
KY_PS_PSZ-AC_2:7 Cooling Capacity [ton] | PSZ-AC_2:7 Cooling Capacity [ton] | 10.5074 | 10.5074 | [8 empty] | 2021-05-06
KY_PS_VAV_POD_1 Supply Flow Rate [cfm] | VAV_POD_1 Supply Flow Rate [cfm] | 5826.92 | 5615.032 | [8 empty] | 2021-05-06
KY_PS_VAV_POD_2 Supply Flow Rate [cfm] | VAV_POD_2 Supply Flow Rate [cfm] | 5742.1648 | 5551.4656 | [8 empty] | 2021-05-06
KY_PS_VAV_POD_3 Supply Flow Rate [cfm] | VAV_POD_3 Supply Flow Rate [cfm] | 5318.3888 | 5064.1232 | [8 empty] | 2021-05-06
KY_PS_VAV_OTHER Supply Flow Rate [cfm] | VAV_OTHER Supply Flow Rate [cfm] | 8221.2544 | 7755.1008 | [8 empty] | 2021-05-06
KY_PS_PSZ-AC_2:5 Supply Flow Rate [cfm] | PSZ-AC_2:5 Supply Flow Rate [cfm] | 1695.104 | 1695.104 | [8 empty] | 2021-05-06
KY_PS_PSZ-AC_1:6 Supply Flow Rate [cfm] | PSZ-AC_1:6 Supply Flow Rate [cfm] | 2627.4112 | 2500.2784 | [8 empty] | 2021-05-06
KY_PS_PSZ-AC_2:7 Supply Flow Rate [cfm] | PSZ-AC_2:7 Supply Flow Rate [cfm] | 3157.1312 | 3157.1312 | [8 empty] | 2021-05-06
KY_PS_Supply Air Temp. Reset Flag | Supply Air Temp. Reset Flag | Yes | Yes | [8 empty] | 2021-05-06
KY_PS_VAV_POD_1 OA Rate [cfm] | VAV_POD_1 OA Rate [cfm] | 5823.4027 | 5613.1674 | [8 empty] | 2021-05-06
KY_PS_VAV_POD_2 OA Rate [cfm] | VAV_POD_2 OA Rate [cfm] | 5750.1742 | 5556.8476 | [8 empty] | 2021-05-06
KY_PS_VAV_POD_3 OA Rate [cfm] | VAV_POD_3 OA Rate [cfm] | 5322.118 | 5058.8048 | [8 empty] | 2021-05-06
KY_PS_VAV_OTHER OA Rate [cfm] | VAV_OTHER OA Rate [cfm] | 3736.1787 | 2988.8921 | [8 empty] | 2021-05-06
KY_PS_PSZ-AC_2:5 OA Rate [cfm] | PSZ-AC_2:5 OA Rate [cfm] | 1152.7343 | 1152.7343 | [8 empty] | 2021-05-06
KY_PS_PSZ-AC_1:6 OA Rate [cfm] | PSZ-AC_1:6 OA Rate [cfm] | 539.9118 | 539.9118 | [8 empty] | 2021-05-06
KY_PS_PSZ-AC_2:7 OA Rate [cfm] | PSZ-AC_2:7 OA Rate [cfm] | 3153.0841 | 3153.0841 | [8 empty] | 2021-05-06
KY_PS_VAV_POD_1 OA Damper [gravity, motorized] | VAV_POD_1 OA Damper [gravity, motorized] | motorized | motorized | [8 empty] | 2021-05-06
KY_PS_VAV_POD_2 OA Damper [gravity, motorized] | VAV_POD_2 OA Damper [gravity, motorized] | motorized | motorized | [8 empty] | 2021-05-06
KY_PS_VAV_POD_3 OA Damper [gravity, motorized] | VAV_POD_3 OA Damper [gravity, motorized] | motorized | motorized | [8 empty] | 2021-05-06
KY_PS_VAV_OTHER OA Damper [gravity, motorized] | VAV_OTHER OA Damper [gravity, motorized] | motorized | motorized | [8 empty] | 2021-05-06
KY_PS_PSZ-AC_2:5 OA Damper [gravity, motorized] | PSZ-AC_2:5 OA Damper [gravity, motorized] | motorized | motorized | [8 empty] | 2021-05-06
KY_PS_PSZ-AC_1:6 OA Damper [gravity, motorized] | PSZ-AC_1:6 OA Damper [gravity, motorized] | motorized | motorized | [8 empty] | 2021-05-06
KY_PS_PSZ-AC_2:7 OA Damper [gravity, motorized] | PSZ-AC_2:7 OA Damper [gravity, motorized] | motorized | motorized | [8 empty] | 2021-05-06
KY_PS_VAV_POD_1 (economizer) | VAV_POD_1 (economizer) | DifferentialEnthalpy | DifferentialEnthalpy | [8 empty] | 2021-05-06
KY_PS_VAV_POD_2 (economizer) | VAV_POD_2 (economizer) | DifferentialEnthalpy | DifferentialEnthalpy | [8 empty] | 2021-05-06
KY_PS_VAV_POD_3 (economizer) | VAV_POD_3 (economizer) | DifferentialEnthalpy | DifferentialEnthalpy | [8 empty] | 2021-05-06
KY_PS_VAV_OTHER (economizer) | VAV_OTHER (economizer) | DifferentialEnthalpy | DifferentialEnthalpy | [8 empty] | 2021-05-06
KY_PS_PSZ-AC_2:5 (economizer) | PSZ-AC_2:5 (economizer) | DifferentialEnthalpy | DifferentialEnthalpy | [8 empty] | 2021-05-06
KY_PS_PSZ-AC_1:6 (economizer) | PSZ-AC_1:6 (economizer) | DifferentialEnthalpy | DifferentialEnthalpy | [8 empty] | 2021-05-06
KY_PS_PSZ-AC_2:7 (economizer) | PSZ-AC_2:7 (economizer) | DifferentialEnthalpy | DifferentialEnthalpy | [8 empty] | 2021-05-06
KY_PS_VAV_Pod_1_ERV Flag | VAV_Pod_1_ERV Flag | Yes | Yes | [8 empty] | 2021-05-06
KY_PS_VAV_Pod_2_ERV Flag | VAV_Pod_2_ERV Flag | Yes | Yes | [8 empty] | 2021-05-06
KY_PS_VAV_Pod_3_ERV Flag | VAV_Pod_3_ERV Flag | Yes | Yes | [8 empty] | 2021-05-06
KY_PS_VAV_OTHER_ERV Flag | VAV_OTHER_ERV Flag | Yes | Yes | [8 empty] | 2021-05-06
KY_PS_PSZ_AC_2_5_ERV Flag | PSZ_AC_2_5_ERV Flag | No | No | [8 empty] | 2021-05-06
KY_PS_PSZ_AC_2_7_ERV Flag | PSZ_AC_2_7_ERV Flag | Yes | Yes | [8 empty] | 2021-05-06
KY_PS_HEATSYS1 Capacity [MMBTU/h] | HEATSYS1 Capacity [MMBTU/h] | 1.071 | 1.0241 | [8 empty] | 2021-05-06
KY_PS_HEATSYS1 Flow Rate [gal/min] | HEATSYS1 Flow Rate [gal/min] | 109.9193 | 105.1029 | [8 empty] | 2021-05-06
KY_PS_VAV_POD_1 Fan Power [hp] | VAV_POD_1 Fan Power [hp] | 8.5913 | 8.2811 | [8 empty] | 2021-05-06
KY_PS_VAV_POD_2 Fan Power [hp] | VAV_POD_2 Fan Power [hp] | 8.4852 | 8.198 | [8 empty] | 2021-05-06
KY_PS_VAV_POD_3 Fan Power [hp] | VAV_POD_3 Fan Power [hp] | 7.853 | 7.4632 | [8 empty] | 2021-05-06
KY_PS_VAV_OTHER Fan Power [hp] | VAV_OTHER Fan Power [hp] | 12.0496 | 11.3395 | [8 empty] | 2021-05-06
KY_PS_HEATSYS1 Pump Power [hp] | HEATSYS1 Pump Power [hp] | 2.376 | 2.2494 | [8 empty] | 2021-05-06
KY_PS_PSZ-AC_1:6 Heating Capacity [kBtu/hr] | PSZ-AC_1:6 Heating Capacity [kBtu/hr] | 212.0893 | 203.5429 | [8 empty] | 2021-05-06
KY_PS_PSZ-AC_2:5 Heating Capacity [kBtu/hr] | PSZ-AC_2:5 Heating Capacity [kBtu/hr] | 137.2716 | 137.0661 | [8 empty] | 2021-05-06
KY_PS_PSZ-AC_2:7 Heating Capacity [kBtu/hr] | PSZ-AC_2:7 Heating Capacity [kBtu/hr] | 322.7826 | 322.7826 | [8 empty] | 2021-05-06
KY_PS_ZN_VAV_BOXes_Max_Reheat_Water_Flow_GPM | ZN_VAV_BOXes_Max_Reheat_Water_Flow_GPM | 70.3189 | 67.3212 | [8 empty] | 2021-05-06
id | item | Zone4A(KY-Lexington-KY) ASHRAE901-state_STD2016 | Zone4A(KY-Lexington-KY) ASHRAE901-state_STD2019 | [8 empty] | 2021-05-06
KY_SH_SAC_FRONTOFFICE Cooling Capacity [ton] | SAC_FRONTOFFICE Cooling Capacity [ton] | 2.3135 | 2.1958 | [8 empty] | 2021-05-06
KY_SH_SAC_FRONTLOUNGE Cooling Capacity [ton] | SAC_FRONTLOUNGE Cooling Capacity [ton] | 6.2248 | 5.9068 | [8 empty] | 2021-05-06
KY_SH_SAC_MEETINGROOM Cooling Capacity [ton] | SAC_MEETINGROOM Cooling Capacity [ton] | 2.9558 | 2.8675 | [8 empty] | 2021-05-06
KY_SH_SAC_EXC_EMPLGE_RESTRM Cooling Capacity [ton] | SAC_EXC_EMPLGE_RESTRM Cooling Capacity [ton] | 5.9858 | 5.9447 | [8 empty] | 2021-05-06
KY_SH_SAC_FO_ADDAQ SUPPLY FAN Supply Flow Rate [cfm] | SAC_FO_ADDAQ SUPPLY FAN Supply Flow Rate [cfm] | 783.9856 | 741.608 | [8 empty] | 2021-05-06
KY_SH_SAC_FL_ADDAQ SUPPLY FAN Supply Flow Rate [cfm] | SAC_FL_ADDAQ SUPPLY FAN Supply Flow Rate [cfm] | 1864.6144 | 1779.8592 | [8 empty] | 2021-05-06
KY_SH_SAC_MR_ADDAQ SUPPLY FAN Supply Flow Rate [cfm] | SAC_MR_ADDAQ SUPPLY FAN Supply Flow Rate [cfm] | 889.9296 | 868.7408 | [8 empty] | 2021-05-06
KY_SH_SAC_EXC_ADDAQ SUPPLY FAN Supply Flow Rate [cfm] | SAC_EXC_ADDAQ SUPPLY FAN Supply Flow Rate [cfm] | 2246.0128 | 2224.824 | [8 empty] | 2021-05-06
KY_SH_SAC_Exc_EmpLge_RestRm OA Rate [cfm] | SAC_Exc_EmpLge_RestRm OA Rate [cfm] | 199.9928 | 199.9928 | [8 empty] | 2021-05-06
KY_SH_SAC_FrontLounge OA Rate [cfm] | SAC_FrontLounge OA Rate [cfm] | 500.0133 | 500.0133 | [8 empty] | 2021-05-06
KY_SH_SAC_FrontOffice OA Rate [cfm] | SAC_FrontOffice OA Rate [cfm] | 119.2938 | 119.2938 | [8 empty] | 2021-05-06
KY_SH_SAC_MeetingRoom OA Rate [cfm] | SAC_MeetingRoom OA Rate [cfm] | 267.7629 | 267.7629 | [8 empty] | 2021-05-06
KY_SH_SAC_FrontLounge OA Damper [gravity, motorized] | SAC_FrontLounge OA Damper [gravity, motorized] | motorized | motorized | [8 empty] | 2021-05-06
KY_SH_SAC_FrontOffice (economizer) | SAC_FrontOffice (economizer) | No | No | [8 empty] | 2021-05-06
KY_SH_SAC_FrontLounge (economizer) | SAC_FrontLounge (economizer) | DifferentialEnthalpy | DifferentialEnthalpy | [8 empty] | 2021-05-06
KY_SH_SAC_MeetingRoom (economizer) | SAC_MeetingRoom (economizer) | No | No | [8 empty] | 2021-05-06
KY_SH_SAC_Exc_EmpLge_RestRm (economizer) | SAC_Exc_EmpLge_RestRm (economizer) | DifferentialEnthalpy | DifferentialEnthalpy | [8 empty] | 2021-05-06
KY_SH_SAC_FRONTOFFICE Heating Capacity [kBtu/hr] | SAC_FRONTOFFICE Heating Capacity [kBtu/hr] | 35.9431 | 34.1654 | [8 empty] | 2021-05-06
KY_SH_SAC_FRONTLOUNGE Heating Capacity [kBtu/hr] | SAC_FRONTLOUNGE Heating Capacity [kBtu/hr] | 99.811 | 96.4187 | [8 empty] | 2021-05-06
KY_SH_SAC_MEETINGROOM Heating Capacity [kBtu/hr] | SAC_MEETINGROOM Heating Capacity [kBtu/hr] | 49.4213 | 48.4792 | [8 empty] | 2021-05-06
KY_SH_SAC_EXC_EMPLGE_RESTRM Heating Capacity [kBtu/hr] | SAC_EXC_EMPLGE_RESTRM Heating Capacity [kBtu/hr] | 93.3102 | 92.6512 | [8 empty] | 2021-05-06
id | item | Zone4A(KY-Lexington-KY) ASHRAE901-state_STD2016 | Zone4A(KY-Lexington-KY) ASHRAE901-state_STD2019 | [8 empty] | 2021-05-06
KY_MA_SPLIT GSW COOLING COIL Cooling Capacity [ton] | SPLIT GSW COOLING COIL Cooling Capacity [ton] | 0.86339 | 0.84956 | [8 empty] | 2021-05-06
KY_MA_SPLIT GNW COOLING COIL Cooling Capacity [ton] | SPLIT GNW COOLING COIL Cooling Capacity [ton] | 0.82736 | 0.81383 | [8 empty] | 2021-05-06
KY_MA_SPLIT OFFICE COOLING COIL Cooling Capacity [ton] | SPLIT OFFICE COOLING COIL Cooling Capacity [ton] | 1.7486 | 1.5354 | [8 empty] | 2021-05-06
KY_MA_SPLIT GNE COOLING COIL Cooling Capacity [ton] | SPLIT GNE COOLING COIL Cooling Capacity [ton] | 0.72581 | 0.7136 | [8 empty] | 2021-05-06
KY_MA_SPLIT GN1 COOLING COIL Cooling Capacity [ton] | SPLIT GN1 COOLING COIL Cooling Capacity [ton] | 0.61272 | 0.60304 | [8 empty] | 2021-05-06
KY_MA_SPLIT GN2 COOLING COIL Cooling Capacity [ton] | SPLIT GN2 COOLING COIL Cooling Capacity [ton] | 0.61061 | 0.60097 | [8 empty] | 2021-05-06
KY_MA_SPLIT GS1 COOLING COIL Cooling Capacity [ton] | SPLIT GS1 COOLING COIL Cooling Capacity [ton] | 0.65417 | 0.64384 | [8 empty] | 2021-05-06
KY_MA_SPLIT GS2 COOLING COIL Cooling Capacity [ton] | SPLIT GS2 COOLING COIL Cooling Capacity [ton] | 0.68551 | 0.66897 | [8 empty] | 2021-05-06
KY_MA_SPLIT MSW COOLING COIL Cooling Capacity [ton] | SPLIT MSW COOLING COIL Cooling Capacity [ton] | 2.0384 | 2.0072 | [8 empty] | 2021-05-06
KY_MA_SPLIT MNW COOLING COIL Cooling Capacity [ton] | SPLIT MNW COOLING COIL Cooling Capacity [ton] | 1.9793 | 1.9489 | [8 empty] | 2021-05-06
KY_MA_SPLIT MSE COOLING COIL Cooling Capacity [ton] | SPLIT MSE COOLING COIL Cooling Capacity [ton] | 1.7014 | 1.6773 | [8 empty] | 2021-05-06
KY_MA_SPLIT MNE COOLING COIL Cooling Capacity [ton] | SPLIT MNE COOLING COIL Cooling Capacity [ton] | 1.6343 | 1.6043 | [8 empty] | 2021-05-06
KY_MA_SPLIT MN1 COOLING COIL Cooling Capacity [ton] | SPLIT MN1 COOLING COIL Cooling Capacity [ton] | 1.3419 | 1.3233 | [8 empty] | 2021-05-06
KY_MA_SPLIT MN2 COOLING COIL Cooling Capacity [ton] | SPLIT MN2 COOLING COIL Cooling Capacity [ton] | 1.3362 | 1.3177 | [8 empty] | 2021-05-06
KY_MA_SPLIT MS1 COOLING COIL Cooling Capacity [ton] | SPLIT MS1 COOLING COIL Cooling Capacity [ton] | 1.4197 | 1.4002 | [8 empty] | 2021-05-06
KY_MA_SPLIT MS2 COOLING COIL Cooling Capacity [ton] | SPLIT MS2 COOLING COIL Cooling Capacity [ton] | 1.415 | 1.3956 | [8 empty] | 2021-05-06
KY_MA_SPLIT TSW COOLING COIL Cooling Capacity [ton] | SPLIT TSW COOLING COIL Cooling Capacity [ton] | 1.271 | 1.2542 | [8 empty] | 2021-05-06
KY_MA_SPLIT TNW COOLING COIL Cooling Capacity [ton] | SPLIT TNW COOLING COIL Cooling Capacity [ton] | 1.2356 | 1.2191 | [8 empty] | 2021-05-06
KY_MA_SPLIT TSE COOLING COIL Cooling Capacity [ton] | SPLIT TSE COOLING COIL Cooling Capacity [ton] | 1.1301 | 1.1165 | [8 empty] | 2021-05-06
KY_MA_SPLIT TNE COOLING COIL Cooling Capacity [ton] | SPLIT TNE COOLING COIL Cooling Capacity [ton] | 1.0684 | 1.0556 | [8 empty] | 2021-05-06
KY_MA_SPLIT TN1 COOLING COIL Cooling Capacity [ton] | SPLIT TN1 COOLING COIL Cooling Capacity [ton] | 0.86949 | 0.85978 | [8 empty] | 2021-05-06
KY_MA_SPLIT TN2 COOLING COIL Cooling Capacity [ton] | SPLIT TN2 COOLING COIL Cooling Capacity [ton] | 0.86365 | 0.85408 | [8 empty] | 2021-05-06
KY_MA_SPLIT TS1 COOLING COIL Cooling Capacity [ton] | SPLIT TS1 COOLING COIL Cooling Capacity [ton] | 0.93787 | 0.92711 | [8 empty] | 2021-05-06
KY_MA_SPLIT TS2 COOLING COIL Cooling Capacity [ton] | SPLIT TS2 COOLING COIL Cooling Capacity [ton] | 0.93844 | 0.92771 | [8 empty] | 2021-05-06
KY_MA_Split GN1 Furnace with DX Cooling OA Rate [cfm] | Split GN1 Furnace with DX Cooling OA Rate [cfm] | 54.9913 | 54.9913 | [8 empty] | 2021-05-06
KY_MA_Split GN2 Furnace with DX Cooling OA Rate [cfm] | Split GN2 Furnace with DX Cooling OA Rate [cfm] | 54.9913 | 54.9913 | [8 empty] | 2021-05-06
KY_MA_Split GNE Furnace with DX Cooling OA Rate [cfm] | Split GNE Furnace with DX Cooling OA Rate [cfm] | 54.9913 | 54.9913 | [8 empty] | 2021-05-06
KY_MA_Split GNW Furnace with DX Cooling OA Rate [cfm] | Split GNW Furnace with DX Cooling OA Rate [cfm] | 54.9913 | 54.9913 | [8 empty] | 2021-05-06
KY_MA_Split GS1 Furnace with DX Cooling OA Rate [cfm] | Split GS1 Furnace with DX Cooling OA Rate [cfm] | 54.9913 | 54.9913 | [8 empty] | 2021-05-06
KY_MA_Split GS2 Furnace with DX Cooling OA Rate [cfm] | Split GS2 Furnace with DX Cooling OA Rate [cfm] | 54.9913 | 54.9913 | [8 empty] | 2021-05-06
KY_MA_Split GSW Furnace with DX Cooling OA Rate [cfm] | Split GSW Furnace with DX Cooling OA Rate [cfm] | 56.9945 | 56.9945 | [8 empty] | 2021-05-06
KY_MA_Split MN1 Furnace with DX Cooling OA Rate [cfm] | Split MN1 Furnace with DX Cooling OA Rate [cfm] | 109.9824 | 109.9824 | [8 empty] | 2021-05-06
KY_MA_Split MN2 Furnace with DX Cooling OA Rate [cfm] | Split MN2 Furnace with DX Cooling OA Rate [cfm] | 109.9824 | 109.9824 | [8 empty] | 2021-05-06
KY_MA_Split MNE Furnace with DX Cooling OA Rate [cfm] | Split MNE Furnace with DX Cooling OA Rate [cfm] | 109.9824 | 109.9824 | [8 empty] | 2021-05-06
KY_MA_Split MNW Furnace with DX Cooling OA Rate [cfm] | Split MNW Furnace with DX Cooling OA Rate [cfm] | 109.9824 | 109.9824 | [8 empty] | 2021-05-06
KY_MA_Split MS1 Furnace with DX Cooling OA Rate [cfm] | Split MS1 Furnace with DX Cooling OA Rate [cfm] | 109.9824 | 109.9824 | [8 empty] | 2021-05-06
KY_MA_Split MS2 Furnace with DX Cooling OA Rate [cfm] | Split MS2 Furnace with DX Cooling OA Rate [cfm] | 109.9824 | 109.9824 | [8 empty] | 2021-05-06
KY_MA_Split MSE Furnace with DX Cooling OA Rate [cfm] | Split MSE Furnace with DX Cooling OA Rate [cfm] | 109.9824 | 109.9824 | [8 empty] | 2021-05-06
KY_MA_Split MSW Furnace with DX Cooling OA Rate [cfm] | Split MSW Furnace with DX Cooling OA Rate [cfm] | 109.9824 | 109.9824 | [8 empty] | 2021-05-06
KY_MA_Split Office Furnace with DX Cooling OA Rate [cfm] | Split Office Furnace with DX Cooling OA Rate [cfm] | 80.7372 | 80.7372 | [8 empty] | 2021-05-06
KY_MA_Split TN1 Furnace with DX Cooling OA Rate [cfm] | Split TN1 Furnace with DX Cooling OA Rate [cfm] | 54.9913 | 54.9913 | [8 empty] | 2021-05-06
KY_MA_Split TN2 Furnace with DX Cooling OA Rate [cfm] | Split TN2 Furnace with DX Cooling OA Rate [cfm] | 54.9913 | 54.9913 | [8 empty] | 2021-05-06
KY_MA_Split TNE Furnace with DX Cooling OA Rate [cfm] | Split TNE Furnace with DX Cooling OA Rate [cfm] | 54.9913 | 54.9913 | [8 empty] | 2021-05-06
KY_MA_Split TNW Furnace with DX Cooling OA Rate [cfm] | Split TNW Furnace with DX Cooling OA Rate [cfm] | 54.9913 | 54.9913 | [8 empty] | 2021-05-06
KY_MA_Split TS1 Furnace with DX Cooling OA Rate [cfm] | Split TS1 Furnace with DX Cooling OA Rate [cfm] | 54.9913 | 54.9913 | [8 empty] | 2021-05-06
KY_MA_Split TS2 Furnace with DX Cooling OA Rate [cfm] | Split TS2 Furnace with DX Cooling OA Rate [cfm] | 54.9913 | 54.9913 | [8 empty] | 2021-05-06
KY_MA_Split TSE Furnace with DX Cooling OA Rate [cfm] | Split TSE Furnace with DX Cooling OA Rate [cfm] | 54.9913 | 54.9913 | [8 empty] | 2021-05-06
KY_MA_Split TSW Furnace with DX Cooling OA Rate [cfm] | Split TSW Furnace with DX Cooling OA Rate [cfm] | 54.9913 | 54.9913 | [8 empty] | 2021-05-06
KY_MA_SPLIT GSW HEATING COIL Heating Capacity [kBtu/hr] | SPLIT GSW HEATING COIL Heating Capacity [kBtu/hr] | 9.3365 | 9.3953 | [8 empty] | 2021-05-06
KY_MA_SPLIT GNW HEATING COIL Heating Capacity [kBtu/hr] | SPLIT GNW HEATING COIL Heating Capacity [kBtu/hr] | 9.2671 | 9.3261 | [8 empty] | 2021-05-06
KY_MA_SPLIT OFFICE HEATING COIL Heating Capacity [kBtu/hr] | SPLIT OFFICE HEATING COIL Heating Capacity [kBtu/hr] | 22.0083 | 22.0954 | [8 empty] | 2021-05-06
KY_MA_SPLIT GNE HEATING COIL Heating Capacity [kBtu/hr] | SPLIT GNE HEATING COIL Heating Capacity [kBtu/hr] | 9.2467 | 9.3056 | [8 empty] | 2021-05-06
KY_MA_SPLIT GN1 HEATING COIL Heating Capacity [kBtu/hr] | SPLIT GN1 HEATING COIL Heating Capacity [kBtu/hr] | 6.7974 | 6.8564 | [8 empty] | 2021-05-06
KY_MA_SPLIT GN2 HEATING COIL Heating Capacity [kBtu/hr] | SPLIT GN2 HEATING COIL Heating Capacity [kBtu/hr] | 6.7967 | 6.8557 | [8 empty] | 2021-05-06
KY_MA_SPLIT GS1 HEATING COIL Heating Capacity [kBtu/hr] | SPLIT GS1 HEATING COIL Heating Capacity [kBtu/hr] | 6.7487 | 6.8075 | [8 empty] | 2021-05-06
KY_MA_SPLIT GS2 HEATING COIL Heating Capacity [kBtu/hr] | SPLIT GS2 HEATING COIL Heating Capacity [kBtu/hr] | 7.2483 | 7.3084 | [8 empty] | 2021-05-06
KY_MA_SPLIT MSW HEATING COIL Heating Capacity [kBtu/hr] | SPLIT MSW HEATING COIL Heating Capacity [kBtu/hr] | 16.6283 | 16.7566 | [8 empty] | 2021-05-06
KY_MA_SPLIT MNW HEATING COIL Heating Capacity [kBtu/hr] | SPLIT MNW HEATING COIL Heating Capacity [kBtu/hr] | 16.7123 | 16.8407 | [8 empty] | 2021-05-06
KY_MA_SPLIT MSE HEATING COIL Heating Capacity [kBtu/hr] | SPLIT MSE HEATING COIL Heating Capacity [kBtu/hr] | 16.5797 | 16.708 | [8 empty] | 2021-05-06
KY_MA_SPLIT MNE HEATING COIL Heating Capacity [kBtu/hr] | SPLIT MNE HEATING COIL Heating Capacity [kBtu/hr] | 16.6636 | 16.7921 | [8 empty] | 2021-05-06
KY_MA_SPLIT MN1 HEATING COIL Heating Capacity [kBtu/hr] | SPLIT MN1 HEATING COIL Heating Capacity [kBtu/hr] | 11.5312 | 11.6569 | [8 empty] | 2021-05-06
KY_MA_SPLIT MN2 HEATING COIL Heating Capacity [kBtu/hr] | SPLIT MN2 HEATING COIL Heating Capacity [kBtu/hr] | 11.5299 | 11.6556 | [8 empty] | 2021-05-06
KY_MA_SPLIT MS1 HEATING COIL Heating Capacity [kBtu/hr] | SPLIT MS1 HEATING COIL Heating Capacity [kBtu/hr] | 11.4556 | 11.5813 | [8 empty] | 2021-05-06
KY_MA_SPLIT MS2 HEATING COIL Heating Capacity [kBtu/hr] | SPLIT MS2 HEATING COIL Heating Capacity [kBtu/hr] | 11.4543 | 11.58 | [8 empty] | 2021-05-06
KY_MA_SPLIT TSW HEATING COIL Heating Capacity [kBtu/hr] | SPLIT TSW HEATING COIL Heating Capacity [kBtu/hr] | 11.7302 | 11.7919 | [8 empty] | 2021-05-06
KY_MA_SPLIT TNW HEATING COIL Heating Capacity [kBtu/hr] | SPLIT TNW HEATING COIL Heating Capacity [kBtu/hr] | 11.7806 | 11.8424 | [8 empty] | 2021-05-06
KY_MA_SPLIT TSE HEATING COIL Heating Capacity [kBtu/hr] | SPLIT TSE HEATING COIL Heating Capacity [kBtu/hr] | 11.7045 | 11.7662 | [8 empty] | 2021-05-06
KY_MA_SPLIT TNE HEATING COIL Heating Capacity [kBtu/hr] | SPLIT TNE HEATING COIL Heating Capacity [kBtu/hr] | 11.7549 | 11.8167 | [8 empty] | 2021-05-06
KY_MA_SPLIT TN1 HEATING COIL Heating Capacity [kBtu/hr] | SPLIT TN1 HEATING COIL Heating Capacity [kBtu/hr] | 9.0162 | 9.0779 | [8 empty] | 2021-05-06
KY_MA_SPLIT TN2 HEATING COIL Heating Capacity [kBtu/hr] | SPLIT TN2 HEATING COIL Heating Capacity [kBtu/hr] | 9.0155 | 9.0771 | [8 empty] | 2021-05-06
KY_MA_SPLIT TS1 HEATING COIL Heating Capacity [kBtu/hr] | SPLIT TS1 HEATING COIL Heating Capacity [kBtu/hr] | 8.9588 | 9.0204 | [8 empty] | 2021-05-06
KY_MA_SPLIT TS2 HEATING COIL Heating Capacity [kBtu/hr] | SPLIT TS2 HEATING COIL Heating Capacity [kBtu/hr] | 8.958 | 9.0196 | [8 empty] | 2021-05-06
KY_MA_Split_GSW ERV Flag | Split_GSW ERV Flag | Yes | Yes | [8 empty] | 2021-05-06
KY_MA_Split_GNW ERV Flag | Split_GNW ERV Flag | Yes | Yes | [8 empty] | 2021-05-06
KY_MA_Split_GNE ERV Flag | Split_GNE ERV Flag | Yes | Yes | [8 empty] | 2021-05-06
KY_MA_Split_GN1 ERV Flag | Split_GN1 ERV Flag | Yes | Yes | [8 empty] | 2021-05-06
KY_MA_Split_GN2 ERV Flag | Split_GN2 ERV Flag | Yes | Yes | [8 empty] | 2021-05-06
KY_MA_Split_GS1 ERV Flag | Split_GS1 ERV Flag | Yes | Yes | [8 empty] | 2021-05-06
KY_MA_Split_GS2 ERV Flag | Split_GS2 ERV Flag | Yes | Yes | [8 empty] | 2021-05-06
KY_MA_Split_MSW ERV Flag | Split_MSW ERV Flag | Yes | Yes | [8 empty] | 2021-05-06
KY_MA_Split_MNW ERV Flag | Split_MNW ERV Flag | Yes | Yes | [8 empty] | 2021-05-06
KY_MA_Split_MSE ERV Flag | Split_MSE ERV Flag | Yes | Yes | [8 empty] | 2021-05-06
KY_MA_Split_MNE ERV Flag | Split_MNE ERV Flag | Yes | Yes | [8 empty] | 2021-05-06
KY_MA_Split_MN1 ERV Flag | Split_MN1 ERV Flag | Yes | Yes | [8 empty] | 2021-05-06
KY_MA_Split_MN2 ERV Flag | Split_MN2 ERV Flag | Yes | Yes | [8 empty] | 2021-05-06
KY_MA_Split_MS1 ERV Flag | Split_MS1 ERV Flag | Yes | Yes | [8 empty] | 2021-05-06
KY_MA_Split_MS2 ERV Flag | Split_MS2 ERV Flag | Yes | Yes | [8 empty] | 2021-05-06
KY_MA_Split_TSW ERV Flag | Split_TSW ERV Flag | Yes | Yes | [8 empty] | 2021-05-06
KY_MA_Split_TNW ERV Flag | Split_TNW ERV Flag | Yes | Yes | [8 empty] | 2021-05-06
KY_MA_Split_TSE ERV Flag | Split_TSE ERV Flag | Yes | Yes | [8 empty] | 2021-05-06
KY_MA_Split_TNE ERV Flag | Split_TNE ERV Flag | Yes | Yes | [8 empty] | 2021-05-06
KY_MA_Split_TN1 ERV Flag | Split_TN1 ERV Flag | Yes | Yes | [8 empty] | 2021-05-06
KY_MA_Split_TN2 ERV Flag | Split_TN2 ERV Flag | Yes | Yes | [8 empty] | 2021-05-06
KY_MA_Split_TS1 ERV Flag | Split_TS1 ERV Flag | Yes | Yes | [8 empty] | 2021-05-06
KY_MA_Split_TS2 ERV Flag | Split_TS2 ERV Flag | Yes | Yes | [8 empty] | 2021-05-06
id | item | Zone2A(LA-BatonRouge-LA) ASHRAE901-state_STD2016 | Zone2A(LA-BatonRouge-LA) ASHRAE901-state_STD2019 | Zone3A(LA-Shreveport-LA) ASHRAE901-state_STD2016 | Zone3A(LA-Shreveport-LA) ASHRAE901-state_STD2019 | [6 empty] | 2021-05-06
LA_SO_PSZ-AC:1 Cooling Capacity [ton] | PSZ-AC:1 Cooling Capacity [ton] | 2.0712 | 1.973 | 2.0686 | 1.9699 | [6 empty] | 2021-05-06
LA_SO_PSZ-AC:2 Cooling Capacity [ton] | PSZ-AC:2 Cooling Capacity [ton] | 1.8505 | 1.7567 | 1.8709 | 1.782 | [6 empty] | 2021-05-06
LA_SO_PSZ-AC:3 Cooling Capacity [ton] | PSZ-AC:3 Cooling Capacity [ton] | 1.221 | 1.1747 | 1.2331 | 1.1919 | [6 empty] | 2021-05-06
LA_SO_PSZ-AC:4 Cooling Capacity [ton] | PSZ-AC:4 Cooling Capacity [ton] | 1.836 | 1.7487 | 1.872 | 1.7813 | [6 empty] | 2021-05-06
LA_SO_PSZ-AC:5 Cooling Capacity [ton] | PSZ-AC:5 Cooling Capacity [ton] | 1.4263 | 1.3747 | 1.4553 | 1.4107 | [6 empty] | 2021-05-06
LA_SO_PSZ-AC:1 Supply Flow Rate [cfm] | PSZ-AC:1 Supply Flow Rate [cfm] | 678.0416 | 635.664 | 678.0416 | 635.664 | [6 empty] | 2021-05-06
LA_SO_PSZ-AC:2 Supply Flow Rate [cfm] | PSZ-AC:2 Supply Flow Rate [cfm] | 635.664 | 593.2864 | 656.8528 | 614.4752 | [6 empty] | 2021-05-06
LA_SO_PSZ-AC:3 Supply Flow Rate [cfm] | PSZ-AC:3 Supply Flow Rate [cfm] | 466.1536 | 444.9648 | 466.1536 | 466.1536 | [6 empty] | 2021-05-06
LA_SO_PSZ-AC:4 Supply Flow Rate [cfm] | PSZ-AC:4 Supply Flow Rate [cfm] | 635.664 | 593.2864 | 656.8528 | 614.4752 | [6 empty] | 2021-05-06
LA_SO_PSZ-AC:5 Supply Flow Rate [cfm] | PSZ-AC:5 Supply Flow Rate [cfm] | 550.9088 | 508.5312 | 572.0976 | 550.9088 | [6 empty] | 2021-05-06
LA_SO_PSZ-AC:1 OA Rate [cfm] | PSZ-AC:1 OA Rate [cfm] | 136.9178 | 136.9178 | 136.9178 | 136.9178 | [6 empty] | 2021-05-06
LA_SO_PSZ-AC:2 OA Rate [cfm] | PSZ-AC:2 OA Rate [cfm] | 103.7925 | 103.7925 | 103.7925 | 103.7925 | [6 empty] | 2021-05-06
LA_SO_PSZ-AC:3 OA Rate [cfm] | PSZ-AC:3 OA Rate [cfm] | 61.5711 | 61.5711 | 61.5711 | 61.5711 | [6 empty] | 2021-05-06
LA_SO_PSZ-AC:4 OA Rate [cfm] | PSZ-AC:4 OA Rate [cfm] | 103.7925 | 103.7925 | 103.7925 | 103.7925 | [6 empty] | 2021-05-06
LA_SO_PSZ-AC:5 OA Rate [cfm] | PSZ-AC:5 OA Rate [cfm] | 61.5711 | 61.5711 | 61.5711 | 61.5711 | [6 empty] | 2021-05-06
LA_SO_PSZ-AC:1 heating Capacity [kBtu/hr] | PSZ-AC:1 heating Capacity [kBtu/hr] | 11.3131 | 11.3131 | 11.7921 | 11.7921 | [6 empty] | 2021-05-06
LA_SO_PSZ-AC:2 heating Capacity [kBtu/hr] | PSZ-AC:2 heating Capacity [kBtu/hr] | 14.5393 | 14.0471 | 15.8211 | 15.6066 | [6 empty] | 2021-05-06
LA_SO_PSZ-AC:3 heating Capacity [kBtu/hr] | PSZ-AC:3 heating Capacity [kBtu/hr] | 8.8834 | 8.5995 | 9.7352 | 9.6112 | [6 empty] | 2021-05-06
LA_SO_PSZ-AC:4 heating Capacity [kBtu/hr] | PSZ-AC:4 heating Capacity [kBtu/hr] | 14.2896 | 13.8692 | 15.6538 | 15.4702 | [6 empty] | 2021-05-06
LA_SO_PSZ-AC:5 heating Capacity [kBtu/hr] | PSZ-AC:5 heating Capacity [kBtu/hr] | 8.8834 | 8.5995 | 9.7352 | 9.6112 | [6 empty] | 2021-05-06
id | item | Zone2A(LA-BatonRouge-LA) ASHRAE901-state_STD2016 | Zone2A(LA-BatonRouge-LA) ASHRAE901-state_STD2019 | Zone3A(LA-Shreveport-LA) ASHRAE901-state_STD2016 | Zone3A(LA-Shreveport-LA) ASHRAE901-state_STD2019 | [6 empty] | 2021-05-06
LA_LO_CAV_BAS Supply Flow Rate [cfm] | CAV_BAS Supply Flow Rate [cfm] | 11632.6512 | 10785.0992 | 11696.2176 | 10827.4768 | [6 empty] | 2021-05-06
LA_LO_VAV_BOT WITH REHEAT Supply Flow Rate [cfm] | VAV_BOT WITH REHEAT Supply Flow Rate [cfm] | 19154.6752 | 18222.368 | 19408.9408 | 18455.4448 | [6 empty] | 2021-05-06
LA_LO_VAV_MID WITH REHEAT Supply Flow Rate [cfm] | VAV_MID WITH REHEAT Supply Flow Rate [cfm] | 177774.0323 | 168832.3587 | 180549.7651 | 171459.7699 | [6 empty] | 2021-05-06
LA_LO_VAV_TOP WITH REHEAT Supply Flow Rate [cfm] | VAV_TOP WITH REHEAT Supply Flow Rate [cfm] | 18646.144 | 17777.4032 | 19006.3536 | 18201.1792 | [6 empty] | 2021-05-06
LA_LO_Supply Air Temp. Reset Flag | Supply Air Temp. Reset Flag | No | No | No | Yes | [6 empty] | 2021-05-06
LA_LO_CAV_BAS OA Rate [cfm] | CAV_BAS OA Rate [cfm] | 2542.8255 | 2542.8255 | 2542.8255 | 2542.8255 | [6 empty] | 2021-05-06
LA_LO_VAV_BOT WITH REHEAT OA Rate [cfm] | VAV_BOT WITH REHEAT OA Rate [cfm] | 5377.8022 | 4302.174 | 5377.8022 | 4302.174 | [6 empty] | 2021-05-06
LA_LO_VAV_MID WITH REHEAT OA Rate [cfm] | VAV_MID WITH REHEAT OA Rate [cfm] | 53777.9373 | 43021.7396 | 53777.9373 | 43021.7396 | [6 empty] | 2021-05-06
LA_LO_VAV_TOP WITH REHEAT OA Rate [cfm] | VAV_TOP WITH REHEAT OA Rate [cfm] | 5377.8022 | 4302.174 | 5377.8022 | 4302.174 | [6 empty] | 2021-05-06
LA_LO_AIRLOOP DATACENTER BASEMENT OA Rate [cfm] | AIRLOOP DATACENTER BASEMENT OA Rate [cfm] | 716.9654 | 716.9654 | 716.9654 | 716.9654 | [6 empty] | 2021-05-06
LA_LO_VAV_bot_WITH_REHEAT ERV Flag | VAV_bot_WITH_REHEAT ERV Flag | Yes | Yes | Yes | Yes | [6 empty] | 2021-05-06
LA_LO_VAV_mid_WITH_REHEAT ERV Flag | VAV_mid_WITH_REHEAT ERV Flag | Yes | Yes | Yes | Yes | [6 empty] | 2021-05-06
LA_LO_VAV_top_WITH_REHEAT ERV Flag | VAV_top_WITH_REHEAT ERV Flag | Yes | Yes | Yes | Yes | [6 empty] | 2021-05-06
LA_LO_COOLSYS1 CHILLER1 Capacity [ton] | COOLSYS1 CHILLER1 Capacity [ton] | 449.9161 | 403.1301 | 436.5944 | 391.7602 | [6 empty] | 2021-05-06
LA_LO_COOLSYS1 CHILLER2 Capacity [ton] | COOLSYS1 CHILLER2 Capacity [ton] | 449.9161 | 403.1301 | 436.5944 | 391.7602 | [6 empty] | 2021-05-06
LA_LO_TOWERWATERSYS COOLTOWER 1 Capacity [ton] | TOWERWATERSYS COOLTOWER 1 Capacity [ton] | 427.048 | 382.6393 | 414.4067 | 371.8489 | [6 empty] | 2021-05-06
LA_LO_TOWERWATERSYS COOLTOWER 2 Capacity [ton] | TOWERWATERSYS COOLTOWER 2 Capacity [ton] | 427.048 | 382.6393 | 414.4067 | 371.8489 | [6 empty] | 2021-05-06
LA_LO_HEATSYS1 BOILER Capacity [MMBTU/h] | HEATSYS1 BOILER Capacity [MMBTU/h] | 3432.376 | 3025.2733 | 3541.0944 | 3162.2258 | [6 empty] | 2021-05-06
LA_LO_COOLSYS1 PUMP Flow Rate [gal/min] | COOLSYS1 PUMP Flow Rate [gal/min] | 0 | 0 | 0 | 0 | [6 empty] | 2021-05-06
LA_LO_COOLSYS1 CHILLER1 PUMP Flow Rate [gal/min] | COOLSYS1 CHILLER1 PUMP Flow Rate [gal/min] | 706.4758 | 632.7243 | 688.1862 | 614.6502 | [6 empty] | 2021-05-06
LA_LO_COOLSYS1 CHILLER2 PUMP Flow Rate [gal/min] | COOLSYS1 CHILLER2 PUMP Flow Rate [gal/min] | 706.4758 | 632.7243 | 688.1862 | 614.6502 | [6 empty] | 2021-05-06
LA_LO_COOLSYS1 PUMP SECONDARY Flow Rate [gal/min] | COOLSYS1 PUMP SECONDARY Flow Rate [gal/min] | 1412.9517 | 1265.447 | 1376.3707 | 1229.3003 | [6 empty] | 2021-05-06
LA_LO_HEATSYS1 PUMP Flow Rate [gal/min] | HEATSYS1 PUMP Flow Rate [gal/min] | 704.5405 | 620.9776 | 726.8562 | 649.0882 | [6 empty] | 2021-05-06
LA_LO_TOWERWATERSYS PUMP Flow Rate [gal/min] | TOWERWATERSYS PUMP Flow Rate [gal/min] | 2482.1606 | 2224.1173 | 2408.7736 | 2161.3501 | [6 empty] | 2021-05-06
LA_LO_PLANT CIRC PUMP Flow Rate [gal/min] | PLANT CIRC PUMP Flow Rate [gal/min] | 208.4634 | 207.579 | 208.3192 | 207.4221 | [6 empty] | 2021-05-06
LA_LO_COOLSYS1 PUMP SECONDARY Pressure setpoint reset [yes,no] | COOLSYS1 PUMP SECONDARY Pressure setpoint reset [yes,no] | pump_ride_on_curve | pump_ride_on_curve | pump_ride_on_curve | pump_ride_on_curve | [6 empty] | 2021-05-06
LA_LO_COOLSYS1 CHILLER1 PUMP Pump Power [hp] | COOLSYS1 CHILLER1 PUMP Pump Power [hp] | 3.8112 | 3.3795 | 3.7125 | 3.283 | [6 empty] | 2021-05-06
LA_LO_COOLSYS1 CHILLER2 PUMP Pump Power [hp] | COOLSYS1 CHILLER2 PUMP Pump Power [hp] | 3.8112 | 3.3795 | 3.7125 | 3.283 | [6 empty] | 2021-05-06
LA_LO_COOLSYS1 PUMP SECONDARY Pump Power [hp] | COOLSYS1 PUMP SECONDARY Pump Power [hp] | 22.8671 | 20.2772 | 22.2751 | 19.6979 | [6 empty] | 2021-05-06
LA_LO_HEATSYS1 PUMP Pump Power [hp] | HEATSYS1 PUMP Pump Power [hp] | 15.229 | 13.2899 | 15.7114 | 13.8915 | [6 empty] | 2021-05-06
LA_LO_TOWERWATERSYS PUMP Pump Power [hp] | TOWERWATERSYS PUMP Pump Power [hp] | 44.4418 | 39.4261 | 43.1259 | 38.3141 | [6 empty] | 2021-05-06
LA_LO_PLANT CIRC PUMP Pump Power [hp] | PLANT CIRC PUMP Pump Power [hp] | 4.4983 | 4.4349 | 4.4952 | 4.4316 | [6 empty] | 2021-05-06
LA_LO_Datacenter PLANT CIRC PUMP Pump Power [hp] | Datacenter PLANT CIRC PUMP Pump Power [hp] | 4.4983 | 4.4349 | 4.4952 | 4.4316 | [6 empty] | 2021-05-06
LA_LO_ZN_VAV_BOXes_Max_Reheat_Water_Flow_GPM | ZN_VAV_BOXes_Max_Reheat_Water_Flow_GPM | 414.7809 | 386.1338 | 410.0169 | 394.0411 | [6 empty] | 2021-05-06
LA_LO_COOLSYS1 PUMP SECONDARY VSD | COOLSYS1 PUMP SECONDARY VSD | No | No | No | No | [6 empty] | 2021-05-06
LA_LO_HEATSYS1 PUMP VSD | HEATSYS1 PUMP VSD | No | No | No | No | [6 empty] | 2021-05-06
LA_LO_DATACENTER BASEMENT Cooling Capacity [ton] | DATACENTER BASEMENT Cooling Capacity [ton] | 122.2841 | 121.928 | 122.268 | 121.9106 | [6 empty] | 2021-05-06
LA_LO_DATACENTER BOT Cooling Capacity [ton] | DATACENTER BOT Cooling Capacity [ton] | 2.6498 | 2.6233 | 2.6406 | 2.6132 | [6 empty] | 2021-05-06
LA_LO_DATACENTER MID Cooling Capacity [ton] | DATACENTER MID Cooling Capacity [ton] | 25.223 | 24.9792 | 25.1357 | 24.8835 | [6 empty] | 2021-05-06
LA_LO_DATACENTER TOP Cooling Capacity [ton] | DATACENTER TOP Cooling Capacity [ton] | 2.5467 | 2.5259 | 2.5538 | 2.5339 | [6 empty] | 2021-05-06
id | item | Zone2A(LA-BatonRouge-LA) ASHRAE901-state_STD2016 | Zone2A(LA-BatonRouge-LA) ASHRAE901-state_STD2019 | Zone3A(LA-Shreveport-LA) ASHRAE901-state_STD2016 | Zone3A(LA-Shreveport-LA) ASHRAE901-state_STD2019 | [6 empty] | 2021-05-06
LA_RS_PSZ-AC:1 Cooling Capacity [ton] | PSZ-AC:1 Cooling Capacity [ton] | 11.2662 | 10.9118 | 11.1325 | 10.7472 | [6 empty] | 2021-05-06
LA_RS_PSZ-AC:2 Cooling Capacity [ton] | PSZ-AC:2 Cooling Capacity [ton] | 51.0679 | 48.1751 | 51.8865 | 48.6719 | [6 empty] | 2021-05-06
LA_RS_PSZ-AC:3 Cooling Capacity [ton] | PSZ-AC:3 Cooling Capacity [ton] | 6.91 | 6.7694 | 6.9634 | 6.7987 | [6 empty] | 2021-05-06
LA_RS_PSZ-AC:4 Cooling Capacity [ton] | PSZ-AC:4 Cooling Capacity [ton] | 5.6985 | 5.5593 | 5.7089 | 5.5454 | [6 empty] | 2021-05-06
LA_RS_PSZ-AC:1 Supply Flow Rate [cfm] | PSZ-AC:1 Supply Flow Rate [cfm] | 4153.0048 | 3919.928 | 4216.5712 | 3983.4944 | [6 empty] | 2021-05-06
LA_RS_PSZ-AC:2 Supply Flow Rate [cfm] | PSZ-AC:2 Supply Flow Rate [cfm] | 15319.5024 | 14450.7616 | 15573.768 | 14599.0832 | [6 empty] | 2021-05-06
LA_RS_PSZ-AC:3 Supply Flow Rate [cfm] | PSZ-AC:3 Supply Flow Rate [cfm] | 2288.3904 | 2224.824 | 2330.768 | 2267.2016 | [6 empty] | 2021-05-06
LA_RS_PSZ-AC:4 Supply Flow Rate [cfm] | PSZ-AC:4 Supply Flow Rate [cfm] | 1758.6704 | 1695.104 | 1801.048 | 1737.4816 | [6 empty] | 2021-05-06
LA_RS_PSZ-AC:1 OA Rate [cfm] | PSZ-AC:1 OA Rate [cfm] | 490.669 | 490.669 | 490.669 | 490.669 | [6 empty] | 2021-05-06
LA_RS_PSZ-AC:2 OA Rate [cfm] | PSZ-AC:2 OA Rate [cfm] | 4005.1282 | 4005.1282 | 4005.1282 | 4005.1282 | [6 empty] | 2021-05-06
LA_RS_PSZ-AC:3 OA Rate [cfm] | PSZ-AC:3 OA Rate [cfm] | 377.3937 | 377.3937 | 377.3937 | 377.3937 | [6 empty] | 2021-05-06
LA_RS_PSZ-AC:4 OA Rate [cfm] | PSZ-AC:4 OA Rate [cfm] | 377.3937 | 377.3937 | 377.3937 | 377.3937 | [6 empty] | 2021-05-06
LA_RS_PSZ-AC:1 OA Damper [gravity, motorized] | PSZ-AC:1 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2021-05-06
LA_RS_PSZ-AC:2 OA Damper [gravity, motorized] | PSZ-AC:2 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2021-05-06
LA_RS_PSZ-AC:3 OA Damper [gravity, motorized] | PSZ-AC:3 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2021-05-06
LA_RS_PSZ-AC:4 OA Damper [gravity, motorized] | PSZ-AC:4 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2021-05-06
LA_RS_PSZ-AC:1 Heating Capacity [kBtu/hr] | PSZ-AC:1 Heating Capacity [kBtu/hr] | 175.4299 | 165.4452 | 179.3497 | 169.2204 | [6 empty] | 2021-05-06
LA_RS_PSZ-AC:2 Heating Capacity [kBtu/hr] | PSZ-AC:2 Heating Capacity [kBtu/hr] | 737.8668 | 700.6902 | 758.1817 | 718.2848 | [6 empty] | 2021-05-06
LA_RS_PSZ-AC:3 Heating Capacity [kBtu/hr] | PSZ-AC:3 Heating Capacity [kBtu/hr] | 102.0465 | 99.5189 | 104.8757 | 102.1349 | [6 empty] | 2021-05-06
LA_RS_PSZ-AC:4 Heating Capacity [kBtu/hr] | PSZ-AC:4 Heating Capacity [kBtu/hr] | 82.4016 | 79.7169 | 84.9584 | 82.102 | [6 empty] | 2021-05-06
id | item | Zone2A(LA-BatonRouge-LA) ASHRAE901-state_STD2016 | Zone2A(LA-BatonRouge-LA) ASHRAE901-state_STD2019 | Zone3A(LA-Shreveport-LA) ASHRAE901-state_STD2016 | Zone3A(LA-Shreveport-LA) ASHRAE901-state_STD2019 | [6 empty] | 2021-05-06
LA_PS_VAV_POD_1 Cooling Capacity [ton] | VAV_POD_1 Cooling Capacity [ton] | 18.618 | 18.1862 | 19.2416 | 18.3855 | [6 empty] | 2021-05-06
LA_PS_VAV_POD_2 Cooling Capacity [ton] | VAV_POD_2 Cooling Capacity [ton] | 18.6531 | 18.1569 | 19.3475 | 18.3626 | [6 empty] | 2021-05-06
LA_PS_VAV_POD_3 Cooling Capacity [ton] | VAV_POD_3 Cooling Capacity [ton] | 17.0191 | 16.0881 | 17.6021 | 16.5307 | [6 empty] | 2021-05-06
LA_PS_VAV_OTHER Cooling Capacity [ton] | VAV_OTHER Cooling Capacity [ton] | 26.0534 | 24.3874 | 26.8812 | 25.1966 | [6 empty] | 2021-05-06
LA_PS_PSZ-AC_1:6 Cooling Capacity [ton] | PSZ-AC_1:6 Cooling Capacity [ton] | 8.3598 | 7.9816 | 8.4522 | 8.0742 | [6 empty] | 2021-05-06
LA_PS_PSZ-AC_2:5 Cooling Capacity [ton] | PSZ-AC_2:5 Cooling Capacity [ton] | 5.2605 | 5.0828 | 5.3425 | 5.1675 | [6 empty] | 2021-05-06
LA_PS_PSZ-AC_2:7 Cooling Capacity [ton] | PSZ-AC_2:7 Cooling Capacity [ton] | 10.5074 | 10.5074 | 10.5074 | 10.5074 | [6 empty] | 2021-05-06
LA_PS_VAV_POD_1 Supply Flow Rate [cfm] | VAV_POD_1 Supply Flow Rate [cfm] | 5593.8432 | 5466.7104 | 5784.5424 | 5509.088 | [6 empty] | 2021-05-06
LA_PS_VAV_POD_2 Supply Flow Rate [cfm] | VAV_POD_2 Supply Flow Rate [cfm] | 5593.8432 | 5445.5216 | 5805.7312 | 5509.088 | [6 empty] | 2021-05-06
LA_PS_VAV_POD_3 Supply Flow Rate [cfm] | VAV_POD_3 Supply Flow Rate [cfm] | 5106.5008 | 4831.0464 | 5276.0112 | 4958.1792 | [6 empty] | 2021-05-06
LA_PS_VAV_OTHER Supply Flow Rate [cfm] | VAV_OTHER Supply Flow Rate [cfm] | 7818.6672 | 7310.136 | 8072.9328 | 7564.4016 | [6 empty] | 2021-05-06
LA_PS_PSZ-AC_2:5 Supply Flow Rate [cfm] | PSZ-AC_2:5 Supply Flow Rate [cfm] | 1589.16 | 1525.5936 | 1610.3488 | 1546.7824 | [6 empty] | 2021-05-06
LA_PS_PSZ-AC_1:6 Supply Flow Rate [cfm] | PSZ-AC_1:6 Supply Flow Rate [cfm] | 2500.2784 | 2394.3344 | 2542.656 | 2415.5232 | [6 empty] | 2021-05-06
LA_PS_PSZ-AC_2:7 Supply Flow Rate [cfm] | PSZ-AC_2:7 Supply Flow Rate [cfm] | 3157.1312 | 3157.1312 | 3157.1312 | 3157.1312 | [6 empty] | 2021-05-06
LA_PS_Supply Air Temp. Reset Flag | Supply Air Temp. Reset Flag | No | No | No | No | [6 empty] | 2021-05-06
LA_PS_VAV_POD_1 OA Rate [cfm] | VAV_POD_1 OA Rate [cfm] | 5586.9568 | 5457.3873 | 5774.0963 | 5517.1821 | [6 empty] | 2021-05-06
LA_PS_VAV_POD_2 OA Rate [cfm] | VAV_POD_2 OA Rate [cfm] | 5597.4877 | 5448.5728 | 5805.8583 | 5510.317 | [6 empty] | 2021-05-06
LA_PS_VAV_POD_3 OA Rate [cfm] | VAV_POD_3 OA Rate [cfm] | 5107.1577 | 4827.7621 | 5282.0924 | 4960.5947 | [6 empty] | 2021-05-06
LA_PS_VAV_OTHER OA Rate [cfm] | VAV_OTHER OA Rate [cfm] | 3736.1787 | 2988.8921 | 3736.1787 | 2988.8921 | [6 empty] | 2021-05-06
LA_PS_PSZ-AC_2:5 OA Rate [cfm] | PSZ-AC_2:5 OA Rate [cfm] | 1152.7343 | 1152.7343 | 1152.7343 | 1152.7343 | [6 empty] | 2021-05-06
LA_PS_PSZ-AC_1:6 OA Rate [cfm] | PSZ-AC_1:6 OA Rate [cfm] | 539.9118 | 539.9118 | 539.9118 | 539.9118 | [6 empty] | 2021-05-06
LA_PS_PSZ-AC_2:7 OA Rate [cfm] | PSZ-AC_2:7 OA Rate [cfm] | 3153.0841 | 3153.0841 | 3153.0841 | 3153.0841 | [6 empty] | 2021-05-06
LA_PS_VAV_POD_1 OA Damper [gravity, motorized] | VAV_POD_1 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2021-05-06
LA_PS_VAV_POD_2 OA Damper [gravity, motorized] | VAV_POD_2 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2021-05-06
LA_PS_VAV_POD_3 OA Damper [gravity, motorized] | VAV_POD_3 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2021-05-06
LA_PS_VAV_OTHER OA Damper [gravity, motorized] | VAV_OTHER OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2021-05-06
LA_PS_PSZ-AC_2:5 OA Damper [gravity, motorized] | PSZ-AC_2:5 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2021-05-06
LA_PS_PSZ-AC_1:6 OA Damper [gravity, motorized] | PSZ-AC_1:6 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2021-05-06
LA_PS_PSZ-AC_2:7 OA Damper [gravity, motorized] | PSZ-AC_2:7 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2021-05-06
LA_PS_VAV_POD_1 (economizer) | VAV_POD_1 (economizer) | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialEnthalpy | [6 empty] | 2021-05-06
LA_PS_VAV_POD_2 (economizer) | VAV_POD_2 (economizer) | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialEnthalpy | [6 empty] | 2021-05-06
LA_PS_VAV_POD_3 (economizer) | VAV_POD_3 (economizer) | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialEnthalpy | [6 empty] | 2021-05-06
LA_PS_VAV_OTHER (economizer) | VAV_OTHER (economizer) | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialEnthalpy | [6 empty] | 2021-05-06
LA_PS_PSZ-AC_2:5 (economizer) | PSZ-AC_2:5 (economizer) | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialEnthalpy | [6 empty] | 2021-05-06
LA_PS_PSZ-AC_1:6 (economizer) | PSZ-AC_1:6 (economizer) | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialEnthalpy | [6 empty] | 2021-05-06
LA_PS_PSZ-AC_2:7 (economizer) | PSZ-AC_2:7 (economizer) | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialEnthalpy | [6 empty] | 2021-05-06
LA_PS_VAV_Pod_1_ERV Flag | VAV_Pod_1_ERV Flag | Yes | Yes | Yes | Yes | [6 empty] | 2021-05-06
LA_PS_VAV_Pod_2_ERV Flag | VAV_Pod_2_ERV Flag | Yes | Yes | Yes | Yes | [6 empty] | 2021-05-06
LA_PS_VAV_Pod_3_ERV Flag | VAV_Pod_3_ERV Flag | Yes | Yes | Yes | Yes | [6 empty] | 2021-05-06
LA_PS_VAV_OTHER_ERV Flag | VAV_OTHER_ERV Flag | Yes | Yes | Yes | Yes | [6 empty] | 2021-05-06
LA_PS_PSZ_AC_2_5_ERV Flag | PSZ_AC_2_5_ERV Flag | Yes | Yes | Yes | Yes | [6 empty] | 2021-05-06
LA_PS_PSZ_AC_2_7_ERV Flag | PSZ_AC_2_7_ERV Flag | Yes | Yes | Yes | Yes | [6 empty] | 2021-05-06
LA_PS_HEATSYS1 Capacity [MMBTU/h] | HEATSYS1 Capacity [MMBTU/h] | 0.81168 | 0.75893 | 0.87446 | 0.82184 | [6 empty] | 2021-05-06
LA_PS_HEATSYS1 Flow Rate [gal/min] | HEATSYS1 Flow Rate [gal/min] | 83.3036 | 77.8898 | 89.7477 | 84.3467 | [6 empty] | 2021-05-06
LA_PS_VAV_POD_1 Fan Power [hp] | VAV_POD_1 Fan Power [hp] | 8.2424 | 8.0513 | 8.5185 | 8.1395 | [6 empty] | 2021-05-06
LA_PS_VAV_POD_2 Fan Power [hp] | VAV_POD_2 Fan Power [hp] | 8.258 | 8.0383 | 8.5654 | 8.1294 | [6 empty] | 2021-05-06
LA_PS_VAV_POD_3 Fan Power [hp] | VAV_POD_3 Fan Power [hp] | 7.5346 | 7.1224 | 7.7927 | 7.3184 | [6 empty] | 2021-05-06
LA_PS_VAV_OTHER Fan Power [hp] | VAV_OTHER Fan Power [hp] | 11.4468 | 10.7148 | 11.8105 | 11.0704 | [6 empty] | 2021-05-06
LA_PS_HEATSYS1 Pump Power [hp] | HEATSYS1 Pump Power [hp] | 1.8007 | 1.667 | 1.9399 | 1.8051 | [6 empty] | 2021-05-06
LA_PS_PSZ-AC_1:6 Heating Capacity [kBtu/hr] | PSZ-AC_1:6 Heating Capacity [kBtu/hr] | 197.7126 | 188.8859 | 200.711 | 191.949 | [6 empty] | 2021-05-06
LA_PS_PSZ-AC_2:5 Heating Capacity [kBtu/hr] | PSZ-AC_2:5 Heating Capacity [kBtu/hr] | 110.9787 | 109.0089 | 115.8076 | 113.8802 | [6 empty] | 2021-05-06
LA_PS_PSZ-AC_2:7 Heating Capacity [kBtu/hr] | PSZ-AC_2:7 Heating Capacity [kBtu/hr] | 260.5306 | 260.5306 | 271.5604 | 271.5604 | [6 empty] | 2021-05-06
LA_PS_ZN_VAV_BOXes_Max_Reheat_Water_Flow_GPM | ZN_VAV_BOXes_Max_Reheat_Water_Flow_GPM | 61.2224 | 56.7775 | 63.958 | 59.9842 | [6 empty] | 2021-05-06
id | item | Zone2A(LA-BatonRouge-LA) ASHRAE901-state_STD2016 | Zone2A(LA-BatonRouge-LA) ASHRAE901-state_STD2019 | Zone3A(LA-Shreveport-LA) ASHRAE901-state_STD2016 | Zone3A(LA-Shreveport-LA) ASHRAE901-state_STD2019 | [6 empty] | 2021-05-06
LA_SH_SAC_FRONTOFFICE Cooling Capacity [ton] | SAC_FRONTOFFICE Cooling Capacity [ton] | 2.5264 | 2.3946 | 2.5788 | 2.4353 | [6 empty] | 2021-05-06
LA_SH_SAC_FRONTLOUNGE Cooling Capacity [ton] | SAC_FRONTLOUNGE Cooling Capacity [ton] | 6.1678 | 5.8515 | 6.2421 | 5.9313 | [6 empty] | 2021-05-06
LA_SH_SAC_MEETINGROOM Cooling Capacity [ton] | SAC_MEETINGROOM Cooling Capacity [ton] | 2.9296 | 2.8348 | 2.9882 | 2.8798 | [6 empty] | 2021-05-06
LA_SH_SAC_EXC_EMPLGE_RESTRM Cooling Capacity [ton] | SAC_EXC_EMPLGE_RESTRM Cooling Capacity [ton] | 6.1907 | 6.1566 | 6.2942 | 6.2516 | [6 empty] | 2021-05-06
LA_SH_SAC_FO_ADDAQ SUPPLY FAN Supply Flow Rate [cfm] | SAC_FO_ADDAQ SUPPLY FAN Supply Flow Rate [cfm] | 805.1744 | 741.608 | 826.3632 | 762.7968 | [6 empty] | 2021-05-06
LA_SH_SAC_FL_ADDAQ SUPPLY FAN Supply Flow Rate [cfm] | SAC_FL_ADDAQ SUPPLY FAN Supply Flow Rate [cfm] | 1843.4256 | 1758.6704 | 1864.6144 | 1779.8592 | [6 empty] | 2021-05-06
LA_SH_SAC_MR_ADDAQ SUPPLY FAN Supply Flow Rate [cfm] | SAC_MR_ADDAQ SUPPLY FAN Supply Flow Rate [cfm] | 868.7408 | 847.552 | 889.9296 | 868.7408 | [6 empty] | 2021-05-06
LA_SH_SAC_EXC_ADDAQ SUPPLY FAN Supply Flow Rate [cfm] | SAC_EXC_ADDAQ SUPPLY FAN Supply Flow Rate [cfm] | 2161.2576 | 2140.0688 | 2182.4464 | 2182.4464 | [6 empty] | 2021-05-06
LA_SH_SAC_Exc_EmpLge_RestRm OA Rate [cfm] | SAC_Exc_EmpLge_RestRm OA Rate [cfm] | 199.9928 | 199.9928 | 199.9928 | 199.9928 | [6 empty] | 2021-05-06
LA_SH_SAC_FrontLounge OA Rate [cfm] | SAC_FrontLounge OA Rate [cfm] | 500.0133 | 500.0133 | 500.0133 | 500.0133 | [6 empty] | 2021-05-06
LA_SH_SAC_FrontOffice OA Rate [cfm] | SAC_FrontOffice OA Rate [cfm] | 119.2938 | 119.2938 | 119.2938 | 119.2938 | [6 empty] | 2021-05-06
LA_SH_SAC_MeetingRoom OA Rate [cfm] | SAC_MeetingRoom OA Rate [cfm] | 267.7629 | 267.7629 | 267.7629 | 267.7629 | [6 empty] | 2021-05-06
LA_SH_SAC_FrontLounge OA Damper [gravity, motorized] | SAC_FrontLounge OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2021-05-06
LA_SH_SAC_FrontOffice (economizer) | SAC_FrontOffice (economizer) | No | No | No | No | [6 empty] | 2021-05-06
LA_SH_SAC_FrontLounge (economizer) | SAC_FrontLounge (economizer) | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialEnthalpy | [6 empty] | 2021-05-06
LA_SH_SAC_MeetingRoom (economizer) | SAC_MeetingRoom (economizer) | No | No | No | No | [6 empty] | 2021-05-06
LA_SH_SAC_Exc_EmpLge_RestRm (economizer) | SAC_Exc_EmpLge_RestRm (economizer) | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialEnthalpy | [6 empty] | 2021-05-06
LA_SH_SAC_FRONTOFFICE Heating Capacity [kBtu/hr] | SAC_FRONTOFFICE Heating Capacity [kBtu/hr] | 34.8031 | 32.7701 | 35.9358 | 33.7676 | [6 empty] | 2021-05-06
LA_SH_SAC_FRONTLOUNGE Heating Capacity [kBtu/hr] | SAC_FRONTLOUNGE Heating Capacity [kBtu/hr] | 90.9218 | 87.4367 | 93.1506 | 89.748 | [6 empty] | 2021-05-06
LA_SH_SAC_MEETINGROOM Heating Capacity [kBtu/hr] | SAC_MEETINGROOM Heating Capacity [kBtu/hr] | 44.575 | 43.5302 | 46.0024 | 44.8159 | [6 empty] | 2021-05-06
LA_SH_SAC_EXC_EMPLGE_RESTRM Heating Capacity [kBtu/hr] | SAC_EXC_EMPLGE_RESTRM Heating Capacity [kBtu/hr] | 88.3466 | 87.8231 | 89.8136 | 89.1575 | [6 empty] | 2021-05-06
id | item | Zone2A(LA-BatonRouge-LA) ASHRAE901-state_STD2016 | Zone2A(LA-BatonRouge-LA) ASHRAE901-state_STD2019 | Zone3A(LA-Shreveport-LA) ASHRAE901-state_STD2016 | Zone3A(LA-Shreveport-LA) ASHRAE901-state_STD2019 | [6 empty] | 2021-05-06
LA_MA_SPLIT GSW COOLING COIL Cooling Capacity [ton] | SPLIT GSW COOLING COIL Cooling Capacity [ton] | 0.91352 | 0.90265 | 0.94619 | 0.93521 | [6 empty] | 2021-05-06
LA_MA_SPLIT GNW COOLING COIL Cooling Capacity [ton] | SPLIT GNW COOLING COIL Cooling Capacity [ton] | 0.90755 | 0.89637 | 0.93306 | 0.92199 | [6 empty] | 2021-05-06
LA_MA_SPLIT OFFICE COOLING COIL Cooling Capacity [ton] | SPLIT OFFICE COOLING COIL Cooling Capacity [ton] | 1.7534 | 1.6732 | 1.7763 | 1.6735 | [6 empty] | 2021-05-06
LA_MA_SPLIT GNE COOLING COIL Cooling Capacity [ton] | SPLIT GNE COOLING COIL Cooling Capacity [ton] | 0.81378 | 0.80427 | 0.82433 | 0.81498 | [6 empty] | 2021-05-06
LA_MA_SPLIT GN1 COOLING COIL Cooling Capacity [ton] | SPLIT GN1 COOLING COIL Cooling Capacity [ton] | 0.71333 | 0.70492 | 0.71108 | 0.70196 | [6 empty] | 2021-05-06
LA_MA_SPLIT GN2 COOLING COIL Cooling Capacity [ton] | SPLIT GN2 COOLING COIL Cooling Capacity [ton] | 0.71175 | 0.70335 | 0.70933 | 0.70022 | [6 empty] | 2021-05-06
LA_MA_SPLIT GS1 COOLING COIL Cooling Capacity [ton] | SPLIT GS1 COOLING COIL Cooling Capacity [ton] | 0.71366 | 0.70527 | 0.72118 | 0.71256 | [6 empty] | 2021-05-06
LA_MA_SPLIT GS2 COOLING COIL Cooling Capacity [ton] | SPLIT GS2 COOLING COIL Cooling Capacity [ton] | 0.74917 | 0.73659 | 0.75688 | 0.74135 | [6 empty] | 2021-05-06
LA_MA_SPLIT MSW COOLING COIL Cooling Capacity [ton] | SPLIT MSW COOLING COIL Cooling Capacity [ton] | 2.0153 | 1.992 | 2.0678 | 2.0452 | [6 empty] | 2021-05-06
LA_MA_SPLIT MNW COOLING COIL Cooling Capacity [ton] | SPLIT MNW COOLING COIL Cooling Capacity [ton] | 2.0108 | 1.9874 | 2.0574 | 2.0349 | [6 empty] | 2021-05-06
LA_MA_SPLIT MSE COOLING COIL Cooling Capacity [ton] | SPLIT MSE COOLING COIL Cooling Capacity [ton] | 1.7513 | 1.7306 | 1.7793 | 1.7586 | [6 empty] | 2021-05-06
LA_MA_SPLIT MNE COOLING COIL Cooling Capacity [ton] | SPLIT MNE COOLING COIL Cooling Capacity [ton] | 1.7582 | 1.7371 | 1.7621 | 1.7416 | [6 empty] | 2021-05-06
LA_MA_SPLIT MN1 COOLING COIL Cooling Capacity [ton] | SPLIT MN1 COOLING COIL Cooling Capacity [ton] | 1.4861 | 1.4688 | 1.4685 | 1.4505 | [6 empty] | 2021-05-06
LA_MA_SPLIT MN2 COOLING COIL Cooling Capacity [ton] | SPLIT MN2 COOLING COIL Cooling Capacity [ton] | 1.482 | 1.4647 | 1.464 | 1.4461 | [6 empty] | 2021-05-06
LA_MA_SPLIT MS1 COOLING COIL Cooling Capacity [ton] | SPLIT MS1 COOLING COIL Cooling Capacity [ton] | 1.4864 | 1.4682 | 1.495 | 1.477 | [6 empty] | 2021-05-06
LA_MA_SPLIT MS2 COOLING COIL Cooling Capacity [ton] | SPLIT MS2 COOLING COIL Cooling Capacity [ton] | 1.4824 | 1.4643 | 1.4908 | 1.4728 | [6 empty] | 2021-05-06
LA_MA_SPLIT TSW COOLING COIL Cooling Capacity [ton] | SPLIT TSW COOLING COIL Cooling Capacity [ton] | 1.2376 | 1.2255 | 1.2767 | 1.2652 | [6 empty] | 2021-05-06
LA_MA_SPLIT TNW COOLING COIL Cooling Capacity [ton] | SPLIT TNW COOLING COIL Cooling Capacity [ton] | 1.2206 | 1.2089 | 1.2581 | 1.2469 | [6 empty] | 2021-05-06
LA_MA_SPLIT TSE COOLING COIL Cooling Capacity [ton] | SPLIT TSE COOLING COIL Cooling Capacity [ton] | 1.126 | 1.115 | 1.1631 | 1.1519 | [6 empty] | 2021-05-06
LA_MA_SPLIT TNE COOLING COIL Cooling Capacity [ton] | SPLIT TNE COOLING COIL Cooling Capacity [ton] | 1.1012 | 1.0901 | 1.1281 | 1.117 | [6 empty] | 2021-05-06
LA_MA_SPLIT TN1 COOLING COIL Cooling Capacity [ton] | SPLIT TN1 COOLING COIL Cooling Capacity [ton] | 0.90342 | 0.8942 | 0.91936 | 0.91059 | [6 empty] | 2021-05-06
LA_MA_SPLIT TN2 COOLING COIL Cooling Capacity [ton] | SPLIT TN2 COOLING COIL Cooling Capacity [ton] | 0.89866 | 0.88947 | 0.9143 | 0.90556 | [6 empty] | 2021-05-06
LA_MA_SPLIT TS1 COOLING COIL Cooling Capacity [ton] | SPLIT TS1 COOLING COIL Cooling Capacity [ton] | 0.9426 | 0.93455 | 0.96908 | 0.9595 | [6 empty] | 2021-05-06
LA_MA_SPLIT TS2 COOLING COIL Cooling Capacity [ton] | SPLIT TS2 COOLING COIL Cooling Capacity [ton] | 0.94502 | 0.93554 | 0.97326 | 0.96363 | [6 empty] | 2021-05-06
LA_MA_Split GN1 Furnace with DX Cooling OA Rate [cfm] | Split GN1 Furnace with DX Cooling OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | [6 empty] | 2021-05-06
LA_MA_Split GN2 Furnace with DX Cooling OA Rate [cfm] | Split GN2 Furnace with DX Cooling OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | [6 empty] | 2021-05-06
LA_MA_Split GNE Furnace with DX Cooling OA Rate [cfm] | Split GNE Furnace with DX Cooling OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | [6 empty] | 2021-05-06
LA_MA_Split GNW Furnace with DX Cooling OA Rate [cfm] | Split GNW Furnace with DX Cooling OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | [6 empty] | 2021-05-06
LA_MA_Split GS1 Furnace with DX Cooling OA Rate [cfm] | Split GS1 Furnace with DX Cooling OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | [6 empty] | 2021-05-06
LA_MA_Split GS2 Furnace with DX Cooling OA Rate [cfm] | Split GS2 Furnace with DX Cooling OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | [6 empty] | 2021-05-06
LA_MA_Split GSW Furnace with DX Cooling OA Rate [cfm] | Split GSW Furnace with DX Cooling OA Rate [cfm] | 56.9945 | 56.9945 | 56.9945 | 56.9945 | [6 empty] | 2021-05-06
LA_MA_Split MN1 Furnace with DX Cooling OA Rate [cfm] | Split MN1 Furnace with DX Cooling OA Rate [cfm] | 109.9824 | 109.9824 | 109.9824 | 109.9824 | [6 empty] | 2021-05-06
LA_MA_Split MN2 Furnace with DX Cooling OA Rate [cfm] | Split MN2 Furnace with DX Cooling OA Rate [cfm] | 109.9824 | 109.9824 | 109.9824 | 109.9824 | [6 empty] | 2021-05-06
LA_MA_Split MNE Furnace with DX Cooling OA Rate [cfm] | Split MNE Furnace with DX Cooling OA Rate [cfm] | 109.9824 | 109.9824 | 109.9824 | 109.9824 | [6 empty] | 2021-05-06
LA_MA_Split MNW Furnace with DX Cooling OA Rate [cfm] | Split MNW Furnace with DX Cooling OA Rate [cfm] | 109.9824 | 109.9824 | 109.9824 | 109.9824 | [6 empty] | 2021-05-06
LA_MA_Split MS1 Furnace with DX Cooling OA Rate [cfm] | Split MS1 Furnace with DX Cooling OA Rate [cfm] | 109.9824 | 109.9824 | 109.9824 | 109.9824 | [6 empty] | 2021-05-06
LA_MA_Split MS2 Furnace with DX Cooling OA Rate [cfm] | Split MS2 Furnace with DX Cooling OA Rate [cfm] | 109.9824 | 109.9824 | 109.9824 | 109.9824 | [6 empty] | 2021-05-06
LA_MA_Split MSE Furnace with DX Cooling OA Rate [cfm] | Split MSE Furnace with DX Cooling OA Rate [cfm] | 109.9824 | 109.9824 | 109.9824 | 109.9824 | [6 empty] | 2021-05-06
LA_MA_Split MSW Furnace with DX Cooling OA Rate [cfm] | Split MSW Furnace with DX Cooling OA Rate [cfm] | 109.9824 | 109.9824 | 109.9824 | 109.9824 | [6 empty] | 2021-05-06
LA_MA_Split Office Furnace with DX Cooling OA Rate [cfm] | Split Office Furnace with DX Cooling OA Rate [cfm] | 80.7372 | 80.7372 | 80.7372 | 80.7372 | [6 empty] | 2021-05-06
LA_MA_Split TN1 Furnace with DX Cooling OA Rate [cfm] | Split TN1 Furnace with DX Cooling OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | [6 empty] | 2021-05-06
LA_MA_Split TN2 Furnace with DX Cooling OA Rate [cfm] | Split TN2 Furnace with DX Cooling OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | [6 empty] | 2021-05-06
LA_MA_Split TNE Furnace with DX Cooling OA Rate [cfm] | Split TNE Furnace with DX Cooling OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | [6 empty] | 2021-05-06
LA_MA_Split TNW Furnace with DX Cooling OA Rate [cfm] | Split TNW Furnace with DX Cooling OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | [6 empty] | 2021-05-06
LA_MA_Split TS1 Furnace with DX Cooling OA Rate [cfm] | Split TS1 Furnace with DX Cooling OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | [6 empty] | 2021-05-06
LA_MA_Split TS2 Furnace with DX Cooling OA Rate [cfm] | Split TS2 Furnace with DX Cooling OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | [6 empty] | 2021-05-06
LA_MA_Split TSE Furnace with DX Cooling OA Rate [cfm] | Split TSE Furnace with DX Cooling OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | [6 empty] | 2021-05-06
LA_MA_Split TSW Furnace with DX Cooling OA Rate [cfm] | Split TSW Furnace with DX Cooling OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | [6 empty] | 2021-05-06
LA_MA_SPLIT GSW HEATING COIL Heating Capacity [kBtu/hr] | SPLIT GSW HEATING COIL Heating Capacity [kBtu/hr] | 5.8197 | 5.7175 | 6.4652 | 6.3866 | [6 empty] | 2021-05-06
LA_MA_SPLIT GNW HEATING COIL Heating Capacity [kBtu/hr] | SPLIT GNW HEATING COIL Heating Capacity [kBtu/hr] | 5.7774 | 5.6713 | 6.4128 | 6.3305 | [6 empty] | 2021-05-06
LA_MA_SPLIT OFFICE HEATING COIL Heating Capacity [kBtu/hr] | SPLIT OFFICE HEATING COIL Heating Capacity [kBtu/hr] | 15.7347 | 15.5485 | 17.1354 | 16.9934 | [6 empty] | 2021-05-06
LA_MA_SPLIT GNE HEATING COIL Heating Capacity [kBtu/hr] | SPLIT GNE HEATING COIL Heating Capacity [kBtu/hr] | 5.7774 | 5.6713 | 6.4128 | 6.3305 | [6 empty] | 2021-05-06
LA_MA_SPLIT GN1 HEATING COIL Heating Capacity [kBtu/hr] | SPLIT GN1 HEATING COIL Heating Capacity [kBtu/hr] | 4.5438 | 4.5438 | 4.7361 | 4.7361 | [6 empty] | 2021-05-06
LA_MA_SPLIT GN2 HEATING COIL Heating Capacity [kBtu/hr] | SPLIT GN2 HEATING COIL Heating Capacity [kBtu/hr] | 4.5438 | 4.5438 | 4.7361 | 4.7361 | [6 empty] | 2021-05-06
LA_MA_SPLIT GS1 HEATING COIL Heating Capacity [kBtu/hr] | SPLIT GS1 HEATING COIL Heating Capacity [kBtu/hr] | 4.5438 | 4.5438 | 4.7361 | 4.7361 | [6 empty] | 2021-05-06
LA_MA_SPLIT GS2 HEATING COIL Heating Capacity [kBtu/hr] | SPLIT GS2 HEATING COIL Heating Capacity [kBtu/hr] | 4.5438 | 4.5438 | 4.9421 | 4.9066 | [6 empty] | 2021-05-06
LA_MA_SPLIT MSW HEATING COIL Heating Capacity [kBtu/hr] | SPLIT MSW HEATING COIL Heating Capacity [kBtu/hr] | 10.0365 | 9.836 | 11.7601 | 11.6086 | [6 empty] | 2021-05-06
LA_MA_SPLIT MNW HEATING COIL Heating Capacity [kBtu/hr] | SPLIT MNW HEATING COIL Heating Capacity [kBtu/hr] | 10.1049 | 9.8942 | 11.8344 | 11.6732 | [6 empty] | 2021-05-06
LA_MA_SPLIT MSE HEATING COIL Heating Capacity [kBtu/hr] | SPLIT MSE HEATING COIL Heating Capacity [kBtu/hr] | 10.0365 | 9.836 | 11.7601 | 11.6086 | [6 empty] | 2021-05-06
LA_MA_SPLIT MNE HEATING COIL Heating Capacity [kBtu/hr] | SPLIT MNE HEATING COIL Heating Capacity [kBtu/hr] | 10.1049 | 9.8942 | 11.8344 | 11.6732 | [6 empty] | 2021-05-06
LA_MA_SPLIT MN1 HEATING COIL Heating Capacity [kBtu/hr] | SPLIT MN1 HEATING COIL Heating Capacity [kBtu/hr] | 9.0875 | 9.0875 | 9.4722 | 9.4722 | [6 empty] | 2021-05-06
LA_MA_SPLIT MN2 HEATING COIL Heating Capacity [kBtu/hr] | SPLIT MN2 HEATING COIL Heating Capacity [kBtu/hr] | 9.0875 | 9.0875 | 9.4722 | 9.4722 | [6 empty] | 2021-05-06
LA_MA_SPLIT MS1 HEATING COIL Heating Capacity [kBtu/hr] | SPLIT MS1 HEATING COIL Heating Capacity [kBtu/hr] | 9.0875 | 9.0875 | 9.4722 | 9.4722 | [6 empty] | 2021-05-06
LA_MA_SPLIT MS2 HEATING COIL Heating Capacity [kBtu/hr] | SPLIT MS2 HEATING COIL Heating Capacity [kBtu/hr] | 9.0875 | 9.0875 | 9.4722 | 9.4722 | [6 empty] | 2021-05-06
LA_MA_SPLIT TSW HEATING COIL Heating Capacity [kBtu/hr] | SPLIT TSW HEATING COIL Heating Capacity [kBtu/hr] | 7.7602 | 7.6631 | 8.9172 | 8.8426 | [6 empty] | 2021-05-06
LA_MA_SPLIT TNW HEATING COIL Heating Capacity [kBtu/hr] | SPLIT TNW HEATING COIL Heating Capacity [kBtu/hr] | 7.8006 | 7.6987 | 8.9615 | 8.8824 | [6 empty] | 2021-05-06
LA_MA_SPLIT TSE HEATING COIL Heating Capacity [kBtu/hr] | SPLIT TSE HEATING COIL Heating Capacity [kBtu/hr] | 7.7602 | 7.6631 | 8.9172 | 8.8426 | [6 empty] | 2021-05-06
LA_MA_SPLIT TNE HEATING COIL Heating Capacity [kBtu/hr] | SPLIT TNE HEATING COIL Heating Capacity [kBtu/hr] | 7.8006 | 7.6987 | 8.9615 | 8.8824 | [6 empty] | 2021-05-06
LA_MA_SPLIT TN1 HEATING COIL Heating Capacity [kBtu/hr] | SPLIT TN1 HEATING COIL Heating Capacity [kBtu/hr] | 5.9664 | 5.9216 | 6.8147 | 6.7847 | [6 empty] | 2021-05-06
LA_MA_SPLIT TN2 HEATING COIL Heating Capacity [kBtu/hr] | SPLIT TN2 HEATING COIL Heating Capacity [kBtu/hr] | 5.9664 | 5.9216 | 6.8147 | 6.7847 | [6 empty] | 2021-05-06
LA_MA_SPLIT TS1 HEATING COIL Heating Capacity [kBtu/hr] | SPLIT TS1 HEATING COIL Heating Capacity [kBtu/hr] | 5.9189 | 5.8787 | 6.7631 | 6.7376 | [6 empty] | 2021-05-06
LA_MA_SPLIT TS2 HEATING COIL Heating Capacity [kBtu/hr] | SPLIT TS2 HEATING COIL Heating Capacity [kBtu/hr] | 5.9189 | 5.8787 | 6.7631 | 6.7376 | [6 empty] | 2021-05-06
LA_MA_Split_GSW ERV Flag | Split_GSW ERV Flag | No | Yes | No | Yes | [6 empty] | 2021-05-06
LA_MA_Split_GNW ERV Flag | Split_GNW ERV Flag | No | Yes | No | Yes | [6 empty] | 2021-05-06
LA_MA_Split_GNE ERV Flag | Split_GNE ERV Flag | No | Yes | No | Yes | [6 empty] | 2021-05-06
LA_MA_Split_GN1 ERV Flag | Split_GN1 ERV Flag | No | Yes | No | Yes | [6 empty] | 2021-05-06
LA_MA_Split_GN2 ERV Flag | Split_GN2 ERV Flag | No | Yes | No | Yes | [6 empty] | 2021-05-06
LA_MA_Split_GS1 ERV Flag | Split_GS1 ERV Flag | No | Yes | No | Yes | [6 empty] | 2021-05-06
LA_MA_Split_GS2 ERV Flag | Split_GS2 ERV Flag | No | Yes | No | Yes | [6 empty] | 2021-05-06
LA_MA_Split_MSW ERV Flag | Split_MSW ERV Flag | No | Yes | No | Yes | [6 empty] | 2021-05-06
LA_MA_Split_MNW ERV Flag | Split_MNW ERV Flag | No | Yes | No | Yes | [6 empty] | 2021-05-06
LA_MA_Split_MSE ERV Flag | Split_MSE ERV Flag | No | Yes | No | Yes | [6 empty] | 2021-05-06
LA_MA_Split_MNE ERV Flag | Split_MNE ERV Flag | No | Yes | No | Yes | [6 empty] | 2021-05-06
LA_MA_Split_MN1 ERV Flag | Split_MN1 ERV Flag | No | Yes | No | Yes | [6 empty] | 2021-05-06
LA_MA_Split_MN2 ERV Flag | Split_MN2 ERV Flag | No | Yes | No | Yes | [6 empty] | 2021-05-06
LA_MA_Split_MS1 ERV Flag | Split_MS1 ERV Flag | No | Yes | No | Yes | [6 empty] | 2021-05-06
LA_MA_Split_MS2 ERV Flag | Split_MS2 ERV Flag | No | Yes | No | Yes | [6 empty] | 2021-05-06
LA_MA_Split_TSW ERV Flag | Split_TSW ERV Flag | No | Yes | No | Yes | [6 empty] | 2021-05-06
LA_MA_Split_TNW ERV Flag | Split_TNW ERV Flag | No | Yes | No | Yes | [6 empty] | 2021-05-06
LA_MA_Split_TSE ERV Flag | Split_TSE ERV Flag | No | Yes | No | Yes | [6 empty] | 2021-05-06
LA_MA_Split_TNE ERV Flag | Split_TNE ERV Flag | No | Yes | No | Yes | [6 empty] | 2021-05-06
LA_MA_Split_TN1 ERV Flag | Split_TN1 ERV Flag | No | Yes | No | Yes | [6 empty] | 2021-05-06
LA_MA_Split_TN2 ERV Flag | Split_TN2 ERV Flag | No | Yes | No | Yes | [6 empty] | 2021-05-06
LA_MA_Split_TS1 ERV Flag | Split_TS1 ERV Flag | No | Yes | No | Yes | [6 empty] | 2021-05-06
LA_MA_Split_TS2 ERV Flag | Split_TS2 ERV Flag | No | Yes | No | Yes | [6 empty] | 2021-05-06
id | item | Zone5A(MA-BostonLogan-MA) ASHRAE901-state_STD2016 | Zone5A(MA-BostonLogan-MA) ASHRAE901-state_STD2019 | [8 empty] | 2021-05-06
MA_SO_PSZ-AC:1 Cooling Capacity [ton] | PSZ-AC:1 Cooling Capacity [ton] | 1.7933 | 1.6985 | [8 empty] | 2021-05-06
MA_SO_PSZ-AC:2 Cooling Capacity [ton] | PSZ-AC:2 Cooling Capacity [ton] | 1.5528 | 1.4909 | [8 empty] | 2021-05-06
MA_SO_PSZ-AC:3 Cooling Capacity [ton] | PSZ-AC:3 Cooling Capacity [ton] | 1.0906 | 1.0524 | [8 empty] | 2021-05-06
MA_SO_PSZ-AC:4 Cooling Capacity [ton] | PSZ-AC:4 Cooling Capacity [ton] | 1.4748 | 1.3974 | [8 empty] | 2021-05-06
MA_SO_PSZ-AC:5 Cooling Capacity [ton] | PSZ-AC:5 Cooling Capacity [ton] | 1.2858 | 1.2462 | [8 empty] | 2021-05-06
MA_SO_PSZ-AC:1 Supply Flow Rate [cfm] | PSZ-AC:1 Supply Flow Rate [cfm] | 635.664 | 593.2864 | [8 empty] | 2021-05-06
MA_SO_PSZ-AC:2 Supply Flow Rate [cfm] | PSZ-AC:2 Supply Flow Rate [cfm] | 572.0976 | 529.72 | [8 empty] | 2021-05-06
MA_SO_PSZ-AC:3 Supply Flow Rate [cfm] | PSZ-AC:3 Supply Flow Rate [cfm] | 444.9648 | 423.776 | [8 empty] | 2021-05-06
MA_SO_PSZ-AC:4 Supply Flow Rate [cfm] | PSZ-AC:4 Supply Flow Rate [cfm] | 529.72 | 487.3424 | [8 empty] | 2021-05-06
MA_SO_PSZ-AC:5 Supply Flow Rate [cfm] | PSZ-AC:5 Supply Flow Rate [cfm] | 529.72 | 508.5312 | [8 empty] | 2021-05-06
MA_SO_PSZ-AC:1 OA Rate [cfm] | PSZ-AC:1 OA Rate [cfm] | 136.9178 | 136.9178 | [8 empty] | 2021-05-06
MA_SO_PSZ-AC:2 OA Rate [cfm] | PSZ-AC:2 OA Rate [cfm] | 103.7925 | 103.7925 | [8 empty] | 2021-05-06
MA_SO_PSZ-AC:3 OA Rate [cfm] | PSZ-AC:3 OA Rate [cfm] | 61.5711 | 61.5711 | [8 empty] | 2021-05-06
MA_SO_PSZ-AC:4 OA Rate [cfm] | PSZ-AC:4 OA Rate [cfm] | 103.7925 | 103.7925 | [8 empty] | 2021-05-06
MA_SO_PSZ-AC:5 OA Rate [cfm] | PSZ-AC:5 OA Rate [cfm] | 61.5711 | 61.5711 | [8 empty] | 2021-05-06
MA_SO_PSZ-AC:1 heating Capacity [kBtu/hr] | PSZ-AC:1 heating Capacity [kBtu/hr] | 14.2916 | 14.2916 | [8 empty] | 2021-05-06
MA_SO_PSZ-AC:2 heating Capacity [kBtu/hr] | PSZ-AC:2 heating Capacity [kBtu/hr] | 20.5507 | 20.3402 | [8 empty] | 2021-05-06
MA_SO_PSZ-AC:3 heating Capacity [kBtu/hr] | PSZ-AC:3 heating Capacity [kBtu/hr] | 12.6071 | 12.4906 | [8 empty] | 2021-05-06
MA_SO_PSZ-AC:4 heating Capacity [kBtu/hr] | PSZ-AC:4 heating Capacity [kBtu/hr] | 20.4721 | 20.2903 | [8 empty] | 2021-05-06
MA_SO_PSZ-AC:5 heating Capacity [kBtu/hr] | PSZ-AC:5 heating Capacity [kBtu/hr] | 12.6683 | 12.5453 | [8 empty] | 2021-05-06
id | item | Zone5A(MA-BostonLogan-MA) ASHRAE901-state_STD2016 | Zone5A(MA-BostonLogan-MA) ASHRAE901-state_STD2019 | [8 empty] | 2021-05-06
MA_LO_CAV_BAS Supply Flow Rate [cfm] | CAV_BAS Supply Flow Rate [cfm] | 11569.0848 | 10700.344 | [8 empty] | 2021-05-06
MA_LO_VAV_BOT WITH REHEAT Supply Flow Rate [cfm] | VAV_BOT WITH REHEAT Supply Flow Rate [cfm] | 19917.472 | 18985.1648 | [8 empty] | 2021-05-06
MA_LO_VAV_MID WITH REHEAT Supply Flow Rate [cfm] | VAV_MID WITH REHEAT Supply Flow Rate [cfm] | 186503.8179 | 177689.2771 | [8 empty] | 2021-05-06
MA_LO_VAV_TOP WITH REHEAT Supply Flow Rate [cfm] | VAV_TOP WITH REHEAT Supply Flow Rate [cfm] | 19324.1856 | 18561.3888 | [8 empty] | 2021-05-06
MA_LO_Supply Air Temp. Reset Flag | Supply Air Temp. Reset Flag | Yes | Yes | [8 empty] | 2021-05-06
MA_LO_CAV_BAS OA Rate [cfm] | CAV_BAS OA Rate [cfm] | 2542.8255 | 2542.8255 | [8 empty] | 2021-05-06
MA_LO_VAV_BOT WITH REHEAT OA Rate [cfm] | VAV_BOT WITH REHEAT OA Rate [cfm] | 5377.8022 | 4302.174 | [8 empty] | 2021-05-06
MA_LO_VAV_MID WITH REHEAT OA Rate [cfm] | VAV_MID WITH REHEAT OA Rate [cfm] | 53777.9373 | 43021.7396 | [8 empty] | 2021-05-06
MA_LO_VAV_TOP WITH REHEAT OA Rate [cfm] | VAV_TOP WITH REHEAT OA Rate [cfm] | 5377.8022 | 4302.174 | [8 empty] | 2021-05-06
MA_LO_AIRLOOP DATACENTER BASEMENT OA Rate [cfm] | AIRLOOP DATACENTER BASEMENT OA Rate [cfm] | 716.9654 | 716.9654 | [8 empty] | 2021-05-06
MA_LO_VAV_bot_WITH_REHEAT ERV Flag | VAV_bot_WITH_REHEAT ERV Flag | Yes | Yes | [8 empty] | 2021-05-06
MA_LO_VAV_mid_WITH_REHEAT ERV Flag | VAV_mid_WITH_REHEAT ERV Flag | Yes | Yes | [8 empty] | 2021-05-06
MA_LO_VAV_top_WITH_REHEAT ERV Flag | VAV_top_WITH_REHEAT ERV Flag | Yes | Yes | [8 empty] | 2021-05-06
MA_LO_COOLSYS1 CHILLER1 Capacity [ton] | COOLSYS1 CHILLER1 Capacity [ton] | 402.5924 | 366.6199 | [8 empty] | 2021-05-06
MA_LO_COOLSYS1 CHILLER2 Capacity [ton] | COOLSYS1 CHILLER2 Capacity [ton] | 402.5924 | 366.6199 | [8 empty] | 2021-05-06
MA_LO_TOWERWATERSYS COOLTOWER 1 Capacity [ton] | TOWERWATERSYS COOLTOWER 1 Capacity [ton] | 382.1274 | 347.984 | [8 empty] | 2021-05-06
MA_LO_TOWERWATERSYS COOLTOWER 2 Capacity [ton] | TOWERWATERSYS COOLTOWER 2 Capacity [ton] | 382.1274 | 347.984 | [8 empty] | 2021-05-06
MA_LO_HEATSYS1 BOILER Capacity [MMBTU/h] | HEATSYS1 BOILER Capacity [MMBTU/h] | 4486.7134 | 3981.9706 | [8 empty] | 2021-05-06
MA_LO_COOLSYS1 PUMP Flow Rate [gal/min] | COOLSYS1 PUMP Flow Rate [gal/min] | 0 | 0 | [8 empty] | 2021-05-06
MA_LO_COOLSYS1 CHILLER1 PUMP Flow Rate [gal/min] | COOLSYS1 CHILLER1 PUMP Flow Rate [gal/min] | 634.3125 | 577.5335 | [8 empty] | 2021-05-06
MA_LO_COOLSYS1 CHILLER2 PUMP Flow Rate [gal/min] | COOLSYS1 CHILLER2 PUMP Flow Rate [gal/min] | 634.3125 | 577.5335 | [8 empty] | 2021-05-06
MA_LO_COOLSYS1 PUMP SECONDARY Flow Rate [gal/min] | COOLSYS1 PUMP SECONDARY Flow Rate [gal/min] | 1268.625 | 1155.0669 | [8 empty] | 2021-05-06
MA_LO_HEATSYS1 PUMP Flow Rate [gal/min] | HEATSYS1 PUMP Flow Rate [gal/min] | 920.9577 | 817.352 | [8 empty] | 2021-05-06
MA_LO_TOWERWATERSYS PUMP Flow Rate [gal/min] | TOWERWATERSYS PUMP Flow Rate [gal/min] | 2221.1058 | 2022.6597 | [8 empty] | 2021-05-06
MA_LO_PLANT CIRC PUMP Flow Rate [gal/min] | PLANT CIRC PUMP Flow Rate [gal/min] | 207.9166 | 207.0829 | [8 empty] | 2021-05-06
MA_LO_COOLSYS1 PUMP SECONDARY Pressure setpoint reset [yes,no] | COOLSYS1 PUMP SECONDARY Pressure setpoint reset [yes,no] | pump_ride_on_curve | pump_ride_on_curve | [8 empty] | 2021-05-06
MA_LO_COOLSYS1 CHILLER1 PUMP Pump Power [hp] | COOLSYS1 CHILLER1 PUMP Pump Power [hp] | 3.4219 | 3.0847 | [8 empty] | 2021-05-06
MA_LO_COOLSYS1 CHILLER2 PUMP Pump Power [hp] | COOLSYS1 CHILLER2 PUMP Pump Power [hp] | 3.4219 | 3.0847 | [8 empty] | 2021-05-06
MA_LO_COOLSYS1 PUMP SECONDARY Pump Power [hp] | COOLSYS1 PUMP SECONDARY Pump Power [hp] | 20.5314 | 18.5085 | [8 empty] | 2021-05-06
MA_LO_HEATSYS1 PUMP Pump Power [hp] | HEATSYS1 PUMP Pump Power [hp] | 19.907 | 17.4926 | [8 empty] | 2021-05-06
MA_LO_TOWERWATERSYS PUMP Pump Power [hp] | TOWERWATERSYS PUMP Pump Power [hp] | 39.7673 | 35.8554 | [8 empty] | 2021-05-06
MA_LO_PLANT CIRC PUMP Pump Power [hp] | PLANT CIRC PUMP Pump Power [hp] | 4.4866 | 4.4243 | [8 empty] | 2021-05-06
MA_LO_Datacenter PLANT CIRC PUMP Pump Power [hp] | Datacenter PLANT CIRC PUMP Pump Power [hp] | 4.4866 | 4.4243 | [8 empty] | 2021-05-06
MA_LO_ZN_VAV_BOXes_Max_Reheat_Water_Flow_GPM | ZN_VAV_BOXes_Max_Reheat_Water_Flow_GPM | 484.0642 | 465.8484 | [8 empty] | 2021-05-06
MA_LO_COOLSYS1 PUMP SECONDARY VSD | COOLSYS1 PUMP SECONDARY VSD | No | No | [8 empty] | 2021-05-06
MA_LO_HEATSYS1 PUMP VSD | HEATSYS1 PUMP VSD | No | No | [8 empty] | 2021-05-06
MA_LO_DATACENTER BASEMENT Cooling Capacity [ton] | DATACENTER BASEMENT Cooling Capacity [ton] | 121.3878 | 121.0277 | [8 empty] | 2021-05-06
MA_LO_DATACENTER BOT Cooling Capacity [ton] | DATACENTER BOT Cooling Capacity [ton] | 2.6747 | 2.6512 | [8 empty] | 2021-05-06
MA_LO_DATACENTER MID Cooling Capacity [ton] | DATACENTER MID Cooling Capacity [ton] | 25.6322 | 25.4249 | [8 empty] | 2021-05-06
MA_LO_DATACENTER TOP Cooling Capacity [ton] | DATACENTER TOP Cooling Capacity [ton] | 2.609 | 2.5889 | [8 empty] | 2021-05-06
id | item | Zone5A(MA-BostonLogan-MA) ASHRAE901-state_STD2016 | Zone5A(MA-BostonLogan-MA) ASHRAE901-state_STD2019 | [8 empty] | 2021-05-06
MA_RS_PSZ-AC:1 Cooling Capacity [ton] | PSZ-AC:1 Cooling Capacity [ton] | 10.275 | 9.899 | [8 empty] | 2021-05-06
MA_RS_PSZ-AC:2 Cooling Capacity [ton] | PSZ-AC:2 Cooling Capacity [ton] | 47.6657 | 46.0406 | [8 empty] | 2021-05-06
MA_RS_PSZ-AC:3 Cooling Capacity [ton] | PSZ-AC:3 Cooling Capacity [ton] | 6.3408 | 6.1807 | [8 empty] | 2021-05-06
MA_RS_PSZ-AC:4 Cooling Capacity [ton] | PSZ-AC:4 Cooling Capacity [ton] | 5.1817 | 5.0206 | [8 empty] | 2021-05-06
MA_RS_PSZ-AC:1 Supply Flow Rate [cfm] | PSZ-AC:1 Supply Flow Rate [cfm] | 3941.1168 | 3686.8512 | [8 empty] | 2021-05-06
MA_RS_PSZ-AC:2 Supply Flow Rate [cfm] | PSZ-AC:2 Supply Flow Rate [cfm] | 15383.0688 | 14577.8944 | [8 empty] | 2021-05-06
MA_RS_PSZ-AC:3 Supply Flow Rate [cfm] | PSZ-AC:3 Supply Flow Rate [cfm] | 2309.5792 | 2246.0128 | [8 empty] | 2021-05-06
MA_RS_PSZ-AC:4 Supply Flow Rate [cfm] | PSZ-AC:4 Supply Flow Rate [cfm] | 1779.8592 | 1695.104 | [8 empty] | 2021-05-06
MA_RS_PSZ-AC:1 OA Rate [cfm] | PSZ-AC:1 OA Rate [cfm] | 490.669 | 490.669 | [8 empty] | 2021-05-06
MA_RS_PSZ-AC:2 OA Rate [cfm] | PSZ-AC:2 OA Rate [cfm] | 4005.1282 | 4005.1282 | [8 empty] | 2021-05-06
MA_RS_PSZ-AC:3 OA Rate [cfm] | PSZ-AC:3 OA Rate [cfm] | 377.3937 | 377.3937 | [8 empty] | 2021-05-06
MA_RS_PSZ-AC:4 OA Rate [cfm] | PSZ-AC:4 OA Rate [cfm] | 377.3937 | 377.3937 | [8 empty] | 2021-05-06
MA_RS_PSZ-AC:1 OA Damper [gravity, motorized] | PSZ-AC:1 OA Damper [gravity, motorized] | motorized | motorized | [8 empty] | 2021-05-06
MA_RS_PSZ-AC:2 OA Damper [gravity, motorized] | PSZ-AC:2 OA Damper [gravity, motorized] | motorized | motorized | [8 empty] | 2021-05-06
MA_RS_PSZ-AC:3 OA Damper [gravity, motorized] | PSZ-AC:3 OA Damper [gravity, motorized] | motorized | motorized | [8 empty] | 2021-05-06
MA_RS_PSZ-AC:4 OA Damper [gravity, motorized] | PSZ-AC:4 OA Damper [gravity, motorized] | motorized | motorized | [8 empty] | 2021-05-06
MA_RS_PSZ-AC:1 Heating Capacity [kBtu/hr] | PSZ-AC:1 Heating Capacity [kBtu/hr] | 178.2015 | 167.0861 | [8 empty] | 2021-05-06
MA_RS_PSZ-AC:2 Heating Capacity [kBtu/hr] | PSZ-AC:2 Heating Capacity [kBtu/hr] | 825.4183 | 791.2297 | [8 empty] | 2021-05-06
MA_RS_PSZ-AC:3 Heating Capacity [kBtu/hr] | PSZ-AC:3 Heating Capacity [kBtu/hr] | 111.0799 | 108.3457 | [8 empty] | 2021-05-06
MA_RS_PSZ-AC:4 Heating Capacity [kBtu/hr] | PSZ-AC:4 Heating Capacity [kBtu/hr] | 91.0906 | 88.086 | [8 empty] | 2021-05-06
id | item | Zone5A(MA-BostonLogan-MA) ASHRAE901-state_STD2016 | Zone5A(MA-BostonLogan-MA) ASHRAE901-state_STD2019 | [8 empty] | 2021-05-06
MA_PS_VAV_POD_1 Cooling Capacity [ton] | VAV_POD_1 Cooling Capacity [ton] | 18.8862 | 18.342 | [8 empty] | 2021-05-06
MA_PS_VAV_POD_2 Cooling Capacity [ton] | VAV_POD_2 Cooling Capacity [ton] | 18.6497 | 18.2905 | [8 empty] | 2021-05-06
MA_PS_VAV_POD_3 Cooling Capacity [ton] | VAV_POD_3 Cooling Capacity [ton] | 17.1512 | 16.3651 | [8 empty] | 2021-05-06
MA_PS_VAV_OTHER Cooling Capacity [ton] | VAV_OTHER Cooling Capacity [ton] | 25.982 | 24.4571 | [8 empty] | 2021-05-06
MA_PS_PSZ-AC_1:6 Cooling Capacity [ton] | PSZ-AC_1:6 Cooling Capacity [ton] | 8.1097 | 7.8468 | [8 empty] | 2021-05-06
MA_PS_PSZ-AC_2:5 Cooling Capacity [ton] | PSZ-AC_2:5 Cooling Capacity [ton] | 5.3578 | 5.3303 | [8 empty] | 2021-05-06
MA_PS_PSZ-AC_2:7 Cooling Capacity [ton] | PSZ-AC_2:7 Cooling Capacity [ton] | 10.5074 | 10.5074 | [8 empty] | 2021-05-06
MA_PS_VAV_POD_1 Supply Flow Rate [cfm] | VAV_POD_1 Supply Flow Rate [cfm] | 5657.4096 | 5509.088 | [8 empty] | 2021-05-06
MA_PS_VAV_POD_2 Supply Flow Rate [cfm] | VAV_POD_2 Supply Flow Rate [cfm] | 5593.8432 | 5487.8992 | [8 empty] | 2021-05-06
MA_PS_VAV_POD_3 Supply Flow Rate [cfm] | VAV_POD_3 Supply Flow Rate [cfm] | 5148.8784 | 4915.8016 | [8 empty] | 2021-05-06
MA_PS_VAV_OTHER Supply Flow Rate [cfm] | VAV_OTHER Supply Flow Rate [cfm] | 7797.4784 | 7331.3248 | [8 empty] | 2021-05-06
MA_PS_PSZ-AC_2:5 Supply Flow Rate [cfm] | PSZ-AC_2:5 Supply Flow Rate [cfm] | 1610.3488 | 1589.16 | [8 empty] | 2021-05-06
MA_PS_PSZ-AC_1:6 Supply Flow Rate [cfm] | PSZ-AC_1:6 Supply Flow Rate [cfm] | 2521.4672 | 2415.5232 | [8 empty] | 2021-05-06
MA_PS_PSZ-AC_2:7 Supply Flow Rate [cfm] | PSZ-AC_2:7 Supply Flow Rate [cfm] | 3157.1312 | 3157.1312 | [8 empty] | 2021-05-06
MA_PS_Supply Air Temp. Reset Flag | Supply Air Temp. Reset Flag | Yes | Yes | [8 empty] | 2021-05-06
MA_PS_VAV_POD_1 OA Rate [cfm] | VAV_POD_1 OA Rate [cfm] | 5666.2665 | 5504.1298 | [8 empty] | 2021-05-06
MA_PS_VAV_POD_2 OA Rate [cfm] | VAV_POD_2 OA Rate [cfm] | 5594.1822 | 5488.6832 | [8 empty] | 2021-05-06
MA_PS_VAV_POD_3 OA Rate [cfm] | VAV_POD_3 OA Rate [cfm] | 5145.3611 | 4910.8858 | [8 empty] | 2021-05-06
MA_PS_VAV_OTHER OA Rate [cfm] | VAV_OTHER OA Rate [cfm] | 3736.1787 | 2988.8921 | [8 empty] | 2021-05-06
MA_PS_PSZ-AC_2:5 OA Rate [cfm] | PSZ-AC_2:5 OA Rate [cfm] | 1152.7343 | 1152.7343 | [8 empty] | 2021-05-06
MA_PS_PSZ-AC_1:6 OA Rate [cfm] | PSZ-AC_1:6 OA Rate [cfm] | 539.9118 | 539.9118 | [8 empty] | 2021-05-06
MA_PS_PSZ-AC_2:7 OA Rate [cfm] | PSZ-AC_2:7 OA Rate [cfm] | 3153.0841 | 3153.0841 | [8 empty] | 2021-05-06
MA_PS_VAV_POD_1 OA Damper [gravity, motorized] | VAV_POD_1 OA Damper [gravity, motorized] | motorized | motorized | [8 empty] | 2021-05-06
MA_PS_VAV_POD_2 OA Damper [gravity, motorized] | VAV_POD_2 OA Damper [gravity, motorized] | motorized | motorized | [8 empty] | 2021-05-06
MA_PS_VAV_POD_3 OA Damper [gravity, motorized] | VAV_POD_3 OA Damper [gravity, motorized] | motorized | motorized | [8 empty] | 2021-05-06
MA_PS_VAV_OTHER OA Damper [gravity, motorized] | VAV_OTHER OA Damper [gravity, motorized] | motorized | motorized | [8 empty] | 2021-05-06
MA_PS_PSZ-AC_2:5 OA Damper [gravity, motorized] | PSZ-AC_2:5 OA Damper [gravity, motorized] | motorized | motorized | [8 empty] | 2021-05-06
MA_PS_PSZ-AC_1:6 OA Damper [gravity, motorized] | PSZ-AC_1:6 OA Damper [gravity, motorized] | motorized | motorized | [8 empty] | 2021-05-06
MA_PS_PSZ-AC_2:7 OA Damper [gravity, motorized] | PSZ-AC_2:7 OA Damper [gravity, motorized] | motorized | motorized | [8 empty] | 2021-05-06
MA_PS_VAV_POD_1 (economizer) | VAV_POD_1 (economizer) | DifferentialDryBulb | DifferentialDryBulb | [8 empty] | 2021-05-06
MA_PS_VAV_POD_2 (economizer) | VAV_POD_2 (economizer) | DifferentialDryBulb | DifferentialDryBulb | [8 empty] | 2021-05-06
MA_PS_VAV_POD_3 (economizer) | VAV_POD_3 (economizer) | DifferentialDryBulb | DifferentialDryBulb | [8 empty] | 2021-05-06
MA_PS_VAV_OTHER (economizer) | VAV_OTHER (economizer) | DifferentialDryBulb | DifferentialDryBulb | [8 empty] | 2021-05-06
MA_PS_PSZ-AC_2:5 (economizer) | PSZ-AC_2:5 (economizer) | DifferentialDryBulb | DifferentialDryBulb | [8 empty] | 2021-05-06
MA_PS_PSZ-AC_1:6 (economizer) | PSZ-AC_1:6 (economizer) | DifferentialDryBulb | DifferentialDryBulb | [8 empty] | 2021-05-06
MA_PS_PSZ-AC_2:7 (economizer) | PSZ-AC_2:7 (economizer) | DifferentialDryBulb | DifferentialDryBulb | [8 empty] | 2021-05-06
MA_PS_VAV_Pod_1_ERV Flag | VAV_Pod_1_ERV Flag | Yes | Yes | [8 empty] | 2021-05-06
MA_PS_VAV_Pod_2_ERV Flag | VAV_Pod_2_ERV Flag | Yes | Yes | [8 empty] | 2021-05-06
MA_PS_VAV_Pod_3_ERV Flag | VAV_Pod_3_ERV Flag | Yes | Yes | [8 empty] | 2021-05-06
MA_PS_VAV_OTHER_ERV Flag | VAV_OTHER_ERV Flag | Yes | Yes | [8 empty] | 2021-05-06
MA_PS_PSZ_AC_2_5_ERV Flag | PSZ_AC_2_5_ERV Flag | Yes | Yes | [8 empty] | 2021-05-06
MA_PS_PSZ_AC_2_7_ERV Flag | PSZ_AC_2_7_ERV Flag | Yes | Yes | [8 empty] | 2021-05-06
MA_PS_HEATSYS1 Capacity [MMBTU/h] | HEATSYS1 Capacity [MMBTU/h] | 1.0932 | 1.0512 | [8 empty] | 2021-05-06
MA_PS_HEATSYS1 Flow Rate [gal/min] | HEATSYS1 Flow Rate [gal/min] | 112.2 | 107.889 | [8 empty] | 2021-05-06
MA_PS_VAV_POD_1 Fan Power [hp] | VAV_POD_1 Fan Power [hp] | 8.3612 | 8.1203 | [8 empty] | 2021-05-06
MA_PS_VAV_POD_2 Fan Power [hp] | VAV_POD_2 Fan Power [hp] | 8.2565 | 8.0975 | [8 empty] | 2021-05-06
MA_PS_VAV_POD_3 Fan Power [hp] | VAV_POD_3 Fan Power [hp] | 7.5931 | 7.245 | [8 empty] | 2021-05-06
MA_PS_VAV_OTHER Fan Power [hp] | VAV_OTHER Fan Power [hp] | 11.4154 | 10.7455 | [8 empty] | 2021-05-06
MA_PS_HEATSYS1 Pump Power [hp] | HEATSYS1 Pump Power [hp] | 2.4253 | 2.309 | [8 empty] | 2021-05-06
MA_PS_PSZ-AC_1:6 Heating Capacity [kBtu/hr] | PSZ-AC_1:6 Heating Capacity [kBtu/hr] | 211.3305 | 202.731 | [8 empty] | 2021-05-06
MA_PS_PSZ-AC_2:5 Heating Capacity [kBtu/hr] | PSZ-AC_2:5 Heating Capacity [kBtu/hr] | 137.1613 | 136.8562 | [8 empty] | 2021-05-06
MA_PS_PSZ-AC_2:7 Heating Capacity [kBtu/hr] | PSZ-AC_2:7 Heating Capacity [kBtu/hr] | 329.1211 | 329.1211 | [8 empty] | 2021-05-06
MA_PS_ZN_VAV_BOXes_Max_Reheat_Water_Flow_GPM | ZN_VAV_BOXes_Max_Reheat_Water_Flow_GPM | 73.8813 | 71.0972 | [8 empty] | 2021-05-06
id | item | Zone5A(MA-BostonLogan-MA) ASHRAE901-state_STD2016 | Zone5A(MA-BostonLogan-MA) ASHRAE901-state_STD2019 | [8 empty] | 2021-05-06
MA_SH_SAC_FRONTOFFICE Cooling Capacity [ton] | SAC_FRONTOFFICE Cooling Capacity [ton] | 2.2732 | 2.153 | [8 empty] | 2021-05-06
MA_SH_SAC_FRONTLOUNGE Cooling Capacity [ton] | SAC_FRONTLOUNGE Cooling Capacity [ton] | 6.0296 | 5.7279 | [8 empty] | 2021-05-06
MA_SH_SAC_MEETINGROOM Cooling Capacity [ton] | SAC_MEETINGROOM Cooling Capacity [ton] | 2.8586 | 2.7745 | [8 empty] | 2021-05-06
MA_SH_SAC_EXC_EMPLGE_RESTRM Cooling Capacity [ton] | SAC_EXC_EMPLGE_RESTRM Cooling Capacity [ton] | 5.8283 | 5.7875 | [8 empty] | 2021-05-06
MA_SH_SAC_FO_ADDAQ SUPPLY FAN Supply Flow Rate [cfm] | SAC_FO_ADDAQ SUPPLY FAN Supply Flow Rate [cfm] | 762.7968 | 720.4192 | [8 empty] | 2021-05-06
MA_SH_SAC_FL_ADDAQ SUPPLY FAN Supply Flow Rate [cfm] | SAC_FL_ADDAQ SUPPLY FAN Supply Flow Rate [cfm] | 1801.048 | 1716.2928 | [8 empty] | 2021-05-06
MA_SH_SAC_MR_ADDAQ SUPPLY FAN Supply Flow Rate [cfm] | SAC_MR_ADDAQ SUPPLY FAN Supply Flow Rate [cfm] | 847.552 | 826.3632 | [8 empty] | 2021-05-06
MA_SH_SAC_EXC_ADDAQ SUPPLY FAN Supply Flow Rate [cfm] | SAC_EXC_ADDAQ SUPPLY FAN Supply Flow Rate [cfm] | 2161.2576 | 2140.0688 | [8 empty] | 2021-05-06
MA_SH_SAC_Exc_EmpLge_RestRm OA Rate [cfm] | SAC_Exc_EmpLge_RestRm OA Rate [cfm] | 199.9928 | 199.9928 | [8 empty] | 2021-05-06
MA_SH_SAC_FrontLounge OA Rate [cfm] | SAC_FrontLounge OA Rate [cfm] | 500.0133 | 500.0133 | [8 empty] | 2021-05-06
MA_SH_SAC_FrontOffice OA Rate [cfm] | SAC_FrontOffice OA Rate [cfm] | 119.2938 | 119.2938 | [8 empty] | 2021-05-06
MA_SH_SAC_MeetingRoom OA Rate [cfm] | SAC_MeetingRoom OA Rate [cfm] | 267.7629 | 267.7629 | [8 empty] | 2021-05-06
MA_SH_SAC_FrontLounge OA Damper [gravity, motorized] | SAC_FrontLounge OA Damper [gravity, motorized] | motorized | motorized | [8 empty] | 2021-05-06
MA_SH_SAC_FrontOffice (economizer) | SAC_FrontOffice (economizer) | No | No | [8 empty] | 2021-05-06
MA_SH_SAC_FrontLounge (economizer) | SAC_FrontLounge (economizer) | DifferentialDryBulb | DifferentialDryBulb | [8 empty] | 2021-05-06
MA_SH_SAC_MeetingRoom (economizer) | SAC_MeetingRoom (economizer) | No | No | [8 empty] | 2021-05-06
MA_SH_SAC_Exc_EmpLge_RestRm (economizer) | SAC_Exc_EmpLge_RestRm (economizer) | DifferentialDryBulb | DifferentialDryBulb | [8 empty] | 2021-05-06
MA_SH_SAC_FRONTOFFICE Heating Capacity [kBtu/hr] | SAC_FRONTOFFICE Heating Capacity [kBtu/hr] | 36.3278 | 34.5342 | [8 empty] | 2021-05-06
MA_SH_SAC_FRONTLOUNGE Heating Capacity [kBtu/hr] | SAC_FRONTLOUNGE Heating Capacity [kBtu/hr] | 100.3566 | 97.0257 | [8 empty] | 2021-05-06
MA_SH_SAC_MEETINGROOM Heating Capacity [kBtu/hr] | SAC_MEETINGROOM Heating Capacity [kBtu/hr] | 49.6537 | 48.7257 | [8 empty] | 2021-05-06
MA_SH_SAC_EXC_EMPLGE_RESTRM Heating Capacity [kBtu/hr] | SAC_EXC_EMPLGE_RESTRM Heating Capacity [kBtu/hr] | 92.7961 | 92.137 | [8 empty] | 2021-05-06
id | item | Zone5A(MA-BostonLogan-MA) ASHRAE901-state_STD2016 | Zone5A(MA-BostonLogan-MA) ASHRAE901-state_STD2019 | [8 empty] | 2021-05-06
MA_MA_SPLIT GSW COOLING COIL Cooling Capacity [ton] | SPLIT GSW COOLING COIL Cooling Capacity [ton] | 0.83782 | 0.82374 | [8 empty] | 2021-05-06
MA_MA_SPLIT GNW COOLING COIL Cooling Capacity [ton] | SPLIT GNW COOLING COIL Cooling Capacity [ton] | 0.79537 | 0.78203 | [8 empty] | 2021-05-06
MA_MA_SPLIT OFFICE COOLING COIL Cooling Capacity [ton] | SPLIT OFFICE COOLING COIL Cooling Capacity [ton] | 1.648 | 1.5176 | [8 empty] | 2021-05-06
MA_MA_SPLIT GNE COOLING COIL Cooling Capacity [ton] | SPLIT GNE COOLING COIL Cooling Capacity [ton] | 0.69298 | 0.68139 | [8 empty] | 2021-05-06
MA_MA_SPLIT GN1 COOLING COIL Cooling Capacity [ton] | SPLIT GN1 COOLING COIL Cooling Capacity [ton] | 0.59047 | 0.5812 | [8 empty] | 2021-05-06
MA_MA_SPLIT GN2 COOLING COIL Cooling Capacity [ton] | SPLIT GN2 COOLING COIL Cooling Capacity [ton] | 0.58842 | 0.5792 | [8 empty] | 2021-05-06
MA_MA_SPLIT GS1 COOLING COIL Cooling Capacity [ton] | SPLIT GS1 COOLING COIL Cooling Capacity [ton] | 0.6335 | 0.62326 | [8 empty] | 2021-05-06
MA_MA_SPLIT GS2 COOLING COIL Cooling Capacity [ton] | SPLIT GS2 COOLING COIL Cooling Capacity [ton] | 0.66503 | 0.65031 | [8 empty] | 2021-05-06
MA_MA_SPLIT MSW COOLING COIL Cooling Capacity [ton] | SPLIT MSW COOLING COIL Cooling Capacity [ton] | 2.0627 | 2.0275 | [8 empty] | 2021-05-06
MA_MA_SPLIT MNW COOLING COIL Cooling Capacity [ton] | SPLIT MNW COOLING COIL Cooling Capacity [ton] | 1.9804 | 1.9503 | [8 empty] | 2021-05-06
MA_MA_SPLIT MSE COOLING COIL Cooling Capacity [ton] | SPLIT MSE COOLING COIL Cooling Capacity [ton] | 1.8081 | 1.7796 | [8 empty] | 2021-05-06
MA_MA_SPLIT MNE COOLING COIL Cooling Capacity [ton] | SPLIT MNE COOLING COIL Cooling Capacity [ton] | 1.6435 | 1.6146 | [8 empty] | 2021-05-06
MA_MA_SPLIT MN1 COOLING COIL Cooling Capacity [ton] | SPLIT MN1 COOLING COIL Cooling Capacity [ton] | 1.339 | 1.3211 | [8 empty] | 2021-05-06
MA_MA_SPLIT MN2 COOLING COIL Cooling Capacity [ton] | SPLIT MN2 COOLING COIL Cooling Capacity [ton] | 1.3331 | 1.3154 | [8 empty] | 2021-05-06
MA_MA_SPLIT MS1 COOLING COIL Cooling Capacity [ton] | SPLIT MS1 COOLING COIL Cooling Capacity [ton] | 1.4128 | 1.3937 | [8 empty] | 2021-05-06
MA_MA_SPLIT MS2 COOLING COIL Cooling Capacity [ton] | SPLIT MS2 COOLING COIL Cooling Capacity [ton] | 1.4068 | 1.3878 | [8 empty] | 2021-05-06
MA_MA_SPLIT TSW COOLING COIL Cooling Capacity [ton] | SPLIT TSW COOLING COIL Cooling Capacity [ton] | 1.2834 | 1.2662 | [8 empty] | 2021-05-06
MA_MA_SPLIT TNW COOLING COIL Cooling Capacity [ton] | SPLIT TNW COOLING COIL Cooling Capacity [ton] | 1.2285 | 1.2122 | [8 empty] | 2021-05-06
MA_MA_SPLIT TSE COOLING COIL Cooling Capacity [ton] | SPLIT TSE COOLING COIL Cooling Capacity [ton] | 1.1537 | 1.1388 | [8 empty] | 2021-05-06
MA_MA_SPLIT TNE COOLING COIL Cooling Capacity [ton] | SPLIT TNE COOLING COIL Cooling Capacity [ton] | 1.063 | 1.0505 | [8 empty] | 2021-05-06
MA_MA_SPLIT TN1 COOLING COIL Cooling Capacity [ton] | SPLIT TN1 COOLING COIL Cooling Capacity [ton] | 0.86058 | 0.85087 | [8 empty] | 2021-05-06
MA_MA_SPLIT TN2 COOLING COIL Cooling Capacity [ton] | SPLIT TN2 COOLING COIL Cooling Capacity [ton] | 0.86207 | 0.85235 | [8 empty] | 2021-05-06
MA_MA_SPLIT TS1 COOLING COIL Cooling Capacity [ton] | SPLIT TS1 COOLING COIL Cooling Capacity [ton] | 0.9446 | 0.93388 | [8 empty] | 2021-05-06
MA_MA_SPLIT TS2 COOLING COIL Cooling Capacity [ton] | SPLIT TS2 COOLING COIL Cooling Capacity [ton] | 0.94759 | 0.93582 | [8 empty] | 2021-05-06
MA_MA_Split GN1 Furnace with DX Cooling OA Rate [cfm] | Split GN1 Furnace with DX Cooling OA Rate [cfm] | 54.9913 | 54.9913 | [8 empty] | 2021-05-06
MA_MA_Split GN2 Furnace with DX Cooling OA Rate [cfm] | Split GN2 Furnace with DX Cooling OA Rate [cfm] | 54.9913 | 54.9913 | [8 empty] | 2021-05-06
MA_MA_Split GNE Furnace with DX Cooling OA Rate [cfm] | Split GNE Furnace with DX Cooling OA Rate [cfm] | 54.9913 | 54.9913 | [8 empty] | 2021-05-06
MA_MA_Split GNW Furnace with DX Cooling OA Rate [cfm] | Split GNW Furnace with DX Cooling OA Rate [cfm] | 54.9913 | 54.9913 | [8 empty] | 2021-05-06
MA_MA_Split GS1 Furnace with DX Cooling OA Rate [cfm] | Split GS1 Furnace with DX Cooling OA Rate [cfm] | 54.9913 | 54.9913 | [8 empty] | 2021-05-06
MA_MA_Split GS2 Furnace with DX Cooling OA Rate [cfm] | Split GS2 Furnace with DX Cooling OA Rate [cfm] | 54.9913 | 54.9913 | [8 empty] | 2021-05-06
MA_MA_Split GSW Furnace with DX Cooling OA Rate [cfm] | Split GSW Furnace with DX Cooling OA Rate [cfm] | 56.9945 | 56.9945 | [8 empty] | 2021-05-06
MA_MA_Split MN1 Furnace with DX Cooling OA Rate [cfm] | Split MN1 Furnace with DX Cooling OA Rate [cfm] | 109.9824 | 109.9824 | [8 empty] | 2021-05-06
MA_MA_Split MN2 Furnace with DX Cooling OA Rate [cfm] | Split MN2 Furnace with DX Cooling OA Rate [cfm] | 109.9824 | 109.9824 | [8 empty] | 2021-05-06
MA_MA_Split MNE Furnace with DX Cooling OA Rate [cfm] | Split MNE Furnace with DX Cooling OA Rate [cfm] | 109.9824 | 109.9824 | [8 empty] | 2021-05-06
MA_MA_Split MNW Furnace with DX Cooling OA Rate [cfm] | Split MNW Furnace with DX Cooling OA Rate [cfm] | 109.9824 | 109.9824 | [8 empty] | 2021-05-06
MA_MA_Split MS1 Furnace with DX Cooling OA Rate [cfm] | Split MS1 Furnace with DX Cooling OA Rate [cfm] | 109.9824 | 109.9824 | [8 empty] | 2021-05-06
MA_MA_Split MS2 Furnace with DX Cooling OA Rate [cfm] | Split MS2 Furnace with DX Cooling OA Rate [cfm] | 109.9824 | 109.9824 | [8 empty] | 2021-05-06
MA_MA_Split MSE Furnace with DX Cooling OA Rate [cfm] | Split MSE Furnace with DX Cooling OA Rate [cfm] | 109.9824 | 109.9824 | [8 empty] | 2021-05-06
MA_MA_Split MSW Furnace with DX Cooling OA Rate [cfm] | Split MSW Furnace with DX Cooling OA Rate [cfm] | 109.9824 | 109.9824 | [8 empty] | 2021-05-06
MA_MA_Split Office Furnace with DX Cooling OA Rate [cfm] | Split Office Furnace with DX Cooling OA Rate [cfm] | 80.7372 | 80.7372 | [8 empty] | 2021-05-06
MA_MA_Split TN1 Furnace with DX Cooling OA Rate [cfm] | Split TN1 Furnace with DX Cooling OA Rate [cfm] | 54.9913 | 54.9913 | [8 empty] | 2021-05-06
MA_MA_Split TN2 Furnace with DX Cooling OA Rate [cfm] | Split TN2 Furnace with DX Cooling OA Rate [cfm] | 54.9913 | 54.9913 | [8 empty] | 2021-05-06
MA_MA_Split TNE Furnace with DX Cooling OA Rate [cfm] | Split TNE Furnace with DX Cooling OA Rate [cfm] | 54.9913 | 54.9913 | [8 empty] | 2021-05-06
MA_MA_Split TNW Furnace with DX Cooling OA Rate [cfm] | Split TNW Furnace with DX Cooling OA Rate [cfm] | 54.9913 | 54.9913 | [8 empty] | 2021-05-06
MA_MA_Split TS1 Furnace with DX Cooling OA Rate [cfm] | Split TS1 Furnace with DX Cooling OA Rate [cfm] | 54.9913 | 54.9913 | [8 empty] | 2021-05-06
MA_MA_Split TS2 Furnace with DX Cooling OA Rate [cfm] | Split TS2 Furnace with DX Cooling OA Rate [cfm] | 54.9913 | 54.9913 | [8 empty] | 2021-05-06
MA_MA_Split TSE Furnace with DX Cooling OA Rate [cfm] | Split TSE Furnace with DX Cooling OA Rate [cfm] | 54.9913 | 54.9913 | [8 empty] | 2021-05-06
MA_MA_Split TSW Furnace with DX Cooling OA Rate [cfm] | Split TSW Furnace with DX Cooling OA Rate [cfm] | 54.9913 | 54.9913 | [8 empty] | 2021-05-06
MA_MA_SPLIT GSW HEATING COIL Heating Capacity [kBtu/hr] | SPLIT GSW HEATING COIL Heating Capacity [kBtu/hr] | 10.346 | 10.4046 | [8 empty] | 2021-05-06
MA_MA_SPLIT GNW HEATING COIL Heating Capacity [kBtu/hr] | SPLIT GNW HEATING COIL Heating Capacity [kBtu/hr] | 10.2829 | 10.3415 | [8 empty] | 2021-05-06
MA_MA_SPLIT OFFICE HEATING COIL Heating Capacity [kBtu/hr] | SPLIT OFFICE HEATING COIL Heating Capacity [kBtu/hr] | 23.0381 | 23.1168 | [8 empty] | 2021-05-06
MA_MA_SPLIT GNE HEATING COIL Heating Capacity [kBtu/hr] | SPLIT GNE HEATING COIL Heating Capacity [kBtu/hr] | 10.2576 | 10.3163 | [8 empty] | 2021-05-06
MA_MA_SPLIT GN1 HEATING COIL Heating Capacity [kBtu/hr] | SPLIT GN1 HEATING COIL Heating Capacity [kBtu/hr] | 7.4172 | 7.4759 | [8 empty] | 2021-05-06
MA_MA_SPLIT GN2 HEATING COIL Heating Capacity [kBtu/hr] | SPLIT GN2 HEATING COIL Heating Capacity [kBtu/hr] | 7.4165 | 7.4751 | [8 empty] | 2021-05-06
MA_MA_SPLIT GS1 HEATING COIL Heating Capacity [kBtu/hr] | SPLIT GS1 HEATING COIL Heating Capacity [kBtu/hr] | 7.3614 | 7.4199 | [8 empty] | 2021-05-06
MA_MA_SPLIT GS2 HEATING COIL Heating Capacity [kBtu/hr] | SPLIT GS2 HEATING COIL Heating Capacity [kBtu/hr] | 7.8648 | 7.9241 | [8 empty] | 2021-05-06
MA_MA_SPLIT MSW HEATING COIL Heating Capacity [kBtu/hr] | SPLIT MSW HEATING COIL Heating Capacity [kBtu/hr] | 19.6887 | 19.8182 | [8 empty] | 2021-05-06
MA_MA_SPLIT MNW HEATING COIL Heating Capacity [kBtu/hr] | SPLIT MNW HEATING COIL Heating Capacity [kBtu/hr] | 19.7885 | 19.9179 | [8 empty] | 2021-05-06
MA_MA_SPLIT MSE HEATING COIL Heating Capacity [kBtu/hr] | SPLIT MSE HEATING COIL Heating Capacity [kBtu/hr] | 19.6299 | 19.7595 | [8 empty] | 2021-05-06
MA_MA_SPLIT MNE HEATING COIL Heating Capacity [kBtu/hr] | SPLIT MNE HEATING COIL Heating Capacity [kBtu/hr] | 19.7297 | 19.8591 | [8 empty] | 2021-05-06
MA_MA_SPLIT MN1 HEATING COIL Heating Capacity [kBtu/hr] | SPLIT MN1 HEATING COIL Heating Capacity [kBtu/hr] | 13.4179 | 13.5423 | [8 empty] | 2021-05-06
MA_MA_SPLIT MN2 HEATING COIL Heating Capacity [kBtu/hr] | SPLIT MN2 HEATING COIL Heating Capacity [kBtu/hr] | 13.4163 | 13.5407 | [8 empty] | 2021-05-06
MA_MA_SPLIT MS1 HEATING COIL Heating Capacity [kBtu/hr] | SPLIT MS1 HEATING COIL Heating Capacity [kBtu/hr] | 13.327 | 13.4513 | [8 empty] | 2021-05-06
MA_MA_SPLIT MS2 HEATING COIL Heating Capacity [kBtu/hr] | SPLIT MS2 HEATING COIL Heating Capacity [kBtu/hr] | 13.3255 | 13.4498 | [8 empty] | 2021-05-06
MA_MA_SPLIT TSW HEATING COIL Heating Capacity [kBtu/hr] | SPLIT TSW HEATING COIL Heating Capacity [kBtu/hr] | 13.7745 | 13.8362 | [8 empty] | 2021-05-06
MA_MA_SPLIT TNW HEATING COIL Heating Capacity [kBtu/hr] | SPLIT TNW HEATING COIL Heating Capacity [kBtu/hr] | 13.8328 | 13.8945 | [8 empty] | 2021-05-06
MA_MA_SPLIT TSE HEATING COIL Heating Capacity [kBtu/hr] | SPLIT TSE HEATING COIL Heating Capacity [kBtu/hr] | 13.7439 | 13.8055 | [8 empty] | 2021-05-06
MA_MA_SPLIT TNE HEATING COIL Heating Capacity [kBtu/hr] | SPLIT TNE HEATING COIL Heating Capacity [kBtu/hr] | 13.8021 | 13.8638 | [8 empty] | 2021-05-06
MA_MA_SPLIT TN1 HEATING COIL Heating Capacity [kBtu/hr] | SPLIT TN1 HEATING COIL Heating Capacity [kBtu/hr] | 10.2254 | 10.2869 | [8 empty] | 2021-05-06
MA_MA_SPLIT TN2 HEATING COIL Heating Capacity [kBtu/hr] | SPLIT TN2 HEATING COIL Heating Capacity [kBtu/hr] | 10.2246 | 10.286 | [8 empty] | 2021-05-06
MA_MA_SPLIT TS1 HEATING COIL Heating Capacity [kBtu/hr] | SPLIT TS1 HEATING COIL Heating Capacity [kBtu/hr] | 10.1602 | 10.2215 | [8 empty] | 2021-05-06
MA_MA_SPLIT TS2 HEATING COIL Heating Capacity [kBtu/hr] | SPLIT TS2 HEATING COIL Heating Capacity [kBtu/hr] | 10.1593 | 10.2207 | [8 empty] | 2021-05-06
MA_MA_Split_GSW ERV Flag | Split_GSW ERV Flag | Yes | Yes | [8 empty] | 2021-05-06
MA_MA_Split_GNW ERV Flag | Split_GNW ERV Flag | Yes | Yes | [8 empty] | 2021-05-06
MA_MA_Split_GNE ERV Flag | Split_GNE ERV Flag | Yes | Yes | [8 empty] | 2021-05-06
MA_MA_Split_GN1 ERV Flag | Split_GN1 ERV Flag | Yes | Yes | [8 empty] | 2021-05-06
MA_MA_Split_GN2 ERV Flag | Split_GN2 ERV Flag | Yes | Yes | [8 empty] | 2021-05-06
MA_MA_Split_GS1 ERV Flag | Split_GS1 ERV Flag | Yes | Yes | [8 empty] | 2021-05-06
MA_MA_Split_GS2 ERV Flag | Split_GS2 ERV Flag | Yes | Yes | [8 empty] | 2021-05-06
MA_MA_Split_MSW ERV Flag | Split_MSW ERV Flag | Yes | Yes | [8 empty] | 2021-05-06
MA_MA_Split_MNW ERV Flag | Split_MNW ERV Flag | Yes | Yes | [8 empty] | 2021-05-06
MA_MA_Split_MSE ERV Flag | Split_MSE ERV Flag | Yes | Yes | [8 empty] | 2021-05-06
MA_MA_Split_MNE ERV Flag | Split_MNE ERV Flag | Yes | Yes | [8 empty] | 2021-05-06
MA_MA_Split_MN1 ERV Flag | Split_MN1 ERV Flag | Yes | Yes | [8 empty] | 2021-05-06
MA_MA_Split_MN2 ERV Flag | Split_MN2 ERV Flag | Yes | Yes | [8 empty] | 2021-05-06
MA_MA_Split_MS1 ERV Flag | Split_MS1 ERV Flag | Yes | Yes | [8 empty] | 2021-05-06
MA_MA_Split_MS2 ERV Flag | Split_MS2 ERV Flag | Yes | Yes | [8 empty] | 2021-05-06
MA_MA_Split_TSW ERV Flag | Split_TSW ERV Flag | Yes | Yes | [8 empty] | 2021-05-06
MA_MA_Split_TNW ERV Flag | Split_TNW ERV Flag | Yes | Yes | [8 empty] | 2021-05-06
MA_MA_Split_TSE ERV Flag | Split_TSE ERV Flag | Yes | Yes | [8 empty] | 2021-05-06
MA_MA_Split_TNE ERV Flag | Split_TNE ERV Flag | Yes | Yes | [8 empty] | 2021-05-06
MA_MA_Split_TN1 ERV Flag | Split_TN1 ERV Flag | Yes | Yes | [8 empty] | 2021-05-06
MA_MA_Split_TN2 ERV Flag | Split_TN2 ERV Flag | Yes | Yes | [8 empty] | 2021-05-06
MA_MA_Split_TS1 ERV Flag | Split_TS1 ERV Flag | Yes | Yes | [8 empty] | 2021-05-06
MA_MA_Split_TS2 ERV Flag | Split_TS2 ERV Flag | Yes | Yes | [8 empty] | 2021-05-06
id | item | Zone4A(MD-Baltimore-MD) ASHRAE901-state_STD2016 | Zone4A(MD-Baltimore-MD) ASHRAE901-state_STD2019 | Zone5A(MD-Pittsburgh-PA) ASHRAE901-state_STD2016 | Zone5A(MD-Pittsburgh-PA) ASHRAE901-state_STD2019 | [6 empty] | 2021-05-06
MD_SO_PSZ-AC:1 Cooling Capacity [ton] | PSZ-AC:1 Cooling Capacity [ton] | 1.9002 | 1.8024 | 1.7871 | 1.6908 | [6 empty] | 2021-05-06
MD_SO_PSZ-AC:2 Cooling Capacity [ton] | PSZ-AC:2 Cooling Capacity [ton] | 1.6912 | 1.625 | 1.5246 | 1.463 | [6 empty] | 2021-05-06
MD_SO_PSZ-AC:3 Cooling Capacity [ton] | PSZ-AC:3 Cooling Capacity [ton] | 1.1296 | 1.091 | 1.0865 | 1.0481 | [6 empty] | 2021-05-06
MD_SO_PSZ-AC:4 Cooling Capacity [ton] | PSZ-AC:4 Cooling Capacity [ton] | 1.6237 | 1.5542 | 1.4683 | 1.3872 | [6 empty] | 2021-05-06
MD_SO_PSZ-AC:5 Cooling Capacity [ton] | PSZ-AC:5 Cooling Capacity [ton] | 1.3376 | 1.2979 | 1.2735 | 1.2342 | [6 empty] | 2021-05-06
MD_SO_PSZ-AC:1 Supply Flow Rate [cfm] | PSZ-AC:1 Supply Flow Rate [cfm] | 656.8528 | 614.4752 | 656.8528 | 614.4752 | [6 empty] | 2021-05-06
MD_SO_PSZ-AC:2 Supply Flow Rate [cfm] | PSZ-AC:2 Supply Flow Rate [cfm] | 593.2864 | 572.0976 | 572.0976 | 550.9088 | [6 empty] | 2021-05-06
MD_SO_PSZ-AC:3 Supply Flow Rate [cfm] | PSZ-AC:3 Supply Flow Rate [cfm] | 444.9648 | 423.776 | 466.1536 | 444.9648 | [6 empty] | 2021-05-06
MD_SO_PSZ-AC:4 Supply Flow Rate [cfm] | PSZ-AC:4 Supply Flow Rate [cfm] | 572.0976 | 529.72 | 550.9088 | 508.5312 | [6 empty] | 2021-05-06
MD_SO_PSZ-AC:5 Supply Flow Rate [cfm] | PSZ-AC:5 Supply Flow Rate [cfm] | 529.72 | 508.5312 | 550.9088 | 529.72 | [6 empty] | 2021-05-06
MD_SO_PSZ-AC:1 OA Rate [cfm] | PSZ-AC:1 OA Rate [cfm] | 136.9178 | 136.9178 | 136.9178 | 136.9178 | [6 empty] | 2021-05-06
MD_SO_PSZ-AC:2 OA Rate [cfm] | PSZ-AC:2 OA Rate [cfm] | 103.7925 | 103.7925 | 103.7925 | 103.7925 | [6 empty] | 2021-05-06
MD_SO_PSZ-AC:3 OA Rate [cfm] | PSZ-AC:3 OA Rate [cfm] | 61.5711 | 61.5711 | 61.5711 | 61.5711 | [6 empty] | 2021-05-06
MD_SO_PSZ-AC:4 OA Rate [cfm] | PSZ-AC:4 OA Rate [cfm] | 103.7925 | 103.7925 | 103.7925 | 103.7925 | [6 empty] | 2021-05-06
MD_SO_PSZ-AC:5 OA Rate [cfm] | PSZ-AC:5 OA Rate [cfm] | 61.5711 | 61.5711 | 61.5711 | 61.5711 | [6 empty] | 2021-05-06
MD_SO_PSZ-AC:1 heating Capacity [kBtu/hr] | PSZ-AC:1 heating Capacity [kBtu/hr] | 13.4294 | 13.4294 | 14.2556 | 14.2556 | [6 empty] | 2021-05-06
MD_SO_PSZ-AC:2 heating Capacity [kBtu/hr] | PSZ-AC:2 heating Capacity [kBtu/hr] | 17.7984 | 17.6098 | 19.7423 | 19.5151 | [6 empty] | 2021-05-06
MD_SO_PSZ-AC:3 heating Capacity [kBtu/hr] | PSZ-AC:3 heating Capacity [kBtu/hr] | 10.8894 | 10.7851 | 11.9643 | 11.844 | [6 empty] | 2021-05-06
MD_SO_PSZ-AC:4 heating Capacity [kBtu/hr] | PSZ-AC:4 heating Capacity [kBtu/hr] | 17.7032 | 17.5421 | 19.4546 | 19.2767 | [6 empty] | 2021-05-06
MD_SO_PSZ-AC:5 heating Capacity [kBtu/hr] | PSZ-AC:5 heating Capacity [kBtu/hr] | 10.9318 | 10.8228 | 12.0169 | 11.8913 | [6 empty] | 2021-05-06
id | item | Zone4A(MD-Baltimore-MD) ASHRAE901-state_STD2016 | Zone4A(MD-Baltimore-MD) ASHRAE901-state_STD2019 | Zone5A(MD-Pittsburgh-PA) ASHRAE901-state_STD2016 | Zone5A(MD-Pittsburgh-PA) ASHRAE901-state_STD2019 | [6 empty] | 2021-05-06
MD_LO_CAV_BAS Supply Flow Rate [cfm] | CAV_BAS Supply Flow Rate [cfm] | 11717.4064 | 10848.6656 | 12056.4272 | 11166.4976 | [6 empty] | 2021-05-06
MD_LO_VAV_BOT WITH REHEAT Supply Flow Rate [cfm] | VAV_BOT WITH REHEAT Supply Flow Rate [cfm] | 19620.8288 | 18688.5216 | 20150.5488 | 19175.864 | [6 empty] | 2021-05-06
MD_LO_VAV_MID WITH REHEAT Supply Flow Rate [cfm] | VAV_MID WITH REHEAT Supply Flow Rate [cfm] | 182605.0787 | 173684.5939 | 186779.2723 | 177583.3331 | [6 empty] | 2021-05-06
MD_LO_VAV_TOP WITH REHEAT Supply Flow Rate [cfm] | VAV_TOP WITH REHEAT Supply Flow Rate [cfm] | 19451.3184 | 18667.3328 | 19811.528 | 19006.3536 | [6 empty] | 2021-05-06
MD_LO_Supply Air Temp. Reset Flag | Supply Air Temp. Reset Flag | Yes | Yes | Yes | Yes | [6 empty] | 2021-05-06
MD_LO_CAV_BAS OA Rate [cfm] | CAV_BAS OA Rate [cfm] | 2542.8255 | 2542.8255 | 2542.8255 | 2542.8255 | [6 empty] | 2021-05-06
MD_LO_VAV_BOT WITH REHEAT OA Rate [cfm] | VAV_BOT WITH REHEAT OA Rate [cfm] | 5377.8022 | 4302.174 | 5377.8022 | 4302.174 | [6 empty] | 2021-05-06
MD_LO_VAV_MID WITH REHEAT OA Rate [cfm] | VAV_MID WITH REHEAT OA Rate [cfm] | 53777.9373 | 43021.7396 | 53777.9373 | 43021.7396 | [6 empty] | 2021-05-06
MD_LO_VAV_TOP WITH REHEAT OA Rate [cfm] | VAV_TOP WITH REHEAT OA Rate [cfm] | 5377.8022 | 4302.174 | 5377.8022 | 4302.174 | [6 empty] | 2021-05-06
MD_LO_AIRLOOP DATACENTER BASEMENT OA Rate [cfm] | AIRLOOP DATACENTER BASEMENT OA Rate [cfm] | 716.9654 | 716.9654 | 716.9654 | 716.9654 | [6 empty] | 2021-05-06
MD_LO_VAV_bot_WITH_REHEAT ERV Flag | VAV_bot_WITH_REHEAT ERV Flag | Yes | Yes | Yes | Yes | [6 empty] | 2021-05-06
MD_LO_VAV_mid_WITH_REHEAT ERV Flag | VAV_mid_WITH_REHEAT ERV Flag | Yes | Yes | Yes | Yes | [6 empty] | 2021-05-06
MD_LO_VAV_top_WITH_REHEAT ERV Flag | VAV_top_WITH_REHEAT ERV Flag | Yes | Yes | Yes | Yes | [6 empty] | 2021-05-06
MD_LO_COOLSYS1 CHILLER1 Capacity [ton] | COOLSYS1 CHILLER1 Capacity [ton] | 419.3885 | 377.8111 | 389.5913 | 353.3461 | [6 empty] | 2021-05-06
MD_LO_COOLSYS1 CHILLER2 Capacity [ton] | COOLSYS1 CHILLER2 Capacity [ton] | 419.3885 | 377.8111 | 389.5913 | 353.3461 | [6 empty] | 2021-05-06
MD_LO_TOWERWATERSYS COOLTOWER 1 Capacity [ton] | TOWERWATERSYS COOLTOWER 1 Capacity [ton] | 398.0767 | 358.6169 | 369.788 | 335.3952 | [6 empty] | 2021-05-06
MD_LO_TOWERWATERSYS COOLTOWER 2 Capacity [ton] | TOWERWATERSYS COOLTOWER 2 Capacity [ton] | 398.0767 | 358.6169 | 369.788 | 335.3952 | [6 empty] | 2021-05-06
MD_LO_HEATSYS1 BOILER Capacity [MMBTU/h] | HEATSYS1 BOILER Capacity [MMBTU/h] | 4070.838 | 3599.392 | 4462.6288 | 3946.5572 | [6 empty] | 2021-05-06
MD_LO_COOLSYS1 PUMP Flow Rate [gal/min] | COOLSYS1 PUMP Flow Rate [gal/min] | 0 | 0 | 0 | 0 | [6 empty] | 2021-05-06
MD_LO_COOLSYS1 CHILLER1 PUMP Flow Rate [gal/min] | COOLSYS1 CHILLER1 PUMP Flow Rate [gal/min] | 660.9236 | 592.5025 | 613.6896 | 556.4842 | [6 empty] | 2021-05-06
MD_LO_COOLSYS1 CHILLER2 PUMP Flow Rate [gal/min] | COOLSYS1 CHILLER2 PUMP Flow Rate [gal/min] | 660.9236 | 592.5025 | 613.6896 | 556.4842 | [6 empty] | 2021-05-06
MD_LO_COOLSYS1 PUMP SECONDARY Flow Rate [gal/min] | COOLSYS1 PUMP SECONDARY Flow Rate [gal/min] | 1321.8472 | 1185.005 | 1227.3777 | 1112.9701 | [6 empty] | 2021-05-06
MD_LO_HEATSYS1 PUMP Flow Rate [gal/min] | HEATSYS1 PUMP Flow Rate [gal/min] | 835.5926 | 738.8232 | 916.0139 | 810.0831 | [6 empty] | 2021-05-06
MD_LO_TOWERWATERSYS PUMP Flow Rate [gal/min] | TOWERWATERSYS PUMP Flow Rate [gal/min] | 2313.8302 | 2084.476 | 2149.4623 | 1949.4312 | [6 empty] | 2021-05-06
MD_LO_PLANT CIRC PUMP Flow Rate [gal/min] | PLANT CIRC PUMP Flow Rate [gal/min] | 208.4096 | 207.5632 | 210.7839 | 209.9391 | [6 empty] | 2021-05-06
MD_LO_COOLSYS1 PUMP SECONDARY Pressure setpoint reset [yes,no] | COOLSYS1 PUMP SECONDARY Pressure setpoint reset [yes,no] | pump_ride_on_curve | pump_ride_on_curve | pump_ride_on_curve | pump_ride_on_curve | [6 empty] | 2021-05-06
MD_LO_COOLSYS1 CHILLER1 PUMP Pump Power [hp] | COOLSYS1 CHILLER1 PUMP Pump Power [hp] | 3.5655 | 3.1647 | 3.3106 | 2.9723 | [6 empty] | 2021-05-06
MD_LO_COOLSYS1 CHILLER2 PUMP Pump Power [hp] | COOLSYS1 CHILLER2 PUMP Pump Power [hp] | 3.5655 | 3.1647 | 3.3106 | 2.9723 | [6 empty] | 2021-05-06
MD_LO_COOLSYS1 PUMP SECONDARY Pump Power [hp] | COOLSYS1 PUMP SECONDARY Pump Power [hp] | 21.3927 | 18.9882 | 19.8638 | 17.8339 | [6 empty] | 2021-05-06
MD_LO_HEATSYS1 PUMP Pump Power [hp] | HEATSYS1 PUMP Pump Power [hp] | 18.0618 | 15.812 | 19.8002 | 17.337 | [6 empty] | 2021-05-06
MD_LO_TOWERWATERSYS PUMP Pump Power [hp] | TOWERWATERSYS PUMP Pump Power [hp] | 41.4263 | 36.9499 | 38.483 | 34.5572 | [6 empty] | 2021-05-06
MD_LO_PLANT CIRC PUMP Pump Power [hp] | PLANT CIRC PUMP Pump Power [hp] | 4.4972 | 4.4346 | 4.5484 | 4.4853 | [6 empty] | 2021-05-06
MD_LO_Datacenter PLANT CIRC PUMP Pump Power [hp] | Datacenter PLANT CIRC PUMP Pump Power [hp] | 4.4972 | 4.4346 | 4.5484 | 4.4853 | [6 empty] | 2021-05-06
MD_LO_ZN_VAV_BOXes_Max_Reheat_Water_Flow_GPM | ZN_VAV_BOXes_Max_Reheat_Water_Flow_GPM | 438.3628 | 419.0812 | 466.1073 | 447.9179 | [6 empty] | 2021-05-06
MD_LO_COOLSYS1 PUMP SECONDARY VSD | COOLSYS1 PUMP SECONDARY VSD | No | No | No | No | [6 empty] | 2021-05-06
MD_LO_HEATSYS1 PUMP VSD | HEATSYS1 PUMP VSD | No | No | No | No | [6 empty] | 2021-05-06
MD_LO_DATACENTER BASEMENT Cooling Capacity [ton] | DATACENTER BASEMENT Cooling Capacity [ton] | 122.0782 | 121.7171 | 123.1812 | 122.8159 | [6 empty] | 2021-05-06
MD_LO_DATACENTER BOT Cooling Capacity [ton] | DATACENTER BOT Cooling Capacity [ton] | 2.6505 | 2.6272 | 2.7023 | 2.6785 | [6 empty] | 2021-05-06
MD_LO_DATACENTER MID Cooling Capacity [ton] | DATACENTER MID Cooling Capacity [ton] | 25.352 | 25.1355 | 25.8844 | 25.6746 | [6 empty] | 2021-05-06
MD_LO_DATACENTER TOP Cooling Capacity [ton] | DATACENTER TOP Cooling Capacity [ton] | 2.5842 | 2.5643 | 2.6357 | 2.6155 | [6 empty] | 2021-05-06
id | item | Zone4A(MD-Baltimore-MD) ASHRAE901-state_STD2016 | Zone4A(MD-Baltimore-MD) ASHRAE901-state_STD2019 | Zone5A(MD-Pittsburgh-PA) ASHRAE901-state_STD2016 | Zone5A(MD-Pittsburgh-PA) ASHRAE901-state_STD2019 | [6 empty] | 2021-05-06
MD_RS_PSZ-AC:1 Cooling Capacity [ton] | PSZ-AC:1 Cooling Capacity [ton] | 10.5815 | 10.2464 | 9.9665 | 9.5661 | [6 empty] | 2021-05-06
MD_RS_PSZ-AC:2 Cooling Capacity [ton] | PSZ-AC:2 Cooling Capacity [ton] | 50.5021 | 48.4923 | 46.8162 | 44.9445 | [6 empty] | 2021-05-06
MD_RS_PSZ-AC:3 Cooling Capacity [ton] | PSZ-AC:3 Cooling Capacity [ton] | 6.6414 | 6.4807 | 6.1009 | 5.9405 | [6 empty] | 2021-05-06
MD_RS_PSZ-AC:4 Cooling Capacity [ton] | PSZ-AC:4 Cooling Capacity [ton] | 5.427 | 5.2702 | 4.8966 | 4.7223 | [6 empty] | 2021-05-06
MD_RS_PSZ-AC:1 Supply Flow Rate [cfm] | PSZ-AC:1 Supply Flow Rate [cfm] | 4025.872 | 3771.6064 | 3962.3056 | 3665.6624 | [6 empty] | 2021-05-06
MD_RS_PSZ-AC:2 Supply Flow Rate [cfm] | PSZ-AC:2 Supply Flow Rate [cfm] | 15340.6912 | 14556.7056 | 15552.5792 | 14662.6496 | [6 empty] | 2021-05-06
MD_RS_PSZ-AC:3 Supply Flow Rate [cfm] | PSZ-AC:3 Supply Flow Rate [cfm] | 2330.768 | 2246.0128 | 2288.3904 | 2203.6352 | [6 empty] | 2021-05-06
MD_RS_PSZ-AC:4 Supply Flow Rate [cfm] | PSZ-AC:4 Supply Flow Rate [cfm] | 1779.8592 | 1716.2928 | 1716.2928 | 1652.7264 | [6 empty] | 2021-05-06
MD_RS_PSZ-AC:1 OA Rate [cfm] | PSZ-AC:1 OA Rate [cfm] | 490.669 | 490.669 | 490.669 | 490.669 | [6 empty] | 2021-05-06
MD_RS_PSZ-AC:2 OA Rate [cfm] | PSZ-AC:2 OA Rate [cfm] | 4005.1282 | 4005.1282 | 4005.1282 | 4005.1282 | [6 empty] | 2021-05-06
MD_RS_PSZ-AC:3 OA Rate [cfm] | PSZ-AC:3 OA Rate [cfm] | 377.3937 | 377.3937 | 377.3937 | 377.3937 | [6 empty] | 2021-05-06
MD_RS_PSZ-AC:4 OA Rate [cfm] | PSZ-AC:4 OA Rate [cfm] | 377.3937 | 377.3937 | 377.3937 | 377.3937 | [6 empty] | 2021-05-06
MD_RS_PSZ-AC:1 OA Damper [gravity, motorized] | PSZ-AC:1 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2021-05-06
MD_RS_PSZ-AC:2 OA Damper [gravity, motorized] | PSZ-AC:2 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2021-05-06
MD_RS_PSZ-AC:3 OA Damper [gravity, motorized] | PSZ-AC:3 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2021-05-06
MD_RS_PSZ-AC:4 OA Damper [gravity, motorized] | PSZ-AC:4 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2021-05-06
MD_RS_PSZ-AC:1 Heating Capacity [kBtu/hr] | PSZ-AC:1 Heating Capacity [kBtu/hr] | 177.8179 | 167.5076 | 173.2632 | 161.598 | [6 empty] | 2021-05-06
MD_RS_PSZ-AC:2 Heating Capacity [kBtu/hr] | PSZ-AC:2 Heating Capacity [kBtu/hr] | 798.1653 | 764.8143 | 814.7737 | 778.0039 | [6 empty] | 2021-05-06
MD_RS_PSZ-AC:3 Heating Capacity [kBtu/hr] | PSZ-AC:3 Heating Capacity [kBtu/hr] | 108.941 | 106.2685 | 107.171 | 104.471 | [6 empty] | 2021-05-06
MD_RS_PSZ-AC:4 Heating Capacity [kBtu/hr] | PSZ-AC:4 Heating Capacity [kBtu/hr] | 88.9721 | 86.1477 | 86.8284 | 83.6636 | [6 empty] | 2021-05-06
id | item | Zone4A(MD-Baltimore-MD) ASHRAE901-state_STD2016 | Zone4A(MD-Baltimore-MD) ASHRAE901-state_STD2019 | Zone5A(MD-Pittsburgh-PA) ASHRAE901-state_STD2016 | Zone5A(MD-Pittsburgh-PA) ASHRAE901-state_STD2019 | [6 empty] | 2021-05-06
MD_PS_VAV_POD_1 Cooling Capacity [ton] | VAV_POD_1 Cooling Capacity [ton] | 19.2855 | 18.6268 | 19.2922 | 18.5917 | [6 empty] | 2021-05-06
MD_PS_VAV_POD_2 Cooling Capacity [ton] | VAV_POD_2 Cooling Capacity [ton] | 18.9849 | 18.4274 | 19.0113 | 18.4805 | [6 empty] | 2021-05-06
MD_PS_VAV_POD_3 Cooling Capacity [ton] | VAV_POD_3 Cooling Capacity [ton] | 17.5233 | 16.7415 | 17.5728 | 16.7439 | [6 empty] | 2021-05-06
MD_PS_VAV_OTHER Cooling Capacity [ton] | VAV_OTHER Cooling Capacity [ton] | 26.8056 | 25.2864 | 27.1456 | 25.5085 | [6 empty] | 2021-05-06
MD_PS_PSZ-AC_1:6 Cooling Capacity [ton] | PSZ-AC_1:6 Cooling Capacity [ton] | 8.4875 | 8.1383 | 8.1327 | 7.87 | [6 empty] | 2021-05-06
MD_PS_PSZ-AC_2:5 Cooling Capacity [ton] | PSZ-AC_2:5 Cooling Capacity [ton] | 5.3757 | 5.4614 | 5.5896 | 5.5665 | [6 empty] | 2021-05-06
MD_PS_PSZ-AC_2:7 Cooling Capacity [ton] | PSZ-AC_2:7 Cooling Capacity [ton] | 10.5074 | 10.5074 | 10.5074 | 10.5074 | [6 empty] | 2021-05-06
MD_PS_VAV_POD_1 Supply Flow Rate [cfm] | VAV_POD_1 Supply Flow Rate [cfm] | 5784.5424 | 5593.8432 | 5784.5424 | 5572.6544 | [6 empty] | 2021-05-06
MD_PS_VAV_POD_2 Supply Flow Rate [cfm] | VAV_POD_2 Supply Flow Rate [cfm] | 5699.7872 | 5530.2768 | 5699.7872 | 5551.4656 | [6 empty] | 2021-05-06
MD_PS_VAV_POD_3 Supply Flow Rate [cfm] | VAV_POD_3 Supply Flow Rate [cfm] | 5254.8224 | 5021.7456 | 5276.0112 | 5021.7456 | [6 empty] | 2021-05-06
MD_PS_VAV_OTHER Supply Flow Rate [cfm] | VAV_OTHER Supply Flow Rate [cfm] | 8051.744 | 7585.5904 | 8136.4992 | 7649.1568 | [6 empty] | 2021-05-06
MD_PS_PSZ-AC_2:5 Supply Flow Rate [cfm] | PSZ-AC_2:5 Supply Flow Rate [cfm] | 1610.3488 | 1631.5376 | 1673.9152 | 1673.9152 | [6 empty] | 2021-05-06
MD_PS_PSZ-AC_1:6 Supply Flow Rate [cfm] | PSZ-AC_1:6 Supply Flow Rate [cfm] | 2542.656 | 2436.712 | 2627.4112 | 2521.4672 | [6 empty] | 2021-05-06
MD_PS_PSZ-AC_2:7 Supply Flow Rate [cfm] | PSZ-AC_2:7 Supply Flow Rate [cfm] | 3157.1312 | 3157.1312 | 3157.1312 | 3157.1312 | [6 empty] | 2021-05-06
MD_PS_Supply Air Temp. Reset Flag | Supply Air Temp. Reset Flag | Yes | Yes | Yes | Yes | [6 empty] | 2021-05-06
MD_PS_VAV_POD_1 OA Rate [cfm] | VAV_POD_1 OA Rate [cfm] | 5787.2758 | 5589.5843 | 5789.2887 | 5579.0534 | [6 empty] | 2021-05-06
MD_PS_VAV_POD_2 OA Rate [cfm] | VAV_POD_2 OA Rate [cfm] | 5696.4606 | 5529.7471 | 5704.9997 | 5545.7023 | [6 empty] | 2021-05-06
MD_PS_VAV_POD_3 OA Rate [cfm] | VAV_POD_3 OA Rate [cfm] | 5257.7465 | 5023.8645 | 5273.3202 | 5024.5637 | [6 empty] | 2021-05-06
MD_PS_VAV_OTHER OA Rate [cfm] | VAV_OTHER OA Rate [cfm] | 3736.1787 | 2988.8921 | 3736.1787 | 2988.8921 | [6 empty] | 2021-05-06
MD_PS_PSZ-AC_2:5 OA Rate [cfm] | PSZ-AC_2:5 OA Rate [cfm] | 1152.7343 | 1152.7343 | 1152.7343 | 1152.7343 | [6 empty] | 2021-05-06
MD_PS_PSZ-AC_1:6 OA Rate [cfm] | PSZ-AC_1:6 OA Rate [cfm] | 539.9118 | 539.9118 | 539.9118 | 539.9118 | [6 empty] | 2021-05-06
MD_PS_PSZ-AC_2:7 OA Rate [cfm] | PSZ-AC_2:7 OA Rate [cfm] | 3153.0841 | 3153.0841 | 3153.0841 | 3153.0841 | [6 empty] | 2021-05-06
MD_PS_VAV_POD_1 OA Damper [gravity, motorized] | VAV_POD_1 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2021-05-06
MD_PS_VAV_POD_2 OA Damper [gravity, motorized] | VAV_POD_2 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2021-05-06
MD_PS_VAV_POD_3 OA Damper [gravity, motorized] | VAV_POD_3 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2021-05-06
MD_PS_VAV_OTHER OA Damper [gravity, motorized] | VAV_OTHER OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2021-05-06
MD_PS_PSZ-AC_2:5 OA Damper [gravity, motorized] | PSZ-AC_2:5 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2021-05-06
MD_PS_PSZ-AC_1:6 OA Damper [gravity, motorized] | PSZ-AC_1:6 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2021-05-06
MD_PS_PSZ-AC_2:7 OA Damper [gravity, motorized] | PSZ-AC_2:7 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2021-05-06
MD_PS_VAV_POD_1 (economizer) | VAV_POD_1 (economizer) | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialDryBulb | DifferentialDryBulb | [6 empty] | 2021-05-06
MD_PS_VAV_POD_2 (economizer) | VAV_POD_2 (economizer) | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialDryBulb | DifferentialDryBulb | [6 empty] | 2021-05-06
MD_PS_VAV_POD_3 (economizer) | VAV_POD_3 (economizer) | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialDryBulb | DifferentialDryBulb | [6 empty] | 2021-05-06
MD_PS_VAV_OTHER (economizer) | VAV_OTHER (economizer) | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialDryBulb | DifferentialDryBulb | [6 empty] | 2021-05-06
MD_PS_PSZ-AC_2:5 (economizer) | PSZ-AC_2:5 (economizer) | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialDryBulb | DifferentialDryBulb | [6 empty] | 2021-05-06
MD_PS_PSZ-AC_1:6 (economizer) | PSZ-AC_1:6 (economizer) | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialDryBulb | DifferentialDryBulb | [6 empty] | 2021-05-06
MD_PS_PSZ-AC_2:7 (economizer) | PSZ-AC_2:7 (economizer) | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialDryBulb | DifferentialDryBulb | [6 empty] | 2021-05-06
MD_PS_VAV_Pod_1_ERV Flag | VAV_Pod_1_ERV Flag | Yes | Yes | Yes | Yes | [6 empty] | 2021-05-06
MD_PS_VAV_Pod_2_ERV Flag | VAV_Pod_2_ERV Flag | Yes | Yes | Yes | Yes | [6 empty] | 2021-05-06
MD_PS_VAV_Pod_3_ERV Flag | VAV_Pod_3_ERV Flag | Yes | Yes | Yes | Yes | [6 empty] | 2021-05-06
MD_PS_VAV_OTHER_ERV Flag | VAV_OTHER_ERV Flag | Yes | Yes | Yes | Yes | [6 empty] | 2021-05-06
MD_PS_PSZ_AC_2_5_ERV Flag | PSZ_AC_2_5_ERV Flag | Yes | Yes | No | No | [6 empty] | 2021-05-06
MD_PS_PSZ_AC_2_7_ERV Flag | PSZ_AC_2_7_ERV Flag | Yes | Yes | Yes | Yes | [6 empty] | 2021-05-06
MD_PS_HEATSYS1 Capacity [MMBTU/h] | HEATSYS1 Capacity [MMBTU/h] | 0.99182 | 0.94583 | 1.0921 | 1.0467 | [6 empty] | 2021-05-06
MD_PS_HEATSYS1 Flow Rate [gal/min] | HEATSYS1 Flow Rate [gal/min] | 101.7924 | 97.0723 | 112.0814 | 107.4286 | [6 empty] | 2021-05-06
MD_PS_VAV_POD_1 Fan Power [hp] | VAV_POD_1 Fan Power [hp] | 8.538 | 8.2463 | 8.5409 | 8.2308 | [6 empty] | 2021-05-06
MD_PS_VAV_POD_2 Fan Power [hp] | VAV_POD_2 Fan Power [hp] | 8.4049 | 8.158 | 8.4166 | 8.1816 | [6 empty] | 2021-05-06
MD_PS_VAV_POD_3 Fan Power [hp] | VAV_POD_3 Fan Power [hp] | 7.7578 | 7.4117 | 7.7797 | 7.4127 | [6 empty] | 2021-05-06
MD_PS_VAV_OTHER Fan Power [hp] | VAV_OTHER Fan Power [hp] | 11.7773 | 11.1098 | 11.9267 | 11.2074 | [6 empty] | 2021-05-06
MD_PS_HEATSYS1 Pump Power [hp] | HEATSYS1 Pump Power [hp] | 2.2003 | 2.0775 | 2.4227 | 2.2991 | [6 empty] | 2021-05-06
MD_PS_PSZ-AC_1:6 Heating Capacity [kBtu/hr] | PSZ-AC_1:6 Heating Capacity [kBtu/hr] | 209.0182 | 200.4499 | 212.5855 | 204.0379 | [6 empty] | 2021-05-06
MD_PS_PSZ-AC_2:5 Heating Capacity [kBtu/hr] | PSZ-AC_2:5 Heating Capacity [kBtu/hr] | 130.0227 | 130.969 | 138.653 | 138.4071 | [6 empty] | 2021-05-06
MD_PS_PSZ-AC_2:7 Heating Capacity [kBtu/hr] | PSZ-AC_2:7 Heating Capacity [kBtu/hr] | 309.2659 | 309.2659 | 328.2932 | 328.2932 | [6 empty] | 2021-05-06
MD_PS_ZN_VAV_BOXes_Max_Reheat_Water_Flow_GPM | ZN_VAV_BOXes_Max_Reheat_Water_Flow_GPM | 67.176 | 63.9299 | 71.2163 | 68.3833 | [6 empty] | 2021-05-06
id | item | Zone4A(MD-Baltimore-MD) ASHRAE901-state_STD2016 | Zone4A(MD-Baltimore-MD) ASHRAE901-state_STD2019 | Zone5A(MD-Pittsburgh-PA) ASHRAE901-state_STD2016 | Zone5A(MD-Pittsburgh-PA) ASHRAE901-state_STD2019 | [6 empty] | 2021-05-06
MD_SH_SAC_FRONTOFFICE Cooling Capacity [ton] | SAC_FRONTOFFICE Cooling Capacity [ton] | 2.403 | 2.2861 | 2.2155 | 2.1042 | [6 empty] | 2021-05-06
MD_SH_SAC_FRONTLOUNGE Cooling Capacity [ton] | SAC_FRONTLOUNGE Cooling Capacity [ton] | 6.152 | 5.8438 | 6.1066 | 5.8648 | [6 empty] | 2021-05-06
MD_SH_SAC_MEETINGROOM Cooling Capacity [ton] | SAC_MEETINGROOM Cooling Capacity [ton] | 2.8896 | 2.8184 | 2.9467 | 2.8554 | [6 empty] | 2021-05-06
MD_SH_SAC_EXC_EMPLGE_RESTRM Cooling Capacity [ton] | SAC_EXC_EMPLGE_RESTRM Cooling Capacity [ton] | 6.087 | 6.0449 | 5.8241 | 5.7835 | [6 empty] | 2021-05-06
MD_SH_SAC_FO_ADDAQ SUPPLY FAN Supply Flow Rate [cfm] | SAC_FO_ADDAQ SUPPLY FAN Supply Flow Rate [cfm] | 783.9856 | 741.608 | 783.9856 | 720.4192 | [6 empty] | 2021-05-06
MD_SH_SAC_FL_ADDAQ SUPPLY FAN Supply Flow Rate [cfm] | SAC_FL_ADDAQ SUPPLY FAN Supply Flow Rate [cfm] | 1843.4256 | 1758.6704 | 1864.6144 | 1758.6704 | [6 empty] | 2021-05-06
MD_SH_SAC_MR_ADDAQ SUPPLY FAN Supply Flow Rate [cfm] | SAC_MR_ADDAQ SUPPLY FAN Supply Flow Rate [cfm] | 868.7408 | 847.552 | 889.9296 | 847.552 | [6 empty] | 2021-05-06
MD_SH_SAC_EXC_ADDAQ SUPPLY FAN Supply Flow Rate [cfm] | SAC_EXC_ADDAQ SUPPLY FAN Supply Flow Rate [cfm] | 2182.4464 | 2161.2576 | 2246.0128 | 2224.824 | [6 empty] | 2021-05-06
MD_SH_SAC_Exc_EmpLge_RestRm OA Rate [cfm] | SAC_Exc_EmpLge_RestRm OA Rate [cfm] | 199.9928 | 199.9928 | 199.9928 | 199.9928 | [6 empty] | 2021-05-06
MD_SH_SAC_FrontLounge OA Rate [cfm] | SAC_FrontLounge OA Rate [cfm] | 500.0133 | 500.0133 | 500.0133 | 500.0133 | [6 empty] | 2021-05-06
MD_SH_SAC_FrontOffice OA Rate [cfm] | SAC_FrontOffice OA Rate [cfm] | 119.2938 | 119.2938 | 119.2938 | 119.2938 | [6 empty] | 2021-05-06
MD_SH_SAC_MeetingRoom OA Rate [cfm] | SAC_MeetingRoom OA Rate [cfm] | 267.7629 | 267.7629 | 267.7629 | 267.7629 | [6 empty] | 2021-05-06
MD_SH_SAC_FrontLounge OA Damper [gravity, motorized] | SAC_FrontLounge OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2021-05-06
MD_SH_SAC_FrontOffice (economizer) | SAC_FrontOffice (economizer) | No | No | No | No | [6 empty] | 2021-05-06
MD_SH_SAC_FrontLounge (economizer) | SAC_FrontLounge (economizer) | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialDryBulb | DifferentialDryBulb | [6 empty] | 2021-05-06
MD_SH_SAC_MeetingRoom (economizer) | SAC_MeetingRoom (economizer) | No | No | No | No | [6 empty] | 2021-05-06
MD_SH_SAC_Exc_EmpLge_RestRm (economizer) | SAC_Exc_EmpLge_RestRm (economizer) | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialDryBulb | DifferentialDryBulb | [6 empty] | 2021-05-06
MD_SH_SAC_FRONTOFFICE Heating Capacity [kBtu/hr] | SAC_FRONTOFFICE Heating Capacity [kBtu/hr] | 36.078 | 34.3251 | 35.6069 | 33.8275 | [6 empty] | 2021-05-06
MD_SH_SAC_FRONTLOUNGE Heating Capacity [kBtu/hr] | SAC_FRONTLOUNGE Heating Capacity [kBtu/hr] | 98.3301 | 94.9441 | 99.913 | 96.5469 | [6 empty] | 2021-05-06
MD_SH_SAC_MEETINGROOM Heating Capacity [kBtu/hr] | SAC_MEETINGROOM Heating Capacity [kBtu/hr] | 48.2083 | 47.4257 | 49.6459 | 48.6789 | [6 empty] | 2021-05-06
MD_SH_SAC_EXC_EMPLGE_RESTRM Heating Capacity [kBtu/hr] | SAC_EXC_EMPLGE_RESTRM Heating Capacity [kBtu/hr] | 92.4562 | 91.8045 | 93.208 | 92.5514 | [6 empty] | 2021-05-06
id | item | Zone4A(MD-Baltimore-MD) ASHRAE901-state_STD2016 | Zone4A(MD-Baltimore-MD) ASHRAE901-state_STD2019 | Zone5A(MD-Pittsburgh-PA) ASHRAE901-state_STD2016 | Zone5A(MD-Pittsburgh-PA) ASHRAE901-state_STD2019 | [6 empty] | 2021-05-06
MD_MA_SPLIT GSW COOLING COIL Cooling Capacity [ton] | SPLIT GSW COOLING COIL Cooling Capacity [ton] | 0.89896 | 0.88507 | 0.81155 | 0.7974 | [6 empty] | 2021-05-06
MD_MA_SPLIT GNW COOLING COIL Cooling Capacity [ton] | SPLIT GNW COOLING COIL Cooling Capacity [ton] | 0.86337 | 0.8499 | 0.77387 | 0.76018 | [6 empty] | 2021-05-06
MD_MA_SPLIT OFFICE COOLING COIL Cooling Capacity [ton] | SPLIT OFFICE COOLING COIL Cooling Capacity [ton] | 1.701 | 1.6099 | 1.6816 | 1.5507 | [6 empty] | 2021-05-06
MD_MA_SPLIT GNE COOLING COIL Cooling Capacity [ton] | SPLIT GNE COOLING COIL Cooling Capacity [ton] | 0.76485 | 0.75291 | 0.66787 | 0.65572 | [6 empty] | 2021-05-06
MD_MA_SPLIT GN1 COOLING COIL Cooling Capacity [ton] | SPLIT GN1 COOLING COIL Cooling Capacity [ton] | 0.64449 | 0.63483 | 0.56386 | 0.55475 | [6 empty] | 2021-05-06
MD_MA_SPLIT GN2 COOLING COIL Cooling Capacity [ton] | SPLIT GN2 COOLING COIL Cooling Capacity [ton] | 0.64259 | 0.63297 | 0.56164 | 0.55258 | [6 empty] | 2021-05-06
MD_MA_SPLIT GS1 COOLING COIL Cooling Capacity [ton] | SPLIT GS1 COOLING COIL Cooling Capacity [ton] | 0.68794 | 0.67759 | 0.61029 | 0.59984 | [6 empty] | 2021-05-06
MD_MA_SPLIT GS2 COOLING COIL Cooling Capacity [ton] | SPLIT GS2 COOLING COIL Cooling Capacity [ton] | 0.71843 | 0.70434 | 0.6426 | 0.62707 | [6 empty] | 2021-05-06
MD_MA_SPLIT MSW COOLING COIL Cooling Capacity [ton] | SPLIT MSW COOLING COIL Cooling Capacity [ton] | 2.104 | 2.0732 | 1.9708 | 1.9392 | [6 empty] | 2021-05-06
MD_MA_SPLIT MNW COOLING COIL Cooling Capacity [ton] | SPLIT MNW COOLING COIL Cooling Capacity [ton] | 2.034 | 2.0043 | 1.9055 | 1.8749 | [6 empty] | 2021-05-06
MD_MA_SPLIT MSE COOLING COIL Cooling Capacity [ton] | SPLIT MSE COOLING COIL Cooling Capacity [ton] | 1.8679 | 1.8411 | 1.6869 | 1.6594 | [6 empty] | 2021-05-06
MD_MA_SPLIT MNE COOLING COIL Cooling Capacity [ton] | SPLIT MNE COOLING COIL Cooling Capacity [ton] | 1.7241 | 1.7011 | 1.5553 | 1.5256 | [6 empty] | 2021-05-06
MD_MA_SPLIT MN1 COOLING COIL Cooling Capacity [ton] | SPLIT MN1 COOLING COIL Cooling Capacity [ton] | 1.404 | 1.3854 | 1.2676 | 1.2501 | [6 empty] | 2021-05-06
MD_MA_SPLIT MN2 COOLING COIL Cooling Capacity [ton] | SPLIT MN2 COOLING COIL Cooling Capacity [ton] | 1.3987 | 1.3803 | 1.2615 | 1.2442 | [6 empty] | 2021-05-06
MD_MA_SPLIT MS1 COOLING COIL Cooling Capacity [ton] | SPLIT MS1 COOLING COIL Cooling Capacity [ton] | 1.4831 | 1.4635 | 1.3518 | 1.3322 | [6 empty] | 2021-05-06
MD_MA_SPLIT MS2 COOLING COIL Cooling Capacity [ton] | SPLIT MS2 COOLING COIL Cooling Capacity [ton] | 1.4779 | 1.4585 | 1.3464 | 1.3269 | [6 empty] | 2021-05-06
MD_MA_SPLIT TSW COOLING COIL Cooling Capacity [ton] | SPLIT TSW COOLING COIL Cooling Capacity [ton] | 1.3201 | 1.3031 | 1.2264 | 1.2092 | [6 empty] | 2021-05-06
MD_MA_SPLIT TNW COOLING COIL Cooling Capacity [ton] | SPLIT TNW COOLING COIL Cooling Capacity [ton] | 1.2709 | 1.2548 | 1.1847 | 1.1681 | [6 empty] | 2021-05-06
MD_MA_SPLIT TSE COOLING COIL Cooling Capacity [ton] | SPLIT TSE COOLING COIL Cooling Capacity [ton] | 1.1993 | 1.1854 | 1.0881 | 1.0739 | [6 empty] | 2021-05-06
MD_MA_SPLIT TNE COOLING COIL Cooling Capacity [ton] | SPLIT TNE COOLING COIL Cooling Capacity [ton] | 1.1256 | 1.1128 | 1.0125 | 0.9998 | [6 empty] | 2021-05-06
MD_MA_SPLIT TN1 COOLING COIL Cooling Capacity [ton] | SPLIT TN1 COOLING COIL Cooling Capacity [ton] | 0.89139 | 0.88184 | 0.81287 | 0.80329 | [6 empty] | 2021-05-06
MD_MA_SPLIT TN2 COOLING COIL Cooling Capacity [ton] | SPLIT TN2 COOLING COIL Cooling Capacity [ton] | 0.92 | 0.91007 | 0.80627 | 0.79686 | [6 empty] | 2021-05-06
MD_MA_SPLIT TS1 COOLING COIL Cooling Capacity [ton] | SPLIT TS1 COOLING COIL Cooling Capacity [ton] | 0.9933 | 0.98226 | 0.89672 | 0.88583 | [6 empty] | 2021-05-06
MD_MA_SPLIT TS2 COOLING COIL Cooling Capacity [ton] | SPLIT TS2 COOLING COIL Cooling Capacity [ton] | 0.99478 | 0.98373 | 0.90159 | 0.8905 | [6 empty] | 2021-05-06
MD_MA_Split GN1 Furnace with DX Cooling OA Rate [cfm] | Split GN1 Furnace with DX Cooling OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | [6 empty] | 2021-05-06
MD_MA_Split GN2 Furnace with DX Cooling OA Rate [cfm] | Split GN2 Furnace with DX Cooling OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | [6 empty] | 2021-05-06
MD_MA_Split GNE Furnace with DX Cooling OA Rate [cfm] | Split GNE Furnace with DX Cooling OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | [6 empty] | 2021-05-06
MD_MA_Split GNW Furnace with DX Cooling OA Rate [cfm] | Split GNW Furnace with DX Cooling OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | [6 empty] | 2021-05-06
MD_MA_Split GS1 Furnace with DX Cooling OA Rate [cfm] | Split GS1 Furnace with DX Cooling OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | [6 empty] | 2021-05-06
MD_MA_Split GS2 Furnace with DX Cooling OA Rate [cfm] | Split GS2 Furnace with DX Cooling OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | [6 empty] | 2021-05-06
MD_MA_Split GSW Furnace with DX Cooling OA Rate [cfm] | Split GSW Furnace with DX Cooling OA Rate [cfm] | 56.9945 | 56.9945 | 56.9945 | 56.9945 | [6 empty] | 2021-05-06
MD_MA_Split MN1 Furnace with DX Cooling OA Rate [cfm] | Split MN1 Furnace with DX Cooling OA Rate [cfm] | 109.9824 | 109.9824 | 109.9824 | 109.9824 | [6 empty] | 2021-05-06
MD_MA_Split MN2 Furnace with DX Cooling OA Rate [cfm] | Split MN2 Furnace with DX Cooling OA Rate [cfm] | 109.9824 | 109.9824 | 109.9824 | 109.9824 | [6 empty] | 2021-05-06
MD_MA_Split MNE Furnace with DX Cooling OA Rate [cfm] | Split MNE Furnace with DX Cooling OA Rate [cfm] | 109.9824 | 109.9824 | 109.9824 | 109.9824 | [6 empty] | 2021-05-06
MD_MA_Split MNW Furnace with DX Cooling OA Rate [cfm] | Split MNW Furnace with DX Cooling OA Rate [cfm] | 109.9824 | 109.9824 | 109.9824 | 109.9824 | [6 empty] | 2021-05-06
MD_MA_Split MS1 Furnace with DX Cooling OA Rate [cfm] | Split MS1 Furnace with DX Cooling OA Rate [cfm] | 109.9824 | 109.9824 | 109.9824 | 109.9824 | [6 empty] | 2021-05-06
MD_MA_Split MS2 Furnace with DX Cooling OA Rate [cfm] | Split MS2 Furnace with DX Cooling OA Rate [cfm] | 109.9824 | 109.9824 | 109.9824 | 109.9824 | [6 empty] | 2021-05-06
MD_MA_Split MSE Furnace with DX Cooling OA Rate [cfm] | Split MSE Furnace with DX Cooling OA Rate [cfm] | 109.9824 | 109.9824 | 109.9824 | 109.9824 | [6 empty] | 2021-05-06
MD_MA_Split MSW Furnace with DX Cooling OA Rate [cfm] | Split MSW Furnace with DX Cooling OA Rate [cfm] | 109.9824 | 109.9824 | 109.9824 | 109.9824 | [6 empty] | 2021-05-06
MD_MA_Split Office Furnace with DX Cooling OA Rate [cfm] | Split Office Furnace with DX Cooling OA Rate [cfm] | 80.7372 | 80.7372 | 80.7372 | 80.7372 | [6 empty] | 2021-05-06
MD_MA_Split TN1 Furnace with DX Cooling OA Rate [cfm] | Split TN1 Furnace with DX Cooling OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | [6 empty] | 2021-05-06
MD_MA_Split TN2 Furnace with DX Cooling OA Rate [cfm] | Split TN2 Furnace with DX Cooling OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | [6 empty] | 2021-05-06
MD_MA_Split TNE Furnace with DX Cooling OA Rate [cfm] | Split TNE Furnace with DX Cooling OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | [6 empty] | 2021-05-06
MD_MA_Split TNW Furnace with DX Cooling OA Rate [cfm] | Split TNW Furnace with DX Cooling OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | [6 empty] | 2021-05-06
MD_MA_Split TS1 Furnace with DX Cooling OA Rate [cfm] | Split TS1 Furnace with DX Cooling OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | [6 empty] | 2021-05-06
MD_MA_Split TS2 Furnace with DX Cooling OA Rate [cfm] | Split TS2 Furnace with DX Cooling OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | [6 empty] | 2021-05-06
MD_MA_Split TSE Furnace with DX Cooling OA Rate [cfm] | Split TSE Furnace with DX Cooling OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | [6 empty] | 2021-05-06
MD_MA_Split TSW Furnace with DX Cooling OA Rate [cfm] | Split TSW Furnace with DX Cooling OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | [6 empty] | 2021-05-06
MD_MA_SPLIT GSW HEATING COIL Heating Capacity [kBtu/hr] | SPLIT GSW HEATING COIL Heating Capacity [kBtu/hr] | 8.3973 | 8.4561 | 9.6661 | 9.7243 | [6 empty] | 2021-05-06
MD_MA_SPLIT GNW HEATING COIL Heating Capacity [kBtu/hr] | SPLIT GNW HEATING COIL Heating Capacity [kBtu/hr] | 8.3321 | 8.391 | 9.53 | 9.5884 | [6 empty] | 2021-05-06
MD_MA_SPLIT OFFICE HEATING COIL Heating Capacity [kBtu/hr] | SPLIT OFFICE HEATING COIL Heating Capacity [kBtu/hr] | 20.5861 | 20.6925 | 22.4236 | 22.5057 | [6 empty] | 2021-05-06
MD_MA_SPLIT GNE HEATING COIL Heating Capacity [kBtu/hr] | SPLIT GNE HEATING COIL Heating Capacity [kBtu/hr] | 8.3152 | 8.374 | 9.5081 | 9.5664 | [6 empty] | 2021-05-06
MD_MA_SPLIT GN1 HEATING COIL Heating Capacity [kBtu/hr] | SPLIT GN1 HEATING COIL Heating Capacity [kBtu/hr] | 6.0399 | 6.0989 | 7.0072 | 7.0657 | [6 empty] | 2021-05-06
MD_MA_SPLIT GN2 HEATING COIL Heating Capacity [kBtu/hr] | SPLIT GN2 HEATING COIL Heating Capacity [kBtu/hr] | 6.0394 | 6.0984 | 7.0066 | 7.065 | [6 empty] | 2021-05-06
MD_MA_SPLIT GS1 HEATING COIL Heating Capacity [kBtu/hr] | SPLIT GS1 HEATING COIL Heating Capacity [kBtu/hr] | 5.9974 | 6.0562 | 7.0228 | 7.0811 | [6 empty] | 2021-05-06
MD_MA_SPLIT GS2 HEATING COIL Heating Capacity [kBtu/hr] | SPLIT GS2 HEATING COIL Heating Capacity [kBtu/hr] | 6.4799 | 6.5408 | 7.5269 | 7.5861 | [6 empty] | 2021-05-06
MD_MA_SPLIT MSW HEATING COIL Heating Capacity [kBtu/hr] | SPLIT MSW HEATING COIL Heating Capacity [kBtu/hr] | 14.978 | 15.1067 | 16.8486 | 16.9775 | [6 empty] | 2021-05-06
MD_MA_SPLIT MNW HEATING COIL Heating Capacity [kBtu/hr] | SPLIT MNW HEATING COIL Heating Capacity [kBtu/hr] | 15.0488 | 15.1774 | 16.7806 | 16.9097 | [6 empty] | 2021-05-06
MD_MA_SPLIT MSE HEATING COIL Heating Capacity [kBtu/hr] | SPLIT MSE HEATING COIL Heating Capacity [kBtu/hr] | 14.9376 | 15.0663 | 16.7965 | 16.9255 | [6 empty] | 2021-05-06
MD_MA_SPLIT MNE HEATING COIL Heating Capacity [kBtu/hr] | SPLIT MNE HEATING COIL Heating Capacity [kBtu/hr] | 15.0084 | 15.1371 | 16.7285 | 16.8575 | [6 empty] | 2021-05-06
MD_MA_SPLIT MN1 HEATING COIL Heating Capacity [kBtu/hr] | SPLIT MN1 HEATING COIL Heating Capacity [kBtu/hr] | 10.7875 | 10.7875 | 11.6142 | 11.7398 | [6 empty] | 2021-05-06
MD_MA_SPLIT MN2 HEATING COIL Heating Capacity [kBtu/hr] | SPLIT MN2 HEATING COIL Heating Capacity [kBtu/hr] | 10.7875 | 10.7875 | 11.6128 | 11.7384 | [6 empty] | 2021-05-06
MD_MA_SPLIT MS1 HEATING COIL Heating Capacity [kBtu/hr] | SPLIT MS1 HEATING COIL Heating Capacity [kBtu/hr] | 10.7875 | 10.7875 | 11.6902 | 11.8159 | [6 empty] | 2021-05-06
MD_MA_SPLIT MS2 HEATING COIL Heating Capacity [kBtu/hr] | SPLIT MS2 HEATING COIL Heating Capacity [kBtu/hr] | 10.7875 | 10.7875 | 11.6888 | 11.8145 | [6 empty] | 2021-05-06
MD_MA_SPLIT TSW HEATING COIL Heating Capacity [kBtu/hr] | SPLIT TSW HEATING COIL Heating Capacity [kBtu/hr] | 10.6517 | 10.7132 | 11.9759 | 12.0378 | [6 empty] | 2021-05-06
MD_MA_SPLIT TNW HEATING COIL Heating Capacity [kBtu/hr] | SPLIT TNW HEATING COIL Heating Capacity [kBtu/hr] | 10.6948 | 10.7564 | 11.9464 | 12.0084 | [6 empty] | 2021-05-06
MD_MA_SPLIT TSE HEATING COIL Heating Capacity [kBtu/hr] | SPLIT TSE HEATING COIL Heating Capacity [kBtu/hr] | 10.6304 | 10.692 | 11.9484 | 12.0102 | [6 empty] | 2021-05-06
MD_MA_SPLIT TNE HEATING COIL Heating Capacity [kBtu/hr] | SPLIT TNE HEATING COIL Heating Capacity [kBtu/hr] | 10.6735 | 10.7352 | 11.9188 | 11.9807 | [6 empty] | 2021-05-06
MD_MA_SPLIT TN1 HEATING COIL Heating Capacity [kBtu/hr] | SPLIT TN1 HEATING COIL Heating Capacity [kBtu/hr] | 8.1153 | 8.1768 | 9.1686 | 9.2305 | [6 empty] | 2021-05-06
MD_MA_SPLIT TN2 HEATING COIL Heating Capacity [kBtu/hr] | SPLIT TN2 HEATING COIL Heating Capacity [kBtu/hr] | 8.1147 | 8.1761 | 9.1678 | 9.2296 | [6 empty] | 2021-05-06
MD_MA_SPLIT TS1 HEATING COIL Heating Capacity [kBtu/hr] | SPLIT TS1 HEATING COIL Heating Capacity [kBtu/hr] | 8.0648 | 8.1262 | 9.1922 | 9.254 | [6 empty] | 2021-05-06
MD_MA_SPLIT TS2 HEATING COIL Heating Capacity [kBtu/hr] | SPLIT TS2 HEATING COIL Heating Capacity [kBtu/hr] | 8.0642 | 8.1256 | 9.1915 | 9.2532 | [6 empty] | 2021-05-06
MD_MA_Split_GSW ERV Flag | Split_GSW ERV Flag | Yes | Yes | Yes | Yes | [6 empty] | 2021-05-06
MD_MA_Split_GNW ERV Flag | Split_GNW ERV Flag | Yes | Yes | Yes | Yes | [6 empty] | 2021-05-06
MD_MA_Split_GNE ERV Flag | Split_GNE ERV Flag | Yes | Yes | Yes | Yes | [6 empty] | 2021-05-06
MD_MA_Split_GN1 ERV Flag | Split_GN1 ERV Flag | Yes | Yes | Yes | Yes | [6 empty] | 2021-05-06
MD_MA_Split_GN2 ERV Flag | Split_GN2 ERV Flag | Yes | Yes | Yes | Yes | [6 empty] | 2021-05-06
MD_MA_Split_GS1 ERV Flag | Split_GS1 ERV Flag | Yes | Yes | Yes | Yes | [6 empty] | 2021-05-06
MD_MA_Split_GS2 ERV Flag | Split_GS2 ERV Flag | Yes | Yes | Yes | Yes | [6 empty] | 2021-05-06
MD_MA_Split_MSW ERV Flag | Split_MSW ERV Flag | Yes | Yes | Yes | Yes | [6 empty] | 2021-05-06
MD_MA_Split_MNW ERV Flag | Split_MNW ERV Flag | Yes | Yes | Yes | Yes | [6 empty] | 2021-05-06
MD_MA_Split_MSE ERV Flag | Split_MSE ERV Flag | Yes | Yes | Yes | Yes | [6 empty] | 2021-05-06
MD_MA_Split_MNE ERV Flag | Split_MNE ERV Flag | Yes | Yes | Yes | Yes | [6 empty] | 2021-05-06
MD_MA_Split_MN1 ERV Flag | Split_MN1 ERV Flag | Yes | Yes | Yes | Yes | [6 empty] | 2021-05-06
MD_MA_Split_MN2 ERV Flag | Split_MN2 ERV Flag | Yes | Yes | Yes | Yes | [6 empty] | 2021-05-06
MD_MA_Split_MS1 ERV Flag | Split_MS1 ERV Flag | Yes | Yes | Yes | Yes | [6 empty] | 2021-05-06
MD_MA_Split_MS2 ERV Flag | Split_MS2 ERV Flag | Yes | Yes | Yes | Yes | [6 empty] | 2021-05-06
MD_MA_Split_TSW ERV Flag | Split_TSW ERV Flag | Yes | Yes | Yes | Yes | [6 empty] | 2021-05-06
MD_MA_Split_TNW ERV Flag | Split_TNW ERV Flag | Yes | Yes | Yes | Yes | [6 empty] | 2021-05-06
MD_MA_Split_TSE ERV Flag | Split_TSE ERV Flag | Yes | Yes | Yes | Yes | [6 empty] | 2021-05-06
MD_MA_Split_TNE ERV Flag | Split_TNE ERV Flag | Yes | Yes | Yes | Yes | [6 empty] | 2021-05-06
MD_MA_Split_TN1 ERV Flag | Split_TN1 ERV Flag | Yes | Yes | Yes | Yes | [6 empty] | 2021-05-06
MD_MA_Split_TN2 ERV Flag | Split_TN2 ERV Flag | Yes | Yes | Yes | Yes | [6 empty] | 2021-05-06
MD_MA_Split_TS1 ERV Flag | Split_TS1 ERV Flag | Yes | Yes | Yes | Yes | [6 empty] | 2021-05-06
MD_MA_Split_TS2 ERV Flag | Split_TS2 ERV Flag | Yes | Yes | Yes | Yes | [6 empty] | 2021-05-06
id | item | Zone6A(ME-Bangor-ME) ASHRAE901-state_STD2016 | Zone6A(ME-Bangor-ME) ASHRAE901-state_STD2019 | Zone7(ME-Caribou-ME) ASHRAE901-state_STD2016 | Zone7(ME-Caribou-ME) ASHRAE901-state_STD2019 | [6 empty] | 2021-05-06
ME_SO_PSZ-AC:1 Cooling Capacity [ton] | PSZ-AC:1 Cooling Capacity [ton] | 1.6695 | 1.5713 | 1.5726 | 1.4678 | [6 empty] | 2021-05-06
ME_SO_PSZ-AC:2 Cooling Capacity [ton] | PSZ-AC:2 Cooling Capacity [ton] | 1.4261 | 1.3466 | 1.3761 | 1.2454 | [6 empty] | 2021-05-06
ME_SO_PSZ-AC:3 Cooling Capacity [ton] | PSZ-AC:3 Cooling Capacity [ton] | 0.98826 | 0.92792 | 1.0259 | 0.91396 | [6 empty] | 2021-05-06
ME_SO_PSZ-AC:4 Cooling Capacity [ton] | PSZ-AC:4 Cooling Capacity [ton] | 1.3193 | 1.2284 | 1.2032 | 1.0968 | [6 empty] | 2021-05-06
ME_SO_PSZ-AC:5 Cooling Capacity [ton] | PSZ-AC:5 Cooling Capacity [ton] | 1.2208 | 1.1556 | 1.2239 | 1.1116 | [6 empty] | 2021-05-06
ME_SO_PSZ-AC:1 Supply Flow Rate [cfm] | PSZ-AC:1 Supply Flow Rate [cfm] | 635.664 | 593.2864 | 635.664 | 572.0976 | [6 empty] | 2021-05-06
ME_SO_PSZ-AC:2 Supply Flow Rate [cfm] | PSZ-AC:2 Supply Flow Rate [cfm] | 550.9088 | 508.5312 | 550.9088 | 487.3424 | [6 empty] | 2021-05-06
ME_SO_PSZ-AC:3 Supply Flow Rate [cfm] | PSZ-AC:3 Supply Flow Rate [cfm] | 444.9648 | 402.5872 | 466.1536 | 402.5872 | [6 empty] | 2021-05-06
ME_SO_PSZ-AC:4 Supply Flow Rate [cfm] | PSZ-AC:4 Supply Flow Rate [cfm] | 487.3424 | 444.9648 | 466.1536 | 423.776 | [6 empty] | 2021-05-06
ME_SO_PSZ-AC:5 Supply Flow Rate [cfm] | PSZ-AC:5 Supply Flow Rate [cfm] | 529.72 | 487.3424 | 550.9088 | 487.3424 | [6 empty] | 2021-05-06
ME_SO_PSZ-AC:1 OA Rate [cfm] | PSZ-AC:1 OA Rate [cfm] | 136.9178 | 136.9178 | 136.9178 | 136.9178 | [6 empty] | 2021-05-06
ME_SO_PSZ-AC:2 OA Rate [cfm] | PSZ-AC:2 OA Rate [cfm] | 103.7925 | 103.7925 | 103.7925 | 103.7925 | [6 empty] | 2021-05-06
ME_SO_PSZ-AC:3 OA Rate [cfm] | PSZ-AC:3 OA Rate [cfm] | 61.5711 | 61.5711 | 61.5711 | 61.5711 | [6 empty] | 2021-05-06
ME_SO_PSZ-AC:4 OA Rate [cfm] | PSZ-AC:4 OA Rate [cfm] | 103.7925 | 103.7925 | 103.7925 | 103.7925 | [6 empty] | 2021-05-06
ME_SO_PSZ-AC:5 OA Rate [cfm] | PSZ-AC:5 OA Rate [cfm] | 61.5711 | 61.5711 | 61.5711 | 61.5711 | [6 empty] | 2021-05-06
ME_SO_PSZ-AC:1 heating Capacity [kBtu/hr] | PSZ-AC:1 heating Capacity [kBtu/hr] | 16.407 | 16.407 | 17.2172 | 17.2172 | [6 empty] | 2021-05-06
ME_SO_PSZ-AC:2 heating Capacity [kBtu/hr] | PSZ-AC:2 heating Capacity [kBtu/hr] | 22.1707 | 21.9137 | 23.811 | 23.2253 | [6 empty] | 2021-05-06
ME_SO_PSZ-AC:3 heating Capacity [kBtu/hr] | PSZ-AC:3 heating Capacity [kBtu/hr] | 13.4687 | 13.3268 | 14.5339 | 14.2105 | [6 empty] | 2021-05-06
ME_SO_PSZ-AC:4 heating Capacity [kBtu/hr] | PSZ-AC:4 heating Capacity [kBtu/hr] | 22.0894 | 21.8715 | 23.8 | 23.3033 | [6 empty] | 2021-05-06
ME_SO_PSZ-AC:5 heating Capacity [kBtu/hr] | PSZ-AC:5 heating Capacity [kBtu/hr] | 13.5221 | 13.3749 | 14.5928 | 14.2571 | [6 empty] | 2021-05-06
id | item | Zone6A(ME-Bangor-ME) ASHRAE901-state_STD2016 | Zone6A(ME-Bangor-ME) ASHRAE901-state_STD2019 | Zone7(ME-Caribou-ME) ASHRAE901-state_STD2016 | Zone7(ME-Caribou-ME) ASHRAE901-state_STD2019 | [6 empty] | 2021-05-06
ME_LO_CAV_BAS Supply Flow Rate [cfm] | CAV_BAS Supply Flow Rate [cfm] | 11632.6512 | 10742.7216 | 11886.9168 | 10975.7984 | [6 empty] | 2021-05-06
ME_LO_VAV_BOT WITH REHEAT Supply Flow Rate [cfm] | VAV_BOT WITH REHEAT Supply Flow Rate [cfm] | 19747.9616 | 18667.3328 | 20447.192 | 19112.2976 | [6 empty] | 2021-05-06
ME_LO_VAV_MID WITH REHEAT Supply Flow Rate [cfm] | VAV_MID WITH REHEAT Supply Flow Rate [cfm] | 184278.9939 | 173705.7827 | 191652.6963 | 178113.0531 | [6 empty] | 2021-05-06
ME_LO_VAV_TOP WITH REHEAT Supply Flow Rate [cfm] | VAV_TOP WITH REHEAT Supply Flow Rate [cfm] | 19175.864 | 18158.8016 | 19536.0736 | 18052.8576 | [6 empty] | 2021-05-06
ME_LO_Supply Air Temp. Reset Flag | Supply Air Temp. Reset Flag | Yes | Yes | Yes | Yes | [6 empty] | 2021-05-06
ME_LO_CAV_BAS OA Rate [cfm] | CAV_BAS OA Rate [cfm] | 2542.8255 | 2542.8255 | 2542.8255 | 2542.8255 | [6 empty] | 2021-05-06
ME_LO_VAV_BOT WITH REHEAT OA Rate [cfm] | VAV_BOT WITH REHEAT OA Rate [cfm] | 5377.8022 | 4302.174 | 5377.8022 | 4302.174 | [6 empty] | 2021-05-06
ME_LO_VAV_MID WITH REHEAT OA Rate [cfm] | VAV_MID WITH REHEAT OA Rate [cfm] | 53777.9373 | 43021.7396 | 53777.9373 | 43021.7396 | [6 empty] | 2021-05-06
ME_LO_VAV_TOP WITH REHEAT OA Rate [cfm] | VAV_TOP WITH REHEAT OA Rate [cfm] | 5377.8022 | 4302.174 | 5377.8022 | 4302.174 | [6 empty] | 2021-05-06
ME_LO_AIRLOOP DATACENTER BASEMENT OA Rate [cfm] | AIRLOOP DATACENTER BASEMENT OA Rate [cfm] | 716.9654 | 716.9654 | 716.9654 | 716.9654 | [6 empty] | 2021-05-06
ME_LO_VAV_bot_WITH_REHEAT ERV Flag | VAV_bot_WITH_REHEAT ERV Flag | Yes | Yes | Yes | Yes | [6 empty] | 2021-05-06
ME_LO_VAV_mid_WITH_REHEAT ERV Flag | VAV_mid_WITH_REHEAT ERV Flag | Yes | Yes | Yes | Yes | [6 empty] | 2021-05-06
ME_LO_VAV_top_WITH_REHEAT ERV Flag | VAV_top_WITH_REHEAT ERV Flag | Yes | Yes | Yes | Yes | [6 empty] | 2021-05-06
ME_LO_COOLSYS1 CHILLER1 Capacity [ton] | COOLSYS1 CHILLER1 Capacity [ton] | 371.988 | 337.9058 | 356.3263 | 323.6675 | [6 empty] | 2021-05-06
ME_LO_COOLSYS1 CHILLER2 Capacity [ton] | COOLSYS1 CHILLER2 Capacity [ton] | 371.988 | 337.9058 | 356.3263 | 323.6675 | [6 empty] | 2021-05-06
ME_LO_TOWERWATERSYS COOLTOWER 1 Capacity [ton] | TOWERWATERSYS COOLTOWER 1 Capacity [ton] | 353.1915 | 320.8241 | 338.4014 | 307.3917 | [6 empty] | 2021-05-06
ME_LO_TOWERWATERSYS COOLTOWER 2 Capacity [ton] | TOWERWATERSYS COOLTOWER 2 Capacity [ton] | 353.1915 | 320.8241 | 338.4014 | 307.3917 | [6 empty] | 2021-05-06
ME_LO_HEATSYS1 BOILER Capacity [MMBTU/h] | HEATSYS1 BOILER Capacity [MMBTU/h] | 5045.7131 | 4433.3463 | 5323.5484 | 4614.7539 | [6 empty] | 2021-05-06
ME_LO_COOLSYS1 PUMP Flow Rate [gal/min] | COOLSYS1 PUMP Flow Rate [gal/min] | 0 | 0 | 0 | 0 | [6 empty] | 2021-05-06
ME_LO_COOLSYS1 CHILLER1 PUMP Flow Rate [gal/min] | COOLSYS1 CHILLER1 PUMP Flow Rate [gal/min] | 585.8898 | 532.1239 | 560.9762 | 509.5261 | [6 empty] | 2021-05-06
ME_LO_COOLSYS1 CHILLER2 PUMP Flow Rate [gal/min] | COOLSYS1 CHILLER2 PUMP Flow Rate [gal/min] | 585.8898 | 532.1239 | 560.9762 | 509.5261 | [6 empty] | 2021-05-06
ME_LO_COOLSYS1 PUMP SECONDARY Flow Rate [gal/min] | COOLSYS1 PUMP SECONDARY Flow Rate [gal/min] | 1171.7779 | 1064.2478 | 1121.9509 | 1019.0521 | [6 empty] | 2021-05-06
ME_LO_HEATSYS1 PUMP Flow Rate [gal/min] | HEATSYS1 PUMP Flow Rate [gal/min] | 1035.6997 | 910.0035 | 1092.7292 | 947.2391 | [6 empty] | 2021-05-06
ME_LO_TOWERWATERSYS PUMP Flow Rate [gal/min] | TOWERWATERSYS PUMP Flow Rate [gal/min] | 2052.2998 | 1864.315 | 1965.9156 | 1785.6974 | [6 empty] | 2021-05-06
ME_LO_PLANT CIRC PUMP Flow Rate [gal/min] | PLANT CIRC PUMP Flow Rate [gal/min] | 207.8405 | 206.6961 | 209.5207 | 207.896 | [6 empty] | 2021-05-06
ME_LO_COOLSYS1 PUMP SECONDARY Pressure setpoint reset [yes,no] | COOLSYS1 PUMP SECONDARY Pressure setpoint reset [yes,no] | pump_ride_on_curve | pump_ride_on_curve | pump_ride_on_curve | pump_ride_on_curve | [6 empty] | 2021-05-06
ME_LO_COOLSYS1 CHILLER1 PUMP Pump Power [hp] | COOLSYS1 CHILLER1 PUMP Pump Power [hp] | 3.1607 | 2.8422 | 3.0263 | 2.7215 | [6 empty] | 2021-05-06
ME_LO_COOLSYS1 CHILLER2 PUMP Pump Power [hp] | COOLSYS1 CHILLER2 PUMP Pump Power [hp] | 3.1607 | 2.8422 | 3.0263 | 2.7215 | [6 empty] | 2021-05-06
ME_LO_COOLSYS1 PUMP SECONDARY Pump Power [hp] | COOLSYS1 PUMP SECONDARY Pump Power [hp] | 18.964 | 17.0532 | 18.1576 | 16.329 | [6 empty] | 2021-05-06
ME_LO_HEATSYS1 PUMP Pump Power [hp] | HEATSYS1 PUMP Pump Power [hp] | 22.3872 | 19.4755 | 23.62 | 20.2724 | [6 empty] | 2021-05-06
ME_LO_TOWERWATERSYS PUMP Pump Power [hp] | TOWERWATERSYS PUMP Pump Power [hp] | 36.7442 | 33.0472 | 35.1972 | 31.6547 | [6 empty] | 2021-05-06
ME_LO_PLANT CIRC PUMP Pump Power [hp] | PLANT CIRC PUMP Pump Power [hp] | 4.4849 | 4.416 | 4.5211 | 4.4417 | [6 empty] | 2021-05-06
ME_LO_Datacenter PLANT CIRC PUMP Pump Power [hp] | Datacenter PLANT CIRC PUMP Pump Power [hp] | 4.4849 | 4.416 | 4.5211 | 4.4417 | [6 empty] | 2021-05-06
ME_LO_ZN_VAV_BOXes_Max_Reheat_Water_Flow_GPM | ZN_VAV_BOXes_Max_Reheat_Water_Flow_GPM | 489.4745 | 469.9023 | 502.0317 | 470.1108 | [6 empty] | 2021-05-06
ME_LO_COOLSYS1 PUMP SECONDARY VSD | COOLSYS1 PUMP SECONDARY VSD | No | No | No | No | [6 empty] | 2021-05-06
ME_LO_HEATSYS1 PUMP VSD | HEATSYS1 PUMP VSD | No | No | No | No | [6 empty] | 2021-05-06
ME_LO_DATACENTER BASEMENT Cooling Capacity [ton] | DATACENTER BASEMENT Cooling Capacity [ton] | 121.2168 | 120.8467 | 121.6358 | 121.2984 | [6 empty] | 2021-05-06
ME_LO_DATACENTER BOT Cooling Capacity [ton] | DATACENTER BOT Cooling Capacity [ton] | 2.6835 | 2.6434 | 2.7475 | 2.6781 | [6 empty] | 2021-05-06
ME_LO_DATACENTER MID Cooling Capacity [ton] | DATACENTER MID Cooling Capacity [ton] | 25.7295 | 25.3401 | 26.4165 | 25.7047 | [6 empty] | 2021-05-06
ME_LO_DATACENTER TOP Cooling Capacity [ton] | DATACENTER TOP Cooling Capacity [ton] | 2.6173 | 2.5788 | 2.678 | 2.6069 | [6 empty] | 2021-05-06
id | item | Zone6A(ME-Bangor-ME) ASHRAE901-state_STD2016 | Zone6A(ME-Bangor-ME) ASHRAE901-state_STD2019 | Zone7(ME-Caribou-ME) ASHRAE901-state_STD2016 | Zone7(ME-Caribou-ME) ASHRAE901-state_STD2019 | [6 empty] | 2021-05-06
ME_RS_PSZ-AC:1 Cooling Capacity [ton] | PSZ-AC:1 Cooling Capacity [ton] | 9.3084 | 8.8488 | 8.8431 | 8.3871 | [6 empty] | 2021-05-06
ME_RS_PSZ-AC:2 Cooling Capacity [ton] | PSZ-AC:2 Cooling Capacity [ton] | 43.8625 | 42.7352 | 41.3453 | 39.8207 | [6 empty] | 2021-05-06
ME_RS_PSZ-AC:3 Cooling Capacity [ton] | PSZ-AC:3 Cooling Capacity [ton] | 5.7134 | 5.5547 | 5.4949 | 5.2522 | [6 empty] | 2021-05-06
ME_RS_PSZ-AC:4 Cooling Capacity [ton] | PSZ-AC:4 Cooling Capacity [ton] | 4.5421 | 4.3588 | 4.4625 | 4.0819 | [6 empty] | 2021-05-06
ME_RS_PSZ-AC:1 Supply Flow Rate [cfm] | PSZ-AC:1 Supply Flow Rate [cfm] | 3686.8512 | 3390.208 | 3602.096 | 3284.264 | [6 empty] | 2021-05-06
ME_RS_PSZ-AC:2 Supply Flow Rate [cfm] | PSZ-AC:2 Supply Flow Rate [cfm] | 15086.4256 | 14281.2512 | 15065.2368 | 14281.2512 | [6 empty] | 2021-05-06
ME_RS_PSZ-AC:3 Supply Flow Rate [cfm] | PSZ-AC:3 Supply Flow Rate [cfm] | 2203.6352 | 2140.0688 | 2267.2016 | 2140.0688 | [6 empty] | 2021-05-06
ME_RS_PSZ-AC:4 Supply Flow Rate [cfm] | PSZ-AC:4 Supply Flow Rate [cfm] | 1652.7264 | 1567.9712 | 1758.6704 | 1567.9712 | [6 empty] | 2021-05-06
ME_RS_PSZ-AC:1 OA Rate [cfm] | PSZ-AC:1 OA Rate [cfm] | 490.669 | 490.669 | 490.669 | 490.669 | [6 empty] | 2021-05-06
ME_RS_PSZ-AC:2 OA Rate [cfm] | PSZ-AC:2 OA Rate [cfm] | 4005.1282 | 4005.1282 | 4005.1282 | 4005.1282 | [6 empty] | 2021-05-06
ME_RS_PSZ-AC:3 OA Rate [cfm] | PSZ-AC:3 OA Rate [cfm] | 377.3937 | 377.3937 | 377.3937 | 377.3937 | [6 empty] | 2021-05-06
ME_RS_PSZ-AC:4 OA Rate [cfm] | PSZ-AC:4 OA Rate [cfm] | 377.3937 | 377.3937 | 377.3937 | 377.3937 | [6 empty] | 2021-05-06
ME_RS_PSZ-AC:1 OA Damper [gravity, motorized] | PSZ-AC:1 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2021-05-06
ME_RS_PSZ-AC:2 OA Damper [gravity, motorized] | PSZ-AC:2 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2021-05-06
ME_RS_PSZ-AC:3 OA Damper [gravity, motorized] | PSZ-AC:3 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2021-05-06
ME_RS_PSZ-AC:4 OA Damper [gravity, motorized] | PSZ-AC:4 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2021-05-06
ME_RS_PSZ-AC:1 Heating Capacity [kBtu/hr] | PSZ-AC:1 Heating Capacity [kBtu/hr] | 174.4878 | 161.7326 | 171.722 | 163.651 | [6 empty] | 2021-05-06
ME_RS_PSZ-AC:2 Heating Capacity [kBtu/hr] | PSZ-AC:2 Heating Capacity [kBtu/hr] | 872.5944 | 839.8368 | 889.835 | 857.8166 | [6 empty] | 2021-05-06
ME_RS_PSZ-AC:3 Heating Capacity [kBtu/hr] | PSZ-AC:3 Heating Capacity [kBtu/hr] | 112.8564 | 109.8114 | 114.5433 | 111.0313 | [6 empty] | 2021-05-06
ME_RS_PSZ-AC:4 Heating Capacity [kBtu/hr] | PSZ-AC:4 Heating Capacity [kBtu/hr] | 91.8893 | 88.1658 | 97.3377 | 88.8164 | [6 empty] | 2021-05-06
id | item | Zone6A(ME-Bangor-ME) ASHRAE901-state_STD2016 | Zone6A(ME-Bangor-ME) ASHRAE901-state_STD2019 | Zone7(ME-Caribou-ME) ASHRAE901-state_STD2016 | Zone7(ME-Caribou-ME) ASHRAE901-state_STD2019 | [6 empty] | 2021-05-06
ME_PS_VAV_POD_1 Cooling Capacity [ton] | VAV_POD_1 Cooling Capacity [ton] | 18.7256 | 18.1338 | 18.9541 | 18.0214 | [6 empty] | 2021-05-06
ME_PS_VAV_POD_2 Cooling Capacity [ton] | VAV_POD_2 Cooling Capacity [ton] | 18.5708 | 18.0851 | 18.7036 | 17.969 | [6 empty] | 2021-05-06
ME_PS_VAV_POD_3 Cooling Capacity [ton] | VAV_POD_3 Cooling Capacity [ton] | 16.9998 | 16.037 | 17.1992 | 15.9264 | [6 empty] | 2021-05-06
ME_PS_VAV_OTHER Cooling Capacity [ton] | VAV_OTHER Cooling Capacity [ton] | 25.669 | 22.8914 | 23.6585 | 20.7147 | [6 empty] | 2021-05-06
ME_PS_PSZ-AC_1:6 Cooling Capacity [ton] | PSZ-AC_1:6 Cooling Capacity [ton] | 7.6608 | 7.3838 | 7.3875 | 7.0837 | [6 empty] | 2021-05-06
ME_PS_PSZ-AC_2:5 Cooling Capacity [ton] | PSZ-AC_2:5 Cooling Capacity [ton] | 5.242 | 5.1622 | 5.4988 | 5.435 | [6 empty] | 2021-05-06
ME_PS_PSZ-AC_2:7 Cooling Capacity [ton] | PSZ-AC_2:7 Cooling Capacity [ton] | 10.5074 | 10.5074 | 10.5074 | 10.5074 | [6 empty] | 2021-05-06
ME_PS_VAV_POD_1 Supply Flow Rate [cfm] | VAV_POD_1 Supply Flow Rate [cfm] | 5615.032 | 5445.5216 | 5678.5984 | 5403.144 | [6 empty] | 2021-05-06
ME_PS_VAV_POD_2 Supply Flow Rate [cfm] | VAV_POD_2 Supply Flow Rate [cfm] | 5572.6544 | 5424.3328 | 5615.032 | 5381.9552 | [6 empty] | 2021-05-06
ME_PS_VAV_POD_3 Supply Flow Rate [cfm] | VAV_POD_3 Supply Flow Rate [cfm] | 5106.5008 | 4809.8576 | 5170.0672 | 4788.6688 | [6 empty] | 2021-05-06
ME_PS_VAV_OTHER Supply Flow Rate [cfm] | VAV_OTHER Supply Flow Rate [cfm] | 7712.7232 | 7119.4368 | 7649.1568 | 6886.36 | [6 empty] | 2021-05-06
ME_PS_PSZ-AC_2:5 Supply Flow Rate [cfm] | PSZ-AC_2:5 Supply Flow Rate [cfm] | 1567.9712 | 1546.7824 | 1652.7264 | 1631.5376 | [6 empty] | 2021-05-06
ME_PS_PSZ-AC_1:6 Supply Flow Rate [cfm] | PSZ-AC_1:6 Supply Flow Rate [cfm] | 2521.4672 | 2415.5232 | 2563.8448 | 2415.5232 | [6 empty] | 2021-05-06
ME_PS_PSZ-AC_2:7 Supply Flow Rate [cfm] | PSZ-AC_2:7 Supply Flow Rate [cfm] | 3157.1312 | 3157.1312 | 3157.1312 | 3157.1312 | [6 empty] | 2021-05-06
ME_PS_Supply Air Temp. Reset Flag | Supply Air Temp. Reset Flag | Yes | Yes | Yes | Yes | [6 empty] | 2021-05-06
ME_PS_VAV_POD_1 OA Rate [cfm] | VAV_POD_1 OA Rate [cfm] | 5617.1297 | 5441.6652 | 5685.5695 | 5407.9115 | [6 empty] | 2021-05-06
ME_PS_VAV_POD_2 OA Rate [cfm] | VAV_POD_2 OA Rate [cfm] | 5572.8027 | 5427.0238 | 5611.4087 | 5392.1894 | [6 empty] | 2021-05-06
ME_PS_VAV_POD_3 OA Rate [cfm] | VAV_POD_3 OA Rate [cfm] | 5100.4832 | 4812.4426 | 5158.5829 | 4779.261 | [6 empty] | 2021-05-06
ME_PS_VAV_OTHER OA Rate [cfm] | VAV_OTHER OA Rate [cfm] | 3736.1787 | 2988.8921 | 3736.1787 | 2988.8921 | [6 empty] | 2021-05-06
ME_PS_PSZ-AC_2:5 OA Rate [cfm] | PSZ-AC_2:5 OA Rate [cfm] | 1152.7343 | 1152.7343 | 1152.7343 | 1152.7343 | [6 empty] | 2021-05-06
ME_PS_PSZ-AC_1:6 OA Rate [cfm] | PSZ-AC_1:6 OA Rate [cfm] | 539.9118 | 539.9118 | 539.9118 | 539.9118 | [6 empty] | 2021-05-06
ME_PS_PSZ-AC_2:7 OA Rate [cfm] | PSZ-AC_2:7 OA Rate [cfm] | 3153.0841 | 3153.0841 | 3153.0841 | 3153.0841 | [6 empty] | 2021-05-06
ME_PS_VAV_POD_1 OA Damper [gravity, motorized] | VAV_POD_1 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2021-05-06
ME_PS_VAV_POD_2 OA Damper [gravity, motorized] | VAV_POD_2 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2021-05-06
ME_PS_VAV_POD_3 OA Damper [gravity, motorized] | VAV_POD_3 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2021-05-06
ME_PS_VAV_OTHER OA Damper [gravity, motorized] | VAV_OTHER OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2021-05-06
ME_PS_PSZ-AC_2:5 OA Damper [gravity, motorized] | PSZ-AC_2:5 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2021-05-06
ME_PS_PSZ-AC_1:6 OA Damper [gravity, motorized] | PSZ-AC_1:6 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2021-05-06
ME_PS_PSZ-AC_2:7 OA Damper [gravity, motorized] | PSZ-AC_2:7 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2021-05-06
ME_PS_VAV_POD_1 (economizer) | VAV_POD_1 (economizer) | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | [6 empty] | 2021-05-06
ME_PS_VAV_POD_2 (economizer) | VAV_POD_2 (economizer) | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | [6 empty] | 2021-05-06
ME_PS_VAV_POD_3 (economizer) | VAV_POD_3 (economizer) | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | [6 empty] | 2021-05-06
ME_PS_VAV_OTHER (economizer) | VAV_OTHER (economizer) | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | [6 empty] | 2021-05-06
ME_PS_PSZ-AC_2:5 (economizer) | PSZ-AC_2:5 (economizer) | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | [6 empty] | 2021-05-06
ME_PS_PSZ-AC_1:6 (economizer) | PSZ-AC_1:6 (economizer) | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | [6 empty] | 2021-05-06
ME_PS_PSZ-AC_2:7 (economizer) | PSZ-AC_2:7 (economizer) | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | [6 empty] | 2021-05-06
ME_PS_VAV_Pod_1_ERV Flag | VAV_Pod_1_ERV Flag | Yes | Yes | Yes | Yes | [6 empty] | 2021-05-06
ME_PS_VAV_Pod_2_ERV Flag | VAV_Pod_2_ERV Flag | Yes | Yes | Yes | Yes | [6 empty] | 2021-05-06
ME_PS_VAV_Pod_3_ERV Flag | VAV_Pod_3_ERV Flag | Yes | Yes | Yes | Yes | [6 empty] | 2021-05-06
ME_PS_VAV_OTHER_ERV Flag | VAV_OTHER_ERV Flag | Yes | Yes | Yes | Yes | [6 empty] | 2021-05-06
ME_PS_PSZ_AC_2_5_ERV Flag | PSZ_AC_2_5_ERV Flag | Yes | Yes | Yes | Yes | [6 empty] | 2021-05-06
ME_PS_PSZ_AC_2_7_ERV Flag | PSZ_AC_2_7_ERV Flag | Yes | Yes | Yes | Yes | [6 empty] | 2021-05-06
ME_PS_HEATSYS1 Capacity [MMBTU/h] | HEATSYS1 Capacity [MMBTU/h] | 1.2205 | 1.1709 | 1.2899 | 1.2134 | [6 empty] | 2021-05-06
ME_PS_HEATSYS1 Flow Rate [gal/min] | HEATSYS1 Flow Rate [gal/min] | 125.2651 | 120.1668 | 132.3828 | 124.5289 | [6 empty] | 2021-05-06
ME_PS_VAV_POD_1 Fan Power [hp] | VAV_POD_1 Fan Power [hp] | 8.2901 | 8.0281 | 8.3912 | 7.9783 | [6 empty] | 2021-05-06
ME_PS_VAV_POD_2 Fan Power [hp] | VAV_POD_2 Fan Power [hp] | 8.2216 | 8.0065 | 8.2803 | 7.9551 | [6 empty] | 2021-05-06
ME_PS_VAV_POD_3 Fan Power [hp] | VAV_POD_3 Fan Power [hp] | 7.526 | 7.0998 | 7.6143 | 7.0508 | [6 empty] | 2021-05-06
ME_PS_VAV_OTHER Fan Power [hp] | VAV_OTHER Fan Power [hp] | 11.2779 | 10.4347 | 11.2071 | 10.0907 | [6 empty] | 2021-05-06
ME_PS_HEATSYS1 Pump Power [hp] | HEATSYS1 Pump Power [hp] | 2.7077 | 2.5718 | 2.8615 | 2.6651 | [6 empty] | 2021-05-06
ME_PS_PSZ-AC_1:6 Heating Capacity [kBtu/hr] | PSZ-AC_1:6 Heating Capacity [kBtu/hr] | 218.5176 | 209.2804 | 221.8351 | 211.5746 | [6 empty] | 2021-05-06
ME_PS_PSZ-AC_2:5 Heating Capacity [kBtu/hr] | PSZ-AC_2:5 Heating Capacity [kBtu/hr] | 153.5932 | 152.7127 | 162.9605 | 162.268 | [6 empty] | 2021-05-06
ME_PS_PSZ-AC_2:7 Heating Capacity [kBtu/hr] | PSZ-AC_2:7 Heating Capacity [kBtu/hr] | 377.8376 | 377.8376 | 396.4967 | 396.4967 | [6 empty] | 2021-05-06
ME_PS_ZN_VAV_BOXes_Max_Reheat_Water_Flow_GPM | ZN_VAV_BOXes_Max_Reheat_Water_Flow_GPM | 75.634 | 72.9933 | 77.4919 | 73.3816 | [6 empty] | 2021-05-06
id | item | Zone6A(ME-Bangor-ME) ASHRAE901-state_STD2016 | Zone6A(ME-Bangor-ME) ASHRAE901-state_STD2019 | Zone7(ME-Caribou-ME) ASHRAE901-state_STD2016 | Zone7(ME-Caribou-ME) ASHRAE901-state_STD2019 | [6 empty] | 2021-05-06
ME_SH_SAC_FRONTOFFICE Cooling Capacity [ton] | SAC_FRONTOFFICE Cooling Capacity [ton] | 2.056 | 1.9449 | 1.9393 | 1.8201 | [6 empty] | 2021-05-06
ME_SH_SAC_FRONTLOUNGE Cooling Capacity [ton] | SAC_FRONTLOUNGE Cooling Capacity [ton] | 5.6183 | 5.3897 | 5.2662 | 5.0287 | [6 empty] | 2021-05-06
ME_SH_SAC_MEETINGROOM Cooling Capacity [ton] | SAC_MEETINGROOM Cooling Capacity [ton] | 2.807 | 2.712 | 2.731 | 2.662 | [6 empty] | 2021-05-06
ME_SH_SAC_EXC_EMPLGE_RESTRM Cooling Capacity [ton] | SAC_EXC_EMPLGE_RESTRM Cooling Capacity [ton] | 5.5692 | 5.523 | 5.4123 | 5.3336 | [6 empty] | 2021-05-06
ME_SH_SAC_FO_ADDAQ SUPPLY FAN Supply Flow Rate [cfm] | SAC_FO_ADDAQ SUPPLY FAN Supply Flow Rate [cfm] | 741.608 | 678.0416 | 741.608 | 678.0416 | [6 empty] | 2021-05-06
ME_SH_SAC_FL_ADDAQ SUPPLY FAN Supply Flow Rate [cfm] | SAC_FL_ADDAQ SUPPLY FAN Supply Flow Rate [cfm] | 1758.6704 | 1652.7264 | 1758.6704 | 1652.7264 | [6 empty] | 2021-05-06
ME_SH_SAC_MR_ADDAQ SUPPLY FAN Supply Flow Rate [cfm] | SAC_MR_ADDAQ SUPPLY FAN Supply Flow Rate [cfm] | 847.552 | 805.1744 | 847.552 | 805.1744 | [6 empty] | 2021-05-06
ME_SH_SAC_EXC_ADDAQ SUPPLY FAN Supply Flow Rate [cfm] | SAC_EXC_ADDAQ SUPPLY FAN Supply Flow Rate [cfm] | 2161.2576 | 2140.0688 | 2203.6352 | 2161.2576 | [6 empty] | 2021-05-06
ME_SH_SAC_Exc_EmpLge_RestRm OA Rate [cfm] | SAC_Exc_EmpLge_RestRm OA Rate [cfm] | 199.9928 | 199.9928 | 199.9928 | 199.9928 | [6 empty] | 2021-05-06
ME_SH_SAC_FrontLounge OA Rate [cfm] | SAC_FrontLounge OA Rate [cfm] | 500.0133 | 500.0133 | 500.0133 | 500.0133 | [6 empty] | 2021-05-06
ME_SH_SAC_FrontOffice OA Rate [cfm] | SAC_FrontOffice OA Rate [cfm] | 119.2938 | 119.2938 | 119.2938 | 119.2938 | [6 empty] | 2021-05-06
ME_SH_SAC_MeetingRoom OA Rate [cfm] | SAC_MeetingRoom OA Rate [cfm] | 267.7629 | 267.7629 | 267.7629 | 267.7629 | [6 empty] | 2021-05-06
ME_SH_SAC_FrontLounge OA Damper [gravity, motorized] | SAC_FrontLounge OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2021-05-06
ME_SH_SAC_FrontOffice (economizer) | SAC_FrontOffice (economizer) | No | No | No | No | [6 empty] | 2021-05-06
ME_SH_SAC_FrontLounge (economizer) | SAC_FrontLounge (economizer) | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | [6 empty] | 2021-05-06
ME_SH_SAC_MeetingRoom (economizer) | SAC_MeetingRoom (economizer) | No | No | No | No | [6 empty] | 2021-05-06
ME_SH_SAC_Exc_EmpLge_RestRm (economizer) | SAC_Exc_EmpLge_RestRm (economizer) | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | [6 empty] | 2021-05-06
ME_SH_SAC_FRONTOFFICE Heating Capacity [kBtu/hr] | SAC_FRONTOFFICE Heating Capacity [kBtu/hr] | 36.7997 | 34.9922 | 37.0807 | 35.0901 | [6 empty] | 2021-05-06
ME_SH_SAC_FRONTLOUNGE Heating Capacity [kBtu/hr] | SAC_FRONTLOUNGE Heating Capacity [kBtu/hr] | 105.8378 | 102.3818 | 107.901 | 104.2282 | [6 empty] | 2021-05-06
ME_SH_SAC_MEETINGROOM Heating Capacity [kBtu/hr] | SAC_MEETINGROOM Heating Capacity [kBtu/hr] | 53.0957 | 52.053 | 54.2894 | 53.2842 | [6 empty] | 2021-05-06
ME_SH_SAC_EXC_EMPLGE_RESTRM Heating Capacity [kBtu/hr] | SAC_EXC_EMPLGE_RESTRM Heating Capacity [kBtu/hr] | 95.7757 | 95.0225 | 96.9848 | 96.0283 | [6 empty] | 2021-05-06
id | item | Zone6A(ME-Bangor-ME) ASHRAE901-state_STD2016 | Zone6A(ME-Bangor-ME) ASHRAE901-state_STD2019 | Zone7(ME-Caribou-ME) ASHRAE901-state_STD2016 | Zone7(ME-Caribou-ME) ASHRAE901-state_STD2019 | [6 empty] | 2021-05-06
ME_MA_SPLIT GSW COOLING COIL Cooling Capacity [ton] | SPLIT GSW COOLING COIL Cooling Capacity [ton] | 0.73779 | 0.70636 | 0.70459 | 0.64421 | [6 empty] | 2021-05-06
ME_MA_SPLIT GNW COOLING COIL Cooling Capacity [ton] | SPLIT GNW COOLING COIL Cooling Capacity [ton] | 0.68395 | 0.65799 | 0.63699 | 0.58881 | [6 empty] | 2021-05-06
ME_MA_SPLIT OFFICE COOLING COIL Cooling Capacity [ton] | SPLIT OFFICE COOLING COIL Cooling Capacity [ton] | 1.6028 | 1.4508 | 1.6008 | 1.3632 | [6 empty] | 2021-05-06
ME_MA_SPLIT GNE COOLING COIL Cooling Capacity [ton] | SPLIT GNE COOLING COIL Cooling Capacity [ton] | 0.58089 | 0.56011 | 0.52647 | 0.48898 | [6 empty] | 2021-05-06
ME_MA_SPLIT GN1 COOLING COIL Cooling Capacity [ton] | SPLIT GN1 COOLING COIL Cooling Capacity [ton] | 0.49563 | 0.48167 | 0.44963 | 0.42535 | [6 empty] | 2021-05-06
ME_MA_SPLIT GN2 COOLING COIL Cooling Capacity [ton] | SPLIT GN2 COOLING COIL Cooling Capacity [ton] | 0.49353 | 0.47971 | 0.44722 | 0.42325 | [6 empty] | 2021-05-06
ME_MA_SPLIT GS1 COOLING COIL Cooling Capacity [ton] | SPLIT GS1 COOLING COIL Cooling Capacity [ton] | 0.55057 | 0.53318 | 0.51568 | 0.48245 | [6 empty] | 2021-05-06
ME_MA_SPLIT GS2 COOLING COIL Cooling Capacity [ton] | SPLIT GS2 COOLING COIL Cooling Capacity [ton] | 0.58505 | 0.56289 | 0.54939 | 0.51126 | [6 empty] | 2021-05-06
ME_MA_SPLIT MSW COOLING COIL Cooling Capacity [ton] | SPLIT MSW COOLING COIL Cooling Capacity [ton] | 1.8439 | 1.7733 | 1.8329 | 1.6858 | [6 empty] | 2021-05-06
ME_MA_SPLIT MNW COOLING COIL Cooling Capacity [ton] | SPLIT MNW COOLING COIL Cooling Capacity [ton] | 1.7402 | 1.6764 | 1.7009 | 1.5807 | [6 empty] | 2021-05-06
ME_MA_SPLIT MSE COOLING COIL Cooling Capacity [ton] | SPLIT MSE COOLING COIL Cooling Capacity [ton] | 1.6096 | 1.5455 | 1.6276 | 1.4756 | [6 empty] | 2021-05-06
ME_MA_SPLIT MNE COOLING COIL Cooling Capacity [ton] | SPLIT MNE COOLING COIL Cooling Capacity [ton] | 1.3795 | 1.3175 | 1.3624 | 1.2483 | [6 empty] | 2021-05-06
ME_MA_SPLIT MN1 COOLING COIL Cooling Capacity [ton] | SPLIT MN1 COOLING COIL Cooling Capacity [ton] | 1.1424 | 1.1149 | 1.0807 | 1.0274 | [6 empty] | 2021-05-06
ME_MA_SPLIT MN2 COOLING COIL Cooling Capacity [ton] | SPLIT MN2 COOLING COIL Cooling Capacity [ton] | 1.1362 | 1.1092 | 1.0697 | 1.0213 | [6 empty] | 2021-05-06
ME_MA_SPLIT MS1 COOLING COIL Cooling Capacity [ton] | SPLIT MS1 COOLING COIL Cooling Capacity [ton] | 1.234 | 1.2014 | 1.2922 | 1.1794 | [6 empty] | 2021-05-06
ME_MA_SPLIT MS2 COOLING COIL Cooling Capacity [ton] | SPLIT MS2 COOLING COIL Cooling Capacity [ton] | 1.279 | 1.1955 | 1.2973 | 1.1839 | [6 empty] | 2021-05-06
ME_MA_SPLIT TSW COOLING COIL Cooling Capacity [ton] | SPLIT TSW COOLING COIL Cooling Capacity [ton] | 1.154 | 1.1142 | 1.1187 | 1.0347 | [6 empty] | 2021-05-06
ME_MA_SPLIT TNW COOLING COIL Cooling Capacity [ton] | SPLIT TNW COOLING COIL Cooling Capacity [ton] | 1.0854 | 1.0489 | 1.0379 | 0.96715 | [6 empty] | 2021-05-06
ME_MA_SPLIT TSE COOLING COIL Cooling Capacity [ton] | SPLIT TSE COOLING COIL Cooling Capacity [ton] | 1.0283 | 0.99305 | 1.0121 | 0.92565 | [6 empty] | 2021-05-06
ME_MA_SPLIT TNE COOLING COIL Cooling Capacity [ton] | SPLIT TNE COOLING COIL Cooling Capacity [ton] | 0.91028 | 0.88703 | 0.7957 | 0.78619 | [6 empty] | 2021-05-06
ME_MA_SPLIT TN1 COOLING COIL Cooling Capacity [ton] | SPLIT TN1 COOLING COIL Cooling Capacity [ton] | 0.74684 | 0.73066 | 0.64832 | 0.62297 | [6 empty] | 2021-05-06
ME_MA_SPLIT TN2 COOLING COIL Cooling Capacity [ton] | SPLIT TN2 COOLING COIL Cooling Capacity [ton] | 0.7479 | 0.73178 | 0.67337 | 0.646 | [6 empty] | 2021-05-06
ME_MA_SPLIT TS1 COOLING COIL Cooling Capacity [ton] | SPLIT TS1 COOLING COIL Cooling Capacity [ton] | 0.85283 | 0.82861 | 0.83874 | 0.77072 | [6 empty] | 2021-05-06
ME_MA_SPLIT TS2 COOLING COIL Cooling Capacity [ton] | SPLIT TS2 COOLING COIL Cooling Capacity [ton] | 0.85635 | 0.83174 | 0.84282 | 0.77439 | [6 empty] | 2021-05-06
ME_MA_Split GN1 Furnace with DX Cooling OA Rate [cfm] | Split GN1 Furnace with DX Cooling OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | [6 empty] | 2021-05-06
ME_MA_Split GN2 Furnace with DX Cooling OA Rate [cfm] | Split GN2 Furnace with DX Cooling OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | [6 empty] | 2021-05-06
ME_MA_Split GNE Furnace with DX Cooling OA Rate [cfm] | Split GNE Furnace with DX Cooling OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | [6 empty] | 2021-05-06
ME_MA_Split GNW Furnace with DX Cooling OA Rate [cfm] | Split GNW Furnace with DX Cooling OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | [6 empty] | 2021-05-06
ME_MA_Split GS1 Furnace with DX Cooling OA Rate [cfm] | Split GS1 Furnace with DX Cooling OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | [6 empty] | 2021-05-06
ME_MA_Split GS2 Furnace with DX Cooling OA Rate [cfm] | Split GS2 Furnace with DX Cooling OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | [6 empty] | 2021-05-06
ME_MA_Split GSW Furnace with DX Cooling OA Rate [cfm] | Split GSW Furnace with DX Cooling OA Rate [cfm] | 56.9945 | 56.9945 | 56.9945 | 56.9945 | [6 empty] | 2021-05-06
ME_MA_Split MN1 Furnace with DX Cooling OA Rate [cfm] | Split MN1 Furnace with DX Cooling OA Rate [cfm] | 109.9824 | 109.9824 | 109.9824 | 109.9824 | [6 empty] | 2021-05-06
ME_MA_Split MN2 Furnace with DX Cooling OA Rate [cfm] | Split MN2 Furnace with DX Cooling OA Rate [cfm] | 109.9824 | 109.9824 | 109.9824 | 109.9824 | [6 empty] | 2021-05-06
ME_MA_Split MNE Furnace with DX Cooling OA Rate [cfm] | Split MNE Furnace with DX Cooling OA Rate [cfm] | 109.9824 | 109.9824 | 109.9824 | 109.9824 | [6 empty] | 2021-05-06
ME_MA_Split MNW Furnace with DX Cooling OA Rate [cfm] | Split MNW Furnace with DX Cooling OA Rate [cfm] | 109.9824 | 109.9824 | 109.9824 | 109.9824 | [6 empty] | 2021-05-06
ME_MA_Split MS1 Furnace with DX Cooling OA Rate [cfm] | Split MS1 Furnace with DX Cooling OA Rate [cfm] | 109.9824 | 109.9824 | 109.9824 | 109.9824 | [6 empty] | 2021-05-06
ME_MA_Split MS2 Furnace with DX Cooling OA Rate [cfm] | Split MS2 Furnace with DX Cooling OA Rate [cfm] | 109.9824 | 109.9824 | 109.9824 | 109.9824 | [6 empty] | 2021-05-06
ME_MA_Split MSE Furnace with DX Cooling OA Rate [cfm] | Split MSE Furnace with DX Cooling OA Rate [cfm] | 109.9824 | 109.9824 | 109.9824 | 109.9824 | [6 empty] | 2021-05-06
ME_MA_Split MSW Furnace with DX Cooling OA Rate [cfm] | Split MSW Furnace with DX Cooling OA Rate [cfm] | 109.9824 | 109.9824 | 109.9824 | 109.9824 | [6 empty] | 2021-05-06
ME_MA_Split Office Furnace with DX Cooling OA Rate [cfm] | Split Office Furnace with DX Cooling OA Rate [cfm] | 80.7372 | 80.7372 | 80.7372 | 80.7372 | [6 empty] | 2021-05-06
ME_MA_Split TN1 Furnace with DX Cooling OA Rate [cfm] | Split TN1 Furnace with DX Cooling OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | [6 empty] | 2021-05-06
ME_MA_Split TN2 Furnace with DX Cooling OA Rate [cfm] | Split TN2 Furnace with DX Cooling OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | [6 empty] | 2021-05-06
ME_MA_Split TNE Furnace with DX Cooling OA Rate [cfm] | Split TNE Furnace with DX Cooling OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | [6 empty] | 2021-05-06
ME_MA_Split TNW Furnace with DX Cooling OA Rate [cfm] | Split TNW Furnace with DX Cooling OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | [6 empty] | 2021-05-06
ME_MA_Split TS1 Furnace with DX Cooling OA Rate [cfm] | Split TS1 Furnace with DX Cooling OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | [6 empty] | 2021-05-06
ME_MA_Split TS2 Furnace with DX Cooling OA Rate [cfm] | Split TS2 Furnace with DX Cooling OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | [6 empty] | 2021-05-06
ME_MA_Split TSE Furnace with DX Cooling OA Rate [cfm] | Split TSE Furnace with DX Cooling OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | [6 empty] | 2021-05-06
ME_MA_Split TSW Furnace with DX Cooling OA Rate [cfm] | Split TSW Furnace with DX Cooling OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | [6 empty] | 2021-05-06
ME_MA_SPLIT GSW HEATING COIL Heating Capacity [kBtu/hr] | SPLIT GSW HEATING COIL Heating Capacity [kBtu/hr] | 10.888 | 10.9474 | 11.9195 | 11.8217 | [6 empty] | 2021-05-06
ME_MA_SPLIT GNW HEATING COIL Heating Capacity [kBtu/hr] | SPLIT GNW HEATING COIL Heating Capacity [kBtu/hr] | 10.7926 | 10.8521 | 11.8163 | 11.7144 | [6 empty] | 2021-05-06
ME_MA_SPLIT OFFICE HEATING COIL Heating Capacity [kBtu/hr] | SPLIT OFFICE HEATING COIL Heating Capacity [kBtu/hr] | 24.2597 | 24.3416 | 25.5308 | 25.4535 | [6 empty] | 2021-05-06
ME_MA_SPLIT GNE HEATING COIL Heating Capacity [kBtu/hr] | SPLIT GNE HEATING COIL Heating Capacity [kBtu/hr] | 10.7702 | 10.8297 | 11.7919 | 11.6928 | [6 empty] | 2021-05-06
ME_MA_SPLIT GN1 HEATING COIL Heating Capacity [kBtu/hr] | SPLIT GN1 HEATING COIL Heating Capacity [kBtu/hr] | 8.2209 | 8.2804 | 9.035 | 9.0035 | [6 empty] | 2021-05-06
ME_MA_SPLIT GN2 HEATING COIL Heating Capacity [kBtu/hr] | SPLIT GN2 HEATING COIL Heating Capacity [kBtu/hr] | 8.2202 | 8.2798 | 9.0343 | 9.0029 | [6 empty] | 2021-05-06
ME_MA_SPLIT GS1 HEATING COIL Heating Capacity [kBtu/hr] | SPLIT GS1 HEATING COIL Heating Capacity [kBtu/hr] | 8.1662 | 8.2256 | 8.9753 | 8.9479 | [6 empty] | 2021-05-06
ME_MA_SPLIT GS2 HEATING COIL Heating Capacity [kBtu/hr] | SPLIT GS2 HEATING COIL Heating Capacity [kBtu/hr] | 8.6837 | 8.744 | 9.4978 | 9.4725 | [6 empty] | 2021-05-06
ME_MA_SPLIT MSW HEATING COIL Heating Capacity [kBtu/hr] | SPLIT MSW HEATING COIL Heating Capacity [kBtu/hr] | 18.522 | 18.6506 | 20.3483 | 20.1078 | [6 empty] | 2021-05-06
ME_MA_SPLIT MNW HEATING COIL Heating Capacity [kBtu/hr] | SPLIT MNW HEATING COIL Heating Capacity [kBtu/hr] | 18.6142 | 18.7428 | 20.4473 | 20.1966 | [6 empty] | 2021-05-06
ME_MA_SPLIT MSE HEATING COIL Heating Capacity [kBtu/hr] | SPLIT MSE HEATING COIL Heating Capacity [kBtu/hr] | 18.4687 | 18.5974 | 20.2911 | 20.0574 | [6 empty] | 2021-05-06
ME_MA_SPLIT MNE HEATING COIL Heating Capacity [kBtu/hr] | SPLIT MNE HEATING COIL Heating Capacity [kBtu/hr] | 18.5609 | 18.6896 | 20.3901 | 20.1461 | [6 empty] | 2021-05-06
ME_MA_SPLIT MN1 HEATING COIL Heating Capacity [kBtu/hr] | SPLIT MN1 HEATING COIL Heating Capacity [kBtu/hr] | 13.3937 | 13.5205 | 14.7797 | 14.6672 | [6 empty] | 2021-05-06
ME_MA_SPLIT MN2 HEATING COIL Heating Capacity [kBtu/hr] | SPLIT MN2 HEATING COIL Heating Capacity [kBtu/hr] | 13.3923 | 13.5191 | 14.7782 | 14.6659 | [6 empty] | 2021-05-06
ME_MA_SPLIT MS1 HEATING COIL Heating Capacity [kBtu/hr] | SPLIT MS1 HEATING COIL Heating Capacity [kBtu/hr] | 13.3118 | 13.4385 | 14.6917 | 14.5895 | [6 empty] | 2021-05-06
ME_MA_SPLIT MS2 HEATING COIL Heating Capacity [kBtu/hr] | SPLIT MS2 HEATING COIL Heating Capacity [kBtu/hr] | 13.3104 | 13.4372 | 14.6902 | 14.5881 | [6 empty] | 2021-05-06
ME_MA_SPLIT TSW HEATING COIL Heating Capacity [kBtu/hr] | SPLIT TSW HEATING COIL Heating Capacity [kBtu/hr] | 13.1598 | 13.2219 | 14.1103 | 13.99 | [6 empty] | 2021-05-06
ME_MA_SPLIT TNW HEATING COIL Heating Capacity [kBtu/hr] | SPLIT TNW HEATING COIL Heating Capacity [kBtu/hr] | 13.2163 | 13.2785 | 14.1705 | 14.0451 | [6 empty] | 2021-05-06
ME_MA_SPLIT TSE HEATING COIL Heating Capacity [kBtu/hr] | SPLIT TSE HEATING COIL Heating Capacity [kBtu/hr] | 13.1313 | 13.1934 | 14.0798 | 13.9631 | [6 empty] | 2021-05-06
ME_MA_SPLIT TNE HEATING COIL Heating Capacity [kBtu/hr] | SPLIT TNE HEATING COIL Heating Capacity [kBtu/hr] | 13.1878 | 13.25 | 14.1398 | 14.0181 | [6 empty] | 2021-05-06
ME_MA_SPLIT TN1 HEATING COIL Heating Capacity [kBtu/hr] | SPLIT TN1 HEATING COIL Heating Capacity [kBtu/hr] | 10.4551 | 10.5172 | 11.0985 | 11.0402 | [6 empty] | 2021-05-06
ME_MA_SPLIT TN2 HEATING COIL Heating Capacity [kBtu/hr] | SPLIT TN2 HEATING COIL Heating Capacity [kBtu/hr] | 10.4543 | 10.5164 | 11.0976 | 11.0394 | [6 empty] | 2021-05-06
ME_MA_SPLIT TS1 HEATING COIL Heating Capacity [kBtu/hr] | SPLIT TS1 HEATING COIL Heating Capacity [kBtu/hr] | 10.3921 | 10.4541 | 11.032 | 10.9785 | [6 empty] | 2021-05-06
ME_MA_SPLIT TS2 HEATING COIL Heating Capacity [kBtu/hr] | SPLIT TS2 HEATING COIL Heating Capacity [kBtu/hr] | 10.3913 | 10.4533 | 11.0311 | 10.9777 | [6 empty] | 2021-05-06
ME_MA_Split_GSW ERV Flag | Split_GSW ERV Flag | Yes | Yes | Yes | Yes | [6 empty] | 2021-05-06
ME_MA_Split_GNW ERV Flag | Split_GNW ERV Flag | Yes | Yes | Yes | Yes | [6 empty] | 2021-05-06
ME_MA_Split_GNE ERV Flag | Split_GNE ERV Flag | Yes | Yes | Yes | Yes | [6 empty] | 2021-05-06
ME_MA_Split_GN1 ERV Flag | Split_GN1 ERV Flag | Yes | Yes | Yes | Yes | [6 empty] | 2021-05-06
ME_MA_Split_GN2 ERV Flag | Split_GN2 ERV Flag | Yes | Yes | Yes | Yes | [6 empty] | 2021-05-06
ME_MA_Split_GS1 ERV Flag | Split_GS1 ERV Flag | Yes | Yes | Yes | Yes | [6 empty] | 2021-05-06
ME_MA_Split_GS2 ERV Flag | Split_GS2 ERV Flag | Yes | Yes | Yes | Yes | [6 empty] | 2021-05-06
ME_MA_Split_MSW ERV Flag | Split_MSW ERV Flag | Yes | Yes | Yes | Yes | [6 empty] | 2021-05-06
ME_MA_Split_MNW ERV Flag | Split_MNW ERV Flag | Yes | Yes | Yes | Yes | [6 empty] | 2021-05-06
ME_MA_Split_MSE ERV Flag | Split_MSE ERV Flag | Yes | Yes | Yes | Yes | [6 empty] | 2021-05-06
ME_MA_Split_MNE ERV Flag | Split_MNE ERV Flag | Yes | Yes | Yes | Yes | [6 empty] | 2021-05-06
ME_MA_Split_MN1 ERV Flag | Split_MN1 ERV Flag | Yes | Yes | Yes | Yes | [6 empty] | 2021-05-06
ME_MA_Split_MN2 ERV Flag | Split_MN2 ERV Flag | Yes | Yes | Yes | Yes | [6 empty] | 2021-05-06
ME_MA_Split_MS1 ERV Flag | Split_MS1 ERV Flag | Yes | Yes | Yes | Yes | [6 empty] | 2021-05-06
ME_MA_Split_MS2 ERV Flag | Split_MS2 ERV Flag | Yes | Yes | Yes | Yes | [6 empty] | 2021-05-06
ME_MA_Split_TSW ERV Flag | Split_TSW ERV Flag | Yes | Yes | Yes | Yes | [6 empty] | 2021-05-06
ME_MA_Split_TNW ERV Flag | Split_TNW ERV Flag | Yes | Yes | Yes | Yes | [6 empty] | 2021-05-06
ME_MA_Split_TSE ERV Flag | Split_TSE ERV Flag | Yes | Yes | Yes | Yes | [6 empty] | 2021-05-06
ME_MA_Split_TNE ERV Flag | Split_TNE ERV Flag | Yes | Yes | Yes | Yes | [6 empty] | 2021-05-06
ME_MA_Split_TN1 ERV Flag | Split_TN1 ERV Flag | Yes | Yes | Yes | Yes | [6 empty] | 2021-05-06
ME_MA_Split_TN2 ERV Flag | Split_TN2 ERV Flag | Yes | Yes | Yes | Yes | [6 empty] | 2021-05-06
ME_MA_Split_TS1 ERV Flag | Split_TS1 ERV Flag | Yes | Yes | Yes | Yes | [6 empty] | 2021-05-06
ME_MA_Split_TS2 ERV Flag | Split_TS2 ERV Flag | Yes | Yes | Yes | Yes | [6 empty] | 2021-05-06
id | item | Zone5A(MI-Lansing-MI) ASHRAE901-state_STD2016 | Zone5A(MI-Lansing-MI) ASHRAE901-state_STD2019 | Zone6A(MI-AlpenaCounty-MI) ASHRAE901-state_STD2016 | Zone6A(MI-AlpenaCounty-MI) ASHRAE901-state_STD2019 | Zone7(MI-SaultSteMarie-MI) ASHRAE901-state_STD2016 | Zone7(MI-SaultSteMarie-MI) ASHRAE901-state_STD2019 |  |  |  |  | 2021-05-06
MI_SO_PSZ-AC:1 Cooling Capacity [ton] | PSZ-AC:1 Cooling Capacity [ton] | 1.7947 | 1.6975 | 1.712 | 1.6163 | 1.5845 | 1.483 |  |  |  |  | 2021-05-06
MI_SO_PSZ-AC:2 Cooling Capacity [ton] | PSZ-AC:2 Cooling Capacity [ton] | 1.5274 | 1.4651 | 1.4632 | 1.3856 | 1.3868 | 1.2504 |  |  |  |  | 2021-05-06
MI_SO_PSZ-AC:3 Cooling Capacity [ton] | PSZ-AC:3 Cooling Capacity [ton] | 1.101 | 1.0626 | 1.0638 | 1.0014 | 1.0418 | 0.94319 |  |  |  |  | 2021-05-06
MI_SO_PSZ-AC:4 Cooling Capacity [ton] | PSZ-AC:4 Cooling Capacity [ton] | 1.4541 | 1.3751 | 1.3577 | 1.2749 | 1.2101 | 1.1009 |  |  |  |  | 2021-05-06
MI_SO_PSZ-AC:5 Cooling Capacity [ton] | PSZ-AC:5 Cooling Capacity [ton] | 1.2827 | 1.2434 | 1.2517 | 1.1855 | 1.2256 | 1.1037 |  |  |  |  | 2021-05-06
MI_SO_PSZ-AC:1 Supply Flow Rate [cfm] | PSZ-AC:1 Supply Flow Rate [cfm] | 656.8528 | 614.4752 | 635.664 | 593.2864 | 635.664 | 572.0976 |  |  |  |  | 2021-05-06
MI_SO_PSZ-AC:2 Supply Flow Rate [cfm] | PSZ-AC:2 Supply Flow Rate [cfm] | 550.9088 | 529.72 | 550.9088 | 529.72 | 550.9088 | 487.3424 |  |  |  |  | 2021-05-06
MI_SO_PSZ-AC:3 Supply Flow Rate [cfm] | PSZ-AC:3 Supply Flow Rate [cfm] | 466.1536 | 444.9648 | 466.1536 | 423.776 | 466.1536 | 423.776 |  |  |  |  | 2021-05-06
MI_SO_PSZ-AC:4 Supply Flow Rate [cfm] | PSZ-AC:4 Supply Flow Rate [cfm] | 529.72 | 487.3424 | 508.5312 | 466.1536 | 466.1536 | 423.776 |  |  |  |  | 2021-05-06
MI_SO_PSZ-AC:5 Supply Flow Rate [cfm] | PSZ-AC:5 Supply Flow Rate [cfm] | 550.9088 | 529.72 | 550.9088 | 508.5312 | 550.9088 | 487.3424 |  |  |  |  | 2021-05-06
MI_SO_PSZ-AC:1 OA Rate [cfm] | PSZ-AC:1 OA Rate [cfm] | 136.9178 | 136.9178 | 136.9178 | 136.9178 | 136.9178 | 136.9178 |  |  |  |  | 2021-05-06
MI_SO_PSZ-AC:2 OA Rate [cfm] | PSZ-AC:2 OA Rate [cfm] | 103.7925 | 103.7925 | 103.7925 | 103.7925 | 103.7925 | 103.7925 |  |  |  |  | 2021-05-06
MI_SO_PSZ-AC:3 OA Rate [cfm] | PSZ-AC:3 OA Rate [cfm] | 61.5711 | 61.5711 | 61.5711 | 61.5711 | 61.5711 | 61.5711 |  |  |  |  | 2021-05-06
MI_SO_PSZ-AC:4 OA Rate [cfm] | PSZ-AC:4 OA Rate [cfm] | 103.7925 | 103.7925 | 103.7925 | 103.7925 | 103.7925 | 103.7925 |  |  |  |  | 2021-05-06
MI_SO_PSZ-AC:5 OA Rate [cfm] | PSZ-AC:5 OA Rate [cfm] | 61.5711 | 61.5711 | 61.5711 | 61.5711 | 61.5711 | 61.5711 |  |  |  |  | 2021-05-06
MI_SO_PSZ-AC:1 heating Capacity [kBtu/hr] | PSZ-AC:1 heating Capacity [kBtu/hr] | 15.2965 | 15.2965 | 15.849 | 15.849 | 16.6379 | 16.6379 |  |  |  |  | 2021-05-06
MI_SO_PSZ-AC:2 heating Capacity [kBtu/hr] | PSZ-AC:2 heating Capacity [kBtu/hr] | 21.3559 | 21.109 | 21.4543 | 21.1961 | 22.4348 | 21.8576 |  |  |  |  | 2021-05-06
MI_SO_PSZ-AC:3 heating Capacity [kBtu/hr] | PSZ-AC:3 heating Capacity [kBtu/hr] | 12.9283 | 12.7972 | 12.9778 | 12.8398 | 13.6669 | 13.3478 |  |  |  |  | 2021-05-06
MI_SO_PSZ-AC:4 heating Capacity [kBtu/hr] | PSZ-AC:4 heating Capacity [kBtu/hr] | 21.1431 | 20.9412 | 21.2814 | 21.0703 | 22.3212 | 21.8495 |  |  |  |  | 2021-05-06
MI_SO_PSZ-AC:5 heating Capacity [kBtu/hr] | PSZ-AC:5 heating Capacity [kBtu/hr] | 12.9862 | 12.8496 | 13.0253 | 12.8826 | 13.6174 | 13.3089 |  |  |  |  | 2021-05-06
id | item | Zone5A(MI-Lansing-MI) ASHRAE901-state_STD2016 | Zone5A(MI-Lansing-MI) ASHRAE901-state_STD2019 | Zone6A(MI-AlpenaCounty-MI) ASHRAE901-state_STD2016 | Zone6A(MI-AlpenaCounty-MI) ASHRAE901-state_STD2019 | Zone7(MI-SaultSteMarie-MI) ASHRAE901-state_STD2016 | Zone7(MI-SaultSteMarie-MI) ASHRAE901-state_STD2019 |  |  |  |  | 2021-05-06
MI_LO_CAV_BAS Supply Flow Rate [cfm] | CAV_BAS Supply Flow Rate [cfm] | 11865.728 | 10975.7984 | 11844.5392 | 10933.4208 | 11886.9168 | 10975.7984 |  |  |  |  | 2021-05-06
MI_LO_VAV_BOT WITH REHEAT Supply Flow Rate [cfm] | VAV_BOT WITH REHEAT Supply Flow Rate [cfm] | 19705.584 | 18773.2768 | 19726.7728 | 18624.9552 | 20002.2272 | 18688.5216 |  |  |  |  | 2021-05-06
MI_LO_VAV_MID WITH REHEAT Supply Flow Rate [cfm] | VAV_MID WITH REHEAT Supply Flow Rate [cfm] | 182223.6803 | 173154.8739 | 182456.7571 | 171819.9795 | 185190.1123 | 172307.3219 |  |  |  |  | 2021-05-06
MI_LO_VAV_TOP WITH REHEAT Supply Flow Rate [cfm] | VAV_TOP WITH REHEAT Supply Flow Rate [cfm] | 19430.1296 | 18646.144 | 19366.5632 | 18349.5008 | 19281.808 | 17819.7808 |  |  |  |  | 2021-05-06
MI_LO_Supply Air Temp. Reset Flag | Supply Air Temp. Reset Flag | Yes | Yes | Yes | Yes | Yes | Yes |  |  |  |  | 2021-05-06
MI_LO_CAV_BAS OA Rate [cfm] | CAV_BAS OA Rate [cfm] | 2542.8255 | 2542.8255 | 2542.8255 | 2542.8255 | 2542.8255 | 2542.8255 |  |  |  |  | 2021-05-06
MI_LO_VAV_BOT WITH REHEAT OA Rate [cfm] | VAV_BOT WITH REHEAT OA Rate [cfm] | 5377.8022 | 4302.174 | 5377.8022 | 4302.174 | 5377.8022 | 4302.174 |  |  |  |  | 2021-05-06
MI_LO_VAV_MID WITH REHEAT OA Rate [cfm] | VAV_MID WITH REHEAT OA Rate [cfm] | 53777.9373 | 43021.7396 | 53777.9373 | 43021.7396 | 53777.9373 | 43021.7396 |  |  |  |  | 2021-05-06
MI_LO_VAV_TOP WITH REHEAT OA Rate [cfm] | VAV_TOP WITH REHEAT OA Rate [cfm] | 5377.8022 | 4302.174 | 5377.8022 | 4302.174 | 5377.8022 | 4302.174 |  |  |  |  | 2021-05-06
MI_LO_AIRLOOP DATACENTER BASEMENT OA Rate [cfm] | AIRLOOP DATACENTER BASEMENT OA Rate [cfm] | 716.9654 | 716.9654 | 716.9654 | 716.9654 | 716.9654 | 716.9654 |  |  |  |  | 2021-05-06
MI_LO_VAV_bot_WITH_REHEAT ERV Flag | VAV_bot_WITH_REHEAT ERV Flag | Yes | Yes | Yes | Yes | Yes | Yes |  |  |  |  | 2021-05-06
MI_LO_VAV_mid_WITH_REHEAT ERV Flag | VAV_mid_WITH_REHEAT ERV Flag | Yes | Yes | Yes | Yes | Yes | Yes |  |  |  |  | 2021-05-06
MI_LO_VAV_top_WITH_REHEAT ERV Flag | VAV_top_WITH_REHEAT ERV Flag | Yes | Yes | Yes | Yes | Yes | Yes |  |  |  |  | 2021-05-06
MI_LO_COOLSYS1 CHILLER1 Capacity [ton] | COOLSYS1 CHILLER1 Capacity [ton] | 397.0129 | 358.674 | 377.711 | 341.556 | 361.33 | 323.226 |  |  |  |  | 2021-05-06
MI_LO_COOLSYS1 CHILLER2 Capacity [ton] | COOLSYS1 CHILLER2 Capacity [ton] | 397.0129 | 358.674 | 377.711 | 341.556 | 361.33 | 323.226 |  |  |  |  | 2021-05-06
MI_LO_TOWERWATERSYS COOLTOWER 1 Capacity [ton] | TOWERWATERSYS COOLTOWER 1 Capacity [ton] | 376.8372 | 340.4491 | 358.5452 | 324.228 | 343.1229 | 306.9418 |  |  |  |  | 2021-05-06
MI_LO_TOWERWATERSYS COOLTOWER 2 Capacity [ton] | TOWERWATERSYS COOLTOWER 2 Capacity [ton] | 376.8372 | 340.4491 | 358.5452 | 324.228 | 343.1229 | 306.9418 |  |  |  |  | 2021-05-06
MI_LO_HEATSYS1 BOILER Capacity [MMBTU/h] | HEATSYS1 BOILER Capacity [MMBTU/h] | 4830.5647 | 4267.6526 | 4880.6658 | 4290.8653 | 5085.2189 | 4407.2023 |  |  |  |  | 2021-05-06
MI_LO_COOLSYS1 PUMP Flow Rate [gal/min] | COOLSYS1 PUMP Flow Rate [gal/min] | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 2021-05-06
MI_LO_COOLSYS1 CHILLER1 PUMP Flow Rate [gal/min] | COOLSYS1 CHILLER1 PUMP Flow Rate [gal/min] | 625.4997 | 564.98 | 594.9482 | 537.9045 | 568.9886 | 508.8873 |  |  |  |  | 2021-05-06
MI_LO_COOLSYS1 CHILLER2 PUMP Flow Rate [gal/min] | COOLSYS1 CHILLER2 PUMP Flow Rate [gal/min] | 625.4997 | 564.98 | 594.9482 | 537.9045 | 568.9886 | 508.8873 |  |  |  |  | 2021-05-06
MI_LO_COOLSYS1 PUMP SECONDARY Flow Rate [gal/min] | COOLSYS1 PUMP SECONDARY Flow Rate [gal/min] | 1250.9994 | 1129.9584 | 1189.8964 | 1075.8074 | 1137.9771 | 1017.7746 |  |  |  |  | 2021-05-06
MI_LO_HEATSYS1 PUMP Flow Rate [gal/min] | HEATSYS1 PUMP Flow Rate [gal/min] | 991.5376 | 875.9919 | 1001.8213 | 880.7565 | 1043.8088 | 904.6366 |  |  |  |  | 2021-05-06
MI_LO_TOWERWATERSYS PUMP Flow Rate [gal/min] | TOWERWATERSYS PUMP Flow Rate [gal/min] | 2190.3562 | 1978.7543 | 2083.842 | 1884.4449 | 1993.4951 | 1783.3199 |  |  |  |  | 2021-05-06
MI_LO_PLANT CIRC PUMP Flow Rate [gal/min] | PLANT CIRC PUMP Flow Rate [gal/min] | 210.7507 | 209.9058 | 210.0564 | 208.8692 | 210.3481 | 208.6124 |  |  |  |  | 2021-05-06
MI_LO_COOLSYS1 PUMP SECONDARY Pressure setpoint reset [yes,no] | COOLSYS1 PUMP SECONDARY Pressure setpoint reset [yes,no] | pump_ride_on_curve | pump_ride_on_curve | pump_ride_on_curve | pump_ride_on_curve | pump_ride_on_curve | pump_ride_on_curve |  |  |  |  | 2021-05-06
MI_LO_COOLSYS1 CHILLER1 PUMP Pump Power [hp] | COOLSYS1 CHILLER1 PUMP Pump Power [hp] | 3.3743 | 3.0177 | 3.2095 | 2.8731 | 3.0695 | 2.7181 |  |  |  |  | 2021-05-06
MI_LO_COOLSYS1 CHILLER2 PUMP Pump Power [hp] | COOLSYS1 CHILLER2 PUMP Pump Power [hp] | 3.3743 | 3.0177 | 3.2095 | 2.8731 | 3.0695 | 2.7181 |  |  |  |  | 2021-05-06
MI_LO_COOLSYS1 PUMP SECONDARY Pump Power [hp] | COOLSYS1 PUMP SECONDARY Pump Power [hp] | 20.2461 | 18.1061 | 19.2572 | 17.2384 | 18.417 | 16.3085 |  |  |  |  | 2021-05-06
MI_LO_HEATSYS1 PUMP Pump Power [hp] | HEATSYS1 PUMP Pump Power [hp] | 21.4326 | 18.7476 | 21.6549 | 18.8496 | 22.5625 | 19.3606 |  |  |  |  | 2021-05-06
MI_LO_TOWERWATERSYS PUMP Pump Power [hp] | TOWERWATERSYS PUMP Pump Power [hp] | 39.2161 | 35.0783 | 37.3095 | 33.4042 | 35.6914 | 31.6115 |  |  |  |  | 2021-05-06
MI_LO_PLANT CIRC PUMP Pump Power [hp] | PLANT CIRC PUMP Pump Power [hp] | 4.5477 | 4.4846 | 4.5327 | 4.4625 | 4.539 | 4.457 |  |  |  |  | 2021-05-06
MI_LO_Datacenter PLANT CIRC PUMP Pump Power [hp] | Datacenter PLANT CIRC PUMP Pump Power [hp] | 4.5477 | 4.4846 | 4.5327 | 4.4625 | 4.539 | 4.457 |  |  |  |  | 2021-05-06
MI_LO_ZN_VAV_BOXes_Max_Reheat_Water_Flow_GPM | ZN_VAV_BOXes_Max_Reheat_Water_Flow_GPM | 492.0615 | 473.5664 | 476.3418 | 457.7797 | 478.8964 | 448.8648 |  |  |  |  | 2021-05-06
MI_LO_COOLSYS1 PUMP SECONDARY VSD | COOLSYS1 PUMP SECONDARY VSD | No | No | No | No | No | No |  |  |  |  | 2021-05-06
MI_LO_HEATSYS1 PUMP VSD | HEATSYS1 PUMP VSD | No | No | No | No | No | No |  |  |  |  | 2021-05-06
MI_LO_DATACENTER BASEMENT Cooling Capacity [ton] | DATACENTER BASEMENT Cooling Capacity [ton] | 122.8381 | 122.4746 | 122.2862 | 121.913 | 122.0285 | 121.6392 |  |  |  |  | 2021-05-06
MI_LO_DATACENTER BOT Cooling Capacity [ton] | DATACENTER BOT Cooling Capacity [ton] | 2.7269 | 2.7031 | 2.7298 | 2.6875 | 2.765 | 2.6934 |  |  |  |  | 2021-05-06
MI_LO_DATACENTER MID Cooling Capacity [ton] | DATACENTER MID Cooling Capacity [ton] | 26.154 | 25.943 | 26.1913 | 25.7782 | 26.596 | 25.8594 |  |  |  |  | 2021-05-06
MI_LO_DATACENTER TOP Cooling Capacity [ton] | DATACENTER TOP Cooling Capacity [ton] | 2.6605 | 2.6401 | 2.6633 | 2.6226 | 2.6949 | 2.6214 |  |  |  |  | 2021-05-06
id | item | Zone5A(MI-Lansing-MI) ASHRAE901-state_STD2016 | Zone5A(MI-Lansing-MI) ASHRAE901-state_STD2019 | Zone6A(MI-AlpenaCounty-MI) ASHRAE901-state_STD2016 | Zone6A(MI-AlpenaCounty-MI) ASHRAE901-state_STD2019 | Zone7(MI-SaultSteMarie-MI) ASHRAE901-state_STD2016 | Zone7(MI-SaultSteMarie-MI) ASHRAE901-state_STD2019 |  |  |  |  | 2021-05-06
MI_RS_PSZ-AC:1 Cooling Capacity [ton] | PSZ-AC:1 Cooling Capacity [ton] | 9.8246 | 9.3523 | 9.3089 | 8.8521 | 8.7633 | 8.3083 |  |  |  |  | 2021-05-06
MI_RS_PSZ-AC:2 Cooling Capacity [ton] | PSZ-AC:2 Cooling Capacity [ton] | 47.4902 | 45.3105 | 44.6577 | 43.1304 | 41.8497 | 40.0983 |  |  |  |  | 2021-05-06
MI_RS_PSZ-AC:3 Cooling Capacity [ton] | PSZ-AC:3 Cooling Capacity [ton] | 6.0267 | 5.866 | 5.7207 | 5.5573 | 5.4955 | 5.1713 |  |  |  |  | 2021-05-06
MI_RS_PSZ-AC:4 Cooling Capacity [ton] | PSZ-AC:4 Cooling Capacity [ton] | 4.8591 | 4.7032 | 4.6583 | 4.4573 | 4.4639 | 4.0935 |  |  |  |  | 2021-05-06
MI_RS_PSZ-AC:1 Supply Flow Rate [cfm] | PSZ-AC:1 Supply Flow Rate [cfm] | 3792.7952 | 3474.9632 | 3665.6624 | 3347.8304 | 3474.9632 | 3157.1312 |  |  |  |  | 2021-05-06
MI_RS_PSZ-AC:2 Supply Flow Rate [cfm] | PSZ-AC:2 Supply Flow Rate [cfm] | 15255.936 | 14281.2512 | 14938.104 | 14154.1184 | 14705.0272 | 13878.664 |  |  |  |  | 2021-05-06
MI_RS_PSZ-AC:3 Supply Flow Rate [cfm] | PSZ-AC:3 Supply Flow Rate [cfm] | 2203.6352 | 2118.88 | 2161.2576 | 2076.5024 | 2182.4464 | 2034.1248 |  |  |  |  | 2021-05-06
MI_RS_PSZ-AC:4 Supply Flow Rate [cfm] | PSZ-AC:4 Supply Flow Rate [cfm] | 1652.7264 | 1589.16 | 1652.7264 | 1546.7824 | 1695.104 | 1504.4048 |  |  |  |  | 2021-05-06
MI_RS_PSZ-AC:1 OA Rate [cfm] | PSZ-AC:1 OA Rate [cfm] | 490.669 | 490.669 | 490.669 | 490.669 | 490.669 | 490.669 |  |  |  |  | 2021-05-06
MI_RS_PSZ-AC:2 OA Rate [cfm] | PSZ-AC:2 OA Rate [cfm] | 4005.1282 | 4005.1282 | 4005.1282 | 4005.1282 | 4005.1282 | 4005.1282 |  |  |  |  | 2021-05-06
MI_RS_PSZ-AC:3 OA Rate [cfm] | PSZ-AC:3 OA Rate [cfm] | 377.3937 | 377.3937 | 377.3937 | 377.3937 | 377.3937 | 377.3937 |  |  |  |  | 2021-05-06
MI_RS_PSZ-AC:4 OA Rate [cfm] | PSZ-AC:4 OA Rate [cfm] | 377.3937 | 377.3937 | 377.3937 | 377.3937 | 377.3937 | 377.3937 |  |  |  |  | 2021-05-06
MI_RS_PSZ-AC:1 OA Damper [gravity, motorized] | PSZ-AC:1 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | motorized | motorized |  |  |  |  | 2021-05-06
MI_RS_PSZ-AC:2 OA Damper [gravity, motorized] | PSZ-AC:2 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | motorized | motorized |  |  |  |  | 2021-05-06
MI_RS_PSZ-AC:3 OA Damper [gravity, motorized] | PSZ-AC:3 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | motorized | motorized |  |  |  |  | 2021-05-06
MI_RS_PSZ-AC:4 OA Damper [gravity, motorized] | PSZ-AC:4 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | motorized | motorized |  |  |  |  | 2021-05-06
MI_RS_PSZ-AC:1 Heating Capacity [kBtu/hr] | PSZ-AC:1 Heating Capacity [kBtu/hr] | 171.4919 | 158.6959 | 168.877 | 155.9655 | 163.8092 | 156.1726 |  |  |  |  | 2021-05-06
MI_RS_PSZ-AC:2 Heating Capacity [kBtu/hr] | PSZ-AC:2 Heating Capacity [kBtu/hr] | 836.1964 | 797.9734 | 842.6818 | 811.01 | 856.8241 | 823.6375 |  |  |  |  | 2021-05-06
MI_RS_PSZ-AC:3 Heating Capacity [kBtu/hr] | PSZ-AC:3 Heating Capacity [kBtu/hr] | 107.5307 | 104.8349 | 108.1006 | 105.1748 | 111.415 | 105.5498 |  |  |  |  | 2021-05-06
MI_RS_PSZ-AC:4 Heating Capacity [kBtu/hr] | PSZ-AC:4 Heating Capacity [kBtu/hr] | 86.6914 | 83.3863 | 89.8043 | 86.363 | 93.129 | 86.6364 |  |  |  |  | 2021-05-06
id | item | Zone5A(MI-Lansing-MI) ASHRAE901-state_STD2016 | Zone5A(MI-Lansing-MI) ASHRAE901-state_STD2019 | Zone6A(MI-AlpenaCounty-MI) ASHRAE901-state_STD2016 | Zone6A(MI-AlpenaCounty-MI) ASHRAE901-state_STD2019 | Zone7(MI-SaultSteMarie-MI) ASHRAE901-state_STD2016 | Zone7(MI-SaultSteMarie-MI) ASHRAE901-state_STD2019 |  |  |  |  | 2021-05-06
MI_PS_VAV_POD_1 Cooling Capacity [ton] | VAV_POD_1 Cooling Capacity [ton] | 18.9911 | 18.3797 | 18.8941 | 18.2096 | 18.7372 | 17.8945 |  |  |  |  | 2021-05-06
MI_PS_VAV_POD_2 Cooling Capacity [ton] | VAV_POD_2 Cooling Capacity [ton] | 18.8 | 18.3341 | 18.6812 | 18.1669 | 18.584 | 17.8467 |  |  |  |  | 2021-05-06
MI_PS_VAV_POD_3 Cooling Capacity [ton] | VAV_POD_3 Cooling Capacity [ton] | 17.3172 | 16.4587 | 17.2108 | 16.1463 | 17.0044 | 15.7992 |  |  |  |  | 2021-05-06
MI_PS_VAV_OTHER Cooling Capacity [ton] | VAV_OTHER Cooling Capacity [ton] | 26.5441 | 24.9167 | 26.1714 | 24.2018 | 24.6637 | 21.4861 |  |  |  |  | 2021-05-06
MI_PS_PSZ-AC_1:6 Cooling Capacity [ton] | PSZ-AC_1:6 Cooling Capacity [ton] | 8.2043 | 7.942 | 7.8989 | 7.6188 | 7.5421 | 7.23 |  |  |  |  | 2021-05-06
MI_PS_PSZ-AC_2:5 Cooling Capacity [ton] | PSZ-AC_2:5 Cooling Capacity [ton] | 5.4776 | 5.4512 | 5.3852 | 5.3053 | 5.5169 | 5.4544 |  |  |  |  | 2021-05-06
MI_PS_PSZ-AC_2:7 Cooling Capacity [ton] | PSZ-AC_2:7 Cooling Capacity [ton] | 10.5074 | 10.5074 | 10.5074 | 10.5074 | 10.5074 | 10.5074 |  |  |  |  | 2021-05-06
MI_PS_VAV_POD_1 Supply Flow Rate [cfm] | VAV_POD_1 Supply Flow Rate [cfm] | 5699.7872 | 5509.088 | 5678.5984 | 5466.7104 | 5615.032 | 5360.7664 |  |  |  |  | 2021-05-06
MI_PS_VAV_POD_2 Supply Flow Rate [cfm] | VAV_POD_2 Supply Flow Rate [cfm] | 5636.2208 | 5509.088 | 5615.032 | 5445.5216 | 5572.6544 | 5360.7664 |  |  |  |  | 2021-05-06
MI_PS_VAV_POD_3 Supply Flow Rate [cfm] | VAV_POD_3 Supply Flow Rate [cfm] | 5191.256 | 4936.9904 | 5170.0672 | 4852.2352 | 5106.5008 | 4746.2912 |  |  |  |  | 2021-05-06
MI_PS_VAV_OTHER Supply Flow Rate [cfm] | VAV_OTHER Supply Flow Rate [cfm] | 7966.9888 | 7479.6464 | 7861.0448 | 7267.7584 | 7627.968 | 6843.9824 |  |  |  |  | 2021-05-06
MI_PS_PSZ-AC_2:5 Supply Flow Rate [cfm] | PSZ-AC_2:5 Supply Flow Rate [cfm] | 1652.7264 | 1631.5376 | 1610.3488 | 1589.16 | 1652.7264 | 1631.5376 |  |  |  |  | 2021-05-06
MI_PS_PSZ-AC_1:6 Supply Flow Rate [cfm] | PSZ-AC_1:6 Supply Flow Rate [cfm] | 2585.0336 | 2479.0896 | 2585.0336 | 2457.9008 | 2563.8448 | 2436.712 |  |  |  |  | 2021-05-06
MI_PS_PSZ-AC_2:7 Supply Flow Rate [cfm] | PSZ-AC_2:7 Supply Flow Rate [cfm] | 3157.1312 | 3157.1312 | 3157.1312 | 3157.1312 | 3157.1312 | 3157.1312 |  |  |  |  | 2021-05-06
MI_PS_Supply Air Temp. Reset Flag | Supply Air Temp. Reset Flag | Yes | Yes | Yes | Yes | Yes | Yes |  |  |  |  | 2021-05-06
MI_PS_VAV_POD_1 OA Rate [cfm] | VAV_POD_1 OA Rate [cfm] | 5696.7996 | 5515.4658 | 5668.9151 | 5464.4008 | 5622.7447 | 5369.8564 |  |  |  |  | 2021-05-06
MI_PS_VAV_POD_2 OA Rate [cfm] | VAV_POD_2 OA Rate [cfm] | 5641.5816 | 5501.7567 | 5605.9208 | 5451.6028 | 5576.765 | 5355.5116 |  |  |  |  | 2021-05-06
MI_PS_VAV_POD_3 OA Rate [cfm] | VAV_POD_3 OA Rate [cfm] | 5196.6168 | 4939.0033 | 5164.6641 | 4845.2429 | 5102.263 | 4741.1 |  |  |  |  | 2021-05-06
MI_PS_VAV_OTHER OA Rate [cfm] | VAV_OTHER OA Rate [cfm] | 3736.1787 | 2988.8921 | 3736.1787 | 2988.8921 | 3736.1787 | 2988.8921 |  |  |  |  | 2021-05-06
MI_PS_PSZ-AC_2:5 OA Rate [cfm] | PSZ-AC_2:5 OA Rate [cfm] | 1152.7343 | 1152.7343 | 1152.7343 | 1152.7343 | 1152.7343 | 1152.7343 |  |  |  |  | 2021-05-06
MI_PS_PSZ-AC_1:6 OA Rate [cfm] | PSZ-AC_1:6 OA Rate [cfm] | 539.9118 | 539.9118 | 539.9118 | 539.9118 | 539.9118 | 539.9118 |  |  |  |  | 2021-05-06
MI_PS_PSZ-AC_2:7 OA Rate [cfm] | PSZ-AC_2:7 OA Rate [cfm] | 3153.0841 | 3153.0841 | 3153.0841 | 3153.0841 | 3153.0841 | 3153.0841 |  |  |  |  | 2021-05-06
MI_PS_VAV_POD_1 OA Damper [gravity, motorized] | VAV_POD_1 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | motorized | motorized |  |  |  |  | 2021-05-06
MI_PS_VAV_POD_2 OA Damper [gravity, motorized] | VAV_POD_2 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | motorized | motorized |  |  |  |  | 2021-05-06
MI_PS_VAV_POD_3 OA Damper [gravity, motorized] | VAV_POD_3 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | motorized | motorized |  |  |  |  | 2021-05-06
MI_PS_VAV_OTHER OA Damper [gravity, motorized] | VAV_OTHER OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | motorized | motorized |  |  |  |  | 2021-05-06
MI_PS_PSZ-AC_2:5 OA Damper [gravity, motorized] | PSZ-AC_2:5 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | motorized | motorized |  |  |  |  | 2021-05-06
MI_PS_PSZ-AC_1:6 OA Damper [gravity, motorized] | PSZ-AC_1:6 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | motorized | motorized |  |  |  |  | 2021-05-06
MI_PS_PSZ-AC_2:7 OA Damper [gravity, motorized] | PSZ-AC_2:7 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | motorized | motorized |  |  |  |  | 2021-05-06
MI_PS_VAV_POD_1 (economizer) | VAV_POD_1 (economizer) | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb |  |  |  |  | 2021-05-06
MI_PS_VAV_POD_2 (economizer) | VAV_POD_2 (economizer) | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb |  |  |  |  | 2021-05-06
MI_PS_VAV_POD_3 (economizer) | VAV_POD_3 (economizer) | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb |  |  |  |  | 2021-05-06
MI_PS_VAV_OTHER (economizer) | VAV_OTHER (economizer) | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb |  |  |  |  | 2021-05-06
MI_PS_PSZ-AC_2:5 (economizer) | PSZ-AC_2:5 (economizer) | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb |  |  |  |  | 2021-05-06
MI_PS_PSZ-AC_1:6 (economizer) | PSZ-AC_1:6 (economizer) | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb |  |  |  |  | 2021-05-06
MI_PS_PSZ-AC_2:7 (economizer) | PSZ-AC_2:7 (economizer) | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb |  |  |  |  | 2021-05-06
MI_PS_VAV_Pod_1_ERV Flag | VAV_Pod_1_ERV Flag | Yes | Yes | Yes | Yes | Yes | Yes |  |  |  |  | 2021-05-06
MI_PS_VAV_Pod_2_ERV Flag | VAV_Pod_2_ERV Flag | Yes | Yes | Yes | Yes | Yes | Yes |  |  |  |  | 2021-05-06
MI_PS_VAV_Pod_3_ERV Flag | VAV_Pod_3_ERV Flag | Yes | Yes | Yes | Yes | Yes | Yes |  |  |  |  | 2021-05-06
MI_PS_VAV_OTHER_ERV Flag | VAV_OTHER_ERV Flag | Yes | Yes | Yes | Yes | Yes | Yes |  |  |  |  | 2021-05-06
MI_PS_PSZ_AC_2_5_ERV Flag | PSZ_AC_2_5_ERV Flag | No | Yes | Yes | Yes | Yes | Yes |  |  |  |  | 2021-05-06
MI_PS_PSZ_AC_2_7_ERV Flag | PSZ_AC_2_7_ERV Flag | Yes | Yes | Yes | Yes | Yes | Yes |  |  |  |  | 2021-05-06
MI_PS_HEATSYS1 Capacity [MMBTU/h] | HEATSYS1 Capacity [MMBTU/h] | 1.1728 | 1.128 | 1.1866 | 1.136 | 1.2217 | 1.1473 |  |  |  |  | 2021-05-06
MI_PS_HEATSYS1 Flow Rate [gal/min] | HEATSYS1 Flow Rate [gal/min] | 120.3655 | 115.773 | 121.7871 | 116.5856 | 125.3895 | 117.7528 |  |  |  |  | 2021-05-06
MI_PS_VAV_POD_1 Fan Power [hp] | VAV_POD_1 Fan Power [hp] | 8.4076 | 8.137 | 8.3647 | 8.0616 | 8.2952 | 7.9221 |  |  |  |  | 2021-05-06
MI_PS_VAV_POD_2 Fan Power [hp] | VAV_POD_2 Fan Power [hp] | 8.323 | 8.1168 | 8.2704 | 8.0427 | 8.2274 | 7.901 |  |  |  |  | 2021-05-06
MI_PS_VAV_POD_3 Fan Power [hp] | VAV_POD_3 Fan Power [hp] | 7.6666 | 7.2865 | 7.6194 | 7.1482 | 7.5281 | 6.9945 |  |  |  |  | 2021-05-06
MI_PS_VAV_OTHER Fan Power [hp] | VAV_OTHER Fan Power [hp] | 11.6624 | 10.9474 | 11.4987 | 10.6508 | 11.1639 | 10.0137 |  |  |  |  | 2021-05-06
MI_PS_HEATSYS1 Pump Power [hp] | HEATSYS1 Pump Power [hp] | 2.6018 | 2.4777 | 2.6325 | 2.4951 | 2.7104 | 2.5201 |  |  |  |  | 2021-05-06
MI_PS_PSZ-AC_1:6 Heating Capacity [kBtu/hr] | PSZ-AC_1:6 Heating Capacity [kBtu/hr] | 215.637 | 207.0837 | 217.313 | 208.0465 | 220.0026 | 209.475 |  |  |  |  | 2021-05-06
MI_PS_PSZ-AC_2:5 Heating Capacity [kBtu/hr] | PSZ-AC_2:5 Heating Capacity [kBtu/hr] | 146.4197 | 146.1356 | 150.1668 | 149.3016 | 158.2168 | 157.5402 |  |  |  |  | 2021-05-06
MI_PS_PSZ-AC_2:7 Heating Capacity [kBtu/hr] | PSZ-AC_2:7 Heating Capacity [kBtu/hr] | 352.2634 | 352.2634 | 364.9879 | 364.9879 | 383.1559 | 383.1559 |  |  |  |  | 2021-05-06
MI_PS_ZN_VAV_BOXes_Max_Reheat_Water_Flow_GPM | ZN_VAV_BOXes_Max_Reheat_Water_Flow_GPM | 74.8721 | 72.2649 | 73.8738 | 71.1539 | 73.914 | 69.7653 |  |  |  |  | 2021-05-06
id | item | Zone5A(MI-Lansing-MI) ASHRAE901-state_STD2016 | Zone5A(MI-Lansing-MI) ASHRAE901-state_STD2019 | Zone6A(MI-AlpenaCounty-MI) ASHRAE901-state_STD2016 | Zone6A(MI-AlpenaCounty-MI) ASHRAE901-state_STD2019 | Zone7(MI-SaultSteMarie-MI) ASHRAE901-state_STD2016 | Zone7(MI-SaultSteMarie-MI) ASHRAE901-state_STD2019 |  |  |  |  | 2021-05-06
MI_SH_SAC_FRONTOFFICE Cooling Capacity [ton] | SAC_FRONTOFFICE Cooling Capacity [ton] | 2.2695 | 2.1469 | 2.1371 | 2.017 | 1.9557 | 1.8348 |  |  |  |  | 2021-05-06
MI_SH_SAC_FRONTLOUNGE Cooling Capacity [ton] | SAC_FRONTLOUNGE Cooling Capacity [ton] | 6.0975 | 5.7851 | 5.8402 | 5.6064 | 5.3619 | 5.1229 |  |  |  |  | 2021-05-06
MI_SH_SAC_MEETINGROOM Cooling Capacity [ton] | SAC_MEETINGROOM Cooling Capacity [ton] | 2.9105 | 2.8184 | 2.8626 | 2.7682 | 2.7907 | 2.7059 |  |  |  |  | 2021-05-06
MI_SH_SAC_EXC_EMPLGE_RESTRM Cooling Capacity [ton] | SAC_EXC_EMPLGE_RESTRM Cooling Capacity [ton] | 5.8201 | 5.768 | 5.6453 | 5.5996 | 5.4514 | 5.3862 |  |  |  |  | 2021-05-06
MI_SH_SAC_FO_ADDAQ SUPPLY FAN Supply Flow Rate [cfm] | SAC_FO_ADDAQ SUPPLY FAN Supply Flow Rate [cfm] | 762.7968 | 720.4192 | 741.608 | 699.2304 | 720.4192 | 678.0416 |  |  |  |  | 2021-05-06
MI_SH_SAC_FL_ADDAQ SUPPLY FAN Supply Flow Rate [cfm] | SAC_FL_ADDAQ SUPPLY FAN Supply Flow Rate [cfm] | 1822.2368 | 1737.4816 | 1801.048 | 1695.104 | 1758.6704 | 1652.7264 |  |  |  |  | 2021-05-06
MI_SH_SAC_MR_ADDAQ SUPPLY FAN Supply Flow Rate [cfm] | SAC_MR_ADDAQ SUPPLY FAN Supply Flow Rate [cfm] | 868.7408 | 847.552 | 868.7408 | 826.3632 | 847.552 | 805.1744 |  |  |  |  | 2021-05-06
MI_SH_SAC_EXC_ADDAQ SUPPLY FAN Supply Flow Rate [cfm] | SAC_EXC_ADDAQ SUPPLY FAN Supply Flow Rate [cfm] | 2203.6352 | 2203.6352 | 2203.6352 | 2182.4464 | 2203.6352 | 2182.4464 |  |  |  |  | 2021-05-06
MI_SH_SAC_Exc_EmpLge_RestRm OA Rate [cfm] | SAC_Exc_EmpLge_RestRm OA Rate [cfm] | 199.9928 | 199.9928 | 199.9928 | 199.9928 | 199.9928 | 199.9928 |  |  |  |  | 2021-05-06
MI_SH_SAC_FrontLounge OA Rate [cfm] | SAC_FrontLounge OA Rate [cfm] | 500.0133 | 500.0133 | 500.0133 | 500.0133 | 500.0133 | 500.0133 |  |  |  |  | 2021-05-06
MI_SH_SAC_FrontOffice OA Rate [cfm] | SAC_FrontOffice OA Rate [cfm] | 119.2938 | 119.2938 | 119.2938 | 119.2938 | 119.2938 | 119.2938 |  |  |  |  | 2021-05-06
MI_SH_SAC_MeetingRoom OA Rate [cfm] | SAC_MeetingRoom OA Rate [cfm] | 267.7629 | 267.7629 | 267.7629 | 267.7629 | 267.7629 | 267.7629 |  |  |  |  | 2021-05-06
MI_SH_SAC_FrontLounge OA Damper [gravity, motorized] | SAC_FrontLounge OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | motorized | motorized |  |  |  |  | 2021-05-06
MI_SH_SAC_FrontOffice (economizer) | SAC_FrontOffice (economizer) | No | No | No | No | No | No |  |  |  |  | 2021-05-06
MI_SH_SAC_FrontLounge (economizer) | SAC_FrontLounge (economizer) | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb |  |  |  |  | 2021-05-06
MI_SH_SAC_MeetingRoom (economizer) | SAC_MeetingRoom (economizer) | No | No | No | No | No | No |  |  |  |  | 2021-05-06
MI_SH_SAC_Exc_EmpLge_RestRm (economizer) | SAC_Exc_EmpLge_RestRm (economizer) | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb |  |  |  |  | 2021-05-06
MI_SH_SAC_FRONTOFFICE Heating Capacity [kBtu/hr] | SAC_FRONTOFFICE Heating Capacity [kBtu/hr] | 36.6471 | 34.7307 | 36.52 | 34.5989 | 36.2617 | 34.2522 |  |  |  |  | 2021-05-06
MI_SH_SAC_FRONTLOUNGE Heating Capacity [kBtu/hr] | SAC_FRONTLOUNGE Heating Capacity [kBtu/hr] | 103.3431 | 99.9962 | 104.273 | 100.791 | 105.5423 | 101.8547 |  |  |  |  | 2021-05-06
MI_SH_SAC_MEETINGROOM Heating Capacity [kBtu/hr] | SAC_MEETINGROOM Heating Capacity [kBtu/hr] | 51.5386 | 50.5522 | 52.2221 | 51.2057 | 53.1286 | 52.0559 |  |  |  |  | 2021-05-06
MI_SH_SAC_EXC_EMPLGE_RESTRM Heating Capacity [kBtu/hr] | SAC_EXC_EMPLGE_RESTRM Heating Capacity [kBtu/hr] | 94.2181 | 93.5577 | 95.1109 | 94.3572 | 96.0622 | 95.0918 |  |  |  |  | 2021-05-06
id | item | Zone5A(MI-Lansing-MI) ASHRAE901-state_STD2016 | Zone5A(MI-Lansing-MI) ASHRAE901-state_STD2019 | Zone6A(MI-AlpenaCounty-MI) ASHRAE901-state_STD2016 | Zone6A(MI-AlpenaCounty-MI) ASHRAE901-state_STD2019 | Zone7(MI-SaultSteMarie-MI) ASHRAE901-state_STD2016 | Zone7(MI-SaultSteMarie-MI) ASHRAE901-state_STD2019 |  |  |  |  | 2021-05-06
MI_MA_SPLIT GSW COOLING COIL Cooling Capacity [ton] | SPLIT GSW COOLING COIL Cooling Capacity [ton] | 0.82713 | 0.81267 | 0.78395 | 0.75722 | 0.7226 | 0.66352 |  |  |  |  | 2021-05-06
MI_MA_SPLIT GNW COOLING COIL Cooling Capacity [ton] | SPLIT GNW COOLING COIL Cooling Capacity [ton] | 0.77866 | 0.76459 | 0.72751 | 0.7001 | 0.65395 | 0.60622 |  |  |  |  | 2021-05-06
MI_MA_SPLIT OFFICE COOLING COIL Cooling Capacity [ton] | SPLIT OFFICE COOLING COIL Cooling Capacity [ton] | 1.6847 | 1.5588 | 1.5975 | 1.4458 | 1.5362 | 1.3336 |  |  |  |  | 2021-05-06
MI_MA_SPLIT GNE COOLING COIL Cooling Capacity [ton] | SPLIT GNE COOLING COIL Cooling Capacity [ton] | 0.6727 | 0.66033 | 0.62163 | 0.59907 | 0.54598 | 0.50774 |  |  |  |  | 2021-05-06
MI_MA_SPLIT GN1 COOLING COIL Cooling Capacity [ton] | SPLIT GN1 COOLING COIL Cooling Capacity [ton] | 0.57271 | 0.56268 | 0.52767 | 0.51242 | 0.46162 | 0.43868 |  |  |  |  | 2021-05-06
MI_MA_SPLIT GN2 COOLING COIL Cooling Capacity [ton] | SPLIT GN2 COOLING COIL Cooling Capacity [ton] | 0.57068 | 0.5607 | 0.52558 | 0.51048 | 0.46152 | 0.43667 |  |  |  |  | 2021-05-06
MI_MA_SPLIT GS1 COOLING COIL Cooling Capacity [ton] | SPLIT GS1 COOLING COIL Cooling Capacity [ton] | 0.6211 | 0.61039 | 0.58468 | 0.56635 | 0.53329 | 0.49898 |  |  |  |  | 2021-05-06
MI_MA_SPLIT GS2 COOLING COIL Cooling Capacity [ton] | SPLIT GS2 COOLING COIL Cooling Capacity [ton] | 0.65677 | 0.64122 | 0.62007 | 0.5968 | 0.5676 | 0.52819 |  |  |  |  | 2021-05-06
MI_MA_SPLIT MSW COOLING COIL Cooling Capacity [ton] | SPLIT MSW COOLING COIL Cooling Capacity [ton] | 2.0626 | 2.0302 | 1.9582 | 1.8857 | 1.8952 | 1.7501 |  |  |  |  | 2021-05-06
MI_MA_SPLIT MNW COOLING COIL Cooling Capacity [ton] | SPLIT MNW COOLING COIL Cooling Capacity [ton] | 1.9684 | 1.9373 | 1.8415 | 1.7739 | 1.7552 | 1.6333 |  |  |  |  | 2021-05-06
MI_MA_SPLIT MSE COOLING COIL Cooling Capacity [ton] | SPLIT MSE COOLING COIL Cooling Capacity [ton] | 1.7852 | 1.7559 | 1.6995 | 1.633 | 1.6588 | 1.5048 |  |  |  |  | 2021-05-06
MI_MA_SPLIT MNE COOLING COIL Cooling Capacity [ton] | SPLIT MNE COOLING COIL Cooling Capacity [ton] | 1.6149 | 1.5844 | 1.4958 | 1.4311 | 1.4389 | 1.3238 |  |  |  |  | 2021-05-06
MI_MA_SPLIT MN1 COOLING COIL Cooling Capacity [ton] | SPLIT MN1 COOLING COIL Cooling Capacity [ton] | 1.2859 | 1.2683 | 1.1821 | 1.1546 | 1.0936 | 1.0468 |  |  |  |  | 2021-05-06
MI_MA_SPLIT MN2 COOLING COIL Cooling Capacity [ton] | SPLIT MN2 COOLING COIL Cooling Capacity [ton] | 1.2954 | 1.2765 | 1.1753 | 1.1483 | 1.0861 | 1.0404 |  |  |  |  | 2021-05-06
MI_MA_SPLIT MS1 COOLING COIL Cooling Capacity [ton] | SPLIT MS1 COOLING COIL Cooling Capacity [ton] | 1.4011 | 1.381 | 1.3129 | 1.2778 | 1.3073 | 1.1723 |  |  |  |  | 2021-05-06
MI_MA_SPLIT MS2 COOLING COIL Cooling Capacity [ton] | SPLIT MS2 COOLING COIL Cooling Capacity [ton] | 1.396 | 1.376 | 1.3075 | 1.2729 | 1.3126 | 1.1673 |  |  |  |  | 2021-05-06
MI_MA_SPLIT TSW COOLING COIL Cooling Capacity [ton] | SPLIT TSW COOLING COIL Cooling Capacity [ton] | 1.2767 | 1.2592 | 1.2099 | 1.1696 | 1.145 | 1.0653 |  |  |  |  | 2021-05-06
MI_MA_SPLIT TNW COOLING COIL Cooling Capacity [ton] | SPLIT TNW COOLING COIL Cooling Capacity [ton] | 1.2291 | 1.2124 | 1.1537 | 1.1164 | 1.0779 | 1.0084 |  |  |  |  | 2021-05-06
MI_MA_SPLIT TSE COOLING COIL Cooling Capacity [ton] | SPLIT TSE COOLING COIL Cooling Capacity [ton] | 1.1411 | 1.126 | 1.0865 | 1.0503 | 1.031 | 0.9432 |  |  |  |  | 2021-05-06
MI_MA_SPLIT TNE COOLING COIL Cooling Capacity [ton] | SPLIT TNE COOLING COIL Cooling Capacity [ton] | 1.0449 | 1.0322 | 0.96292 | 0.93796 | 0.84771 | 0.77903 |  |  |  |  | 2021-05-06
MI_MA_SPLIT TN1 COOLING COIL Cooling Capacity [ton] | SPLIT TN1 COOLING COIL Cooling Capacity [ton] | 0.83376 | 0.82422 | 0.76818 | 0.75275 | 0.68594 | 0.66192 |  |  |  |  | 2021-05-06
MI_MA_SPLIT TN2 COOLING COIL Cooling Capacity [ton] | SPLIT TN2 COOLING COIL Cooling Capacity [ton] | 0.82742 | 0.81804 | 0.76155 | 0.74661 | 0.67874 | 0.65573 |  |  |  |  | 2021-05-06
MI_MA_SPLIT TS1 COOLING COIL Cooling Capacity [ton] | SPLIT TS1 COOLING COIL Cooling Capacity [ton] | 0.93437 | 0.92247 | 0.894 | 0.86838 | 0.84767 | 0.78148 |  |  |  |  | 2021-05-06
MI_MA_SPLIT TS2 COOLING COIL Cooling Capacity [ton] | SPLIT TS2 COOLING COIL Cooling Capacity [ton] | 0.93761 | 0.92567 | 0.89785 | 0.87174 | 0.85211 | 0.78518 |  |  |  |  | 2021-05-06
MI_MA_Split GN1 Furnace with DX Cooling OA Rate [cfm] | Split GN1 Furnace with DX Cooling OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 |  |  |  |  | 2021-05-06
MI_MA_Split GN2 Furnace with DX Cooling OA Rate [cfm] | Split GN2 Furnace with DX Cooling OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 |  |  |  |  | 2021-05-06
MI_MA_Split GNE Furnace with DX Cooling OA Rate [cfm] | Split GNE Furnace with DX Cooling OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 |  |  |  |  | 2021-05-06
MI_MA_Split GNW Furnace with DX Cooling OA Rate [cfm] | Split GNW Furnace with DX Cooling OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 |  |  |  |  | 2021-05-06
MI_MA_Split GS1 Furnace with DX Cooling OA Rate [cfm] | Split GS1 Furnace with DX Cooling OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 |  |  |  |  | 2021-05-06
MI_MA_Split GS2 Furnace with DX Cooling OA Rate [cfm] | Split GS2 Furnace with DX Cooling OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 |  |  |  |  | 2021-05-06
MI_MA_Split GSW Furnace with DX Cooling OA Rate [cfm] | Split GSW Furnace with DX Cooling OA Rate [cfm] | 56.9945 | 56.9945 | 56.9945 | 56.9945 | 56.9945 | 56.9945 |  |  |  |  | 2021-05-06
MI_MA_Split MN1 Furnace with DX Cooling OA Rate [cfm] | Split MN1 Furnace with DX Cooling OA Rate [cfm] | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824 |  |  |  |  | 2021-05-06
MI_MA_Split MN2 Furnace with DX Cooling OA Rate [cfm] | Split MN2 Furnace with DX Cooling OA Rate [cfm] | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824 |  |  |  |  | 2021-05-06
MI_MA_Split MNE Furnace with DX Cooling OA Rate [cfm] | Split MNE Furnace with DX Cooling OA Rate [cfm] | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824 |  |  |  |  | 2021-05-06
MI_MA_Split MNW Furnace with DX Cooling OA Rate [cfm] | Split MNW Furnace with DX Cooling OA Rate [cfm] | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824 |  |  |  |  | 2021-05-06
MI_MA_Split MS1 Furnace with DX Cooling OA Rate [cfm] | Split MS1 Furnace with DX Cooling OA Rate [cfm] | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824 |  |  |  |  | 2021-05-06
MI_MA_Split MS2 Furnace with DX Cooling OA Rate [cfm] | Split MS2 Furnace with DX Cooling OA Rate [cfm] | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824 |  |  |  |  | 2021-05-06
MI_MA_Split MSE Furnace with DX Cooling OA Rate [cfm] | Split MSE Furnace with DX Cooling OA Rate [cfm] | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824 |  |  |  |  | 2021-05-06
MI_MA_Split MSW Furnace with DX Cooling OA Rate [cfm] | Split MSW Furnace with DX Cooling OA Rate [cfm] | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824 |  |  |  |  | 2021-05-06
MI_MA_Split Office Furnace with DX Cooling OA Rate [cfm] | Split Office Furnace with DX Cooling OA Rate [cfm] | 80.7372 | 80.7372 | 80.7372 | 80.7372 | 80.7372 | 80.7372 |  |  |  |  | 2021-05-06
MI_MA_Split TN1 Furnace with DX Cooling OA Rate [cfm] | Split TN1 Furnace with DX Cooling OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 |  |  |  |  | 2021-05-06
MI_MA_Split TN2 Furnace with DX Cooling OA Rate [cfm] | Split TN2 Furnace with DX Cooling OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 |  |  |  |  | 2021-05-06
MI_MA_Split TNE Furnace with DX Cooling OA Rate [cfm] | Split TNE Furnace with DX Cooling OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 |  |  |  |  | 2021-05-06
MI_MA_Split TNW Furnace with DX Cooling OA Rate [cfm] | Split TNW Furnace with DX Cooling OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 |  |  |  |  | 2021-05-06
MI_MA_Split TS1 Furnace with DX Cooling OA Rate [cfm] | Split TS1 Furnace with DX Cooling OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 |  |  |  |  | 2021-05-06
MI_MA_Split TS2 Furnace with DX Cooling OA Rate [cfm] | Split TS2 Furnace with DX Cooling OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 |  |  |  |  | 2021-05-06
MI_MA_Split TSE Furnace with DX Cooling OA Rate [cfm] | Split TSE Furnace with DX Cooling OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 |  |  |  |  | 2021-05-06
MI_MA_Split TSW Furnace with DX Cooling OA Rate [cfm] | Split TSW Furnace with DX Cooling OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 |  |  |  |  | 2021-05-06
MI_MA_SPLIT GSW HEATING COIL Heating Capacity [kBtu/hr] | SPLIT GSW HEATING COIL Heating Capacity [kBtu/hr] | 10.7087 | 10.7678 | 10.3864 | 10.4459 | 10.9848 | 10.8689 |  |  |  |  | 2021-05-06
MI_MA_SPLIT GNW HEATING COIL Heating Capacity [kBtu/hr] | SPLIT GNW HEATING COIL Heating Capacity [kBtu/hr] | 10.5928 | 10.6519 | 10.2638 | 10.3234 | 10.8521 | 10.7365 |  |  |  |  | 2021-05-06
MI_MA_SPLIT OFFICE HEATING COIL Heating Capacity [kBtu/hr] | SPLIT OFFICE HEATING COIL Heating Capacity [kBtu/hr] | 24.0346 | 24.1154 | 23.7961 | 23.88 | 24.4599 | 24.326 |  |  |  |  | 2021-05-06
MI_MA_SPLIT GNE HEATING COIL Heating Capacity [kBtu/hr] | SPLIT GNE HEATING COIL Heating Capacity [kBtu/hr] | 10.5683 | 10.6275 | 10.2438 | 10.3034 | 10.8726 | 10.7546 |  |  |  |  | 2021-05-06
MI_MA_SPLIT GN1 HEATING COIL Heating Capacity [kBtu/hr] | SPLIT GN1 HEATING COIL Heating Capacity [kBtu/hr] | 7.9029 | 7.9621 | 7.8009 | 7.8605 | 8.3408 | 8.2841 |  |  |  |  | 2021-05-06
MI_MA_SPLIT GN2 HEATING COIL Heating Capacity [kBtu/hr] | SPLIT GN2 HEATING COIL Heating Capacity [kBtu/hr] | 7.9022 | 7.9614 | 7.8003 | 7.8599 | 8.3414 | 8.2846 |  |  |  |  | 2021-05-06
MI_MA_SPLIT GS1 HEATING COIL Heating Capacity [kBtu/hr] | SPLIT GS1 HEATING COIL Heating Capacity [kBtu/hr] | 7.8835 | 7.9425 | 7.7806 | 7.8401 | 8.3191 | 8.262 |  |  |  |  | 2021-05-06
MI_MA_SPLIT GS2 HEATING COIL Heating Capacity [kBtu/hr] | SPLIT GS2 HEATING COIL Heating Capacity [kBtu/hr] | 8.3965 | 8.4563 | 8.2947 | 8.3552 | 8.8401 | 8.7829 |  |  |  |  | 2021-05-06
MI_MA_SPLIT MSW HEATING COIL Heating Capacity [kBtu/hr] | SPLIT MSW HEATING COIL Heating Capacity [kBtu/hr] | 18.4403 | 18.5689 | 17.3128 | 17.4416 | 18.2758 | 18.0459 |  |  |  |  | 2021-05-06
MI_MA_SPLIT MNW HEATING COIL Heating Capacity [kBtu/hr] | SPLIT MNW HEATING COIL Heating Capacity [kBtu/hr] | 18.4517 | 18.5805 | 17.3247 | 17.4533 | 18.2879 | 18.0579 |  |  |  |  | 2021-05-06
MI_MA_SPLIT MSE HEATING COIL Heating Capacity [kBtu/hr] | SPLIT MSE HEATING COIL Heating Capacity [kBtu/hr] | 18.3823 | 18.511 | 17.2652 | 17.394 | 18.3242 | 18.0884 |  |  |  |  | 2021-05-06
MI_MA_SPLIT MNE HEATING COIL Heating Capacity [kBtu/hr] | SPLIT MNE HEATING COIL Heating Capacity [kBtu/hr] | 18.3937 | 18.5225 | 17.2771 | 17.4057 | 18.3363 | 18.1005 |  |  |  |  | 2021-05-06
MI_MA_SPLIT MN1 HEATING COIL Heating Capacity [kBtu/hr] | SPLIT MN1 HEATING COIL Heating Capacity [kBtu/hr] | 12.9957 | 13.1218 | 12.7311 | 12.7311 | 13.3648 | 13.3648 |  |  |  |  | 2021-05-06
MI_MA_SPLIT MN2 HEATING COIL Heating Capacity [kBtu/hr] | SPLIT MN2 HEATING COIL Heating Capacity [kBtu/hr] | 12.9942 | 13.1203 | 12.7311 | 12.7311 | 13.3648 | 13.3648 |  |  |  |  | 2021-05-06
MI_MA_SPLIT MS1 HEATING COIL Heating Capacity [kBtu/hr] | SPLIT MS1 HEATING COIL Heating Capacity [kBtu/hr] | 12.9932 | 13.1194 | 12.7311 | 12.7311 | 13.3648 | 13.3648 |  |  |  |  | 2021-05-06
MI_MA_SPLIT MS2 HEATING COIL Heating Capacity [kBtu/hr] | SPLIT MS2 HEATING COIL Heating Capacity [kBtu/hr] | 12.9917 | 13.1179 | 12.7311 | 12.7311 | 13.3648 | 13.3648 |  |  |  |  | 2021-05-06
MI_MA_SPLIT TSW HEATING COIL Heating Capacity [kBtu/hr] | SPLIT TSW HEATING COIL Heating Capacity [kBtu/hr] | 12.9871 | 13.0491 | 12.4021 | 12.4643 | 12.7844 | 12.6714 |  |  |  |  | 2021-05-06
MI_MA_SPLIT TNW HEATING COIL Heating Capacity [kBtu/hr] | SPLIT TNW HEATING COIL Heating Capacity [kBtu/hr] | 12.9997 | 13.0617 | 12.4155 | 12.4778 | 12.7981 | 12.6854 |  |  |  |  | 2021-05-06
MI_MA_SPLIT TSE HEATING COIL Heating Capacity [kBtu/hr] | SPLIT TSE HEATING COIL Heating Capacity [kBtu/hr] | 12.9563 | 13.0182 | 12.3766 | 12.4387 | 12.8104 | 12.6943 |  |  |  |  | 2021-05-06
MI_MA_SPLIT TNE HEATING COIL Heating Capacity [kBtu/hr] | SPLIT TNE HEATING COIL Heating Capacity [kBtu/hr] | 12.9688 | 13.0309 | 12.39 | 12.4522 | 12.8241 | 12.7082 |  |  |  |  | 2021-05-06
MI_MA_SPLIT TN1 HEATING COIL Heating Capacity [kBtu/hr] | SPLIT TN1 HEATING COIL Heating Capacity [kBtu/hr] | 10.0922 | 10.1541 | 9.8683 | 9.9304 | 10.1413 | 10.089 |  |  |  |  | 2021-05-06
MI_MA_SPLIT TN2 HEATING COIL Heating Capacity [kBtu/hr] | SPLIT TN2 HEATING COIL Heating Capacity [kBtu/hr] | 10.0913 | 10.1532 | 9.8675 | 9.9297 | 10.1421 | 10.0897 |  |  |  |  | 2021-05-06
MI_MA_SPLIT TS1 HEATING COIL Heating Capacity [kBtu/hr] | SPLIT TS1 HEATING COIL Heating Capacity [kBtu/hr] | 10.0735 | 10.1354 | 9.8487 | 9.9107 | 10.1214 | 10.0685 |  |  |  |  | 2021-05-06
MI_MA_SPLIT TS2 HEATING COIL Heating Capacity [kBtu/hr] | SPLIT TS2 HEATING COIL Heating Capacity [kBtu/hr] | 10.0726 | 10.1345 | 9.848 | 9.91 | 10.1221 | 10.0691 |  |  |  |  | 2021-05-06
MI_MA_Split_GSW ERV Flag | Split_GSW ERV Flag | Yes | Yes | Yes | Yes | Yes | Yes |  |  |  |  | 2021-05-06
MI_MA_Split_GNW ERV Flag | Split_GNW ERV Flag | Yes | Yes | Yes | Yes | Yes | Yes |  |  |  |  | 2021-05-06
MI_MA_Split_GNE ERV Flag | Split_GNE ERV Flag | Yes | Yes | Yes | Yes | Yes | Yes |  |  |  |  | 2021-05-06
MI_MA_Split_GN1 ERV Flag | Split_GN1 ERV Flag | Yes | Yes | Yes | Yes | Yes | Yes |  |  |  |  | 2021-05-06
MI_MA_Split_GN2 ERV Flag | Split_GN2 ERV Flag | Yes | Yes | Yes | Yes | Yes | Yes |  |  |  |  | 2021-05-06
MI_MA_Split_GS1 ERV Flag | Split_GS1 ERV Flag | Yes | Yes | Yes | Yes | Yes | Yes |  |  |  |  | 2021-05-06
MI_MA_Split_GS2 ERV Flag | Split_GS2 ERV Flag | Yes | Yes | Yes | Yes | Yes | Yes |  |  |  |  | 2021-05-06
MI_MA_Split_MSW ERV Flag | Split_MSW ERV Flag | Yes | Yes | Yes | Yes | Yes | Yes |  |  |  |  | 2021-05-06
MI_MA_Split_MNW ERV Flag | Split_MNW ERV Flag | Yes | Yes | Yes | Yes | Yes | Yes |  |  |  |  | 2021-05-06
MI_MA_Split_MSE ERV Flag | Split_MSE ERV Flag | Yes | Yes | Yes | Yes | Yes | Yes |  |  |  |  | 2021-05-06
MI_MA_Split_MNE ERV Flag | Split_MNE ERV Flag | Yes | Yes | Yes | Yes | Yes | Yes |  |  |  |  | 2021-05-06
MI_MA_Split_MN1 ERV Flag | Split_MN1 ERV Flag | Yes | Yes | Yes | Yes | Yes | Yes |  |  |  |  | 2021-05-06
MI_MA_Split_MN2 ERV Flag | Split_MN2 ERV Flag | Yes | Yes | Yes | Yes | Yes | Yes |  |  |  |  | 2021-05-06
MI_MA_Split_MS1 ERV Flag | Split_MS1 ERV Flag | Yes | Yes | Yes | Yes | Yes | Yes |  |  |  |  | 2021-05-06
MI_MA_Split_MS2 ERV Flag | Split_MS2 ERV Flag | Yes | Yes | Yes | Yes | Yes | Yes |  |  |  |  | 2021-05-06
MI_MA_Split_TSW ERV Flag | Split_TSW ERV Flag | Yes | Yes | Yes | Yes | Yes | Yes |  |  |  |  | 2021-05-06
MI_MA_Split_TNW ERV Flag | Split_TNW ERV Flag | Yes | Yes | Yes | Yes | Yes | Yes |  |  |  |  | 2021-05-06
MI_MA_Split_TSE ERV Flag | Split_TSE ERV Flag | Yes | Yes | Yes | Yes | Yes | Yes |  |  |  |  | 2021-05-06
MI_MA_Split_TNE ERV Flag | Split_TNE ERV Flag | Yes | Yes | Yes | Yes | Yes | Yes |  |  |  |  | 2021-05-06
MI_MA_Split_TN1 ERV Flag | Split_TN1 ERV Flag | Yes | Yes | Yes | Yes | Yes | Yes |  |  |  |  | 2021-05-06
MI_MA_Split_TN2 ERV Flag | Split_TN2 ERV Flag | Yes | Yes | Yes | Yes | Yes | Yes |  |  |  |  | 2021-05-06
MI_MA_Split_TS1 ERV Flag | Split_TS1 ERV Flag | Yes | Yes | Yes | Yes | Yes | Yes |  |  |  |  | 2021-05-06
MI_MA_Split_TS2 ERV Flag | Split_TS2 ERV Flag | Yes | Yes | Yes | Yes | Yes | Yes |  |  |  |  | 2021-05-06
id | item | Zone5A(MN-Winona-MN) ASHRAE901-state_STD2016 | Zone5A(MN-Winona-MN) ASHRAE901-state_STD2019 | Zone6A(MN-MinneapolisStPaul-MN) ASHRAE901-state_STD2016 | Zone6A(MN-MinneapolisStPaul-MN) ASHRAE901-state_STD2019 | Zone7(MN-Duluth-MN) ASHRAE901-state_STD2016 | Zone7(MN-Duluth-MN) ASHRAE901-state_STD2019 |  |  |  |  | 2021-05-06
MN_SO_PSZ-AC:1 Cooling Capacity [ton] | PSZ-AC:1 Cooling Capacity [ton] | 1.8222 | 1.7289 | 1.8255 | 1.7281 | 1.6281 | 1.5217 |  |  |  |  | 2021-05-06
MN_SO_PSZ-AC:2 Cooling Capacity [ton] | PSZ-AC:2 Cooling Capacity [ton] | 1.585 | 1.5219 | 1.5986 | 1.5188 | 1.4436 | 1.2958 |  |  |  |  | 2021-05-06
MN_SO_PSZ-AC:3 Cooling Capacity [ton] | PSZ-AC:3 Cooling Capacity [ton] | 1.1223 | 1.0838 | 1.153 | 1.0899 | 1.0972 | 0.97933 |  |  |  |  | 2021-05-06
MN_SO_PSZ-AC:4 Cooling Capacity [ton] | PSZ-AC:4 Cooling Capacity [ton] | 1.4974 | 1.4187 | 1.4951 | 1.4059 | 1.261 | 1.1692 |  |  |  |  | 2021-05-06
MN_SO_PSZ-AC:5 Cooling Capacity [ton] | PSZ-AC:5 Cooling Capacity [ton] | 1.342 | 1.3017 | 1.3625 | 1.2943 | 1.2985 | 1.1662 |  |  |  |  | 2021-05-06
MN_SO_PSZ-AC:1 Supply Flow Rate [cfm] | PSZ-AC:1 Supply Flow Rate [cfm] | 656.8528 | 614.4752 | 656.8528 | 614.4752 | 656.8528 | 593.2864 |  |  |  |  | 2021-05-06
MN_SO_PSZ-AC:2 Supply Flow Rate [cfm] | PSZ-AC:2 Supply Flow Rate [cfm] | 593.2864 | 550.9088 | 593.2864 | 550.9088 | 572.0976 | 508.5312 |  |  |  |  | 2021-05-06
MN_SO_PSZ-AC:3 Supply Flow Rate [cfm] | PSZ-AC:3 Supply Flow Rate [cfm] | 466.1536 | 444.9648 | 487.3424 | 444.9648 | 487.3424 | 444.9648 |  |  |  |  | 2021-05-06
MN_SO_PSZ-AC:4 Supply Flow Rate [cfm] | PSZ-AC:4 Supply Flow Rate [cfm] | 550.9088 | 508.5312 | 550.9088 | 508.5312 | 487.3424 | 444.9648 |  |  |  |  | 2021-05-06
MN_SO_PSZ-AC:5 Supply Flow Rate [cfm] | PSZ-AC:5 Supply Flow Rate [cfm] | 572.0976 | 550.9088 | 572.0976 | 529.72 | 593.2864 | 529.72 |  |  |  |  | 2021-05-06
MN_SO_PSZ-AC:1 OA Rate [cfm] | PSZ-AC:1 OA Rate [cfm] | 136.9178 | 136.9178 | 136.9178 | 136.9178 | 136.9178 | 136.9178 |  |  |  |  | 2021-05-06
MN_SO_PSZ-AC:2 OA Rate [cfm] | PSZ-AC:2 OA Rate [cfm] | 103.7925 | 103.7925 | 103.7925 | 103.7925 | 103.7925 | 103.7925 |  |  |  |  | 2021-05-06
MN_SO_PSZ-AC:3 OA Rate [cfm] | PSZ-AC:3 OA Rate [cfm] | 61.5711 | 61.5711 | 61.5711 | 61.5711 | 61.5711 | 61.5711 |  |  |  |  | 2021-05-06
MN_SO_PSZ-AC:4 OA Rate [cfm] | PSZ-AC:4 OA Rate [cfm] | 103.7925 | 103.7925 | 103.7925 | 103.7925 | 103.7925 | 103.7925 |  |  |  |  | 2021-05-06
MN_SO_PSZ-AC:5 OA Rate [cfm] | PSZ-AC:5 OA Rate [cfm] | 61.5711 | 61.5711 | 61.5711 | 61.5711 | 61.5711 | 61.5711 |  |  |  |  | 2021-05-06
MN_SO_PSZ-AC:1 heating Capacity [kBtu/hr] | PSZ-AC:1 heating Capacity [kBtu/hr] | 16.4151 | 16.4151 | 16.9359 | 16.9023 | 17.3837 | 17.3837 |  |  |  |  | 2021-05-06
MN_SO_PSZ-AC:2 heating Capacity [kBtu/hr] | PSZ-AC:2 heating Capacity [kBtu/hr] | 22.29 | 22.034 | 24.5222 | 24.2436 | 25.8014 | 25.18 |  |  |  |  | 2021-05-06
MN_SO_PSZ-AC:3 heating Capacity [kBtu/hr] | PSZ-AC:3 heating Capacity [kBtu/hr] | 13.4991 | 13.3578 | 14.9531 | 14.7992 | 15.8082 | 15.4651 |  |  |  |  | 2021-05-06
MN_SO_PSZ-AC:4 heating Capacity [kBtu/hr] | PSZ-AC:4 heating Capacity [kBtu/hr] | 22.1536 | 21.9378 | 24.4602 | 24.2223 | 25.8129 | 25.2827 |  |  |  |  | 2021-05-06
MN_SO_PSZ-AC:5 heating Capacity [kBtu/hr] | PSZ-AC:5 heating Capacity [kBtu/hr] | 13.5496 | 13.4038 | 15.0249 | 14.8641 | 15.8827 | 15.5244 |  |  |  |  | 2021-05-06
id | item | Zone5A(MN-Winona-MN) ASHRAE901-state_STD2016 | Zone5A(MN-Winona-MN) ASHRAE901-state_STD2019 | Zone6A(MN-MinneapolisStPaul-MN) ASHRAE901-state_STD2016 | Zone6A(MN-MinneapolisStPaul-MN) ASHRAE901-state_STD2019 | Zone7(MN-Duluth-MN) ASHRAE901-state_STD2016 | Zone7(MN-Duluth-MN) ASHRAE901-state_STD2019 |  |  |  |  | 2021-05-06
MN_LO_CAV_BAS Supply Flow Rate [cfm] | CAV_BAS Supply Flow Rate [cfm] | 11886.9168 | 10996.9872 | 11971.672 | 11060.5536 | 12247.1264 | 11314.8192 |  |  |  |  | 2021-05-06
MN_LO_VAV_BOT WITH REHEAT Supply Flow Rate [cfm] | VAV_BOT WITH REHEAT Supply Flow Rate [cfm] | 20192.9264 | 19260.6192 | 20553.136 | 19430.1296 | 20976.912 | 19599.64 |  |  |  |  | 2021-05-06
MN_LO_VAV_MID WITH REHEAT Supply Flow Rate [cfm] | VAV_MID WITH REHEAT Supply Flow Rate [cfm] | 188431.9987 | 179447.9475 | 191885.7731 | 181079.4851 | 195424.3027 | 181715.1491 |  |  |  |  | 2021-05-06
MN_LO_VAV_TOP WITH REHEAT Supply Flow Rate [cfm] | VAV_TOP WITH REHEAT Supply Flow Rate [cfm] | 19747.9616 | 18963.976 | 20086.9824 | 19027.5424 | 20065.7936 | 18540.2 |  |  |  |  | 2021-05-06
MN_LO_Supply Air Temp. Reset Flag | Supply Air Temp. Reset Flag | Yes | Yes | Yes | Yes | Yes | Yes |  |  |  |  | 2021-05-06
MN_LO_CAV_BAS OA Rate [cfm] | CAV_BAS OA Rate [cfm] | 2542.8255 | 2542.8255 | 2542.8255 | 2542.8255 | 2542.8255 | 2542.8255 |  |  |  |  | 2021-05-06
MN_LO_VAV_BOT WITH REHEAT OA Rate [cfm] | VAV_BOT WITH REHEAT OA Rate [cfm] | 5377.8022 | 4302.174 | 5377.8022 | 4302.174 | 5377.8022 | 4302.174 |  |  |  |  | 2021-05-06
MN_LO_VAV_MID WITH REHEAT OA Rate [cfm] | VAV_MID WITH REHEAT OA Rate [cfm] | 53777.9373 | 43021.7396 | 53777.9373 | 43021.7396 | 53777.9373 | 43021.7396 |  |  |  |  | 2021-05-06
MN_LO_VAV_TOP WITH REHEAT OA Rate [cfm] | VAV_TOP WITH REHEAT OA Rate [cfm] | 5377.8022 | 4302.174 | 5377.8022 | 4302.174 | 5377.8022 | 4302.174 |  |  |  |  | 2021-05-06
MN_LO_AIRLOOP DATACENTER BASEMENT OA Rate [cfm] | AIRLOOP DATACENTER BASEMENT OA Rate [cfm] | 716.9654 | 716.9654 | 716.9654 | 716.9654 | 716.9654 | 716.9654 |  |  |  |  | 2021-05-06
MN_LO_VAV_bot_WITH_REHEAT ERV Flag | VAV_bot_WITH_REHEAT ERV Flag | Yes | Yes | Yes | Yes | Yes | Yes |  |  |  |  | 2021-05-06
MN_LO_VAV_mid_WITH_REHEAT ERV Flag | VAV_mid_WITH_REHEAT ERV Flag | Yes | Yes | Yes | Yes | Yes | Yes |  |  |  |  | 2021-05-06
MN_LO_VAV_top_WITH_REHEAT ERV Flag | VAV_top_WITH_REHEAT ERV Flag | Yes | Yes | Yes | Yes | Yes | Yes |  |  |  |  | 2021-05-06
MN_LO_COOLSYS1 CHILLER1 Capacity [ton] | COOLSYS1 CHILLER1 Capacity [ton] | 405.5195 | 367.6981 | 409.3666 | 369.4305 | 369.5212 | 333.2367 |  |  |  |  | 2021-05-06
MN_LO_COOLSYS1 CHILLER2 Capacity [ton] | COOLSYS1 CHILLER2 Capacity [ton] | 405.5195 | 367.6981 | 409.3666 | 369.4305 | 369.5212 | 333.2367 |  |  |  |  | 2021-05-06
MN_LO_TOWERWATERSYS COOLTOWER 1 Capacity [ton] | TOWERWATERSYS COOLTOWER 1 Capacity [ton] | 384.9103 | 349.0079 | 388.5596 | 350.6619 | 350.8862 | 316.4398 |  |  |  |  | 2021-05-06
MN_LO_TOWERWATERSYS COOLTOWER 2 Capacity [ton] | TOWERWATERSYS COOLTOWER 2 Capacity [ton] | 384.9103 | 349.0079 | 388.5596 | 350.6619 | 350.8862 | 316.4398 |  |  |  |  | 2021-05-06
MN_LO_HEATSYS1 BOILER Capacity [MMBTU/h] | HEATSYS1 BOILER Capacity [MMBTU/h] | 5137.1464 | 4522.5257 | 5394.6367 | 4755.2509 | 5582.3435 | 4861.949 |  |  |  |  | 2021-05-06
MN_LO_COOLSYS1 PUMP Flow Rate [gal/min] | COOLSYS1 PUMP Flow Rate [gal/min] | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 2021-05-06
MN_LO_COOLSYS1 CHILLER1 PUMP Flow Rate [gal/min] | COOLSYS1 CHILLER1 PUMP Flow Rate [gal/min] | 638.8726 | 579.1962 | 644.9164 | 581.9161 | 581.7893 | 524.6061 |  |  |  |  | 2021-05-06
MN_LO_COOLSYS1 CHILLER2 PUMP Flow Rate [gal/min] | COOLSYS1 CHILLER2 PUMP Flow Rate [gal/min] | 638.8726 | 579.1962 | 644.9164 | 581.9161 | 581.7893 | 524.6061 |  |  |  |  | 2021-05-06
MN_LO_COOLSYS1 PUMP SECONDARY Flow Rate [gal/min] | COOLSYS1 PUMP SECONDARY Flow Rate [gal/min] | 1277.7437 | 1158.3923 | 1289.8327 | 1163.8322 | 1163.5801 | 1049.2121 |  |  |  |  | 2021-05-06
MN_LO_HEATSYS1 PUMP Flow Rate [gal/min] | HEATSYS1 PUMP Flow Rate [gal/min] | 1054.4665 | 928.3075 | 1107.321 | 976.0772 | 1145.85 | 997.9791 |  |  |  |  | 2021-05-06
MN_LO_TOWERWATERSYS PUMP Flow Rate [gal/min] | TOWERWATERSYS PUMP Flow Rate [gal/min] | 2237.2731 | 2028.6829 | 2258.5125 | 2038.1931 | 2038.6686 | 1838.479 |  |  |  |  | 2021-05-06
MN_LO_PLANT CIRC PUMP Flow Rate [gal/min] | PLANT CIRC PUMP Flow Rate [gal/min] | 210.4384 | 209.6601 | 211.4528 | 210.2593 | 212.7573 | 210.9757 |  |  |  |  | 2021-05-06
MN_LO_COOLSYS1 PUMP SECONDARY Pressure setpoint reset [yes,no] | COOLSYS1 PUMP SECONDARY Pressure setpoint reset [yes,no] | pump_ride_on_curve | pump_ride_on_curve | pump_ride_on_curve | pump_ride_on_curve | pump_ride_on_curve | pump_ride_on_curve |  |  |  |  | 2021-05-06
MN_LO_COOLSYS1 CHILLER1 PUMP Pump Power [hp] | COOLSYS1 CHILLER1 PUMP Pump Power [hp] | 3.4465 | 3.0936 | 3.4791 | 3.1082 | 3.1386 | 2.802 |  |  |  |  | 2021-05-06
MN_LO_COOLSYS1 CHILLER2 PUMP Pump Power [hp] | COOLSYS1 CHILLER2 PUMP Pump Power [hp] | 3.4465 | 3.0936 | 3.4791 | 3.1082 | 3.1386 | 2.802 |  |  |  |  | 2021-05-06
MN_LO_COOLSYS1 PUMP SECONDARY Pump Power [hp] | COOLSYS1 PUMP SECONDARY Pump Power [hp] | 20.6789 | 18.5617 | 20.8746 | 18.6489 | 18.8313 | 16.8123 |  |  |  |  | 2021-05-06
MN_LO_HEATSYS1 PUMP Pump Power [hp] | HEATSYS1 PUMP Pump Power [hp] | 22.7929 | 19.8672 | 23.9354 | 20.8896 | 24.7682 | 21.3583 |  |  |  |  | 2021-05-06
MN_LO_TOWERWATERSYS PUMP Pump Power [hp] | TOWERWATERSYS PUMP Pump Power [hp] | 40.0564 | 35.9608 | 40.4364 | 36.1303 | 36.5005 | 32.5905 |  |  |  |  | 2021-05-06
MN_LO_PLANT CIRC PUMP Pump Power [hp] | PLANT CIRC PUMP Pump Power [hp] | 4.541 | 4.4794 | 4.5629 | 4.4922 | 4.591 | 4.5075 |  |  |  |  | 2021-05-06
MN_LO_Datacenter PLANT CIRC PUMP Pump Power [hp] | Datacenter PLANT CIRC PUMP Pump Power [hp] | 4.541 | 4.4794 | 4.5629 | 4.4922 | 4.591 | 4.5075 |  |  |  |  | 2021-05-06
MN_LO_ZN_VAV_BOXes_Max_Reheat_Water_Flow_GPM | ZN_VAV_BOXes_Max_Reheat_Water_Flow_GPM | 503.8699 | 484.3546 | 531.2058 | 510.9779 | 537.4807 | 505.5138 |  |  |  |  | 2021-05-06
MN_LO_COOLSYS1 PUMP SECONDARY VSD | COOLSYS1 PUMP SECONDARY VSD | No | No | No | No | No | No |  |  |  |  | 2021-05-06
MN_LO_HEATSYS1 PUMP VSD | HEATSYS1 PUMP VSD | No | No | No | No | No | No |  |  |  |  | 2021-05-06
MN_LO_DATACENTER BASEMENT Cooling Capacity [ton] | DATACENTER BASEMENT Cooling Capacity [ton] | 122.5207 | 122.2075 | 122.8638 | 122.4897 | 123.248 | 122.8553 |  |  |  |  | 2021-05-06
MN_LO_DATACENTER BOT Cooling Capacity [ton] | DATACENTER BOT Cooling Capacity [ton] | 2.7343 | 2.7103 | 2.7651 | 2.7224 | 2.8102 | 2.7362 |  |  |  |  | 2021-05-06
MN_LO_DATACENTER MID Cooling Capacity [ton] | DATACENTER MID Cooling Capacity [ton] | 26.225 | 26.0125 | 26.562 | 26.1451 | 27.0493 | 26.2875 |  |  |  |  | 2021-05-06
MN_LO_DATACENTER TOP Cooling Capacity [ton] | DATACENTER TOP Cooling Capacity [ton] | 2.6709 | 2.6504 | 2.7031 | 2.6618 | 2.7414 | 2.6654 |  |  |  |  | 2021-05-06
id | item | Zone5A(MN-Winona-MN) ASHRAE901-state_STD2016 | Zone5A(MN-Winona-MN) ASHRAE901-state_STD2019 | Zone6A(MN-MinneapolisStPaul-MN) ASHRAE901-state_STD2016 | Zone6A(MN-MinneapolisStPaul-MN) ASHRAE901-state_STD2019 | Zone7(MN-Duluth-MN) ASHRAE901-state_STD2016 | Zone7(MN-Duluth-MN) ASHRAE901-state_STD2019 |  |  |  |  | 2021-05-06
MN_RS_PSZ-AC:1 Cooling Capacity [ton] | PSZ-AC:1 Cooling Capacity [ton] | 10.1609 | 9.813 | 10.1684 | 9.7685 | 9.0263 | 8.5711 |  |  |  |  | 2021-05-06
MN_RS_PSZ-AC:2 Cooling Capacity [ton] | PSZ-AC:2 Cooling Capacity [ton] | 48.5855 | 46.5932 | 48.8104 | 47.0168 | 43.1592 | 41.4127 |  |  |  |  | 2021-05-06
MN_RS_PSZ-AC:3 Cooling Capacity [ton] | PSZ-AC:3 Cooling Capacity [ton] | 6.3226 | 6.1622 | 6.3251 | 6.1681 | 5.6678 | 5.3806 |  |  |  |  | 2021-05-06
MN_RS_PSZ-AC:4 Cooling Capacity [ton] | PSZ-AC:4 Cooling Capacity [ton] | 5.1116 | 4.9501 | 5.1126 | 4.9454 | 4.6367 | 4.2538 |  |  |  |  | 2021-05-06
MN_RS_PSZ-AC:1 Supply Flow Rate [cfm] | PSZ-AC:1 Supply Flow Rate [cfm] | 3983.4944 | 3708.04 | 3962.3056 | 3686.8512 | 3665.6624 | 3347.8304 |  |  |  |  | 2021-05-06
MN_RS_PSZ-AC:2 Supply Flow Rate [cfm] | PSZ-AC:2 Supply Flow Rate [cfm] | 15594.9568 | 14705.0272 | 15594.9568 | 14789.7824 | 15383.0688 | 14535.5168 |  |  |  |  | 2021-05-06
MN_RS_PSZ-AC:3 Supply Flow Rate [cfm] | PSZ-AC:3 Supply Flow Rate [cfm] | 2309.5792 | 2246.0128 | 2330.768 | 2246.0128 | 2309.5792 | 2161.2576 |  |  |  |  | 2021-05-06
MN_RS_PSZ-AC:4 Supply Flow Rate [cfm] | PSZ-AC:4 Supply Flow Rate [cfm] | 1758.6704 | 1695.104 | 1779.8592 | 1695.104 | 1779.8592 | 1589.16 |  |  |  |  | 2021-05-06
MN_RS_PSZ-AC:1 OA Rate [cfm] | PSZ-AC:1 OA Rate [cfm] | 490.669 | 490.669 | 490.669 | 490.669 | 490.669 | 490.669 |  |  |  |  | 2021-05-06
MN_RS_PSZ-AC:2 OA Rate [cfm] | PSZ-AC:2 OA Rate [cfm] | 4005.1282 | 4005.1282 | 4005.1282 | 4005.1282 | 4005.1282 | 4005.1282 |  |  |  |  | 2021-05-06
MN_RS_PSZ-AC:3 OA Rate [cfm] | PSZ-AC:3 OA Rate [cfm] | 377.3937 | 377.3937 | 377.3937 | 377.3937 | 377.3937 | 377.3937 |  |  |  |  | 2021-05-06
MN_RS_PSZ-AC:4 OA Rate [cfm] | PSZ-AC:4 OA Rate [cfm] | 377.3937 | 377.3937 | 377.3937 | 377.3937 | 377.3937 | 377.3937 |  |  |  |  | 2021-05-06
MN_RS_PSZ-AC:1 OA Damper [gravity, motorized] | PSZ-AC:1 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | motorized | motorized |  |  |  |  | 2021-05-06
MN_RS_PSZ-AC:2 OA Damper [gravity, motorized] | PSZ-AC:2 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | motorized | motorized |  |  |  |  | 2021-05-06
MN_RS_PSZ-AC:3 OA Damper [gravity, motorized] | PSZ-AC:3 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | motorized | motorized |  |  |  |  | 2021-05-06
MN_RS_PSZ-AC:4 OA Damper [gravity, motorized] | PSZ-AC:4 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | motorized | motorized |  |  |  |  | 2021-05-06
MN_RS_PSZ-AC:1 Heating Capacity [kBtu/hr] | PSZ-AC:1 Heating Capacity [kBtu/hr] | 184.4101 | 173.4464 | 184.4405 | 173.0577 | 172.0552 | 163.6014 |  |  |  |  | 2021-05-06
MN_RS_PSZ-AC:2 Heating Capacity [kBtu/hr] | PSZ-AC:2 Heating Capacity [kBtu/hr] | 885.5659 | 848.7111 | 894.6483 | 863.593 | 893.6659 | 860.1924 |  |  |  |  | 2021-05-06
MN_RS_PSZ-AC:3 Heating Capacity [kBtu/hr] | PSZ-AC:3 Heating Capacity [kBtu/hr] | 115.5414 | 112.8558 | 116.8167 | 113.8507 | 114.0648 | 110.5299 |  |  |  |  | 2021-05-06
MN_RS_PSZ-AC:4 Heating Capacity [kBtu/hr] | PSZ-AC:4 Heating Capacity [kBtu/hr] | 95.2822 | 92.3573 | 96.5088 | 93.1763 | 97.6005 | 90.9448 |  |  |  |  | 2021-05-06
id | item | Zone5A(MN-Winona-MN) ASHRAE901-state_STD2016 | Zone5A(MN-Winona-MN) ASHRAE901-state_STD2019 | Zone6A(MN-MinneapolisStPaul-MN) ASHRAE901-state_STD2016 | Zone6A(MN-MinneapolisStPaul-MN) ASHRAE901-state_STD2019 | Zone7(MN-Duluth-MN) ASHRAE901-state_STD2016 | Zone7(MN-Duluth-MN) ASHRAE901-state_STD2019 |  |  |  |  | 2021-05-06
MN_PS_VAV_POD_1 Cooling Capacity [ton] | VAV_POD_1 Cooling Capacity [ton] | 19.4903 | 18.808 | 19.6031 | 18.672 | 19.3734 | 18.2398 |  |  |  |  | 2021-05-06
MN_PS_VAV_POD_2 Cooling Capacity [ton] | VAV_POD_2 Cooling Capacity [ton] | 19.3555 | 18.6209 | 19.4064 | 18.542 | 19.0577 | 18.1911 |  |  |  |  | 2021-05-06
MN_PS_VAV_POD_3 Cooling Capacity [ton] | VAV_POD_3 Cooling Capacity [ton] | 17.8497 | 16.9896 | 17.9355 | 16.8565 | 17.6605 | 16.1446 |  |  |  |  | 2021-05-06
MN_PS_VAV_OTHER Cooling Capacity [ton] | VAV_OTHER Cooling Capacity [ton] | 27.247 | 25.6624 | 27.374 | 25.449 | 25.3114 | 22.0976 |  |  |  |  | 2021-05-06
MN_PS_PSZ-AC_1:6 Cooling Capacity [ton] | PSZ-AC_1:6 Cooling Capacity [ton] | 8.2455 | 7.9816 | 8.2842 | 7.9985 | 7.6681 | 7.3582 |  |  |  |  | 2021-05-06
MN_PS_PSZ-AC_2:5 Cooling Capacity [ton] | PSZ-AC_2:5 Cooling Capacity [ton] | 5.5591 | 5.5307 | 5.5934 | 5.5084 | 5.7367 | 5.6659 |  |  |  |  | 2021-05-06
MN_PS_PSZ-AC_2:7 Cooling Capacity [ton] | PSZ-AC_2:7 Cooling Capacity [ton] | 10.5074 | 10.5074 | 10.5074 | 10.5074 | 10.5074 | 10.5074 |  |  |  |  | 2021-05-06
MN_PS_VAV_POD_1 Supply Flow Rate [cfm] | VAV_POD_1 Supply Flow Rate [cfm] | 5848.1088 | 5636.2208 | 5890.4864 | 5593.8432 | 5805.7312 | 5466.7104 |  |  |  |  | 2021-05-06
MN_PS_VAV_POD_2 Supply Flow Rate [cfm] | VAV_POD_2 Supply Flow Rate [cfm] | 5805.7312 | 5593.8432 | 5826.92 | 5572.6544 | 5720.976 | 5466.7104 |  |  |  |  | 2021-05-06
MN_PS_VAV_POD_3 Supply Flow Rate [cfm] | VAV_POD_3 Supply Flow Rate [cfm] | 5360.7664 | 5106.5008 | 5381.9552 | 5064.1232 | 5297.2 | 4852.2352 |  |  |  |  | 2021-05-06
MN_PS_VAV_OTHER Supply Flow Rate [cfm] | VAV_OTHER Supply Flow Rate [cfm] | 8178.8768 | 7691.5344 | 8221.2544 | 7627.968 | 7966.9888 | 7161.8144 |  |  |  |  | 2021-05-06
MN_PS_PSZ-AC_2:5 Supply Flow Rate [cfm] | PSZ-AC_2:5 Supply Flow Rate [cfm] | 1673.9152 | 1652.7264 | 1673.9152 | 1652.7264 | 1716.2928 | 1695.104 |  |  |  |  | 2021-05-06
MN_PS_PSZ-AC_1:6 Supply Flow Rate [cfm] | PSZ-AC_1:6 Supply Flow Rate [cfm] | 2606.2224 | 2479.0896 | 2606.2224 | 2500.2784 | 2648.6 | 2500.2784 |  |  |  |  | 2021-05-06
MN_PS_PSZ-AC_2:7 Supply Flow Rate [cfm] | PSZ-AC_2:7 Supply Flow Rate [cfm] | 3157.1312 | 3157.1312 | 3157.1312 | 3157.1312 | 3157.1312 | 3157.1312 |  |  |  |  | 2021-05-06
MN_PS_Supply Air Temp. Reset Flag | Supply Air Temp. Reset Flag | Yes | Yes | Yes | Yes | Yes | Yes |  |  |  |  | 2021-05-06
MN_PS_VAV_POD_1 OA Rate [cfm] | VAV_POD_1 OA Rate [cfm] | 5848.5326 | 5643.9759 | 5880.1251 | 5603.1663 | 5813.6346 | 5473.4484 |  |  |  |  | 2021-05-06
MN_PS_VAV_POD_2 OA Rate [cfm] | VAV_POD_2 OA Rate [cfm] | 5806.049 | 5587.8256 | 5823.5298 | 5564.1577 | 5717.7341 | 5458.8494 |  |  |  |  | 2021-05-06
MN_PS_VAV_POD_3 OA Rate [cfm] | VAV_POD_3 OA Rate [cfm] | 5354.6217 | 5098.3007 | 5380.5567 | 5058.3599 | 5297.3271 | 4844.7344 |  |  |  |  | 2021-05-06
MN_PS_VAV_OTHER OA Rate [cfm] | VAV_OTHER OA Rate [cfm] | 3736.1787 | 2988.8921 | 3736.1787 | 2988.8921 | 3736.1787 | 2988.8921 |  |  |  |  | 2021-05-06
MN_PS_PSZ-AC_2:5 OA Rate [cfm] | PSZ-AC_2:5 OA Rate [cfm] | 1152.7343 | 1152.7343 | 1152.7343 | 1152.7343 | 1152.7343 | 1152.7343 |  |  |  |  | 2021-05-06
MN_PS_PSZ-AC_1:6 OA Rate [cfm] | PSZ-AC_1:6 OA Rate [cfm] | 539.9118 | 539.9118 | 539.9118 | 539.9118 | 539.9118 | 539.9118 |  |  |  |  | 2021-05-06
MN_PS_PSZ-AC_2:7 OA Rate [cfm] | PSZ-AC_2:7 OA Rate [cfm] | 3153.0841 | 3153.0841 | 3153.0841 | 3153.0841 | 3153.0841 | 3153.0841 |  |  |  |  | 2021-05-06
MN_PS_VAV_POD_1 OA Damper [gravity, motorized] | VAV_POD_1 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | motorized | motorized |  |  |  |  | 2021-05-06
MN_PS_VAV_POD_2 OA Damper [gravity, motorized] | VAV_POD_2 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | motorized | motorized |  |  |  |  | 2021-05-06
MN_PS_VAV_POD_3 OA Damper [gravity, motorized] | VAV_POD_3 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | motorized | motorized |  |  |  |  | 2021-05-06
MN_PS_VAV_OTHER OA Damper [gravity, motorized] | VAV_OTHER OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | motorized | motorized |  |  |  |  | 2021-05-06
MN_PS_PSZ-AC_2:5 OA Damper [gravity, motorized] | PSZ-AC_2:5 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | motorized | motorized |  |  |  |  | 2021-05-06
MN_PS_PSZ-AC_1:6 OA Damper [gravity, motorized] | PSZ-AC_1:6 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | motorized | motorized |  |  |  |  | 2021-05-06
MN_PS_PSZ-AC_2:7 OA Damper [gravity, motorized] | PSZ-AC_2:7 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | motorized | motorized |  |  |  |  | 2021-05-06
MN_PS_VAV_POD_1 (economizer) | VAV_POD_1 (economizer) | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb |  |  |  |  | 2021-05-06
MN_PS_VAV_POD_2 (economizer) | VAV_POD_2 (economizer) | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb |  |  |  |  | 2021-05-06
MN_PS_VAV_POD_3 (economizer) | VAV_POD_3 (economizer) | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb |  |  |  |  | 2021-05-06
MN_PS_VAV_OTHER (economizer) | VAV_OTHER (economizer) | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb |  |  |  |  | 2021-05-06
MN_PS_PSZ-AC_2:5 (economizer) | PSZ-AC_2:5 (economizer) | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb |  |  |  |  | 2021-05-06
MN_PS_PSZ-AC_1:6 (economizer) | PSZ-AC_1:6 (economizer) | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb |  |  |  |  | 2021-05-06
MN_PS_PSZ-AC_2:7 (economizer) | PSZ-AC_2:7 (economizer) | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb |  |  |  |  | 2021-05-06
MN_PS_VAV_Pod_1_ERV Flag | VAV_Pod_1_ERV Flag | Yes | Yes | Yes | Yes | Yes | Yes |  |  |  |  | 2021-05-06
MN_PS_VAV_Pod_2_ERV Flag | VAV_Pod_2_ERV Flag | Yes | Yes | Yes | Yes | Yes | Yes |  |  |  |  | 2021-05-06
MN_PS_VAV_Pod_3_ERV Flag | VAV_Pod_3_ERV Flag | Yes | Yes | Yes | Yes | Yes | Yes |  |  |  |  | 2021-05-06
MN_PS_VAV_OTHER_ERV Flag | VAV_OTHER_ERV Flag | Yes | Yes | Yes | Yes | Yes | Yes |  |  |  |  | 2021-05-06
MN_PS_PSZ_AC_2_5_ERV Flag | PSZ_AC_2_5_ERV Flag | No | No | No | No | Yes | Yes |  |  |  |  | 2021-05-06
MN_PS_PSZ_AC_2_7_ERV Flag | PSZ_AC_2_7_ERV Flag | Yes | Yes | Yes | Yes | Yes | Yes |  |  |  |  | 2021-05-06
MN_PS_HEATSYS1 Capacity [MMBTU/h] | HEATSYS1 Capacity [MMBTU/h] | 1.2723 | 1.2226 | 1.3486 | 1.2898 | 1.3772 | 1.2928 |  |  |  |  | 2021-05-06
MN_PS_HEATSYS1 Flow Rate [gal/min] | HEATSYS1 Flow Rate [gal/min] | 130.5778 | 125.4813 | 138.4126 | 132.3786 | 141.3478 | 132.685 |  |  |  |  | 2021-05-06
MN_PS_VAV_POD_1 Fan Power [hp] | VAV_POD_1 Fan Power [hp] | 8.6286 | 8.3266 | 8.6785 | 8.2664 | 8.5768 | 8.075 |  |  |  |  | 2021-05-06
MN_PS_VAV_POD_2 Fan Power [hp] | VAV_POD_2 Fan Power [hp] | 8.569 | 8.2437 | 8.5915 | 8.2088 | 8.4371 | 8.0534 |  |  |  |  | 2021-05-06
MN_PS_VAV_POD_3 Fan Power [hp] | VAV_POD_3 Fan Power [hp] | 7.9023 | 7.5215 | 7.9403 | 7.4626 | 7.8185 | 7.1474 |  |  |  |  | 2021-05-06
MN_PS_VAV_OTHER Fan Power [hp] | VAV_OTHER Fan Power [hp] | 11.9712 | 11.275 | 12.027 | 11.1813 | 11.6511 | 10.4807 |  |  |  |  | 2021-05-06
MN_PS_HEATSYS1 Pump Power [hp] | HEATSYS1 Pump Power [hp] | 2.8225 | 2.6855 | 2.9919 | 2.8331 | 3.0553 | 2.8397 |  |  |  |  | 2021-05-06
MN_PS_PSZ-AC_1:6 Heating Capacity [kBtu/hr] | PSZ-AC_1:6 Heating Capacity [kBtu/hr] | 221.3505 | 212.7782 | 223.4311 | 214.1547 | 224.4219 | 214.0705 |  |  |  |  | 2021-05-06
MN_PS_PSZ-AC_2:5 Heating Capacity [kBtu/hr] | PSZ-AC_2:5 Heating Capacity [kBtu/hr] | 156.8401 | 156.5315 | 160.9982 | 160.0828 | 166.3583 | 165.6111 |  |  |  |  | 2021-05-06
MN_PS_PSZ-AC_2:7 Heating Capacity [kBtu/hr] | PSZ-AC_2:7 Heating Capacity [kBtu/hr] | 378.0237 | 378.0237 | 388.715 | 388.715 | 400.3308 | 400.3308 |  |  |  |  | 2021-05-06
MN_PS_ZN_VAV_BOXes_Max_Reheat_Water_Flow_GPM | ZN_VAV_BOXes_Max_Reheat_Water_Flow_GPM | 77.7392 | 75.0735 | 82.4367 | 79.5889 | 82.864 | 78.5762 |  |  |  |  | 2021-05-06
id | item | Zone5A(MN-Winona-MN) ASHRAE901-state_STD2016 | Zone5A(MN-Winona-MN) ASHRAE901-state_STD2019 | Zone6A(MN-MinneapolisStPaul-MN) ASHRAE901-state_STD2016 | Zone6A(MN-MinneapolisStPaul-MN) ASHRAE901-state_STD2019 | Zone7(MN-Duluth-MN) ASHRAE901-state_STD2016 | Zone7(MN-Duluth-MN) ASHRAE901-state_STD2019 |  |  |  |  | 2021-05-06
MN_SH_SAC_FRONTOFFICE Cooling Capacity [ton] | SAC_FRONTOFFICE Cooling Capacity [ton] | 2.2407 | 2.1329 | 2.3202 | 2.194 | 2.0306 | 1.9075 |  |  |  |  | 2021-05-06
MN_SH_SAC_FRONTLOUNGE Cooling Capacity [ton] | SAC_FRONTLOUNGE Cooling Capacity [ton] | 6.0492 | 5.7414 | 6.1581 | 5.8341 | 5.5316 | 5.2777 |  |  |  |  | 2021-05-06
MN_SH_SAC_MEETINGROOM Cooling Capacity [ton] | SAC_MEETINGROOM Cooling Capacity [ton] | 2.9044 | 2.8088 | 2.9389 | 2.844 | 2.8661 | 2.791 |  |  |  |  | 2021-05-06
MN_SH_SAC_EXC_EMPLGE_RESTRM Cooling Capacity [ton] | SAC_EXC_EMPLGE_RESTRM Cooling Capacity [ton] | 5.9055 | 5.8646 | 5.9259 | 5.8787 | 5.555 | 5.4521 |  |  |  |  | 2021-05-06
MN_SH_SAC_FO_ADDAQ SUPPLY FAN Supply Flow Rate [cfm] | SAC_FO_ADDAQ SUPPLY FAN Supply Flow Rate [cfm] | 783.9856 | 720.4192 | 783.9856 | 741.608 | 762.7968 | 699.2304 |  |  |  |  | 2021-05-06
MN_SH_SAC_FL_ADDAQ SUPPLY FAN Supply Flow Rate [cfm] | SAC_FL_ADDAQ SUPPLY FAN Supply Flow Rate [cfm] | 1822.2368 | 1716.2928 | 1843.4256 | 1758.6704 | 1822.2368 | 1716.2928 |  |  |  |  | 2021-05-06
MN_SH_SAC_MR_ADDAQ SUPPLY FAN Supply Flow Rate [cfm] | SAC_MR_ADDAQ SUPPLY FAN Supply Flow Rate [cfm] | 868.7408 | 847.552 | 889.9296 | 847.552 | 868.7408 | 847.552 |  |  |  |  | 2021-05-06
MN_SH_SAC_EXC_ADDAQ SUPPLY FAN Supply Flow Rate [cfm] | SAC_EXC_ADDAQ SUPPLY FAN Supply Flow Rate [cfm] | 2224.824 | 2203.6352 | 2224.824 | 2203.6352 | 2267.2016 | 2224.824 |  |  |  |  | 2021-05-06
MN_SH_SAC_Exc_EmpLge_RestRm OA Rate [cfm] | SAC_Exc_EmpLge_RestRm OA Rate [cfm] | 199.9928 | 199.9928 | 199.9928 | 199.9928 | 199.9928 | 199.9928 |  |  |  |  | 2021-05-06
MN_SH_SAC_FrontLounge OA Rate [cfm] | SAC_FrontLounge OA Rate [cfm] | 500.0133 | 500.0133 | 500.0133 | 500.0133 | 500.0133 | 500.0133 |  |  |  |  | 2021-05-06
MN_SH_SAC_FrontOffice OA Rate [cfm] | SAC_FrontOffice OA Rate [cfm] | 119.2938 | 119.2938 | 119.2938 | 119.2938 | 119.2938 | 119.2938 |  |  |  |  | 2021-05-06
MN_SH_SAC_MeetingRoom OA Rate [cfm] | SAC_MeetingRoom OA Rate [cfm] | 267.7629 | 267.7629 | 267.7629 | 267.7629 | 267.7629 | 267.7629 |  |  |  |  | 2021-05-06
MN_SH_SAC_FrontLounge OA Damper [gravity, motorized] | SAC_FrontLounge OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | motorized | motorized |  |  |  |  | 2021-05-06
MN_SH_SAC_FrontOffice (economizer) | SAC_FrontOffice (economizer) | No | No | No | No | No | No |  |  |  |  | 2021-05-06
MN_SH_SAC_FrontLounge (economizer) | SAC_FrontLounge (economizer) | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb |  |  |  |  | 2021-05-06
MN_SH_SAC_MeetingRoom (economizer) | SAC_MeetingRoom (economizer) | No | No | No | No | No | No |  |  |  |  | 2021-05-06
MN_SH_SAC_Exc_EmpLge_RestRm (economizer) | SAC_Exc_EmpLge_RestRm (economizer) | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb |  |  |  |  | 2021-05-06
MN_SH_SAC_FRONTOFFICE Heating Capacity [kBtu/hr] | SAC_FRONTOFFICE Heating Capacity [kBtu/hr] | 38.0599 | 36.0581 | 38.6167 | 36.6643 | 37.5557 | 35.533 |  |  |  |  | 2021-05-06
MN_SH_SAC_FRONTLOUNGE Heating Capacity [kBtu/hr] | SAC_FRONTLOUNGE Heating Capacity [kBtu/hr] | 107.2252 | 103.9045 | 109.7849 | 106.3119 | 109.4253 | 105.7512 |  |  |  |  | 2021-05-06
MN_SH_SAC_MEETINGROOM Heating Capacity [kBtu/hr] | SAC_MEETINGROOM Heating Capacity [kBtu/hr] | 53.8054 | 52.7743 | 54.9444 | 53.927 | 55.1035 | 54.028 |  |  |  |  | 2021-05-06
MN_SH_SAC_EXC_EMPLGE_RESTRM Heating Capacity [kBtu/hr] | SAC_EXC_EMPLGE_RESTRM Heating Capacity [kBtu/hr] | 96.8718 | 96.2109 | 97.095 | 96.3393 | 97.3794 | 96.4065 |  |  |  |  | 2021-05-06
id | item | Zone5A(MN-Winona-MN) ASHRAE901-state_STD2016 | Zone5A(MN-Winona-MN) ASHRAE901-state_STD2019 | Zone6A(MN-MinneapolisStPaul-MN) ASHRAE901-state_STD2016 | Zone6A(MN-MinneapolisStPaul-MN) ASHRAE901-state_STD2019 | Zone7(MN-Duluth-MN) ASHRAE901-state_STD2016 | Zone7(MN-Duluth-MN) ASHRAE901-state_STD2019 |  |  |  |  | 2021-05-06
MN_MA_SPLIT GSW COOLING COIL Cooling Capacity [ton] | SPLIT GSW COOLING COIL Cooling Capacity [ton] | 0.84753 | 0.83286 | 0.8944 | 0.86362 | 0.76729 | 0.70652 |  |  |  |  | 2021-05-06
MN_MA_SPLIT GNW COOLING COIL Cooling Capacity [ton] | SPLIT GNW COOLING COIL Cooling Capacity [ton] | 0.79696 | 0.78314 | 0.84038 | 0.81267 | 0.69939 | 0.65041 |  |  |  |  | 2021-05-06
MN_MA_SPLIT OFFICE COOLING COIL Cooling Capacity [ton] | SPLIT OFFICE COOLING COIL Cooling Capacity [ton] | 1.7407 | 1.6144 | 1.8132 | 1.6678 | 1.6554 | 1.4149 |  |  |  |  | 2021-05-06
MN_MA_SPLIT GNE COOLING COIL Cooling Capacity [ton] | SPLIT GNE COOLING COIL Cooling Capacity [ton] | 0.67806 | 0.66604 | 0.71991 | 0.69721 | 0.59345 | 0.59552 |  |  |  |  | 2021-05-06
MN_MA_SPLIT GN1 COOLING COIL Cooling Capacity [ton] | SPLIT GN1 COOLING COIL Cooling Capacity [ton] | 0.57514 | 0.56559 | 0.59878 | 0.58422 | 0.48291 | 0.45794 |  |  |  |  | 2021-05-06
MN_MA_SPLIT GN2 COOLING COIL Cooling Capacity [ton] | SPLIT GN2 COOLING COIL Cooling Capacity [ton] | 0.57267 | 0.56317 | 0.59616 | 0.58176 | 0.48015 | 0.45554 |  |  |  |  | 2021-05-06
MN_MA_SPLIT GS1 COOLING COIL Cooling Capacity [ton] | SPLIT GS1 COOLING COIL Cooling Capacity [ton] | 0.63202 | 0.62135 | 0.66109 | 0.64276 | 0.55728 | 0.52261 |  |  |  |  | 2021-05-06
MN_MA_SPLIT GS2 COOLING COIL Cooling Capacity [ton] | SPLIT GS2 COOLING COIL Cooling Capacity [ton] | 0.66168 | 0.64718 | 0.69427 | 0.6697 | 0.592 | 0.5523 |  |  |  |  | 2021-05-06
MN_MA_SPLIT MSW COOLING COIL Cooling Capacity [ton] | SPLIT MSW COOLING COIL Cooling Capacity [ton] | 2.0357 | 2.0028 | 2.1732 | 2.0992 | 1.9661 | 1.8189 |  |  |  |  | 2021-05-06
MN_MA_SPLIT MNW COOLING COIL Cooling Capacity [ton] | SPLIT MNW COOLING COIL Cooling Capacity [ton] | 1.9462 | 1.9151 | 2.0766 | 2.0083 | 1.8395 | 1.7149 |  |  |  |  | 2021-05-06
MN_MA_SPLIT MSE COOLING COIL Cooling Capacity [ton] | SPLIT MSE COOLING COIL Cooling Capacity [ton] | 1.7485 | 1.7186 | 1.8914 | 1.8241 | 1.7331 | 1.5739 |  |  |  |  | 2021-05-06
MN_MA_SPLIT MNE COOLING COIL Cooling Capacity [ton] | SPLIT MNE COOLING COIL Cooling Capacity [ton] | 1.5759 | 1.5417 | 1.7063 | 1.636 | 1.4884 | 1.3704 |  |  |  |  | 2021-05-06
MN_MA_SPLIT MN1 COOLING COIL Cooling Capacity [ton] | SPLIT MN1 COOLING COIL Cooling Capacity [ton] | 1.2811 | 1.2626 | 1.3459 | 1.317 | 1.1437 | 1.0915 |  |  |  |  | 2021-05-06
MN_MA_SPLIT MN2 COOLING COIL Cooling Capacity [ton] | SPLIT MN2 COOLING COIL Cooling Capacity [ton] | 1.2742 | 1.256 | 1.3386 | 1.3102 | 1.1357 | 1.0846 |  |  |  |  | 2021-05-06
MN_MA_SPLIT MS1 COOLING COIL Cooling Capacity [ton] | SPLIT MS1 COOLING COIL Cooling Capacity [ton] | 1.3827 | 1.3626 | 1.4585 | 1.4235 | 1.3611 | 1.2066 |  |  |  |  | 2021-05-06
MN_MA_SPLIT MS2 COOLING COIL Cooling Capacity [ton] | SPLIT MS2 COOLING COIL Cooling Capacity [ton] | 1.3765 | 1.3566 | 1.4521 | 1.4176 | 1.3665 | 1.2513 |  |  |  |  | 2021-05-06
MN_MA_SPLIT TSW COOLING COIL Cooling Capacity [ton] | SPLIT TSW COOLING COIL Cooling Capacity [ton] | 1.2611 | 1.2411 | 1.3386 | 1.2973 | 1.1855 | 1.1029 |  |  |  |  | 2021-05-06
MN_MA_SPLIT TNW COOLING COIL Cooling Capacity [ton] | SPLIT TNW COOLING COIL Cooling Capacity [ton] | 1.2049 | 1.188 | 1.2832 | 1.2447 | 1.1151 | 1.0446 |  |  |  |  | 2021-05-06
MN_MA_SPLIT TSE COOLING COIL Cooling Capacity [ton] | SPLIT TSE COOLING COIL Cooling Capacity [ton] | 1.1216 | 1.106 | 1.2024 | 1.167 | 1.074 | 0.98489 |  |  |  |  | 2021-05-06
MN_MA_SPLIT TNE COOLING COIL Cooling Capacity [ton] | SPLIT TNE COOLING COIL Cooling Capacity [ton] | 1.0118 | 0.9992 | 1.0803 | 1.0559 | 0.87449 | 0.84604 |  |  |  |  | 2021-05-06
MN_MA_SPLIT TN1 COOLING COIL Cooling Capacity [ton] | SPLIT TN1 COOLING COIL Cooling Capacity [ton] | 0.81598 | 0.80661 | 0.85675 | 0.84118 | 0.70296 | 0.67893 |  |  |  |  | 2021-05-06
MN_MA_SPLIT TN2 COOLING COIL Cooling Capacity [ton] | SPLIT TN2 COOLING COIL Cooling Capacity [ton] | 0.80864 | 0.79945 | 0.84911 | 0.83408 | 0.69456 | 0.67164 |  |  |  |  | 2021-05-06
MN_MA_SPLIT TS1 COOLING COIL Cooling Capacity [ton] | SPLIT TS1 COOLING COIL Cooling Capacity [ton] | 0.93745 | 0.92513 | 0.98704 | 0.96091 | 0.88085 | 0.8128 |  |  |  |  | 2021-05-06
MN_MA_SPLIT TS2 COOLING COIL Cooling Capacity [ton] | SPLIT TS2 COOLING COIL Cooling Capacity [ton] | 0.94054 | 0.92818 | 0.98949 | 0.96423 | 0.88532 | 0.81581 |  |  |  |  | 2021-05-06
MN_MA_Split GN1 Furnace with DX Cooling OA Rate [cfm] | Split GN1 Furnace with DX Cooling OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 |  |  |  |  | 2021-05-06
MN_MA_Split GN2 Furnace with DX Cooling OA Rate [cfm] | Split GN2 Furnace with DX Cooling OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 |  |  |  |  | 2021-05-06
MN_MA_Split GNE Furnace with DX Cooling OA Rate [cfm] | Split GNE Furnace with DX Cooling OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 |  |  |  |  | 2021-05-06
MN_MA_Split GNW Furnace with DX Cooling OA Rate [cfm] | Split GNW Furnace with DX Cooling OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 |  |  |  |  | 2021-05-06
MN_MA_Split GS1 Furnace with DX Cooling OA Rate [cfm] | Split GS1 Furnace with DX Cooling OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 |  |  |  |  | 2021-05-06
MN_MA_Split GS2 Furnace with DX Cooling OA Rate [cfm] | Split GS2 Furnace with DX Cooling OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 |  |  |  |  | 2021-05-06
MN_MA_Split GSW Furnace with DX Cooling OA Rate [cfm] | Split GSW Furnace with DX Cooling OA Rate [cfm] | 56.9945 | 56.9945 | 56.9945 | 56.9945 | 56.9945 | 56.9945 |  |  |  |  | 2021-05-06
MN_MA_Split MN1 Furnace with DX Cooling OA Rate [cfm] | Split MN1 Furnace with DX Cooling OA Rate [cfm] | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824 |  |  |  |  | 2021-05-06
MN_MA_Split MN2 Furnace with DX Cooling OA Rate [cfm] | Split MN2 Furnace with DX Cooling OA Rate [cfm] | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824 |  |  |  |  | 2021-05-06
MN_MA_Split MNE Furnace with DX Cooling OA Rate [cfm] | Split MNE Furnace with DX Cooling OA Rate [cfm] | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824 |  |  |  |  | 2021-05-06
MN_MA_Split MNW Furnace with DX Cooling OA Rate [cfm] | Split MNW Furnace with DX Cooling OA Rate [cfm] | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824 |  |  |  |  | 2021-05-06
MN_MA_Split MS1 Furnace with DX Cooling OA Rate [cfm] | Split MS1 Furnace with DX Cooling OA Rate [cfm] | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824 |  |  |  |  | 2021-05-06
MN_MA_Split MS2 Furnace with DX Cooling OA Rate [cfm] | Split MS2 Furnace with DX Cooling OA Rate [cfm] | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824 |  |  |  |  | 2021-05-06
MN_MA_Split MSE Furnace with DX Cooling OA Rate [cfm] | Split MSE Furnace with DX Cooling OA Rate [cfm] | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824 |  |  |  |  | 2021-05-06
MN_MA_Split MSW Furnace with DX Cooling OA Rate [cfm] | Split MSW Furnace with DX Cooling OA Rate [cfm] | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824 |  |  |  |  | 2021-05-06
MN_MA_Split Office Furnace with DX Cooling OA Rate [cfm] | Split Office Furnace with DX Cooling OA Rate [cfm] | 80.7372 | 80.7372 | 80.7372 | 80.7372 | 80.7372 | 80.7372 |  |  |  |  | 2021-05-06
MN_MA_Split TN1 Furnace with DX Cooling OA Rate [cfm] | Split TN1 Furnace with DX Cooling OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 |  |  |  |  | 2021-05-06
MN_MA_Split TN2 Furnace with DX Cooling OA Rate [cfm] | Split TN2 Furnace with DX Cooling OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 |  |  |  |  | 2021-05-06
MN_MA_Split TNE Furnace with DX Cooling OA Rate [cfm] | Split TNE Furnace with DX Cooling OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 |  |  |  |  | 2021-05-06
MN_MA_Split TNW Furnace with DX Cooling OA Rate [cfm] | Split TNW Furnace with DX Cooling OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 |  |  |  |  | 2021-05-06
MN_MA_Split TS1 Furnace with DX Cooling OA Rate [cfm] | Split TS1 Furnace with DX Cooling OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 |  |  |  |  | 2021-05-06
MN_MA_Split TS2 Furnace with DX Cooling OA Rate [cfm] | Split TS2 Furnace with DX Cooling OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 |  |  |  |  | 2021-05-06
MN_MA_Split TSE Furnace with DX Cooling OA Rate [cfm] | Split TSE Furnace with DX Cooling OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 |  |  |  |  | 2021-05-06
MN_MA_Split TSW Furnace with DX Cooling OA Rate [cfm] | Split TSW Furnace with DX Cooling OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 |  |  |  |  | 2021-05-06
MN_MA_SPLIT GSW HEATING COIL Heating Capacity [kBtu/hr] | SPLIT GSW HEATING COIL Heating Capacity [kBtu/hr] | 11.259 | 11.3209 | 12.4363 | 12.4957 | 13.2652 | 13.1306 |  |  |  |  | 2021-05-06
MN_MA_SPLIT GNW HEATING COIL Heating Capacity [kBtu/hr] | SPLIT GNW HEATING COIL Heating Capacity [kBtu/hr] | 11.1613 | 11.2233 | 12.3454 | 12.405 | 13.1679 | 13.0283 |  |  |  |  | 2021-05-06
MN_MA_SPLIT OFFICE HEATING COIL Heating Capacity [kBtu/hr] | SPLIT OFFICE HEATING COIL Heating Capacity [kBtu/hr] | 24.8021 | 25.0711 | 26.0662 | 26.1485 | 27.051 | 26.9045 |  |  |  |  | 2021-05-06
MN_MA_SPLIT GNE HEATING COIL Heating Capacity [kBtu/hr] | SPLIT GNE HEATING COIL Heating Capacity [kBtu/hr] | 11.1396 | 11.2017 | 12.3151 | 12.3747 | 13.1372 | 13.001 |  |  |  |  | 2021-05-06
MN_MA_SPLIT GN1 HEATING COIL Heating Capacity [kBtu/hr] | SPLIT GN1 HEATING COIL Heating Capacity [kBtu/hr] | 8.5064 | 8.5685 | 9.3119 | 9.3715 | 9.9536 | 9.8832 |  |  |  |  | 2021-05-06
MN_MA_SPLIT GN2 HEATING COIL Heating Capacity [kBtu/hr] | SPLIT GN2 HEATING COIL Heating Capacity [kBtu/hr] | 8.5058 | 8.5679 | 9.311 | 9.3706 | 9.9527 | 9.8823 |  |  |  |  | 2021-05-06
MN_MA_SPLIT GS1 HEATING COIL Heating Capacity [kBtu/hr] | SPLIT GS1 HEATING COIL Heating Capacity [kBtu/hr] | 8.4525 | 8.5145 | 9.2441 | 9.3036 | 9.8836 | 9.8181 |  |  |  |  | 2021-05-06
MN_MA_SPLIT GS2 HEATING COIL Heating Capacity [kBtu/hr] | SPLIT GS2 HEATING COIL Heating Capacity [kBtu/hr] | 8.9739 | 9.0359 | 9.768 | 9.8284 | 10.4124 | 10.347 |  |  |  |  | 2021-05-06
MN_MA_SPLIT MSW HEATING COIL Heating Capacity [kBtu/hr] | SPLIT MSW HEATING COIL Heating Capacity [kBtu/hr] | 18.5634 | 18.6917 | 22.0004 | 22.13 | 23.5812 | 23.3135 |  |  |  |  | 2021-05-06
MN_MA_SPLIT MNW HEATING COIL Heating Capacity [kBtu/hr] | SPLIT MNW HEATING COIL Heating Capacity [kBtu/hr] | 18.6538 | 18.7818 | 22.1204 | 22.2499 | 23.7025 | 23.4223 |  |  |  |  | 2021-05-06
MN_MA_SPLIT MSE HEATING COIL Heating Capacity [kBtu/hr] | SPLIT MSE HEATING COIL Heating Capacity [kBtu/hr] | 18.5117 | 18.6399 | 21.9295 | 22.0591 | 23.51 | 23.2504 |  |  |  |  | 2021-05-06
MN_MA_SPLIT MNE HEATING COIL Heating Capacity [kBtu/hr] | SPLIT MNE HEATING COIL Heating Capacity [kBtu/hr] | 18.602 | 18.73 | 22.0495 | 22.179 | 23.6312 | 23.3591 |  |  |  |  | 2021-05-06
MN_MA_SPLIT MN1 HEATING COIL Heating Capacity [kBtu/hr] | SPLIT MN1 HEATING COIL Heating Capacity [kBtu/hr] | 13.4787 | 13.6058 | 15.7413 | 15.8677 | 16.8815 | 16.7472 |  |  |  |  | 2021-05-06
MN_MA_SPLIT MN2 HEATING COIL Heating Capacity [kBtu/hr] | SPLIT MN2 HEATING COIL Heating Capacity [kBtu/hr] | 13.4774 | 13.6044 | 15.7394 | 15.8659 | 16.8797 | 16.7456 |  |  |  |  | 2021-05-06
MN_MA_SPLIT MS1 HEATING COIL Heating Capacity [kBtu/hr] | SPLIT MS1 HEATING COIL Heating Capacity [kBtu/hr] | 13.3986 | 13.5257 | 15.6322 | 15.7586 | 16.772 | 16.6499 |  |  |  |  | 2021-05-06
MN_MA_SPLIT MS2 HEATING COIL Heating Capacity [kBtu/hr] | SPLIT MS2 HEATING COIL Heating Capacity [kBtu/hr] | 13.3973 | 13.5244 | 15.6303 | 15.7568 | 16.7702 | 16.6483 |  |  |  |  | 2021-05-06
MN_MA_SPLIT TSW HEATING COIL Heating Capacity [kBtu/hr] | SPLIT TSW HEATING COIL Heating Capacity [kBtu/hr] | 13.0882 | 13.1503 | 15.428 | 15.4901 | 16.2299 | 16.0974 |  |  |  |  | 2021-05-06
MN_MA_SPLIT TNW HEATING COIL Heating Capacity [kBtu/hr] | SPLIT TNW HEATING COIL Heating Capacity [kBtu/hr] | 13.1435 | 13.2057 | 15.4989 | 15.5611 | 16.3014 | 16.1627 |  |  |  |  | 2021-05-06
MN_MA_SPLIT TSE HEATING COIL Heating Capacity [kBtu/hr] | SPLIT TSE HEATING COIL Heating Capacity [kBtu/hr] | 13.0602 | 13.1223 | 15.3903 | 15.4525 | 16.1921 | 16.064 |  |  |  |  | 2021-05-06
MN_MA_SPLIT TNE HEATING COIL Heating Capacity [kBtu/hr] | SPLIT TNE HEATING COIL Heating Capacity [kBtu/hr] | 13.1155 | 13.1777 | 15.4612 | 15.5234 | 16.2636 | 16.1292 |  |  |  |  | 2021-05-06
MN_MA_SPLIT TN1 HEATING COIL Heating Capacity [kBtu/hr] | SPLIT TN1 HEATING COIL Heating Capacity [kBtu/hr] | 10.4876 | 10.5497 | 12.0291 | 12.0912 | 12.5082 | 12.4414 |  |  |  |  | 2021-05-06
MN_MA_SPLIT TN2 HEATING COIL Heating Capacity [kBtu/hr] | SPLIT TN2 HEATING COIL Heating Capacity [kBtu/hr] | 10.4868 | 10.549 | 12.0281 | 12.0902 | 12.5071 | 12.4404 |  |  |  |  | 2021-05-06
MN_MA_SPLIT TS1 HEATING COIL Heating Capacity [kBtu/hr] | SPLIT TS1 HEATING COIL Heating Capacity [kBtu/hr] | 10.426 | 10.4881 | 11.9519 | 12.014 | 12.4305 | 12.3697 |  |  |  |  | 2021-05-06
MN_MA_SPLIT TS2 HEATING COIL Heating Capacity [kBtu/hr] | SPLIT TS2 HEATING COIL Heating Capacity [kBtu/hr] | 10.4253 | 10.4873 | 11.9509 | 12.013 | 12.4294 | 12.3687 |  |  |  |  | 2021-05-06
MN_MA_Split_GSW ERV Flag | Split_GSW ERV Flag | Yes | Yes | Yes | Yes | Yes | Yes |  |  |  |  | 2021-05-06
MN_MA_Split_GNW ERV Flag | Split_GNW ERV Flag | Yes | Yes | Yes | Yes | Yes | Yes |  |  |  |  | 2021-05-06
MN_MA_Split_GNE ERV Flag | Split_GNE ERV Flag | Yes | Yes | Yes | Yes | Yes | Yes |  |  |  |  | 2021-05-06
MN_MA_Split_GN1 ERV Flag | Split_GN1 ERV Flag | Yes | Yes | Yes | Yes | Yes | Yes |  |  |  |  | 2021-05-06
MN_MA_Split_GN2 ERV Flag | Split_GN2 ERV Flag | Yes | Yes | Yes | Yes | Yes | Yes |  |  |  |  | 2021-05-06
MN_MA_Split_GS1 ERV Flag | Split_GS1 ERV Flag | Yes | Yes | Yes | Yes | Yes | Yes |  |  |  |  | 2021-05-06
MN_MA_Split_GS2 ERV Flag | Split_GS2 ERV Flag | Yes | Yes | Yes | Yes | Yes | Yes |  |  |  |  | 2021-05-06
MN_MA_Split_MSW ERV Flag | Split_MSW ERV Flag | Yes | Yes | Yes | Yes | Yes | Yes |  |  |  |  | 2021-05-06
MN_MA_Split_MNW ERV Flag | Split_MNW ERV Flag | Yes | Yes | Yes | Yes | Yes | Yes |  |  |  |  | 2021-05-06
MN_MA_Split_MSE ERV Flag | Split_MSE ERV Flag | Yes | Yes | Yes | Yes | Yes | Yes |  |  |  |  | 2021-05-06
MN_MA_Split_MNE ERV Flag | Split_MNE ERV Flag | Yes | Yes | Yes | Yes | Yes | Yes |  |  |  |  | 2021-05-06
MN_MA_Split_MN1 ERV Flag | Split_MN1 ERV Flag | Yes | Yes | Yes | Yes | Yes | Yes |  |  |  |  | 2021-05-06
MN_MA_Split_MN2 ERV Flag | Split_MN2 ERV Flag | Yes | Yes | Yes | Yes | Yes | Yes |  |  |  |  | 2021-05-06
MN_MA_Split_MS1 ERV Flag | Split_MS1 ERV Flag | Yes | Yes | Yes | Yes | Yes | Yes |  |  |  |  | 2021-05-06
MN_MA_Split_MS2 ERV Flag | Split_MS2 ERV Flag | Yes | Yes | Yes | Yes | Yes | Yes |  |  |  |  | 2021-05-06
MN_MA_Split_TSW ERV Flag | Split_TSW ERV Flag | Yes | Yes | Yes | Yes | Yes | Yes |  |  |  |  | 2021-05-06
MN_MA_Split_TNW ERV Flag | Split_TNW ERV Flag | Yes | Yes | Yes | Yes | Yes | Yes |  |  |  |  | 2021-05-06
MN_MA_Split_TSE ERV Flag | Split_TSE ERV Flag | Yes | Yes | Yes | Yes | Yes | Yes |  |  |  |  | 2021-05-06
MN_MA_Split_TNE ERV Flag | Split_TNE ERV Flag | Yes | Yes | Yes | Yes | Yes | Yes |  |  |  |  | 2021-05-06
MN_MA_Split_TN1 ERV Flag | Split_TN1 ERV Flag | Yes | Yes | Yes | Yes | Yes | Yes |  |  |  |  | 2021-05-06
MN_MA_Split_TN2 ERV Flag | Split_TN2 ERV Flag | Yes | Yes | Yes | Yes | Yes | Yes |  |  |  |  | 2021-05-06
MN_MA_Split_TS1 ERV Flag | Split_TS1 ERV Flag | Yes | Yes | Yes | Yes | Yes | Yes |  |  |  |  | 2021-05-06
MN_MA_Split_TS2 ERV Flag | Split_TS2 ERV Flag | Yes | Yes | Yes | Yes | Yes | Yes |  |  |  |  | 2021-05-06
id | item | Zone3A(MO-Memphis-TN) ASHRAE901-state_STD2016 | Zone3A(MO-Memphis-TN) ASHRAE901-state_STD2019 | Zone4A(MO-StLouis-MO) ASHRAE901-state_STD2016 | Zone4A(MO-StLouis-MO) ASHRAE901-state_STD2019 | Zone5A(MO-Kirksville-MO) ASHRAE901-state_STD2016 | Zone5A(MO-Kirksville-MO) ASHRAE901-state_STD2019 |  |  |  |  | 2021-05-06
MO_SO_PSZ-AC:1 Cooling Capacity [ton] | PSZ-AC:1 Cooling Capacity [ton] | 2.0998 | 2.0018 | 2.0297 | 1.9336 | 1.9557 | 1.86 |  |  |  |  | 2021-05-06
MO_SO_PSZ-AC:2 Cooling Capacity [ton] | PSZ-AC:2 Cooling Capacity [ton] | 1.8625 | 1.7879 | 1.8157 | 1.7487 | 1.7039 | 1.638 |  |  |  |  | 2021-05-06
MO_SO_PSZ-AC:3 Cooling Capacity [ton] | PSZ-AC:3 Cooling Capacity [ton] | 1.2349 | 1.1938 | 1.2589 | 1.2191 | 1.2027 | 1.1631 |  |  |  |  | 2021-05-06
MO_SO_PSZ-AC:4 Cooling Capacity [ton] | PSZ-AC:4 Cooling Capacity [ton] | 1.8457 | 1.7674 | 1.773 | 1.6842 | 1.6528 | 1.5667 |  |  |  |  | 2021-05-06
MO_SO_PSZ-AC:5 Cooling Capacity [ton] | PSZ-AC:5 Cooling Capacity [ton] | 1.4414 | 1.3943 | 1.4801 | 1.4385 | 1.4214 | 1.3803 |  |  |  |  | 2021-05-06
MO_SO_PSZ-AC:1 Supply Flow Rate [cfm] | PSZ-AC:1 Supply Flow Rate [cfm] | 678.0416 | 635.664 | 678.0416 | 614.4752 | 678.0416 | 614.4752 |  |  |  |  | 2021-05-06
MO_SO_PSZ-AC:2 Supply Flow Rate [cfm] | PSZ-AC:2 Supply Flow Rate [cfm] | 635.664 | 593.2864 | 614.4752 | 593.2864 | 593.2864 | 572.0976 |  |  |  |  | 2021-05-06
MO_SO_PSZ-AC:3 Supply Flow Rate [cfm] | PSZ-AC:3 Supply Flow Rate [cfm] | 466.1536 | 444.9648 | 487.3424 | 466.1536 | 487.3424 | 466.1536 |  |  |  |  | 2021-05-06
MO_SO_PSZ-AC:4 Supply Flow Rate [cfm] | PSZ-AC:4 Supply Flow Rate [cfm] | 635.664 | 593.2864 | 593.2864 | 572.0976 | 572.0976 | 529.72 |  |  |  |  | 2021-05-06
MO_SO_PSZ-AC:5 Supply Flow Rate [cfm] | PSZ-AC:5 Supply Flow Rate [cfm] | 550.9088 | 529.72 | 572.0976 | 550.9088 | 572.0976 | 550.9088 |  |  |  |  | 2021-05-06
MO_SO_PSZ-AC:1 OA Rate [cfm] | PSZ-AC:1 OA Rate [cfm] | 136.9178 | 136.9178 | 136.9178 | 136.9178 | 136.9178 | 136.9178 |  |  |  |  | 2021-05-06
MO_SO_PSZ-AC:2 OA Rate [cfm] | PSZ-AC:2 OA Rate [cfm] | 103.7925 | 103.7925 | 103.7925 | 103.7925 | 103.7925 | 103.7925 |  |  |  |  | 2021-05-06
MO_SO_PSZ-AC:3 OA Rate [cfm] | PSZ-AC:3 OA Rate [cfm] | 61.5711 | 61.5711 | 61.5711 | 61.5711 | 61.5711 | 61.5711 |  |  |  |  | 2021-05-06
MO_SO_PSZ-AC:4 OA Rate [cfm] | PSZ-AC:4 OA Rate [cfm] | 103.7925 | 103.7925 | 103.7925 | 103.7925 | 103.7925 | 103.7925 |  |  |  |  | 2021-05-06
MO_SO_PSZ-AC:5 OA Rate [cfm] | PSZ-AC:5 OA Rate [cfm] | 61.5711 | 61.5711 | 61.5711 | 61.5711 | 61.5711 | 61.5711 |  |  |  |  | 2021-05-06
MO_SO_PSZ-AC:1 heating Capacity [kBtu/hr] | PSZ-AC:1 heating Capacity [kBtu/hr] | 12.7643 | 12.7643 | 14.5075 | 14.5075 | 15.3819 | 15.3819 |  |  |  |  | 2021-05-06
MO_SO_PSZ-AC:2 heating Capacity [kBtu/hr] | PSZ-AC:2 heating Capacity [kBtu/hr] | 18.303 | 18.0567 | 20.6305 | 20.4123 | 22.0614 | 21.8184 |  |  |  |  | 2021-05-06
MO_SO_PSZ-AC:3 heating Capacity [kBtu/hr] | PSZ-AC:3 heating Capacity [kBtu/hr] | 11.2873 | 11.1443 | 12.6384 | 12.5177 | 13.5182 | 13.3773 |  |  |  |  | 2021-05-06
MO_SO_PSZ-AC:4 heating Capacity [kBtu/hr] | PSZ-AC:4 heating Capacity [kBtu/hr] | 18.1282 | 17.9165 | 20.5381 | 20.351 | 21.9678 | 21.7594 |  |  |  |  | 2021-05-06
MO_SO_PSZ-AC:5 heating Capacity [kBtu/hr] | PSZ-AC:5 heating Capacity [kBtu/hr] | 11.2873 | 11.1443 | 12.6977 | 12.5712 | 13.5182 | 13.3773 |  |  |  |  | 2021-05-06
id | item | Zone3A(MO-Memphis-TN) ASHRAE901-state_STD2016 | Zone3A(MO-Memphis-TN) ASHRAE901-state_STD2019 | Zone4A(MO-StLouis-MO) ASHRAE901-state_STD2016 | Zone4A(MO-StLouis-MO) ASHRAE901-state_STD2019 | Zone5A(MO-Kirksville-MO) ASHRAE901-state_STD2016 | Zone5A(MO-Kirksville-MO) ASHRAE901-state_STD2019 |  |  |  |  | 2021-05-06
MO_LO_CAV_BAS Supply Flow Rate [cfm] | CAV_BAS Supply Flow Rate [cfm] | 11569.0848 | 10700.344 | 11950.4832 | 11081.7424 | 12035.2384 | 11145.3088 |  |  |  |  | 2021-05-06
MO_LO_VAV_BOT WITH REHEAT Supply Flow Rate [cfm] | VAV_BOT WITH REHEAT Supply Flow Rate [cfm] | 19557.2624 | 18603.7664 | 20468.3808 | 19514.8848 | 20616.7024 | 19642.0176 |  |  |  |  | 2021-05-06
MO_LO_VAV_MID WITH REHEAT Supply Flow Rate [cfm] | VAV_MID WITH REHEAT Supply Flow Rate [cfm] | 182520.3235 | 173430.3283 | 191440.8083 | 182372.0019 | 192479.0595 | 183304.3091 |  |  |  |  | 2021-05-06
MO_LO_VAV_TOP WITH REHEAT Supply Flow Rate [cfm] | VAV_TOP WITH REHEAT Supply Flow Rate [cfm] | 18985.1648 | 18179.9904 | 20129.36 | 19324.1856 | 20298.8704 | 19493.696 |  |  |  |  | 2021-05-06
MO_LO_Supply Air Temp. Reset Flag | Supply Air Temp. Reset Flag | No | Yes | Yes | Yes | Yes | Yes |  |  |  |  | 2021-05-06
MO_LO_CAV_BAS OA Rate [cfm] | CAV_BAS OA Rate [cfm] | 2542.8255 | 2542.8255 | 2542.8255 | 2542.8255 | 2542.8255 | 2542.8255 |  |  |  |  | 2021-05-06
MO_LO_VAV_BOT WITH REHEAT OA Rate [cfm] | VAV_BOT WITH REHEAT OA Rate [cfm] | 5377.8022 | 4302.174 | 5377.8022 | 4302.174 | 5377.8022 | 4302.174 |  |  |  |  | 2021-05-06
MO_LO_VAV_MID WITH REHEAT OA Rate [cfm] | VAV_MID WITH REHEAT OA Rate [cfm] | 53777.9373 | 43021.7396 | 53777.9373 | 43021.7396 | 53777.9373 | 43021.7396 |  |  |  |  | 2021-05-06
MO_LO_VAV_TOP WITH REHEAT OA Rate [cfm] | VAV_TOP WITH REHEAT OA Rate [cfm] | 5377.8022 | 4302.174 | 5377.8022 | 4302.174 | 5377.8022 | 4302.174 |  |  |  |  | 2021-05-06
MO_LO_AIRLOOP DATACENTER BASEMENT OA Rate [cfm] | AIRLOOP DATACENTER BASEMENT OA Rate [cfm] | 716.9654 | 716.9654 | 716.9654 | 716.9654 | 716.9654 | 716.9654 |  |  |  |  | 2021-05-06
MO_LO_VAV_bot_WITH_REHEAT ERV Flag | VAV_bot_WITH_REHEAT ERV Flag | Yes | Yes | Yes | Yes | Yes | Yes |  |  |  |  | 2021-05-06
MO_LO_VAV_mid_WITH_REHEAT ERV Flag | VAV_mid_WITH_REHEAT ERV Flag | Yes | Yes | Yes | Yes | Yes | Yes |  |  |  |  | 2021-05-06
MO_LO_VAV_top_WITH_REHEAT ERV Flag | VAV_top_WITH_REHEAT ERV Flag | Yes | Yes | Yes | Yes | Yes | Yes |  |  |  |  | 2021-05-06
MO_LO_COOLSYS1 CHILLER1 Capacity [ton] | COOLSYS1 CHILLER1 Capacity [ton] | 454.5843 | 406.7483 | 456.1557 | 409.5927 | 437.8577 | 394.0977 |  |  |  |  | 2021-05-06
MO_LO_COOLSYS1 CHILLER2 Capacity [ton] | COOLSYS1 CHILLER2 Capacity [ton] | 454.5843 | 406.7483 | 456.1557 | 409.5927 | 437.8577 | 394.0977 |  |  |  |  | 2021-05-06
MO_LO_TOWERWATERSYS COOLTOWER 1 Capacity [ton] | TOWERWATERSYS COOLTOWER 1 Capacity [ton] | 431.485 | 386.0786 | 432.9683 | 388.7828 | 415.6013 | 374.0674 |  |  |  |  | 2021-05-06
MO_LO_TOWERWATERSYS COOLTOWER 2 Capacity [ton] | TOWERWATERSYS COOLTOWER 2 Capacity [ton] | 431.485 | 386.0786 | 432.9683 | 388.7828 | 415.6013 | 374.0674 |  |  |  |  | 2021-05-06
MO_LO_HEATSYS1 BOILER Capacity [MMBTU/h] | HEATSYS1 BOILER Capacity [MMBTU/h] | 3989.7855 | 3545.0706 | 4600.1432 | 4076.0788 | 4948.5273 | 4352.4036 |  |  |  |  | 2021-05-06
MO_LO_COOLSYS1 PUMP Flow Rate [gal/min] | COOLSYS1 PUMP Flow Rate [gal/min] | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 2021-05-06
MO_LO_COOLSYS1 CHILLER1 PUMP Flow Rate [gal/min] | COOLSYS1 CHILLER1 PUMP Flow Rate [gal/min] | 716.6502 | 638.3353 | 718.9802 | 642.5642 | 689.9741 | 620.9269 |  |  |  |  | 2021-05-06
MO_LO_COOLSYS1 CHILLER2 PUMP Flow Rate [gal/min] | COOLSYS1 CHILLER2 PUMP Flow Rate [gal/min] | 716.6502 | 638.3353 | 718.9802 | 642.5642 | 689.9741 | 620.9269 |  |  |  |  | 2021-05-06
MO_LO_COOLSYS1 PUMP SECONDARY Flow Rate [gal/min] | COOLSYS1 PUMP SECONDARY Flow Rate [gal/min] | 1433.2988 | 1276.6706 | 1437.9619 | 1285.1283 | 1379.9466 | 1241.8554 |  |  |  |  | 2021-05-06
MO_LO_HEATSYS1 PUMP Flow Rate [gal/min] | HEATSYS1 PUMP Flow Rate [gal/min] | 818.9561 | 727.6725 | 944.2402 | 836.6688 | 1015.7505 | 893.3876 |  |  |  |  | 2021-05-06
MO_LO_TOWERWATERSYS PUMP Flow Rate [gal/min] | TOWERWATERSYS PUMP Flow Rate [gal/min] | 2507.9966 | 2244.0888 | 2516.7143 | 2259.7806 | 2415.7477 | 2174.1888 |  |  |  |  | 2021-05-06
MO_LO_PLANT CIRC PUMP Flow Rate [gal/min] | PLANT CIRC PUMP Flow Rate [gal/min] | 208.8534 | 207.9547 | 211.223 | 210.4463 | 212.2121 | 211.3609 |  |  |  |  | 2021-05-06
MO_LO_COOLSYS1 PUMP SECONDARY Pressure setpoint reset [yes,no] | COOLSYS1 PUMP SECONDARY Pressure setpoint reset [yes,no] | pump_ride_on_curve | pump_ride_on_curve | pump_ride_on_curve | pump_ride_on_curve | pump_ride_on_curve | pump_ride_on_curve |  |  |  |  | 2021-05-06
MO_LO_COOLSYS1 CHILLER1 PUMP Pump Power [hp] | COOLSYS1 CHILLER1 PUMP Pump Power [hp] | 3.8661 | 3.4095 | 3.8787 | 3.4321 | 3.7222 | 3.3165 |  |  |  |  | 2021-05-06
MO_LO_COOLSYS1 CHILLER2 PUMP Pump Power [hp] | COOLSYS1 CHILLER2 PUMP Pump Power [hp] | 3.8661 | 3.4095 | 3.8787 | 3.4321 | 3.7222 | 3.3165 |  |  |  |  | 2021-05-06
MO_LO_COOLSYS1 PUMP SECONDARY Pump Power [hp] | COOLSYS1 PUMP SECONDARY Pump Power [hp] | 23.1964 | 20.457 | 23.2719 | 20.5925 | 22.333 | 19.8991 |  |  |  |  | 2021-05-06
MO_LO_HEATSYS1 PUMP Pump Power [hp] | HEATSYS1 PUMP Pump Power [hp] | 17.7022 | 15.5733 | 20.4103 | 17.906 | 21.956 | 19.1199 |  |  |  |  | 2021-05-06
MO_LO_TOWERWATERSYS PUMP Pump Power [hp] | TOWERWATERSYS PUMP Pump Power [hp] | 44.9029 | 39.78 | 45.0581 | 40.0581 | 43.2507 | 38.5427 |  |  |  |  | 2021-05-06
MO_LO_PLANT CIRC PUMP Pump Power [hp] | PLANT CIRC PUMP Pump Power [hp] | 4.5068 | 4.443 | 4.5579 | 4.4962 | 4.5792 | 4.5157 |  |  |  |  | 2021-05-06
MO_LO_Datacenter PLANT CIRC PUMP Pump Power [hp] | Datacenter PLANT CIRC PUMP Pump Power [hp] | 4.5068 | 4.443 | 4.5579 | 4.4962 | 4.5792 | 4.5157 |  |  |  |  | 2021-05-06
MO_LO_ZN_VAV_BOXes_Max_Reheat_Water_Flow_GPM | ZN_VAV_BOXes_Max_Reheat_Water_Flow_GPM | 455.0206 | 435.773 | 489.9475 | 471.1107 | 513.4089 | 493.7283 |  |  |  |  | 2021-05-06
MO_LO_COOLSYS1 PUMP SECONDARY VSD | COOLSYS1 PUMP SECONDARY VSD | No | No | No | No | No | No |  |  |  |  | 2021-05-06
MO_LO_HEATSYS1 PUMP VSD | HEATSYS1 PUMP VSD | No | No | No | No | No | No |  |  |  |  | 2021-05-06
MO_LO_DATACENTER BASEMENT Cooling Capacity [ton] | DATACENTER BASEMENT Cooling Capacity [ton] | 122.4493 | 122.092 | 123.1994 | 122.8857 | 123.5402 | 123.1755 |  |  |  |  | 2021-05-06
MO_LO_DATACENTER BOT Cooling Capacity [ton] | DATACENTER BOT Cooling Capacity [ton] | 2.6582 | 2.6307 | 2.7273 | 2.7034 | 2.7576 | 2.7335 |  |  |  |  | 2021-05-06
MO_LO_DATACENTER MID Cooling Capacity [ton] | DATACENTER MID Cooling Capacity [ton] | 25.3207 | 25.0675 | 26.1324 | 25.922 | 26.4554 | 26.2414 |  |  |  |  | 2021-05-06
MO_LO_DATACENTER TOP Cooling Capacity [ton] | DATACENTER TOP Cooling Capacity [ton] | 2.5611 | 2.5413 | 2.666 | 2.6457 | 2.6969 | 2.6763 |  |  |  |  | 2021-05-06
id | item | Zone3A(MO-Memphis-TN) ASHRAE901-state_STD2016 | Zone3A(MO-Memphis-TN) ASHRAE901-state_STD2019 | Zone4A(MO-StLouis-MO) ASHRAE901-state_STD2016 | Zone4A(MO-StLouis-MO) ASHRAE901-state_STD2019 | Zone5A(MO-Kirksville-MO) ASHRAE901-state_STD2016 | Zone5A(MO-Kirksville-MO) ASHRAE901-state_STD2019 |  |  |  |  | 2021-05-06
MO_RS_PSZ-AC:1 Cooling Capacity [ton] | PSZ-AC:1 Cooling Capacity [ton] | 11.384 | 11.0037 | 11.3604 | 10.9772 | 10.7905 | 10.4489 |  |  |  |  | 2021-05-06
MO_RS_PSZ-AC:2 Cooling Capacity [ton] | PSZ-AC:2 Cooling Capacity [ton] | 51.9006 | 48.9007 | 53.6286 | 50.6436 | 52.3761 | 50.1913 |  |  |  |  | 2021-05-06
MO_RS_PSZ-AC:3 Cooling Capacity [ton] | PSZ-AC:3 Cooling Capacity [ton] | 7.0894 | 6.924 | 7.1931 | 7.0241 | 6.814 | 6.6462 |  |  |  |  | 2021-05-06
MO_RS_PSZ-AC:4 Cooling Capacity [ton] | PSZ-AC:4 Cooling Capacity [ton] | 5.8565 | 5.6875 | 5.9605 | 5.7725 | 5.5696 | 5.4031 |  |  |  |  | 2021-05-06
MO_RS_PSZ-AC:1 Supply Flow Rate [cfm] | PSZ-AC:1 Supply Flow Rate [cfm] | 4216.5712 | 3962.3056 | 4280.1376 | 4025.872 | 4153.0048 | 3877.5504 |  |  |  |  | 2021-05-06
MO_RS_PSZ-AC:2 Supply Flow Rate [cfm] | PSZ-AC:2 Supply Flow Rate [cfm] | 15573.768 | 14683.8384 | 16103.488 | 15192.3696 | 15976.3552 | 15065.2368 |  |  |  |  | 2021-05-06
MO_RS_PSZ-AC:3 Supply Flow Rate [cfm] | PSZ-AC:3 Supply Flow Rate [cfm] | 2351.9568 | 2288.3904 | 2436.712 | 2373.1456 | 2373.1456 | 2309.5792 |  |  |  |  | 2021-05-06
MO_RS_PSZ-AC:4 Supply Flow Rate [cfm] | PSZ-AC:4 Supply Flow Rate [cfm] | 1822.2368 | 1737.4816 | 1906.992 | 1822.2368 | 1822.2368 | 1737.4816 |  |  |  |  | 2021-05-06
MO_RS_PSZ-AC:1 OA Rate [cfm] | PSZ-AC:1 OA Rate [cfm] | 490.669 | 490.669 | 490.669 | 490.669 | 490.669 | 490.669 |  |  |  |  | 2021-05-06
MO_RS_PSZ-AC:2 OA Rate [cfm] | PSZ-AC:2 OA Rate [cfm] | 4005.1282 | 4005.1282 | 4005.1282 | 4005.1282 | 4005.1282 | 4005.1282 |  |  |  |  | 2021-05-06
MO_RS_PSZ-AC:3 OA Rate [cfm] | PSZ-AC:3 OA Rate [cfm] | 377.3937 | 377.3937 | 377.3937 | 377.3937 | 377.3937 | 377.3937 |  |  |  |  | 2021-05-06
MO_RS_PSZ-AC:4 OA Rate [cfm] | PSZ-AC:4 OA Rate [cfm] | 377.3937 | 377.3937 | 377.3937 | 377.3937 | 377.3937 | 377.3937 |  |  |  |  | 2021-05-06
MO_RS_PSZ-AC:1 OA Damper [gravity, motorized] | PSZ-AC:1 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | motorized | motorized |  |  |  |  | 2021-05-06
MO_RS_PSZ-AC:2 OA Damper [gravity, motorized] | PSZ-AC:2 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | motorized | motorized |  |  |  |  | 2021-05-06
MO_RS_PSZ-AC:3 OA Damper [gravity, motorized] | PSZ-AC:3 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | motorized | motorized |  |  |  |  | 2021-05-06
MO_RS_PSZ-AC:4 OA Damper [gravity, motorized] | PSZ-AC:4 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | motorized | motorized |  |  |  |  | 2021-05-06
MO_RS_PSZ-AC:1 Heating Capacity [kBtu/hr] | PSZ-AC:1 Heating Capacity [kBtu/hr] | 182.3901 | 172.1883 | 189.8628 | 179.5287 | 185.4741 | 174.8726 |  |  |  |  | 2021-05-06
MO_RS_PSZ-AC:2 Heating Capacity [kBtu/hr] | PSZ-AC:2 Heating Capacity [kBtu/hr] | 786.3374 | 748.2071 | 852.6338 | 814.6412 | 867.1459 | 829.3975 |  |  |  |  | 2021-05-06
MO_RS_PSZ-AC:3 Heating Capacity [kBtu/hr] | PSZ-AC:3 Heating Capacity [kBtu/hr] | 108.1506 | 105.3786 | 115.0155 | 112.2588 | 114.1538 | 111.3979 |  |  |  |  | 2021-05-06
MO_RS_PSZ-AC:4 Heating Capacity [kBtu/hr] | PSZ-AC:4 Heating Capacity [kBtu/hr] | 88.4535 | 85.576 | 95.2672 | 92.3329 | 94.16 | 91.2544 |  |  |  |  | 2021-05-06
id | item | Zone3A(MO-Memphis-TN) ASHRAE901-state_STD2016 | Zone3A(MO-Memphis-TN) ASHRAE901-state_STD2019 | Zone4A(MO-StLouis-MO) ASHRAE901-state_STD2016 | Zone4A(MO-StLouis-MO) ASHRAE901-state_STD2019 | Zone5A(MO-Kirksville-MO) ASHRAE901-state_STD2016 | Zone5A(MO-Kirksville-MO) ASHRAE901-state_STD2019 |  |  |  |  | 2021-05-06
MO_PS_VAV_POD_1 Cooling Capacity [ton] | VAV_POD_1 Cooling Capacity [ton] | 18.9453 | 18.2722 | 19.9864 | 19.1475 | 19.693 | 19.0119 |  |  |  |  | 2021-05-06
MO_PS_VAV_POD_2 Cooling Capacity [ton] | VAV_POD_2 Cooling Capacity [ton] | 18.9361 | 18.2425 | 19.7904 | 18.8772 | 19.5391 | 18.7486 |  |  |  |  | 2021-05-06
MO_PS_VAV_POD_3 Cooling Capacity [ton] | VAV_POD_3 Cooling Capacity [ton] | 17.2252 | 16.3627 | 18.2881 | 17.3041 | 18.0702 | 17.1712 |  |  |  |  | 2021-05-06
MO_PS_VAV_OTHER Cooling Capacity [ton] | VAV_OTHER Cooling Capacity [ton] | 26.3812 | 24.7958 | 28.0422 | 26.4424 | 27.8805 | 26.2787 |  |  |  |  | 2021-05-06
MO_PS_PSZ-AC_1:6 Cooling Capacity [ton] | PSZ-AC_1:6 Cooling Capacity [ton] | 8.4312 | 8.053 | 8.7122 | 8.3376 | 8.7444 | 8.4219 |  |  |  |  | 2021-05-06
MO_PS_PSZ-AC_2:5 Cooling Capacity [ton] | PSZ-AC_2:5 Cooling Capacity [ton] | 5.2754 | 5.1016 | 5.7662 | 5.7396 | 5.7696 | 5.7459 |  |  |  |  | 2021-05-06
MO_PS_PSZ-AC_2:7 Cooling Capacity [ton] | PSZ-AC_2:7 Cooling Capacity [ton] | 10.5074 | 10.5074 | 10.5074 | 10.5074 | 10.5074 | 10.5074 |  |  |  |  | 2021-05-06
MO_PS_VAV_POD_1 Supply Flow Rate [cfm] | VAV_POD_1 Supply Flow Rate [cfm] | 5678.5984 | 5487.8992 | 5996.4304 | 5742.1648 | 5911.6752 | 5699.7872 |  |  |  |  | 2021-05-06
MO_PS_VAV_POD_2 Supply Flow Rate [cfm] | VAV_POD_2 Supply Flow Rate [cfm] | 5678.5984 | 5466.7104 | 5932.864 | 5657.4096 | 5869.2976 | 5636.2208 |  |  |  |  | 2021-05-06
MO_PS_VAV_POD_3 Supply Flow Rate [cfm] | VAV_POD_3 Supply Flow Rate [cfm] | 5170.0672 | 4915.8016 | 5487.8992 | 5191.256 | 5424.3328 | 5148.8784 |  |  |  |  | 2021-05-06
MO_PS_VAV_OTHER Supply Flow Rate [cfm] | VAV_OTHER Supply Flow Rate [cfm] | 7924.6112 | 7437.2688 | 8411.9536 | 7924.6112 | 8369.576 | 7882.2336 |  |  |  |  | 2021-05-06
MO_PS_PSZ-AC_2:5 Supply Flow Rate [cfm] | PSZ-AC_2:5 Supply Flow Rate [cfm] | 1589.16 | 1525.5936 | 1737.4816 | 1716.2928 | 1737.4816 | 1716.2928 |  |  |  |  | 2021-05-06
MO_PS_PSZ-AC_1:6 Supply Flow Rate [cfm] | PSZ-AC_1:6 Supply Flow Rate [cfm] | 2521.4672 | 2415.5232 | 2606.2224 | 2500.2784 | 2648.6 | 2521.4672 |  |  |  |  | 2021-05-06
MO_PS_PSZ-AC_2:7 Supply Flow Rate [cfm] | PSZ-AC_2:7 Supply Flow Rate [cfm] | 3157.1312 | 3157.1312 | 3157.1312 | 3157.1312 | 3157.1312 | 3157.1312 |  |  |  |  | 2021-05-06
MO_PS_Supply Air Temp. Reset Flag | Supply Air Temp. Reset Flag | No | No | Yes | Yes | Yes | Yes |  |  |  |  | 2021-05-06
MO_PS_VAV_POD_1 OA Rate [cfm] | VAV_POD_1 OA Rate [cfm] | 5683.5142 | 5483.1741 | 5994.9684 | 5745.8517 | 5909.5563 | 5705.148 |  |  |  |  | 2021-05-06
MO_PS_VAV_POD_2 OA Rate [cfm] | VAV_POD_2 OA Rate [cfm] | 5682.4124 | 5474.2748 | 5936.9111 | 5664.7197 | 5861.818 | 5626.1349 |  |  |  |  | 2021-05-06
MO_PS_VAV_POD_3 OA Rate [cfm] | VAV_POD_3 OA Rate [cfm] | 5168.9866 | 4910.1654 | 5487.9628 | 5192.6757 | 5422.1504 | 5152.7983 |  |  |  |  | 2021-05-06
MO_PS_VAV_OTHER OA Rate [cfm] | VAV_OTHER OA Rate [cfm] | 3736.1787 | 2988.8921 | 3736.1787 | 2988.8921 | 3736.1787 | 2988.8921 |  |  |  |  | 2021-05-06
MO_PS_PSZ-AC_2:5 OA Rate [cfm] | PSZ-AC_2:5 OA Rate [cfm] | 1152.7343 | 1152.7343 | 1152.7343 | 1152.7343 | 1152.7343 | 1152.7343 |  |  |  |  | 2021-05-06
MO_PS_PSZ-AC_1:6 OA Rate [cfm] | PSZ-AC_1:6 OA Rate [cfm] | 539.9118 | 539.9118 | 539.9118 | 539.9118 | 539.9118 | 539.9118 |  |  |  |  | 2021-05-06
MO_PS_PSZ-AC_2:7 OA Rate [cfm] | PSZ-AC_2:7 OA Rate [cfm] | 3153.0841 | 3153.0841 | 3153.0841 | 3153.0841 | 3153.0841 | 3153.0841 |  |  |  |  | 2021-05-06
MO_PS_VAV_POD_1 OA Damper [gravity, motorized] | VAV_POD_1 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | motorized | motorized |  |  |  |  | 2021-05-06
MO_PS_VAV_POD_2 OA Damper [gravity, motorized] | VAV_POD_2 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | motorized | motorized |  |  |  |  | 2021-05-06
MO_PS_VAV_POD_3 OA Damper [gravity, motorized] | VAV_POD_3 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | motorized | motorized |  |  |  |  | 2021-05-06
MO_PS_VAV_OTHER OA Damper [gravity, motorized] | VAV_OTHER OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | motorized | motorized |  |  |  |  | 2021-05-06
MO_PS_PSZ-AC_2:5 OA Damper [gravity, motorized] | PSZ-AC_2:5 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | motorized | motorized |  |  |  |  | 2021-05-06
MO_PS_PSZ-AC_1:6 OA Damper [gravity, motorized] | PSZ-AC_1:6 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | motorized | motorized |  |  |  |  | 2021-05-06
MO_PS_PSZ-AC_2:7 OA Damper [gravity, motorized] | PSZ-AC_2:7 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | motorized | motorized |  |  |  |  | 2021-05-06
MO_PS_VAV_POD_1 (economizer) | VAV_POD_1 (economizer) | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialDryBulb | DifferentialDryBulb |  |  |  |  | 2021-05-06
MO_PS_VAV_POD_2 (economizer) | VAV_POD_2 (economizer) | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialDryBulb | DifferentialDryBulb |  |  |  |  | 2021-05-06
MO_PS_VAV_POD_3 (economizer) | VAV_POD_3 (economizer) | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialDryBulb | DifferentialDryBulb |  |  |  |  | 2021-05-06
MO_PS_VAV_OTHER (economizer) | VAV_OTHER (economizer) | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialDryBulb | DifferentialDryBulb |  |  |  |  | 2021-05-06
MO_PS_PSZ-AC_2:5 (economizer) | PSZ-AC_2:5 (economizer) | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialDryBulb | DifferentialDryBulb |  |  |  |  | 2021-05-06
MO_PS_PSZ-AC_1:6 (economizer) | PSZ-AC_1:6 (economizer) | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialDryBulb | DifferentialDryBulb |  |  |  |  | 2021-05-06
MO_PS_PSZ-AC_2:7 (economizer) | PSZ-AC_2:7 (economizer) | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialDryBulb | DifferentialDryBulb |  |  |  |  | 2021-05-06
MO_PS_VAV_Pod_1_ERV Flag | VAV_Pod_1_ERV Flag | Yes | Yes | Yes | Yes | Yes | Yes |  |  |  |  | 2021-05-06
MO_PS_VAV_Pod_2_ERV Flag | VAV_Pod_2_ERV Flag | Yes | Yes | Yes | Yes | Yes | Yes |  |  |  |  | 2021-05-06
MO_PS_VAV_Pod_3_ERV Flag | VAV_Pod_3_ERV Flag | Yes | Yes | Yes | Yes | Yes | Yes |  |  |  |  | 2021-05-06
MO_PS_VAV_OTHER_ERV Flag | VAV_OTHER_ERV Flag | Yes | Yes | Yes | Yes | Yes | Yes |  |  |  |  | 2021-05-06
MO_PS_PSZ_AC_2_5_ERV Flag | PSZ_AC_2_5_ERV Flag | Yes | Yes | No | No | No | No |  |  |  |  | 2021-05-06
MO_PS_PSZ_AC_2_7_ERV Flag | PSZ_AC_2_7_ERV Flag | Yes | Yes | Yes | Yes | Yes | Yes |  |  |  |  | 2021-05-06
MO_PS_HEATSYS1 Capacity [MMBTU/h] | HEATSYS1 Capacity [MMBTU/h] | 0.9734 | 0.92735 | 1.1457 | 1.0918 | 1.2289 | 1.1784 |  |  |  |  | 2021-05-06
MO_PS_HEATSYS1 Flow Rate [gal/min] | HEATSYS1 Flow Rate [gal/min] | 99.9021 | 95.175 | 117.5856 | 112.0486 | 126.1207 | 120.9411 |  |  |  |  | 2021-05-06
MO_PS_VAV_POD_1 Fan Power [hp] | VAV_POD_1 Fan Power [hp] | 8.3873 | 8.0893 | 8.8482 | 8.4769 | 8.7184 | 8.4168 |  |  |  |  | 2021-05-06
MO_PS_VAV_POD_2 Fan Power [hp] | VAV_POD_2 Fan Power [hp] | 8.3833 | 8.0762 | 8.7615 | 8.3572 | 8.6502 | 8.3003 |  |  |  |  | 2021-05-06
MO_PS_VAV_POD_3 Fan Power [hp] | VAV_POD_3 Fan Power [hp] | 7.6258 | 7.244 | 8.0964 | 7.6607 | 7.9999 | 7.6019 |  |  |  |  | 2021-05-06
MO_PS_VAV_OTHER Fan Power [hp] | VAV_OTHER Fan Power [hp] | 11.5908 | 10.8943 | 12.3206 | 11.6177 | 12.2496 | 11.5458 |  |  |  |  | 2021-05-06
MO_PS_HEATSYS1 Pump Power [hp] | HEATSYS1 Pump Power [hp] | 2.1594 | 2.0369 | 2.5417 | 2.398 | 2.7262 | 2.5883 |  |  |  |  | 2021-05-06
MO_PS_PSZ-AC_1:6 Heating Capacity [kBtu/hr] | PSZ-AC_1:6 Heating Capacity [kBtu/hr] | 203.9838 | 195.2217 | 215.6275 | 207.0427 | 218.8149 | 210.2485 |  |  |  |  | 2021-05-06
MO_PS_PSZ-AC_2:5 Heating Capacity [kBtu/hr] | PSZ-AC_2:5 Heating Capacity [kBtu/hr] | 123.2467 | 121.3334 | 143.0933 | 142.8043 | 150.192 | 149.9372 |  |  |  |  | 2021-05-06
MO_PS_PSZ-AC_2:7 Heating Capacity [kBtu/hr] | PSZ-AC_2:7 Heating Capacity [kBtu/hr] | 293.9493 | 293.9493 | 334.0931 | 334.0931 | 354.2302 | 354.2302 |  |  |  |  | 2021-05-06
MO_PS_ZN_VAV_BOXes_Max_Reheat_Water_Flow_GPM | ZN_VAV_BOXes_Max_Reheat_Water_Flow_GPM | 69.2394 | 65.9478 | 74.6015 | 71.229 | 77.9864 | 75.0515 |  |  |  |  | 2021-05-06
id | item | Zone3A(MO-Memphis-TN) ASHRAE901-state_STD2016 | Zone3A(MO-Memphis-TN) ASHRAE901-state_STD2019 | Zone4A(MO-StLouis-MO) ASHRAE901-state_STD2016 | Zone4A(MO-StLouis-MO) ASHRAE901-state_STD2019 | Zone5A(MO-Kirksville-MO) ASHRAE901-state_STD2016 | Zone5A(MO-Kirksville-MO) ASHRAE901-state_STD2019 |  |  |  |  | 2021-05-06
MO_SH_SAC_FRONTOFFICE Cooling Capacity [ton] | SAC_FRONTOFFICE Cooling Capacity [ton] | 2.578 | 2.4464 | 2.5713 | 2.4438 | 2.4452 | 2.3357 |  |  |  |  | 2021-05-06
MO_SH_SAC_FRONTLOUNGE Cooling Capacity [ton] | SAC_FRONTLOUNGE Cooling Capacity [ton] | 6.2075 | 5.8961 | 6.3103 | 5.9991 | 6.2899 | 5.9737 |  |  |  |  | 2021-05-06
MO_SH_SAC_MEETINGROOM Cooling Capacity [ton] | SAC_MEETINGROOM Cooling Capacity [ton] | 2.972 | 2.8609 | 2.9907 | 2.897 | 2.99 | 2.8961 |  |  |  |  | 2021-05-06
MO_SH_SAC_EXC_EMPLGE_RESTRM Cooling Capacity [ton] | SAC_EXC_EMPLGE_RESTRM Cooling Capacity [ton] | 6.3079 | 6.2661 | 6.3538 | 6.3113 | 6.2124 | 6.1697 |  |  |  |  | 2021-05-06
MO_SH_SAC_FO_ADDAQ SUPPLY FAN Supply Flow Rate [cfm] | SAC_FO_ADDAQ SUPPLY FAN Supply Flow Rate [cfm] | 805.1744 | 762.7968 | 805.1744 | 762.7968 | 805.1744 | 762.7968 |  |  |  |  | 2021-05-06
MO_SH_SAC_FL_ADDAQ SUPPLY FAN Supply Flow Rate [cfm] | SAC_FL_ADDAQ SUPPLY FAN Supply Flow Rate [cfm] | 1864.6144 | 1779.8592 | 1885.8032 | 1801.048 | 1885.8032 | 1801.048 |  |  |  |  | 2021-05-06
MO_SH_SAC_MR_ADDAQ SUPPLY FAN Supply Flow Rate [cfm] | SAC_MR_ADDAQ SUPPLY FAN Supply Flow Rate [cfm] | 889.9296 | 868.7408 | 889.9296 | 868.7408 | 889.9296 | 868.7408 |  |  |  |  | 2021-05-06
MO_SH_SAC_EXC_ADDAQ SUPPLY FAN Supply Flow Rate [cfm] | SAC_EXC_ADDAQ SUPPLY FAN Supply Flow Rate [cfm] | 2182.4464 | 2161.2576 | 2224.824 | 2224.824 | 2246.0128 | 2224.824 |  |  |  |  | 2021-05-06
MO_SH_SAC_Exc_EmpLge_RestRm OA Rate [cfm] | SAC_Exc_EmpLge_RestRm OA Rate [cfm] | 199.9928 | 199.9928 | 199.9928 | 199.9928 | 199.9928 | 199.9928 |  |  |  |  | 2021-05-06
MO_SH_SAC_FrontLounge OA Rate [cfm] | SAC_FrontLounge OA Rate [cfm] | 500.0133 | 500.0133 | 500.0133 | 500.0133 | 500.0133 | 500.0133 |  |  |  |  | 2021-05-06
MO_SH_SAC_FrontOffice OA Rate [cfm] | SAC_FrontOffice OA Rate [cfm] | 119.2938 | 119.2938 | 119.2938 | 119.2938 | 119.2938 | 119.2938 |  |  |  |  | 2021-05-06
MO_SH_SAC_MeetingRoom OA Rate [cfm] | SAC_MeetingRoom OA Rate [cfm] | 267.7629 | 267.7629 | 267.7629 | 267.7629 | 267.7629 | 267.7629 |  |  |  |  | 2021-05-06
MO_SH_SAC_FrontLounge OA Damper [gravity, motorized] | SAC_FrontLounge OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | motorized | motorized |  |  |  |  | 2021-05-06
MO_SH_SAC_FrontOffice (economizer) | SAC_FrontOffice (economizer) | No | No | No | No | No | No |  |  |  |  | 2021-05-06
MO_SH_SAC_FrontLounge (economizer) | SAC_FrontLounge (economizer) | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialDryBulb | DifferentialDryBulb |  |  |  |  | 2021-05-06
MO_SH_SAC_MeetingRoom (economizer) | SAC_MeetingRoom (economizer) | No | No | No | No | No | No |  |  |  |  | 2021-05-06
MO_SH_SAC_Exc_EmpLge_RestRm (economizer) | SAC_Exc_EmpLge_RestRm (economizer) | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialDryBulb | DifferentialDryBulb |  |  |  |  | 2021-05-06
MO_SH_SAC_FRONTOFFICE Heating Capacity [kBtu/hr] | SAC_FRONTOFFICE Heating Capacity [kBtu/hr] | 36.3576 | 34.3623 | 37.7558 | 35.9329 | 37.8538 | 35.9042 |  |  |  |  | 2021-05-06
MO_SH_SAC_FRONTLOUNGE Heating Capacity [kBtu/hr] | SAC_FRONTLOUNGE Heating Capacity [kBtu/hr] | 96.2978 | 92.8911 | 103.2367 | 99.8691 | 105.4921 | 102.1199 |  |  |  |  | 2021-05-06
MO_SH_SAC_MEETINGROOM Heating Capacity [kBtu/hr] | SAC_MEETINGROOM Heating Capacity [kBtu/hr] | 47.715 | 46.4995 | 51.0788 | 50.0653 | 52.4564 | 51.4552 |  |  |  |  | 2021-05-06
MO_SH_SAC_EXC_EMPLGE_RESTRM Heating Capacity [kBtu/hr] | SAC_EXC_EMPLGE_RESTRM Heating Capacity [kBtu/hr] | 90.8977 | 90.2494 | 94.549 | 93.8896 | 95.4147 | 94.7484 |  |  |  |  | 2021-05-06
id | item | Zone3A(MO-Memphis-TN) ASHRAE901-state_STD2016 | Zone3A(MO-Memphis-TN) ASHRAE901-state_STD2019 | Zone4A(MO-StLouis-MO) ASHRAE901-state_STD2016 | Zone4A(MO-StLouis-MO) ASHRAE901-state_STD2019 | Zone5A(MO-Kirksville-MO) ASHRAE901-state_STD2016 | Zone5A(MO-Kirksville-MO) ASHRAE901-state_STD2019 |  |  |  |  | 2021-05-06
MO_MA_SPLIT GSW COOLING COIL Cooling Capacity [ton] | SPLIT GSW COOLING COIL Cooling Capacity [ton] | 0.95082 | 0.93989 | 0.99777 | 0.98378 | 0.93891 | 0.92449 |  |  |  |  | 2021-05-06
MO_MA_SPLIT GNW COOLING COIL Cooling Capacity [ton] | SPLIT GNW COOLING COIL Cooling Capacity [ton] | 0.9321 | 0.92112 | 0.96349 | 0.94984 | 0.90148 | 0.88751 |  |  |  |  | 2021-05-06
MO_MA_SPLIT OFFICE COOLING COIL Cooling Capacity [ton] | SPLIT OFFICE COOLING COIL Cooling Capacity [ton] | 1.8214 | 1.7148 | 1.8626 | 1.7479 | 1.7604 | 1.6318 |  |  |  |  | 2021-05-06
MO_MA_SPLIT GNE COOLING COIL Cooling Capacity [ton] | SPLIT GNE COOLING COIL Cooling Capacity [ton] | 0.83422 | 0.8222 | 0.84857 | 0.83673 | 0.78321 | 0.77094 |  |  |  |  | 2021-05-06
MO_MA_SPLIT GN1 COOLING COIL Cooling Capacity [ton] | SPLIT GN1 COOLING COIL Cooling Capacity [ton] | 0.72393 | 0.71484 | 0.71509 | 0.70543 | 0.65718 | 0.64742 |  |  |  |  | 2021-05-06
MO_MA_SPLIT GN2 COOLING COIL Cooling Capacity [ton] | SPLIT GN2 COOLING COIL Cooling Capacity [ton] | 0.7223 | 0.71321 | 0.71286 | 0.70326 | 0.65475 | 0.64504 |  |  |  |  | 2021-05-06
MO_MA_SPLIT GS1 COOLING COIL Cooling Capacity [ton] | SPLIT GS1 COOLING COIL Cooling Capacity [ton] | 0.7368 | 0.72808 | 0.75185 | 0.74177 | 0.70139 | 0.69091 |  |  |  |  | 2021-05-06
MO_MA_SPLIT GS2 COOLING COIL Cooling Capacity [ton] | SPLIT GS2 COOLING COIL Cooling Capacity [ton] | 0.77323 | 0.76057 | 0.78258 | 0.76916 | 0.73275 | 0.71842 |  |  |  |  | 2021-05-06
MO_MA_SPLIT MSW COOLING COIL Cooling Capacity [ton] | SPLIT MSW COOLING COIL Cooling Capacity [ton] | 2.1222 | 2.0998 | 2.3051 | 2.2732 | 2.2367 | 2.2043 |  |  |  |  | 2021-05-06
MO_MA_SPLIT MNW COOLING COIL Cooling Capacity [ton] | SPLIT MNW COOLING COIL Cooling Capacity [ton] | 2.0907 | 2.0686 | 2.2431 | 2.2123 | 2.1779 | 2.1464 |  |  |  |  | 2021-05-06
MO_MA_SPLIT MSE COOLING COIL Cooling Capacity [ton] | SPLIT MSE COOLING COIL Cooling Capacity [ton] | 1.9163 | 1.8941 | 2.0126 | 1.9856 | 1.9321 | 1.9043 |  |  |  |  | 2021-05-06
MO_MA_SPLIT MNE COOLING COIL Cooling Capacity [ton] | SPLIT MNE COOLING COIL Cooling Capacity [ton] | 1.8175 | 1.7711 | 1.87 | 1.8396 | 1.7952 | 1.7592 |  |  |  |  | 2021-05-06
MO_MA_SPLIT MN1 COOLING COIL Cooling Capacity [ton] | SPLIT MN1 COOLING COIL Cooling Capacity [ton] | 1.5261 | 1.5092 | 1.5324 | 1.5135 | 1.4502 | 1.4314 |  |  |  |  | 2021-05-06
MO_MA_SPLIT MN2 COOLING COIL Cooling Capacity [ton] | SPLIT MN2 COOLING COIL Cooling Capacity [ton] | 1.5218 | 1.5049 | 1.5263 | 1.5077 | 1.4435 | 1.4249 |  |  |  |  | 2021-05-06
MO_MA_SPLIT MS1 COOLING COIL Cooling Capacity [ton] | SPLIT MS1 COOLING COIL Cooling Capacity [ton] | 1.5528 | 1.5346 | 1.6004 | 1.5811 | 1.5299 | 1.5101 |  |  |  |  | 2021-05-06
MO_MA_SPLIT MS2 COOLING COIL Cooling Capacity [ton] | SPLIT MS2 COOLING COIL Cooling Capacity [ton] | 1.5486 | 1.5304 | 1.5944 | 1.5753 | 1.5237 | 1.5041 |  |  |  |  | 2021-05-06
MO_MA_SPLIT TSW COOLING COIL Cooling Capacity [ton] | SPLIT TSW COOLING COIL Cooling Capacity [ton] | 1.3049 | 1.2935 | 1.4321 | 1.4148 | 1.3915 | 1.3741 |  |  |  |  | 2021-05-06
MO_MA_SPLIT TNW COOLING COIL Cooling Capacity [ton] | SPLIT TNW COOLING COIL Cooling Capacity [ton] | 1.2726 | 1.2617 | 1.3942 | 1.3772 | 1.3525 | 1.3354 |  |  |  |  | 2021-05-06
MO_MA_SPLIT TSE COOLING COIL Cooling Capacity [ton] | SPLIT TSE COOLING COIL Cooling Capacity [ton] | 1.2022 | 1.1912 | 1.2895 | 1.2756 | 1.2409 | 1.2266 |  |  |  |  | 2021-05-06
MO_MA_SPLIT TNE COOLING COIL Cooling Capacity [ton] | SPLIT TNE COOLING COIL Cooling Capacity [ton] | 1.1497 | 1.1392 | 1.2227 | 1.2097 | 1.1688 | 1.1559 |  |  |  |  | 2021-05-06
MO_MA_SPLIT TN1 COOLING COIL Cooling Capacity [ton] | SPLIT TN1 COOLING COIL Cooling Capacity [ton] | 0.93344 | 0.92462 | 0.9682 | 0.95886 | 0.92529 | 0.91569 |  |  |  |  | 2021-05-06
MO_MA_SPLIT TN2 COOLING COIL Cooling Capacity [ton] | SPLIT TN2 COOLING COIL Cooling Capacity [ton] | 0.92842 | 0.91961 | 0.99918 | 0.98915 | 0.94854 | 0.90854 |  |  |  |  | 2021-05-06
MO_MA_SPLIT TS1 COOLING COIL Cooling Capacity [ton] | SPLIT TS1 COOLING COIL Cooling Capacity [ton] | 1.0024 | 0.99281 | 1.0638 | 1.0545 | 1.0179 | 1.0069 |  |  |  |  | 2021-05-06
MO_MA_SPLIT TS2 COOLING COIL Cooling Capacity [ton] | SPLIT TS2 COOLING COIL Cooling Capacity [ton] | 1.0041 | 0.99454 | 1.0669 | 1.0561 | 1.0231 | 1.012 |  |  |  |  | 2021-05-06
MO_MA_Split GN1 Furnace with DX Cooling OA Rate [cfm] | Split GN1 Furnace with DX Cooling OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 |  |  |  |  | 2021-05-06
MO_MA_Split GN2 Furnace with DX Cooling OA Rate [cfm] | Split GN2 Furnace with DX Cooling OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 |  |  |  |  | 2021-05-06
MO_MA_Split GNE Furnace with DX Cooling OA Rate [cfm] | Split GNE Furnace with DX Cooling OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 |  |  |  |  | 2021-05-06
MO_MA_Split GNW Furnace with DX Cooling OA Rate [cfm] | Split GNW Furnace with DX Cooling OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 |  |  |  |  | 2021-05-06
MO_MA_Split GS1 Furnace with DX Cooling OA Rate [cfm] | Split GS1 Furnace with DX Cooling OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 |  |  |  |  | 2021-05-06
MO_MA_Split GS2 Furnace with DX Cooling OA Rate [cfm] | Split GS2 Furnace with DX Cooling OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 |  |  |  |  | 2021-05-06
MO_MA_Split GSW Furnace with DX Cooling OA Rate [cfm] | Split GSW Furnace with DX Cooling OA Rate [cfm] | 56.9945 | 56.9945 | 56.9945 | 56.9945 | 56.9945 | 56.9945 |  |  |  |  | 2021-05-06
MO_MA_Split MN1 Furnace with DX Cooling OA Rate [cfm] | Split MN1 Furnace with DX Cooling OA Rate [cfm] | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824 |  |  |  |  | 2021-05-06
MO_MA_Split MN2 Furnace with DX Cooling OA Rate [cfm] | Split MN2 Furnace with DX Cooling OA Rate [cfm] | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824 |  |  |  |  | 2021-05-06
MO_MA_Split MNE Furnace with DX Cooling OA Rate [cfm] | Split MNE Furnace with DX Cooling OA Rate [cfm] | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824 |  |  |  |  | 2021-05-06
MO_MA_Split MNW Furnace with DX Cooling OA Rate [cfm] | Split MNW Furnace with DX Cooling OA Rate [cfm] | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824 |  |  |  |  | 2021-05-06
MO_MA_Split MS1 Furnace with DX Cooling OA Rate [cfm] | Split MS1 Furnace with DX Cooling OA Rate [cfm] | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824 |  |  |  |  | 2021-05-06
MO_MA_Split MS2 Furnace with DX Cooling OA Rate [cfm] | Split MS2 Furnace with DX Cooling OA Rate [cfm] | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824 |  |  |  |  | 2021-05-06
MO_MA_Split MSE Furnace with DX Cooling OA Rate [cfm] | Split MSE Furnace with DX Cooling OA Rate [cfm] | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824 |  |  |  |  | 2021-05-06
MO_MA_Split MSW Furnace with DX Cooling OA Rate [cfm] | Split MSW Furnace with DX Cooling OA Rate [cfm] | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824 |  |  |  |  | 2021-05-06
MO_MA_Split Office Furnace with DX Cooling OA Rate [cfm] | Split Office Furnace with DX Cooling OA Rate [cfm] | 80.7372 | 80.7372 | 80.7372 | 80.7372 | 80.7372 | 80.7372 |  |  |  |  | 2021-05-06
MO_MA_Split TN1 Furnace with DX Cooling OA Rate [cfm] | Split TN1 Furnace with DX Cooling OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 |  |  |  |  | 2021-05-06
MO_MA_Split TN2 Furnace with DX Cooling OA Rate [cfm] | Split TN2 Furnace with DX Cooling OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 |  |  |  |  | 2021-05-06
MO_MA_Split TNE Furnace with DX Cooling OA Rate [cfm] | Split TNE Furnace with DX Cooling OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 |  |  |  |  | 2021-05-06
MO_MA_Split TNW Furnace with DX Cooling OA Rate [cfm] | Split TNW Furnace with DX Cooling OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 |  |  |  |  | 2021-05-06
MO_MA_Split TS1 Furnace with DX Cooling OA Rate [cfm] | Split TS1 Furnace with DX Cooling OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 |  |  |  |  | 2021-05-06
MO_MA_Split TS2 Furnace with DX Cooling OA Rate [cfm] | Split TS2 Furnace with DX Cooling OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 |  |  |  |  | 2021-05-06
MO_MA_Split TSE Furnace with DX Cooling OA Rate [cfm] | Split TSE Furnace with DX Cooling OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 |  |  |  |  | 2021-05-06
MO_MA_Split TSW Furnace with DX Cooling OA Rate [cfm] | Split TSW Furnace with DX Cooling OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 |  |  |  |  | 2021-05-06
MO_MA_SPLIT GSW HEATING COIL Heating Capacity [kBtu/hr] | SPLIT GSW HEATING COIL Heating Capacity [kBtu/hr] | 7.9381 | 7.84 | 10.2452 | 10.3039 | 11.2119 | 11.2709 |  |  |  |  | 2021-05-06
MO_MA_SPLIT GNW HEATING COIL Heating Capacity [kBtu/hr] | SPLIT GNW HEATING COIL Heating Capacity [kBtu/hr] | 7.8919 | 7.7891 | 10.176 | 10.2348 | 11.1377 | 11.1968 |  |  |  |  | 2021-05-06
MO_MA_SPLIT OFFICE HEATING COIL Heating Capacity [kBtu/hr] | SPLIT OFFICE HEATING COIL Heating Capacity [kBtu/hr] | 19.7517 | 19.5824 | 23.0975 | 23.1773 | 24.5273 | 24.6069 |  |  |  |  | 2021-05-06
MO_MA_SPLIT GNE HEATING COIL Heating Capacity [kBtu/hr] | SPLIT GNE HEATING COIL Heating Capacity [kBtu/hr] | 7.8919 | 7.7891 | 10.1518 | 10.2106 | 11.1377 | 11.1968 |  |  |  |  | 2021-05-06
MO_MA_SPLIT GN1 HEATING COIL Heating Capacity [kBtu/hr] | SPLIT GN1 HEATING COIL Heating Capacity [kBtu/hr] | 5.634 | 5.5857 | 7.4479 | 7.5067 | 8.2391 | 8.2983 |  |  |  |  | 2021-05-06
MO_MA_SPLIT GN2 HEATING COIL Heating Capacity [kBtu/hr] | SPLIT GN2 HEATING COIL Heating Capacity [kBtu/hr] | 5.634 | 5.5857 | 7.4472 | 7.506 | 8.2391 | 8.2983 |  |  |  |  | 2021-05-06
MO_MA_SPLIT GS1 HEATING COIL Heating Capacity [kBtu/hr] | SPLIT GS1 HEATING COIL Heating Capacity [kBtu/hr] | 5.5816 | 5.5378 | 7.3931 | 7.4517 | 8.1757 | 8.2347 |  |  |  |  | 2021-05-06
MO_MA_SPLIT GS2 HEATING COIL Heating Capacity [kBtu/hr] | SPLIT GS2 HEATING COIL Heating Capacity [kBtu/hr] | 6.0855 | 6.0366 | 7.8991 | 7.9586 | 8.688 | 8.7478 |  |  |  |  | 2021-05-06
MO_MA_SPLIT MSW HEATING COIL Heating Capacity [kBtu/hr] | SPLIT MSW HEATING COIL Heating Capacity [kBtu/hr] | 14.7563 | 14.5626 | 18.7647 | 18.8935 | 20.459 | 20.5882 |  |  |  |  | 2021-05-06
MO_MA_SPLIT MNW HEATING COIL Heating Capacity [kBtu/hr] | SPLIT MNW HEATING COIL Heating Capacity [kBtu/hr] | 14.8555 | 14.6504 | 18.8621 | 18.9909 | 20.5738 | 20.703 |  |  |  |  | 2021-05-06
MO_MA_SPLIT MSE HEATING COIL Heating Capacity [kBtu/hr] | SPLIT MSE HEATING COIL Heating Capacity [kBtu/hr] | 14.7563 | 14.5626 | 18.7075 | 18.8364 | 20.459 | 20.5882 |  |  |  |  | 2021-05-06
MO_MA_SPLIT MNE HEATING COIL Heating Capacity [kBtu/hr] | SPLIT MNE HEATING COIL Heating Capacity [kBtu/hr] | 14.8555 | 14.6504 | 18.805 | 18.9337 | 20.5738 | 20.703 |  |  |  |  | 2021-05-06
MO_MA_SPLIT MN1 HEATING COIL Heating Capacity [kBtu/hr] | SPLIT MN1 HEATING COIL Heating Capacity [kBtu/hr] | 10.2532 | 10.2532 | 12.985 | 13.1103 | 14.33 | 14.4559 |  |  |  |  | 2021-05-06
MO_MA_SPLIT MN2 HEATING COIL Heating Capacity [kBtu/hr] | SPLIT MN2 HEATING COIL Heating Capacity [kBtu/hr] | 10.2532 | 10.2532 | 12.9835 | 13.1087 | 14.33 | 14.4559 |  |  |  |  | 2021-05-06
MO_MA_SPLIT MS1 HEATING COIL Heating Capacity [kBtu/hr] | SPLIT MS1 HEATING COIL Heating Capacity [kBtu/hr] | 10.2532 | 10.2532 | 12.8964 | 13.0216 | 14.2249 | 14.3508 |  |  |  |  | 2021-05-06
MO_MA_SPLIT MS2 HEATING COIL Heating Capacity [kBtu/hr] | SPLIT MS2 HEATING COIL Heating Capacity [kBtu/hr] | 10.2532 | 10.2532 | 12.8948 | 13.0201 | 14.2249 | 14.3508 |  |  |  |  | 2021-05-06
MO_MA_SPLIT TSW HEATING COIL Heating Capacity [kBtu/hr] | SPLIT TSW HEATING COIL Heating Capacity [kBtu/hr] | 10.8525 | 10.7577 | 13.0824 | 13.144 | 14.2979 | 14.3598 |  |  |  |  | 2021-05-06
MO_MA_SPLIT TNW HEATING COIL Heating Capacity [kBtu/hr] | SPLIT TNW HEATING COIL Heating Capacity [kBtu/hr] | 10.9103 | 10.8097 | 13.1395 | 13.2013 | 14.3649 | 14.4269 |  |  |  |  | 2021-05-06
MO_MA_SPLIT TSE HEATING COIL Heating Capacity [kBtu/hr] | SPLIT TSE HEATING COIL Heating Capacity [kBtu/hr] | 10.8525 | 10.7577 | 13.0523 | 13.114 | 14.2979 | 14.3598 |  |  |  |  | 2021-05-06
MO_MA_SPLIT TNE HEATING COIL Heating Capacity [kBtu/hr] | SPLIT TNE HEATING COIL Heating Capacity [kBtu/hr] | 10.9103 | 10.8097 | 13.1095 | 13.1712 | 14.3649 | 14.4269 |  |  |  |  | 2021-05-06
MO_MA_SPLIT TN1 HEATING COIL Heating Capacity [kBtu/hr] | SPLIT TN1 HEATING COIL Heating Capacity [kBtu/hr] | 8.2916 | 8.2481 | 9.9378 | 9.9994 | 10.9506 | 11.0124 |  |  |  |  | 2021-05-06
MO_MA_SPLIT TN2 HEATING COIL Heating Capacity [kBtu/hr] | SPLIT TN2 HEATING COIL Heating Capacity [kBtu/hr] | 8.2916 | 8.2481 | 9.9369 | 9.9985 | 10.9506 | 11.0124 |  |  |  |  | 2021-05-06
MO_MA_SPLIT TS1 HEATING COIL Heating Capacity [kBtu/hr] | SPLIT TS1 HEATING COIL Heating Capacity [kBtu/hr] | 8.2268 | 8.189 | 9.8736 | 9.9352 | 10.877 | 10.9387 |  |  |  |  | 2021-05-06
MO_MA_SPLIT TS2 HEATING COIL Heating Capacity [kBtu/hr] | SPLIT TS2 HEATING COIL Heating Capacity [kBtu/hr] | 8.2268 | 8.189 | 9.8728 | 9.9343 | 10.877 | 10.9387 |  |  |  |  | 2021-05-06
MO_MA_Split_GSW ERV Flag | Split_GSW ERV Flag | No | Yes | Yes | Yes | Yes | Yes |  |  |  |  | 2021-05-06
MO_MA_Split_GNW ERV Flag | Split_GNW ERV Flag | No | Yes | Yes | Yes | Yes | Yes |  |  |  |  | 2021-05-06
MO_MA_Split_GNE ERV Flag | Split_GNE ERV Flag | No | Yes | Yes | Yes | Yes | Yes |  |  |  |  | 2021-05-06
MO_MA_Split_GN1 ERV Flag | Split_GN1 ERV Flag | No | Yes | Yes | Yes | Yes | Yes |  |  |  |  | 2021-05-06
MO_MA_Split_GN2 ERV Flag | Split_GN2 ERV Flag | No | Yes | Yes | Yes | Yes | Yes |  |  |  |  | 2021-05-06
MO_MA_Split_GS1 ERV Flag | Split_GS1 ERV Flag | No | Yes | Yes | Yes | Yes | Yes |  |  |  |  | 2021-05-06
MO_MA_Split_GS2 ERV Flag | Split_GS2 ERV Flag | No | Yes | Yes | Yes | Yes | Yes |  |  |  |  | 2021-05-06
MO_MA_Split_MSW ERV Flag | Split_MSW ERV Flag | No | Yes | Yes | Yes | Yes | Yes |  |  |  |  | 2021-05-06
MO_MA_Split_MNW ERV Flag | Split_MNW ERV Flag | No | Yes | Yes | Yes | Yes | Yes |  |  |  |  | 2021-05-06
MO_MA_Split_MSE ERV Flag | Split_MSE ERV Flag | No | Yes | Yes | Yes | Yes | Yes |  |  |  |  | 2021-05-06
MO_MA_Split_MNE ERV Flag | Split_MNE ERV Flag | No | Yes | Yes | Yes | Yes | Yes |  |  |  |  | 2021-05-06
MO_MA_Split_MN1 ERV Flag | Split_MN1 ERV Flag | No | Yes | Yes | Yes | Yes | Yes |  |  |  |  | 2021-05-06
MO_MA_Split_MN2 ERV Flag | Split_MN2 ERV Flag | No | Yes | Yes | Yes | Yes | Yes |  |  |  |  | 2021-05-06
MO_MA_Split_MS1 ERV Flag | Split_MS1 ERV Flag | No | Yes | Yes | Yes | Yes | Yes |  |  |  |  | 2021-05-06
MO_MA_Split_MS2 ERV Flag | Split_MS2 ERV Flag | No | Yes | Yes | Yes | Yes | Yes |  |  |  |  | 2021-05-06
MO_MA_Split_TSW ERV Flag | Split_TSW ERV Flag | No | Yes | Yes | Yes | Yes | Yes |  |  |  |  | 2021-05-06
MO_MA_Split_TNW ERV Flag | Split_TNW ERV Flag | No | Yes | Yes | Yes | Yes | Yes |  |  |  |  | 2021-05-06
MO_MA_Split_TSE ERV Flag | Split_TSE ERV Flag | No | Yes | Yes | Yes | Yes | Yes |  |  |  |  | 2021-05-06
MO_MA_Split_TNE ERV Flag | Split_TNE ERV Flag | No | Yes | Yes | Yes | Yes | Yes |  |  |  |  | 2021-05-06
MO_MA_Split_TN1 ERV Flag | Split_TN1 ERV Flag | No | Yes | Yes | Yes | Yes | Yes |  |  |  |  | 2021-05-06
MO_MA_Split_TN2 ERV Flag | Split_TN2 ERV Flag | No | Yes | Yes | Yes | Yes | Yes |  |  |  |  | 2021-05-06
MO_MA_Split_TS1 ERV Flag | Split_TS1 ERV Flag | No | Yes | Yes | Yes | Yes | Yes |  |  |  |  | 2021-05-06
MO_MA_Split_TS2 ERV Flag | Split_TS2 ERV Flag | No | Yes | Yes | Yes | Yes | Yes |  |  |  |  | 2021-05-06
id | item | Zone2A(MS-Mobile-AL) ASHRAE901-state_STD2016 | Zone2A(MS-Mobile-AL) ASHRAE901-state_STD2019 | Zone3A(MS-Jackson-MS) ASHRAE901-state_STD2016 | Zone3A(MS-Jackson-MS) ASHRAE901-state_STD2019 | [6 empty] | 2021-05-06
MS_SO_PSZ-AC:1 Cooling Capacity [ton] | PSZ-AC:1 Cooling Capacity [ton] | 2.039 | 1.9412 | 2.0574 | 1.9596 | [6 empty] | 2021-05-06
MS_SO_PSZ-AC:2 Cooling Capacity [ton] | PSZ-AC:2 Cooling Capacity [ton] | 1.8074 | 1.7152 | 1.8173 | 1.7316 | [6 empty] | 2021-05-06
MS_SO_PSZ-AC:3 Cooling Capacity [ton] | PSZ-AC:3 Cooling Capacity [ton] | 1.1801 | 1.1355 | 1.1747 | 1.1345 | [6 empty] | 2021-05-06
MS_SO_PSZ-AC:4 Cooling Capacity [ton] | PSZ-AC:4 Cooling Capacity [ton] | 1.7974 | 1.7082 | 1.8056 | 1.7265 | [6 empty] | 2021-05-06
MS_SO_PSZ-AC:5 Cooling Capacity [ton] | PSZ-AC:5 Cooling Capacity [ton] | 1.4067 | 1.3556 | 1.4047 | 1.361 | [6 empty] | 2021-05-06
MS_SO_PSZ-AC:1 Supply Flow Rate [cfm] | PSZ-AC:1 Supply Flow Rate [cfm] | 678.0416 | 635.664 | 678.0416 | 635.664 | [6 empty] | 2021-05-06
MS_SO_PSZ-AC:2 Supply Flow Rate [cfm] | PSZ-AC:2 Supply Flow Rate [cfm] | 635.664 | 593.2864 | 635.664 | 593.2864 | [6 empty] | 2021-05-06
MS_SO_PSZ-AC:3 Supply Flow Rate [cfm] | PSZ-AC:3 Supply Flow Rate [cfm] | 444.9648 | 423.776 | 444.9648 | 423.776 | [6 empty] | 2021-05-06
MS_SO_PSZ-AC:4 Supply Flow Rate [cfm] | PSZ-AC:4 Supply Flow Rate [cfm] | 614.4752 | 572.0976 | 614.4752 | 593.2864 | [6 empty] | 2021-05-06
MS_SO_PSZ-AC:5 Supply Flow Rate [cfm] | PSZ-AC:5 Supply Flow Rate [cfm] | 550.9088 | 508.5312 | 550.9088 | 529.72 | [6 empty] | 2021-05-06
MS_SO_PSZ-AC:1 OA Rate [cfm] | PSZ-AC:1 OA Rate [cfm] | 136.9178 | 136.9178 | 136.9178 | 136.9178 | [6 empty] | 2021-05-06
MS_SO_PSZ-AC:2 OA Rate [cfm] | PSZ-AC:2 OA Rate [cfm] | 103.7925 | 103.7925 | 103.7925 | 103.7925 | [6 empty] | 2021-05-06
MS_SO_PSZ-AC:3 OA Rate [cfm] | PSZ-AC:3 OA Rate [cfm] | 61.5711 | 61.5711 | 61.5711 | 61.5711 | [6 empty] | 2021-05-06
MS_SO_PSZ-AC:4 OA Rate [cfm] | PSZ-AC:4 OA Rate [cfm] | 103.7925 | 103.7925 | 103.7925 | 103.7925 | [6 empty] | 2021-05-06
MS_SO_PSZ-AC:5 OA Rate [cfm] | PSZ-AC:5 OA Rate [cfm] | 61.5711 | 61.5711 | 61.5711 | 61.5711 | [6 empty] | 2021-05-06
MS_SO_PSZ-AC:1 heating Capacity [kBtu/hr] | PSZ-AC:1 heating Capacity [kBtu/hr] | 11.3309 | 11.3309 | 12.0321 | 12.0321 | [6 empty] | 2021-05-06
MS_SO_PSZ-AC:2 heating Capacity [kBtu/hr] | PSZ-AC:2 heating Capacity [kBtu/hr] | 15.1982 | 14.6931 | 16.1033 | 15.8822 | [6 empty] | 2021-05-06
MS_SO_PSZ-AC:3 heating Capacity [kBtu/hr] | PSZ-AC:3 heating Capacity [kBtu/hr] | 9.324 | 9.0298 | 9.8916 | 9.7642 | [6 empty] | 2021-05-06
MS_SO_PSZ-AC:4 heating Capacity [kBtu/hr] | PSZ-AC:4 heating Capacity [kBtu/hr] | 14.9586 | 14.523 | 15.9268 | 15.7382 | [6 empty] | 2021-05-06
MS_SO_PSZ-AC:5 heating Capacity [kBtu/hr] | PSZ-AC:5 heating Capacity [kBtu/hr] | 9.324 | 9.0298 | 9.8916 | 9.7642 | [6 empty] | 2021-05-06
id | item | Zone2A(MS-Mobile-AL) ASHRAE901-state_STD2016 | Zone2A(MS-Mobile-AL) ASHRAE901-state_STD2019 | Zone3A(MS-Jackson-MS) ASHRAE901-state_STD2016 | Zone3A(MS-Jackson-MS) ASHRAE901-state_STD2019 | [6 empty] | 2021-05-06
MS_LO_CAV_BAS Supply Flow Rate [cfm] | CAV_BAS Supply Flow Rate [cfm] | 11675.0288 | 10806.288 | 11632.6512 | 10763.9104 | [6 empty] | 2021-05-06
MS_LO_VAV_BOT WITH REHEAT Supply Flow Rate [cfm] | VAV_BOT WITH REHEAT Supply Flow Rate [cfm] | 19218.2416 | 18285.9344 | 19218.2416 | 18285.9344 | [6 empty] | 2021-05-06
MS_LO_VAV_MID WITH REHEAT Supply Flow Rate [cfm] | VAV_MID WITH REHEAT Supply Flow Rate [cfm] | 178388.5075 | 169531.5891 | 178536.8291 | 169510.4003 | [6 empty] | 2021-05-06
MS_LO_VAV_TOP WITH REHEAT Supply Flow Rate [cfm] | VAV_TOP WITH REHEAT Supply Flow Rate [cfm] | 18603.7664 | 17735.0256 | 18709.7104 | 17904.536 | [6 empty] | 2021-05-06
MS_LO_Supply Air Temp. Reset Flag | Supply Air Temp. Reset Flag | No | No | No | Yes | [6 empty] | 2021-05-06
MS_LO_CAV_BAS OA Rate [cfm] | CAV_BAS OA Rate [cfm] | 2542.8255 | 2542.8255 | 2542.8255 | 2542.8255 | [6 empty] | 2021-05-06
MS_LO_VAV_BOT WITH REHEAT OA Rate [cfm] | VAV_BOT WITH REHEAT OA Rate [cfm] | 5377.8022 | 4302.174 | 5377.8022 | 4302.174 | [6 empty] | 2021-05-06
MS_LO_VAV_MID WITH REHEAT OA Rate [cfm] | VAV_MID WITH REHEAT OA Rate [cfm] | 53777.9373 | 43021.7396 | 53777.9373 | 43021.7396 | [6 empty] | 2021-05-06
MS_LO_VAV_TOP WITH REHEAT OA Rate [cfm] | VAV_TOP WITH REHEAT OA Rate [cfm] | 5377.8022 | 4302.174 | 5377.8022 | 4302.174 | [6 empty] | 2021-05-06
MS_LO_AIRLOOP DATACENTER BASEMENT OA Rate [cfm] | AIRLOOP DATACENTER BASEMENT OA Rate [cfm] | 716.9654 | 716.9654 | 716.9654 | 716.9654 | [6 empty] | 2021-05-06
MS_LO_VAV_bot_WITH_REHEAT ERV Flag | VAV_bot_WITH_REHEAT ERV Flag | Yes | Yes | Yes | Yes | [6 empty] | 2021-05-06
MS_LO_VAV_mid_WITH_REHEAT ERV Flag | VAV_mid_WITH_REHEAT ERV Flag | Yes | Yes | Yes | Yes | [6 empty] | 2021-05-06
MS_LO_VAV_top_WITH_REHEAT ERV Flag | VAV_top_WITH_REHEAT ERV Flag | Yes | Yes | Yes | Yes | [6 empty] | 2021-05-06
MS_LO_COOLSYS1 CHILLER1 Capacity [ton] | COOLSYS1 CHILLER1 Capacity [ton] | 440.5384 | 395.609 | 440.855 | 394.6815 | [6 empty] | 2021-05-06
MS_LO_COOLSYS1 CHILLER2 Capacity [ton] | COOLSYS1 CHILLER2 Capacity [ton] | 440.5384 | 395.609 | 440.855 | 394.6815 | [6 empty] | 2021-05-06
MS_LO_TOWERWATERSYS COOLTOWER 1 Capacity [ton] | TOWERWATERSYS COOLTOWER 1 Capacity [ton] | 418.1479 | 375.4982 | 418.4498 | 374.6187 | [6 empty] | 2021-05-06
MS_LO_TOWERWATERSYS COOLTOWER 2 Capacity [ton] | TOWERWATERSYS COOLTOWER 2 Capacity [ton] | 418.1479 | 375.4982 | 418.4498 | 374.6187 | [6 empty] | 2021-05-06
MS_LO_HEATSYS1 BOILER Capacity [MMBTU/h] | HEATSYS1 BOILER Capacity [MMBTU/h] | 3511.8649 | 3106.194 | 3618.0862 | 3207.9661 | [6 empty] | 2021-05-06
MS_LO_COOLSYS1 PUMP Flow Rate [gal/min] | COOLSYS1 PUMP Flow Rate [gal/min] | 0 | 0 | 0 | 0 | [6 empty] | 2021-05-06
MS_LO_COOLSYS1 CHILLER1 PUMP Flow Rate [gal/min] | COOLSYS1 CHILLER1 PUMP Flow Rate [gal/min] | 691.6146 | 620.8001 | 694.9558 | 619.3324 | [6 empty] | 2021-05-06
MS_LO_COOLSYS1 CHILLER2 PUMP Flow Rate [gal/min] | COOLSYS1 CHILLER2 PUMP Flow Rate [gal/min] | 691.6146 | 620.8001 | 694.9558 | 619.3324 | [6 empty] | 2021-05-06
MS_LO_COOLSYS1 PUMP SECONDARY Flow Rate [gal/min] | COOLSYS1 PUMP SECONDARY Flow Rate [gal/min] | 1383.2292 | 1241.5986 | 1389.9117 | 1238.6631 | [6 empty] | 2021-05-06
MS_LO_HEATSYS1 PUMP Flow Rate [gal/min] | HEATSYS1 PUMP Flow Rate [gal/min] | 720.8568 | 637.5872 | 742.6606 | 658.4779 | [6 empty] | 2021-05-06
MS_LO_TOWERWATERSYS PUMP Flow Rate [gal/min] | TOWERWATERSYS PUMP Flow Rate [gal/min] | 2430.4886 | 2182.5895 | 2432.2321 | 2177.5174 | [6 empty] | 2021-05-06
MS_LO_PLANT CIRC PUMP Flow Rate [gal/min] | PLANT CIRC PUMP Flow Rate [gal/min] | 208.5078 | 207.625 | 208.6299 | 207.7328 | [6 empty] | 2021-05-06
MS_LO_COOLSYS1 PUMP SECONDARY Pressure setpoint reset [yes,no] | COOLSYS1 PUMP SECONDARY Pressure setpoint reset [yes,no] | pump_ride_on_curve | pump_ride_on_curve | pump_ride_on_curve | pump_ride_on_curve | [6 empty] | 2021-05-06
MS_LO_COOLSYS1 CHILLER1 PUMP Pump Power [hp] | COOLSYS1 CHILLER1 PUMP Pump Power [hp] | 3.731 | 3.3158 | 3.749 | 3.308 | [6 empty] | 2021-05-06
MS_LO_COOLSYS1 CHILLER2 PUMP Pump Power [hp] | COOLSYS1 CHILLER2 PUMP Pump Power [hp] | 3.731 | 3.3158 | 3.749 | 3.308 | [6 empty] | 2021-05-06
MS_LO_COOLSYS1 PUMP SECONDARY Pump Power [hp] | COOLSYS1 PUMP SECONDARY Pump Power [hp] | 22.3861 | 19.895 | 22.4943 | 19.848 | [6 empty] | 2021-05-06
MS_LO_HEATSYS1 PUMP Pump Power [hp] | HEATSYS1 PUMP Pump Power [hp] | 15.5817 | 13.6454 | 16.053 | 14.0924 | [6 empty] | 2021-05-06
MS_LO_TOWERWATERSYS PUMP Pump Power [hp] | TOWERWATERSYS PUMP Pump Power [hp] | 43.5155 | 38.6905 | 43.5467 | 38.5998 | [6 empty] | 2021-05-06
MS_LO_PLANT CIRC PUMP Pump Power [hp] | PLANT CIRC PUMP Pump Power [hp] | 4.4993 | 4.4359 | 4.5019 | 4.4382 | [6 empty] | 2021-05-06
MS_LO_Datacenter PLANT CIRC PUMP Pump Power [hp] | Datacenter PLANT CIRC PUMP Pump Power [hp] | 4.4993 | 4.4359 | 4.5019 | 4.4382 | [6 empty] | 2021-05-06
MS_LO_ZN_VAV_BOXes_Max_Reheat_Water_Flow_GPM | ZN_VAV_BOXes_Max_Reheat_Water_Flow_GPM | 427.872 | 400.8238 | 413.6952 | 392.8744 | [6 empty] | 2021-05-06
MS_LO_COOLSYS1 PUMP SECONDARY VSD | COOLSYS1 PUMP SECONDARY VSD | No | No | No | No | [6 empty] | 2021-05-06
MS_LO_HEATSYS1 PUMP VSD | HEATSYS1 PUMP VSD | No | No | No | No | [6 empty] | 2021-05-06
MS_LO_DATACENTER BASEMENT Cooling Capacity [ton] | DATACENTER BASEMENT Cooling Capacity [ton] | 122.3604 | 122.0038 | 122.445 | 122.0874 | [6 empty] | 2021-05-06
MS_LO_DATACENTER BOT Cooling Capacity [ton] | DATACENTER BOT Cooling Capacity [ton] | 2.6465 | 2.6201 | 2.6466 | 2.6192 | [6 empty] | 2021-05-06
MS_LO_DATACENTER MID Cooling Capacity [ton] | DATACENTER MID Cooling Capacity [ton] | 25.1851 | 24.9419 | 25.1877 | 24.9357 | [6 empty] | 2021-05-06
MS_LO_DATACENTER TOP Cooling Capacity [ton] | DATACENTER TOP Cooling Capacity [ton] | 2.5445 | 2.5238 | 2.5462 | 2.5265 | [6 empty] | 2021-05-06
id | item | Zone2A(MS-Mobile-AL) ASHRAE901-state_STD2016 | Zone2A(MS-Mobile-AL) ASHRAE901-state_STD2019 | Zone3A(MS-Jackson-MS) ASHRAE901-state_STD2016 | Zone3A(MS-Jackson-MS) ASHRAE901-state_STD2019 | [6 empty] | 2021-05-06
MS_RS_PSZ-AC:1 Cooling Capacity [ton] | PSZ-AC:1 Cooling Capacity [ton] | 11.0913 | 10.7503 | 10.9677 | 10.6358 | [6 empty] | 2021-05-06
MS_RS_PSZ-AC:2 Cooling Capacity [ton] | PSZ-AC:2 Cooling Capacity [ton] | 51.2051 | 48.3375 | 50.984 | 48.0929 | [6 empty] | 2021-05-06
MS_RS_PSZ-AC:3 Cooling Capacity [ton] | PSZ-AC:3 Cooling Capacity [ton] | 6.8125 | 6.6753 | 6.8606 | 6.7014 | [6 empty] | 2021-05-06
MS_RS_PSZ-AC:4 Cooling Capacity [ton] | PSZ-AC:4 Cooling Capacity [ton] | 5.5983 | 5.4627 | 5.6234 | 5.4695 | [6 empty] | 2021-05-06
MS_RS_PSZ-AC:1 Supply Flow Rate [cfm] | PSZ-AC:1 Supply Flow Rate [cfm] | 4131.816 | 3898.7392 | 4089.4384 | 3856.3616 | [6 empty] | 2021-05-06
MS_RS_PSZ-AC:2 Supply Flow Rate [cfm] | PSZ-AC:2 Supply Flow Rate [cfm] | 15361.88 | 14514.328 | 15298.3136 | 14429.5728 | [6 empty] | 2021-05-06
MS_RS_PSZ-AC:3 Supply Flow Rate [cfm] | PSZ-AC:3 Supply Flow Rate [cfm] | 2288.3904 | 2224.824 | 2288.3904 | 2224.824 | [6 empty] | 2021-05-06
MS_RS_PSZ-AC:4 Supply Flow Rate [cfm] | PSZ-AC:4 Supply Flow Rate [cfm] | 1758.6704 | 1695.104 | 1758.6704 | 1695.104 | [6 empty] | 2021-05-06
MS_RS_PSZ-AC:1 OA Rate [cfm] | PSZ-AC:1 OA Rate [cfm] | 490.669 | 490.669 | 490.669 | 490.669 | [6 empty] | 2021-05-06
MS_RS_PSZ-AC:2 OA Rate [cfm] | PSZ-AC:2 OA Rate [cfm] | 4005.1282 | 4005.1282 | 4005.1282 | 4005.1282 | [6 empty] | 2021-05-06
MS_RS_PSZ-AC:3 OA Rate [cfm] | PSZ-AC:3 OA Rate [cfm] | 377.3937 | 377.3937 | 377.3937 | 377.3937 | [6 empty] | 2021-05-06
MS_RS_PSZ-AC:4 OA Rate [cfm] | PSZ-AC:4 OA Rate [cfm] | 377.3937 | 377.3937 | 377.3937 | 377.3937 | [6 empty] | 2021-05-06
MS_RS_PSZ-AC:1 OA Damper [gravity, motorized] | PSZ-AC:1 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2021-05-06
MS_RS_PSZ-AC:2 OA Damper [gravity, motorized] | PSZ-AC:2 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2021-05-06
MS_RS_PSZ-AC:3 OA Damper [gravity, motorized] | PSZ-AC:3 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2021-05-06
MS_RS_PSZ-AC:4 OA Damper [gravity, motorized] | PSZ-AC:4 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2021-05-06
MS_RS_PSZ-AC:1 Heating Capacity [kBtu/hr] | PSZ-AC:1 Heating Capacity [kBtu/hr] | 174.1187 | 164.2095 | 174.7879 | 164.7203 | [6 empty] | 2021-05-06
MS_RS_PSZ-AC:2 Heating Capacity [kBtu/hr] | PSZ-AC:2 Heating Capacity [kBtu/hr] | 736.3535 | 700.5125 | 754.1683 | 717.4283 | [6 empty] | 2021-05-06
MS_RS_PSZ-AC:3 Heating Capacity [kBtu/hr] | PSZ-AC:3 Heating Capacity [kBtu/hr] | 101.9474 | 99.4746 | 103.7319 | 101.0476 | [6 empty] | 2021-05-06
MS_RS_PSZ-AC:4 Heating Capacity [kBtu/hr] | PSZ-AC:4 Heating Capacity [kBtu/hr] | 82.0639 | 79.4189 | 83.7456 | 80.9118 | [6 empty] | 2021-05-06
id | item | Zone2A(MS-Mobile-AL) ASHRAE901-state_STD2016 | Zone2A(MS-Mobile-AL) ASHRAE901-state_STD2019 | Zone3A(MS-Jackson-MS) ASHRAE901-state_STD2016 | Zone3A(MS-Jackson-MS) ASHRAE901-state_STD2019 | [6 empty] | 2021-05-06
MS_PS_VAV_POD_1 Cooling Capacity [ton] | VAV_POD_1 Cooling Capacity [ton] | 18.5544 | 18.1427 | 18.5854 | 18.1704 | [6 empty] | 2021-05-06
MS_PS_VAV_POD_2 Cooling Capacity [ton] | VAV_POD_2 Cooling Capacity [ton] | 18.5804 | 18.1142 | 18.6029 | 18.1412 | [6 empty] | 2021-05-06
MS_PS_VAV_POD_3 Cooling Capacity [ton] | VAV_POD_3 Cooling Capacity [ton] | 16.929 | 16.0361 | 16.9755 | 16.1088 | [6 empty] | 2021-05-06
MS_PS_VAV_OTHER Cooling Capacity [ton] | VAV_OTHER Cooling Capacity [ton] | 25.8806 | 24.2116 | 26.0154 | 24.4323 | [6 empty] | 2021-05-06
MS_PS_PSZ-AC_1:6 Cooling Capacity [ton] | PSZ-AC_1:6 Cooling Capacity [ton] | 8.3738 | 7.9939 | 8.4036 | 8.0253 | [6 empty] | 2021-05-06
MS_PS_PSZ-AC_2:5 Cooling Capacity [ton] | PSZ-AC_2:5 Cooling Capacity [ton] | 5.2294 | 5.0494 | 5.2011 | 5.0291 | [6 empty] | 2021-05-06
MS_PS_PSZ-AC_2:7 Cooling Capacity [ton] | PSZ-AC_2:7 Cooling Capacity [ton] | 10.5074 | 10.5074 | 10.5074 | 10.5074 | [6 empty] | 2021-05-06
MS_PS_VAV_POD_1 Supply Flow Rate [cfm] | VAV_POD_1 Supply Flow Rate [cfm] | 5572.6544 | 5445.5216 | 5572.6544 | 5445.5216 | [6 empty] | 2021-05-06
MS_PS_VAV_POD_2 Supply Flow Rate [cfm] | VAV_POD_2 Supply Flow Rate [cfm] | 5572.6544 | 5445.5216 | 5572.6544 | 5445.5216 | [6 empty] | 2021-05-06
MS_PS_VAV_POD_3 Supply Flow Rate [cfm] | VAV_POD_3 Supply Flow Rate [cfm] | 5085.312 | 4809.8576 | 5085.312 | 4831.0464 | [6 empty] | 2021-05-06
MS_PS_VAV_OTHER Supply Flow Rate [cfm] | VAV_OTHER Supply Flow Rate [cfm] | 7776.2896 | 7267.7584 | 7797.4784 | 7331.3248 | [6 empty] | 2021-05-06
MS_PS_PSZ-AC_2:5 Supply Flow Rate [cfm] | PSZ-AC_2:5 Supply Flow Rate [cfm] | 1567.9712 | 1525.5936 | 1567.9712 | 1504.4048 | [6 empty] | 2021-05-06
MS_PS_PSZ-AC_1:6 Supply Flow Rate [cfm] | PSZ-AC_1:6 Supply Flow Rate [cfm] | 2521.4672 | 2394.3344 | 2521.4672 | 2415.5232 | [6 empty] | 2021-05-06
MS_PS_PSZ-AC_2:7 Supply Flow Rate [cfm] | PSZ-AC_2:7 Supply Flow Rate [cfm] | 3157.1312 | 3157.1312 | 3157.1312 | 3157.1312 | [6 empty] | 2021-05-06
MS_PS_Supply Air Temp. Reset Flag | Supply Air Temp. Reset Flag | No | No | No | No | [6 empty] | 2021-05-06
MS_PS_VAV_POD_1 OA Rate [cfm] | VAV_POD_1 OA Rate [cfm] | 5565.9587 | 5444.335 | 5574.5826 | 5452.6199 | [6 empty] | 2021-05-06
MS_PS_VAV_POD_2 OA Rate [cfm] | VAV_POD_2 OA Rate [cfm] | 5575.1547 | 5435.7959 | 5581.4901 | 5443.8689 | [6 empty] | 2021-05-06
MS_PS_VAV_POD_3 OA Rate [cfm] | VAV_POD_3 OA Rate [cfm] | 5078.129 | 4812.1672 | 5094.0842 | 4833.9705 | [6 empty] | 2021-05-06
MS_PS_VAV_OTHER OA Rate [cfm] | VAV_OTHER OA Rate [cfm] | 3736.1787 | 2988.8921 | 3736.1787 | 2988.8921 | [6 empty] | 2021-05-06
MS_PS_PSZ-AC_2:5 OA Rate [cfm] | PSZ-AC_2:5 OA Rate [cfm] | 1152.7343 | 1152.7343 | 1152.7343 | 1152.7343 | [6 empty] | 2021-05-06
MS_PS_PSZ-AC_1:6 OA Rate [cfm] | PSZ-AC_1:6 OA Rate [cfm] | 539.9118 | 539.9118 | 539.9118 | 539.9118 | [6 empty] | 2021-05-06
MS_PS_PSZ-AC_2:7 OA Rate [cfm] | PSZ-AC_2:7 OA Rate [cfm] | 3153.0841 | 3153.0841 | 3153.0841 | 3153.0841 | [6 empty] | 2021-05-06
MS_PS_VAV_POD_1 OA Damper [gravity, motorized] | VAV_POD_1 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2021-05-06
MS_PS_VAV_POD_2 OA Damper [gravity, motorized] | VAV_POD_2 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2021-05-06
MS_PS_VAV_POD_3 OA Damper [gravity, motorized] | VAV_POD_3 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2021-05-06
MS_PS_VAV_OTHER OA Damper [gravity, motorized] | VAV_OTHER OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2021-05-06
MS_PS_PSZ-AC_2:5 OA Damper [gravity, motorized] | PSZ-AC_2:5 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2021-05-06
MS_PS_PSZ-AC_1:6 OA Damper [gravity, motorized] | PSZ-AC_1:6 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2021-05-06
MS_PS_PSZ-AC_2:7 OA Damper [gravity, motorized] | PSZ-AC_2:7 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2021-05-06
MS_PS_VAV_POD_1 (economizer) | VAV_POD_1 (economizer) | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialEnthalpy | [6 empty] | 2021-05-06
MS_PS_VAV_POD_2 (economizer) | VAV_POD_2 (economizer) | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialEnthalpy | [6 empty] | 2021-05-06
MS_PS_VAV_POD_3 (economizer) | VAV_POD_3 (economizer) | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialEnthalpy | [6 empty] | 2021-05-06
MS_PS_VAV_OTHER (economizer) | VAV_OTHER (economizer) | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialEnthalpy | [6 empty] | 2021-05-06
MS_PS_PSZ-AC_2:5 (economizer) | PSZ-AC_2:5 (economizer) | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialEnthalpy | [6 empty] | 2021-05-06
MS_PS_PSZ-AC_1:6 (economizer) | PSZ-AC_1:6 (economizer) | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialEnthalpy | [6 empty] | 2021-05-06
MS_PS_PSZ-AC_2:7 (economizer) | PSZ-AC_2:7 (economizer) | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialEnthalpy | [6 empty] | 2021-05-06
MS_PS_VAV_Pod_1_ERV Flag | VAV_Pod_1_ERV Flag | Yes | Yes | Yes | Yes | [6 empty] | 2021-05-06
MS_PS_VAV_Pod_2_ERV Flag | VAV_Pod_2_ERV Flag | Yes | Yes | Yes | Yes | [6 empty] | 2021-05-06
MS_PS_VAV_Pod_3_ERV Flag | VAV_Pod_3_ERV Flag | Yes | Yes | Yes | Yes | [6 empty] | 2021-05-06
MS_PS_VAV_OTHER_ERV Flag | VAV_OTHER_ERV Flag | Yes | Yes | Yes | Yes | [6 empty] | 2021-05-06
MS_PS_PSZ_AC_2_5_ERV Flag | PSZ_AC_2_5_ERV Flag | Yes | Yes | Yes | Yes | [6 empty] | 2021-05-06
MS_PS_PSZ_AC_2_7_ERV Flag | PSZ_AC_2_7_ERV Flag | Yes | Yes | Yes | Yes | [6 empty] | 2021-05-06
MS_PS_HEATSYS1 Capacity [MMBTU/h] | HEATSYS1 Capacity [MMBTU/h] | 0.82674 | 0.77479 | 0.87528 | 0.83206 | [6 empty] | 2021-05-06
MS_PS_HEATSYS1 Flow Rate [gal/min] | HEATSYS1 Flow Rate [gal/min] | 84.8499 | 79.5177 | 89.8319 | 85.3955 | [6 empty] | 2021-05-06
MS_PS_VAV_POD_1 Fan Power [hp] | VAV_POD_1 Fan Power [hp] | 8.2143 | 8.032 | 8.228 | 8.0443 | [6 empty] | 2021-05-06
MS_PS_VAV_POD_2 Fan Power [hp] | VAV_POD_2 Fan Power [hp] | 8.2258 | 8.0194 | 8.2358 | 8.0313 | [6 empty] | 2021-05-06
MS_PS_VAV_POD_3 Fan Power [hp] | VAV_POD_3 Fan Power [hp] | 7.4947 | 7.0994 | 7.5153 | 7.1316 | [6 empty] | 2021-05-06
MS_PS_VAV_OTHER Fan Power [hp] | VAV_OTHER Fan Power [hp] | 11.3709 | 10.6376 | 11.4301 | 10.7345 | [6 empty] | 2021-05-06
MS_PS_HEATSYS1 Pump Power [hp] | HEATSYS1 Pump Power [hp] | 1.8341 | 1.7018 | 1.9418 | 1.8276 | [6 empty] | 2021-05-06
MS_PS_PSZ-AC_1:6 Heating Capacity [kBtu/hr] | PSZ-AC_1:6 Heating Capacity [kBtu/hr] | 197.2746 | 188.4578 | 200.2221 | 191.4716 | [6 empty] | 2021-05-06
MS_PS_PSZ-AC_2:5 Heating Capacity [kBtu/hr] | PSZ-AC_2:5 Heating Capacity [kBtu/hr] | 110.7002 | 108.7157 | 116.2419 | 114.3515 | [6 empty] | 2021-05-06
MS_PS_PSZ-AC_2:7 Heating Capacity [kBtu/hr] | PSZ-AC_2:7 Heating Capacity [kBtu/hr] | 260.9412 | 260.9412 | 277.0891 | 277.0891 | [6 empty] | 2021-05-06
MS_PS_ZN_VAV_BOXes_Max_Reheat_Water_Flow_GPM | ZN_VAV_BOXes_Max_Reheat_Water_Flow_GPM | 62.5698 | 58.1962 | 63.563 | 60.2164 | [6 empty] | 2021-05-06
id | item | Zone2A(MS-Mobile-AL) ASHRAE901-state_STD2016 | Zone2A(MS-Mobile-AL) ASHRAE901-state_STD2019 | Zone3A(MS-Jackson-MS) ASHRAE901-state_STD2016 | Zone3A(MS-Jackson-MS) ASHRAE901-state_STD2019 | [6 empty] | 2021-05-06
MS_SH_SAC_FRONTOFFICE Cooling Capacity [ton] | SAC_FRONTOFFICE Cooling Capacity [ton] | 2.4943 | 2.3639 | 2.5147 | 2.3851 | [6 empty] | 2021-05-06
MS_SH_SAC_FRONTLOUNGE Cooling Capacity [ton] | SAC_FRONTLOUNGE Cooling Capacity [ton] | 6.1703 | 5.8538 | 6.1685 | 5.8565 | [6 empty] | 2021-05-06
MS_SH_SAC_MEETINGROOM Cooling Capacity [ton] | SAC_MEETINGROOM Cooling Capacity [ton] | 2.938 | 2.843 | 2.9428 | 2.8474 | [6 empty] | 2021-05-06
MS_SH_SAC_EXC_EMPLGE_RESTRM Cooling Capacity [ton] | SAC_EXC_EMPLGE_RESTRM Cooling Capacity [ton] | 6.1317 | 6.0975 | 6.2319 | 6.1894 | [6 empty] | 2021-05-06
MS_SH_SAC_FO_ADDAQ SUPPLY FAN Supply Flow Rate [cfm] | SAC_FO_ADDAQ SUPPLY FAN Supply Flow Rate [cfm] | 805.1744 | 741.608 | 805.1744 | 741.608 | [6 empty] | 2021-05-06
MS_SH_SAC_FL_ADDAQ SUPPLY FAN Supply Flow Rate [cfm] | SAC_FL_ADDAQ SUPPLY FAN Supply Flow Rate [cfm] | 1843.4256 | 1758.6704 | 1843.4256 | 1758.6704 | [6 empty] | 2021-05-06
MS_SH_SAC_MR_ADDAQ SUPPLY FAN Supply Flow Rate [cfm] | SAC_MR_ADDAQ SUPPLY FAN Supply Flow Rate [cfm] | 889.9296 | 847.552 | 889.9296 | 847.552 | [6 empty] | 2021-05-06
MS_SH_SAC_EXC_ADDAQ SUPPLY FAN Supply Flow Rate [cfm] | SAC_EXC_ADDAQ SUPPLY FAN Supply Flow Rate [cfm] | 2161.2576 | 2161.2576 | 2182.4464 | 2161.2576 | [6 empty] | 2021-05-06
MS_SH_SAC_Exc_EmpLge_RestRm OA Rate [cfm] | SAC_Exc_EmpLge_RestRm OA Rate [cfm] | 199.9928 | 199.9928 | 199.9928 | 199.9928 | [6 empty] | 2021-05-06
MS_SH_SAC_FrontLounge OA Rate [cfm] | SAC_FrontLounge OA Rate [cfm] | 500.0133 | 500.0133 | 500.0133 | 500.0133 | [6 empty] | 2021-05-06
MS_SH_SAC_FrontOffice OA Rate [cfm] | SAC_FrontOffice OA Rate [cfm] | 119.2938 | 119.2938 | 119.2938 | 119.2938 | [6 empty] | 2021-05-06
MS_SH_SAC_MeetingRoom OA Rate [cfm] | SAC_MeetingRoom OA Rate [cfm] | 267.7629 | 267.7629 | 267.7629 | 267.7629 | [6 empty] | 2021-05-06
MS_SH_SAC_FrontLounge OA Damper [gravity, motorized] | SAC_FrontLounge OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2021-05-06
MS_SH_SAC_FrontOffice (economizer) | SAC_FrontOffice (economizer) | No | No | No | No | [6 empty] | 2021-05-06
MS_SH_SAC_FrontLounge (economizer) | SAC_FrontLounge (economizer) | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialEnthalpy | [6 empty] | 2021-05-06
MS_SH_SAC_MeetingRoom (economizer) | SAC_MeetingRoom (economizer) | No | No | No | No | [6 empty] | 2021-05-06
MS_SH_SAC_Exc_EmpLge_RestRm (economizer) | SAC_Exc_EmpLge_RestRm (economizer) | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialEnthalpy | [6 empty] | 2021-05-06
MS_SH_SAC_FRONTOFFICE Heating Capacity [kBtu/hr] | SAC_FRONTOFFICE Heating Capacity [kBtu/hr] | 34.7792 | 32.7596 | 35.3057 | 33.3256 | [6 empty] | 2021-05-06
MS_SH_SAC_FRONTLOUNGE Heating Capacity [kBtu/hr] | SAC_FRONTLOUNGE Heating Capacity [kBtu/hr] | 90.7448 | 87.2755 | 93.1224 | 89.7142 | [6 empty] | 2021-05-06
MS_SH_SAC_MEETINGROOM Heating Capacity [kBtu/hr] | SAC_MEETINGROOM Heating Capacity [kBtu/hr] | 44.5797 | 43.5389 | 45.9292 | 44.887 | [6 empty] | 2021-05-06
MS_SH_SAC_EXC_EMPLGE_RESTRM Heating Capacity [kBtu/hr] | SAC_EXC_EMPLGE_RESTRM Heating Capacity [kBtu/hr] | 88.3329 | 87.8053 | 89.7913 | 89.144 | [6 empty] | 2021-05-06
id | item | Zone2A(MS-Mobile-AL) ASHRAE901-state_STD2016 | Zone2A(MS-Mobile-AL) ASHRAE901-state_STD2019 | Zone3A(MS-Jackson-MS) ASHRAE901-state_STD2016 | Zone3A(MS-Jackson-MS) ASHRAE901-state_STD2019 | [6 empty] | 2021-05-06
MS_MA_SPLIT GSW COOLING COIL Cooling Capacity [ton] | SPLIT GSW COOLING COIL Cooling Capacity [ton] | 0.88639 | 0.87606 | 0.90296 | 0.89272 | [6 empty] | 2021-05-06
MS_MA_SPLIT GNW COOLING COIL Cooling Capacity [ton] | SPLIT GNW COOLING COIL Cooling Capacity [ton] | 0.88001 | 0.86933 | 0.89226 | 0.88167 | [6 empty] | 2021-05-06
MS_MA_SPLIT OFFICE COOLING COIL Cooling Capacity [ton] | SPLIT OFFICE COOLING COIL Cooling Capacity [ton] | 1.7179 | 1.6347 | 1.7356 | 1.6551 | [6 empty] | 2021-05-06
MS_MA_SPLIT GNE COOLING COIL Cooling Capacity [ton] | SPLIT GNE COOLING COIL Cooling Capacity [ton] | 0.79075 | 0.78105 | 0.7964 | 0.78716 | [6 empty] | 2021-05-06
MS_MA_SPLIT GN1 COOLING COIL Cooling Capacity [ton] | SPLIT GN1 COOLING COIL Cooling Capacity [ton] | 0.6949 | 0.68634 | 0.6956 | 0.68728 | [6 empty] | 2021-05-06
MS_MA_SPLIT GN2 COOLING COIL Cooling Capacity [ton] | SPLIT GN2 COOLING COIL Cooling Capacity [ton] | 0.69327 | 0.68472 | 0.69397 | 0.68566 | [6 empty] | 2021-05-06
MS_MA_SPLIT GS1 COOLING COIL Cooling Capacity [ton] | SPLIT GS1 COOLING COIL Cooling Capacity [ton] | 0.69458 | 0.68451 | 0.70421 | 0.6933 | [6 empty] | 2021-05-06
MS_MA_SPLIT GS2 COOLING COIL Cooling Capacity [ton] | SPLIT GS2 COOLING COIL Cooling Capacity [ton] | 0.72776 | 0.71514 | 0.73651 | 0.724 | [6 empty] | 2021-05-06
MS_MA_SPLIT MSW COOLING COIL Cooling Capacity [ton] | SPLIT MSW COOLING COIL Cooling Capacity [ton] | 1.9698 | 1.9474 | 1.9994 | 1.9784 | [6 empty] | 2021-05-06
MS_MA_SPLIT MNW COOLING COIL Cooling Capacity [ton] | SPLIT MNW COOLING COIL Cooling Capacity [ton] | 1.963 | 1.9404 | 1.9809 | 1.9597 | [6 empty] | 2021-05-06
MS_MA_SPLIT MSE COOLING COIL Cooling Capacity [ton] | SPLIT MSE COOLING COIL Cooling Capacity [ton] | 1.7019 | 1.6825 | 1.7294 | 1.7102 | [6 empty] | 2021-05-06
MS_MA_SPLIT MNE COOLING COIL Cooling Capacity [ton] | SPLIT MNE COOLING COIL Cooling Capacity [ton] | 1.7127 | 1.6924 | 1.7251 | 1.7054 | [6 empty] | 2021-05-06
MS_MA_SPLIT MN1 COOLING COIL Cooling Capacity [ton] | SPLIT MN1 COOLING COIL Cooling Capacity [ton] | 1.4553 | 1.4375 | 1.456 | 1.4399 | [6 empty] | 2021-05-06
MS_MA_SPLIT MN2 COOLING COIL Cooling Capacity [ton] | SPLIT MN2 COOLING COIL Cooling Capacity [ton] | 1.451 | 1.4333 | 1.4518 | 1.4303 | [6 empty] | 2021-05-06
MS_MA_SPLIT MS1 COOLING COIL Cooling Capacity [ton] | SPLIT MS1 COOLING COIL Cooling Capacity [ton] | 1.4492 | 1.4322 | 1.4697 | 1.4527 | [6 empty] | 2021-05-06
MS_MA_SPLIT MS2 COOLING COIL Cooling Capacity [ton] | SPLIT MS2 COOLING COIL Cooling Capacity [ton] | 1.445 | 1.428 | 1.4655 | 1.4486 | [6 empty] | 2021-05-06
MS_MA_SPLIT TSW COOLING COIL Cooling Capacity [ton] | SPLIT TSW COOLING COIL Cooling Capacity [ton] | 1.2133 | 1.2016 | 1.2394 | 1.2284 | [6 empty] | 2021-05-06
MS_MA_SPLIT TNW COOLING COIL Cooling Capacity [ton] | SPLIT TNW COOLING COIL Cooling Capacity [ton] | 1.1974 | 1.1856 | 1.2127 | 1.202 | [6 empty] | 2021-05-06
MS_MA_SPLIT TSE COOLING COIL Cooling Capacity [ton] | SPLIT TSE COOLING COIL Cooling Capacity [ton] | 1.097 | 1.0864 | 1.1264 | 1.1162 | [6 empty] | 2021-05-06
MS_MA_SPLIT TNE COOLING COIL Cooling Capacity [ton] | SPLIT TNE COOLING COIL Cooling Capacity [ton] | 1.0707 | 1.0598 | 1.0909 | 1.0805 | [6 empty] | 2021-05-06
MS_MA_SPLIT TN1 COOLING COIL Cooling Capacity [ton] | SPLIT TN1 COOLING COIL Cooling Capacity [ton] | 0.8766 | 0.86777 | 0.89079 | 0.8821 | [6 empty] | 2021-05-06
MS_MA_SPLIT TN2 COOLING COIL Cooling Capacity [ton] | SPLIT TN2 COOLING COIL Cooling Capacity [ton] | 0.87171 | 0.86291 | 0.88591 | 0.87722 | [6 empty] | 2021-05-06
MS_MA_SPLIT TS1 COOLING COIL Cooling Capacity [ton] | SPLIT TS1 COOLING COIL Cooling Capacity [ton] | 0.92261 | 0.91354 | 0.94827 | 0.93935 | [6 empty] | 2021-05-06
MS_MA_SPLIT TS2 COOLING COIL Cooling Capacity [ton] | SPLIT TS2 COOLING COIL Cooling Capacity [ton] | 0.92318 | 0.91421 | 0.94916 | 0.94026 | [6 empty] | 2021-05-06
MS_MA_Split GN1 Furnace with DX Cooling OA Rate [cfm] | Split GN1 Furnace with DX Cooling OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | [6 empty] | 2021-05-06
MS_MA_Split GN2 Furnace with DX Cooling OA Rate [cfm] | Split GN2 Furnace with DX Cooling OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | [6 empty] | 2021-05-06
MS_MA_Split GNE Furnace with DX Cooling OA Rate [cfm] | Split GNE Furnace with DX Cooling OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | [6 empty] | 2021-05-06
MS_MA_Split GNW Furnace with DX Cooling OA Rate [cfm] | Split GNW Furnace with DX Cooling OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | [6 empty] | 2021-05-06
MS_MA_Split GS1 Furnace with DX Cooling OA Rate [cfm] | Split GS1 Furnace with DX Cooling OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | [6 empty] | 2021-05-06
MS_MA_Split GS2 Furnace with DX Cooling OA Rate [cfm] | Split GS2 Furnace with DX Cooling OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | [6 empty] | 2021-05-06
MS_MA_Split GSW Furnace with DX Cooling OA Rate [cfm] | Split GSW Furnace with DX Cooling OA Rate [cfm] | 56.9945 | 56.9945 | 56.9945 | 56.9945 | [6 empty] | 2021-05-06
MS_MA_Split MN1 Furnace with DX Cooling OA Rate [cfm] | Split MN1 Furnace with DX Cooling OA Rate [cfm] | 109.9824 | 109.9824 | 109.9824 | 109.9824 | [6 empty] | 2021-05-06
MS_MA_Split MN2 Furnace with DX Cooling OA Rate [cfm] | Split MN2 Furnace with DX Cooling OA Rate [cfm] | 109.9824 | 109.9824 | 109.9824 | 109.9824 | [6 empty] | 2021-05-06
MS_MA_Split MNE Furnace with DX Cooling OA Rate [cfm] | Split MNE Furnace with DX Cooling OA Rate [cfm] | 109.9824 | 109.9824 | 109.9824 | 109.9824 | [6 empty] | 2021-05-06
MS_MA_Split MNW Furnace with DX Cooling OA Rate [cfm] | Split MNW Furnace with DX Cooling OA Rate [cfm] | 109.9824 | 109.9824 | 109.9824 | 109.9824 | [6 empty] | 2021-05-06
MS_MA_Split MS1 Furnace with DX Cooling OA Rate [cfm] | Split MS1 Furnace with DX Cooling OA Rate [cfm] | 109.9824 | 109.9824 | 109.9824 | 109.9824 | [6 empty] | 2021-05-06
MS_MA_Split MS2 Furnace with DX Cooling OA Rate [cfm] | Split MS2 Furnace with DX Cooling OA Rate [cfm] | 109.9824 | 109.9824 | 109.9824 | 109.9824 | [6 empty] | 2021-05-06
MS_MA_Split MSE Furnace with DX Cooling OA Rate [cfm] | Split MSE Furnace with DX Cooling OA Rate [cfm] | 109.9824 | 109.9824 | 109.9824 | 109.9824 | [6 empty] | 2021-05-06
MS_MA_Split MSW Furnace with DX Cooling OA Rate [cfm] | Split MSW Furnace with DX Cooling OA Rate [cfm] | 109.9824 | 109.9824 | 109.9824 | 109.9824 | [6 empty] | 2021-05-06
MS_MA_Split Office Furnace with DX Cooling OA Rate [cfm] | Split Office Furnace with DX Cooling OA Rate [cfm] | 80.7372 | 80.7372 | 80.7372 | 80.7372 | [6 empty] | 2021-05-06
MS_MA_Split TN1 Furnace with DX Cooling OA Rate [cfm] | Split TN1 Furnace with DX Cooling OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | [6 empty] | 2021-05-06
MS_MA_Split TN2 Furnace with DX Cooling OA Rate [cfm] | Split TN2 Furnace with DX Cooling OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | [6 empty] | 2021-05-06
MS_MA_Split TNE Furnace with DX Cooling OA Rate [cfm] | Split TNE Furnace with DX Cooling OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | [6 empty] | 2021-05-06
MS_MA_Split TNW Furnace with DX Cooling OA Rate [cfm] | Split TNW Furnace with DX Cooling OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | [6 empty] | 2021-05-06
MS_MA_Split TS1 Furnace with DX Cooling OA Rate [cfm] | Split TS1 Furnace with DX Cooling OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | [6 empty] | 2021-05-06
MS_MA_Split TS2 Furnace with DX Cooling OA Rate [cfm] | Split TS2 Furnace with DX Cooling OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | [6 empty] | 2021-05-06
MS_MA_Split TSE Furnace with DX Cooling OA Rate [cfm] | Split TSE Furnace with DX Cooling OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | [6 empty] | 2021-05-06
MS_MA_Split TSW Furnace with DX Cooling OA Rate [cfm] | Split TSW Furnace with DX Cooling OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | [6 empty] | 2021-05-06
MS_MA_SPLIT GSW HEATING COIL Heating Capacity [kBtu/hr] | SPLIT GSW HEATING COIL Heating Capacity [kBtu/hr] | 6.2828 | 6.1758 | 6.573 | 6.4908 | [6 empty] | 2021-05-06
MS_MA_SPLIT GNW HEATING COIL Heating Capacity [kBtu/hr] | SPLIT GNW HEATING COIL Heating Capacity [kBtu/hr] | 6.2472 | 6.1352 | 6.5161 | 6.4305 | [6 empty] | 2021-05-06
MS_MA_SPLIT OFFICE HEATING COIL Heating Capacity [kBtu/hr] | SPLIT OFFICE HEATING COIL Heating Capacity [kBtu/hr] | 16.5454 | 16.382 | 17.186 | 17.0366 | [6 empty] | 2021-05-06
MS_MA_SPLIT GNE HEATING COIL Heating Capacity [kBtu/hr] | SPLIT GNE HEATING COIL Heating Capacity [kBtu/hr] | 6.2472 | 6.1352 | 6.5161 | 6.4305 | [6 empty] | 2021-05-06
MS_MA_SPLIT GN1 HEATING COIL Heating Capacity [kBtu/hr] | SPLIT GN1 HEATING COIL Heating Capacity [kBtu/hr] | 4.5509 | 4.5509 | 4.8325 | 4.8325 | [6 empty] | 2021-05-06
MS_MA_SPLIT GN2 HEATING COIL Heating Capacity [kBtu/hr] | SPLIT GN2 HEATING COIL Heating Capacity [kBtu/hr] | 4.5509 | 4.5509 | 4.8325 | 4.8325 | [6 empty] | 2021-05-06
MS_MA_SPLIT GS1 HEATING COIL Heating Capacity [kBtu/hr] | SPLIT GS1 HEATING COIL Heating Capacity [kBtu/hr] | 4.5509 | 4.5509 | 4.8325 | 4.8325 | [6 empty] | 2021-05-06
MS_MA_SPLIT GS2 HEATING COIL Heating Capacity [kBtu/hr] | SPLIT GS2 HEATING COIL Heating Capacity [kBtu/hr] | 4.7953 | 4.7393 | 5.0632 | 5.025 | [6 empty] | 2021-05-06
MS_MA_SPLIT MSW HEATING COIL Heating Capacity [kBtu/hr] | SPLIT MSW HEATING COIL Heating Capacity [kBtu/hr] | 11.2378 | 11.0279 | 11.768 | 11.6099 | [6 empty] | 2021-05-06
MS_MA_SPLIT MNW HEATING COIL Heating Capacity [kBtu/hr] | SPLIT MNW HEATING COIL Heating Capacity [kBtu/hr] | 11.32 | 11.0975 | 11.8405 | 11.6733 | [6 empty] | 2021-05-06
MS_MA_SPLIT MSE HEATING COIL Heating Capacity [kBtu/hr] | SPLIT MSE HEATING COIL Heating Capacity [kBtu/hr] | 11.2378 | 11.0279 | 11.768 | 11.6099 | [6 empty] | 2021-05-06
MS_MA_SPLIT MNE HEATING COIL Heating Capacity [kBtu/hr] | SPLIT MNE HEATING COIL Heating Capacity [kBtu/hr] | 11.32 | 11.0975 | 11.8405 | 11.6733 | [6 empty] | 2021-05-06
MS_MA_SPLIT MN1 HEATING COIL Heating Capacity [kBtu/hr] | SPLIT MN1 HEATING COIL Heating Capacity [kBtu/hr] | 9.1019 | 9.1019 | 9.6651 | 9.6651 | [6 empty] | 2021-05-06
MS_MA_SPLIT MN2 HEATING COIL Heating Capacity [kBtu/hr] | SPLIT MN2 HEATING COIL Heating Capacity [kBtu/hr] | 9.1019 | 9.1019 | 9.6651 | 9.6651 | [6 empty] | 2021-05-06
MS_MA_SPLIT MS1 HEATING COIL Heating Capacity [kBtu/hr] | SPLIT MS1 HEATING COIL Heating Capacity [kBtu/hr] | 9.1019 | 9.1019 | 9.6651 | 9.6651 | [6 empty] | 2021-05-06
MS_MA_SPLIT MS2 HEATING COIL Heating Capacity [kBtu/hr] | SPLIT MS2 HEATING COIL Heating Capacity [kBtu/hr] | 9.1019 | 9.1019 | 9.6651 | 9.6651 | [6 empty] | 2021-05-06
MS_MA_SPLIT TSW HEATING COIL Heating Capacity [kBtu/hr] | SPLIT TSW HEATING COIL Heating Capacity [kBtu/hr] | 8.5 | 8.3971 | 8.9435 | 8.8655 | [6 empty] | 2021-05-06
MS_MA_SPLIT TNW HEATING COIL Heating Capacity [kBtu/hr] | SPLIT TNW HEATING COIL Heating Capacity [kBtu/hr] | 8.5479 | 8.439 | 8.9872 | 8.9049 | [6 empty] | 2021-05-06
MS_MA_SPLIT TSE HEATING COIL Heating Capacity [kBtu/hr] | SPLIT TSE HEATING COIL Heating Capacity [kBtu/hr] | 8.5 | 8.3971 | 8.9435 | 8.8655 | [6 empty] | 2021-05-06
MS_MA_SPLIT TNE HEATING COIL Heating Capacity [kBtu/hr] | SPLIT TNE HEATING COIL Heating Capacity [kBtu/hr] | 8.5479 | 8.439 | 8.9872 | 8.9049 | [6 empty] | 2021-05-06
MS_MA_SPLIT TN1 HEATING COIL Heating Capacity [kBtu/hr] | SPLIT TN1 HEATING COIL Heating Capacity [kBtu/hr] | 6.4254 | 6.3761 | 6.916 | 6.8842 | [6 empty] | 2021-05-06
MS_MA_SPLIT TN2 HEATING COIL Heating Capacity [kBtu/hr] | SPLIT TN2 HEATING COIL Heating Capacity [kBtu/hr] | 6.4254 | 6.3761 | 6.916 | 6.8842 | [6 empty] | 2021-05-06
MS_MA_SPLIT TS1 HEATING COIL Heating Capacity [kBtu/hr] | SPLIT TS1 HEATING COIL Heating Capacity [kBtu/hr] | 6.3704 | 6.327 | 6.8652 | 6.8376 | [6 empty] | 2021-05-06
MS_MA_SPLIT TS2 HEATING COIL Heating Capacity [kBtu/hr] | SPLIT TS2 HEATING COIL Heating Capacity [kBtu/hr] | 6.3704 | 6.327 | 6.8652 | 6.8376 | [6 empty] | 2021-05-06
MS_MA_Split_GSW ERV Flag | Split_GSW ERV Flag | No | Yes | No | Yes | [6 empty] | 2021-05-06
MS_MA_Split_GNW ERV Flag | Split_GNW ERV Flag | No | Yes | No | Yes | [6 empty] | 2021-05-06
MS_MA_Split_GNE ERV Flag | Split_GNE ERV Flag | No | Yes | No | Yes | [6 empty] | 2021-05-06
MS_MA_Split_GN1 ERV Flag | Split_GN1 ERV Flag | No | Yes | No | Yes | [6 empty] | 2021-05-06
MS_MA_Split_GN2 ERV Flag | Split_GN2 ERV Flag | No | Yes | No | Yes | [6 empty] | 2021-05-06
MS_MA_Split_GS1 ERV Flag | Split_GS1 ERV Flag | No | Yes | No | Yes | [6 empty] | 2021-05-06
MS_MA_Split_GS2 ERV Flag | Split_GS2 ERV Flag | No | Yes | No | Yes | [6 empty] | 2021-05-06
MS_MA_Split_MSW ERV Flag | Split_MSW ERV Flag | No | Yes | No | Yes | [6 empty] | 2021-05-06
MS_MA_Split_MNW ERV Flag | Split_MNW ERV Flag | No | Yes | No | Yes | [6 empty] | 2021-05-06
MS_MA_Split_MSE ERV Flag | Split_MSE ERV Flag | No | Yes | No | Yes | [6 empty] | 2021-05-06
MS_MA_Split_MNE ERV Flag | Split_MNE ERV Flag | No | Yes | No | Yes | [6 empty] | 2021-05-06
MS_MA_Split_MN1 ERV Flag | Split_MN1 ERV Flag | No | Yes | No | Yes | [6 empty] | 2021-05-06
MS_MA_Split_MN2 ERV Flag | Split_MN2 ERV Flag | No | Yes | No | Yes | [6 empty] | 2021-05-06
MS_MA_Split_MS1 ERV Flag | Split_MS1 ERV Flag | No | Yes | No | Yes | [6 empty] | 2021-05-06
MS_MA_Split_MS2 ERV Flag | Split_MS2 ERV Flag | No | Yes | No | Yes | [6 empty] | 2021-05-06
MS_MA_Split_TSW ERV Flag | Split_TSW ERV Flag | No | Yes | No | Yes | [6 empty] | 2021-05-06
MS_MA_Split_TNW ERV Flag | Split_TNW ERV Flag | No | Yes | No | Yes | [6 empty] | 2021-05-06
MS_MA_Split_TSE ERV Flag | Split_TSE ERV Flag | No | Yes | No | Yes | [6 empty] | 2021-05-06
MS_MA_Split_TNE ERV Flag | Split_TNE ERV Flag | No | Yes | No | Yes | [6 empty] | 2021-05-06
MS_MA_Split_TN1 ERV Flag | Split_TN1 ERV Flag | No | Yes | No | Yes | [6 empty] | 2021-05-06
MS_MA_Split_TN2 ERV Flag | Split_TN2 ERV Flag | No | Yes | No | Yes | [6 empty] | 2021-05-06
MS_MA_Split_TS1 ERV Flag | Split_TS1 ERV Flag | No | Yes | No | Yes | [6 empty] | 2021-05-06
MS_MA_Split_TS2 ERV Flag | Split_TS2 ERV Flag | No | Yes | No | Yes | [6 empty] | 2021-05-06
id | item | Zone6B(MT-Helena-MT) ASHRAE901-state_STD2016 | Zone6B(MT-Helena-MT) ASHRAE901-state_STD2019 | [8 empty] | 2021-05-06
MT_SO_PSZ-AC:1 Cooling Capacity [ton] | PSZ-AC:1 Cooling Capacity [ton] | 1.6212 | 1.5034 | [8 empty] | 2021-05-06
MT_SO_PSZ-AC:2 Cooling Capacity [ton] | PSZ-AC:2 Cooling Capacity [ton] | 1.4585 | 1.3597 | [8 empty] | 2021-05-06
MT_SO_PSZ-AC:3 Cooling Capacity [ton] | PSZ-AC:3 Cooling Capacity [ton] | 1.1714 | 1.0897 | [8 empty] | 2021-05-06
MT_SO_PSZ-AC:4 Cooling Capacity [ton] | PSZ-AC:4 Cooling Capacity [ton] | 1.3044 | 1.2019 | [8 empty] | 2021-05-06
MT_SO_PSZ-AC:5 Cooling Capacity [ton] | PSZ-AC:5 Cooling Capacity [ton] | 1.4291 | 1.3412 | [8 empty] | 2021-05-06
MT_SO_PSZ-AC:1 Supply Flow Rate [cfm] | PSZ-AC:1 Supply Flow Rate [cfm] | 720.4192 | 678.0416 | [8 empty] | 2021-05-06
MT_SO_PSZ-AC:2 Supply Flow Rate [cfm] | PSZ-AC:2 Supply Flow Rate [cfm] | 656.8528 | 614.4752 | [8 empty] | 2021-05-06
MT_SO_PSZ-AC:3 Supply Flow Rate [cfm] | PSZ-AC:3 Supply Flow Rate [cfm] | 529.72 | 487.3424 | [8 empty] | 2021-05-06
MT_SO_PSZ-AC:4 Supply Flow Rate [cfm] | PSZ-AC:4 Supply Flow Rate [cfm] | 593.2864 | 550.9088 | [8 empty] | 2021-05-06
MT_SO_PSZ-AC:5 Supply Flow Rate [cfm] | PSZ-AC:5 Supply Flow Rate [cfm] | 635.664 | 593.2864 | [8 empty] | 2021-05-06
MT_SO_PSZ-AC:1 OA Rate [cfm] | PSZ-AC:1 OA Rate [cfm] | 136.9178 | 136.9178 | [8 empty] | 2021-05-06
MT_SO_PSZ-AC:2 OA Rate [cfm] | PSZ-AC:2 OA Rate [cfm] | 103.7925 | 103.7925 | [8 empty] | 2021-05-06
MT_SO_PSZ-AC:3 OA Rate [cfm] | PSZ-AC:3 OA Rate [cfm] | 61.5711 | 61.5711 | [8 empty] | 2021-05-06
MT_SO_PSZ-AC:4 OA Rate [cfm] | PSZ-AC:4 OA Rate [cfm] | 103.7925 | 103.7925 | [8 empty] | 2021-05-06
MT_SO_PSZ-AC:5 OA Rate [cfm] | PSZ-AC:5 OA Rate [cfm] | 61.5711 | 61.5711 | [8 empty] | 2021-05-06
MT_SO_PSZ-AC:1 heating Capacity [kBtu/hr] | PSZ-AC:1 heating Capacity [kBtu/hr] | 15.988 | 15.9538 | [8 empty] | 2021-05-06
MT_SO_PSZ-AC:2 heating Capacity [kBtu/hr] | PSZ-AC:2 heating Capacity [kBtu/hr] | 21.8197 | 21.5429 | [8 empty] | 2021-05-06
MT_SO_PSZ-AC:3 heating Capacity [kBtu/hr] | PSZ-AC:3 heating Capacity [kBtu/hr] | 13.1982 | 13.0453 | [8 empty] | 2021-05-06
MT_SO_PSZ-AC:4 heating Capacity [kBtu/hr] | PSZ-AC:4 heating Capacity [kBtu/hr] | 21.7258 | 21.4924 | [8 empty] | 2021-05-06
MT_SO_PSZ-AC:5 heating Capacity [kBtu/hr] | PSZ-AC:5 heating Capacity [kBtu/hr] | 13.2508 | 13.093 | [8 empty] | 2021-05-06
id | item | Zone6B(MT-Helena-MT) ASHRAE901-state_STD2016 | Zone6B(MT-Helena-MT) ASHRAE901-state_STD2019 | [8 empty] | 2021-05-06
MT_LO_CAV_BAS Supply Flow Rate [cfm] | CAV_BAS Supply Flow Rate [cfm] | 13327.7552 | 12310.6928 | [8 empty] | 2021-05-06
MT_LO_VAV_BOT WITH REHEAT Supply Flow Rate [cfm] | VAV_BOT WITH REHEAT Supply Flow Rate [cfm] | 22396.5616 | 21167.6112 | [8 empty] | 2021-05-06
MT_LO_VAV_MID WITH REHEAT Supply Flow Rate [cfm] | VAV_MID WITH REHEAT Supply Flow Rate [cfm] | 208010.4499 | 195954.0227 | [8 empty] | 2021-05-06
MT_LO_VAV_TOP WITH REHEAT Supply Flow Rate [cfm] | VAV_TOP WITH REHEAT Supply Flow Rate [cfm] | 22332.9952 | 21167.6112 | [8 empty] | 2021-05-06
MT_LO_Supply Air Temp. Reset Flag | Supply Air Temp. Reset Flag | Yes | Yes | [8 empty] | 2021-05-06
MT_LO_CAV_BAS OA Rate [cfm] | CAV_BAS OA Rate [cfm] | 2542.8255 | 2542.8255 | [8 empty] | 2021-05-06
MT_LO_VAV_BOT WITH REHEAT OA Rate [cfm] | VAV_BOT WITH REHEAT OA Rate [cfm] | 5377.8022 | 4302.174 | [8 empty] | 2021-05-06
MT_LO_VAV_MID WITH REHEAT OA Rate [cfm] | VAV_MID WITH REHEAT OA Rate [cfm] | 53777.9373 | 43021.7396 | [8 empty] | 2021-05-06
MT_LO_VAV_TOP WITH REHEAT OA Rate [cfm] | VAV_TOP WITH REHEAT OA Rate [cfm] | 5377.8022 | 4302.174 | [8 empty] | 2021-05-06
MT_LO_AIRLOOP DATACENTER BASEMENT OA Rate [cfm] | AIRLOOP DATACENTER BASEMENT OA Rate [cfm] | 716.9654 | 716.9654 | [8 empty] | 2021-05-06
MT_LO_VAV_bot_WITH_REHEAT ERV Flag | VAV_bot_WITH_REHEAT ERV Flag | No | No | [8 empty] | 2021-05-06
MT_LO_VAV_mid_WITH_REHEAT ERV Flag | VAV_mid_WITH_REHEAT ERV Flag | No | No | [8 empty] | 2021-05-06
MT_LO_VAV_top_WITH_REHEAT ERV Flag | VAV_top_WITH_REHEAT ERV Flag | No | No | [8 empty] | 2021-05-06
MT_LO_COOLSYS1 CHILLER1 Capacity [ton] | COOLSYS1 CHILLER1 Capacity [ton] | 313.6733 | 287.6933 | [8 empty] | 2021-05-06
MT_LO_COOLSYS1 CHILLER2 Capacity [ton] | COOLSYS1 CHILLER2 Capacity [ton] | 313.6733 | 287.6933 | [8 empty] | 2021-05-06
MT_LO_TOWERWATERSYS COOLTOWER 1 Capacity [ton] | TOWERWATERSYS COOLTOWER 1 Capacity [ton] | 298.1066 | 273.41 | [8 empty] | 2021-05-06
MT_LO_TOWERWATERSYS COOLTOWER 2 Capacity [ton] | TOWERWATERSYS COOLTOWER 2 Capacity [ton] | 298.1066 | 273.41 | [8 empty] | 2021-05-06
MT_LO_HEATSYS1 BOILER Capacity [MMBTU/h] | HEATSYS1 BOILER Capacity [MMBTU/h] | 5045.6351 | 4414.709 | [8 empty] | 2021-05-06
MT_LO_COOLSYS1 PUMP Flow Rate [gal/min] | COOLSYS1 PUMP Flow Rate [gal/min] | 0 | 0 | [8 empty] | 2021-05-06
MT_LO_COOLSYS1 CHILLER1 PUMP Flow Rate [gal/min] | COOLSYS1 CHILLER1 PUMP Flow Rate [gal/min] | 492.8626 | 452.2208 | [8 empty] | 2021-05-06
MT_LO_COOLSYS1 CHILLER2 PUMP Flow Rate [gal/min] | COOLSYS1 CHILLER2 PUMP Flow Rate [gal/min] | 492.8626 | 452.2208 | [8 empty] | 2021-05-06
MT_LO_COOLSYS1 PUMP SECONDARY Flow Rate [gal/min] | COOLSYS1 PUMP SECONDARY Flow Rate [gal/min] | 985.7253 | 904.4416 | [8 empty] | 2021-05-06
MT_LO_HEATSYS1 PUMP Flow Rate [gal/min] | HEATSYS1 PUMP Flow Rate [gal/min] | 1035.6839 | 906.1772 | [8 empty] | 2021-05-06
MT_LO_TOWERWATERSYS PUMP Flow Rate [gal/min] | TOWERWATERSYS PUMP Flow Rate [gal/min] | 1730.5383 | 1626.0847 | [8 empty] | 2021-05-06
MT_LO_PLANT CIRC PUMP Flow Rate [gal/min] | PLANT CIRC PUMP Flow Rate [gal/min] | 225.6785 | 224.355 | [8 empty] | 2021-05-06
MT_LO_COOLSYS1 PUMP SECONDARY Pressure setpoint reset [yes,no] | COOLSYS1 PUMP SECONDARY Pressure setpoint reset [yes,no] | pump_ride_on_curve | pump_ride_on_curve | [8 empty] | 2021-05-06
MT_LO_COOLSYS1 CHILLER1 PUMP Pump Power [hp] | COOLSYS1 CHILLER1 PUMP Pump Power [hp] | 2.6588 | 2.4154 | [8 empty] | 2021-05-06
MT_LO_COOLSYS1 CHILLER2 PUMP Pump Power [hp] | COOLSYS1 CHILLER2 PUMP Pump Power [hp] | 2.6588 | 2.4154 | [8 empty] | 2021-05-06
MT_LO_COOLSYS1 PUMP SECONDARY Pump Power [hp] | COOLSYS1 PUMP SECONDARY Pump Power [hp] | 15.9529 | 14.4925 | [8 empty] | 2021-05-06
MT_LO_HEATSYS1 PUMP Pump Power [hp] | HEATSYS1 PUMP Pump Power [hp] | 22.3869 | 19.3936 | [8 empty] | 2021-05-06
MT_LO_TOWERWATERSYS PUMP Pump Power [hp] | TOWERWATERSYS PUMP Pump Power [hp] | 30.984 | 28.8253 | [8 empty] | 2021-05-06
MT_LO_PLANT CIRC PUMP Pump Power [hp] | PLANT CIRC PUMP Pump Power [hp] | 4.8698 | 4.7933 | [8 empty] | 2021-05-06
MT_LO_Datacenter PLANT CIRC PUMP Pump Power [hp] | Datacenter PLANT CIRC PUMP Pump Power [hp] | 4.8698 | 4.7933 | [8 empty] | 2021-05-06
MT_LO_ZN_VAV_BOXes_Max_Reheat_Water_Flow_GPM | ZN_VAV_BOXes_Max_Reheat_Water_Flow_GPM | 503.0652 | 481.8593 | [8 empty] | 2021-05-06
MT_LO_COOLSYS1 PUMP SECONDARY VSD | COOLSYS1 PUMP SECONDARY VSD | No | No | [8 empty] | 2021-05-06
MT_LO_HEATSYS1 PUMP VSD | HEATSYS1 PUMP VSD | No | No | [8 empty] | 2021-05-06
MT_LO_DATACENTER BASEMENT Cooling Capacity [ton] | DATACENTER BASEMENT Cooling Capacity [ton] | 131.4004 | 130.9956 | [8 empty] | 2021-05-06
MT_LO_DATACENTER BOT Cooling Capacity [ton] | DATACENTER BOT Cooling Capacity [ton] | 2.9285 | 2.8805 | [8 empty] | 2021-05-06
MT_LO_DATACENTER MID Cooling Capacity [ton] | DATACENTER MID Cooling Capacity [ton] | 28.1238 | 27.6528 | [8 empty] | 2021-05-06
MT_LO_DATACENTER TOP Cooling Capacity [ton] | DATACENTER TOP Cooling Capacity [ton] | 2.8621 | 2.8155 | [8 empty] | 2021-05-06
id | item | Zone6B(MT-Helena-MT) ASHRAE901-state_STD2016 | Zone6B(MT-Helena-MT) ASHRAE901-state_STD2019 | [8 empty] | 2021-05-06
MT_RS_PSZ-AC:1 Cooling Capacity [ton] | PSZ-AC:1 Cooling Capacity [ton] | 9.5932 | 8.8707 | [8 empty] | 2021-05-06
MT_RS_PSZ-AC:2 Cooling Capacity [ton] | PSZ-AC:2 Cooling Capacity [ton] | 41.1869 | 39.2644 | [8 empty] | 2021-05-06
MT_RS_PSZ-AC:3 Cooling Capacity [ton] | PSZ-AC:3 Cooling Capacity [ton] | 5.7246 | 5.5083 | [8 empty] | 2021-05-06
MT_RS_PSZ-AC:4 Cooling Capacity [ton] | PSZ-AC:4 Cooling Capacity [ton] | 4.605 | 4.3711 | [8 empty] | 2021-05-06
MT_RS_PSZ-AC:1 Supply Flow Rate [cfm] | PSZ-AC:1 Supply Flow Rate [cfm] | 4068.2496 | 3729.2288 | [8 empty] | 2021-05-06
MT_RS_PSZ-AC:2 Supply Flow Rate [cfm] | PSZ-AC:2 Supply Flow Rate [cfm] | 16802.7184 | 15891.6 | [8 empty] | 2021-05-06
MT_RS_PSZ-AC:3 Supply Flow Rate [cfm] | PSZ-AC:3 Supply Flow Rate [cfm] | 2521.4672 | 2415.5232 | [8 empty] | 2021-05-06
MT_RS_PSZ-AC:4 Supply Flow Rate [cfm] | PSZ-AC:4 Supply Flow Rate [cfm] | 1970.5584 | 1843.4256 | [8 empty] | 2021-05-06
MT_RS_PSZ-AC:1 OA Rate [cfm] | PSZ-AC:1 OA Rate [cfm] | 490.669 | 490.669 | [8 empty] | 2021-05-06
MT_RS_PSZ-AC:2 OA Rate [cfm] | PSZ-AC:2 OA Rate [cfm] | 4005.1282 | 4005.1282 | [8 empty] | 2021-05-06
MT_RS_PSZ-AC:3 OA Rate [cfm] | PSZ-AC:3 OA Rate [cfm] | 377.3937 | 377.3937 | [8 empty] | 2021-05-06
MT_RS_PSZ-AC:4 OA Rate [cfm] | PSZ-AC:4 OA Rate [cfm] | 377.3937 | 377.3937 | [8 empty] | 2021-05-06
MT_RS_PSZ-AC:1 OA Damper [gravity, motorized] | PSZ-AC:1 OA Damper [gravity, motorized] | motorized | motorized | [8 empty] | 2021-05-06
MT_RS_PSZ-AC:2 OA Damper [gravity, motorized] | PSZ-AC:2 OA Damper [gravity, motorized] | motorized | motorized | [8 empty] | 2021-05-06
MT_RS_PSZ-AC:3 OA Damper [gravity, motorized] | PSZ-AC:3 OA Damper [gravity, motorized] | motorized | motorized | [8 empty] | 2021-05-06
MT_RS_PSZ-AC:4 OA Damper [gravity, motorized] | PSZ-AC:4 OA Damper [gravity, motorized] | motorized | motorized | [8 empty] | 2021-05-06
MT_RS_PSZ-AC:1 Heating Capacity [kBtu/hr] | PSZ-AC:1 Heating Capacity [kBtu/hr] | 168.9351 | 155.878 | [8 empty] | 2021-05-06
MT_RS_PSZ-AC:2 Heating Capacity [kBtu/hr] | PSZ-AC:2 Heating Capacity [kBtu/hr] | 849.2116 | 817.064 | [8 empty] | 2021-05-06
MT_RS_PSZ-AC:3 Heating Capacity [kBtu/hr] | PSZ-AC:3 Heating Capacity [kBtu/hr] | 109.4316 | 106.4186 | [8 empty] | 2021-05-06
MT_RS_PSZ-AC:4 Heating Capacity [kBtu/hr] | PSZ-AC:4 Heating Capacity [kBtu/hr] | 93.6213 | 89.9153 | [8 empty] | 2021-05-06
id | item | Zone6B(MT-Helena-MT) ASHRAE901-state_STD2016 | Zone6B(MT-Helena-MT) ASHRAE901-state_STD2019 | [8 empty] | 2021-05-06
MT_PS_VAV_POD_1 Cooling Capacity [ton] | VAV_POD_1 Cooling Capacity [ton] | 20.9117 | 19.6533 | [8 empty] | 2021-05-06
MT_PS_VAV_POD_2 Cooling Capacity [ton] | VAV_POD_2 Cooling Capacity [ton] | 20.7166 | 19.3864 | [8 empty] | 2021-05-06
MT_PS_VAV_POD_3 Cooling Capacity [ton] | VAV_POD_3 Cooling Capacity [ton] | 19.3324 | 17.9199 | [8 empty] | 2021-05-06
MT_PS_VAV_OTHER Cooling Capacity [ton] | VAV_OTHER Cooling Capacity [ton] | 22.8007 | 20.5283 | [8 empty] | 2021-05-06
MT_PS_PSZ-AC_1:6 Cooling Capacity [ton] | PSZ-AC_1:6 Cooling Capacity [ton] | 7.6684 | 7.3682 | [8 empty] | 2021-05-06
MT_PS_PSZ-AC_2:5 Cooling Capacity [ton] | PSZ-AC_2:5 Cooling Capacity [ton] | 5.0927 | 5.0346 | [8 empty] | 2021-05-06
MT_PS_PSZ-AC_2:7 Cooling Capacity [ton] | PSZ-AC_2:7 Cooling Capacity [ton] | 10.0591 | 10.0591 | [8 empty] | 2021-05-06
MT_PS_VAV_POD_1 Supply Flow Rate [cfm] | VAV_POD_1 Supply Flow Rate [cfm] | 6377.8288 | 5996.4304 | [8 empty] | 2021-05-06
MT_PS_VAV_POD_2 Supply Flow Rate [cfm] | VAV_POD_2 Supply Flow Rate [cfm] | 6314.2624 | 5911.6752 | [8 empty] | 2021-05-06
MT_PS_VAV_POD_3 Supply Flow Rate [cfm] | VAV_POD_3 Supply Flow Rate [cfm] | 5890.4864 | 5466.7104 | [8 empty] | 2021-05-06
MT_PS_VAV_OTHER Supply Flow Rate [cfm] | VAV_OTHER Supply Flow Rate [cfm] | 9068.8064 | 8411.9536 | [8 empty] | 2021-05-06
MT_PS_PSZ-AC_2:5 Supply Flow Rate [cfm] | PSZ-AC_2:5 Supply Flow Rate [cfm] | 1843.4256 | 1822.2368 | [8 empty] | 2021-05-06
MT_PS_PSZ-AC_1:6 Supply Flow Rate [cfm] | PSZ-AC_1:6 Supply Flow Rate [cfm] | 2902.8656 | 2754.544 | [8 empty] | 2021-05-06
MT_PS_PSZ-AC_2:7 Supply Flow Rate [cfm] | PSZ-AC_2:7 Supply Flow Rate [cfm] | 3157.1312 | 3157.1312 | [8 empty] | 2021-05-06
MT_PS_Supply Air Temp. Reset Flag | Supply Air Temp. Reset Flag | Yes | Yes | [8 empty] | 2021-05-06
MT_PS_VAV_POD_1 OA Rate [cfm] | VAV_POD_1 OA Rate [cfm] | 6377.5745 | 5993.803 | [8 empty] | 2021-05-06
MT_PS_VAV_POD_2 OA Rate [cfm] | VAV_POD_2 OA Rate [cfm] | 6318.0764 | 5912.4168 | [8 empty] | 2021-05-06
MT_PS_VAV_POD_3 OA Rate [cfm] | VAV_POD_3 OA Rate [cfm] | 5893.8554 | 5422.002 | [8 empty] | 2021-05-06
MT_PS_VAV_OTHER OA Rate [cfm] | VAV_OTHER OA Rate [cfm] | 3736.1787 | 2988.8921 | [8 empty] | 2021-05-06
MT_PS_PSZ-AC_2:5 OA Rate [cfm] | PSZ-AC_2:5 OA Rate [cfm] | 1152.7343 | 1152.7343 | [8 empty] | 2021-05-06
MT_PS_PSZ-AC_1:6 OA Rate [cfm] | PSZ-AC_1:6 OA Rate [cfm] | 539.9118 | 539.9118 | [8 empty] | 2021-05-06
MT_PS_PSZ-AC_2:7 OA Rate [cfm] | PSZ-AC_2:7 OA Rate [cfm] | 3153.0841 | 3153.0841 | [8 empty] | 2021-05-06
MT_PS_VAV_POD_1 OA Damper [gravity, motorized] | VAV_POD_1 OA Damper [gravity, motorized] | motorized | motorized | [8 empty] | 2021-05-06
MT_PS_VAV_POD_2 OA Damper [gravity, motorized] | VAV_POD_2 OA Damper [gravity, motorized] | motorized | motorized | [8 empty] | 2021-05-06
MT_PS_VAV_POD_3 OA Damper [gravity, motorized] | VAV_POD_3 OA Damper [gravity, motorized] | motorized | motorized | [8 empty] | 2021-05-06
MT_PS_VAV_OTHER OA Damper [gravity, motorized] | VAV_OTHER OA Damper [gravity, motorized] | motorized | motorized | [8 empty] | 2021-05-06
MT_PS_PSZ-AC_2:5 OA Damper [gravity, motorized] | PSZ-AC_2:5 OA Damper [gravity, motorized] | motorized | motorized | [8 empty] | 2021-05-06
MT_PS_PSZ-AC_1:6 OA Damper [gravity, motorized] | PSZ-AC_1:6 OA Damper [gravity, motorized] | motorized | motorized | [8 empty] | 2021-05-06
MT_PS_PSZ-AC_2:7 OA Damper [gravity, motorized] | PSZ-AC_2:7 OA Damper [gravity, motorized] | motorized | motorized | [8 empty] | 2021-05-06
MT_PS_VAV_POD_1 (economizer) | VAV_POD_1 (economizer) | DifferentialDryBulb | DifferentialDryBulb | [8 empty] | 2021-05-06
MT_PS_VAV_POD_2 (economizer) | VAV_POD_2 (economizer) | DifferentialDryBulb | DifferentialDryBulb | [8 empty] | 2021-05-06
MT_PS_VAV_POD_3 (economizer) | VAV_POD_3 (economizer) | DifferentialDryBulb | DifferentialDryBulb | [8 empty] | 2021-05-06
MT_PS_VAV_OTHER (economizer) | VAV_OTHER (economizer) | DifferentialDryBulb | DifferentialDryBulb | [8 empty] | 2021-05-06
MT_PS_PSZ-AC_2:5 (economizer) | PSZ-AC_2:5 (economizer) | DifferentialDryBulb | DifferentialDryBulb | [8 empty] | 2021-05-06
MT_PS_PSZ-AC_1:6 (economizer) | PSZ-AC_1:6 (economizer) | DifferentialDryBulb | DifferentialDryBulb | [8 empty] | 2021-05-06
MT_PS_PSZ-AC_2:7 (economizer) | PSZ-AC_2:7 (economizer) | DifferentialDryBulb | DifferentialDryBulb | [8 empty] | 2021-05-06
MT_PS_VAV_Pod_1_ERV Flag | VAV_Pod_1_ERV Flag | Yes | Yes | [8 empty] | 2021-05-06
MT_PS_VAV_Pod_2_ERV Flag | VAV_Pod_2_ERV Flag | Yes | Yes | [8 empty] | 2021-05-06
MT_PS_VAV_Pod_3_ERV Flag | VAV_Pod_3_ERV Flag | Yes | Yes | [8 empty] | 2021-05-06
MT_PS_VAV_OTHER_ERV Flag | VAV_OTHER_ERV Flag | Yes | No | [8 empty] | 2021-05-06
MT_PS_PSZ_AC_2_5_ERV Flag | PSZ_AC_2_5_ERV Flag | No | No | [8 empty] | 2021-05-06
MT_PS_PSZ_AC_2_7_ERV Flag | PSZ_AC_2_7_ERV Flag | Yes | Yes | [8 empty] | 2021-05-06
MT_PS_HEATSYS1 Capacity [MMBTU/h] | HEATSYS1 Capacity [MMBTU/h] | 1.3074 | 1.231 | [8 empty] | 2021-05-06
MT_PS_HEATSYS1 Flow Rate [gal/min] | HEATSYS1 Flow Rate [gal/min] | 134.182 | 126.3366 | [8 empty] | 2021-05-06
MT_PS_VAV_POD_1 Fan Power [hp] | VAV_POD_1 Fan Power [hp] | 9.4088 | 8.8426 | [8 empty] | 2021-05-06
MT_PS_VAV_POD_2 Fan Power [hp] | VAV_POD_2 Fan Power [hp] | 9.3211 | 8.7226 | [8 empty] | 2021-05-06
MT_PS_VAV_POD_3 Fan Power [hp] | VAV_POD_3 Fan Power [hp] | 8.6983 | 8.0627 | [8 empty] | 2021-05-06
MT_PS_VAV_OTHER Fan Power [hp] | VAV_OTHER Fan Power [hp] | 13.2745 | 12.3223 | [8 empty] | 2021-05-06
MT_PS_HEATSYS1 Pump Power [hp] | HEATSYS1 Pump Power [hp] | 2.9004 | 2.7038 | [8 empty] | 2021-05-06
MT_PS_PSZ-AC_1:6 Heating Capacity [kBtu/hr] | PSZ-AC_1:6 Heating Capacity [kBtu/hr] | 220.3622 | 211.1802 | [8 empty] | 2021-05-06
MT_PS_PSZ-AC_2:5 Heating Capacity [kBtu/hr] | PSZ-AC_2:5 Heating Capacity [kBtu/hr] | 151.9883 | 151.0591 | [8 empty] | 2021-05-06
MT_PS_PSZ-AC_2:7 Heating Capacity [kBtu/hr] | PSZ-AC_2:7 Heating Capacity [kBtu/hr] | 354.0943 | 354.0943 | [8 empty] | 2021-05-06
MT_PS_ZN_VAV_BOXes_Max_Reheat_Water_Flow_GPM | ZN_VAV_BOXes_Max_Reheat_Water_Flow_GPM | 77.7831 | 73.752 | [8 empty] | 2021-05-06
id | item | Zone6B(MT-Helena-MT) ASHRAE901-state_STD2016 | Zone6B(MT-Helena-MT) ASHRAE901-state_STD2019 | [8 empty] | 2021-05-06
MT_SH_SAC_FRONTOFFICE Cooling Capacity [ton] | SAC_FRONTOFFICE Cooling Capacity [ton] | 2.0104 | 1.8797 | [8 empty] | 2021-05-06
MT_SH_SAC_FRONTLOUNGE Cooling Capacity [ton] | SAC_FRONTLOUNGE Cooling Capacity [ton] | 5.1907 | 4.9516 | [8 empty] | 2021-05-06
MT_SH_SAC_MEETINGROOM Cooling Capacity [ton] | SAC_MEETINGROOM Cooling Capacity [ton] | 2.7401 | 2.6474 | [8 empty] | 2021-05-06
MT_SH_SAC_EXC_EMPLGE_RESTRM Cooling Capacity [ton] | SAC_EXC_EMPLGE_RESTRM Cooling Capacity [ton] | 5.6358 | 5.5466 | [8 empty] | 2021-05-06
MT_SH_SAC_FO_ADDAQ SUPPLY FAN Supply Flow Rate [cfm] | SAC_FO_ADDAQ SUPPLY FAN Supply Flow Rate [cfm] | 868.7408 | 805.1744 | [8 empty] | 2021-05-06
MT_SH_SAC_FL_ADDAQ SUPPLY FAN Supply Flow Rate [cfm] | SAC_FL_ADDAQ SUPPLY FAN Supply Flow Rate [cfm] | 2034.1248 | 1928.1808 | [8 empty] | 2021-05-06
MT_SH_SAC_MR_ADDAQ SUPPLY FAN Supply Flow Rate [cfm] | SAC_MR_ADDAQ SUPPLY FAN Supply Flow Rate [cfm] | 974.6848 | 932.3072 | [8 empty] | 2021-05-06
MT_SH_SAC_EXC_ADDAQ SUPPLY FAN Supply Flow Rate [cfm] | SAC_EXC_ADDAQ SUPPLY FAN Supply Flow Rate [cfm] | 2500.2784 | 2479.0896 | [8 empty] | 2021-05-06
MT_SH_SAC_Exc_EmpLge_RestRm OA Rate [cfm] | SAC_Exc_EmpLge_RestRm OA Rate [cfm] | 199.9928 | 199.9928 | [8 empty] | 2021-05-06
MT_SH_SAC_FrontLounge OA Rate [cfm] | SAC_FrontLounge OA Rate [cfm] | 500.0133 | 500.0133 | [8 empty] | 2021-05-06
MT_SH_SAC_FrontOffice OA Rate [cfm] | SAC_FrontOffice OA Rate [cfm] | 119.2938 | 119.2938 | [8 empty] | 2021-05-06
MT_SH_SAC_MeetingRoom OA Rate [cfm] | SAC_MeetingRoom OA Rate [cfm] | 267.7629 | 267.7629 | [8 empty] | 2021-05-06
MT_SH_SAC_FrontLounge OA Damper [gravity, motorized] | SAC_FrontLounge OA Damper [gravity, motorized] | motorized | motorized | [8 empty] | 2021-05-06
MT_SH_SAC_FrontOffice (economizer) | SAC_FrontOffice (economizer) | No | No | [8 empty] | 2021-05-06
MT_SH_SAC_FrontLounge (economizer) | SAC_FrontLounge (economizer) | DifferentialDryBulb | DifferentialDryBulb | [8 empty] | 2021-05-06
MT_SH_SAC_MeetingRoom (economizer) | SAC_MeetingRoom (economizer) | No | No | [8 empty] | 2021-05-06
MT_SH_SAC_Exc_EmpLge_RestRm (economizer) | SAC_Exc_EmpLge_RestRm (economizer) | DifferentialDryBulb | DifferentialDryBulb | [8 empty] | 2021-05-06
MT_SH_SAC_FRONTOFFICE Heating Capacity [kBtu/hr] | SAC_FRONTOFFICE Heating Capacity [kBtu/hr] | 37.3664 | 35.3778 | [8 empty] | 2021-05-06
MT_SH_SAC_FRONTLOUNGE Heating Capacity [kBtu/hr] | SAC_FRONTLOUNGE Heating Capacity [kBtu/hr] | 105.1677 | 101.6925 | [8 empty] | 2021-05-06
MT_SH_SAC_MEETINGROOM Heating Capacity [kBtu/hr] | SAC_MEETINGROOM Heating Capacity [kBtu/hr] | 52.8771 | 51.6031 | [8 empty] | 2021-05-06
MT_SH_SAC_EXC_EMPLGE_RESTRM Heating Capacity [kBtu/hr] | SAC_EXC_EMPLGE_RESTRM Heating Capacity [kBtu/hr] | 95.9278 | 95.1598 | [8 empty] | 2021-05-06
id | item | Zone6B(MT-Helena-MT) ASHRAE901-state_STD2016 | Zone6B(MT-Helena-MT) ASHRAE901-state_STD2019 | [8 empty] | 2021-05-06
MT_MA_SPLIT GSW COOLING COIL Cooling Capacity [ton] | SPLIT GSW COOLING COIL Cooling Capacity [ton] | 0.81307 | 0.77394 | [8 empty] | 2021-05-06
MT_MA_SPLIT GNW COOLING COIL Cooling Capacity [ton] | SPLIT GNW COOLING COIL Cooling Capacity [ton] | 0.7384 | 0.70383 | [8 empty] | 2021-05-06
MT_MA_SPLIT OFFICE COOLING COIL Cooling Capacity [ton] | SPLIT OFFICE COOLING COIL Cooling Capacity [ton] | 1.7913 | 1.5781 | [8 empty] | 2021-05-06
MT_MA_SPLIT GNE COOLING COIL Cooling Capacity [ton] | SPLIT GNE COOLING COIL Cooling Capacity [ton] | 0.59561 | 0.5677 | [8 empty] | 2021-05-06
MT_MA_SPLIT GN1 COOLING COIL Cooling Capacity [ton] | SPLIT GN1 COOLING COIL Cooling Capacity [ton] | 0.48882 | 0.47043 | [8 empty] | 2021-05-06
MT_MA_SPLIT GN2 COOLING COIL Cooling Capacity [ton] | SPLIT GN2 COOLING COIL Cooling Capacity [ton] | 0.48614 | 0.46796 | [8 empty] | 2021-05-06
MT_MA_SPLIT GS1 COOLING COIL Cooling Capacity [ton] | SPLIT GS1 COOLING COIL Cooling Capacity [ton] | 0.56465 | 0.54118 | [8 empty] | 2021-05-06
MT_MA_SPLIT GS2 COOLING COIL Cooling Capacity [ton] | SPLIT GS2 COOLING COIL Cooling Capacity [ton] | 0.60839 | 0.57886 | [8 empty] | 2021-05-06
MT_MA_SPLIT MSW COOLING COIL Cooling Capacity [ton] | SPLIT MSW COOLING COIL Cooling Capacity [ton] | 2.105 | 2.0103 | [8 empty] | 2021-05-06
MT_MA_SPLIT MNW COOLING COIL Cooling Capacity [ton] | SPLIT MNW COOLING COIL Cooling Capacity [ton] | 1.9462 | 1.8606 | [8 empty] | 2021-05-06
MT_MA_SPLIT MSE COOLING COIL Cooling Capacity [ton] | SPLIT MSE COOLING COIL Cooling Capacity [ton] | 1.7169 | 1.629 | [8 empty] | 2021-05-06
MT_MA_SPLIT MNE COOLING COIL Cooling Capacity [ton] | SPLIT MNE COOLING COIL Cooling Capacity [ton] | 1.5036 | 1.4203 | [8 empty] | 2021-05-06
MT_MA_SPLIT MN1 COOLING COIL Cooling Capacity [ton] | SPLIT MN1 COOLING COIL Cooling Capacity [ton] | 1.1431 | 1.1085 | [8 empty] | 2021-05-06
MT_MA_SPLIT MN2 COOLING COIL Cooling Capacity [ton] | SPLIT MN2 COOLING COIL Cooling Capacity [ton] | 1.1343 | 1.1003 | [8 empty] | 2021-05-06
MT_MA_SPLIT MS1 COOLING COIL Cooling Capacity [ton] | SPLIT MS1 COOLING COIL Cooling Capacity [ton] | 1.2929 | 1.2484 | [8 empty] | 2021-05-06
MT_MA_SPLIT MS2 COOLING COIL Cooling Capacity [ton] | SPLIT MS2 COOLING COIL Cooling Capacity [ton] | 1.2859 | 1.2419 | [8 empty] | 2021-05-06
MT_MA_SPLIT TSW COOLING COIL Cooling Capacity [ton] | SPLIT TSW COOLING COIL Cooling Capacity [ton] | 1.3346 | 1.2823 | [8 empty] | 2021-05-06
MT_MA_SPLIT TNW COOLING COIL Cooling Capacity [ton] | SPLIT TNW COOLING COIL Cooling Capacity [ton] | 1.2523 | 1.2042 | [8 empty] | 2021-05-06
MT_MA_SPLIT TSE COOLING COIL Cooling Capacity [ton] | SPLIT TSE COOLING COIL Cooling Capacity [ton] | 1.1427 | 1.0944 | [8 empty] | 2021-05-06
MT_MA_SPLIT TNE COOLING COIL Cooling Capacity [ton] | SPLIT TNE COOLING COIL Cooling Capacity [ton] | 0.96065 | 0.93011 | [8 empty] | 2021-05-06
MT_MA_SPLIT TN1 COOLING COIL Cooling Capacity [ton] | SPLIT TN1 COOLING COIL Cooling Capacity [ton] | 0.76981 | 0.75097 | [8 empty] | 2021-05-06
MT_MA_SPLIT TN2 COOLING COIL Cooling Capacity [ton] | SPLIT TN2 COOLING COIL Cooling Capacity [ton] | 0.76115 | 0.74297 | [8 empty] | 2021-05-06
MT_MA_SPLIT TS1 COOLING COIL Cooling Capacity [ton] | SPLIT TS1 COOLING COIL Cooling Capacity [ton] | 0.91726 | 0.88205 | [8 empty] | 2021-05-06
MT_MA_SPLIT TS2 COOLING COIL Cooling Capacity [ton] | SPLIT TS2 COOLING COIL Cooling Capacity [ton] | 0.92221 | 0.88649 | [8 empty] | 2021-05-06
MT_MA_Split GN1 Furnace with DX Cooling OA Rate [cfm] | Split GN1 Furnace with DX Cooling OA Rate [cfm] | 54.9913 | 54.9913 | [8 empty] | 2021-05-06
MT_MA_Split GN2 Furnace with DX Cooling OA Rate [cfm] | Split GN2 Furnace with DX Cooling OA Rate [cfm] | 54.9913 | 54.9913 | [8 empty] | 2021-05-06
MT_MA_Split GNE Furnace with DX Cooling OA Rate [cfm] | Split GNE Furnace with DX Cooling OA Rate [cfm] | 54.9913 | 54.9913 | [8 empty] | 2021-05-06
MT_MA_Split GNW Furnace with DX Cooling OA Rate [cfm] | Split GNW Furnace with DX Cooling OA Rate [cfm] | 54.9913 | 54.9913 | [8 empty] | 2021-05-06
MT_MA_Split GS1 Furnace with DX Cooling OA Rate [cfm] | Split GS1 Furnace with DX Cooling OA Rate [cfm] | 54.9913 | 54.9913 | [8 empty] | 2021-05-06
MT_MA_Split GS2 Furnace with DX Cooling OA Rate [cfm] | Split GS2 Furnace with DX Cooling OA Rate [cfm] | 54.9913 | 54.9913 | [8 empty] | 2021-05-06
MT_MA_Split GSW Furnace with DX Cooling OA Rate [cfm] | Split GSW Furnace with DX Cooling OA Rate [cfm] | 56.9945 | 56.9945 | [8 empty] | 2021-05-06
MT_MA_Split MN1 Furnace with DX Cooling OA Rate [cfm] | Split MN1 Furnace with DX Cooling OA Rate [cfm] | 109.9824 | 109.9824 | [8 empty] | 2021-05-06
MT_MA_Split MN2 Furnace with DX Cooling OA Rate [cfm] | Split MN2 Furnace with DX Cooling OA Rate [cfm] | 109.9824 | 109.9824 | [8 empty] | 2021-05-06
MT_MA_Split MNE Furnace with DX Cooling OA Rate [cfm] | Split MNE Furnace with DX Cooling OA Rate [cfm] | 109.9824 | 109.9824 | [8 empty] | 2021-05-06
MT_MA_Split MNW Furnace with DX Cooling OA Rate [cfm] | Split MNW Furnace with DX Cooling OA Rate [cfm] | 109.9824 | 109.9824 | [8 empty] | 2021-05-06
MT_MA_Split MS1 Furnace with DX Cooling OA Rate [cfm] | Split MS1 Furnace with DX Cooling OA Rate [cfm] | 109.9824 | 109.9824 | [8 empty] | 2021-05-06
MT_MA_Split MS2 Furnace with DX Cooling OA Rate [cfm] | Split MS2 Furnace with DX Cooling OA Rate [cfm] | 109.9824 | 109.9824 | [8 empty] | 2021-05-06
MT_MA_Split MSE Furnace with DX Cooling OA Rate [cfm] | Split MSE Furnace with DX Cooling OA Rate [cfm] | 109.9824 | 109.9824 | [8 empty] | 2021-05-06
MT_MA_Split MSW Furnace with DX Cooling OA Rate [cfm] | Split MSW Furnace with DX Cooling OA Rate [cfm] | 109.9824 | 109.9824 | [8 empty] | 2021-05-06
MT_MA_Split Office Furnace with DX Cooling OA Rate [cfm] | Split Office Furnace with DX Cooling OA Rate [cfm] | 80.7372 | 80.7372 | [8 empty] | 2021-05-06
MT_MA_Split TN1 Furnace with DX Cooling OA Rate [cfm] | Split TN1 Furnace with DX Cooling OA Rate [cfm] | 54.9913 | 54.9913 | [8 empty] | 2021-05-06
MT_MA_Split TN2 Furnace with DX Cooling OA Rate [cfm] | Split TN2 Furnace with DX Cooling OA Rate [cfm] | 54.9913 | 54.9913 | [8 empty] | 2021-05-06
MT_MA_Split TNE Furnace with DX Cooling OA Rate [cfm] | Split TNE Furnace with DX Cooling OA Rate [cfm] | 54.9913 | 54.9913 | [8 empty] | 2021-05-06
MT_MA_Split TNW Furnace with DX Cooling OA Rate [cfm] | Split TNW Furnace with DX Cooling OA Rate [cfm] | 54.9913 | 54.9913 | [8 empty] | 2021-05-06
MT_MA_Split TS1 Furnace with DX Cooling OA Rate [cfm] | Split TS1 Furnace with DX Cooling OA Rate [cfm] | 54.9913 | 54.9913 | [8 empty] | 2021-05-06
MT_MA_Split TS2 Furnace with DX Cooling OA Rate [cfm] | Split TS2 Furnace with DX Cooling OA Rate [cfm] | 54.9913 | 54.9913 | [8 empty] | 2021-05-06
MT_MA_Split TSE Furnace with DX Cooling OA Rate [cfm] | Split TSE Furnace with DX Cooling OA Rate [cfm] | 54.9913 | 54.9913 | [8 empty] | 2021-05-06
MT_MA_Split TSW Furnace with DX Cooling OA Rate [cfm] | Split TSW Furnace with DX Cooling OA Rate [cfm] | 54.9913 | 54.9913 | [8 empty] | 2021-05-06
MT_MA_SPLIT GSW HEATING COIL Heating Capacity [kBtu/hr] | SPLIT GSW HEATING COIL Heating Capacity [kBtu/hr] | 10.5645 | 10.6244 | [8 empty] | 2021-05-06
MT_MA_SPLIT GNW HEATING COIL Heating Capacity [kBtu/hr] | SPLIT GNW HEATING COIL Heating Capacity [kBtu/hr] | 10.4742 | 10.5341 | [8 empty] | 2021-05-06
MT_MA_SPLIT OFFICE HEATING COIL Heating Capacity [kBtu/hr] | SPLIT OFFICE HEATING COIL Heating Capacity [kBtu/hr] | 23.9455 | 24.0289 | [8 empty] | 2021-05-06
MT_MA_SPLIT GNE HEATING COIL Heating Capacity [kBtu/hr] | SPLIT GNE HEATING COIL Heating Capacity [kBtu/hr] | 10.4519 | 10.5119 | [8 empty] | 2021-05-06
MT_MA_SPLIT GN1 HEATING COIL Heating Capacity [kBtu/hr] | SPLIT GN1 HEATING COIL Heating Capacity [kBtu/hr] | 7.9837 | 8.0436 | [8 empty] | 2021-05-06
MT_MA_SPLIT GN2 HEATING COIL Heating Capacity [kBtu/hr] | SPLIT GN2 HEATING COIL Heating Capacity [kBtu/hr] | 7.983 | 8.0429 | [8 empty] | 2021-05-06
MT_MA_SPLIT GS1 HEATING COIL Heating Capacity [kBtu/hr] | SPLIT GS1 HEATING COIL Heating Capacity [kBtu/hr] | 7.93 | 7.9898 | [8 empty] | 2021-05-06
MT_MA_SPLIT GS2 HEATING COIL Heating Capacity [kBtu/hr] | SPLIT GS2 HEATING COIL Heating Capacity [kBtu/hr] | 8.4497 | 8.5105 | [8 empty] | 2021-05-06
MT_MA_SPLIT MSW HEATING COIL Heating Capacity [kBtu/hr] | SPLIT MSW HEATING COIL Heating Capacity [kBtu/hr] | 18.1497 | 18.2784 | [8 empty] | 2021-05-06
MT_MA_SPLIT MNW HEATING COIL Heating Capacity [kBtu/hr] | SPLIT MNW HEATING COIL Heating Capacity [kBtu/hr] | 18.2425 | 18.3709 | [8 empty] | 2021-05-06
MT_MA_SPLIT MSE HEATING COIL Heating Capacity [kBtu/hr] | SPLIT MSE HEATING COIL Heating Capacity [kBtu/hr] | 18.0968 | 18.2254 | [8 empty] | 2021-05-06
MT_MA_SPLIT MNE HEATING COIL Heating Capacity [kBtu/hr] | SPLIT MNE HEATING COIL Heating Capacity [kBtu/hr] | 18.1895 | 18.3179 | [8 empty] | 2021-05-06
MT_MA_SPLIT MN1 HEATING COIL Heating Capacity [kBtu/hr] | SPLIT MN1 HEATING COIL Heating Capacity [kBtu/hr] | 13.0691 | 13.1965 | [8 empty] | 2021-05-06
MT_MA_SPLIT MN2 HEATING COIL Heating Capacity [kBtu/hr] | SPLIT MN2 HEATING COIL Heating Capacity [kBtu/hr] | 13.0677 | 13.1951 | [8 empty] | 2021-05-06
MT_MA_SPLIT MS1 HEATING COIL Heating Capacity [kBtu/hr] | SPLIT MS1 HEATING COIL Heating Capacity [kBtu/hr] | 12.9873 | 13.1146 | [8 empty] | 2021-05-06
MT_MA_SPLIT MS2 HEATING COIL Heating Capacity [kBtu/hr] | SPLIT MS2 HEATING COIL Heating Capacity [kBtu/hr] | 12.9859 | 13.1132 | [8 empty] | 2021-05-06
MT_MA_SPLIT TSW HEATING COIL Heating Capacity [kBtu/hr] | SPLIT TSW HEATING COIL Heating Capacity [kBtu/hr] | 13.1171 | 13.1794 | [8 empty] | 2021-05-06
MT_MA_SPLIT TNW HEATING COIL Heating Capacity [kBtu/hr] | SPLIT TNW HEATING COIL Heating Capacity [kBtu/hr] | 13.1742 | 13.2366 | [8 empty] | 2021-05-06
MT_MA_SPLIT TSE HEATING COIL Heating Capacity [kBtu/hr] | SPLIT TSE HEATING COIL Heating Capacity [kBtu/hr] | 13.0885 | 13.1508 | [8 empty] | 2021-05-06
MT_MA_SPLIT TNE HEATING COIL Heating Capacity [kBtu/hr] | SPLIT TNE HEATING COIL Heating Capacity [kBtu/hr] | 13.1456 | 13.208 | [8 empty] | 2021-05-06
MT_MA_SPLIT TN1 HEATING COIL Heating Capacity [kBtu/hr] | SPLIT TN1 HEATING COIL Heating Capacity [kBtu/hr] | 10.5127 | 10.575 | [8 empty] | 2021-05-06
MT_MA_SPLIT TN2 HEATING COIL Heating Capacity [kBtu/hr] | SPLIT TN2 HEATING COIL Heating Capacity [kBtu/hr] | 10.5119 | 10.5742 | [8 empty] | 2021-05-06
MT_MA_SPLIT TS1 HEATING COIL Heating Capacity [kBtu/hr] | SPLIT TS1 HEATING COIL Heating Capacity [kBtu/hr] | 10.4494 | 10.5117 | [8 empty] | 2021-05-06
MT_MA_SPLIT TS2 HEATING COIL Heating Capacity [kBtu/hr] | SPLIT TS2 HEATING COIL Heating Capacity [kBtu/hr] | 10.4486 | 10.5109 | [8 empty] | 2021-05-06
MT_MA_Split_GSW ERV Flag | Split_GSW ERV Flag | Yes | Yes | [8 empty] | 2021-05-06
MT_MA_Split_GNW ERV Flag | Split_GNW ERV Flag | Yes | Yes | [8 empty] | 2021-05-06
MT_MA_Split_GNE ERV Flag | Split_GNE ERV Flag | Yes | Yes | [8 empty] | 2021-05-06
MT_MA_Split_GN1 ERV Flag | Split_GN1 ERV Flag | Yes | Yes | [8 empty] | 2021-05-06
MT_MA_Split_GN2 ERV Flag | Split_GN2 ERV Flag | Yes | Yes | [8 empty] | 2021-05-06
MT_MA_Split_GS1 ERV Flag | Split_GS1 ERV Flag | Yes | Yes | [8 empty] | 2021-05-06
MT_MA_Split_GS2 ERV Flag | Split_GS2 ERV Flag | Yes | Yes | [8 empty] | 2021-05-06
MT_MA_Split_MSW ERV Flag | Split_MSW ERV Flag | Yes | Yes | [8 empty] | 2021-05-06
MT_MA_Split_MNW ERV Flag | Split_MNW ERV Flag | Yes | Yes | [8 empty] | 2021-05-06
MT_MA_Split_MSE ERV Flag | Split_MSE ERV Flag | Yes | Yes | [8 empty] | 2021-05-06
MT_MA_Split_MNE ERV Flag | Split_MNE ERV Flag | Yes | Yes | [8 empty] | 2021-05-06
MT_MA_Split_MN1 ERV Flag | Split_MN1 ERV Flag | Yes | Yes | [8 empty] | 2021-05-06
MT_MA_Split_MN2 ERV Flag | Split_MN2 ERV Flag | Yes | Yes | [8 empty] | 2021-05-06
MT_MA_Split_MS1 ERV Flag | Split_MS1 ERV Flag | Yes | Yes | [8 empty] | 2021-05-06
MT_MA_Split_MS2 ERV Flag | Split_MS2 ERV Flag | Yes | Yes | [8 empty] | 2021-05-06
MT_MA_Split_TSW ERV Flag | Split_TSW ERV Flag | No | No | [8 empty] | 2021-05-06
MT_MA_Split_TNW ERV Flag | Split_TNW ERV Flag | No | No | [8 empty] | 2021-05-06
MT_MA_Split_TSE ERV Flag | Split_TSE ERV Flag | Yes | Yes | [8 empty] | 2021-05-06
MT_MA_Split_TNE ERV Flag | Split_TNE ERV Flag | Yes | Yes | [8 empty] | 2021-05-06
MT_MA_Split_TN1 ERV Flag | Split_TN1 ERV Flag | Yes | Yes | [8 empty] | 2021-05-06
MT_MA_Split_TN2 ERV Flag | Split_TN2 ERV Flag | Yes | Yes | [8 empty] | 2021-05-06
MT_MA_Split_TS1 ERV Flag | Split_TS1 ERV Flag | Yes | Yes | [8 empty] | 2021-05-06
MT_MA_Split_TS2 ERV Flag | Split_TS2 ERV Flag | Yes | Yes | [8 empty] | 2021-05-06
id | item | Zone3A(NC-Charlotte-NC) ASHRAE901-state_STD2016 | Zone3A(NC-Charlotte-NC) ASHRAE901-state_STD2019 | Zone4A(NC-Asheville-NC) ASHRAE901-state_STD2016 | Zone4A(NC-Asheville-NC) ASHRAE901-state_STD2019 | Zone5A(NC-Elkins-WV) ASHRAE901-state_STD2016 | Zone5A(NC-Elkins-WV) ASHRAE901-state_STD2019 |  |  |  |  | 2021-05-06
NC_SO_PSZ-AC:1 Cooling Capacity [ton] | PSZ-AC:1 Cooling Capacity [ton] | 1.9577 | 1.8624 | 1.7747 | 1.6783 | 1.7003 | 1.6084 |  |  |  |  | 2021-05-06
NC_SO_PSZ-AC:2 Cooling Capacity [ton] | PSZ-AC:2 Cooling Capacity [ton] | 1.7184 | 1.6512 | 1.4951 | 1.4338 | 1.3959 | 1.3356 |  |  |  |  | 2021-05-06
NC_SO_PSZ-AC:3 Cooling Capacity [ton] | PSZ-AC:3 Cooling Capacity [ton] | 1.1386 | 1.0983 | 1.0617 | 1.0234 | 0.9916 | 0.95384 |  |  |  |  | 2021-05-06
NC_SO_PSZ-AC:4 Cooling Capacity [ton] | PSZ-AC:4 Cooling Capacity [ton] | 1.6981 | 1.6255 | 1.4637 | 1.3928 | 1.3535 | 1.275 |  |  |  |  | 2021-05-06
NC_SO_PSZ-AC:5 Cooling Capacity [ton] | PSZ-AC:5 Cooling Capacity [ton] | 1.323 | 1.2806 | 1.2498 | 1.2107 | 1.1913 | 1.1525 |  |  |  |  | 2021-05-06
NC_SO_PSZ-AC:1 Supply Flow Rate [cfm] | PSZ-AC:1 Supply Flow Rate [cfm] | 678.0416 | 635.664 | 678.0416 | 635.664 | 678.0416 | 614.4752 |  |  |  |  | 2021-05-06
NC_SO_PSZ-AC:2 Supply Flow Rate [cfm] | PSZ-AC:2 Supply Flow Rate [cfm] | 614.4752 | 593.2864 | 593.2864 | 550.9088 | 550.9088 | 529.72 |  |  |  |  | 2021-05-06
NC_SO_PSZ-AC:3 Supply Flow Rate [cfm] | PSZ-AC:3 Supply Flow Rate [cfm] | 444.9648 | 423.776 | 466.1536 | 444.9648 | 444.9648 | 423.776 |  |  |  |  | 2021-05-06
NC_SO_PSZ-AC:4 Supply Flow Rate [cfm] | PSZ-AC:4 Supply Flow Rate [cfm] | 614.4752 | 572.0976 | 572.0976 | 529.72 | 529.72 | 487.3424 |  |  |  |  | 2021-05-06
NC_SO_PSZ-AC:5 Supply Flow Rate [cfm] | PSZ-AC:5 Supply Flow Rate [cfm] | 529.72 | 508.5312 | 550.9088 | 529.72 | 529.72 | 508.5312 |  |  |  |  | 2021-05-06
NC_SO_PSZ-AC:1 OA Rate [cfm] | PSZ-AC:1 OA Rate [cfm] | 136.9178 | 136.9178 | 136.9178 | 136.9178 | 136.9178 | 136.9178 |  |  |  |  | 2021-05-06
NC_SO_PSZ-AC:2 OA Rate [cfm] | PSZ-AC:2 OA Rate [cfm] | 103.7925 | 103.7925 | 103.7925 | 103.7925 | 103.7925 | 103.7925 |  |  |  |  | 2021-05-06
NC_SO_PSZ-AC:3 OA Rate [cfm] | PSZ-AC:3 OA Rate [cfm] | 61.5711 | 61.5711 | 61.5711 | 61.5711 | 61.5711 | 61.5711 |  |  |  |  | 2021-05-06
NC_SO_PSZ-AC:4 OA Rate [cfm] | PSZ-AC:4 OA Rate [cfm] | 103.7925 | 103.7925 | 103.7925 | 103.7925 | 103.7925 | 103.7925 |  |  |  |  | 2021-05-06
NC_SO_PSZ-AC:5 OA Rate [cfm] | PSZ-AC:5 OA Rate [cfm] | 61.5711 | 61.5711 | 61.5711 | 61.5711 | 61.5711 | 61.5711 |  |  |  |  | 2021-05-06
NC_SO_PSZ-AC:1 heating Capacity [kBtu/hr] | PSZ-AC:1 heating Capacity [kBtu/hr] | 12.0582 | 12.0582 | 12.391 | 12.391 | 14.3668 | 14.3668 |  |  |  |  | 2021-05-06
NC_SO_PSZ-AC:2 heating Capacity [kBtu/hr] | PSZ-AC:2 heating Capacity [kBtu/hr] | 16.7496 | 16.5224 | 17.6442 | 17.4577 | 19.3723 | 19.1413 |  |  |  |  | 2021-05-06
NC_SO_PSZ-AC:3 heating Capacity [kBtu/hr] | PSZ-AC:3 heating Capacity [kBtu/hr] | 10.3065 | 10.1756 | 10.8329 | 10.7298 | 11.6946 | 11.5705 |  |  |  |  | 2021-05-06
NC_SO_PSZ-AC:4 heating Capacity [kBtu/hr] | PSZ-AC:4 heating Capacity [kBtu/hr] | 16.5731 | 16.3793 | 17.5602 | 17.4002 | 19.1738 | 18.985 |  |  |  |  | 2021-05-06
NC_SO_PSZ-AC:5 heating Capacity [kBtu/hr] | PSZ-AC:5 heating Capacity [kBtu/hr] | 10.2651 | 10.1395 | 10.8789 | 10.7706 | 11.7329 | 11.6052 |  |  |  |  | 2021-05-06
id | item | Zone3A(NC-Charlotte-NC) ASHRAE901-state_STD2016 | Zone3A(NC-Charlotte-NC) ASHRAE901-state_STD2019 | Zone4A(NC-Asheville-NC) ASHRAE901-state_STD2016 | Zone4A(NC-Asheville-NC) ASHRAE901-state_STD2019 | Zone5A(NC-Elkins-WV) ASHRAE901-state_STD2016 | Zone5A(NC-Elkins-WV) ASHRAE901-state_STD2019 |  |  |  |  | 2021-05-06
NC_LO_CAV_BAS Supply Flow Rate [cfm] | CAV_BAS Supply Flow Rate [cfm] | 11717.4064 | 10827.4768 | 12543.7696 | 11611.4624 | 12331.8816 | 11399.5744 |  |  |  |  | 2021-05-06
NC_LO_VAV_BOT WITH REHEAT Supply Flow Rate [cfm] | VAV_BOT WITH REHEAT Supply Flow Rate [cfm] | 19260.6192 | 18307.1232 | 20256.4928 | 19260.6192 | 20235.304 | 19260.6192 |  |  |  |  | 2021-05-06
NC_LO_VAV_MID WITH REHEAT Supply Flow Rate [cfm] | VAV_MID WITH REHEAT Supply Flow Rate [cfm] | 178727.5283 | 169531.5891 | 186567.3843 | 177011.2355 | 186842.8387 | 177392.6339 |  |  |  |  | 2021-05-06
NC_LO_VAV_TOP WITH REHEAT Supply Flow Rate [cfm] | VAV_TOP WITH REHEAT Supply Flow Rate [cfm] | 18858.032 | 18031.6688 | 19981.0384 | 19133.4864 | 19896.2832 | 19069.92 |  |  |  |  | 2021-05-06
NC_LO_Supply Air Temp. Reset Flag | Supply Air Temp. Reset Flag | No | Yes | Yes | Yes | Yes | Yes |  |  |  |  | 2021-05-06
NC_LO_CAV_BAS OA Rate [cfm] | CAV_BAS OA Rate [cfm] | 2542.8255 | 2542.8255 | 2542.8255 | 2542.8255 | 2542.8255 | 2542.8255 |  |  |  |  | 2021-05-06
NC_LO_VAV_BOT WITH REHEAT OA Rate [cfm] | VAV_BOT WITH REHEAT OA Rate [cfm] | 5377.8022 | 4302.174 | 5377.8022 | 4302.174 | 5377.8022 | 4302.174 |  |  |  |  | 2021-05-06
NC_LO_VAV_MID WITH REHEAT OA Rate [cfm] | VAV_MID WITH REHEAT OA Rate [cfm] | 53777.9373 | 43021.7396 | 53777.9373 | 43021.7396 | 53777.9373 | 43021.7396 |  |  |  |  | 2021-05-06
NC_LO_VAV_TOP WITH REHEAT OA Rate [cfm] | VAV_TOP WITH REHEAT OA Rate [cfm] | 5377.8022 | 4302.174 | 5377.8022 | 4302.174 | 5377.8022 | 4302.174 |  |  |  |  | 2021-05-06
NC_LO_AIRLOOP DATACENTER BASEMENT OA Rate [cfm] | AIRLOOP DATACENTER BASEMENT OA Rate [cfm] | 716.9654 | 716.9654 | 716.9654 | 716.9654 | 716.9654 | 716.9654 |  |  |  |  | 2021-05-06
NC_LO_VAV_bot_WITH_REHEAT ERV Flag | VAV_bot_WITH_REHEAT ERV Flag | Yes | Yes | Yes | Yes | Yes | Yes |  |  |  |  | 2021-05-06
NC_LO_VAV_mid_WITH_REHEAT ERV Flag | VAV_mid_WITH_REHEAT ERV Flag | Yes | Yes | Yes | Yes | Yes | Yes |  |  |  |  | 2021-05-06
NC_LO_VAV_top_WITH_REHEAT ERV Flag | VAV_top_WITH_REHEAT ERV Flag | Yes | Yes | Yes | Yes | Yes | Yes |  |  |  |  | 2021-05-06
NC_LO_COOLSYS1 CHILLER1 Capacity [ton] | COOLSYS1 CHILLER1 Capacity [ton] | 409.8874 | 368.9163 | 375.1972 | 340.8933 | 363.4577 | 331.1099 |  |  |  |  | 2021-05-06
NC_LO_COOLSYS1 CHILLER2 Capacity [ton] | COOLSYS1 CHILLER2 Capacity [ton] | 409.8874 | 368.9163 | 375.1972 | 340.8933 | 363.4577 | 331.1099 |  |  |  |  | 2021-05-06
NC_LO_TOWERWATERSYS COOLTOWER 1 Capacity [ton] | TOWERWATERSYS COOLTOWER 1 Capacity [ton] | 389.0585 | 350.1631 | 356.192 | 323.6187 | 345.0898 | 314.3769 |  |  |  |  | 2021-05-06
NC_LO_TOWERWATERSYS COOLTOWER 2 Capacity [ton] | TOWERWATERSYS COOLTOWER 2 Capacity [ton] | 389.0585 | 350.1631 | 356.192 | 323.6187 | 345.0898 | 314.3769 |  |  |  |  | 2021-05-06
NC_LO_HEATSYS1 BOILER Capacity [MMBTU/h] | HEATSYS1 BOILER Capacity [MMBTU/h] | 3686.9538 | 3283.8359 | 3933.2049 | 3505.4207 | 4500.1534 | 3968.7556 |  |  |  |  | 2021-05-06
NC_LO_COOLSYS1 PUMP Flow Rate [gal/min] | COOLSYS1 PUMP Flow Rate [gal/min] | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 2021-05-06
NC_LO_COOLSYS1 CHILLER1 PUMP Flow Rate [gal/min] | COOLSYS1 CHILLER1 PUMP Flow Rate [gal/min] | 645.9308 | 578.5415 | 590.843 | 533.915 | 572.2743 | 521.2712 |  |  |  |  | 2021-05-06
NC_LO_COOLSYS1 CHILLER2 PUMP Flow Rate [gal/min] | COOLSYS1 CHILLER2 PUMP Flow Rate [gal/min] | 645.9308 | 578.5415 | 590.843 | 533.915 | 572.2743 | 521.2712 |  |  |  |  | 2021-05-06
NC_LO_COOLSYS1 PUMP SECONDARY Flow Rate [gal/min] | COOLSYS1 PUMP SECONDARY Flow Rate [gal/min] | 1291.8616 | 1157.0831 | 1181.686 | 1067.8299 | 1144.5502 | 1042.5423 |  |  |  |  | 2021-05-06
NC_LO_HEATSYS1 PUMP Flow Rate [gal/min] | HEATSYS1 PUMP Flow Rate [gal/min] | 756.7959 | 674.0508 | 807.3425 | 719.5333 | 923.7156 | 814.64 |  |  |  |  | 2021-05-06
NC_LO_TOWERWATERSYS PUMP Flow Rate [gal/min] | TOWERWATERSYS PUMP Flow Rate [gal/min] | 2261.3656 | 2035.34 | 2070.0522 | 1880.7993 | 2005.2244 | 1826.7497 |  |  |  |  | 2021-05-06
NC_LO_PLANT CIRC PUMP Flow Rate [gal/min] | PLANT CIRC PUMP Flow Rate [gal/min] | 208.6188 | 207.7882 | 212.8286 | 211.9791 | 212.0789 | 211.2277 |  |  |  |  | 2021-05-06
NC_LO_COOLSYS1 PUMP SECONDARY Pressure setpoint reset [yes,no] | COOLSYS1 PUMP SECONDARY Pressure setpoint reset [yes,no] | pump_ride_on_curve | pump_ride_on_curve | pump_ride_on_curve | pump_ride_on_curve | pump_ride_on_curve | pump_ride_on_curve |  |  |  |  | 2021-05-06
NC_LO_COOLSYS1 CHILLER1 PUMP Pump Power [hp] | COOLSYS1 CHILLER1 PUMP Pump Power [hp] | 3.4846 | 3.0901 | 3.1874 | 2.8518 | 3.0872 | 2.7842 |  |  |  |  | 2021-05-06
NC_LO_COOLSYS1 CHILLER2 PUMP Pump Power [hp] | COOLSYS1 CHILLER2 PUMP Pump Power [hp] | 3.4846 | 3.0901 | 3.1874 | 2.8518 | 3.0872 | 2.7842 |  |  |  |  | 2021-05-06
NC_LO_COOLSYS1 PUMP SECONDARY Pump Power [hp] | COOLSYS1 PUMP SECONDARY Pump Power [hp] | 20.9074 | 18.5408 | 19.1243 | 17.1106 | 18.5233 | 16.7054 |  |  |  |  | 2021-05-06
NC_LO_HEATSYS1 PUMP Pump Power [hp] | HEATSYS1 PUMP Pump Power [hp] | 16.3586 | 14.4257 | 17.4512 | 15.3991 | 19.9667 | 17.4346 |  |  |  |  | 2021-05-06
NC_LO_TOWERWATERSYS PUMP Pump Power [hp] | TOWERWATERSYS PUMP Pump Power [hp] | 40.4878 | 36.08 | 37.0612 | 33.3393 | 35.9016 | 32.3825 |  |  |  |  | 2021-05-06
NC_LO_PLANT CIRC PUMP Pump Power [hp] | PLANT CIRC PUMP Pump Power [hp] | 4.5017 | 4.4394 | 4.5925 | 4.5289 | 4.5764 | 4.5129 |  |  |  |  | 2021-05-06
NC_LO_Datacenter PLANT CIRC PUMP Pump Power [hp] | Datacenter PLANT CIRC PUMP Pump Power [hp] | 4.5017 | 4.4394 | 4.5925 | 4.5289 | 4.5764 | 4.5129 |  |  |  |  | 2021-05-06
NC_LO_ZN_VAV_BOXes_Max_Reheat_Water_Flow_GPM | ZN_VAV_BOXes_Max_Reheat_Water_Flow_GPM | 421.798 | 403.7185 | 438.5876 | 421.6711 | 458.5624 | 440.301 |  |  |  |  | 2021-05-06
NC_LO_COOLSYS1 PUMP SECONDARY VSD | COOLSYS1 PUMP SECONDARY VSD | No | No | No | No | No | No |  |  |  |  | 2021-05-06
NC_LO_HEATSYS1 PUMP VSD | HEATSYS1 PUMP VSD | No | No | No | No | No | No |  |  |  |  | 2021-05-06
NC_LO_DATACENTER BASEMENT Cooling Capacity [ton] | DATACENTER BASEMENT Cooling Capacity [ton] | 122.556 | 122.2465 | 124.8246 | 124.4542 | 124.1601 | 123.791 |  |  |  |  | 2021-05-06
NC_LO_DATACENTER BOT Cooling Capacity [ton] | DATACENTER BOT Cooling Capacity [ton] | 2.6374 | 2.6099 | 2.6947 | 2.6709 | 2.7015 | 2.6776 |  |  |  |  | 2021-05-06
NC_LO_DATACENTER MID Cooling Capacity [ton] | DATACENTER MID Cooling Capacity [ton] | 25.0959 | 24.8438 | 25.7592 | 25.5507 | 25.8589 | 25.6489 |  |  |  |  | 2021-05-06
NC_LO_DATACENTER TOP Cooling Capacity [ton] | DATACENTER TOP Cooling Capacity [ton] | 2.5281 | 2.5085 | 2.6232 | 2.603 | 2.6321 | 2.6117 |  |  |  |  | 2021-05-06
id | item | Zone3A(NC-Charlotte-NC) ASHRAE901-state_STD2016 | Zone3A(NC-Charlotte-NC) ASHRAE901-state_STD2019 | Zone4A(NC-Asheville-NC) ASHRAE901-state_STD2016 | Zone4A(NC-Asheville-NC) ASHRAE901-state_STD2019 | Zone5A(NC-Elkins-WV) ASHRAE901-state_STD2016 | Zone5A(NC-Elkins-WV) ASHRAE901-state_STD2019 |  |  |  |  | 2021-05-06
NC_RS_PSZ-AC:1 Cooling Capacity [ton] | PSZ-AC:1 Cooling Capacity [ton] | 10.5643 | 10.241 | 9.8372 | 9.4351 | 9.3456 | 8.872 |  |  |  |  | 2021-05-06
NC_RS_PSZ-AC:2 Cooling Capacity [ton] | PSZ-AC:2 Cooling Capacity [ton] | 49.8737 | 47.9688 | 45.9519 | 44.0359 | 44.0328 | 42.0973 |  |  |  |  | 2021-05-06
NC_RS_PSZ-AC:3 Cooling Capacity [ton] | PSZ-AC:3 Cooling Capacity [ton] | 6.4742 | 6.3166 | 5.956 | 5.7941 | 5.6682 | 5.5067 |  |  |  |  | 2021-05-06
NC_RS_PSZ-AC:4 Cooling Capacity [ton] | PSZ-AC:4 Cooling Capacity [ton] | 5.254 | 5.1007 | 4.7384 | 4.5561 | 4.4422 | 4.2758 |  |  |  |  | 2021-05-06
NC_RS_PSZ-AC:1 Supply Flow Rate [cfm] | PSZ-AC:1 Supply Flow Rate [cfm] | 4089.4384 | 3835.1728 | 4025.872 | 3729.2288 | 3835.1728 | 3496.152 |  |  |  |  | 2021-05-06
NC_RS_PSZ-AC:2 Supply Flow Rate [cfm] | PSZ-AC:2 Supply Flow Rate [cfm] | 15277.1248 | 14408.384 | 15870.4112 | 14938.104 | 15594.9568 | 14641.4608 |  |  |  |  | 2021-05-06
NC_RS_PSZ-AC:3 Supply Flow Rate [cfm] | PSZ-AC:3 Supply Flow Rate [cfm] | 2288.3904 | 2203.6352 | 2309.5792 | 2224.824 | 2224.824 | 2161.2576 |  |  |  |  | 2021-05-06
NC_RS_PSZ-AC:4 Supply Flow Rate [cfm] | PSZ-AC:4 Supply Flow Rate [cfm] | 1737.4816 | 1673.9152 | 1716.2928 | 1631.5376 | 1652.7264 | 1567.9712 |  |  |  |  | 2021-05-06
NC_RS_PSZ-AC:1 OA Rate [cfm] | PSZ-AC:1 OA Rate [cfm] | 490.669 | 490.669 | 490.669 | 490.669 | 490.669 | 490.669 |  |  |  |  | 2021-05-06
NC_RS_PSZ-AC:2 OA Rate [cfm] | PSZ-AC:2 OA Rate [cfm] | 4005.1282 | 4005.1282 | 4005.1282 | 4005.1282 | 4005.1282 | 4005.1282 |  |  |  |  | 2021-05-06
NC_RS_PSZ-AC:3 OA Rate [cfm] | PSZ-AC:3 OA Rate [cfm] | 377.3937 | 377.3937 | 377.3937 | 377.3937 | 377.3937 | 377.3937 |  |  |  |  | 2021-05-06
NC_RS_PSZ-AC:4 OA Rate [cfm] | PSZ-AC:4 OA Rate [cfm] | 377.3937 | 377.3937 | 377.3937 | 377.3937 | 377.3937 | 377.3937 |  |  |  |  | 2021-05-06
NC_RS_PSZ-AC:1 OA Damper [gravity, motorized] | PSZ-AC:1 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | motorized | motorized |  |  |  |  | 2021-05-06
NC_RS_PSZ-AC:2 OA Damper [gravity, motorized] | PSZ-AC:2 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | motorized | motorized |  |  |  |  | 2021-05-06
NC_RS_PSZ-AC:3 OA Damper [gravity, motorized] | PSZ-AC:3 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | motorized | motorized |  |  |  |  | 2021-05-06
NC_RS_PSZ-AC:4 OA Damper [gravity, motorized] | PSZ-AC:4 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | motorized | motorized |  |  |  |  | 2021-05-06
NC_RS_PSZ-AC:1 Heating Capacity [kBtu/hr] | PSZ-AC:1 Heating Capacity [kBtu/hr] | 172.1251 | 162.0856 | 164.4909 | 152.7416 | 164.8422 | 151.7326 |  |  |  |  | 2021-05-06
NC_RS_PSZ-AC:2 Heating Capacity [kBtu/hr] | PSZ-AC:2 Heating Capacity [kBtu/hr] | 747.3574 | 711.4475 | 757.2311 | 720.2567 | 807.2915 | 769.1389 |  |  |  |  | 2021-05-06
NC_RS_PSZ-AC:3 Heating Capacity [kBtu/hr] | PSZ-AC:3 Heating Capacity [kBtu/hr] | 102.3476 | 99.7097 | 100.2808 | 97.5911 | 103.7532 | 101.0419 |  |  |  |  | 2021-05-06
NC_RS_PSZ-AC:4 Heating Capacity [kBtu/hr] | PSZ-AC:4 Heating Capacity [kBtu/hr] | 82.5197 | 79.7358 | 79.8507 | 76.5974 | 82.6649 | 79.3067 |  |  |  |  | 2021-05-06
id | item | Zone3A(NC-Charlotte-NC) ASHRAE901-state_STD2016 | Zone3A(NC-Charlotte-NC) ASHRAE901-state_STD2019 | Zone4A(NC-Asheville-NC) ASHRAE901-state_STD2016 | Zone4A(NC-Asheville-NC) ASHRAE901-state_STD2019 | Zone5A(NC-Elkins-WV) ASHRAE901-state_STD2016 | Zone5A(NC-Elkins-WV) ASHRAE901-state_STD2019 |  |  |  |  | 2021-05-06
NC_PS_VAV_POD_1 Cooling Capacity [ton] | VAV_POD_1 Cooling Capacity [ton] | 18.6516 | 18.1284 | 19.3034 | 18.5739 | 19.0068 | 18.4003 |  |  |  |  | 2021-05-06
NC_PS_VAV_POD_2 Cooling Capacity [ton] | VAV_POD_2 Cooling Capacity [ton] | 18.5872 | 18.092 | 19.0425 | 18.4809 | 18.7328 | 18.3446 |  |  |  |  | 2021-05-06
NC_PS_VAV_POD_3 Cooling Capacity [ton] | VAV_POD_3 Cooling Capacity [ton] | 17.0068 | 16.1279 | 17.6597 | 16.7385 | 17.2954 | 16.4449 |  |  |  |  | 2021-05-06
NC_PS_VAV_OTHER Cooling Capacity [ton] | VAV_OTHER Cooling Capacity [ton] | 26.0394 | 24.4504 | 27.636 | 25.1109 | 26.4605 | 23.7189 |  |  |  |  | 2021-05-06
NC_PS_PSZ-AC_1:6 Cooling Capacity [ton] | PSZ-AC_1:6 Cooling Capacity [ton] | 8.4195 | 8.1248 | 8.1066 | 7.8436 | 7.861 | 7.6005 |  |  |  |  | 2021-05-06
NC_PS_PSZ-AC_2:5 Cooling Capacity [ton] | PSZ-AC_2:5 Cooling Capacity [ton] | 5.1956 | 5.0252 | 5.7139 | 5.7016 | 5.6024 | 5.5826 |  |  |  |  | 2021-05-06
NC_PS_PSZ-AC_2:7 Cooling Capacity [ton] | PSZ-AC_2:7 Cooling Capacity [ton] | 10.5074 | 10.5074 | 10.5074 | 10.5074 | 10.5074 | 10.5074 |  |  |  |  | 2021-05-06
NC_PS_VAV_POD_1 Supply Flow Rate [cfm] | VAV_POD_1 Supply Flow Rate [cfm] | 5593.8432 | 5445.5216 | 5784.5424 | 5572.6544 | 5699.7872 | 5530.2768 |  |  |  |  | 2021-05-06
NC_PS_VAV_POD_2 Supply Flow Rate [cfm] | VAV_POD_2 Supply Flow Rate [cfm] | 5572.6544 | 5424.3328 | 5720.976 | 5551.4656 | 5615.032 | 5509.088 |  |  |  |  | 2021-05-06
NC_PS_VAV_POD_3 Supply Flow Rate [cfm] | VAV_POD_3 Supply Flow Rate [cfm] | 5106.5008 | 4831.0464 | 5297.2 | 5021.7456 | 5191.256 | 4936.9904 |  |  |  |  | 2021-05-06
NC_PS_VAV_OTHER Supply Flow Rate [cfm] | VAV_OTHER Supply Flow Rate [cfm] | 7818.6672 | 7331.3248 | 8284.8208 | 7797.4784 | 8094.1216 | 7585.5904 |  |  |  |  | 2021-05-06
NC_PS_PSZ-AC_2:5 Supply Flow Rate [cfm] | PSZ-AC_2:5 Supply Flow Rate [cfm] | 1567.9712 | 1504.4048 | 1716.2928 | 1716.2928 | 1673.9152 | 1673.9152 |  |  |  |  | 2021-05-06
NC_PS_PSZ-AC_1:6 Supply Flow Rate [cfm] | PSZ-AC_1:6 Supply Flow Rate [cfm] | 2542.656 | 2436.712 | 2712.1664 | 2585.0336 | 2690.9776 | 2563.8448 |  |  |  |  | 2021-05-06
NC_PS_PSZ-AC_2:7 Supply Flow Rate [cfm] | PSZ-AC_2:7 Supply Flow Rate [cfm] | 3157.1312 | 3157.1312 | 3157.1312 | 3157.1312 | 3157.1312 | 3157.1312 |  |  |  |  | 2021-05-06
NC_PS_Supply Air Temp. Reset Flag | Supply Air Temp. Reset Flag | No | No | Yes | Yes | Yes | Yes |  |  |  |  | 2021-05-06
NC_PS_VAV_POD_1 OA Rate [cfm] | VAV_POD_1 OA Rate [cfm] | 5595.4536 | 5440.0337 | 5792.6365 | 5573.7138 | 5702.9867 | 5521.6318 |  |  |  |  | 2021-05-06
NC_PS_VAV_POD_2 OA Rate [cfm] | VAV_POD_2 OA Rate [cfm] | 5576.2353 | 5429.1003 | 5713.5599 | 5545.8082 | 5621.3886 | 5504.935 |  |  |  |  | 2021-05-06
NC_PS_VAV_POD_3 OA Rate [cfm] | VAV_POD_3 OA Rate [cfm] | 5103.4708 | 4839.7126 | 5299.3825 | 5022.9534 | 5189.7728 | 4934.8503 |  |  |  |  | 2021-05-06
NC_PS_VAV_OTHER OA Rate [cfm] | VAV_OTHER OA Rate [cfm] | 3736.1787 | 2988.8921 | 3736.1787 | 2988.8921 | 3736.1787 | 2988.8921 |  |  |  |  | 2021-05-06
NC_PS_PSZ-AC_2:5 OA Rate [cfm] | PSZ-AC_2:5 OA Rate [cfm] | 1152.7343 | 1152.7343 | 1152.7343 | 1152.7343 | 1152.7343 | 1152.7343 |  |  |  |  | 2021-05-06
NC_PS_PSZ-AC_1:6 OA Rate [cfm] | PSZ-AC_1:6 OA Rate [cfm] | 539.9118 | 539.9118 | 539.9118 | 539.9118 | 539.9118 | 539.9118 |  |  |  |  | 2021-05-06
NC_PS_PSZ-AC_2:7 OA Rate [cfm] | PSZ-AC_2:7 OA Rate [cfm] | 3153.0841 | 3153.0841 | 3153.0841 | 3153.0841 | 3153.0841 | 3153.0841 |  |  |  |  | 2021-05-06
NC_PS_VAV_POD_1 OA Damper [gravity, motorized] | VAV_POD_1 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | motorized | motorized |  |  |  |  | 2021-05-06
NC_PS_VAV_POD_2 OA Damper [gravity, motorized] | VAV_POD_2 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | motorized | motorized |  |  |  |  | 2021-05-06
NC_PS_VAV_POD_3 OA Damper [gravity, motorized] | VAV_POD_3 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | motorized | motorized |  |  |  |  | 2021-05-06
NC_PS_VAV_OTHER OA Damper [gravity, motorized] | VAV_OTHER OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | motorized | motorized |  |  |  |  | 2021-05-06
NC_PS_PSZ-AC_2:5 OA Damper [gravity, motorized] | PSZ-AC_2:5 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | motorized | motorized |  |  |  |  | 2021-05-06
NC_PS_PSZ-AC_1:6 OA Damper [gravity, motorized] | PSZ-AC_1:6 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | motorized | motorized |  |  |  |  | 2021-05-06
NC_PS_PSZ-AC_2:7 OA Damper [gravity, motorized] | PSZ-AC_2:7 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | motorized | motorized |  |  |  |  | 2021-05-06
NC_PS_VAV_POD_1 (economizer) | VAV_POD_1 (economizer) | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialDryBulb | DifferentialDryBulb |  |  |  |  | 2021-05-06
NC_PS_VAV_POD_2 (economizer) | VAV_POD_2 (economizer) | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialDryBulb | DifferentialDryBulb |  |  |  |  | 2021-05-06
NC_PS_VAV_POD_3 (economizer) | VAV_POD_3 (economizer) | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialDryBulb | DifferentialDryBulb |  |  |  |  | 2021-05-06
NC_PS_VAV_OTHER (economizer) | VAV_OTHER (economizer) | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialDryBulb | DifferentialDryBulb |  |  |  |  | 2021-05-06
NC_PS_PSZ-AC_2:5 (economizer) | PSZ-AC_2:5 (economizer) | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialDryBulb | DifferentialDryBulb |  |  |  |  | 2021-05-06
NC_PS_PSZ-AC_1:6 (economizer) | PSZ-AC_1:6 (economizer) | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialDryBulb | DifferentialDryBulb |  |  |  |  | 2021-05-06
NC_PS_PSZ-AC_2:7 (economizer) | PSZ-AC_2:7 (economizer) | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialDryBulb | DifferentialDryBulb |  |  |  |  | 2021-05-06
NC_PS_VAV_Pod_1_ERV Flag | VAV_Pod_1_ERV Flag | Yes | Yes | Yes | Yes | Yes | Yes |  |  |  |  | 2021-05-06
NC_PS_VAV_Pod_2_ERV Flag | VAV_Pod_2_ERV Flag | Yes | Yes | Yes | Yes | Yes | Yes |  |  |  |  | 2021-05-06
NC_PS_VAV_Pod_3_ERV Flag | VAV_Pod_3_ERV Flag | Yes | Yes | Yes | Yes | Yes | Yes |  |  |  |  | 2021-05-06
NC_PS_VAV_OTHER_ERV Flag | VAV_OTHER_ERV Flag | Yes | Yes | Yes | Yes | Yes | Yes |  |  |  |  | 2021-05-06
NC_PS_PSZ_AC_2_5_ERV Flag | PSZ_AC_2_5_ERV Flag | Yes | Yes | No | No | No | No |  |  |  |  | 2021-05-06
NC_PS_PSZ_AC_2_7_ERV Flag | PSZ_AC_2_7_ERV Flag | Yes | Yes | Yes | Yes | Yes | Yes |  |  |  |  | 2021-05-06
NC_PS_HEATSYS1 Capacity [MMBTU/h] | HEATSYS1 Capacity [MMBTU/h] | 0.89312 | 0.85059 | 0.95208 | 0.90907 | 1.0873 | 1.0454 |  |  |  |  | 2021-05-06
NC_PS_HEATSYS1 Flow Rate [gal/min] | HEATSYS1 Flow Rate [gal/min] | 91.6621 | 87.2977 | 97.7134 | 93.2993 | 111.5864 | 107.2919 |  |  |  |  | 2021-05-06
NC_PS_VAV_POD_1 Fan Power [hp] | VAV_POD_1 Fan Power [hp] | 8.2573 | 8.0257 | 8.5459 | 8.2229 | 8.4146 | 8.1461 |  |  |  |  | 2021-05-06
NC_PS_VAV_POD_2 Fan Power [hp] | VAV_POD_2 Fan Power [hp] | 8.2288 | 8.0095 | 8.4304 | 8.1817 | 8.2933 | 8.1214 |  |  |  |  | 2021-05-06
NC_PS_VAV_POD_3 Fan Power [hp] | VAV_POD_3 Fan Power [hp] | 7.5291 | 7.14 | 7.8182 | 7.4104 | 7.6569 | 7.2804 |  |  |  |  | 2021-05-06
NC_PS_VAV_OTHER Fan Power [hp] | VAV_OTHER Fan Power [hp] | 11.4406 | 10.7425 | 12.1421 | 11.4075 | 11.8369 | 11.1054 |  |  |  |  | 2021-05-06
NC_PS_HEATSYS1 Pump Power [hp] | HEATSYS1 Pump Power [hp] | 1.9813 | 1.8683 | 2.1121 | 1.9968 | 2.412 | 2.2962 |  |  |  |  | 2021-05-06
NC_PS_PSZ-AC_1:6 Heating Capacity [kBtu/hr] | PSZ-AC_1:6 Heating Capacity [kBtu/hr] | 200.3773 | 191.6635 | 205.569 | 197.0629 | 212.4876 | 203.9726 |  |  |  |  | 2021-05-06
NC_PS_PSZ-AC_2:5 Heating Capacity [kBtu/hr] | PSZ-AC_2:5 Heating Capacity [kBtu/hr] | 116.1756 | 114.3316 | 123.5703 | 123.4436 | 139.1847 | 138.9798 |  |  |  |  | 2021-05-06
NC_PS_PSZ-AC_2:7 Heating Capacity [kBtu/hr] | PSZ-AC_2:7 Heating Capacity [kBtu/hr] | 277.6887 | 277.6887 | 285.353 | 285.353 | 330.8534 | 330.8534 |  |  |  |  | 2021-05-06
NC_PS_ZN_VAV_BOXes_Max_Reheat_Water_Flow_GPM | ZN_VAV_BOXes_Max_Reheat_Water_Flow_GPM | 64.6298 | 61.4393 | 65.6702 | 62.7441 | 69.5114 | 67.0183 |  |  |  |  | 2021-05-06
id | item | Zone3A(NC-Charlotte-NC) ASHRAE901-state_STD2016 | Zone3A(NC-Charlotte-NC) ASHRAE901-state_STD2019 | Zone4A(NC-Asheville-NC) ASHRAE901-state_STD2016 | Zone4A(NC-Asheville-NC) ASHRAE901-state_STD2019 | Zone5A(NC-Elkins-WV) ASHRAE901-state_STD2016 | Zone5A(NC-Elkins-WV) ASHRAE901-state_STD2019 |  |  |  |  | 2021-05-06
NC_SH_SAC_FRONTOFFICE Cooling Capacity [ton] | SAC_FRONTOFFICE Cooling Capacity [ton] | 2.4175 | 2.273 | 2.194 | 2.0736 | 2.076 | 1.9507 |  |  |  |  | 2021-05-06
NC_SH_SAC_FRONTLOUNGE Cooling Capacity [ton] | SAC_FRONTLOUNGE Cooling Capacity [ton] | 6.2109 | 5.8961 | 6.07 | 5.8276 | 5.7536 | 5.5151 |  |  |  |  | 2021-05-06
NC_SH_SAC_MEETINGROOM Cooling Capacity [ton] | SAC_MEETINGROOM Cooling Capacity [ton] | 2.9553 | 2.8677 | 3.0386 | 2.95 | 2.9724 | 2.8791 |  |  |  |  | 2021-05-06
NC_SH_SAC_EXC_EMPLGE_RESTRM Cooling Capacity [ton] | SAC_EXC_EMPLGE_RESTRM Cooling Capacity [ton] | 6.0743 | 6.0331 | 5.8317 | 5.7899 | 5.6643 | 5.6237 |  |  |  |  | 2021-05-06
NC_SH_SAC_FO_ADDAQ SUPPLY FAN Supply Flow Rate [cfm] | SAC_FO_ADDAQ SUPPLY FAN Supply Flow Rate [cfm] | 805.1744 | 741.608 | 805.1744 | 741.608 | 762.7968 | 720.4192 |  |  |  |  | 2021-05-06
NC_SH_SAC_FL_ADDAQ SUPPLY FAN Supply Flow Rate [cfm] | SAC_FL_ADDAQ SUPPLY FAN Supply Flow Rate [cfm] | 1864.6144 | 1779.8592 | 1928.1808 | 1822.2368 | 1864.6144 | 1758.6704 |  |  |  |  | 2021-05-06
NC_SH_SAC_MR_ADDAQ SUPPLY FAN Supply Flow Rate [cfm] | SAC_MR_ADDAQ SUPPLY FAN Supply Flow Rate [cfm] | 889.9296 | 868.7408 | 911.1184 | 889.9296 | 889.9296 | 868.7408 |  |  |  |  | 2021-05-06
NC_SH_SAC_EXC_ADDAQ SUPPLY FAN Supply Flow Rate [cfm] | SAC_EXC_ADDAQ SUPPLY FAN Supply Flow Rate [cfm] | 2203.6352 | 2182.4464 | 2330.768 | 2309.5792 | 2309.5792 | 2288.3904 |  |  |  |  | 2021-05-06
NC_SH_SAC_Exc_EmpLge_RestRm OA Rate [cfm] | SAC_Exc_EmpLge_RestRm OA Rate [cfm] | 199.9928 | 199.9928 | 199.9928 | 199.9928 | 199.9928 | 199.9928 |  |  |  |  | 2021-05-06
NC_SH_SAC_FrontLounge OA Rate [cfm] | SAC_FrontLounge OA Rate [cfm] | 500.0133 | 500.0133 | 500.0133 | 500.0133 | 500.0133 | 500.0133 |  |  |  |  | 2021-05-06
NC_SH_SAC_FrontOffice OA Rate [cfm] | SAC_FrontOffice OA Rate [cfm] | 119.2938 | 119.2938 | 119.2938 | 119.2938 | 119.2938 | 119.2938 |  |  |  |  | 2021-05-06
NC_SH_SAC_MeetingRoom OA Rate [cfm] | SAC_MeetingRoom OA Rate [cfm] | 267.7629 | 267.7629 | 267.7629 | 267.7629 | 267.7629 | 267.7629 |  |  |  |  | 2021-05-06
NC_SH_SAC_FrontLounge OA Damper [gravity, motorized] | SAC_FrontLounge OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | motorized | motorized |  |  |  |  | 2021-05-06
NC_SH_SAC_FrontOffice (economizer) | SAC_FrontOffice (economizer) | No | No | No | No | No | No |  |  |  |  | 2021-05-06
NC_SH_SAC_FrontLounge (economizer) | SAC_FrontLounge (economizer) | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialDryBulb | DifferentialDryBulb |  |  |  |  | 2021-05-06
NC_SH_SAC_MeetingRoom (economizer) | SAC_MeetingRoom (economizer) | No | No | No | No | No | No |  |  |  |  | 2021-05-06
NC_SH_SAC_Exc_EmpLge_RestRm (economizer) | SAC_Exc_EmpLge_RestRm (economizer) | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialDryBulb | DifferentialDryBulb |  |  |  |  | 2021-05-06
NC_SH_SAC_FRONTOFFICE Heating Capacity [kBtu/hr] | SAC_FRONTOFFICE Heating Capacity [kBtu/hr] | 35.1585 | 32.932 | 33.9567 | 32.1993 | 34.8152 | 33.0316 |  |  |  |  | 2021-05-06
NC_SH_SAC_FRONTLOUNGE Heating Capacity [kBtu/hr] | SAC_FRONTLOUNGE Heating Capacity [kBtu/hr] | 92.9296 | 89.5425 | 93.5626 | 90.1819 | 99.1768 | 95.8175 |  |  |  |  | 2021-05-06
NC_SH_SAC_MEETINGROOM Heating Capacity [kBtu/hr] | SAC_MEETINGROOM Heating Capacity [kBtu/hr] | 45.7762 | 44.8334 | 46.1646 | 45.2585 | 49.5008 | 48.5407 |  |  |  |  | 2021-05-06
NC_SH_SAC_EXC_EMPLGE_RESTRM Heating Capacity [kBtu/hr] | SAC_EXC_EMPLGE_RESTRM Heating Capacity [kBtu/hr] | 89.699 | 89.0499 | 90.6907 | 90.0314 | 93.2931 | 92.6291 |  |  |  |  | 2021-05-06
id | item | Zone3A(NC-Charlotte-NC) ASHRAE901-state_STD2016 | Zone3A(NC-Charlotte-NC) ASHRAE901-state_STD2019 | Zone4A(NC-Asheville-NC) ASHRAE901-state_STD2016 | Zone4A(NC-Asheville-NC) ASHRAE901-state_STD2019 | Zone5A(NC-Elkins-WV) ASHRAE901-state_STD2016 | Zone5A(NC-Elkins-WV) ASHRAE901-state_STD2019 |  |  |  |  | 2021-05-06
NC_MA_SPLIT GSW COOLING COIL Cooling Capacity [ton] | SPLIT GSW COOLING COIL Cooling Capacity [ton] | 0.86024 | 0.8501 | 0.78256 | 0.76895 | 0.71127 | 0.69747 |  |  |  |  | 2021-05-06
NC_MA_SPLIT GNW COOLING COIL Cooling Capacity [ton] | SPLIT GNW COOLING COIL Cooling Capacity [ton] | 0.83632 | 0.82617 | 0.75594 | 0.74244 | 0.6776 | 0.66405 |  |  |  |  | 2021-05-06
NC_MA_SPLIT OFFICE COOLING COIL Cooling Capacity [ton] | SPLIT OFFICE COOLING COIL Cooling Capacity [ton] | 1.6499 | 1.5691 | 1.6406 | 1.4381 | 1.5419 | 1.3715 |  |  |  |  | 2021-05-06
NC_MA_SPLIT GNE COOLING COIL Cooling Capacity [ton] | SPLIT GNE COOLING COIL Cooling Capacity [ton] | 0.74233 | 0.73358 | 0.65574 | 0.64369 | 0.57612 | 0.56424 |  |  |  |  | 2021-05-06
NC_MA_SPLIT GN1 COOLING COIL Cooling Capacity [ton] | SPLIT GN1 COOLING COIL Cooling Capacity [ton] | 0.64494 | 0.63637 | 0.55695 | 0.54786 | 0.4927 | 0.48328 |  |  |  |  | 2021-05-06
NC_MA_SPLIT GN2 COOLING COIL Cooling Capacity [ton] | SPLIT GN2 COOLING COIL Cooling Capacity [ton] | 0.6434 | 0.63485 | 0.55491 | 0.54587 | 0.49059 | 0.48123 |  |  |  |  | 2021-05-06
NC_MA_SPLIT GS1 COOLING COIL Cooling Capacity [ton] | SPLIT GS1 COOLING COIL Cooling Capacity [ton] | 0.66896 | 0.6603 | 0.5918 | 0.58169 | 0.53668 | 0.52657 |  |  |  |  | 2021-05-06
NC_MA_SPLIT GS2 COOLING COIL Cooling Capacity [ton] | SPLIT GS2 COOLING COIL Cooling Capacity [ton] | 0.7014 | 0.68879 | 0.62207 | 0.60672 | 0.5711 | 0.55614 |  |  |  |  | 2021-05-06
NC_MA_SPLIT MSW COOLING COIL Cooling Capacity [ton] | SPLIT MSW COOLING COIL Cooling Capacity [ton] | 1.9302 | 1.9098 | 1.8621 | 1.8315 | 1.7797 | 1.749 |  |  |  |  | 2021-05-06
NC_MA_SPLIT MNW COOLING COIL Cooling Capacity [ton] | SPLIT MNW COOLING COIL Cooling Capacity [ton] | 1.8937 | 1.8736 | 1.8172 | 1.787 | 1.7199 | 1.6898 |  |  |  |  | 2021-05-06
NC_MA_SPLIT MSE COOLING COIL Cooling Capacity [ton] | SPLIT MSE COOLING COIL Cooling Capacity [ton] | 1.7366 | 1.7162 | 1.5379 | 1.5143 | 1.4902 | 1.4157 |  |  |  |  | 2021-05-06
NC_MA_SPLIT MNE COOLING COIL Cooling Capacity [ton] | SPLIT MNE COOLING COIL Cooling Capacity [ton] | 1.6381 | 1.6198 | 1.4719 | 1.4703 | 1.3646 | 1.3356 |  |  |  |  | 2021-05-06
NC_MA_SPLIT MN1 COOLING COIL Cooling Capacity [ton] | SPLIT MN1 COOLING COIL Cooling Capacity [ton] | 1.3672 | 1.3507 | 1.23 | 1.2124 | 1.1387 | 1.1207 |  |  |  |  | 2021-05-06
NC_MA_SPLIT MN2 COOLING COIL Cooling Capacity [ton] | SPLIT MN2 COOLING COIL Cooling Capacity [ton] | 1.3633 | 1.3468 | 1.2245 | 1.2071 | 1.1328 | 1.115 |  |  |  |  | 2021-05-06
NC_MA_SPLIT MS1 COOLING COIL Cooling Capacity [ton] | SPLIT MS1 COOLING COIL Cooling Capacity [ton] | 1.417 | 1.4001 | 1.293 | 1.2739 | 1.218 | 1.1992 |  |  |  |  | 2021-05-06
NC_MA_SPLIT MS2 COOLING COIL Cooling Capacity [ton] | SPLIT MS2 COOLING COIL Cooling Capacity [ton] | 1.4133 | 1.3965 | 1.2882 | 1.2692 | 1.2127 | 1.194 |  |  |  |  | 2021-05-06
NC_MA_SPLIT TSW COOLING COIL Cooling Capacity [ton] | SPLIT TSW COOLING COIL Cooling Capacity [ton] | 1.185 | 1.1747 | 1.1671 | 1.1503 | 1.1192 | 1.1025 |  |  |  |  | 2021-05-06
NC_MA_SPLIT TNW COOLING COIL Cooling Capacity [ton] | SPLIT TNW COOLING COIL Cooling Capacity [ton] | 1.1551 | 1.1451 | 1.1356 | 1.1191 | 1.0782 | 1.0619 |  |  |  |  | 2021-05-06
NC_MA_SPLIT TSE COOLING COIL Cooling Capacity [ton] | SPLIT TSE COOLING COIL Cooling Capacity [ton] | 1.0944 | 1.0842 | 1.0285 | 1.0152 | 0.97559 | 0.96212 |  |  |  |  | 2021-05-06
NC_MA_SPLIT TNE COOLING COIL Cooling Capacity [ton] | SPLIT TNE COOLING COIL Cooling Capacity [ton] | 1.0371 | 1.0273 | 0.97468 | 0.96199 | 0.90959 | 0.89703 |  |  |  |  | 2021-05-06
NC_MA_SPLIT TN1 COOLING COIL Cooling Capacity [ton] | SPLIT TN1 COOLING COIL Cooling Capacity [ton] | 0.85126 | 0.84307 | 0.79241 | 0.78272 | 0.73428 | 0.72498 |  |  |  |  | 2021-05-06
NC_MA_SPLIT TN2 COOLING COIL Cooling Capacity [ton] | SPLIT TN2 COOLING COIL Cooling Capacity [ton] | 0.8468 | 0.83863 | 0.78648 | 0.77694 | 0.7278 | 0.71867 |  |  |  |  | 2021-05-06
NC_MA_SPLIT TS1 COOLING COIL Cooling Capacity [ton] | SPLIT TS1 COOLING COIL Cooling Capacity [ton] | 0.91597 | 0.9069 | 0.85747 | 0.84674 | 0.81639 | 0.80566 |  |  |  |  | 2021-05-06
NC_MA_SPLIT TS2 COOLING COIL Cooling Capacity [ton] | SPLIT TS2 COOLING COIL Cooling Capacity [ton] | 0.91768 | 0.90862 | 0.85948 | 0.84881 | 0.81655 | 0.80587 |  |  |  |  | 2021-05-06
NC_MA_Split GN1 Furnace with DX Cooling OA Rate [cfm] | Split GN1 Furnace with DX Cooling OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 |  |  |  |  | 2021-05-06
NC_MA_Split GN2 Furnace with DX Cooling OA Rate [cfm] | Split GN2 Furnace with DX Cooling OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 |  |  |  |  | 2021-05-06
NC_MA_Split GNE Furnace with DX Cooling OA Rate [cfm] | Split GNE Furnace with DX Cooling OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 |  |  |  |  | 2021-05-06
NC_MA_Split GNW Furnace with DX Cooling OA Rate [cfm] | Split GNW Furnace with DX Cooling OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 |  |  |  |  | 2021-05-06
NC_MA_Split GS1 Furnace with DX Cooling OA Rate [cfm] | Split GS1 Furnace with DX Cooling OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 |  |  |  |  | 2021-05-06
NC_MA_Split GS2 Furnace with DX Cooling OA Rate [cfm] | Split GS2 Furnace with DX Cooling OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 |  |  |  |  | 2021-05-06
NC_MA_Split GSW Furnace with DX Cooling OA Rate [cfm] | Split GSW Furnace with DX Cooling OA Rate [cfm] | 56.9945 | 56.9945 | 56.9945 | 56.9945 | 56.9945 | 56.9945 |  |  |  |  | 2021-05-06
NC_MA_Split MN1 Furnace with DX Cooling OA Rate [cfm] | Split MN1 Furnace with DX Cooling OA Rate [cfm] | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824 |  |  |  |  | 2021-05-06
NC_MA_Split MN2 Furnace with DX Cooling OA Rate [cfm] | Split MN2 Furnace with DX Cooling OA Rate [cfm] | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824 |  |  |  |  | 2021-05-06
NC_MA_Split MNE Furnace with DX Cooling OA Rate [cfm] | Split MNE Furnace with DX Cooling OA Rate [cfm] | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824 |  |  |  |  | 2021-05-06
NC_MA_Split MNW Furnace with DX Cooling OA Rate [cfm] | Split MNW Furnace with DX Cooling OA Rate [cfm] | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824 |  |  |  |  | 2021-05-06
NC_MA_Split MS1 Furnace with DX Cooling OA Rate [cfm] | Split MS1 Furnace with DX Cooling OA Rate [cfm] | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824 |  |  |  |  | 2021-05-06
NC_MA_Split MS2 Furnace with DX Cooling OA Rate [cfm] | Split MS2 Furnace with DX Cooling OA Rate [cfm] | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824 |  |  |  |  | 2021-05-06
NC_MA_Split MSE Furnace with DX Cooling OA Rate [cfm] | Split MSE Furnace with DX Cooling OA Rate [cfm] | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824 |  |  |  |  | 2021-05-06
NC_MA_Split MSW Furnace with DX Cooling OA Rate [cfm] | Split MSW Furnace with DX Cooling OA Rate [cfm] | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824 |  |  |  |  | 2021-05-06
NC_MA_Split Office Furnace with DX Cooling OA Rate [cfm] | Split Office Furnace with DX Cooling OA Rate [cfm] | 80.7372 | 80.7372 | 80.7372 | 80.7372 | 80.7372 | 80.7372 |  |  |  |  | 2021-05-06
NC_MA_Split TN1 Furnace with DX Cooling OA Rate [cfm] | Split TN1 Furnace with DX Cooling OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 |  |  |  |  | 2021-05-06
NC_MA_Split TN2 Furnace with DX Cooling OA Rate [cfm] | Split TN2 Furnace with DX Cooling OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 |  |  |  |  | 2021-05-06
NC_MA_Split TNE Furnace with DX Cooling OA Rate [cfm] | Split TNE Furnace with DX Cooling OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 |  |  |  |  | 2021-05-06
NC_MA_Split TNW Furnace with DX Cooling OA Rate [cfm] | Split TNW Furnace with DX Cooling OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 |  |  |  |  | 2021-05-06
NC_MA_Split TS1 Furnace with DX Cooling OA Rate [cfm] | Split TS1 Furnace with DX Cooling OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 |  |  |  |  | 2021-05-06
NC_MA_Split TS2 Furnace with DX Cooling OA Rate [cfm] | Split TS2 Furnace with DX Cooling OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 |  |  |  |  | 2021-05-06
NC_MA_Split TSE Furnace with DX Cooling OA Rate [cfm] | Split TSE Furnace with DX Cooling OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 |  |  |  |  | 2021-05-06
NC_MA_Split TSW Furnace with DX Cooling OA Rate [cfm] | Split TSW Furnace with DX Cooling OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 |  |  |  |  | 2021-05-06
NC_MA_SPLIT GSW HEATING COIL Heating Capacity [kBtu/hr] | SPLIT GSW HEATING COIL Heating Capacity [kBtu/hr] | 6.9081 | 6.8248 | 8.3288 | 8.3877 | 9.3371 | 9.3963 |  |  |  |  | 2021-05-06
NC_MA_SPLIT GNW HEATING COIL Heating Capacity [kBtu/hr] | SPLIT GNW HEATING COIL Heating Capacity [kBtu/hr] | 6.8525 | 6.7657 | 8.2755 | 8.3345 | 9.2312 | 9.2905 |  |  |  |  | 2021-05-06
NC_MA_SPLIT OFFICE HEATING COIL Heating Capacity [kBtu/hr] | SPLIT OFFICE HEATING COIL Heating Capacity [kBtu/hr] | 17.9466 | 17.7922 | 20.4058 | 20.504 | 22.1512 | 22.2428 |  |  |  |  | 2021-05-06
NC_MA_SPLIT GNE HEATING COIL Heating Capacity [kBtu/hr] | SPLIT GNE HEATING COIL Heating Capacity [kBtu/hr] | 6.8713 | 6.7819 | 8.2571 | 8.3162 | 9.215 | 9.2743 |  |  |  |  | 2021-05-06
NC_MA_SPLIT GN1 HEATING COIL Heating Capacity [kBtu/hr] | SPLIT GN1 HEATING COIL Heating Capacity [kBtu/hr] | 4.9003 | 4.8603 | 5.8716 | 5.9307 | 6.9126 | 6.972 |  |  |  |  | 2021-05-06
NC_MA_SPLIT GN2 HEATING COIL Heating Capacity [kBtu/hr] | SPLIT GN2 HEATING COIL Heating Capacity [kBtu/hr] | 4.9009 | 4.8608 | 5.871 | 5.9301 | 6.9121 | 6.9715 |  |  |  |  | 2021-05-06
NC_MA_SPLIT GS1 HEATING COIL Heating Capacity [kBtu/hr] | SPLIT GS1 HEATING COIL Heating Capacity [kBtu/hr] | 4.864 | 4.843 | 5.8275 | 5.8865 | 6.8936 | 6.9528 |  |  |  |  | 2021-05-06
NC_MA_SPLIT GS2 HEATING COIL Heating Capacity [kBtu/hr] | SPLIT GS2 HEATING COIL Heating Capacity [kBtu/hr] | 5.3337 | 5.2932 | 6.342 | 6.4014 | 7.3976 | 7.4583 |  |  |  |  | 2021-05-06
NC_MA_SPLIT MSW HEATING COIL Heating Capacity [kBtu/hr] | SPLIT MSW HEATING COIL Heating Capacity [kBtu/hr] | 12.1751 | 12.0147 | 15.2693 | 15.3985 | 15.1642 | 15.2946 |  |  |  |  | 2021-05-06
NC_MA_SPLIT MNW HEATING COIL Heating Capacity [kBtu/hr] | SPLIT MNW HEATING COIL Heating Capacity [kBtu/hr] | 12.2521 | 12.0822 | 15.3448 | 15.4739 | 15.1758 | 15.3057 |  |  |  |  | 2021-05-06
NC_MA_SPLIT MSE HEATING COIL Heating Capacity [kBtu/hr] | SPLIT MSE HEATING COIL Heating Capacity [kBtu/hr] | 12.2204 | 12.054 | 15.226 | 15.3552 | 15.1253 | 15.2557 |  |  |  |  | 2021-05-06
NC_MA_SPLIT MNE HEATING COIL Heating Capacity [kBtu/hr] | SPLIT MNE HEATING COIL Heating Capacity [kBtu/hr] | 12.2975 | 12.1215 | 15.3014 | 15.4306 | 15.1368 | 15.2667 |  |  |  |  | 2021-05-06
NC_MA_SPLIT MN1 HEATING COIL Heating Capacity [kBtu/hr] | SPLIT MN1 HEATING COIL Heating Capacity [kBtu/hr] | 9.686 | 9.686 | 10.2258 | 10.3501 | 11.5404 | 11.5404 |  |  |  |  | 2021-05-06
NC_MA_SPLIT MN2 HEATING COIL Heating Capacity [kBtu/hr] | SPLIT MN2 HEATING COIL Heating Capacity [kBtu/hr] | 9.686 | 9.686 | 10.2246 | 10.3489 | 11.5404 | 11.5404 |  |  |  |  | 2021-05-06
NC_MA_SPLIT MS1 HEATING COIL Heating Capacity [kBtu/hr] | SPLIT MS1 HEATING COIL Heating Capacity [kBtu/hr] | 9.686 | 9.686 | 10.1583 | 10.2825 | 11.5404 | 11.5404 |  |  |  |  | 2021-05-06
NC_MA_SPLIT MS2 HEATING COIL Heating Capacity [kBtu/hr] | SPLIT MS2 HEATING COIL Heating Capacity [kBtu/hr] | 9.686 | 9.686 | 10.1571 | 10.2813 | 11.5404 | 11.5404 |  |  |  |  | 2021-05-06
NC_MA_SPLIT TSW HEATING COIL Heating Capacity [kBtu/hr] | SPLIT TSW HEATING COIL Heating Capacity [kBtu/hr] | 9.2237 | 9.1452 | 10.8993 | 10.9608 | 10.9654 | 11.0273 |  |  |  |  | 2021-05-06
NC_MA_SPLIT TNW HEATING COIL Heating Capacity [kBtu/hr] | SPLIT TNW HEATING COIL Heating Capacity [kBtu/hr] | 9.2699 | 9.1868 | 10.9445 | 11.006 | 10.9778 | 11.04 |  |  |  |  | 2021-05-06
NC_MA_SPLIT TSE HEATING COIL Heating Capacity [kBtu/hr] | SPLIT TSE HEATING COIL Heating Capacity [kBtu/hr] | 9.2477 | 9.1659 | 10.8767 | 10.9382 | 10.9444 | 11.0063 |  |  |  |  | 2021-05-06
NC_MA_SPLIT TNE HEATING COIL Heating Capacity [kBtu/hr] | SPLIT TNE HEATING COIL Heating Capacity [kBtu/hr] | 9.2939 | 9.2075 | 10.9218 | 10.9834 | 10.9568 | 11.0189 |  |  |  |  | 2021-05-06
NC_MA_SPLIT TN1 HEATING COIL Heating Capacity [kBtu/hr] | SPLIT TN1 HEATING COIL Heating Capacity [kBtu/hr] | 7.148 | 7.1137 | 8.1397 | 8.2011 | 8.7254 | 8.7874 |  |  |  |  | 2021-05-06
NC_MA_SPLIT TN2 HEATING COIL Heating Capacity [kBtu/hr] | SPLIT TN2 HEATING COIL Heating Capacity [kBtu/hr] | 7.1486 | 7.1143 | 8.139 | 8.2004 | 8.7247 | 8.7868 |  |  |  |  | 2021-05-06
NC_MA_SPLIT TS1 HEATING COIL Heating Capacity [kBtu/hr] | SPLIT TS1 HEATING COIL Heating Capacity [kBtu/hr] | 7.0947 | 7.0648 | 8.0872 | 8.1485 | 8.7066 | 8.7685 |  |  |  |  | 2021-05-06
NC_MA_SPLIT TS2 HEATING COIL Heating Capacity [kBtu/hr] | SPLIT TS2 HEATING COIL Heating Capacity [kBtu/hr] | 7.0954 | 7.0654 | 8.0866 | 8.1479 | 8.706 | 8.7679 |  |  |  |  | 2021-05-06
NC_MA_Split_GSW ERV Flag | Split_GSW ERV Flag | No | Yes | Yes | Yes | Yes | Yes |  |  |  |  | 2021-05-06
NC_MA_Split_GNW ERV Flag | Split_GNW ERV Flag | No | Yes | Yes | Yes | Yes | Yes |  |  |  |  | 2021-05-06
NC_MA_Split_GNE ERV Flag | Split_GNE ERV Flag | No | Yes | Yes | Yes | Yes | Yes |  |  |  |  | 2021-05-06
NC_MA_Split_GN1 ERV Flag | Split_GN1 ERV Flag | No | Yes | Yes | Yes | Yes | Yes |  |  |  |  | 2021-05-06
NC_MA_Split_GN2 ERV Flag | Split_GN2 ERV Flag | No | Yes | Yes | Yes | Yes | Yes |  |  |  |  | 2021-05-06
NC_MA_Split_GS1 ERV Flag | Split_GS1 ERV Flag | No | Yes | Yes | Yes | Yes | Yes |  |  |  |  | 2021-05-06
NC_MA_Split_GS2 ERV Flag | Split_GS2 ERV Flag | No | Yes | Yes | Yes | Yes | Yes |  |  |  |  | 2021-05-06
NC_MA_Split_MSW ERV Flag | Split_MSW ERV Flag | No | Yes | Yes | Yes | Yes | Yes |  |  |  |  | 2021-05-06
NC_MA_Split_MNW ERV Flag | Split_MNW ERV Flag | No | Yes | Yes | Yes | Yes | Yes |  |  |  |  | 2021-05-06
NC_MA_Split_MSE ERV Flag | Split_MSE ERV Flag | No | Yes | Yes | Yes | Yes | Yes |  |  |  |  | 2021-05-06
NC_MA_Split_MNE ERV Flag | Split_MNE ERV Flag | No | Yes | Yes | Yes | Yes | Yes |  |  |  |  | 2021-05-06
NC_MA_Split_MN1 ERV Flag | Split_MN1 ERV Flag | No | Yes | Yes | Yes | Yes | Yes |  |  |  |  | 2021-05-06
NC_MA_Split_MN2 ERV Flag | Split_MN2 ERV Flag | No | Yes | Yes | Yes | Yes | Yes |  |  |  |  | 2021-05-06
NC_MA_Split_MS1 ERV Flag | Split_MS1 ERV Flag | No | Yes | Yes | Yes | Yes | Yes |  |  |  |  | 2021-05-06
NC_MA_Split_MS2 ERV Flag | Split_MS2 ERV Flag | No | Yes | Yes | Yes | Yes | Yes |  |  |  |  | 2021-05-06
NC_MA_Split_TSW ERV Flag | Split_TSW ERV Flag | No | Yes | Yes | Yes | Yes | Yes |  |  |  |  | 2021-05-06
NC_MA_Split_TNW ERV Flag | Split_TNW ERV Flag | No | Yes | Yes | Yes | Yes | Yes |  |  |  |  | 2021-05-06
NC_MA_Split_TSE ERV Flag | Split_TSE ERV Flag | No | Yes | Yes | Yes | Yes | Yes |  |  |  |  | 2021-05-06
NC_MA_Split_TNE ERV Flag | Split_TNE ERV Flag | No | Yes | Yes | Yes | Yes | Yes |  |  |  |  | 2021-05-06
NC_MA_Split_TN1 ERV Flag | Split_TN1 ERV Flag | No | Yes | Yes | Yes | Yes | Yes |  |  |  |  | 2021-05-06
NC_MA_Split_TN2 ERV Flag | Split_TN2 ERV Flag | No | Yes | Yes | Yes | Yes | Yes |  |  |  |  | 2021-05-06
NC_MA_Split_TS1 ERV Flag | Split_TS1 ERV Flag | No | Yes | Yes | Yes | Yes | Yes |  |  |  |  | 2021-05-06
NC_MA_Split_TS2 ERV Flag | Split_TS2 ERV Flag | No | Yes | Yes | Yes | Yes | Yes |  |  |  |  | 2021-05-06
id | item | Zone6A(ND-Bismarck-ND) ASHRAE901-state_STD2016 | Zone6A(ND-Bismarck-ND) ASHRAE901-state_STD2019 | Zone7(ND-Minot-ND) ASHRAE901-state_STD2016 | Zone7(ND-Minot-ND) ASHRAE901-state_STD2019 | [6 empty] | 2021-05-06
ND_SO_PSZ-AC:1 Cooling Capacity [ton] | PSZ-AC:1 Cooling Capacity [ton] | 1.7261 | 1.6271 | 1.6612 | 1.5513 | [6 empty] | 2021-05-06
ND_SO_PSZ-AC:2 Cooling Capacity [ton] | PSZ-AC:2 Cooling Capacity [ton] | 1.5615 | 1.4778 | 1.6439 | 1.4852 | [6 empty] | 2021-05-06
ND_SO_PSZ-AC:3 Cooling Capacity [ton] | PSZ-AC:3 Cooling Capacity [ton] | 1.0941 | 1.0206 | 1.2065 | 1.084 | [6 empty] | 2021-05-06
ND_SO_PSZ-AC:4 Cooling Capacity [ton] | PSZ-AC:4 Cooling Capacity [ton] | 1.4241 | 1.3404 | 1.3756 | 1.2724 | [6 empty] | 2021-05-06
ND_SO_PSZ-AC:5 Cooling Capacity [ton] | PSZ-AC:5 Cooling Capacity [ton] | 1.3636 | 1.2841 | 1.4284 | 1.2905 | [6 empty] | 2021-05-06
ND_SO_PSZ-AC:1 Supply Flow Rate [cfm] | PSZ-AC:1 Supply Flow Rate [cfm] | 678.0416 | 635.664 | 678.0416 | 614.4752 | [6 empty] | 2021-05-06
ND_SO_PSZ-AC:2 Supply Flow Rate [cfm] | PSZ-AC:2 Supply Flow Rate [cfm] | 635.664 | 593.2864 | 678.0416 | 593.2864 | [6 empty] | 2021-05-06
ND_SO_PSZ-AC:3 Supply Flow Rate [cfm] | PSZ-AC:3 Supply Flow Rate [cfm] | 487.3424 | 466.1536 | 550.9088 | 487.3424 | [6 empty] | 2021-05-06
ND_SO_PSZ-AC:4 Supply Flow Rate [cfm] | PSZ-AC:4 Supply Flow Rate [cfm] | 572.0976 | 529.72 | 572.0976 | 508.5312 | [6 empty] | 2021-05-06
ND_SO_PSZ-AC:5 Supply Flow Rate [cfm] | PSZ-AC:5 Supply Flow Rate [cfm] | 614.4752 | 572.0976 | 635.664 | 572.0976 | [6 empty] | 2021-05-06
ND_SO_PSZ-AC:1 OA Rate [cfm] | PSZ-AC:1 OA Rate [cfm] | 136.9178 | 136.9178 | 136.9178 | 136.9178 | [6 empty] | 2021-05-06
ND_SO_PSZ-AC:2 OA Rate [cfm] | PSZ-AC:2 OA Rate [cfm] | 103.7925 | 103.7925 | 103.7925 | 103.7925 | [6 empty] | 2021-05-06
ND_SO_PSZ-AC:3 OA Rate [cfm] | PSZ-AC:3 OA Rate [cfm] | 61.5711 | 61.5711 | 61.5711 | 61.5711 | [6 empty] | 2021-05-06
ND_SO_PSZ-AC:4 OA Rate [cfm] | PSZ-AC:4 OA Rate [cfm] | 103.7925 | 103.7925 | 103.7925 | 103.7925 | [6 empty] | 2021-05-06
ND_SO_PSZ-AC:5 OA Rate [cfm] | PSZ-AC:5 OA Rate [cfm] | 61.5711 | 61.5711 | 61.5711 | 61.5711 | [6 empty] | 2021-05-06
ND_SO_PSZ-AC:1 heating Capacity [kBtu/hr] | PSZ-AC:1 heating Capacity [kBtu/hr] | 17.8738 | 17.8384 | 17.2474 | 17.2474 | [6 empty] | 2021-05-06
ND_SO_PSZ-AC:2 heating Capacity [kBtu/hr] | PSZ-AC:2 heating Capacity [kBtu/hr] | 26.0743 | 25.7749 | 26.3315 | 25.6764 | [6 empty] | 2021-05-06
ND_SO_PSZ-AC:3 heating Capacity [kBtu/hr] | PSZ-AC:3 heating Capacity [kBtu/hr] | 15.9012 | 15.7358 | 16.0701 | 15.7239 | [6 empty] | 2021-05-06
ND_SO_PSZ-AC:4 heating Capacity [kBtu/hr] | PSZ-AC:4 heating Capacity [kBtu/hr] | 26.0155 | 25.76 | 26.2054 | 25.67 | [6 empty] | 2021-05-06
ND_SO_PSZ-AC:5 heating Capacity [kBtu/hr] | PSZ-AC:5 heating Capacity [kBtu/hr] | 15.9817 | 15.809 | 16.1493 | 15.7869 | [6 empty] | 2021-05-06
id | item | Zone6A(ND-Bismarck-ND) ASHRAE901-state_STD2016 | Zone6A(ND-Bismarck-ND) ASHRAE901-state_STD2019 | Zone7(ND-Minot-ND) ASHRAE901-state_STD2016 | Zone7(ND-Minot-ND) ASHRAE901-state_STD2019 | [6 empty] | 2021-05-06
ND_LO_CAV_BAS Supply Flow Rate [cfm] | CAV_BAS Supply Flow Rate [cfm] | 12331.8816 | 11420.7632 | 12501.392 | 11569.0848 | [6 empty] | 2021-05-06
ND_LO_VAV_BOT WITH REHEAT Supply Flow Rate [cfm] | VAV_BOT WITH REHEAT Supply Flow Rate [cfm] | 21146.4224 | 20002.2272 | 21358.3104 | 19981.0384 | [6 empty] | 2021-05-06
ND_LO_VAV_MID WITH REHEAT Supply Flow Rate [cfm] | VAV_MID WITH REHEAT Supply Flow Rate [cfm] | 197903.3923 | 186715.7059 | 198856.8883 | 185232.4899 | [6 empty] | 2021-05-06
ND_LO_VAV_TOP WITH REHEAT Supply Flow Rate [cfm] | VAV_TOP WITH REHEAT Supply Flow Rate [cfm] | 20955.7232 | 19875.0944 | 21040.4784 | 19451.3184 | [6 empty] | 2021-05-06
ND_LO_Supply Air Temp. Reset Flag | Supply Air Temp. Reset Flag | Yes | Yes | Yes | Yes | [6 empty] | 2021-05-06
ND_LO_CAV_BAS OA Rate [cfm] | CAV_BAS OA Rate [cfm] | 2542.8255 | 2542.8255 | 2542.8255 | 2542.8255 | [6 empty] | 2021-05-06
ND_LO_VAV_BOT WITH REHEAT OA Rate [cfm] | VAV_BOT WITH REHEAT OA Rate [cfm] | 5377.8022 | 4302.174 | 5377.8022 | 4302.174 | [6 empty] | 2021-05-06
ND_LO_VAV_MID WITH REHEAT OA Rate [cfm] | VAV_MID WITH REHEAT OA Rate [cfm] | 53777.9373 | 43021.7396 | 53777.9373 | 43021.7396 | [6 empty] | 2021-05-06
ND_LO_VAV_TOP WITH REHEAT OA Rate [cfm] | VAV_TOP WITH REHEAT OA Rate [cfm] | 5377.8022 | 4302.174 | 5377.8022 | 4302.174 | [6 empty] | 2021-05-06
ND_LO_AIRLOOP DATACENTER BASEMENT OA Rate [cfm] | AIRLOOP DATACENTER BASEMENT OA Rate [cfm] | 716.9654 | 716.9654 | 716.9654 | 716.9654 | [6 empty] | 2021-05-06
ND_LO_VAV_bot_WITH_REHEAT ERV Flag | VAV_bot_WITH_REHEAT ERV Flag | Yes | Yes | Yes | Yes | [6 empty] | 2021-05-06
ND_LO_VAV_mid_WITH_REHEAT ERV Flag | VAV_mid_WITH_REHEAT ERV Flag | Yes | Yes | Yes | Yes | [6 empty] | 2021-05-06
ND_LO_VAV_top_WITH_REHEAT ERV Flag | VAV_top_WITH_REHEAT ERV Flag | Yes | Yes | Yes | Yes | [6 empty] | 2021-05-06
ND_LO_COOLSYS1 CHILLER1 Capacity [ton] | COOLSYS1 CHILLER1 Capacity [ton] | 368.5955 | 335.4102 | 362.7104 | 330.0608 | [6 empty] | 2021-05-06
ND_LO_COOLSYS1 CHILLER2 Capacity [ton] | COOLSYS1 CHILLER2 Capacity [ton] | 368.5955 | 335.4102 | 362.7104 | 330.0608 | [6 empty] | 2021-05-06
ND_LO_TOWERWATERSYS COOLTOWER 1 Capacity [ton] | TOWERWATERSYS COOLTOWER 1 Capacity [ton] | 349.905 | 318.4093 | 344.3696 | 313.3689 | [6 empty] | 2021-05-06
ND_LO_TOWERWATERSYS COOLTOWER 2 Capacity [ton] | TOWERWATERSYS COOLTOWER 2 Capacity [ton] | 349.905 | 318.4093 | 344.3696 | 313.3689 | [6 empty] | 2021-05-06
ND_LO_HEATSYS1 BOILER Capacity [MMBTU/h] | HEATSYS1 BOILER Capacity [MMBTU/h] | 5615.7035 | 4965.3645 | 5619.8041 | 4895.2652 | [6 empty] | 2021-05-06
ND_LO_COOLSYS1 PUMP Flow Rate [gal/min] | COOLSYS1 PUMP Flow Rate [gal/min] | 0 | 0 | 0 | 0 | [6 empty] | 2021-05-06
ND_LO_COOLSYS1 CHILLER1 PUMP Flow Rate [gal/min] | COOLSYS1 CHILLER1 PUMP Flow Rate [gal/min] | 580.2581 | 527.9774 | 570.9191 | 519.5165 | [6 empty] | 2021-05-06
ND_LO_COOLSYS1 CHILLER2 PUMP Flow Rate [gal/min] | COOLSYS1 CHILLER2 PUMP Flow Rate [gal/min] | 580.2581 | 527.9774 | 570.9191 | 519.5165 | [6 empty] | 2021-05-06
ND_LO_COOLSYS1 PUMP SECONDARY Flow Rate [gal/min] | COOLSYS1 PUMP SECONDARY Flow Rate [gal/min] | 1160.5163 | 1055.9549 | 1141.8367 | 1039.0346 | [6 empty] | 2021-05-06
ND_LO_HEATSYS1 PUMP Flow Rate [gal/min] | HEATSYS1 PUMP Flow Rate [gal/min] | 1152.6973 | 1019.2059 | 1153.539 | 1004.817 | [6 empty] | 2021-05-06
ND_LO_TOWERWATERSYS PUMP Flow Rate [gal/min] | TOWERWATERSYS PUMP Flow Rate [gal/min] | 2033.5965 | 1850.5252 | 2001.1033 | 1820.8851 | [6 empty] | 2021-05-06
ND_LO_PLANT CIRC PUMP Flow Rate [gal/min] | PLANT CIRC PUMP Flow Rate [gal/min] | 212.4863 | 211.2499 | 213.618 | 211.7857 | [6 empty] | 2021-05-06
ND_LO_COOLSYS1 PUMP SECONDARY Pressure setpoint reset [yes,no] | COOLSYS1 PUMP SECONDARY Pressure setpoint reset [yes,no] | pump_ride_on_curve | pump_ride_on_curve | pump_ride_on_curve | pump_ride_on_curve | [6 empty] | 2021-05-06
ND_LO_COOLSYS1 CHILLER1 PUMP Pump Power [hp] | COOLSYS1 CHILLER1 PUMP Pump Power [hp] | 3.1303 | 2.82 | 3.0799 | 2.7749 | [6 empty] | 2021-05-06
ND_LO_COOLSYS1 CHILLER2 PUMP Pump Power [hp] | COOLSYS1 CHILLER2 PUMP Pump Power [hp] | 3.1303 | 2.82 | 3.0799 | 2.7749 | [6 empty] | 2021-05-06
ND_LO_COOLSYS1 PUMP SECONDARY Pump Power [hp] | COOLSYS1 PUMP SECONDARY Pump Power [hp] | 18.7817 | 16.9203 | 18.4794 | 16.6492 | [6 empty] | 2021-05-06
ND_LO_HEATSYS1 PUMP Pump Power [hp] | HEATSYS1 PUMP Pump Power [hp] | 24.9162 | 21.8126 | 24.9344 | 21.5047 | [6 empty] | 2021-05-06
ND_LO_TOWERWATERSYS PUMP Pump Power [hp] | TOWERWATERSYS PUMP Pump Power [hp] | 36.4091 | 32.8031 | 35.8278 | 32.2799 | [6 empty] | 2021-05-06
ND_LO_PLANT CIRC PUMP Pump Power [hp] | PLANT CIRC PUMP Pump Power [hp] | 4.5851 | 4.5133 | 4.6096 | 4.5248 | [6 empty] | 2021-05-06
ND_LO_Datacenter PLANT CIRC PUMP Pump Power [hp] | Datacenter PLANT CIRC PUMP Pump Power [hp] | 4.5851 | 4.5133 | 4.6096 | 4.5248 | [6 empty] | 2021-05-06
ND_LO_ZN_VAV_BOXes_Max_Reheat_Water_Flow_GPM | ZN_VAV_BOXes_Max_Reheat_Water_Flow_GPM | 547.5584 | 528.6718 | 548.392 | 514.9478 | [6 empty] | 2021-05-06
ND_LO_COOLSYS1 PUMP SECONDARY VSD | COOLSYS1 PUMP SECONDARY VSD | No | No | No | No | [6 empty] | 2021-05-06
ND_LO_HEATSYS1 PUMP VSD | HEATSYS1 PUMP VSD | No | No | No | No | [6 empty] | 2021-05-06
ND_LO_DATACENTER BASEMENT Cooling Capacity [ton] | DATACENTER BASEMENT Cooling Capacity [ton] | 123.4693 | 123.0914 | 123.6721 | 123.2749 | [6 empty] | 2021-05-06
ND_LO_DATACENTER BOT Cooling Capacity [ton] | DATACENTER BOT Cooling Capacity [ton] | 2.7777 | 2.733 | 2.8261 | 2.7495 | [6 empty] | 2021-05-06
ND_LO_DATACENTER MID Cooling Capacity [ton] | DATACENTER MID Cooling Capacity [ton] | 26.6847 | 26.2457 | 27.2193 | 26.4297 | [6 empty] | 2021-05-06
ND_LO_DATACENTER TOP Cooling Capacity [ton] | DATACENTER TOP Cooling Capacity [ton] | 2.7184 | 2.675 | 2.7624 | 2.6835 | [6 empty] | 2021-05-06
id | item | Zone6A(ND-Bismarck-ND) ASHRAE901-state_STD2016 | Zone6A(ND-Bismarck-ND) ASHRAE901-state_STD2019 | Zone7(ND-Minot-ND) ASHRAE901-state_STD2016 | Zone7(ND-Minot-ND) ASHRAE901-state_STD2019 | [6 empty] | 2021-05-06
ND_RS_PSZ-AC:1 Cooling Capacity [ton] | PSZ-AC:1 Cooling Capacity [ton] | 9.3438 | 8.8584 | 9.2492 | 8.7742 | [6 empty] | 2021-05-06
ND_RS_PSZ-AC:2 Cooling Capacity [ton] | PSZ-AC:2 Cooling Capacity [ton] | 45.5743 | 43.7232 | 43.7314 | 41.9212 | [6 empty] | 2021-05-06
ND_RS_PSZ-AC:3 Cooling Capacity [ton] | PSZ-AC:3 Cooling Capacity [ton] | 5.9889 | 5.8144 | 6.1502 | 5.7573 | [6 empty] | 2021-05-06
ND_RS_PSZ-AC:4 Cooling Capacity [ton] | PSZ-AC:4 Cooling Capacity [ton] | 4.8915 | 4.6812 | 5.0979 | 4.6907 | [6 empty] | 2021-05-06
ND_RS_PSZ-AC:1 Supply Flow Rate [cfm] | PSZ-AC:1 Supply Flow Rate [cfm] | 4047.0608 | 3729.2288 | 3983.4944 | 3665.6624 | [6 empty] | 2021-05-06
ND_RS_PSZ-AC:2 Supply Flow Rate [cfm] | PSZ-AC:2 Supply Flow Rate [cfm] | 16124.6768 | 15277.1248 | 15806.8448 | 14938.104 | [6 empty] | 2021-05-06
ND_RS_PSZ-AC:3 Supply Flow Rate [cfm] | PSZ-AC:3 Supply Flow Rate [cfm] | 2394.3344 | 2309.5792 | 2521.4672 | 2330.768 | [6 empty] | 2021-05-06
ND_RS_PSZ-AC:4 Supply Flow Rate [cfm] | PSZ-AC:4 Supply Flow Rate [cfm] | 1864.6144 | 1758.6704 | 2012.936 | 1801.048 | [6 empty] | 2021-05-06
ND_RS_PSZ-AC:1 OA Rate [cfm] | PSZ-AC:1 OA Rate [cfm] | 490.669 | 490.669 | 490.669 | 490.669 | [6 empty] | 2021-05-06
ND_RS_PSZ-AC:2 OA Rate [cfm] | PSZ-AC:2 OA Rate [cfm] | 4005.1282 | 4005.1282 | 4005.1282 | 4005.1282 | [6 empty] | 2021-05-06
ND_RS_PSZ-AC:3 OA Rate [cfm] | PSZ-AC:3 OA Rate [cfm] | 377.3937 | 377.3937 | 377.3937 | 377.3937 | [6 empty] | 2021-05-06
ND_RS_PSZ-AC:4 OA Rate [cfm] | PSZ-AC:4 OA Rate [cfm] | 377.3937 | 377.3937 | 377.3937 | 377.3937 | [6 empty] | 2021-05-06
ND_RS_PSZ-AC:1 OA Damper [gravity, motorized] | PSZ-AC:1 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2021-05-06
ND_RS_PSZ-AC:2 OA Damper [gravity, motorized] | PSZ-AC:2 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2021-05-06
ND_RS_PSZ-AC:3 OA Damper [gravity, motorized] | PSZ-AC:3 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2021-05-06
ND_RS_PSZ-AC:4 OA Damper [gravity, motorized] | PSZ-AC:4 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2021-05-06
ND_RS_PSZ-AC:1 Heating Capacity [kBtu/hr] | PSZ-AC:1 Heating Capacity [kBtu/hr] | 184.3632 | 172.1768 | 182.3917 | 170.0894 | [6 empty] | 2021-05-06
ND_RS_PSZ-AC:2 Heating Capacity [kBtu/hr] | PSZ-AC:2 Heating Capacity [kBtu/hr] | 915.7297 | 883.7172 | 901.2592 | 869.0867 | [6 empty] | 2021-05-06
ND_RS_PSZ-AC:3 Heating Capacity [kBtu/hr] | PSZ-AC:3 Heating Capacity [kBtu/hr] | 118.4832 | 115.4398 | 122.303 | 114.5291 | [6 empty] | 2021-05-06
ND_RS_PSZ-AC:4 Heating Capacity [kBtu/hr] | PSZ-AC:4 Heating Capacity [kBtu/hr] | 100.0525 | 96.34 | 104.3459 | 97.4513 | [6 empty] | 2021-05-06
id | item | Zone6A(ND-Bismarck-ND) ASHRAE901-state_STD2016 | Zone6A(ND-Bismarck-ND) ASHRAE901-state_STD2019 | Zone7(ND-Minot-ND) ASHRAE901-state_STD2016 | Zone7(ND-Minot-ND) ASHRAE901-state_STD2019 | [6 empty] | 2021-05-06
ND_PS_VAV_POD_1 Cooling Capacity [ton] | VAV_POD_1 Cooling Capacity [ton] | 20.317 | 19.3373 | 20.7474 | 19.2157 | [6 empty] | 2021-05-06
ND_PS_VAV_POD_2 Cooling Capacity [ton] | VAV_POD_2 Cooling Capacity [ton] | 20.1736 | 19.0938 | 20.4455 | 18.9294 | [6 empty] | 2021-05-06
ND_PS_VAV_POD_3 Cooling Capacity [ton] | VAV_POD_3 Cooling Capacity [ton] | 18.6855 | 17.5426 | 19.0533 | 17.3999 | [6 empty] | 2021-05-06
ND_PS_VAV_OTHER Cooling Capacity [ton] | VAV_OTHER Cooling Capacity [ton] | 26.8104 | 24.0313 | 26.2761 | 23.0712 | [6 empty] | 2021-05-06
ND_PS_PSZ-AC_1:6 Cooling Capacity [ton] | PSZ-AC_1:6 Cooling Capacity [ton] | 7.8841 | 7.5954 | 7.809 | 7.4794 | [6 empty] | 2021-05-06
ND_PS_PSZ-AC_2:5 Cooling Capacity [ton] | PSZ-AC_2:5 Cooling Capacity [ton] | 5.7523 | 5.6573 | 6.0467 | 5.9692 | [6 empty] | 2021-05-06
ND_PS_PSZ-AC_2:7 Cooling Capacity [ton] | PSZ-AC_2:7 Cooling Capacity [ton] | 10.5074 | 10.5074 | 10.5074 | 10.5074 | [6 empty] | 2021-05-06
ND_PS_VAV_POD_1 Supply Flow Rate [cfm] | VAV_POD_1 Supply Flow Rate [cfm] | 6102.3744 | 5805.7312 | 6229.5072 | 5763.3536 | [6 empty] | 2021-05-06
ND_PS_VAV_POD_2 Supply Flow Rate [cfm] | VAV_POD_2 Supply Flow Rate [cfm] | 6059.9968 | 5720.976 | 6144.752 | 5678.5984 | [6 empty] | 2021-05-06
ND_PS_VAV_POD_3 Supply Flow Rate [cfm] | VAV_POD_3 Supply Flow Rate [cfm] | 5615.032 | 5254.8224 | 5720.976 | 5212.4448 | [6 empty] | 2021-05-06
ND_PS_VAV_OTHER Supply Flow Rate [cfm] | VAV_OTHER Supply Flow Rate [cfm] | 8539.0864 | 7945.8 | 8602.6528 | 7755.1008 | [6 empty] | 2021-05-06
ND_PS_PSZ-AC_2:5 Supply Flow Rate [cfm] | PSZ-AC_2:5 Supply Flow Rate [cfm] | 1716.2928 | 1695.104 | 1822.2368 | 1801.048 | [6 empty] | 2021-05-06
ND_PS_PSZ-AC_1:6 Supply Flow Rate [cfm] | PSZ-AC_1:6 Supply Flow Rate [cfm] | 2690.9776 | 2563.8448 | 2712.1664 | 2563.8448 | [6 empty] | 2021-05-06
ND_PS_PSZ-AC_2:7 Supply Flow Rate [cfm] | PSZ-AC_2:7 Supply Flow Rate [cfm] | 3157.1312 | 3157.1312 | 3157.1312 | 3157.1312 | [6 empty] | 2021-05-06
ND_PS_Supply Air Temp. Reset Flag | Supply Air Temp. Reset Flag | Yes | Yes | Yes | Yes | [6 empty] | 2021-05-06
ND_PS_VAV_POD_1 OA Rate [cfm] | VAV_POD_1 OA Rate [cfm] | 6094.4922 | 5802.8283 | 6225.9475 | 5766.32 | [6 empty] | 2021-05-06
ND_PS_VAV_POD_2 OA Rate [cfm] | VAV_POD_2 OA Rate [cfm] | 6051.9451 | 5729.7482 | 6135.3442 | 5680.3995 | [6 empty] | 2021-05-06
ND_PS_VAV_POD_3 OA Rate [cfm] | VAV_POD_3 OA Rate [cfm] | 5605.1368 | 5264.2514 | 5714.9796 | 5221.4077 | [6 empty] | 2021-05-06
ND_PS_VAV_OTHER OA Rate [cfm] | VAV_OTHER OA Rate [cfm] | 3736.1787 | 2988.8921 | 3736.1787 | 2988.8921 | [6 empty] | 2021-05-06
ND_PS_PSZ-AC_2:5 OA Rate [cfm] | PSZ-AC_2:5 OA Rate [cfm] | 1152.7343 | 1152.7343 | 1152.7343 | 1152.7343 | [6 empty] | 2021-05-06
ND_PS_PSZ-AC_1:6 OA Rate [cfm] | PSZ-AC_1:6 OA Rate [cfm] | 539.9118 | 539.9118 | 539.9118 | 539.9118 | [6 empty] | 2021-05-06
ND_PS_PSZ-AC_2:7 OA Rate [cfm] | PSZ-AC_2:7 OA Rate [cfm] | 3153.0841 | 3153.0841 | 3153.0841 | 3153.0841 | [6 empty] | 2021-05-06
ND_PS_VAV_POD_1 OA Damper [gravity, motorized] | VAV_POD_1 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2021-05-06
ND_PS_VAV_POD_2 OA Damper [gravity, motorized] | VAV_POD_2 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2021-05-06
ND_PS_VAV_POD_3 OA Damper [gravity, motorized] | VAV_POD_3 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2021-05-06
ND_PS_VAV_OTHER OA Damper [gravity, motorized] | VAV_OTHER OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2021-05-06
ND_PS_PSZ-AC_2:5 OA Damper [gravity, motorized] | PSZ-AC_2:5 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2021-05-06
ND_PS_PSZ-AC_1:6 OA Damper [gravity, motorized] | PSZ-AC_1:6 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2021-05-06
ND_PS_PSZ-AC_2:7 OA Damper [gravity, motorized] | PSZ-AC_2:7 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2021-05-06
ND_PS_VAV_POD_1 (economizer) | VAV_POD_1 (economizer) | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | [6 empty] | 2021-05-06
ND_PS_VAV_POD_2 (economizer) | VAV_POD_2 (economizer) | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | [6 empty] | 2021-05-06
ND_PS_VAV_POD_3 (economizer) | VAV_POD_3 (economizer) | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | [6 empty] | 2021-05-06
ND_PS_VAV_OTHER (economizer) | VAV_OTHER (economizer) | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | [6 empty] | 2021-05-06
ND_PS_PSZ-AC_2:5 (economizer) | PSZ-AC_2:5 (economizer) | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | [6 empty] | 2021-05-06
ND_PS_PSZ-AC_1:6 (economizer) | PSZ-AC_1:6 (economizer) | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | [6 empty] | 2021-05-06
ND_PS_PSZ-AC_2:7 (economizer) | PSZ-AC_2:7 (economizer) | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | [6 empty] | 2021-05-06
ND_PS_VAV_Pod_1_ERV Flag | VAV_Pod_1_ERV Flag | Yes | Yes | Yes | Yes | [6 empty] | 2021-05-06
ND_PS_VAV_Pod_2_ERV Flag | VAV_Pod_2_ERV Flag | Yes | Yes | Yes | Yes | [6 empty] | 2021-05-06
ND_PS_VAV_Pod_3_ERV Flag | VAV_Pod_3_ERV Flag | Yes | Yes | Yes | Yes | [6 empty] | 2021-05-06
ND_PS_VAV_OTHER_ERV Flag | VAV_OTHER_ERV Flag | Yes | Yes | Yes | Yes | [6 empty] | 2021-05-06
ND_PS_PSZ_AC_2_5_ERV Flag | PSZ_AC_2_5_ERV Flag | No | No | Yes | Yes | [6 empty] | 2021-05-06
ND_PS_PSZ_AC_2_7_ERV Flag | PSZ_AC_2_7_ERV Flag | Yes | Yes | Yes | Yes | [6 empty] | 2021-05-06
ND_PS_HEATSYS1 Capacity [MMBTU/h] | HEATSYS1 Capacity [MMBTU/h] | 1.4511 | 1.3859 | 1.4485 | 1.3513 | [6 empty] | 2021-05-06
ND_PS_HEATSYS1 Flow Rate [gal/min] | HEATSYS1 Flow Rate [gal/min] | 148.9301 | 142.2384 | 148.6635 | 138.6815 | [6 empty] | 2021-05-06
ND_PS_VAV_POD_1 Fan Power [hp] | VAV_POD_1 Fan Power [hp] | 8.9946 | 8.5609 | 9.1851 | 8.5071 | [6 empty] | 2021-05-06
ND_PS_VAV_POD_2 Fan Power [hp] | VAV_POD_2 Fan Power [hp] | 8.9311 | 8.4531 | 9.0515 | 8.3803 | [6 empty] | 2021-05-06
ND_PS_VAV_POD_3 Fan Power [hp] | VAV_POD_3 Fan Power [hp] | 8.2723 | 7.7663 | 8.4352 | 7.7032 | [6 empty] | 2021-05-06
ND_PS_VAV_OTHER Fan Power [hp] | VAV_OTHER Fan Power [hp] | 12.5062 | 11.6344 | 12.5875 | 11.3566 | [6 empty] | 2021-05-06
ND_PS_HEATSYS1 Pump Power [hp] | HEATSYS1 Pump Power [hp] | 3.2192 | 3.0441 | 3.2135 | 2.968 | [6 empty] | 2021-05-06
ND_PS_PSZ-AC_1:6 Heating Capacity [kBtu/hr] | PSZ-AC_1:6 Heating Capacity [kBtu/hr] | 225.9893 | 216.734 | 227.0244 | 216.3146 | [6 empty] | 2021-05-06
ND_PS_PSZ-AC_2:5 Heating Capacity [kBtu/hr] | PSZ-AC_2:5 Heating Capacity [kBtu/hr] | 165.7863 | 164.7919 | 168.2904 | 167.423 | [6 empty] | 2021-05-06
ND_PS_PSZ-AC_2:7 Heating Capacity [kBtu/hr] | PSZ-AC_2:7 Heating Capacity [kBtu/hr] | 398.7709 | 398.7709 | 397.1903 | 397.1903 | [6 empty] | 2021-05-06
ND_PS_ZN_VAV_BOXes_Max_Reheat_Water_Flow_GPM | ZN_VAV_BOXes_Max_Reheat_Water_Flow_GPM | 86.9497 | 83.9261 | 86.1041 | 81.4018 | [6 empty] | 2021-05-06
id | item | Zone6A(ND-Bismarck-ND) ASHRAE901-state_STD2016 | Zone6A(ND-Bismarck-ND) ASHRAE901-state_STD2019 | Zone7(ND-Minot-ND) ASHRAE901-state_STD2016 | Zone7(ND-Minot-ND) ASHRAE901-state_STD2019 | [6 empty] | 2021-05-06
ND_SH_SAC_FRONTOFFICE Cooling Capacity [ton] | SAC_FRONTOFFICE Cooling Capacity [ton] | 2.2634 | 2.1308 | 2.2157 | 2.0767 | [6 empty] | 2021-05-06
ND_SH_SAC_FRONTLOUNGE Cooling Capacity [ton] | SAC_FRONTLOUNGE Cooling Capacity [ton] | 5.988 | 5.7315 | 5.8285 | 5.5738 | [6 empty] | 2021-05-06
ND_SH_SAC_MEETINGROOM Cooling Capacity [ton] | SAC_MEETINGROOM Cooling Capacity [ton] | 3.0697 | 2.9461 | 3.0104 | 2.9316 | [6 empty] | 2021-05-06
ND_SH_SAC_EXC_EMPLGE_RESTRM Cooling Capacity [ton] | SAC_EXC_EMPLGE_RESTRM Cooling Capacity [ton] | 5.884 | 5.8348 | 5.8521 | 5.7876 | [6 empty] | 2021-05-06
ND_SH_SAC_FO_ADDAQ SUPPLY FAN Supply Flow Rate [cfm] | SAC_FO_ADDAQ SUPPLY FAN Supply Flow Rate [cfm] | 826.3632 | 762.7968 | 826.3632 | 762.7968 | [6 empty] | 2021-05-06
ND_SH_SAC_FL_ADDAQ SUPPLY FAN Supply Flow Rate [cfm] | SAC_FL_ADDAQ SUPPLY FAN Supply Flow Rate [cfm] | 1906.992 | 1822.2368 | 1906.992 | 1801.048 | [6 empty] | 2021-05-06
ND_SH_SAC_MR_ADDAQ SUPPLY FAN Supply Flow Rate [cfm] | SAC_MR_ADDAQ SUPPLY FAN Supply Flow Rate [cfm] | 911.1184 | 889.9296 | 911.1184 | 889.9296 | [6 empty] | 2021-05-06
ND_SH_SAC_EXC_ADDAQ SUPPLY FAN Supply Flow Rate [cfm] | SAC_EXC_ADDAQ SUPPLY FAN Supply Flow Rate [cfm] | 2309.5792 | 2288.3904 | 2330.768 | 2288.3904 | [6 empty] | 2021-05-06
ND_SH_SAC_Exc_EmpLge_RestRm OA Rate [cfm] | SAC_Exc_EmpLge_RestRm OA Rate [cfm] | 199.9928 | 199.9928 | 199.9928 | 199.9928 | [6 empty] | 2021-05-06
ND_SH_SAC_FrontLounge OA Rate [cfm] | SAC_FrontLounge OA Rate [cfm] | 500.0133 | 500.0133 | 500.0133 | 500.0133 | [6 empty] | 2021-05-06
ND_SH_SAC_FrontOffice OA Rate [cfm] | SAC_FrontOffice OA Rate [cfm] | 119.2938 | 119.2938 | 119.2938 | 119.2938 | [6 empty] | 2021-05-06
ND_SH_SAC_MeetingRoom OA Rate [cfm] | SAC_MeetingRoom OA Rate [cfm] | 267.7629 | 267.7629 | 267.7629 | 267.7629 | [6 empty] | 2021-05-06
ND_SH_SAC_FrontLounge OA Damper [gravity, motorized] | SAC_FrontLounge OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2021-05-06
ND_SH_SAC_FrontOffice (economizer) | SAC_FrontOffice (economizer) | No | No | No | No | [6 empty] | 2021-05-06
ND_SH_SAC_FrontLounge (economizer) | SAC_FrontLounge (economizer) | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | [6 empty] | 2021-05-06
ND_SH_SAC_MeetingRoom (economizer) | SAC_MeetingRoom (economizer) | No | No | No | No | [6 empty] | 2021-05-06
ND_SH_SAC_Exc_EmpLge_RestRm (economizer) | SAC_Exc_EmpLge_RestRm (economizer) | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | [6 empty] | 2021-05-06
ND_SH_SAC_FRONTOFFICE Heating Capacity [kBtu/hr] | SAC_FRONTOFFICE Heating Capacity [kBtu/hr] | 39.6182 | 37.6137 | 39.6131 | 37.4409 | [6 empty] | 2021-05-06
ND_SH_SAC_FRONTLOUNGE Heating Capacity [kBtu/hr] | SAC_FRONTLOUNGE Heating Capacity [kBtu/hr] | 112.2955 | 108.8495 | 111.9664 | 108.2271 | [6 empty] | 2021-05-06
ND_SH_SAC_MEETINGROOM Heating Capacity [kBtu/hr] | SAC_MEETINGROOM Heating Capacity [kBtu/hr] | 56.518 | 55.2321 | 56.0413 | 54.9508 | [6 empty] | 2021-05-06
ND_SH_SAC_EXC_EMPLGE_RESTRM Heating Capacity [kBtu/hr] | SAC_EXC_EMPLGE_RESTRM Heating Capacity [kBtu/hr] | 98.2802 | 97.5149 | 98.7729 | 97.7496 | [6 empty] | 2021-05-06
id | item | Zone6A(ND-Bismarck-ND) ASHRAE901-state_STD2016 | Zone6A(ND-Bismarck-ND) ASHRAE901-state_STD2019 | Zone7(ND-Minot-ND) ASHRAE901-state_STD2016 | Zone7(ND-Minot-ND) ASHRAE901-state_STD2019 | [6 empty] | 2021-05-06
ND_MA_SPLIT GSW COOLING COIL Cooling Capacity [ton] | SPLIT GSW COOLING COIL Cooling Capacity [ton] | 0.83203 | 0.79975 | 0.86359 | 0.79896 | [6 empty] | 2021-05-06
ND_MA_SPLIT GNW COOLING COIL Cooling Capacity [ton] | SPLIT GNW COOLING COIL Cooling Capacity [ton] | 0.77251 | 0.74434 | 0.78119 | 0.73055 | [6 empty] | 2021-05-06
ND_MA_SPLIT OFFICE COOLING COIL Cooling Capacity [ton] | SPLIT OFFICE COOLING COIL Cooling Capacity [ton] | 1.753 | 1.5644 | 1.8285 | 1.6023 | [6 empty] | 2021-05-06
ND_MA_SPLIT GNE COOLING COIL Cooling Capacity [ton] | SPLIT GNE COOLING COIL Cooling Capacity [ton] | 0.64423 | 0.62209 | 0.66281 | 0.62091 | [6 empty] | 2021-05-06
ND_MA_SPLIT GN1 COOLING COIL Cooling Capacity [ton] | SPLIT GN1 COOLING COIL Cooling Capacity [ton] | 0.52832 | 0.5133 | 0.53739 | 0.51361 | [6 empty] | 2021-05-06
ND_MA_SPLIT GN2 COOLING COIL Cooling Capacity [ton] | SPLIT GN2 COOLING COIL Cooling Capacity [ton] | 0.52562 | 0.51079 | 0.53732 | 0.51128 | [6 empty] | 2021-05-06
ND_MA_SPLIT GS1 COOLING COIL Cooling Capacity [ton] | SPLIT GS1 COOLING COIL Cooling Capacity [ton] | 0.59956 | 0.58057 | 0.62784 | 0.58934 | [6 empty] | 2021-05-06
ND_MA_SPLIT GS2 COOLING COIL Cooling Capacity [ton] | SPLIT GS2 COOLING COIL Cooling Capacity [ton] | 0.63588 | 0.61218 | 0.66561 | 0.62231 | [6 empty] | 2021-05-06
ND_MA_SPLIT MSW COOLING COIL Cooling Capacity [ton] | SPLIT MSW COOLING COIL Cooling Capacity [ton] | 2.048 | 1.971 | 2.1243 | 1.9646 | [6 empty] | 2021-05-06
ND_MA_SPLIT MNW COOLING COIL Cooling Capacity [ton] | SPLIT MNW COOLING COIL Cooling Capacity [ton] | 1.9315 | 1.856 | 1.9515 | 1.8221 | [6 empty] | 2021-05-06
ND_MA_SPLIT MSE COOLING COIL Cooling Capacity [ton] | SPLIT MSE COOLING COIL Cooling Capacity [ton] | 1.8 | 1.7297 | 1.9249 | 1.75 | [6 empty] | 2021-05-06
ND_MA_SPLIT MNE COOLING COIL Cooling Capacity [ton] | SPLIT MNE COOLING COIL Cooling Capacity [ton] | 1.4468 | 1.3809 | 1.6112 | 1.4863 | [6 empty] | 2021-05-06
ND_MA_SPLIT MN1 COOLING COIL Cooling Capacity [ton] | SPLIT MN1 COOLING COIL Cooling Capacity [ton] | 1.1945 | 1.1645 | 1.1877 | 1.1385 | [6 empty] | 2021-05-06
ND_MA_SPLIT MN2 COOLING COIL Cooling Capacity [ton] | SPLIT MN2 COOLING COIL Cooling Capacity [ton] | 1.187 | 1.1575 | 1.1796 | 1.1315 | [6 empty] | 2021-05-06
ND_MA_SPLIT MS1 COOLING COIL Cooling Capacity [ton] | SPLIT MS1 COOLING COIL Cooling Capacity [ton] | 1.4045 | 1.3559 | 1.4987 | 1.3709 | [6 empty] | 2021-05-06
ND_MA_SPLIT MS2 COOLING COIL Cooling Capacity [ton] | SPLIT MS2 COOLING COIL Cooling Capacity [ton] | 1.4095 | 1.3604 | 1.5041 | 1.3756 | [6 empty] | 2021-05-06
ND_MA_SPLIT TSW COOLING COIL Cooling Capacity [ton] | SPLIT TSW COOLING COIL Cooling Capacity [ton] | 1.2896 | 1.2465 | 1.309 | 1.2114 | [6 empty] | 2021-05-06
ND_MA_SPLIT TNW COOLING COIL Cooling Capacity [ton] | SPLIT TNW COOLING COIL Cooling Capacity [ton] | 1.2112 | 1.1716 | 1.2142 | 1.1364 | [6 empty] | 2021-05-06
ND_MA_SPLIT TSE COOLING COIL Cooling Capacity [ton] | SPLIT TSE COOLING COIL Cooling Capacity [ton] | 1.1555 | 1.1153 | 1.2034 | 1.1043 | [6 empty] | 2021-05-06
ND_MA_SPLIT TNE COOLING COIL Cooling Capacity [ton] | SPLIT TNE COOLING COIL Cooling Capacity [ton] | 1.0137 | 0.98831 | 0.96218 | 0.88879 | [6 empty] | 2021-05-06
ND_MA_SPLIT TN1 COOLING COIL Cooling Capacity [ton] | SPLIT TN1 COOLING COIL Cooling Capacity [ton] | 0.81279 | 0.79629 | 0.76727 | 0.74092 | [6 empty] | 2021-05-06
ND_MA_SPLIT TN2 COOLING COIL Cooling Capacity [ton] | SPLIT TN2 COOLING COIL Cooling Capacity [ton] | 0.81781 | 0.80124 | 0.75984 | 0.73451 | [6 empty] | 2021-05-06
ND_MA_SPLIT TS1 COOLING COIL Cooling Capacity [ton] | SPLIT TS1 COOLING COIL Cooling Capacity [ton] | 0.949 | 0.91904 | 0.9813 | 0.90482 | [6 empty] | 2021-05-06
ND_MA_SPLIT TS2 COOLING COIL Cooling Capacity [ton] | SPLIT TS2 COOLING COIL Cooling Capacity [ton] | 0.9528 | 0.92264 | 0.98564 | 0.9087 | [6 empty] | 2021-05-06
ND_MA_Split GN1 Furnace with DX Cooling OA Rate [cfm] | Split GN1 Furnace with DX Cooling OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | [6 empty] | 2021-05-06
ND_MA_Split GN2 Furnace with DX Cooling OA Rate [cfm] | Split GN2 Furnace with DX Cooling OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | [6 empty] | 2021-05-06
ND_MA_Split GNE Furnace with DX Cooling OA Rate [cfm] | Split GNE Furnace with DX Cooling OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | [6 empty] | 2021-05-06
ND_MA_Split GNW Furnace with DX Cooling OA Rate [cfm] | Split GNW Furnace with DX Cooling OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | [6 empty] | 2021-05-06
ND_MA_Split GS1 Furnace with DX Cooling OA Rate [cfm] | Split GS1 Furnace with DX Cooling OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | [6 empty] | 2021-05-06
ND_MA_Split GS2 Furnace with DX Cooling OA Rate [cfm] | Split GS2 Furnace with DX Cooling OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | [6 empty] | 2021-05-06
ND_MA_Split GSW Furnace with DX Cooling OA Rate [cfm] | Split GSW Furnace with DX Cooling OA Rate [cfm] | 56.9945 | 56.9945 | 56.9945 | 56.9945 | [6 empty] | 2021-05-06
ND_MA_Split MN1 Furnace with DX Cooling OA Rate [cfm] | Split MN1 Furnace with DX Cooling OA Rate [cfm] | 109.9824 | 109.9824 | 109.9824 | 109.9824 | [6 empty] | 2021-05-06
ND_MA_Split MN2 Furnace with DX Cooling OA Rate [cfm] | Split MN2 Furnace with DX Cooling OA Rate [cfm] | 109.9824 | 109.9824 | 109.9824 | 109.9824 | [6 empty] | 2021-05-06
ND_MA_Split MNE Furnace with DX Cooling OA Rate [cfm] | Split MNE Furnace with DX Cooling OA Rate [cfm] | 109.9824 | 109.9824 | 109.9824 | 109.9824 | [6 empty] | 2021-05-06
ND_MA_Split MNW Furnace with DX Cooling OA Rate [cfm] | Split MNW Furnace with DX Cooling OA Rate [cfm] | 109.9824 | 109.9824 | 109.9824 | 109.9824 | [6 empty] | 2021-05-06
ND_MA_Split MS1 Furnace with DX Cooling OA Rate [cfm] | Split MS1 Furnace with DX Cooling OA Rate [cfm] | 109.9824 | 109.9824 | 109.9824 | 109.9824 | [6 empty] | 2021-05-06
ND_MA_Split MS2 Furnace with DX Cooling OA Rate [cfm] | Split MS2 Furnace with DX Cooling OA Rate [cfm] | 109.9824 | 109.9824 | 109.9824 | 109.9824 | [6 empty] | 2021-05-06
ND_MA_Split MSE Furnace with DX Cooling OA Rate [cfm] | Split MSE Furnace with DX Cooling OA Rate [cfm] | 109.9824 | 109.9824 | 109.9824 | 109.9824 | [6 empty] | 2021-05-06
ND_MA_Split MSW Furnace with DX Cooling OA Rate [cfm] | Split MSW Furnace with DX Cooling OA Rate [cfm] | 109.9824 | 109.9824 | 109.9824 | 109.9824 | [6 empty] | 2021-05-06
ND_MA_Split Office Furnace with DX Cooling OA Rate [cfm] | Split Office Furnace with DX Cooling OA Rate [cfm] | 80.7372 | 80.7372 | 80.7372 | 80.7372 | [6 empty] | 2021-05-06
ND_MA_Split TN1 Furnace with DX Cooling OA Rate [cfm] | Split TN1 Furnace with DX Cooling OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | [6 empty] | 2021-05-06
ND_MA_Split TN2 Furnace with DX Cooling OA Rate [cfm] | Split TN2 Furnace with DX Cooling OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | [6 empty] | 2021-05-06
ND_MA_Split TNE Furnace with DX Cooling OA Rate [cfm] | Split TNE Furnace with DX Cooling OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | [6 empty] | 2021-05-06
ND_MA_Split TNW Furnace with DX Cooling OA Rate [cfm] | Split TNW Furnace with DX Cooling OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | [6 empty] | 2021-05-06
ND_MA_Split TS1 Furnace with DX Cooling OA Rate [cfm] | Split TS1 Furnace with DX Cooling OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | [6 empty] | 2021-05-06
ND_MA_Split TS2 Furnace with DX Cooling OA Rate [cfm] | Split TS2 Furnace with DX Cooling OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | [6 empty] | 2021-05-06
ND_MA_Split TSE Furnace with DX Cooling OA Rate [cfm] | Split TSE Furnace with DX Cooling OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | [6 empty] | 2021-05-06
ND_MA_Split TSW Furnace with DX Cooling OA Rate [cfm] | Split TSW Furnace with DX Cooling OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | [6 empty] | 2021-05-06
ND_MA_SPLIT GSW HEATING COIL Heating Capacity [kBtu/hr] | SPLIT GSW HEATING COIL Heating Capacity [kBtu/hr] | 13.4186 | 13.4781 | 13.6113 | 13.4694 | [6 empty] | 2021-05-06
ND_MA_SPLIT GNW HEATING COIL Heating Capacity [kBtu/hr] | SPLIT GNW HEATING COIL Heating Capacity [kBtu/hr] | 13.3264 | 13.386 | 13.4685 | 13.3268 | [6 empty] | 2021-05-06
ND_MA_SPLIT OFFICE HEATING COIL Heating Capacity [kBtu/hr] | SPLIT OFFICE HEATING COIL Heating Capacity [kBtu/hr] | 27.3384 | 27.4219 | 27.3626 | 27.2082 | [6 empty] | 2021-05-06
ND_MA_SPLIT GNE HEATING COIL Heating Capacity [kBtu/hr] | SPLIT GNE HEATING COIL Heating Capacity [kBtu/hr] | 13.2923 | 13.3519 | 13.4359 | 13.2979 | [6 empty] | 2021-05-06
ND_MA_SPLIT GN1 HEATING COIL Heating Capacity [kBtu/hr] | SPLIT GN1 HEATING COIL Heating Capacity [kBtu/hr] | 10.0745 | 10.1342 | 10.1196 | 10.0479 | [6 empty] | 2021-05-06
ND_MA_SPLIT GN2 HEATING COIL Heating Capacity [kBtu/hr] | SPLIT GN2 HEATING COIL Heating Capacity [kBtu/hr] | 10.0735 | 10.1332 | 10.1186 | 10.047 | [6 empty] | 2021-05-06
ND_MA_SPLIT GS1 HEATING COIL Heating Capacity [kBtu/hr] | SPLIT GS1 HEATING COIL Heating Capacity [kBtu/hr] | 9.9998 | 10.0593 | 10.0969 | 10.0248 | [6 empty] | 2021-05-06
ND_MA_SPLIT GS2 HEATING COIL Heating Capacity [kBtu/hr] | SPLIT GS2 HEATING COIL Heating Capacity [kBtu/hr] | 10.5316 | 10.5921 | 10.6258 | 10.5538 | [6 empty] | 2021-05-06
ND_MA_SPLIT MSW HEATING COIL Heating Capacity [kBtu/hr] | SPLIT MSW HEATING COIL Heating Capacity [kBtu/hr] | 23.5812 | 23.7108 | 24.8178 | 24.5331 | [6 empty] | 2021-05-06
ND_MA_SPLIT MNW HEATING COIL Heating Capacity [kBtu/hr] | SPLIT MNW HEATING COIL Heating Capacity [kBtu/hr] | 23.7152 | 23.8447 | 24.8313 | 24.5464 | [6 empty] | 2021-05-06
ND_MA_SPLIT MSE HEATING COIL Heating Capacity [kBtu/hr] | SPLIT MSE HEATING COIL Heating Capacity [kBtu/hr] | 23.5017 | 23.6312 | 24.7425 | 24.4664 | [6 empty] | 2021-05-06
ND_MA_SPLIT MNE HEATING COIL Heating Capacity [kBtu/hr] | SPLIT MNE HEATING COIL Heating Capacity [kBtu/hr] | 23.6356 | 23.765 | 24.7559 | 24.4796 | [6 empty] | 2021-05-06
ND_MA_SPLIT MN1 HEATING COIL Heating Capacity [kBtu/hr] | SPLIT MN1 HEATING COIL Heating Capacity [kBtu/hr] | 16.9203 | 17.0471 | 17.548 | 17.4105 | [6 empty] | 2021-05-06
ND_MA_SPLIT MN2 HEATING COIL Heating Capacity [kBtu/hr] | SPLIT MN2 HEATING COIL Heating Capacity [kBtu/hr] | 16.9183 | 17.045 | 17.546 | 17.4087 | [6 empty] | 2021-05-06
ND_MA_SPLIT MS1 HEATING COIL Heating Capacity [kBtu/hr] | SPLIT MS1 HEATING COIL Heating Capacity [kBtu/hr] | 16.798 | 16.9247 | 17.5454 | 17.408 | [6 empty] | 2021-05-06
ND_MA_SPLIT MS2 HEATING COIL Heating Capacity [kBtu/hr] | SPLIT MS2 HEATING COIL Heating Capacity [kBtu/hr] | 16.796 | 16.9227 | 17.5435 | 17.4063 | [6 empty] | 2021-05-06
ND_MA_SPLIT TSW HEATING COIL Heating Capacity [kBtu/hr] | SPLIT TSW HEATING COIL Heating Capacity [kBtu/hr] | 16.4946 | 16.5568 | 17.0328 | 16.8913 | [6 empty] | 2021-05-06
ND_MA_SPLIT TNW HEATING COIL Heating Capacity [kBtu/hr] | SPLIT TNW HEATING COIL Heating Capacity [kBtu/hr] | 16.573 | 16.6354 | 17.0471 | 16.906 | [6 empty] | 2021-05-06
ND_MA_SPLIT TSE HEATING COIL Heating Capacity [kBtu/hr] | SPLIT TSE HEATING COIL Heating Capacity [kBtu/hr] | 16.4523 | 16.5145 | 16.993 | 16.8562 | [6 empty] | 2021-05-06
ND_MA_SPLIT TNE HEATING COIL Heating Capacity [kBtu/hr] | SPLIT TNE HEATING COIL Heating Capacity [kBtu/hr] | 16.5307 | 16.593 | 17.0073 | 16.8708 | [6 empty] | 2021-05-06
ND_MA_SPLIT TN1 HEATING COIL Heating Capacity [kBtu/hr] | SPLIT TN1 HEATING COIL Heating Capacity [kBtu/hr] | 12.8886 | 12.9508 | 12.9526 | 12.8841 | [6 empty] | 2021-05-06
ND_MA_SPLIT TN2 HEATING COIL Heating Capacity [kBtu/hr] | SPLIT TN2 HEATING COIL Heating Capacity [kBtu/hr] | 12.8875 | 12.9497 | 12.9515 | 12.8832 | [6 empty] | 2021-05-06
ND_MA_SPLIT TS1 HEATING COIL Heating Capacity [kBtu/hr] | SPLIT TS1 HEATING COIL Heating Capacity [kBtu/hr] | 12.8042 | 12.8663 | 12.9326 | 12.8635 | [6 empty] | 2021-05-06
ND_MA_SPLIT TS2 HEATING COIL Heating Capacity [kBtu/hr] | SPLIT TS2 HEATING COIL Heating Capacity [kBtu/hr] | 12.803 | 12.8651 | 12.9315 | 12.8625 | [6 empty] | 2021-05-06
ND_MA_Split_GSW ERV Flag | Split_GSW ERV Flag | Yes | Yes | Yes | Yes | [6 empty] | 2021-05-06
ND_MA_Split_GNW ERV Flag | Split_GNW ERV Flag | Yes | Yes | Yes | Yes | [6 empty] | 2021-05-06
ND_MA_Split_GNE ERV Flag | Split_GNE ERV Flag | Yes | Yes | Yes | Yes | [6 empty] | 2021-05-06
ND_MA_Split_GN1 ERV Flag | Split_GN1 ERV Flag | Yes | Yes | Yes | Yes | [6 empty] | 2021-05-06
ND_MA_Split_GN2 ERV Flag | Split_GN2 ERV Flag | Yes | Yes | Yes | Yes | [6 empty] | 2021-05-06
ND_MA_Split_GS1 ERV Flag | Split_GS1 ERV Flag | Yes | Yes | Yes | Yes | [6 empty] | 2021-05-06
ND_MA_Split_GS2 ERV Flag | Split_GS2 ERV Flag | Yes | Yes | Yes | Yes | [6 empty] | 2021-05-06
ND_MA_Split_MSW ERV Flag | Split_MSW ERV Flag | Yes | Yes | Yes | Yes | [6 empty] | 2021-05-06
ND_MA_Split_MNW ERV Flag | Split_MNW ERV Flag | Yes | Yes | Yes | Yes | [6 empty] | 2021-05-06
ND_MA_Split_MSE ERV Flag | Split_MSE ERV Flag | Yes | Yes | Yes | Yes | [6 empty] | 2021-05-06
ND_MA_Split_MNE ERV Flag | Split_MNE ERV Flag | Yes | Yes | Yes | Yes | [6 empty] | 2021-05-06
ND_MA_Split_MN1 ERV Flag | Split_MN1 ERV Flag | Yes | Yes | Yes | Yes | [6 empty] | 2021-05-06
ND_MA_Split_MN2 ERV Flag | Split_MN2 ERV Flag | Yes | Yes | Yes | Yes | [6 empty] | 2021-05-06
ND_MA_Split_MS1 ERV Flag | Split_MS1 ERV Flag | Yes | Yes | Yes | Yes | [6 empty] | 2021-05-06
ND_MA_Split_MS2 ERV Flag | Split_MS2 ERV Flag | Yes | Yes | Yes | Yes | [6 empty] | 2021-05-06
ND_MA_Split_TSW ERV Flag | Split_TSW ERV Flag | No | No | No | No | [6 empty] | 2021-05-06
ND_MA_Split_TNW ERV Flag | Split_TNW ERV Flag | Yes | Yes | No | Yes | [6 empty] | 2021-05-06
ND_MA_Split_TSE ERV Flag | Split_TSE ERV Flag | Yes | Yes | Yes | Yes | [6 empty] | 2021-05-06
ND_MA_Split_TNE ERV Flag | Split_TNE ERV Flag | Yes | Yes | Yes | Yes | [6 empty] | 2021-05-06
ND_MA_Split_TN1 ERV Flag | Split_TN1 ERV Flag | Yes | Yes | Yes | Yes | [6 empty] | 2021-05-06
ND_MA_Split_TN2 ERV Flag | Split_TN2 ERV Flag | Yes | Yes | Yes | Yes | [6 empty] | 2021-05-06
ND_MA_Split_TS1 ERV Flag | Split_TS1 ERV Flag | Yes | Yes | Yes | Yes | [6 empty] | 2021-05-06
ND_MA_Split_TS2 ERV Flag | Split_TS2 ERV Flag | Yes | Yes | Yes | Yes | [6 empty] | 2021-05-06
id | item | Zone5A(NE-Omaha-NE) ASHRAE901-state_STD2016 | Zone5A(NE-Omaha-NE) ASHRAE901-state_STD2019 | [8 empty] | 2021-05-06
NE_SO_PSZ-AC:1 Cooling Capacity [ton] | PSZ-AC:1 Cooling Capacity [ton] | 1.9803 | 1.8843 | [8 empty] | 2021-05-06
NE_SO_PSZ-AC:2 Cooling Capacity [ton] | PSZ-AC:2 Cooling Capacity [ton] | 1.7562 | 1.6896 | [8 empty] | 2021-05-06
NE_SO_PSZ-AC:3 Cooling Capacity [ton] | PSZ-AC:3 Cooling Capacity [ton] | 1.2396 | 1.2001 | [8 empty] | 2021-05-06
NE_SO_PSZ-AC:4 Cooling Capacity [ton] | PSZ-AC:4 Cooling Capacity [ton] | 1.6926 | 1.6105 | [8 empty] | 2021-05-06
NE_SO_PSZ-AC:5 Cooling Capacity [ton] | PSZ-AC:5 Cooling Capacity [ton] | 1.4546 | 1.4133 | [8 empty] | 2021-05-06
NE_SO_PSZ-AC:1 Supply Flow Rate [cfm] | PSZ-AC:1 Supply Flow Rate [cfm] | 678.0416 | 635.664 | [8 empty] | 2021-05-06
NE_SO_PSZ-AC:2 Supply Flow Rate [cfm] | PSZ-AC:2 Supply Flow Rate [cfm] | 614.4752 | 572.0976 | [8 empty] | 2021-05-06
NE_SO_PSZ-AC:3 Supply Flow Rate [cfm] | PSZ-AC:3 Supply Flow Rate [cfm] | 487.3424 | 487.3424 | [8 empty] | 2021-05-06
NE_SO_PSZ-AC:4 Supply Flow Rate [cfm] | PSZ-AC:4 Supply Flow Rate [cfm] | 593.2864 | 550.9088 | [8 empty] | 2021-05-06
NE_SO_PSZ-AC:5 Supply Flow Rate [cfm] | PSZ-AC:5 Supply Flow Rate [cfm] | 593.2864 | 572.0976 | [8 empty] | 2021-05-06
NE_SO_PSZ-AC:1 OA Rate [cfm] | PSZ-AC:1 OA Rate [cfm] | 136.9178 | 136.9178 | [8 empty] | 2021-05-06
NE_SO_PSZ-AC:2 OA Rate [cfm] | PSZ-AC:2 OA Rate [cfm] | 103.7925 | 103.7925 | [8 empty] | 2021-05-06
NE_SO_PSZ-AC:3 OA Rate [cfm] | PSZ-AC:3 OA Rate [cfm] | 61.5711 | 61.5711 | [8 empty] | 2021-05-06
NE_SO_PSZ-AC:4 OA Rate [cfm] | PSZ-AC:4 OA Rate [cfm] | 103.7925 | 103.7925 | [8 empty] | 2021-05-06
NE_SO_PSZ-AC:5 OA Rate [cfm] | PSZ-AC:5 OA Rate [cfm] | 61.5711 | 61.5711 | [8 empty] | 2021-05-06
NE_SO_PSZ-AC:1 heating Capacity [kBtu/hr] | PSZ-AC:1 heating Capacity [kBtu/hr] | 15.7847 | 15.7847 | [8 empty] | 2021-05-06
NE_SO_PSZ-AC:2 heating Capacity [kBtu/hr] | PSZ-AC:2 heating Capacity [kBtu/hr] | 22.805 | 22.5529 | [8 empty] | 2021-05-06
NE_SO_PSZ-AC:3 heating Capacity [kBtu/hr] | PSZ-AC:3 heating Capacity [kBtu/hr] | 13.8977 | 13.7583 | [8 empty] | 2021-05-06
NE_SO_PSZ-AC:4 heating Capacity [kBtu/hr] | PSZ-AC:4 heating Capacity [kBtu/hr] | 22.7099 | 22.4937 | [8 empty] | 2021-05-06
NE_SO_PSZ-AC:5 heating Capacity [kBtu/hr] | PSZ-AC:5 heating Capacity [kBtu/hr] | 13.9703 | 13.8242 | [8 empty] | 2021-05-06
id | item | Zone5A(NE-Omaha-NE) ASHRAE901-state_STD2016 | Zone5A(NE-Omaha-NE) ASHRAE901-state_STD2019 | [8 empty] | 2021-05-06
NE_LO_CAV_BAS Supply Flow Rate [cfm] | CAV_BAS Supply Flow Rate [cfm] | 12077.616 | 11187.6864 | [8 empty] | 2021-05-06
NE_LO_VAV_BOT WITH REHEAT Supply Flow Rate [cfm] | VAV_BOT WITH REHEAT Supply Flow Rate [cfm] | 20595.5136 | 19642.0176 | [8 empty] | 2021-05-06
NE_LO_VAV_MID WITH REHEAT Supply Flow Rate [cfm] | VAV_MID WITH REHEAT Supply Flow Rate [cfm] | 192097.6611 | 182922.9107 | [8 empty] | 2021-05-06
NE_LO_VAV_TOP WITH REHEAT Supply Flow Rate [cfm] | VAV_TOP WITH REHEAT Supply Flow Rate [cfm] | 20383.6256 | 19578.4512 | [8 empty] | 2021-05-06
NE_LO_Supply Air Temp. Reset Flag | Supply Air Temp. Reset Flag | Yes | Yes | [8 empty] | 2021-05-06
NE_LO_CAV_BAS OA Rate [cfm] | CAV_BAS OA Rate [cfm] | 2542.8255 | 2542.8255 | [8 empty] | 2021-05-06
NE_LO_VAV_BOT WITH REHEAT OA Rate [cfm] | VAV_BOT WITH REHEAT OA Rate [cfm] | 5377.8022 | 4302.174 | [8 empty] | 2021-05-06
NE_LO_VAV_MID WITH REHEAT OA Rate [cfm] | VAV_MID WITH REHEAT OA Rate [cfm] | 53777.9373 | 43021.7396 | [8 empty] | 2021-05-06
NE_LO_VAV_TOP WITH REHEAT OA Rate [cfm] | VAV_TOP WITH REHEAT OA Rate [cfm] | 5377.8022 | 4302.174 | [8 empty] | 2021-05-06
NE_LO_AIRLOOP DATACENTER BASEMENT OA Rate [cfm] | AIRLOOP DATACENTER BASEMENT OA Rate [cfm] | 716.9654 | 716.9654 | [8 empty] | 2021-05-06
NE_LO_VAV_bot_WITH_REHEAT ERV Flag | VAV_bot_WITH_REHEAT ERV Flag | Yes | Yes | [8 empty] | 2021-05-06
NE_LO_VAV_mid_WITH_REHEAT ERV Flag | VAV_mid_WITH_REHEAT ERV Flag | Yes | Yes | [8 empty] | 2021-05-06
NE_LO_VAV_top_WITH_REHEAT ERV Flag | VAV_top_WITH_REHEAT ERV Flag | Yes | Yes | [8 empty] | 2021-05-06
NE_LO_COOLSYS1 CHILLER1 Capacity [ton] | COOLSYS1 CHILLER1 Capacity [ton] | 443.5962 | 399.8264 | [8 empty] | 2021-05-06
NE_LO_COOLSYS1 CHILLER2 Capacity [ton] | COOLSYS1 CHILLER2 Capacity [ton] | 443.5962 | 399.8264 | [8 empty] | 2021-05-06
NE_LO_TOWERWATERSYS COOLTOWER 1 Capacity [ton] | TOWERWATERSYS COOLTOWER 1 Capacity [ton] | 421.049 | 379.502 | [8 empty] | 2021-05-06
NE_LO_TOWERWATERSYS COOLTOWER 2 Capacity [ton] | TOWERWATERSYS COOLTOWER 2 Capacity [ton] | 421.049 | 379.502 | [8 empty] | 2021-05-06
NE_LO_HEATSYS1 BOILER Capacity [MMBTU/h] | HEATSYS1 BOILER Capacity [MMBTU/h] | 5106.9895 | 4517.6768 | [8 empty] | 2021-05-06
NE_LO_COOLSYS1 PUMP Flow Rate [gal/min] | COOLSYS1 PUMP Flow Rate [gal/min] | 0 | 0 | [8 empty] | 2021-05-06
NE_LO_COOLSYS1 CHILLER1 PUMP Flow Rate [gal/min] | COOLSYS1 CHILLER1 PUMP Flow Rate [gal/min] | 699.0563 | 629.9949 | [8 empty] | 2021-05-06
NE_LO_COOLSYS1 CHILLER2 PUMP Flow Rate [gal/min] | COOLSYS1 CHILLER2 PUMP Flow Rate [gal/min] | 699.0563 | 629.9949 | [8 empty] | 2021-05-06
NE_LO_COOLSYS1 PUMP SECONDARY Flow Rate [gal/min] | COOLSYS1 PUMP SECONDARY Flow Rate [gal/min] | 1398.1126 | 1259.9897 | [8 empty] | 2021-05-06
NE_LO_HEATSYS1 PUMP Flow Rate [gal/min] | HEATSYS1 PUMP Flow Rate [gal/min] | 1048.277 | 927.3121 | [8 empty] | 2021-05-06
NE_LO_TOWERWATERSYS PUMP Flow Rate [gal/min] | TOWERWATERSYS PUMP Flow Rate [gal/min] | 2447.2899 | 2205.8895 | [8 empty] | 2021-05-06
NE_LO_PLANT CIRC PUMP Flow Rate [gal/min] | PLANT CIRC PUMP Flow Rate [gal/min] | 212.7842 | 211.9315 | [8 empty] | 2021-05-06
NE_LO_COOLSYS1 PUMP SECONDARY Pressure setpoint reset [yes,no] | COOLSYS1 PUMP SECONDARY Pressure setpoint reset [yes,no] | pump_ride_on_curve | pump_ride_on_curve | [8 empty] | 2021-05-06
NE_LO_COOLSYS1 CHILLER1 PUMP Pump Power [hp] | COOLSYS1 CHILLER1 PUMP Pump Power [hp] | 3.7712 | 3.365 | [8 empty] | 2021-05-06
NE_LO_COOLSYS1 CHILLER2 PUMP Pump Power [hp] | COOLSYS1 CHILLER2 PUMP Pump Power [hp] | 3.7712 | 3.365 | [8 empty] | 2021-05-06
NE_LO_COOLSYS1 PUMP SECONDARY Pump Power [hp] | COOLSYS1 PUMP SECONDARY Pump Power [hp] | 22.627 | 20.1897 | [8 empty] | 2021-05-06
NE_LO_HEATSYS1 PUMP Pump Power [hp] | HEATSYS1 PUMP Pump Power [hp] | 22.6591 | 19.8459 | [8 empty] | 2021-05-06
NE_LO_TOWERWATERSYS PUMP Pump Power [hp] | TOWERWATERSYS PUMP Pump Power [hp] | 43.8175 | 39.103 | [8 empty] | 2021-05-06
NE_LO_PLANT CIRC PUMP Pump Power [hp] | PLANT CIRC PUMP Pump Power [hp] | 4.5916 | 4.5279 | [8 empty] | 2021-05-06
NE_LO_Datacenter PLANT CIRC PUMP Pump Power [hp] | Datacenter PLANT CIRC PUMP Pump Power [hp] | 4.5916 | 4.5279 | [8 empty] | 2021-05-06
NE_LO_ZN_VAV_BOXes_Max_Reheat_Water_Flow_GPM | ZN_VAV_BOXes_Max_Reheat_Water_Flow_GPM | 525.0711 | 505.4102 | [8 empty] | 2021-05-06
NE_LO_COOLSYS1 PUMP SECONDARY VSD | COOLSYS1 PUMP SECONDARY VSD | No | No | [8 empty] | 2021-05-06
NE_LO_HEATSYS1 PUMP VSD | HEATSYS1 PUMP VSD | No | No | [8 empty] | 2021-05-06
NE_LO_DATACENTER BASEMENT Cooling Capacity [ton] | DATACENTER BASEMENT Cooling Capacity [ton] | 123.7231 | 123.3584 | [8 empty] | 2021-05-06
NE_LO_DATACENTER BOT Cooling Capacity [ton] | DATACENTER BOT Cooling Capacity [ton] | 2.7769 | 2.7527 | [8 empty] | 2021-05-06
NE_LO_DATACENTER MID Cooling Capacity [ton] | DATACENTER MID Cooling Capacity [ton] | 26.6528 | 26.4378 | [8 empty] | 2021-05-06
NE_LO_DATACENTER TOP Cooling Capacity [ton] | DATACENTER TOP Cooling Capacity [ton] | 2.7156 | 2.6949 | [8 empty] | 2021-05-06
id | item | Zone5A(NE-Omaha-NE) ASHRAE901-state_STD2016 | Zone5A(NE-Omaha-NE) ASHRAE901-state_STD2019 | [8 empty] | 2021-05-06
NE_RS_PSZ-AC:1 Cooling Capacity [ton] | PSZ-AC:1 Cooling Capacity [ton] | 10.9023 | 10.5404 | [8 empty] | 2021-05-06
NE_RS_PSZ-AC:2 Cooling Capacity [ton] | PSZ-AC:2 Cooling Capacity [ton] | 53.2732 | 50.0864 | [8 empty] | 2021-05-06
NE_RS_PSZ-AC:3 Cooling Capacity [ton] | PSZ-AC:3 Cooling Capacity [ton] | 6.9262 | 6.7591 | [8 empty] | 2021-05-06
NE_RS_PSZ-AC:4 Cooling Capacity [ton] | PSZ-AC:4 Cooling Capacity [ton] | 5.6608 | 5.4883 | [8 empty] | 2021-05-06
NE_RS_PSZ-AC:1 Supply Flow Rate [cfm] | PSZ-AC:1 Supply Flow Rate [cfm] | 4153.0048 | 3898.7392 | [8 empty] | 2021-05-06
NE_RS_PSZ-AC:2 Supply Flow Rate [cfm] | PSZ-AC:2 Supply Flow Rate [cfm] | 15997.544 | 15022.8592 | [8 empty] | 2021-05-06
NE_RS_PSZ-AC:3 Supply Flow Rate [cfm] | PSZ-AC:3 Supply Flow Rate [cfm] | 2394.3344 | 2309.5792 | [8 empty] | 2021-05-06
NE_RS_PSZ-AC:4 Supply Flow Rate [cfm] | PSZ-AC:4 Supply Flow Rate [cfm] | 1822.2368 | 1758.6704 | [8 empty] | 2021-05-06
NE_RS_PSZ-AC:1 OA Rate [cfm] | PSZ-AC:1 OA Rate [cfm] | 490.669 | 490.669 | [8 empty] | 2021-05-06
NE_RS_PSZ-AC:2 OA Rate [cfm] | PSZ-AC:2 OA Rate [cfm] | 4005.1282 | 4005.1282 | [8 empty] | 2021-05-06
NE_RS_PSZ-AC:3 OA Rate [cfm] | PSZ-AC:3 OA Rate [cfm] | 377.3937 | 377.3937 | [8 empty] | 2021-05-06
NE_RS_PSZ-AC:4 OA Rate [cfm] | PSZ-AC:4 OA Rate [cfm] | 377.3937 | 377.3937 | [8 empty] | 2021-05-06
NE_RS_PSZ-AC:1 OA Damper [gravity, motorized] | PSZ-AC:1 OA Damper [gravity, motorized] | motorized | motorized | [8 empty] | 2021-05-06
NE_RS_PSZ-AC:2 OA Damper [gravity, motorized] | PSZ-AC:2 OA Damper [gravity, motorized] | motorized | motorized | [8 empty] | 2021-05-06
NE_RS_PSZ-AC:3 OA Damper [gravity, motorized] | PSZ-AC:3 OA Damper [gravity, motorized] | motorized | motorized | [8 empty] | 2021-05-06
NE_RS_PSZ-AC:4 OA Damper [gravity, motorized] | PSZ-AC:4 OA Damper [gravity, motorized] | motorized | motorized | [8 empty] | 2021-05-06
NE_RS_PSZ-AC:1 Heating Capacity [kBtu/hr] | PSZ-AC:1 Heating Capacity [kBtu/hr] | 187.3462 | 176.8205 | [8 empty] | 2021-05-06
NE_RS_PSZ-AC:2 Heating Capacity [kBtu/hr] | PSZ-AC:2 Heating Capacity [kBtu/hr] | 876.5082 | 838.4522 | [8 empty] | 2021-05-06
NE_RS_PSZ-AC:3 Heating Capacity [kBtu/hr] | PSZ-AC:3 Heating Capacity [kBtu/hr] | 115.5507 | 112.8213 | [8 empty] | 2021-05-06
NE_RS_PSZ-AC:4 Heating Capacity [kBtu/hr] | PSZ-AC:4 Heating Capacity [kBtu/hr] | 95.4078 | 92.5309 | [8 empty] | 2021-05-06
id | item | Zone5A(NE-Omaha-NE) ASHRAE901-state_STD2016 | Zone5A(NE-Omaha-NE) ASHRAE901-state_STD2019 | [8 empty] | 2021-05-06
NE_PS_VAV_POD_1 Cooling Capacity [ton] | VAV_POD_1 Cooling Capacity [ton] | 19.9643 | 19.2002 | [8 empty] | 2021-05-06
NE_PS_VAV_POD_2 Cooling Capacity [ton] | VAV_POD_2 Cooling Capacity [ton] | 19.8238 | 18.9487 | [8 empty] | 2021-05-06
NE_PS_VAV_POD_3 Cooling Capacity [ton] | VAV_POD_3 Cooling Capacity [ton] | 18.3369 | 17.3786 | [8 empty] | 2021-05-06
NE_PS_VAV_OTHER Cooling Capacity [ton] | VAV_OTHER Cooling Capacity [ton] | 28.104 | 26.5221 | [8 empty] | 2021-05-06
NE_PS_PSZ-AC_1:6 Cooling Capacity [ton] | PSZ-AC_1:6 Cooling Capacity [ton] | 8.8131 | 8.4334 | [8 empty] | 2021-05-06
NE_PS_PSZ-AC_2:5 Cooling Capacity [ton] | PSZ-AC_2:5 Cooling Capacity [ton] | 5.8031 | 5.7759 | [8 empty] | 2021-05-06
NE_PS_PSZ-AC_2:7 Cooling Capacity [ton] | PSZ-AC_2:7 Cooling Capacity [ton] | 10.5074 | 10.5074 | [8 empty] | 2021-05-06
NE_PS_VAV_POD_1 Supply Flow Rate [cfm] | VAV_POD_1 Supply Flow Rate [cfm] | 5996.4304 | 5763.3536 | [8 empty] | 2021-05-06
NE_PS_VAV_POD_2 Supply Flow Rate [cfm] | VAV_POD_2 Supply Flow Rate [cfm] | 5954.0528 | 5678.5984 | [8 empty] | 2021-05-06
NE_PS_VAV_POD_3 Supply Flow Rate [cfm] | VAV_POD_3 Supply Flow Rate [cfm] | 5509.088 | 5212.4448 | [8 empty] | 2021-05-06
NE_PS_VAV_OTHER Supply Flow Rate [cfm] | VAV_OTHER Supply Flow Rate [cfm] | 8433.1424 | 7966.9888 | [8 empty] | 2021-05-06
NE_PS_PSZ-AC_2:5 Supply Flow Rate [cfm] | PSZ-AC_2:5 Supply Flow Rate [cfm] | 1737.4816 | 1737.4816 | [8 empty] | 2021-05-06
NE_PS_PSZ-AC_1:6 Supply Flow Rate [cfm] | PSZ-AC_1:6 Supply Flow Rate [cfm] | 2648.6 | 2521.4672 | [8 empty] | 2021-05-06
NE_PS_PSZ-AC_2:7 Supply Flow Rate [cfm] | PSZ-AC_2:7 Supply Flow Rate [cfm] | 3157.1312 | 3157.1312 | [8 empty] | 2021-05-06
NE_PS_Supply Air Temp. Reset Flag | Supply Air Temp. Reset Flag | Yes | Yes | [8 empty] | 2021-05-06
NE_PS_VAV_POD_1 OA Rate [cfm] | VAV_POD_1 OA Rate [cfm] | 5987.9761 | 5761.6797 | [8 empty] | 2021-05-06
NE_PS_VAV_POD_2 OA Rate [cfm] | VAV_POD_2 OA Rate [cfm] | 5948.798 | 5686.2052 | [8 empty] | 2021-05-06
NE_PS_VAV_POD_3 OA Rate [cfm] | VAV_POD_3 OA Rate [cfm] | 5499.9344 | 5215.0298 | [8 empty] | 2021-05-06
NE_PS_VAV_OTHER OA Rate [cfm] | VAV_OTHER OA Rate [cfm] | 3736.1787 | 2988.8921 | [8 empty] | 2021-05-06
NE_PS_PSZ-AC_2:5 OA Rate [cfm] | PSZ-AC_2:5 OA Rate [cfm] | 1152.7343 | 1152.7343 | [8 empty] | 2021-05-06
NE_PS_PSZ-AC_1:6 OA Rate [cfm] | PSZ-AC_1:6 OA Rate [cfm] | 539.9118 | 539.9118 | [8 empty] | 2021-05-06
NE_PS_PSZ-AC_2:7 OA Rate [cfm] | PSZ-AC_2:7 OA Rate [cfm] | 3153.0841 | 3153.0841 | [8 empty] | 2021-05-06
NE_PS_VAV_POD_1 OA Damper [gravity, motorized] | VAV_POD_1 OA Damper [gravity, motorized] | motorized | motorized | [8 empty] | 2021-05-06
NE_PS_VAV_POD_2 OA Damper [gravity, motorized] | VAV_POD_2 OA Damper [gravity, motorized] | motorized | motorized | [8 empty] | 2021-05-06
NE_PS_VAV_POD_3 OA Damper [gravity, motorized] | VAV_POD_3 OA Damper [gravity, motorized] | motorized | motorized | [8 empty] | 2021-05-06
NE_PS_VAV_OTHER OA Damper [gravity, motorized] | VAV_OTHER OA Damper [gravity, motorized] | motorized | motorized | [8 empty] | 2021-05-06
NE_PS_PSZ-AC_2:5 OA Damper [gravity, motorized] | PSZ-AC_2:5 OA Damper [gravity, motorized] | motorized | motorized | [8 empty] | 2021-05-06
NE_PS_PSZ-AC_1:6 OA Damper [gravity, motorized] | PSZ-AC_1:6 OA Damper [gravity, motorized] | motorized | motorized | [8 empty] | 2021-05-06
NE_PS_PSZ-AC_2:7 OA Damper [gravity, motorized] | PSZ-AC_2:7 OA Damper [gravity, motorized] | motorized | motorized | [8 empty] | 2021-05-06
NE_PS_VAV_POD_1 (economizer) | VAV_POD_1 (economizer) | DifferentialDryBulb | DifferentialDryBulb | [8 empty] | 2021-05-06
NE_PS_VAV_POD_2 (economizer) | VAV_POD_2 (economizer) | DifferentialDryBulb | DifferentialDryBulb | [8 empty] | 2021-05-06
NE_PS_VAV_POD_3 (economizer) | VAV_POD_3 (economizer) | DifferentialDryBulb | DifferentialDryBulb | [8 empty] | 2021-05-06
NE_PS_VAV_OTHER (economizer) | VAV_OTHER (economizer) | DifferentialDryBulb | DifferentialDryBulb | [8 empty] | 2021-05-06
NE_PS_PSZ-AC_2:5 (economizer) | PSZ-AC_2:5 (economizer) | DifferentialDryBulb | DifferentialDryBulb | [8 empty] | 2021-05-06
NE_PS_PSZ-AC_1:6 (economizer) | PSZ-AC_1:6 (economizer) | DifferentialDryBulb | DifferentialDryBulb | [8 empty] | 2021-05-06
NE_PS_PSZ-AC_2:7 (economizer) | PSZ-AC_2:7 (economizer) | DifferentialDryBulb | DifferentialDryBulb | [8 empty] | 2021-05-06
NE_PS_VAV_Pod_1_ERV Flag | VAV_Pod_1_ERV Flag | Yes | Yes | [8 empty] | 2021-05-06
NE_PS_VAV_Pod_2_ERV Flag | VAV_Pod_2_ERV Flag | Yes | Yes | [8 empty] | 2021-05-06
NE_PS_VAV_Pod_3_ERV Flag | VAV_Pod_3_ERV Flag | Yes | Yes | [8 empty] | 2021-05-06
NE_PS_VAV_OTHER_ERV Flag | VAV_OTHER_ERV Flag | Yes | Yes | [8 empty] | 2021-05-06
NE_PS_PSZ_AC_2_5_ERV Flag | PSZ_AC_2_5_ERV Flag | No | No | [8 empty] | 2021-05-06
NE_PS_PSZ_AC_2_7_ERV Flag | PSZ_AC_2_7_ERV Flag | Yes | Yes | [8 empty] | 2021-05-06
NE_PS_HEATSYS1 Capacity [MMBTU/h] | HEATSYS1 Capacity [MMBTU/h] | 1.2787 | 1.2242 | [8 empty] | 2021-05-06
NE_PS_HEATSYS1 Flow Rate [gal/min] | HEATSYS1 Flow Rate [gal/min] | 131.2386 | 125.6409 | [8 empty] | 2021-05-06
NE_PS_VAV_POD_1 Fan Power [hp] | VAV_POD_1 Fan Power [hp] | 8.8385 | 8.5002 | [8 empty] | 2021-05-06
NE_PS_VAV_POD_2 Fan Power [hp] | VAV_POD_2 Fan Power [hp] | 8.7763 | 8.3888 | [8 empty] | 2021-05-06
NE_PS_VAV_POD_3 Fan Power [hp] | VAV_POD_3 Fan Power [hp] | 8.118 | 7.6938 | [8 empty] | 2021-05-06
NE_PS_VAV_OTHER Fan Power [hp] | VAV_OTHER Fan Power [hp] | 12.3478 | 11.6527 | [8 empty] | 2021-05-06
NE_PS_HEATSYS1 Pump Power [hp] | HEATSYS1 Pump Power [hp] | 2.8368 | 2.6889 | [8 empty] | 2021-05-06
NE_PS_PSZ-AC_1:6 Heating Capacity [kBtu/hr] | PSZ-AC_1:6 Heating Capacity [kBtu/hr] | 220.5792 | 212.009 | [8 empty] | 2021-05-06
NE_PS_PSZ-AC_2:5 Heating Capacity [kBtu/hr] | PSZ-AC_2:5 Heating Capacity [kBtu/hr] | 153.9302 | 153.6388 | [8 empty] | 2021-05-06
NE_PS_PSZ-AC_2:7 Heating Capacity [kBtu/hr] | PSZ-AC_2:7 Heating Capacity [kBtu/hr] | 363.5068 | 363.5068 | [8 empty] | 2021-05-06
NE_PS_ZN_VAV_BOXes_Max_Reheat_Water_Flow_GPM | ZN_VAV_BOXes_Max_Reheat_Water_Flow_GPM | 80.1449 | 77.0235 | [8 empty] | 2021-05-06
id | item | Zone5A(NE-Omaha-NE) ASHRAE901-state_STD2016 | Zone5A(NE-Omaha-NE) ASHRAE901-state_STD2019 | [8 empty] | 2021-05-06
NE_SH_SAC_FRONTOFFICE Cooling Capacity [ton] | SAC_FRONTOFFICE Cooling Capacity [ton] | 2.5359 | 2.4281 | [8 empty] | 2021-05-06
NE_SH_SAC_FRONTLOUNGE Cooling Capacity [ton] | SAC_FRONTLOUNGE Cooling Capacity [ton] | 6.3814 | 6.0645 | [8 empty] | 2021-05-06
NE_SH_SAC_MEETINGROOM Cooling Capacity [ton] | SAC_MEETINGROOM Cooling Capacity [ton] | 3.0361 | 2.9332 | [8 empty] | 2021-05-06
NE_SH_SAC_EXC_EMPLGE_RESTRM Cooling Capacity [ton] | SAC_EXC_EMPLGE_RESTRM Cooling Capacity [ton] | 6.2945 | 6.2401 | [8 empty] | 2021-05-06
NE_SH_SAC_FO_ADDAQ SUPPLY FAN Supply Flow Rate [cfm] | SAC_FO_ADDAQ SUPPLY FAN Supply Flow Rate [cfm] | 826.3632 | 762.7968 | [8 empty] | 2021-05-06
NE_SH_SAC_FL_ADDAQ SUPPLY FAN Supply Flow Rate [cfm] | SAC_FL_ADDAQ SUPPLY FAN Supply Flow Rate [cfm] | 1906.992 | 1822.2368 | [8 empty] | 2021-05-06
NE_SH_SAC_MR_ADDAQ SUPPLY FAN Supply Flow Rate [cfm] | SAC_MR_ADDAQ SUPPLY FAN Supply Flow Rate [cfm] | 911.1184 | 889.9296 | [8 empty] | 2021-05-06
NE_SH_SAC_EXC_ADDAQ SUPPLY FAN Supply Flow Rate [cfm] | SAC_EXC_ADDAQ SUPPLY FAN Supply Flow Rate [cfm] | 2267.2016 | 2246.0128 | [8 empty] | 2021-05-06
NE_SH_SAC_Exc_EmpLge_RestRm OA Rate [cfm] | SAC_Exc_EmpLge_RestRm OA Rate [cfm] | 199.9928 | 199.9928 | [8 empty] | 2021-05-06
NE_SH_SAC_FrontLounge OA Rate [cfm] | SAC_FrontLounge OA Rate [cfm] | 500.0133 | 500.0133 | [8 empty] | 2021-05-06
NE_SH_SAC_FrontOffice OA Rate [cfm] | SAC_FrontOffice OA Rate [cfm] | 119.2938 | 119.2938 | [8 empty] | 2021-05-06
NE_SH_SAC_MeetingRoom OA Rate [cfm] | SAC_MeetingRoom OA Rate [cfm] | 267.7629 | 267.7629 | [8 empty] | 2021-05-06
NE_SH_SAC_FrontLounge OA Damper [gravity, motorized] | SAC_FrontLounge OA Damper [gravity, motorized] | motorized | motorized | [8 empty] | 2021-05-06
NE_SH_SAC_FrontOffice (economizer) | SAC_FrontOffice (economizer) | No | No | [8 empty] | 2021-05-06
NE_SH_SAC_FrontLounge (economizer) | SAC_FrontLounge (economizer) | DifferentialDryBulb | DifferentialDryBulb | [8 empty] | 2021-05-06
NE_SH_SAC_MeetingRoom (economizer) | SAC_MeetingRoom (economizer) | No | No | [8 empty] | 2021-05-06
NE_SH_SAC_Exc_EmpLge_RestRm (economizer) | SAC_Exc_EmpLge_RestRm (economizer) | DifferentialDryBulb | DifferentialDryBulb | [8 empty] | 2021-05-06
NE_SH_SAC_FRONTOFFICE Heating Capacity [kBtu/hr] | SAC_FRONTOFFICE Heating Capacity [kBtu/hr] | 38.926 | 36.8946 | [8 empty] | 2021-05-06
NE_SH_SAC_FRONTLOUNGE Heating Capacity [kBtu/hr] | SAC_FRONTLOUNGE Heating Capacity [kBtu/hr] | 107.9093 | 104.5314 | [8 empty] | 2021-05-06
NE_SH_SAC_MEETINGROOM Heating Capacity [kBtu/hr] | SAC_MEETINGROOM Heating Capacity [kBtu/hr] | 53.7225 | 52.6251 | [8 empty] | 2021-05-06
NE_SH_SAC_EXC_EMPLGE_RESTRM Heating Capacity [kBtu/hr] | SAC_EXC_EMPLGE_RESTRM Heating Capacity [kBtu/hr] | 96.1165 | 95.4468 | [8 empty] | 2021-05-06
id | item | Zone5A(NE-Omaha-NE) ASHRAE901-state_STD2016 | Zone5A(NE-Omaha-NE) ASHRAE901-state_STD2019 | [8 empty] | 2021-05-06
NE_MA_SPLIT GSW COOLING COIL Cooling Capacity [ton] | SPLIT GSW COOLING COIL Cooling Capacity [ton] | 0.99512 | 0.98058 | [8 empty] | 2021-05-06
NE_MA_SPLIT GNW COOLING COIL Cooling Capacity [ton] | SPLIT GNW COOLING COIL Cooling Capacity [ton] | 0.95029 | 0.93629 | [8 empty] | 2021-05-06
NE_MA_SPLIT OFFICE COOLING COIL Cooling Capacity [ton] | SPLIT OFFICE COOLING COIL Cooling Capacity [ton] | 1.8113 | 1.7206 | [8 empty] | 2021-05-06
NE_MA_SPLIT GNE COOLING COIL Cooling Capacity [ton] | SPLIT GNE COOLING COIL Cooling Capacity [ton] | 0.83089 | 0.81842 | [8 empty] | 2021-05-06
NE_MA_SPLIT GN1 COOLING COIL Cooling Capacity [ton] | SPLIT GN1 COOLING COIL Cooling Capacity [ton] | 0.69634 | 0.68429 | [8 empty] | 2021-05-06
NE_MA_SPLIT GN2 COOLING COIL Cooling Capacity [ton] | SPLIT GN2 COOLING COIL Cooling Capacity [ton] | 0.69394 | 0.68187 | [8 empty] | 2021-05-06
NE_MA_SPLIT GS1 COOLING COIL Cooling Capacity [ton] | SPLIT GS1 COOLING COIL Cooling Capacity [ton] | 0.73834 | 0.7277 | [8 empty] | 2021-05-06
NE_MA_SPLIT GS2 COOLING COIL Cooling Capacity [ton] | SPLIT GS2 COOLING COIL Cooling Capacity [ton] | 0.76973 | 0.75531 | [8 empty] | 2021-05-06
NE_MA_SPLIT MSW COOLING COIL Cooling Capacity [ton] | SPLIT MSW COOLING COIL Cooling Capacity [ton] | 2.3606 | 2.3276 | [8 empty] | 2021-05-06
NE_MA_SPLIT MNW COOLING COIL Cooling Capacity [ton] | SPLIT MNW COOLING COIL Cooling Capacity [ton] | 2.2898 | 2.258 | [8 empty] | 2021-05-06
NE_MA_SPLIT MSE COOLING COIL Cooling Capacity [ton] | SPLIT MSE COOLING COIL Cooling Capacity [ton] | 2.0439 | 2.0151 | [8 empty] | 2021-05-06
NE_MA_SPLIT MNE COOLING COIL Cooling Capacity [ton] | SPLIT MNE COOLING COIL Cooling Capacity [ton] | 1.8872 | 1.8562 | [8 empty] | 2021-05-06
NE_MA_SPLIT MN1 COOLING COIL Cooling Capacity [ton] | SPLIT MN1 COOLING COIL Cooling Capacity [ton] | 1.5055 | 1.4866 | [8 empty] | 2021-05-06
NE_MA_SPLIT MN2 COOLING COIL Cooling Capacity [ton] | SPLIT MN2 COOLING COIL Cooling Capacity [ton] | 1.4983 | 1.4796 | [8 empty] | 2021-05-06
NE_MA_SPLIT MS1 COOLING COIL Cooling Capacity [ton] | SPLIT MS1 COOLING COIL Cooling Capacity [ton] | 1.6034 | 1.5833 | [8 empty] | 2021-05-06
NE_MA_SPLIT MS2 COOLING COIL Cooling Capacity [ton] | SPLIT MS2 COOLING COIL Cooling Capacity [ton] | 1.5974 | 1.5774 | [8 empty] | 2021-05-06
NE_MA_SPLIT TSW COOLING COIL Cooling Capacity [ton] | SPLIT TSW COOLING COIL Cooling Capacity [ton] | 1.4621 | 1.4444 | [8 empty] | 2021-05-06
NE_MA_SPLIT TNW COOLING COIL Cooling Capacity [ton] | SPLIT TNW COOLING COIL Cooling Capacity [ton] | 1.4198 | 1.4025 | [8 empty] | 2021-05-06
NE_MA_SPLIT TSE COOLING COIL Cooling Capacity [ton] | SPLIT TSE COOLING COIL Cooling Capacity [ton] | 1.3086 | 1.2939 | [8 empty] | 2021-05-06
NE_MA_SPLIT TNE COOLING COIL Cooling Capacity [ton] | SPLIT TNE COOLING COIL Cooling Capacity [ton] | 1.2298 | 1.2168 | [8 empty] | 2021-05-06
NE_MA_SPLIT TN1 COOLING COIL Cooling Capacity [ton] | SPLIT TN1 COOLING COIL Cooling Capacity [ton] | 0.97036 | 0.96067 | [8 empty] | 2021-05-06
NE_MA_SPLIT TN2 COOLING COIL Cooling Capacity [ton] | SPLIT TN2 COOLING COIL Cooling Capacity [ton] | 0.96313 | 0.95361 | [8 empty] | 2021-05-06
NE_MA_SPLIT TS1 COOLING COIL Cooling Capacity [ton] | SPLIT TS1 COOLING COIL Cooling Capacity [ton] | 1.0637 | 1.0526 | [8 empty] | 2021-05-06
NE_MA_SPLIT TS2 COOLING COIL Cooling Capacity [ton] | SPLIT TS2 COOLING COIL Cooling Capacity [ton] | 1.0695 | 1.0581 | [8 empty] | 2021-05-06
NE_MA_Split GN1 Furnace with DX Cooling OA Rate [cfm] | Split GN1 Furnace with DX Cooling OA Rate [cfm] | 54.9913 | 54.9913 | [8 empty] | 2021-05-06
NE_MA_Split GN2 Furnace with DX Cooling OA Rate [cfm] | Split GN2 Furnace with DX Cooling OA Rate [cfm] | 54.9913 | 54.9913 | [8 empty] | 2021-05-06
NE_MA_Split GNE Furnace with DX Cooling OA Rate [cfm] | Split GNE Furnace with DX Cooling OA Rate [cfm] | 54.9913 | 54.9913 | [8 empty] | 2021-05-06
NE_MA_Split GNW Furnace with DX Cooling OA Rate [cfm] | Split GNW Furnace with DX Cooling OA Rate [cfm] | 54.9913 | 54.9913 | [8 empty] | 2021-05-06
NE_MA_Split GS1 Furnace with DX Cooling OA Rate [cfm] | Split GS1 Furnace with DX Cooling OA Rate [cfm] | 54.9913 | 54.9913 | [8 empty] | 2021-05-06
NE_MA_Split GS2 Furnace with DX Cooling OA Rate [cfm] | Split GS2 Furnace with DX Cooling OA Rate [cfm] | 54.9913 | 54.9913 | [8 empty] | 2021-05-06
NE_MA_Split GSW Furnace with DX Cooling OA Rate [cfm] | Split GSW Furnace with DX Cooling OA Rate [cfm] | 56.9945 | 56.9945 | [8 empty] | 2021-05-06
NE_MA_Split MN1 Furnace with DX Cooling OA Rate [cfm] | Split MN1 Furnace with DX Cooling OA Rate [cfm] | 109.9824 | 109.9824 | [8 empty] | 2021-05-06
NE_MA_Split MN2 Furnace with DX Cooling OA Rate [cfm] | Split MN2 Furnace with DX Cooling OA Rate [cfm] | 109.9824 | 109.9824 | [8 empty] | 2021-05-06
NE_MA_Split MNE Furnace with DX Cooling OA Rate [cfm] | Split MNE Furnace with DX Cooling OA Rate [cfm] | 109.9824 | 109.9824 | [8 empty] | 2021-05-06
NE_MA_Split MNW Furnace with DX Cooling OA Rate [cfm] | Split MNW Furnace with DX Cooling OA Rate [cfm] | 109.9824 | 109.9824 | [8 empty] | 2021-05-06
NE_MA_Split MS1 Furnace with DX Cooling OA Rate [cfm] | Split MS1 Furnace with DX Cooling OA Rate [cfm] | 109.9824 | 109.9824 | [8 empty] | 2021-05-06
NE_MA_Split MS2 Furnace with DX Cooling OA Rate [cfm] | Split MS2 Furnace with DX Cooling OA Rate [cfm] | 109.9824 | 109.9824 | [8 empty] | 2021-05-06
NE_MA_Split MSE Furnace with DX Cooling OA Rate [cfm] | Split MSE Furnace with DX Cooling OA Rate [cfm] | 109.9824 | 109.9824 | [8 empty] | 2021-05-06
NE_MA_Split MSW Furnace with DX Cooling OA Rate [cfm] | Split MSW Furnace with DX Cooling OA Rate [cfm] | 109.9824 | 109.9824 | [8 empty] | 2021-05-06
NE_MA_Split Office Furnace with DX Cooling OA Rate [cfm] | Split Office Furnace with DX Cooling OA Rate [cfm] | 80.7372 | 80.7372 | [8 empty] | 2021-05-06
NE_MA_Split TN1 Furnace with DX Cooling OA Rate [cfm] | Split TN1 Furnace with DX Cooling OA Rate [cfm] | 54.9913 | 54.9913 | [8 empty] | 2021-05-06
NE_MA_Split TN2 Furnace with DX Cooling OA Rate [cfm] | Split TN2 Furnace with DX Cooling OA Rate [cfm] | 54.9913 | 54.9913 | [8 empty] | 2021-05-06
NE_MA_Split TNE Furnace with DX Cooling OA Rate [cfm] | Split TNE Furnace with DX Cooling OA Rate [cfm] | 54.9913 | 54.9913 | [8 empty] | 2021-05-06
NE_MA_Split TNW Furnace with DX Cooling OA Rate [cfm] | Split TNW Furnace with DX Cooling OA Rate [cfm] | 54.9913 | 54.9913 | [8 empty] | 2021-05-06
NE_MA_Split TS1 Furnace with DX Cooling OA Rate [cfm] | Split TS1 Furnace with DX Cooling OA Rate [cfm] | 54.9913 | 54.9913 | [8 empty] | 2021-05-06
NE_MA_Split TS2 Furnace with DX Cooling OA Rate [cfm] | Split TS2 Furnace with DX Cooling OA Rate [cfm] | 54.9913 | 54.9913 | [8 empty] | 2021-05-06
NE_MA_Split TSE Furnace with DX Cooling OA Rate [cfm] | Split TSE Furnace with DX Cooling OA Rate [cfm] | 54.9913 | 54.9913 | [8 empty] | 2021-05-06
NE_MA_Split TSW Furnace with DX Cooling OA Rate [cfm] | Split TSW Furnace with DX Cooling OA Rate [cfm] | 54.9913 | 54.9913 | [8 empty] | 2021-05-06
NE_MA_SPLIT GSW HEATING COIL Heating Capacity [kBtu/hr] | SPLIT GSW HEATING COIL Heating Capacity [kBtu/hr] | 11.6831 | 11.7421 | [8 empty] | 2021-05-06
NE_MA_SPLIT GNW HEATING COIL Heating Capacity [kBtu/hr] | SPLIT GNW HEATING COIL Heating Capacity [kBtu/hr] | 11.6061 | 11.6652 | [8 empty] | 2021-05-06
NE_MA_SPLIT OFFICE HEATING COIL Heating Capacity [kBtu/hr] | SPLIT OFFICE HEATING COIL Heating Capacity [kBtu/hr] | 25.1124 | 25.1924 | [8 empty] | 2021-05-06
NE_MA_SPLIT GNE HEATING COIL Heating Capacity [kBtu/hr] | SPLIT GNE HEATING COIL Heating Capacity [kBtu/hr] | 11.5753 | 11.6344 | [8 empty] | 2021-05-06
NE_MA_SPLIT GN1 HEATING COIL Heating Capacity [kBtu/hr] | SPLIT GN1 HEATING COIL Heating Capacity [kBtu/hr] | 8.6209 | 8.6801 | [8 empty] | 2021-05-06
NE_MA_SPLIT GN2 HEATING COIL Heating Capacity [kBtu/hr] | SPLIT GN2 HEATING COIL Heating Capacity [kBtu/hr] | 8.62 | 8.6792 | [8 empty] | 2021-05-06
NE_MA_SPLIT GS1 HEATING COIL Heating Capacity [kBtu/hr] | SPLIT GS1 HEATING COIL Heating Capacity [kBtu/hr] | 8.5544 | 8.6134 | [8 empty] | 2021-05-06
NE_MA_SPLIT GS2 HEATING COIL Heating Capacity [kBtu/hr] | SPLIT GS2 HEATING COIL Heating Capacity [kBtu/hr] | 9.0689 | 9.1288 | [8 empty] | 2021-05-06
NE_MA_SPLIT MSW HEATING COIL Heating Capacity [kBtu/hr] | SPLIT MSW HEATING COIL Heating Capacity [kBtu/hr] | 21.3409 | 21.4701 | [8 empty] | 2021-05-06
NE_MA_SPLIT MNW HEATING COIL Heating Capacity [kBtu/hr] | SPLIT MNW HEATING COIL Heating Capacity [kBtu/hr] | 21.4623 | 21.5915 | [8 empty] | 2021-05-06
NE_MA_SPLIT MSE HEATING COIL Heating Capacity [kBtu/hr] | SPLIT MSE HEATING COIL Heating Capacity [kBtu/hr] | 21.2687 | 21.3979 | [8 empty] | 2021-05-06
NE_MA_SPLIT MNE HEATING COIL Heating Capacity [kBtu/hr] | SPLIT MNE HEATING COIL Heating Capacity [kBtu/hr] | 21.3901 | 21.5193 | [8 empty] | 2021-05-06
NE_MA_SPLIT MN1 HEATING COIL Heating Capacity [kBtu/hr] | SPLIT MN1 HEATING COIL Heating Capacity [kBtu/hr] | 15.0089 | 15.1349 | [8 empty] | 2021-05-06
NE_MA_SPLIT MN2 HEATING COIL Heating Capacity [kBtu/hr] | SPLIT MN2 HEATING COIL Heating Capacity [kBtu/hr] | 15.007 | 15.1331 | [8 empty] | 2021-05-06
NE_MA_SPLIT MS1 HEATING COIL Heating Capacity [kBtu/hr] | SPLIT MS1 HEATING COIL Heating Capacity [kBtu/hr] | 14.8975 | 15.0235 | [8 empty] | 2021-05-06
NE_MA_SPLIT MS2 HEATING COIL Heating Capacity [kBtu/hr] | SPLIT MS2 HEATING COIL Heating Capacity [kBtu/hr] | 14.8956 | 15.0216 | [8 empty] | 2021-05-06
NE_MA_SPLIT TSW HEATING COIL Heating Capacity [kBtu/hr] | SPLIT TSW HEATING COIL Heating Capacity [kBtu/hr] | 14.8661 | 14.928 | [8 empty] | 2021-05-06
NE_MA_SPLIT TNW HEATING COIL Heating Capacity [kBtu/hr] | SPLIT TNW HEATING COIL Heating Capacity [kBtu/hr] | 14.9367 | 14.9987 | [8 empty] | 2021-05-06
NE_MA_SPLIT TSE HEATING COIL Heating Capacity [kBtu/hr] | SPLIT TSE HEATING COIL Heating Capacity [kBtu/hr] | 14.8279 | 14.8899 | [8 empty] | 2021-05-06
NE_MA_SPLIT TNE HEATING COIL Heating Capacity [kBtu/hr] | SPLIT TNE HEATING COIL Heating Capacity [kBtu/hr] | 14.8985 | 14.9605 | [8 empty] | 2021-05-06
NE_MA_SPLIT TN1 HEATING COIL Heating Capacity [kBtu/hr] | SPLIT TN1 HEATING COIL Heating Capacity [kBtu/hr] | 11.4122 | 11.4741 | [8 empty] | 2021-05-06
NE_MA_SPLIT TN2 HEATING COIL Heating Capacity [kBtu/hr] | SPLIT TN2 HEATING COIL Heating Capacity [kBtu/hr] | 11.4112 | 11.4731 | [8 empty] | 2021-05-06
NE_MA_SPLIT TS1 HEATING COIL Heating Capacity [kBtu/hr] | SPLIT TS1 HEATING COIL Heating Capacity [kBtu/hr] | 11.3352 | 11.397 | [8 empty] | 2021-05-06
NE_MA_SPLIT TS2 HEATING COIL Heating Capacity [kBtu/hr] | SPLIT TS2 HEATING COIL Heating Capacity [kBtu/hr] | 11.3341 | 11.3959 | [8 empty] | 2021-05-06
NE_MA_Split_GSW ERV Flag | Split_GSW ERV Flag | Yes | Yes | [8 empty] | 2021-05-06
NE_MA_Split_GNW ERV Flag | Split_GNW ERV Flag | Yes | Yes | [8 empty] | 2021-05-06
NE_MA_Split_GNE ERV Flag | Split_GNE ERV Flag | Yes | Yes | [8 empty] | 2021-05-06
NE_MA_Split_GN1 ERV Flag | Split_GN1 ERV Flag | Yes | Yes | [8 empty] | 2021-05-06
NE_MA_Split_GN2 ERV Flag | Split_GN2 ERV Flag | Yes | Yes | [8 empty] | 2021-05-06
NE_MA_Split_GS1 ERV Flag | Split_GS1 ERV Flag | Yes | Yes | [8 empty] | 2021-05-06
NE_MA_Split_GS2 ERV Flag | Split_GS2 ERV Flag | Yes | Yes | [8 empty] | 2021-05-06
NE_MA_Split_MSW ERV Flag | Split_MSW ERV Flag | Yes | Yes | [8 empty] | 2021-05-06
NE_MA_Split_MNW ERV Flag | Split_MNW ERV Flag | Yes | Yes | [8 empty] | 2021-05-06
NE_MA_Split_MSE ERV Flag | Split_MSE ERV Flag | Yes | Yes | [8 empty] | 2021-05-06
NE_MA_Split_MNE ERV Flag | Split_MNE ERV Flag | Yes | Yes | [8 empty] | 2021-05-06
NE_MA_Split_MN1 ERV Flag | Split_MN1 ERV Flag | Yes | Yes | [8 empty] | 2021-05-06
NE_MA_Split_MN2 ERV Flag | Split_MN2 ERV Flag | Yes | Yes | [8 empty] | 2021-05-06
NE_MA_Split_MS1 ERV Flag | Split_MS1 ERV Flag | Yes | Yes | [8 empty] | 2021-05-06
NE_MA_Split_MS2 ERV Flag | Split_MS2 ERV Flag | Yes | Yes | [8 empty] | 2021-05-06
NE_MA_Split_TSW ERV Flag | Split_TSW ERV Flag | No | No | [8 empty] | 2021-05-06
NE_MA_Split_TNW ERV Flag | Split_TNW ERV Flag | Yes | Yes | [8 empty] | 2021-05-06
NE_MA_Split_TSE ERV Flag | Split_TSE ERV Flag | Yes | Yes | [8 empty] | 2021-05-06
NE_MA_Split_TNE ERV Flag | Split_TNE ERV Flag | Yes | Yes | [8 empty] | 2021-05-06
NE_MA_Split_TN1 ERV Flag | Split_TN1 ERV Flag | Yes | Yes | [8 empty] | 2021-05-06
NE_MA_Split_TN2 ERV Flag | Split_TN2 ERV Flag | Yes | Yes | [8 empty] | 2021-05-06
NE_MA_Split_TS1 ERV Flag | Split_TS1 ERV Flag | Yes | Yes | [8 empty] | 2021-05-06
NE_MA_Split_TS2 ERV Flag | Split_TS2 ERV Flag | Yes | Yes | [8 empty] | 2021-05-06
id | item | Zone5A(NH-Manchester-NH) ASHRAE901-state_STD2016 | Zone5A(NH-Manchester-NH) ASHRAE901-state_STD2019 | Zone6A(NH-Lebanon-NH) ASHRAE901-state_STD2016 | Zone6A(NH-Lebanon-NH) ASHRAE901-state_STD2019 | [6 empty] | 2021-05-06
NH_SO_PSZ-AC:1 Cooling Capacity [ton] | PSZ-AC:1 Cooling Capacity [ton] | 1.7533 | 1.6606 | 1.6922 | 1.5916 | [6 empty] | 2021-05-06
NH_SO_PSZ-AC:2 Cooling Capacity [ton] | PSZ-AC:2 Cooling Capacity [ton] | 1.5062 | 1.4441 | 1.4412 | 1.3643 | [6 empty] | 2021-05-06
NH_SO_PSZ-AC:3 Cooling Capacity [ton] | PSZ-AC:3 Cooling Capacity [ton] | 1.0374 | 0.99961 | 1.0044 | 0.93942 | [6 empty] | 2021-05-06
NH_SO_PSZ-AC:4 Cooling Capacity [ton] | PSZ-AC:4 Cooling Capacity [ton] | 1.4269 | 1.3432 | 1.3518 | 1.2621 | [6 empty] | 2021-05-06
NH_SO_PSZ-AC:5 Cooling Capacity [ton] | PSZ-AC:5 Cooling Capacity [ton] | 1.266 | 1.226 | 1.2468 | 1.181 | [6 empty] | 2021-05-06
NH_SO_PSZ-AC:1 Supply Flow Rate [cfm] | PSZ-AC:1 Supply Flow Rate [cfm] | 635.664 | 593.2864 | 635.664 | 593.2864 | [6 empty] | 2021-05-06
NH_SO_PSZ-AC:2 Supply Flow Rate [cfm] | PSZ-AC:2 Supply Flow Rate [cfm] | 550.9088 | 529.72 | 550.9088 | 508.5312 | [6 empty] | 2021-05-06
NH_SO_PSZ-AC:3 Supply Flow Rate [cfm] | PSZ-AC:3 Supply Flow Rate [cfm] | 444.9648 | 423.776 | 444.9648 | 423.776 | [6 empty] | 2021-05-06
NH_SO_PSZ-AC:4 Supply Flow Rate [cfm] | PSZ-AC:4 Supply Flow Rate [cfm] | 529.72 | 487.3424 | 508.5312 | 466.1536 | [6 empty] | 2021-05-06
NH_SO_PSZ-AC:5 Supply Flow Rate [cfm] | PSZ-AC:5 Supply Flow Rate [cfm] | 529.72 | 508.5312 | 550.9088 | 508.5312 | [6 empty] | 2021-05-06
NH_SO_PSZ-AC:1 OA Rate [cfm] | PSZ-AC:1 OA Rate [cfm] | 136.9178 | 136.9178 | 136.9178 | 136.9178 | [6 empty] | 2021-05-06
NH_SO_PSZ-AC:2 OA Rate [cfm] | PSZ-AC:2 OA Rate [cfm] | 103.7925 | 103.7925 | 103.7925 | 103.7925 | [6 empty] | 2021-05-06
NH_SO_PSZ-AC:3 OA Rate [cfm] | PSZ-AC:3 OA Rate [cfm] | 61.5711 | 61.5711 | 61.5711 | 61.5711 | [6 empty] | 2021-05-06
NH_SO_PSZ-AC:4 OA Rate [cfm] | PSZ-AC:4 OA Rate [cfm] | 103.7925 | 103.7925 | 103.7925 | 103.7925 | [6 empty] | 2021-05-06
NH_SO_PSZ-AC:5 OA Rate [cfm] | PSZ-AC:5 OA Rate [cfm] | 61.5711 | 61.5711 | 61.5711 | 61.5711 | [6 empty] | 2021-05-06
NH_SO_PSZ-AC:1 heating Capacity [kBtu/hr] | PSZ-AC:1 heating Capacity [kBtu/hr] | 15.1378 | 15.1378 | 16.3197 | 16.3197 | [6 empty] | 2021-05-06
NH_SO_PSZ-AC:2 heating Capacity [kBtu/hr] | PSZ-AC:2 heating Capacity [kBtu/hr] | 20.5643 | 20.3374 | 21.4578 | 21.1948 | [6 empty] | 2021-05-06
NH_SO_PSZ-AC:3 heating Capacity [kBtu/hr] | PSZ-AC:3 heating Capacity [kBtu/hr] | 12.5127 | 12.3872 | 12.9788 | 12.8337 | [6 empty] | 2021-05-06
NH_SO_PSZ-AC:4 heating Capacity [kBtu/hr] | PSZ-AC:4 heating Capacity [kBtu/hr] | 20.4618 | 20.2682 | 21.2115 | 21.002 | [6 empty] | 2021-05-06
NH_SO_PSZ-AC:5 heating Capacity [kBtu/hr] | PSZ-AC:5 heating Capacity [kBtu/hr] | 12.5681 | 12.4372 | 12.9788 | 12.8337 | [6 empty] | 2021-05-06
id | item | Zone5A(NH-Manchester-NH) ASHRAE901-state_STD2016 | Zone5A(NH-Manchester-NH) ASHRAE901-state_STD2019 | Zone6A(NH-Lebanon-NH) ASHRAE901-state_STD2016 | Zone6A(NH-Lebanon-NH) ASHRAE901-state_STD2019 | [6 empty] | 2021-05-06
NH_LO_CAV_BAS Supply Flow Rate [cfm] | CAV_BAS Supply Flow Rate [cfm] | 11611.4624 | 10742.7216 | 11823.3504 | 10933.4208 | [6 empty] | 2021-05-06
NH_LO_VAV_BOT WITH REHEAT Supply Flow Rate [cfm] | VAV_BOT WITH REHEAT Supply Flow Rate [cfm] | 19853.9056 | 18921.5984 | 19917.472 | 18815.6544 | [6 empty] | 2021-05-06
NH_LO_VAV_MID WITH REHEAT Supply Flow Rate [cfm] | VAV_MID WITH REHEAT Supply Flow Rate [cfm] | 185465.5667 | 176651.0259 | 185338.4339 | 174638.0899 | [6 empty] | 2021-05-06
NH_LO_VAV_TOP WITH REHEAT Supply Flow Rate [cfm] | VAV_TOP WITH REHEAT Supply Flow Rate [cfm] | 19430.1296 | 18646.144 | 19472.5072 | 18455.4448 | [6 empty] | 2021-05-06
NH_LO_Supply Air Temp. Reset Flag | Supply Air Temp. Reset Flag | Yes | Yes | Yes | Yes | [6 empty] | 2021-05-06
NH_LO_CAV_BAS OA Rate [cfm] | CAV_BAS OA Rate [cfm] | 2542.8255 | 2542.8255 | 2542.8255 | 2542.8255 | [6 empty] | 2021-05-06
NH_LO_VAV_BOT WITH REHEAT OA Rate [cfm] | VAV_BOT WITH REHEAT OA Rate [cfm] | 5377.8022 | 4302.174 | 5377.8022 | 4302.174 | [6 empty] | 2021-05-06
NH_LO_VAV_MID WITH REHEAT OA Rate [cfm] | VAV_MID WITH REHEAT OA Rate [cfm] | 53777.9373 | 43021.7396 | 53777.9373 | 43021.7396 | [6 empty] | 2021-05-06
NH_LO_VAV_TOP WITH REHEAT OA Rate [cfm] | VAV_TOP WITH REHEAT OA Rate [cfm] | 5377.8022 | 4302.174 | 5377.8022 | 4302.174 | [6 empty] | 2021-05-06
NH_LO_AIRLOOP DATACENTER BASEMENT OA Rate [cfm] | AIRLOOP DATACENTER BASEMENT OA Rate [cfm] | 716.9654 | 716.9654 | 716.9654 | 716.9654 | [6 empty] | 2021-05-06
NH_LO_VAV_bot_WITH_REHEAT ERV Flag | VAV_bot_WITH_REHEAT ERV Flag | Yes | Yes | Yes | Yes | [6 empty] | 2021-05-06
NH_LO_VAV_mid_WITH_REHEAT ERV Flag | VAV_mid_WITH_REHEAT ERV Flag | Yes | Yes | Yes | Yes | [6 empty] | 2021-05-06
NH_LO_VAV_top_WITH_REHEAT ERV Flag | VAV_top_WITH_REHEAT ERV Flag | Yes | Yes | Yes | Yes | [6 empty] | 2021-05-06
NH_LO_COOLSYS1 CHILLER1 Capacity [ton] | COOLSYS1 CHILLER1 Capacity [ton] | 387.0715 | 352.7438 | 371.5597 | 336.4337 | [6 empty] | 2021-05-06
NH_LO_COOLSYS1 CHILLER2 Capacity [ton] | COOLSYS1 CHILLER2 Capacity [ton] | 387.0715 | 352.7438 | 371.5597 | 336.4337 | [6 empty] | 2021-05-06
NH_LO_TOWERWATERSYS COOLTOWER 1 Capacity [ton] | TOWERWATERSYS COOLTOWER 1 Capacity [ton] | 367.3989 | 334.8176 | 352.7504 | 319.4014 | [6 empty] | 2021-05-06
NH_LO_TOWERWATERSYS COOLTOWER 2 Capacity [ton] | TOWERWATERSYS COOLTOWER 2 Capacity [ton] | 367.3989 | 334.8176 | 352.7504 | 319.4014 | [6 empty] | 2021-05-06
NH_LO_HEATSYS1 BOILER Capacity [MMBTU/h] | HEATSYS1 BOILER Capacity [MMBTU/h] | 4689.556 | 4137.8539 | 4984.3436 | 4352.4497 | [6 empty] | 2021-05-06
NH_LO_COOLSYS1 PUMP Flow Rate [gal/min] | COOLSYS1 PUMP Flow Rate [gal/min] | 0 | 0 | 0 | 0 | [6 empty] | 2021-05-06
NH_LO_COOLSYS1 CHILLER1 PUMP Flow Rate [gal/min] | COOLSYS1 CHILLER1 PUMP Flow Rate [gal/min] | 609.7508 | 555.576 | 585.1828 | 529.7669 | [6 empty] | 2021-05-06
NH_LO_COOLSYS1 CHILLER2 PUMP Flow Rate [gal/min] | COOLSYS1 CHILLER2 PUMP Flow Rate [gal/min] | 609.7508 | 555.576 | 585.1828 | 529.7669 | [6 empty] | 2021-05-06
NH_LO_COOLSYS1 PUMP SECONDARY Flow Rate [gal/min] | COOLSYS1 PUMP SECONDARY Flow Rate [gal/min] | 1219.5017 | 1111.152 | 1170.3657 | 1059.5355 | [6 empty] | 2021-05-06
NH_LO_HEATSYS1 PUMP Flow Rate [gal/min] | HEATSYS1 PUMP Flow Rate [gal/min] | 962.5933 | 849.3491 | 1023.1019 | 893.3971 | [6 empty] | 2021-05-06
NH_LO_TOWERWATERSYS PUMP Flow Rate [gal/min] | TOWERWATERSYS PUMP Flow Rate [gal/min] | 2135.514 | 1946.1027 | 2049.9223 | 1856.0728 | [6 empty] | 2021-05-06
NH_LO_PLANT CIRC PUMP Flow Rate [gal/min] | PLANT CIRC PUMP Flow Rate [gal/min] | 208.1084 | 207.2699 | 209.1086 | 208.0165 | [6 empty] | 2021-05-06
NH_LO_COOLSYS1 PUMP SECONDARY Pressure setpoint reset [yes,no] | COOLSYS1 PUMP SECONDARY Pressure setpoint reset [yes,no] | pump_ride_on_curve | pump_ride_on_curve | pump_ride_on_curve | pump_ride_on_curve | [6 empty] | 2021-05-06
NH_LO_COOLSYS1 CHILLER1 PUMP Pump Power [hp] | COOLSYS1 CHILLER1 PUMP Pump Power [hp] | 3.2894 | 2.9675 | 3.1569 | 2.8296 | [6 empty] | 2021-05-06
NH_LO_COOLSYS1 CHILLER2 PUMP Pump Power [hp] | COOLSYS1 CHILLER2 PUMP Pump Power [hp] | 3.2894 | 2.9675 | 3.1569 | 2.8296 | [6 empty] | 2021-05-06
NH_LO_COOLSYS1 PUMP SECONDARY Pump Power [hp] | COOLSYS1 PUMP SECONDARY Pump Power [hp] | 19.7363 | 17.8048 | 18.9411 | 16.9777 | [6 empty] | 2021-05-06
NH_LO_HEATSYS1 PUMP Pump Power [hp] | HEATSYS1 PUMP Pump Power [hp] | 20.807 | 18.1774 | 22.1149 | 19.1201 | [6 empty] | 2021-05-06
NH_LO_TOWERWATERSYS PUMP Pump Power [hp] | TOWERWATERSYS PUMP Pump Power [hp] | 38.2341 | 34.4983 | 36.7019 | 32.9032 | [6 empty] | 2021-05-06
NH_LO_PLANT CIRC PUMP Pump Power [hp] | PLANT CIRC PUMP Pump Power [hp] | 4.4907 | 4.4283 | 4.5123 | 4.4442 | [6 empty] | 2021-05-06
NH_LO_Datacenter PLANT CIRC PUMP Pump Power [hp] | Datacenter PLANT CIRC PUMP Pump Power [hp] | 4.4907 | 4.4283 | 4.5123 | 4.4442 | [6 empty] | 2021-05-06
NH_LO_ZN_VAV_BOXes_Max_Reheat_Water_Flow_GPM | ZN_VAV_BOXes_Max_Reheat_Water_Flow_GPM | 480.3586 | 461.7612 | 476.0391 | 456.3973 | [6 empty] | 2021-05-06
NH_LO_COOLSYS1 PUMP SECONDARY VSD | COOLSYS1 PUMP SECONDARY VSD | No | No | No | No | [6 empty] | 2021-05-06
NH_LO_HEATSYS1 PUMP VSD | HEATSYS1 PUMP VSD | No | No | No | No | [6 empty] | 2021-05-06
NH_LO_DATACENTER BASEMENT Cooling Capacity [ton] | DATACENTER BASEMENT Cooling Capacity [ton] | 121.4841 | 121.1231 | 121.9017 | 121.579 | [6 empty] | 2021-05-06
NH_LO_DATACENTER BOT Cooling Capacity [ton] | DATACENTER BOT Cooling Capacity [ton] | 2.678 | 2.6543 | 2.7039 | 2.663 | [6 empty] | 2021-05-06
NH_LO_DATACENTER MID Cooling Capacity [ton] | DATACENTER MID Cooling Capacity [ton] | 25.6671 | 25.4577 | 25.9326 | 25.5346 | [6 empty] | 2021-05-06
NH_LO_DATACENTER TOP Cooling Capacity [ton] | DATACENTER TOP Cooling Capacity [ton] | 2.6149 | 2.5947 | 2.6387 | 2.5993 | [6 empty] | 2021-05-06
id | item | Zone5A(NH-Manchester-NH) ASHRAE901-state_STD2016 | Zone5A(NH-Manchester-NH) ASHRAE901-state_STD2019 | Zone6A(NH-Lebanon-NH) ASHRAE901-state_STD2016 | Zone6A(NH-Lebanon-NH) ASHRAE901-state_STD2019 | [6 empty] | 2021-05-06
NH_RS_PSZ-AC:1 Cooling Capacity [ton] | PSZ-AC:1 Cooling Capacity [ton] | 9.8177 | 9.4301 | 9.2757 | 8.8193 | [6 empty] | 2021-05-06
NH_RS_PSZ-AC:2 Cooling Capacity [ton] | PSZ-AC:2 Cooling Capacity [ton] | 46.1454 | 44.7591 | 44.5901 | 42.7861 | [6 empty] | 2021-05-06
NH_RS_PSZ-AC:3 Cooling Capacity [ton] | PSZ-AC:3 Cooling Capacity [ton] | 6.0938 | 5.9446 | 5.7279 | 5.572 | [6 empty] | 2021-05-06
NH_RS_PSZ-AC:4 Cooling Capacity [ton] | PSZ-AC:4 Cooling Capacity [ton] | 4.9361 | 4.7689 | 4.5429 | 4.3598 | [6 empty] | 2021-05-06
NH_RS_PSZ-AC:1 Supply Flow Rate [cfm] | PSZ-AC:1 Supply Flow Rate [cfm] | 3877.5504 | 3602.096 | 3729.2288 | 3432.5856 | [6 empty] | 2021-05-06
NH_RS_PSZ-AC:2 Supply Flow Rate [cfm] | PSZ-AC:2 Supply Flow Rate [cfm] | 15340.6912 | 14514.328 | 15213.5584 | 14387.1952 | [6 empty] | 2021-05-06
NH_RS_PSZ-AC:3 Supply Flow Rate [cfm] | PSZ-AC:3 Supply Flow Rate [cfm] | 2267.2016 | 2203.6352 | 2203.6352 | 2118.88 | [6 empty] | 2021-05-06
NH_RS_PSZ-AC:4 Supply Flow Rate [cfm] | PSZ-AC:4 Supply Flow Rate [cfm] | 1737.4816 | 1652.7264 | 1652.7264 | 1567.9712 | [6 empty] | 2021-05-06
NH_RS_PSZ-AC:1 OA Rate [cfm] | PSZ-AC:1 OA Rate [cfm] | 490.669 | 490.669 | 490.669 | 490.669 | [6 empty] | 2021-05-06
NH_RS_PSZ-AC:2 OA Rate [cfm] | PSZ-AC:2 OA Rate [cfm] | 4005.1282 | 4005.1282 | 4005.1282 | 4005.1282 | [6 empty] | 2021-05-06
NH_RS_PSZ-AC:3 OA Rate [cfm] | PSZ-AC:3 OA Rate [cfm] | 377.3937 | 377.3937 | 377.3937 | 377.3937 | [6 empty] | 2021-05-06
NH_RS_PSZ-AC:4 OA Rate [cfm] | PSZ-AC:4 OA Rate [cfm] | 377.3937 | 377.3937 | 377.3937 | 377.3937 | [6 empty] | 2021-05-06
NH_RS_PSZ-AC:1 OA Damper [gravity, motorized] | PSZ-AC:1 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2021-05-06
NH_RS_PSZ-AC:2 OA Damper [gravity, motorized] | PSZ-AC:2 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2021-05-06
NH_RS_PSZ-AC:3 OA Damper [gravity, motorized] | PSZ-AC:3 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2021-05-06
NH_RS_PSZ-AC:4 OA Damper [gravity, motorized] | PSZ-AC:4 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2021-05-06
NH_RS_PSZ-AC:1 Heating Capacity [kBtu/hr] | PSZ-AC:1 Heating Capacity [kBtu/hr] | 177.298 | 165.5892 | 174.1261 | 161.3927 | [6 empty] | 2021-05-06
NH_RS_PSZ-AC:2 Heating Capacity [kBtu/hr] | PSZ-AC:2 Heating Capacity [kBtu/hr] | 845.3301 | 810.3503 | 867.9596 | 835.6431 | [6 empty] | 2021-05-06
NH_RS_PSZ-AC:3 Heating Capacity [kBtu/hr] | PSZ-AC:3 Heating Capacity [kBtu/hr] | 111.3703 | 108.6416 | 111.42 | 108.4459 | [6 empty] | 2021-05-06
NH_RS_PSZ-AC:4 Heating Capacity [kBtu/hr] | PSZ-AC:4 Heating Capacity [kBtu/hr] | 91.1885 | 88.0782 | 90.399 | 86.7451 | [6 empty] | 2021-05-06
id | item | Zone5A(NH-Manchester-NH) ASHRAE901-state_STD2016 | Zone5A(NH-Manchester-NH) ASHRAE901-state_STD2019 | Zone6A(NH-Lebanon-NH) ASHRAE901-state_STD2016 | Zone6A(NH-Lebanon-NH) ASHRAE901-state_STD2019 | [6 empty] | 2021-05-06
NH_PS_VAV_POD_1 Cooling Capacity [ton] | VAV_POD_1 Cooling Capacity [ton] | 19.0608 | 18.4251 | 18.9432 | 18.267 | [6 empty] | 2021-05-06
NH_PS_VAV_POD_2 Cooling Capacity [ton] | VAV_POD_2 Cooling Capacity [ton] | 18.8264 | 18.3763 | 18.7162 | 18.2197 | [6 empty] | 2021-05-06
NH_PS_VAV_POD_3 Cooling Capacity [ton] | VAV_POD_3 Cooling Capacity [ton] | 17.3521 | 16.5304 | 17.23 | 16.19 | [6 empty] | 2021-05-06
NH_PS_VAV_OTHER Cooling Capacity [ton] | VAV_OTHER Cooling Capacity [ton] | 26.4647 | 24.8239 | 26.2523 | 23.3677 | [6 empty] | 2021-05-06
NH_PS_PSZ-AC_1:6 Cooling Capacity [ton] | PSZ-AC_1:6 Cooling Capacity [ton] | 7.9643 | 7.7014 | 7.7452 | 7.4659 | [6 empty] | 2021-05-06
NH_PS_PSZ-AC_2:5 Cooling Capacity [ton] | PSZ-AC_2:5 Cooling Capacity [ton] | 5.3949 | 5.3635 | 5.3807 | 5.2981 | [6 empty] | 2021-05-06
NH_PS_PSZ-AC_2:7 Cooling Capacity [ton] | PSZ-AC_2:7 Cooling Capacity [ton] | 10.5074 | 10.5074 | 10.5074 | 10.5074 | [6 empty] | 2021-05-06
NH_PS_VAV_POD_1 Supply Flow Rate [cfm] | VAV_POD_1 Supply Flow Rate [cfm] | 5720.976 | 5530.2768 | 5678.5984 | 5487.8992 | [6 empty] | 2021-05-06
NH_PS_VAV_POD_2 Supply Flow Rate [cfm] | VAV_POD_2 Supply Flow Rate [cfm] | 5657.4096 | 5509.088 | 5615.032 | 5466.7104 | [6 empty] | 2021-05-06
NH_PS_VAV_POD_3 Supply Flow Rate [cfm] | VAV_POD_3 Supply Flow Rate [cfm] | 5212.4448 | 4958.1792 | 5170.0672 | 4852.2352 | [6 empty] | 2021-05-06
NH_PS_VAV_OTHER Supply Flow Rate [cfm] | VAV_OTHER Supply Flow Rate [cfm] | 7945.8 | 7458.4576 | 7882.2336 | 7310.136 | [6 empty] | 2021-05-06
NH_PS_PSZ-AC_2:5 Supply Flow Rate [cfm] | PSZ-AC_2:5 Supply Flow Rate [cfm] | 1610.3488 | 1610.3488 | 1610.3488 | 1589.16 | [6 empty] | 2021-05-06
NH_PS_PSZ-AC_1:6 Supply Flow Rate [cfm] | PSZ-AC_1:6 Supply Flow Rate [cfm] | 2542.656 | 2436.712 | 2563.8448 | 2457.9008 | [6 empty] | 2021-05-06
NH_PS_PSZ-AC_2:7 Supply Flow Rate [cfm] | PSZ-AC_2:7 Supply Flow Rate [cfm] | 3157.1312 | 3157.1312 | 3157.1312 | 3157.1312 | [6 empty] | 2021-05-06
NH_PS_Supply Air Temp. Reset Flag | Supply Air Temp. Reset Flag | Yes | Yes | Yes | Yes | [6 empty] | 2021-05-06
NH_PS_VAV_POD_1 OA Rate [cfm] | VAV_POD_1 OA Rate [cfm] | 5717.7341 | 5529.0902 | 5683.1752 | 5481.6485 | [6 empty] | 2021-05-06
NH_PS_VAV_POD_2 OA Rate [cfm] | VAV_POD_2 OA Rate [cfm] | 5649.5062 | 5514.4276 | 5615.1803 | 5467.4308 | [6 empty] | 2021-05-06
NH_PS_VAV_POD_3 OA Rate [cfm] | VAV_POD_3 OA Rate [cfm] | 5206.8298 | 4960.51 | 5170.4274 | 4858.3588 | [6 empty] | 2021-05-06
NH_PS_VAV_OTHER OA Rate [cfm] | VAV_OTHER OA Rate [cfm] | 3736.1787 | 2988.8921 | 3736.1787 | 2988.8921 | [6 empty] | 2021-05-06
NH_PS_PSZ-AC_2:5 OA Rate [cfm] | PSZ-AC_2:5 OA Rate [cfm] | 1152.7343 | 1152.7343 | 1152.7343 | 1152.7343 | [6 empty] | 2021-05-06
NH_PS_PSZ-AC_1:6 OA Rate [cfm] | PSZ-AC_1:6 OA Rate [cfm] | 539.9118 | 539.9118 | 539.9118 | 539.9118 | [6 empty] | 2021-05-06
NH_PS_PSZ-AC_2:7 OA Rate [cfm] | PSZ-AC_2:7 OA Rate [cfm] | 3153.0841 | 3153.0841 | 3153.0841 | 3153.0841 | [6 empty] | 2021-05-06
NH_PS_VAV_POD_1 OA Damper [gravity, motorized] | VAV_POD_1 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2021-05-06
NH_PS_VAV_POD_2 OA Damper [gravity, motorized] | VAV_POD_2 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2021-05-06
NH_PS_VAV_POD_3 OA Damper [gravity, motorized] | VAV_POD_3 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2021-05-06
NH_PS_VAV_OTHER OA Damper [gravity, motorized] | VAV_OTHER OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2021-05-06
NH_PS_PSZ-AC_2:5 OA Damper [gravity, motorized] | PSZ-AC_2:5 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2021-05-06
NH_PS_PSZ-AC_1:6 OA Damper [gravity, motorized] | PSZ-AC_1:6 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2021-05-06
NH_PS_PSZ-AC_2:7 OA Damper [gravity, motorized] | PSZ-AC_2:7 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2021-05-06
NH_PS_VAV_POD_1 (economizer) | VAV_POD_1 (economizer) | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | [6 empty] | 2021-05-06
NH_PS_VAV_POD_2 (economizer) | VAV_POD_2 (economizer) | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | [6 empty] | 2021-05-06
NH_PS_VAV_POD_3 (economizer) | VAV_POD_3 (economizer) | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | [6 empty] | 2021-05-06
NH_PS_VAV_OTHER (economizer) | VAV_OTHER (economizer) | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | [6 empty] | 2021-05-06
NH_PS_PSZ-AC_2:5 (economizer) | PSZ-AC_2:5 (economizer) | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | [6 empty] | 2021-05-06
NH_PS_PSZ-AC_1:6 (economizer) | PSZ-AC_1:6 (economizer) | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | [6 empty] | 2021-05-06
NH_PS_PSZ-AC_2:7 (economizer) | PSZ-AC_2:7 (economizer) | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | [6 empty] | 2021-05-06
NH_PS_VAV_Pod_1_ERV Flag | VAV_Pod_1_ERV Flag | Yes | Yes | Yes | Yes | [6 empty] | 2021-05-06
NH_PS_VAV_Pod_2_ERV Flag | VAV_Pod_2_ERV Flag | Yes | Yes | Yes | Yes | [6 empty] | 2021-05-06
NH_PS_VAV_Pod_3_ERV Flag | VAV_Pod_3_ERV Flag | Yes | Yes | Yes | Yes | [6 empty] | 2021-05-06
NH_PS_VAV_OTHER_ERV Flag | VAV_OTHER_ERV Flag | Yes | Yes | Yes | Yes | [6 empty] | 2021-05-06
NH_PS_PSZ_AC_2_5_ERV Flag | PSZ_AC_2_5_ERV Flag | Yes | Yes | Yes | Yes | [6 empty] | 2021-05-06
NH_PS_PSZ_AC_2_7_ERV Flag | PSZ_AC_2_7_ERV Flag | Yes | Yes | Yes | Yes | [6 empty] | 2021-05-06
NH_PS_HEATSYS1 Capacity [MMBTU/h] | HEATSYS1 Capacity [MMBTU/h] | 1.1434 | 1.0973 | 1.2111 | 1.1599 | [6 empty] | 2021-05-06
NH_PS_HEATSYS1 Flow Rate [gal/min] | HEATSYS1 Flow Rate [gal/min] | 117.3506 | 112.618 | 124.3016 | 119.0415 | [6 empty] | 2021-05-06
NH_PS_VAV_POD_1 Fan Power [hp] | VAV_POD_1 Fan Power [hp] | 8.4385 | 8.1571 | 8.3864 | 8.0871 | [6 empty] | 2021-05-06
NH_PS_VAV_POD_2 Fan Power [hp] | VAV_POD_2 Fan Power [hp] | 8.3347 | 8.1354 | 8.2859 | 8.0661 | [6 empty] | 2021-05-06
NH_PS_VAV_POD_3 Fan Power [hp] | VAV_POD_3 Fan Power [hp] | 7.682 | 7.3182 | 7.6279 | 7.1675 | [6 empty] | 2021-05-06
NH_PS_VAV_OTHER Fan Power [hp] | VAV_OTHER Fan Power [hp] | 11.6275 | 10.9066 | 11.5342 | 10.6907 | [6 empty] | 2021-05-06
NH_PS_HEATSYS1 Pump Power [hp] | HEATSYS1 Pump Power [hp] | 2.5366 | 2.4102 | 2.6868 | 2.5477 | [6 empty] | 2021-05-06
NH_PS_PSZ-AC_1:6 Heating Capacity [kBtu/hr] | PSZ-AC_1:6 Heating Capacity [kBtu/hr] | 214.8412 | 206.2403 | 219.2211 | 209.9764 | [6 empty] | 2021-05-06
NH_PS_PSZ-AC_2:5 Heating Capacity [kBtu/hr] | PSZ-AC_2:5 Heating Capacity [kBtu/hr] | 144.5697 | 144.2235 | 154.1376 | 153.2389 | [6 empty] | 2021-05-06
NH_PS_PSZ-AC_2:7 Heating Capacity [kBtu/hr] | PSZ-AC_2:7 Heating Capacity [kBtu/hr] | 348.6103 | 348.6103 | 375.8282 | 375.8282 | [6 empty] | 2021-05-06
NH_PS_ZN_VAV_BOXes_Max_Reheat_Water_Flow_GPM | ZN_VAV_BOXes_Max_Reheat_Water_Flow_GPM | 73.5765 | 70.7449 | 73.8312 | 71.1415 | [6 empty] | 2021-05-06
id | item | Zone5A(NH-Manchester-NH) ASHRAE901-state_STD2016 | Zone5A(NH-Manchester-NH) ASHRAE901-state_STD2019 | Zone6A(NH-Lebanon-NH) ASHRAE901-state_STD2016 | Zone6A(NH-Lebanon-NH) ASHRAE901-state_STD2019 | [6 empty] | 2021-05-06
NH_SH_SAC_FRONTOFFICE Cooling Capacity [ton] | SAC_FRONTOFFICE Cooling Capacity [ton] | 2.1882 | 2.07 | 2.0819 | 1.9703 | [6 empty] | 2021-05-06
NH_SH_SAC_FRONTLOUNGE Cooling Capacity [ton] | SAC_FRONTLOUNGE Cooling Capacity [ton] | 5.9574 | 5.6614 | 5.7095 | 5.4638 | [6 empty] | 2021-05-06
NH_SH_SAC_MEETINGROOM Cooling Capacity [ton] | SAC_MEETINGROOM Cooling Capacity [ton] | 2.8523 | 2.7593 | 2.8563 | 2.7602 | [6 empty] | 2021-05-06
NH_SH_SAC_EXC_EMPLGE_RESTRM Cooling Capacity [ton] | SAC_EXC_EMPLGE_RESTRM Cooling Capacity [ton] | 5.7774 | 5.7365 | 5.6377 | 5.5919 | [6 empty] | 2021-05-06
NH_SH_SAC_FO_ADDAQ SUPPLY FAN Supply Flow Rate [cfm] | SAC_FO_ADDAQ SUPPLY FAN Supply Flow Rate [cfm] | 762.7968 | 699.2304 | 741.608 | 699.2304 | [6 empty] | 2021-05-06
NH_SH_SAC_FL_ADDAQ SUPPLY FAN Supply Flow Rate [cfm] | SAC_FL_ADDAQ SUPPLY FAN Supply Flow Rate [cfm] | 1779.8592 | 1695.104 | 1779.8592 | 1695.104 | [6 empty] | 2021-05-06
NH_SH_SAC_MR_ADDAQ SUPPLY FAN Supply Flow Rate [cfm] | SAC_MR_ADDAQ SUPPLY FAN Supply Flow Rate [cfm] | 847.552 | 826.3632 | 847.552 | 826.3632 | [6 empty] | 2021-05-06
NH_SH_SAC_EXC_ADDAQ SUPPLY FAN Supply Flow Rate [cfm] | SAC_EXC_ADDAQ SUPPLY FAN Supply Flow Rate [cfm] | 2182.4464 | 2161.2576 | 2203.6352 | 2182.4464 | [6 empty] | 2021-05-06
NH_SH_SAC_Exc_EmpLge_RestRm OA Rate [cfm] | SAC_Exc_EmpLge_RestRm OA Rate [cfm] | 199.9928 | 199.9928 | 199.9928 | 199.9928 | [6 empty] | 2021-05-06
NH_SH_SAC_FrontLounge OA Rate [cfm] | SAC_FrontLounge OA Rate [cfm] | 500.0133 | 500.0133 | 500.0133 | 500.0133 | [6 empty] | 2021-05-06
NH_SH_SAC_FrontOffice OA Rate [cfm] | SAC_FrontOffice OA Rate [cfm] | 119.2938 | 119.2938 | 119.2938 | 119.2938 | [6 empty] | 2021-05-06
NH_SH_SAC_MeetingRoom OA Rate [cfm] | SAC_MeetingRoom OA Rate [cfm] | 267.7629 | 267.7629 | 267.7629 | 267.7629 | [6 empty] | 2021-05-06
NH_SH_SAC_FrontLounge OA Damper [gravity, motorized] | SAC_FrontLounge OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2021-05-06
NH_SH_SAC_FrontOffice (economizer) | SAC_FrontOffice (economizer) | No | No | No | No | [6 empty] | 2021-05-06
NH_SH_SAC_FrontLounge (economizer) | SAC_FrontLounge (economizer) | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | [6 empty] | 2021-05-06
NH_SH_SAC_MeetingRoom (economizer) | SAC_MeetingRoom (economizer) | No | No | No | No | [6 empty] | 2021-05-06
NH_SH_SAC_Exc_EmpLge_RestRm (economizer) | SAC_Exc_EmpLge_RestRm (economizer) | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | [6 empty] | 2021-05-06
NH_SH_SAC_FRONTOFFICE Heating Capacity [kBtu/hr] | SAC_FRONTOFFICE Heating Capacity [kBtu/hr] | 36.487 | 34.6827 | 36.7965 | 34.9955 | [6 empty] | 2021-05-06
NH_SH_SAC_FRONTLOUNGE Heating Capacity [kBtu/hr] | SAC_FRONTLOUNGE Heating Capacity [kBtu/hr] | 102.375 | 99.0543 | 105.934 | 102.4757 | [6 empty] | 2021-05-06
NH_SH_SAC_MEETINGROOM Heating Capacity [kBtu/hr] | SAC_MEETINGROOM Heating Capacity [kBtu/hr] | 51.0775 | 50.0586 | 53.1461 | 52.1066 | [6 empty] | 2021-05-06
NH_SH_SAC_EXC_EMPLGE_RESTRM Heating Capacity [kBtu/hr] | SAC_EXC_EMPLGE_RESTRM Heating Capacity [kBtu/hr] | 94.3524 | 93.6936 | 96.0021 | 95.2525 | [6 empty] | 2021-05-06
id | item | Zone5A(NH-Manchester-NH) ASHRAE901-state_STD2016 | Zone5A(NH-Manchester-NH) ASHRAE901-state_STD2019 | Zone6A(NH-Lebanon-NH) ASHRAE901-state_STD2016 | Zone6A(NH-Lebanon-NH) ASHRAE901-state_STD2019 | [6 empty] | 2021-05-06
NH_MA_SPLIT GSW COOLING COIL Cooling Capacity [ton] | SPLIT GSW COOLING COIL Cooling Capacity [ton] | 0.78271 | 0.76827 | 0.74563 | 0.71627 | [6 empty] | 2021-05-06
NH_MA_SPLIT GNW COOLING COIL Cooling Capacity [ton] | SPLIT GNW COOLING COIL Cooling Capacity [ton] | 0.73729 | 0.72372 | 0.69989 | 0.67324 | [6 empty] | 2021-05-06
NH_MA_SPLIT OFFICE COOLING COIL Cooling Capacity [ton] | SPLIT OFFICE COOLING COIL Cooling Capacity [ton] | 1.6505 | 1.5197 | 1.5961 | 1.4397 | [6 empty] | 2021-05-06
NH_MA_SPLIT GNE COOLING COIL Cooling Capacity [ton] | SPLIT GNE COOLING COIL Cooling Capacity [ton] | 0.63161 | 0.61986 | 0.59101 | 0.56962 | [6 empty] | 2021-05-06
NH_MA_SPLIT GN1 COOLING COIL Cooling Capacity [ton] | SPLIT GN1 COOLING COIL Cooling Capacity [ton] | 0.53935 | 0.53031 | 0.49818 | 0.48414 | [6 empty] | 2021-05-06
NH_MA_SPLIT GN2 COOLING COIL Cooling Capacity [ton] | SPLIT GN2 COOLING COIL Cooling Capacity [ton] | 0.53724 | 0.52825 | 0.49593 | 0.48205 | [6 empty] | 2021-05-06
NH_MA_SPLIT GS1 COOLING COIL Cooling Capacity [ton] | SPLIT GS1 COOLING COIL Cooling Capacity [ton] | 0.58865 | 0.57818 | 0.5534 | 0.53603 | [6 empty] | 2021-05-06
NH_MA_SPLIT GS2 COOLING COIL Cooling Capacity [ton] | SPLIT GS2 COOLING COIL Cooling Capacity [ton] | 0.61968 | 0.60422 | 0.58814 | 0.56594 | [6 empty] | 2021-05-06
NH_MA_SPLIT MSW COOLING COIL Cooling Capacity [ton] | SPLIT MSW COOLING COIL Cooling Capacity [ton] | 1.9453 | 1.9131 | 1.8464 | 1.7763 | [6 empty] | 2021-05-06
NH_MA_SPLIT MNW COOLING COIL Cooling Capacity [ton] | SPLIT MNW COOLING COIL Cooling Capacity [ton] | 1.8593 | 1.8291 | 1.758 | 1.6928 | [6 empty] | 2021-05-06
NH_MA_SPLIT MSE COOLING COIL Cooling Capacity [ton] | SPLIT MSE COOLING COIL Cooling Capacity [ton] | 1.6897 | 1.6611 | 1.5917 | 1.5299 | [6 empty] | 2021-05-06
NH_MA_SPLIT MNE COOLING COIL Cooling Capacity [ton] | SPLIT MNE COOLING COIL Cooling Capacity [ton] | 1.4871 | 1.4581 | 1.3744 | 1.3085 | [6 empty] | 2021-05-06
NH_MA_SPLIT MN1 COOLING COIL Cooling Capacity [ton] | SPLIT MN1 COOLING COIL Cooling Capacity [ton] | 1.2307 | 1.2134 | 1.1346 | 1.1071 | [6 empty] | 2021-05-06
NH_MA_SPLIT MN2 COOLING COIL Cooling Capacity [ton] | SPLIT MN2 COOLING COIL Cooling Capacity [ton] | 1.2248 | 1.2076 | 1.1283 | 1.1013 | [6 empty] | 2021-05-06
NH_MA_SPLIT MS1 COOLING COIL Cooling Capacity [ton] | SPLIT MS1 COOLING COIL Cooling Capacity [ton] | 1.3197 | 1.3002 | 1.2313 | 1.1986 | [6 empty] | 2021-05-06
NH_MA_SPLIT MS2 COOLING COIL Cooling Capacity [ton] | SPLIT MS2 COOLING COIL Cooling Capacity [ton] | 1.3136 | 1.2943 | 1.225 | 1.1927 | [6 empty] | 2021-05-06
NH_MA_SPLIT TSW COOLING COIL Cooling Capacity [ton] | SPLIT TSW COOLING COIL Cooling Capacity [ton] | 1.2207 | 1.2034 | 1.1594 | 1.1197 | [6 empty] | 2021-05-06
NH_MA_SPLIT TNW COOLING COIL Cooling Capacity [ton] | SPLIT TNW COOLING COIL Cooling Capacity [ton] | 1.1599 | 1.1435 | 1.1013 | 1.0643 | [6 empty] | 2021-05-06
NH_MA_SPLIT TSE COOLING COIL Cooling Capacity [ton] | SPLIT TSE COOLING COIL Cooling Capacity [ton] | 1.0861 | 1.071 | 1.0233 | 0.99138 | [6 empty] | 2021-05-06
NH_MA_SPLIT TNE COOLING COIL Cooling Capacity [ton] | SPLIT TNE COOLING COIL Cooling Capacity [ton] | 0.99149 | 0.97905 | 0.92265 | 0.89806 | [6 empty] | 2021-05-06
NH_MA_SPLIT TN1 COOLING COIL Cooling Capacity [ton] | SPLIT TN1 COOLING COIL Cooling Capacity [ton] | 0.81271 | 0.80302 | 0.75483 | 0.73859 | [6 empty] | 2021-05-06
NH_MA_SPLIT TN2 COOLING COIL Cooling Capacity [ton] | SPLIT TN2 COOLING COIL Cooling Capacity [ton] | 0.81398 | 0.8043 | 0.75731 | 0.7411 | [6 empty] | 2021-05-06
NH_MA_SPLIT TS1 COOLING COIL Cooling Capacity [ton] | SPLIT TS1 COOLING COIL Cooling Capacity [ton] | 0.90173 | 0.8899 | 0.85103 | 0.82745 | [6 empty] | 2021-05-06
NH_MA_SPLIT TS2 COOLING COIL Cooling Capacity [ton] | SPLIT TS2 COOLING COIL Cooling Capacity [ton] | 0.90344 | 0.8928 | 0.85306 | 0.83054 | [6 empty] | 2021-05-06
NH_MA_Split GN1 Furnace with DX Cooling OA Rate [cfm] | Split GN1 Furnace with DX Cooling OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | [6 empty] | 2021-05-06
NH_MA_Split GN2 Furnace with DX Cooling OA Rate [cfm] | Split GN2 Furnace with DX Cooling OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | [6 empty] | 2021-05-06
NH_MA_Split GNE Furnace with DX Cooling OA Rate [cfm] | Split GNE Furnace with DX Cooling OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | [6 empty] | 2021-05-06
NH_MA_Split GNW Furnace with DX Cooling OA Rate [cfm] | Split GNW Furnace with DX Cooling OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | [6 empty] | 2021-05-06
NH_MA_Split GS1 Furnace with DX Cooling OA Rate [cfm] | Split GS1 Furnace with DX Cooling OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | [6 empty] | 2021-05-06
NH_MA_Split GS2 Furnace with DX Cooling OA Rate [cfm] | Split GS2 Furnace with DX Cooling OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | [6 empty] | 2021-05-06
NH_MA_Split GSW Furnace with DX Cooling OA Rate [cfm] | Split GSW Furnace with DX Cooling OA Rate [cfm] | 56.9945 | 56.9945 | 56.9945 | 56.9945 | [6 empty] | 2021-05-06
NH_MA_Split MN1 Furnace with DX Cooling OA Rate [cfm] | Split MN1 Furnace with DX Cooling OA Rate [cfm] | 109.9824 | 109.9824 | 109.9824 | 109.9824 | [6 empty] | 2021-05-06
NH_MA_Split MN2 Furnace with DX Cooling OA Rate [cfm] | Split MN2 Furnace with DX Cooling OA Rate [cfm] | 109.9824 | 109.9824 | 109.9824 | 109.9824 | [6 empty] | 2021-05-06
NH_MA_Split MNE Furnace with DX Cooling OA Rate [cfm] | Split MNE Furnace with DX Cooling OA Rate [cfm] | 109.9824 | 109.9824 | 109.9824 | 109.9824 | [6 empty] | 2021-05-06
NH_MA_Split MNW Furnace with DX Cooling OA Rate [cfm] | Split MNW Furnace with DX Cooling OA Rate [cfm] | 109.9824 | 109.9824 | 109.9824 | 109.9824 | [6 empty] | 2021-05-06
NH_MA_Split MS1 Furnace with DX Cooling OA Rate [cfm] | Split MS1 Furnace with DX Cooling OA Rate [cfm] | 109.9824 | 109.9824 | 109.9824 | 109.9824 | [6 empty] | 2021-05-06
NH_MA_Split MS2 Furnace with DX Cooling OA Rate [cfm] | Split MS2 Furnace with DX Cooling OA Rate [cfm] | 109.9824 | 109.9824 | 109.9824 | 109.9824 | [6 empty] | 2021-05-06
NH_MA_Split MSE Furnace with DX Cooling OA Rate [cfm] | Split MSE Furnace with DX Cooling OA Rate [cfm] | 109.9824 | 109.9824 | 109.9824 | 109.9824 | [6 empty] | 2021-05-06
NH_MA_Split MSW Furnace with DX Cooling OA Rate [cfm] | Split MSW Furnace with DX Cooling OA Rate [cfm] | 109.9824 | 109.9824 | 109.9824 | 109.9824 | [6 empty] | 2021-05-06
NH_MA_Split Office Furnace with DX Cooling OA Rate [cfm] | Split Office Furnace with DX Cooling OA Rate [cfm] | 80.7372 | 80.7372 | 80.7372 | 80.7372 | [6 empty] | 2021-05-06
NH_MA_Split TN1 Furnace with DX Cooling OA Rate [cfm] | Split TN1 Furnace with DX Cooling OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | [6 empty] | 2021-05-06
NH_MA_Split TN2 Furnace with DX Cooling OA Rate [cfm] | Split TN2 Furnace with DX Cooling OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | [6 empty] | 2021-05-06
NH_MA_Split TNE Furnace with DX Cooling OA Rate [cfm] | Split TNE Furnace with DX Cooling OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | [6 empty] | 2021-05-06
NH_MA_Split TNW Furnace with DX Cooling OA Rate [cfm] | Split TNW Furnace with DX Cooling OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | [6 empty] | 2021-05-06
NH_MA_Split TS1 Furnace with DX Cooling OA Rate [cfm] | Split TS1 Furnace with DX Cooling OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | [6 empty] | 2021-05-06
NH_MA_Split TS2 Furnace with DX Cooling OA Rate [cfm] | Split TS2 Furnace with DX Cooling OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | [6 empty] | 2021-05-06
NH_MA_Split TSE Furnace with DX Cooling OA Rate [cfm] | Split TSE Furnace with DX Cooling OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | [6 empty] | 2021-05-06
NH_MA_Split TSW Furnace with DX Cooling OA Rate [cfm] | Split TSW Furnace with DX Cooling OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | [6 empty] | 2021-05-06
NH_MA_SPLIT GSW HEATING COIL Heating Capacity [kBtu/hr] | SPLIT GSW HEATING COIL Heating Capacity [kBtu/hr] | 10.2249 | 10.2838 | 10.3256 | 10.3876 | [6 empty] | 2021-05-06
NH_MA_SPLIT GNW HEATING COIL Heating Capacity [kBtu/hr] | SPLIT GNW HEATING COIL Heating Capacity [kBtu/hr] | 10.1472 | 10.2062 | 10.1726 | 10.2348 | [6 empty] | 2021-05-06
NH_MA_SPLIT OFFICE HEATING COIL Heating Capacity [kBtu/hr] | SPLIT OFFICE HEATING COIL Heating Capacity [kBtu/hr] | 23.4381 | 23.5196 | 23.7054 | 23.9811 | [6 empty] | 2021-05-06
NH_MA_SPLIT GNE HEATING COIL Heating Capacity [kBtu/hr] | SPLIT GNE HEATING COIL Heating Capacity [kBtu/hr] | 10.1239 | 10.1829 | 10.1726 | 10.2348 | [6 empty] | 2021-05-06
NH_MA_SPLIT GN1 HEATING COIL Heating Capacity [kBtu/hr] | SPLIT GN1 HEATING COIL Heating Capacity [kBtu/hr] | 7.5501 | 7.6092 | 7.8359 | 7.8981 | [6 empty] | 2021-05-06
NH_MA_SPLIT GN2 HEATING COIL Heating Capacity [kBtu/hr] | SPLIT GN2 HEATING COIL Heating Capacity [kBtu/hr] | 7.5495 | 7.6085 | 7.8359 | 7.8981 | [6 empty] | 2021-05-06
NH_MA_SPLIT GS1 HEATING COIL Heating Capacity [kBtu/hr] | SPLIT GS1 HEATING COIL Heating Capacity [kBtu/hr] | 7.4959 | 7.5548 | 7.8396 | 7.9016 | [6 empty] | 2021-05-06
NH_MA_SPLIT GS2 HEATING COIL Heating Capacity [kBtu/hr] | SPLIT GS2 HEATING COIL Heating Capacity [kBtu/hr] | 8.0039 | 8.0637 | 8.3554 | 8.4177 | [6 empty] | 2021-05-06
NH_MA_SPLIT MSW HEATING COIL Heating Capacity [kBtu/hr] | SPLIT MSW HEATING COIL Heating Capacity [kBtu/hr] | 17.8483 | 17.9773 | 16.8399 | 16.9705 | [6 empty] | 2021-05-06
NH_MA_SPLIT MNW HEATING COIL Heating Capacity [kBtu/hr] | SPLIT MNW HEATING COIL Heating Capacity [kBtu/hr] | 17.9427 | 18.0716 | 16.7947 | 16.9248 | [6 empty] | 2021-05-06
NH_MA_SPLIT MSE HEATING COIL Heating Capacity [kBtu/hr] | SPLIT MSE HEATING COIL Heating Capacity [kBtu/hr] | 17.7932 | 17.9222 | 16.8399 | 16.9705 | [6 empty] | 2021-05-06
NH_MA_SPLIT MNE HEATING COIL Heating Capacity [kBtu/hr] | SPLIT MNE HEATING COIL Heating Capacity [kBtu/hr] | 17.8875 | 18.0165 | 16.7947 | 16.9248 | [6 empty] | 2021-05-06
NH_MA_SPLIT MN1 HEATING COIL Heating Capacity [kBtu/hr] | SPLIT MN1 HEATING COIL Heating Capacity [kBtu/hr] | 12.5872 | 12.713 | 13.1092 | 13.1092 | [6 empty] | 2021-05-06
NH_MA_SPLIT MN2 HEATING COIL Heating Capacity [kBtu/hr] | SPLIT MN2 HEATING COIL Heating Capacity [kBtu/hr] | 12.5857 | 12.7115 | 13.1092 | 13.1092 | [6 empty] | 2021-05-06
NH_MA_SPLIT MS1 HEATING COIL Heating Capacity [kBtu/hr] | SPLIT MS1 HEATING COIL Heating Capacity [kBtu/hr] | 12.5021 | 12.6279 | 13.1092 | 13.1092 | [6 empty] | 2021-05-06
NH_MA_SPLIT MS2 HEATING COIL Heating Capacity [kBtu/hr] | SPLIT MS2 HEATING COIL Heating Capacity [kBtu/hr] | 12.5007 | 12.6264 | 13.1092 | 13.1092 | [6 empty] | 2021-05-06
NH_MA_SPLIT TSW HEATING COIL Heating Capacity [kBtu/hr] | SPLIT TSW HEATING COIL Heating Capacity [kBtu/hr] | 12.5914 | 12.6533 | 12.1282 | 12.1904 | [6 empty] | 2021-05-06
NH_MA_SPLIT TNW HEATING COIL Heating Capacity [kBtu/hr] | SPLIT TNW HEATING COIL Heating Capacity [kBtu/hr] | 12.6479 | 12.7099 | 12.1107 | 12.1731 | [6 empty] | 2021-05-06
NH_MA_SPLIT TSE HEATING COIL Heating Capacity [kBtu/hr] | SPLIT TSE HEATING COIL Heating Capacity [kBtu/hr] | 12.5621 | 12.624 | 12.1282 | 12.1904 | [6 empty] | 2021-05-06
NH_MA_SPLIT TNE HEATING COIL Heating Capacity [kBtu/hr] | SPLIT TNE HEATING COIL Heating Capacity [kBtu/hr] | 12.6186 | 12.6806 | 12.1107 | 12.1731 | [6 empty] | 2021-05-06
NH_MA_SPLIT TN1 HEATING COIL Heating Capacity [kBtu/hr] | SPLIT TN1 HEATING COIL Heating Capacity [kBtu/hr] | 9.7732 | 9.835 | 9.8064 | 9.8686 | [6 empty] | 2021-05-06
NH_MA_SPLIT TN2 HEATING COIL Heating Capacity [kBtu/hr] | SPLIT TN2 HEATING COIL Heating Capacity [kBtu/hr] | 9.7723 | 9.8342 | 9.8064 | 9.8686 | [6 empty] | 2021-05-06
NH_MA_SPLIT TS1 HEATING COIL Heating Capacity [kBtu/hr] | SPLIT TS1 HEATING COIL Heating Capacity [kBtu/hr] | 9.7099 | 9.7717 | 9.8179 | 9.88 | [6 empty] | 2021-05-06
NH_MA_SPLIT TS2 HEATING COIL Heating Capacity [kBtu/hr] | SPLIT TS2 HEATING COIL Heating Capacity [kBtu/hr] | 9.7091 | 9.7708 | 9.8179 | 9.88 | [6 empty] | 2021-05-06
NH_MA_Split_GSW ERV Flag | Split_GSW ERV Flag | Yes | Yes | Yes | Yes | [6 empty] | 2021-05-06
NH_MA_Split_GNW ERV Flag | Split_GNW ERV Flag | Yes | Yes | Yes | Yes | [6 empty] | 2021-05-06
NH_MA_Split_GNE ERV Flag | Split_GNE ERV Flag | Yes | Yes | Yes | Yes | [6 empty] | 2021-05-06
NH_MA_Split_GN1 ERV Flag | Split_GN1 ERV Flag | Yes | Yes | Yes | Yes | [6 empty] | 2021-05-06
NH_MA_Split_GN2 ERV Flag | Split_GN2 ERV Flag | Yes | Yes | Yes | Yes | [6 empty] | 2021-05-06
NH_MA_Split_GS1 ERV Flag | Split_GS1 ERV Flag | Yes | Yes | Yes | Yes | [6 empty] | 2021-05-06
NH_MA_Split_GS2 ERV Flag | Split_GS2 ERV Flag | Yes | Yes | Yes | Yes | [6 empty] | 2021-05-06
NH_MA_Split_MSW ERV Flag | Split_MSW ERV Flag | Yes | Yes | Yes | Yes | [6 empty] | 2021-05-06
NH_MA_Split_MNW ERV Flag | Split_MNW ERV Flag | Yes | Yes | Yes | Yes | [6 empty] | 2021-05-06
NH_MA_Split_MSE ERV Flag | Split_MSE ERV Flag | Yes | Yes | Yes | Yes | [6 empty] | 2021-05-06
NH_MA_Split_MNE ERV Flag | Split_MNE ERV Flag | Yes | Yes | Yes | Yes | [6 empty] | 2021-05-06
NH_MA_Split_MN1 ERV Flag | Split_MN1 ERV Flag | Yes | Yes | Yes | Yes | [6 empty] | 2021-05-06
NH_MA_Split_MN2 ERV Flag | Split_MN2 ERV Flag | Yes | Yes | Yes | Yes | [6 empty] | 2021-05-06
NH_MA_Split_MS1 ERV Flag | Split_MS1 ERV Flag | Yes | Yes | Yes | Yes | [6 empty] | 2021-05-06
NH_MA_Split_MS2 ERV Flag | Split_MS2 ERV Flag | Yes | Yes | Yes | Yes | [6 empty] | 2021-05-06
NH_MA_Split_TSW ERV Flag | Split_TSW ERV Flag | Yes | Yes | Yes | Yes | [6 empty] | 2021-05-06
NH_MA_Split_TNW ERV Flag | Split_TNW ERV Flag | Yes | Yes | Yes | Yes | [6 empty] | 2021-05-06
NH_MA_Split_TSE ERV Flag | Split_TSE ERV Flag | Yes | Yes | Yes | Yes | [6 empty] | 2021-05-06
NH_MA_Split_TNE ERV Flag | Split_TNE ERV Flag | Yes | Yes | Yes | Yes | [6 empty] | 2021-05-06
NH_MA_Split_TN1 ERV Flag | Split_TN1 ERV Flag | Yes | Yes | Yes | Yes | [6 empty] | 2021-05-06
NH_MA_Split_TN2 ERV Flag | Split_TN2 ERV Flag | Yes | Yes | Yes | Yes | [6 empty] | 2021-05-06
NH_MA_Split_TS1 ERV Flag | Split_TS1 ERV Flag | Yes | Yes | Yes | Yes | [6 empty] | 2021-05-06
NH_MA_Split_TS2 ERV Flag | Split_TS2 ERV Flag | Yes | Yes | Yes | Yes | [6 empty] | 2021-05-06
id | item | Zone4A(NJ-Newark-NJ) ASHRAE901-state_STD2016 | Zone4A(NJ-Newark-NJ) ASHRAE901-state_STD2019 | Zone5A(NJ-Allentown-PA) ASHRAE901-state_STD2016 | Zone5A(NJ-Allentown-PA) ASHRAE901-state_STD2019 | [6 empty] | 2021-05-06
NJ_SO_PSZ-AC:1 Cooling Capacity [ton] | PSZ-AC:1 Cooling Capacity [ton] | 1.9016 | 1.804 | 1.8272 | 1.7348 | [6 empty] | 2021-05-06
NJ_SO_PSZ-AC:2 Cooling Capacity [ton] | PSZ-AC:2 Cooling Capacity [ton] | 1.7005 | 1.6367 | 1.5853 | 1.5234 | [6 empty] | 2021-05-06
NJ_SO_PSZ-AC:3 Cooling Capacity [ton] | PSZ-AC:3 Cooling Capacity [ton] | 1.1542 | 1.1153 | 1.0898 | 1.0519 | [6 empty] | 2021-05-06
NJ_SO_PSZ-AC:4 Cooling Capacity [ton] | PSZ-AC:4 Cooling Capacity [ton] | 1.6236 | 1.5521 | 1.5139 | 1.4454 | [6 empty] | 2021-05-06
NJ_SO_PSZ-AC:5 Cooling Capacity [ton] | PSZ-AC:5 Cooling Capacity [ton] | 1.3566 | 1.3162 | 1.2981 | 1.2587 | [6 empty] | 2021-05-06
NJ_SO_PSZ-AC:1 Supply Flow Rate [cfm] | PSZ-AC:1 Supply Flow Rate [cfm] | 656.8528 | 593.2864 | 656.8528 | 593.2864 | [6 empty] | 2021-05-06
NJ_SO_PSZ-AC:2 Supply Flow Rate [cfm] | PSZ-AC:2 Supply Flow Rate [cfm] | 593.2864 | 572.0976 | 572.0976 | 550.9088 | [6 empty] | 2021-05-06
NJ_SO_PSZ-AC:3 Supply Flow Rate [cfm] | PSZ-AC:3 Supply Flow Rate [cfm] | 466.1536 | 444.9648 | 444.9648 | 423.776 | [6 empty] | 2021-05-06
NJ_SO_PSZ-AC:4 Supply Flow Rate [cfm] | PSZ-AC:4 Supply Flow Rate [cfm] | 572.0976 | 529.72 | 550.9088 | 508.5312 | [6 empty] | 2021-05-06
NJ_SO_PSZ-AC:5 Supply Flow Rate [cfm] | PSZ-AC:5 Supply Flow Rate [cfm] | 529.72 | 508.5312 | 529.72 | 508.5312 | [6 empty] | 2021-05-06
NJ_SO_PSZ-AC:1 OA Rate [cfm] | PSZ-AC:1 OA Rate [cfm] | 136.9178 | 136.9178 | 136.9178 | 136.9178 | [6 empty] | 2021-05-06
NJ_SO_PSZ-AC:2 OA Rate [cfm] | PSZ-AC:2 OA Rate [cfm] | 103.7925 | 103.7925 | 103.7925 | 103.7925 | [6 empty] | 2021-05-06
NJ_SO_PSZ-AC:3 OA Rate [cfm] | PSZ-AC:3 OA Rate [cfm] | 61.5711 | 61.5711 | 61.5711 | 61.5711 | [6 empty] | 2021-05-06
NJ_SO_PSZ-AC:4 OA Rate [cfm] | PSZ-AC:4 OA Rate [cfm] | 103.7925 | 103.7925 | 103.7925 | 103.7925 | [6 empty] | 2021-05-06
NJ_SO_PSZ-AC:5 OA Rate [cfm] | PSZ-AC:5 OA Rate [cfm] | 61.5711 | 61.5711 | 61.5711 | 61.5711 | [6 empty] | 2021-05-06
NJ_SO_PSZ-AC:1 heating Capacity [kBtu/hr] | PSZ-AC:1 heating Capacity [kBtu/hr] | 13.7632 | 13.7632 | 14.18 | 14.18 | [6 empty] | 2021-05-06
NJ_SO_PSZ-AC:2 heating Capacity [kBtu/hr] | PSZ-AC:2 heating Capacity [kBtu/hr] | 19.3925 | 19.1953 | 18.9843 | 18.7759 | [6 empty] | 2021-05-06
NJ_SO_PSZ-AC:3 heating Capacity [kBtu/hr] | PSZ-AC:3 heating Capacity [kBtu/hr] | 11.9181 | 11.809 | 11.5631 | 11.4479 | [6 empty] | 2021-05-06
NJ_SO_PSZ-AC:4 heating Capacity [kBtu/hr] | PSZ-AC:4 heating Capacity [kBtu/hr] | 19.3079 | 19.1381 | 18.889 | 18.7109 | [6 empty] | 2021-05-06
NJ_SO_PSZ-AC:5 heating Capacity [kBtu/hr] | PSZ-AC:5 heating Capacity [kBtu/hr] | 11.9713 | 11.8564 | 11.6135 | 11.493 | [6 empty] | 2021-05-06
id | item | Zone4A(NJ-Newark-NJ) ASHRAE901-state_STD2016 | Zone4A(NJ-Newark-NJ) ASHRAE901-state_STD2019 | Zone5A(NJ-Allentown-PA) ASHRAE901-state_STD2016 | Zone5A(NJ-Allentown-PA) ASHRAE901-state_STD2019 | [6 empty] | 2021-05-06
NJ_LO_CAV_BAS Supply Flow Rate [cfm] | CAV_BAS Supply Flow Rate [cfm] | 11653.84 | 10785.0992 | 11780.9728 | 10912.232 | [6 empty] | 2021-05-06
NJ_LO_VAV_BOT WITH REHEAT Supply Flow Rate [cfm] | VAV_BOT WITH REHEAT Supply Flow Rate [cfm] | 19853.9056 | 18921.5984 | 19790.3392 | 18858.032 | [6 empty] | 2021-05-06
NJ_LO_VAV_MID WITH REHEAT Supply Flow Rate [cfm] | VAV_MID WITH REHEAT Supply Flow Rate [cfm] | 185741.0211 | 176862.9139 | 183961.1619 | 175040.6771 | [6 empty] | 2021-05-06
NJ_LO_VAV_TOP WITH REHEAT Supply Flow Rate [cfm] | VAV_TOP WITH REHEAT Supply Flow Rate [cfm] | 19514.8848 | 18709.7104 | 19472.5072 | 18667.3328 | [6 empty] | 2021-05-06
NJ_LO_Supply Air Temp. Reset Flag | Supply Air Temp. Reset Flag | Yes | Yes | Yes | Yes | [6 empty] | 2021-05-06
NJ_LO_CAV_BAS OA Rate [cfm] | CAV_BAS OA Rate [cfm] | 2542.8255 | 2542.8255 | 2542.8255 | 2542.8255 | [6 empty] | 2021-05-06
NJ_LO_VAV_BOT WITH REHEAT OA Rate [cfm] | VAV_BOT WITH REHEAT OA Rate [cfm] | 5377.8022 | 4302.174 | 5377.8022 | 4302.174 | [6 empty] | 2021-05-06
NJ_LO_VAV_MID WITH REHEAT OA Rate [cfm] | VAV_MID WITH REHEAT OA Rate [cfm] | 53777.9373 | 43021.7396 | 53777.9373 | 43021.7396 | [6 empty] | 2021-05-06
NJ_LO_VAV_TOP WITH REHEAT OA Rate [cfm] | VAV_TOP WITH REHEAT OA Rate [cfm] | 5377.8022 | 4302.174 | 5377.8022 | 4302.174 | [6 empty] | 2021-05-06
NJ_LO_AIRLOOP DATACENTER BASEMENT OA Rate [cfm] | AIRLOOP DATACENTER BASEMENT OA Rate [cfm] | 716.9654 | 716.9654 | 716.9654 | 716.9654 | [6 empty] | 2021-05-06
NJ_LO_VAV_bot_WITH_REHEAT ERV Flag | VAV_bot_WITH_REHEAT ERV Flag | Yes | Yes | Yes | Yes | [6 empty] | 2021-05-06
NJ_LO_VAV_mid_WITH_REHEAT ERV Flag | VAV_mid_WITH_REHEAT ERV Flag | Yes | Yes | Yes | Yes | [6 empty] | 2021-05-06
NJ_LO_VAV_top_WITH_REHEAT ERV Flag | VAV_top_WITH_REHEAT ERV Flag | Yes | Yes | Yes | Yes | [6 empty] | 2021-05-06
NJ_LO_COOLSYS1 CHILLER1 Capacity [ton] | COOLSYS1 CHILLER1 Capacity [ton] | 422.5783 | 381.5563 | 404.6378 | 366.2686 | [6 empty] | 2021-05-06
NJ_LO_COOLSYS1 CHILLER2 Capacity [ton] | COOLSYS1 CHILLER2 Capacity [ton] | 422.5783 | 381.5563 | 404.6378 | 366.2686 | [6 empty] | 2021-05-06
NJ_LO_TOWERWATERSYS COOLTOWER 1 Capacity [ton] | TOWERWATERSYS COOLTOWER 1 Capacity [ton] | 401.1091 | 362.1612 | 384.0702 | 347.6558 | [6 empty] | 2021-05-06
NJ_LO_TOWERWATERSYS COOLTOWER 2 Capacity [ton] | TOWERWATERSYS COOLTOWER 2 Capacity [ton] | 401.1091 | 362.1612 | 384.0702 | 347.6558 | [6 empty] | 2021-05-06
NJ_LO_HEATSYS1 BOILER Capacity [MMBTU/h] | HEATSYS1 BOILER Capacity [MMBTU/h] | 4275.9294 | 3800.5569 | 4356.5006 | 3853.4927 | [6 empty] | 2021-05-06
NJ_LO_COOLSYS1 PUMP Flow Rate [gal/min] | COOLSYS1 PUMP Flow Rate [gal/min] | 0 | 0 | 0 | 0 | [6 empty] | 2021-05-06
NJ_LO_COOLSYS1 CHILLER1 PUMP Flow Rate [gal/min] | COOLSYS1 CHILLER1 PUMP Flow Rate [gal/min] | 665.9466 | 598.3592 | 637.5571 | 576.9866 | [6 empty] | 2021-05-06
NJ_LO_COOLSYS1 CHILLER2 PUMP Flow Rate [gal/min] | COOLSYS1 CHILLER2 PUMP Flow Rate [gal/min] | 665.9466 | 598.3592 | 637.5571 | 576.9866 | [6 empty] | 2021-05-06
NJ_LO_COOLSYS1 PUMP SECONDARY Flow Rate [gal/min] | COOLSYS1 PUMP SECONDARY Flow Rate [gal/min] | 1331.8931 | 1196.7168 | 1275.1141 | 1153.9733 | [6 empty] | 2021-05-06
NJ_LO_HEATSYS1 PUMP Flow Rate [gal/min] | HEATSYS1 PUMP Flow Rate [gal/min] | 877.691 | 780.1149 | 894.2293 | 790.9803 | [6 empty] | 2021-05-06
NJ_LO_TOWERWATERSYS PUMP Flow Rate [gal/min] | TOWERWATERSYS PUMP Flow Rate [gal/min] | 2331.424 | 2105.0814 | 2232.3595 | 2020.7577 | [6 empty] | 2021-05-06
NJ_LO_PLANT CIRC PUMP Flow Rate [gal/min] | PLANT CIRC PUMP Flow Rate [gal/min] | 208.148 | 207.3159 | 209.0372 | 208.2003 | [6 empty] | 2021-05-06
NJ_LO_COOLSYS1 PUMP SECONDARY Pressure setpoint reset [yes,no] | COOLSYS1 PUMP SECONDARY Pressure setpoint reset [yes,no] | pump_ride_on_curve | pump_ride_on_curve | pump_ride_on_curve | pump_ride_on_curve | [6 empty] | 2021-05-06
NJ_LO_COOLSYS1 CHILLER1 PUMP Pump Power [hp] | COOLSYS1 CHILLER1 PUMP Pump Power [hp] | 3.5925 | 3.196 | 3.4394 | 3.0818 | [6 empty] | 2021-05-06
NJ_LO_COOLSYS1 CHILLER2 PUMP Pump Power [hp] | COOLSYS1 CHILLER2 PUMP Pump Power [hp] | 3.5925 | 3.196 | 3.4394 | 3.0818 | [6 empty] | 2021-05-06
NJ_LO_COOLSYS1 PUMP SECONDARY Pump Power [hp] | COOLSYS1 PUMP SECONDARY Pump Power [hp] | 21.5553 | 19.1759 | 20.6364 | 18.4909 | [6 empty] | 2021-05-06
NJ_LO_HEATSYS1 PUMP Pump Power [hp] | HEATSYS1 PUMP Pump Power [hp] | 18.9718 | 16.6957 | 19.3293 | 16.9282 | [6 empty] | 2021-05-06
NJ_LO_TOWERWATERSYS PUMP Pump Power [hp] | TOWERWATERSYS PUMP Pump Power [hp] | 41.7414 | 37.3162 | 39.9693 | 35.821 | [6 empty] | 2021-05-06
NJ_LO_PLANT CIRC PUMP Pump Power [hp] | PLANT CIRC PUMP Pump Power [hp] | 4.4915 | 4.4293 | 4.5107 | 4.4482 | [6 empty] | 2021-05-06
NJ_LO_Datacenter PLANT CIRC PUMP Pump Power [hp] | Datacenter PLANT CIRC PUMP Pump Power [hp] | 4.4915 | 4.4293 | 4.5107 | 4.4482 | [6 empty] | 2021-05-06
NJ_LO_ZN_VAV_BOXes_Max_Reheat_Water_Flow_GPM | ZN_VAV_BOXes_Max_Reheat_Water_Flow_GPM | 467.2516 | 449.6469 | 457.0144 | 439.0135 | [6 empty] | 2021-05-06
NJ_LO_COOLSYS1 PUMP SECONDARY VSD | COOLSYS1 PUMP SECONDARY VSD | No | No | No | No | [6 empty] | 2021-05-06
NJ_LO_HEATSYS1 PUMP VSD | HEATSYS1 PUMP VSD | No | No | No | No | [6 empty] | 2021-05-06
NJ_LO_DATACENTER BASEMENT Cooling Capacity [ton] | DATACENTER BASEMENT Cooling Capacity [ton] | 121.7781 | 121.4176 | 122.2035 | 121.8415 | [6 empty] | 2021-05-06
NJ_LO_DATACENTER BOT Cooling Capacity [ton] | DATACENTER BOT Cooling Capacity [ton] | 2.6586 | 2.6352 | 2.6768 | 2.6532 | [6 empty] | 2021-05-06
NJ_LO_DATACENTER MID Cooling Capacity [ton] | DATACENTER MID Cooling Capacity [ton] | 25.4427 | 25.2372 | 25.6328 | 25.4254 | [6 empty] | 2021-05-06
NJ_LO_DATACENTER TOP Cooling Capacity [ton] | DATACENTER TOP Cooling Capacity [ton] | 2.5929 | 2.573 | 2.6115 | 2.5914 | [6 empty] | 2021-05-06
id | item | Zone4A(NJ-Newark-NJ) ASHRAE901-state_STD2016 | Zone4A(NJ-Newark-NJ) ASHRAE901-state_STD2019 | Zone5A(NJ-Allentown-PA) ASHRAE901-state_STD2016 | Zone5A(NJ-Allentown-PA) ASHRAE901-state_STD2019 | [6 empty] | 2021-05-06
NJ_RS_PSZ-AC:1 Cooling Capacity [ton] | PSZ-AC:1 Cooling Capacity [ton] | 10.8098 | 10.4354 | 10.1732 | 9.8003 | [6 empty] | 2021-05-06
NJ_RS_PSZ-AC:2 Cooling Capacity [ton] | PSZ-AC:2 Cooling Capacity [ton] | 50.5947 | 48.8608 | 48.1284 | 46.5269 | [6 empty] | 2021-05-06
NJ_RS_PSZ-AC:3 Cooling Capacity [ton] | PSZ-AC:3 Cooling Capacity [ton] | 6.7569 | 6.5905 | 6.313 | 6.1527 | [6 empty] | 2021-05-06
NJ_RS_PSZ-AC:4 Cooling Capacity [ton] | PSZ-AC:4 Cooling Capacity [ton] | 5.5526 | 5.3875 | 5.1208 | 4.9545 | [6 empty] | 2021-05-06
NJ_RS_PSZ-AC:1 Supply Flow Rate [cfm] | PSZ-AC:1 Supply Flow Rate [cfm] | 4110.6272 | 3856.3616 | 3941.1168 | 3665.6624 | [6 empty] | 2021-05-06
NJ_RS_PSZ-AC:2 Supply Flow Rate [cfm] | PSZ-AC:2 Supply Flow Rate [cfm] | 15531.3904 | 14705.0272 | 15298.3136 | 14493.1392 | [6 empty] | 2021-05-06
NJ_RS_PSZ-AC:3 Supply Flow Rate [cfm] | PSZ-AC:3 Supply Flow Rate [cfm] | 2373.1456 | 2288.3904 | 2288.3904 | 2203.6352 | [6 empty] | 2021-05-06
NJ_RS_PSZ-AC:4 Supply Flow Rate [cfm] | PSZ-AC:4 Supply Flow Rate [cfm] | 1843.4256 | 1758.6704 | 1737.4816 | 1652.7264 | [6 empty] | 2021-05-06
NJ_RS_PSZ-AC:1 OA Rate [cfm] | PSZ-AC:1 OA Rate [cfm] | 490.669 | 490.669 | 490.669 | 490.669 | [6 empty] | 2021-05-06
NJ_RS_PSZ-AC:2 OA Rate [cfm] | PSZ-AC:2 OA Rate [cfm] | 4005.1282 | 4005.1282 | 4005.1282 | 4005.1282 | [6 empty] | 2021-05-06
NJ_RS_PSZ-AC:3 OA Rate [cfm] | PSZ-AC:3 OA Rate [cfm] | 377.3937 | 377.3937 | 377.3937 | 377.3937 | [6 empty] | 2021-05-06
NJ_RS_PSZ-AC:4 OA Rate [cfm] | PSZ-AC:4 OA Rate [cfm] | 377.3937 | 377.3937 | 377.3937 | 377.3937 | [6 empty] | 2021-05-06
NJ_RS_PSZ-AC:1 OA Damper [gravity, motorized] | PSZ-AC:1 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2021-05-06
NJ_RS_PSZ-AC:2 OA Damper [gravity, motorized] | PSZ-AC:2 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2021-05-06
NJ_RS_PSZ-AC:3 OA Damper [gravity, motorized] | PSZ-AC:3 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2021-05-06
NJ_RS_PSZ-AC:4 OA Damper [gravity, motorized] | PSZ-AC:4 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2021-05-06
NJ_RS_PSZ-AC:1 Heating Capacity [kBtu/hr] | PSZ-AC:1 Heating Capacity [kBtu/hr] | 183.0187 | 172.6305 | 175.7893 | 164.5342 | [6 empty] | 2021-05-06
NJ_RS_PSZ-AC:2 Heating Capacity [kBtu/hr] | PSZ-AC:2 Heating Capacity [kBtu/hr] | 817.0689 | 781.8462 | 814.2937 | 779.0903 | [6 empty] | 2021-05-06
NJ_RS_PSZ-AC:3 Heating Capacity [kBtu/hr] | PSZ-AC:3 Heating Capacity [kBtu/hr] | 111.9491 | 109.1739 | 108.5868 | 106.1071 | [6 empty] | 2021-05-06
NJ_RS_PSZ-AC:4 Heating Capacity [kBtu/hr] | PSZ-AC:4 Heating Capacity [kBtu/hr] | 92.0965 | 89.1783 | 88.3938 | 85.5081 | [6 empty] | 2021-05-06
id | item | Zone4A(NJ-Newark-NJ) ASHRAE901-state_STD2016 | Zone4A(NJ-Newark-NJ) ASHRAE901-state_STD2019 | Zone5A(NJ-Allentown-PA) ASHRAE901-state_STD2016 | Zone5A(NJ-Allentown-PA) ASHRAE901-state_STD2019 | [6 empty] | 2021-05-06
NJ_PS_VAV_POD_1 Cooling Capacity [ton] | VAV_POD_1 Cooling Capacity [ton] | 19.302 | 18.6488 | 19.2041 | 18.5216 | [6 empty] | 2021-05-06
NJ_PS_VAV_POD_2 Cooling Capacity [ton] | VAV_POD_2 Cooling Capacity [ton] | 19.0403 | 18.4487 | 18.9293 | 18.4264 | [6 empty] | 2021-05-06
NJ_PS_VAV_POD_3 Cooling Capacity [ton] | VAV_POD_3 Cooling Capacity [ton] | 17.5582 | 16.7745 | 17.4729 | 16.6617 | [6 empty] | 2021-05-06
NJ_PS_VAV_OTHER Cooling Capacity [ton] | VAV_OTHER Cooling Capacity [ton] | 26.7361 | 25.2163 | 26.7502 | 25.1769 | [6 empty] | 2021-05-06
NJ_PS_PSZ-AC_1:6 Cooling Capacity [ton] | PSZ-AC_1:6 Cooling Capacity [ton] | 8.4665 | 8.1079 | 8.2375 | 7.9743 | [6 empty] | 2021-05-06
NJ_PS_PSZ-AC_2:5 Cooling Capacity [ton] | PSZ-AC_2:5 Cooling Capacity [ton] | 5.4315 | 5.4502 | 5.4623 | 5.4382 | [6 empty] | 2021-05-06
NJ_PS_PSZ-AC_2:7 Cooling Capacity [ton] | PSZ-AC_2:7 Cooling Capacity [ton] | 10.5074 | 10.5074 | 10.5074 | 10.5074 | [6 empty] | 2021-05-06
NJ_PS_VAV_POD_1 Supply Flow Rate [cfm] | VAV_POD_1 Supply Flow Rate [cfm] | 5784.5424 | 5593.8432 | 5763.3536 | 5551.4656 | [6 empty] | 2021-05-06
NJ_PS_VAV_POD_2 Supply Flow Rate [cfm] | VAV_POD_2 Supply Flow Rate [cfm] | 5720.976 | 5530.2768 | 5678.5984 | 5530.2768 | [6 empty] | 2021-05-06
NJ_PS_VAV_POD_3 Supply Flow Rate [cfm] | VAV_POD_3 Supply Flow Rate [cfm] | 5276.0112 | 5042.9344 | 5233.6336 | 5000.5568 | [6 empty] | 2021-05-06
NJ_PS_VAV_OTHER Supply Flow Rate [cfm] | VAV_OTHER Supply Flow Rate [cfm] | 8030.5552 | 7564.4016 | 8030.5552 | 7564.4016 | [6 empty] | 2021-05-06
NJ_PS_PSZ-AC_2:5 Supply Flow Rate [cfm] | PSZ-AC_2:5 Supply Flow Rate [cfm] | 1631.5376 | 1631.5376 | 1631.5376 | 1631.5376 | [6 empty] | 2021-05-06
NJ_PS_PSZ-AC_1:6 Supply Flow Rate [cfm] | PSZ-AC_1:6 Supply Flow Rate [cfm] | 2542.656 | 2436.712 | 2563.8448 | 2457.9008 | [6 empty] | 2021-05-06
NJ_PS_PSZ-AC_2:7 Supply Flow Rate [cfm] | PSZ-AC_2:7 Supply Flow Rate [cfm] | 3157.1312 | 3157.1312 | 3157.1312 | 3157.1312 | [6 empty] | 2021-05-06
NJ_PS_Supply Air Temp. Reset Flag | Supply Air Temp. Reset Flag | Yes | Yes | Yes | Yes | [6 empty] | 2021-05-06
NJ_PS_VAV_POD_1 OA Rate [cfm] | VAV_POD_1 OA Rate [cfm] | 5792.2128 | 5596.1952 | 5762.8239 | 5558.0341 | [6 empty] | 2021-05-06
NJ_PS_VAV_POD_2 OA Rate [cfm] | VAV_POD_2 OA Rate [cfm] | 5713.6871 | 5536.1461 | 5678.9798 | 5529.4504 | [6 empty] | 2021-05-06
NJ_PS_VAV_POD_3 OA Rate [cfm] | VAV_POD_3 OA Rate [cfm] | 5268.913 | 5033.7597 | 5241.6854 | 4999.9 | [6 empty] | 2021-05-06
NJ_PS_VAV_OTHER OA Rate [cfm] | VAV_OTHER OA Rate [cfm] | 3736.1787 | 2988.8921 | 3736.1787 | 2988.8921 | [6 empty] | 2021-05-06
NJ_PS_PSZ-AC_2:5 OA Rate [cfm] | PSZ-AC_2:5 OA Rate [cfm] | 1152.7343 | 1152.7343 | 1152.7343 | 1152.7343 | [6 empty] | 2021-05-06
NJ_PS_PSZ-AC_1:6 OA Rate [cfm] | PSZ-AC_1:6 OA Rate [cfm] | 539.9118 | 539.9118 | 539.9118 | 539.9118 | [6 empty] | 2021-05-06
NJ_PS_PSZ-AC_2:7 OA Rate [cfm] | PSZ-AC_2:7 OA Rate [cfm] | 3153.0841 | 3153.0841 | 3153.0841 | 3153.0841 | [6 empty] | 2021-05-06
NJ_PS_VAV_POD_1 OA Damper [gravity, motorized] | VAV_POD_1 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2021-05-06
NJ_PS_VAV_POD_2 OA Damper [gravity, motorized] | VAV_POD_2 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2021-05-06
NJ_PS_VAV_POD_3 OA Damper [gravity, motorized] | VAV_POD_3 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2021-05-06
NJ_PS_VAV_OTHER OA Damper [gravity, motorized] | VAV_OTHER OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2021-05-06
NJ_PS_PSZ-AC_2:5 OA Damper [gravity, motorized] | PSZ-AC_2:5 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2021-05-06
NJ_PS_PSZ-AC_1:6 OA Damper [gravity, motorized] | PSZ-AC_1:6 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2021-05-06
NJ_PS_PSZ-AC_2:7 OA Damper [gravity, motorized] | PSZ-AC_2:7 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2021-05-06
NJ_PS_VAV_POD_1 (economizer) | VAV_POD_1 (economizer) | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialDryBulb | DifferentialDryBulb | [6 empty] | 2021-05-06
NJ_PS_VAV_POD_2 (economizer) | VAV_POD_2 (economizer) | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialDryBulb | DifferentialDryBulb | [6 empty] | 2021-05-06
NJ_PS_VAV_POD_3 (economizer) | VAV_POD_3 (economizer) | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialDryBulb | DifferentialDryBulb | [6 empty] | 2021-05-06
NJ_PS_VAV_OTHER (economizer) | VAV_OTHER (economizer) | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialDryBulb | DifferentialDryBulb | [6 empty] | 2021-05-06
NJ_PS_PSZ-AC_2:5 (economizer) | PSZ-AC_2:5 (economizer) | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialDryBulb | DifferentialDryBulb | [6 empty] | 2021-05-06
NJ_PS_PSZ-AC_1:6 (economizer) | PSZ-AC_1:6 (economizer) | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialDryBulb | DifferentialDryBulb | [6 empty] | 2021-05-06
NJ_PS_PSZ-AC_2:7 (economizer) | PSZ-AC_2:7 (economizer) | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialDryBulb | DifferentialDryBulb | [6 empty] | 2021-05-06
NJ_PS_VAV_Pod_1_ERV Flag | VAV_Pod_1_ERV Flag | Yes | Yes | Yes | Yes | [6 empty] | 2021-05-06
NJ_PS_VAV_Pod_2_ERV Flag | VAV_Pod_2_ERV Flag | Yes | Yes | Yes | Yes | [6 empty] | 2021-05-06
NJ_PS_VAV_Pod_3_ERV Flag | VAV_Pod_3_ERV Flag | Yes | Yes | Yes | Yes | [6 empty] | 2021-05-06
NJ_PS_VAV_OTHER_ERV Flag | VAV_OTHER_ERV Flag | Yes | Yes | Yes | Yes | [6 empty] | 2021-05-06
NJ_PS_PSZ_AC_2_5_ERV Flag | PSZ_AC_2_5_ERV Flag | Yes | Yes | Yes | Yes | [6 empty] | 2021-05-06
NJ_PS_PSZ_AC_2_7_ERV Flag | PSZ_AC_2_7_ERV Flag | Yes | Yes | Yes | Yes | [6 empty] | 2021-05-06
NJ_PS_HEATSYS1 Capacity [MMBTU/h] | HEATSYS1 Capacity [MMBTU/h] | 1.0477 | 1.0019 | 1.0634 | 1.0173 | [6 empty] | 2021-05-06
NJ_PS_HEATSYS1 Flow Rate [gal/min] | HEATSYS1 Flow Rate [gal/min] | 107.5268 | 102.8313 | 109.1431 | 104.4119 | [6 empty] | 2021-05-06
NJ_PS_VAV_POD_1 Fan Power [hp] | VAV_POD_1 Fan Power [hp] | 8.5453 | 8.2561 | 8.5019 | 8.1998 | [6 empty] | 2021-05-06
NJ_PS_VAV_POD_2 Fan Power [hp] | VAV_POD_2 Fan Power [hp] | 8.4294 | 8.1675 | 8.3803 | 8.1576 | [6 empty] | 2021-05-06
NJ_PS_VAV_POD_3 Fan Power [hp] | VAV_POD_3 Fan Power [hp] | 7.7732 | 7.4263 | 7.7355 | 7.3763 | [6 empty] | 2021-05-06
NJ_PS_VAV_OTHER Fan Power [hp] | VAV_OTHER Fan Power [hp] | 11.7468 | 11.079 | 11.7529 | 11.0617 | [6 empty] | 2021-05-06
NJ_PS_HEATSYS1 Pump Power [hp] | HEATSYS1 Pump Power [hp] | 2.3243 | 2.2008 | 2.3592 | 2.2346 | [6 empty] | 2021-05-06
NJ_PS_PSZ-AC_1:6 Heating Capacity [kBtu/hr] | PSZ-AC_1:6 Heating Capacity [kBtu/hr] | 210.3811 | 201.7929 | 211.6125 | 203.0432 | [6 empty] | 2021-05-06
NJ_PS_PSZ-AC_2:5 Heating Capacity [kBtu/hr] | PSZ-AC_2:5 Heating Capacity [kBtu/hr] | 133.5376 | 133.7448 | 137.1428 | 136.8789 | [6 empty] | 2021-05-06
NJ_PS_PSZ-AC_2:7 Heating Capacity [kBtu/hr] | PSZ-AC_2:7 Heating Capacity [kBtu/hr] | 316.9532 | 316.9532 | 326.5525 | 326.5525 | [6 empty] | 2021-05-06
NJ_PS_ZN_VAV_BOXes_Max_Reheat_Water_Flow_GPM | ZN_VAV_BOXes_Max_Reheat_Water_Flow_GPM | 71.2345 | 68.0973 | 70.1057 | 67.0667 | [6 empty] | 2021-05-06
id | item | Zone4A(NJ-Newark-NJ) ASHRAE901-state_STD2016 | Zone4A(NJ-Newark-NJ) ASHRAE901-state_STD2019 | Zone5A(NJ-Allentown-PA) ASHRAE901-state_STD2016 | Zone5A(NJ-Allentown-PA) ASHRAE901-state_STD2019 | [6 empty] | 2021-05-06
NJ_SH_SAC_FRONTOFFICE Cooling Capacity [ton] | SAC_FRONTOFFICE Cooling Capacity [ton] | 2.4341 | 2.3131 | 2.2776 | 2.1645 | [6 empty] | 2021-05-06
NJ_SH_SAC_FRONTLOUNGE Cooling Capacity [ton] | SAC_FRONTLOUNGE Cooling Capacity [ton] | 6.1695 | 5.8655 | 6.0827 | 5.7747 | [6 empty] | 2021-05-06
NJ_SH_SAC_MEETINGROOM Cooling Capacity [ton] | SAC_MEETINGROOM Cooling Capacity [ton] | 2.8973 | 2.826 | 2.8813 | 2.8014 | [6 empty] | 2021-05-06
NJ_SH_SAC_EXC_EMPLGE_RESTRM Cooling Capacity [ton] | SAC_EXC_EMPLGE_RESTRM Cooling Capacity [ton] | 6.0853 | 6.0372 | 5.906 | 5.8651 | [6 empty] | 2021-05-06
NJ_SH_SAC_FO_ADDAQ SUPPLY FAN Supply Flow Rate [cfm] | SAC_FO_ADDAQ SUPPLY FAN Supply Flow Rate [cfm] | 783.9856 | 741.608 | 762.7968 | 720.4192 | [6 empty] | 2021-05-06
NJ_SH_SAC_FL_ADDAQ SUPPLY FAN Supply Flow Rate [cfm] | SAC_FL_ADDAQ SUPPLY FAN Supply Flow Rate [cfm] | 1843.4256 | 1758.6704 | 1822.2368 | 1737.4816 | [6 empty] | 2021-05-06
NJ_SH_SAC_MR_ADDAQ SUPPLY FAN Supply Flow Rate [cfm] | SAC_MR_ADDAQ SUPPLY FAN Supply Flow Rate [cfm] | 868.7408 | 847.552 | 868.7408 | 847.552 | [6 empty] | 2021-05-06
NJ_SH_SAC_EXC_ADDAQ SUPPLY FAN Supply Flow Rate [cfm] | SAC_EXC_ADDAQ SUPPLY FAN Supply Flow Rate [cfm] | 2182.4464 | 2161.2576 | 2203.6352 | 2182.4464 | [6 empty] | 2021-05-06
NJ_SH_SAC_Exc_EmpLge_RestRm OA Rate [cfm] | SAC_Exc_EmpLge_RestRm OA Rate [cfm] | 199.9928 | 199.9928 | 199.9928 | 199.9928 | [6 empty] | 2021-05-06
NJ_SH_SAC_FrontLounge OA Rate [cfm] | SAC_FrontLounge OA Rate [cfm] | 500.0133 | 500.0133 | 500.0133 | 500.0133 | [6 empty] | 2021-05-06
NJ_SH_SAC_FrontOffice OA Rate [cfm] | SAC_FrontOffice OA Rate [cfm] | 119.2938 | 119.2938 | 119.2938 | 119.2938 | [6 empty] | 2021-05-06
NJ_SH_SAC_MeetingRoom OA Rate [cfm] | SAC_MeetingRoom OA Rate [cfm] | 267.7629 | 267.7629 | 267.7629 | 267.7629 | [6 empty] | 2021-05-06
NJ_SH_SAC_FrontLounge OA Damper [gravity, motorized] | SAC_FrontLounge OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2021-05-06
NJ_SH_SAC_FrontOffice (economizer) | SAC_FrontOffice (economizer) | No | No | No | No | [6 empty] | 2021-05-06
NJ_SH_SAC_FrontLounge (economizer) | SAC_FrontLounge (economizer) | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialDryBulb | DifferentialDryBulb | [6 empty] | 2021-05-06
NJ_SH_SAC_MeetingRoom (economizer) | SAC_MeetingRoom (economizer) | No | No | No | No | [6 empty] | 2021-05-06
NJ_SH_SAC_Exc_EmpLge_RestRm (economizer) | SAC_Exc_EmpLge_RestRm (economizer) | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialDryBulb | DifferentialDryBulb | [6 empty] | 2021-05-06
NJ_SH_SAC_FRONTOFFICE Heating Capacity [kBtu/hr] | SAC_FRONTOFFICE Heating Capacity [kBtu/hr] | 36.8349 | 35.0741 | 35.9328 | 34.1349 | [6 empty] | 2021-05-06
NJ_SH_SAC_FRONTLOUNGE Heating Capacity [kBtu/hr] | SAC_FRONTLOUNGE Heating Capacity [kBtu/hr] | 99.9885 | 96.6321 | 99.885 | 96.5311 | [6 empty] | 2021-05-06
NJ_SH_SAC_MEETINGROOM Heating Capacity [kBtu/hr] | SAC_MEETINGROOM Heating Capacity [kBtu/hr] | 49.0552 | 48.2677 | 49.3938 | 48.5236 | [6 empty] | 2021-05-06
NJ_SH_SAC_EXC_EMPLGE_RESTRM Heating Capacity [kBtu/hr] | SAC_EXC_EMPLGE_RESTRM Heating Capacity [kBtu/hr] | 92.804 | 92.1492 | 93.1998 | 92.5415 | [6 empty] | 2021-05-06
id | item | Zone4A(NJ-Newark-NJ) ASHRAE901-state_STD2016 | Zone4A(NJ-Newark-NJ) ASHRAE901-state_STD2019 | Zone5A(NJ-Allentown-PA) ASHRAE901-state_STD2016 | Zone5A(NJ-Allentown-PA) ASHRAE901-state_STD2019 | [6 empty] | 2021-05-06
NJ_MA_SPLIT GSW COOLING COIL Cooling Capacity [ton] | SPLIT GSW COOLING COIL Cooling Capacity [ton] | 0.91911 | 0.90504 | 0.83969 | 0.82564 | [6 empty] | 2021-05-06
NJ_MA_SPLIT GNW COOLING COIL Cooling Capacity [ton] | SPLIT GNW COOLING COIL Cooling Capacity [ton] | 0.8803 | 0.8668 | 0.80251 | 0.78897 | [6 empty] | 2021-05-06
NJ_MA_SPLIT OFFICE COOLING COIL Cooling Capacity [ton] | SPLIT OFFICE COOLING COIL Cooling Capacity [ton] | 1.754 | 1.6315 | 1.7431 | 1.6162 | [6 empty] | 2021-05-06
NJ_MA_SPLIT GNE COOLING COIL Cooling Capacity [ton] | SPLIT GNE COOLING COIL Cooling Capacity [ton] | 0.77893 | 0.76705 | 0.7 | 0.6881 | [6 empty] | 2021-05-06
NJ_MA_SPLIT GN1 COOLING COIL Cooling Capacity [ton] | SPLIT GN1 COOLING COIL Cooling Capacity [ton] | 0.65682 | 0.64717 | 0.59174 | 0.58244 | [6 empty] | 2021-05-06
NJ_MA_SPLIT GN2 COOLING COIL Cooling Capacity [ton] | SPLIT GN2 COOLING COIL Cooling Capacity [ton] | 0.65486 | 0.64526 | 0.58967 | 0.58042 | [6 empty] | 2021-05-06
NJ_MA_SPLIT GS1 COOLING COIL Cooling Capacity [ton] | SPLIT GS1 COOLING COIL Cooling Capacity [ton] | 0.69982 | 0.68943 | 0.63669 | 0.62634 | [6 empty] | 2021-05-06
NJ_MA_SPLIT GS2 COOLING COIL Cooling Capacity [ton] | SPLIT GS2 COOLING COIL Cooling Capacity [ton] | 0.73177 | 0.7178 | 0.66896 | 0.65408 | [6 empty] | 2021-05-06
NJ_MA_SPLIT MSW COOLING COIL Cooling Capacity [ton] | SPLIT MSW COOLING COIL Cooling Capacity [ton] | 2.182 | 2.1502 | 2.0058 | 1.9746 | [6 empty] | 2021-05-06
NJ_MA_SPLIT MNW COOLING COIL Cooling Capacity [ton] | SPLIT MNW COOLING COIL Cooling Capacity [ton] | 2.1053 | 2.075 | 1.9366 | 1.9025 | [6 empty] | 2021-05-06
NJ_MA_SPLIT MSE COOLING COIL Cooling Capacity [ton] | SPLIT MSE COOLING COIL Cooling Capacity [ton] | 1.9356 | 1.908 | 1.746 | 1.7187 | [6 empty] | 2021-05-06
NJ_MA_SPLIT MNE COOLING COIL Cooling Capacity [ton] | SPLIT MNE COOLING COIL Cooling Capacity [ton] | 1.7502 | 1.721 | 1.5754 | 1.5463 | [6 empty] | 2021-05-06
NJ_MA_SPLIT MN1 COOLING COIL Cooling Capacity [ton] | SPLIT MN1 COOLING COIL Cooling Capacity [ton] | 1.4457 | 1.4271 | 1.3061 | 1.2883 | [6 empty] | 2021-05-06
NJ_MA_SPLIT MN2 COOLING COIL Cooling Capacity [ton] | SPLIT MN2 COOLING COIL Cooling Capacity [ton] | 1.4402 | 1.4218 | 1.3004 | 1.2827 | [6 empty] | 2021-05-06
NJ_MA_SPLIT MS1 COOLING COIL Cooling Capacity [ton] | SPLIT MS1 COOLING COIL Cooling Capacity [ton] | 1.5236 | 1.5039 | 1.3885 | 1.3691 | [6 empty] | 2021-05-06
NJ_MA_SPLIT MS2 COOLING COIL Cooling Capacity [ton] | SPLIT MS2 COOLING COIL Cooling Capacity [ton] | 1.5181 | 1.4986 | 1.3828 | 1.3635 | [6 empty] | 2021-05-06
NJ_MA_SPLIT TSW COOLING COIL Cooling Capacity [ton] | SPLIT TSW COOLING COIL Cooling Capacity [ton] | 1.3641 | 1.3468 | 1.2572 | 1.2401 | [6 empty] | 2021-05-06
NJ_MA_SPLIT TNW COOLING COIL Cooling Capacity [ton] | SPLIT TNW COOLING COIL Cooling Capacity [ton] | 1.3083 | 1.292 | 1.2086 | 1.1923 | [6 empty] | 2021-05-06
NJ_MA_SPLIT TSE COOLING COIL Cooling Capacity [ton] | SPLIT TSE COOLING COIL Cooling Capacity [ton] | 1.2376 | 1.2232 | 1.1232 | 1.1091 | [6 empty] | 2021-05-06
NJ_MA_SPLIT TNE COOLING COIL Cooling Capacity [ton] | SPLIT TNE COOLING COIL Cooling Capacity [ton] | 1.1551 | 1.1424 | 1.0479 | 1.0353 | [6 empty] | 2021-05-06
NJ_MA_SPLIT TN1 COOLING COIL Cooling Capacity [ton] | SPLIT TN1 COOLING COIL Cooling Capacity [ton] | 0.93681 | 0.92689 | 0.83001 | 0.81893 | [6 empty] | 2021-05-06
NJ_MA_SPLIT TN2 COOLING COIL Cooling Capacity [ton] | SPLIT TN2 COOLING COIL Cooling Capacity [ton] | 0.9381 | 0.9282 | 0.85832 | 0.84849 | [6 empty] | 2021-05-06
NJ_MA_SPLIT TS1 COOLING COIL Cooling Capacity [ton] | SPLIT TS1 COOLING COIL Cooling Capacity [ton] | 1.0164 | 1.0052 | 0.93074 | 0.91973 | [6 empty] | 2021-05-06
NJ_MA_SPLIT TS2 COOLING COIL Cooling Capacity [ton] | SPLIT TS2 COOLING COIL Cooling Capacity [ton] | 1.0185 | 1.0072 | 0.93272 | 0.92165 | [6 empty] | 2021-05-06
NJ_MA_Split GN1 Furnace with DX Cooling OA Rate [cfm] | Split GN1 Furnace with DX Cooling OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | [6 empty] | 2021-05-06
NJ_MA_Split GN2 Furnace with DX Cooling OA Rate [cfm] | Split GN2 Furnace with DX Cooling OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | [6 empty] | 2021-05-06
NJ_MA_Split GNE Furnace with DX Cooling OA Rate [cfm] | Split GNE Furnace with DX Cooling OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | [6 empty] | 2021-05-06
NJ_MA_Split GNW Furnace with DX Cooling OA Rate [cfm] | Split GNW Furnace with DX Cooling OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | [6 empty] | 2021-05-06
NJ_MA_Split GS1 Furnace with DX Cooling OA Rate [cfm] | Split GS1 Furnace with DX Cooling OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | [6 empty] | 2021-05-06
NJ_MA_Split GS2 Furnace with DX Cooling OA Rate [cfm] | Split GS2 Furnace with DX Cooling OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | [6 empty] | 2021-05-06
NJ_MA_Split GSW Furnace with DX Cooling OA Rate [cfm] | Split GSW Furnace with DX Cooling OA Rate [cfm] | 56.9945 | 56.9945 | 56.9945 | 56.9945 | [6 empty] | 2021-05-06
NJ_MA_Split MN1 Furnace with DX Cooling OA Rate [cfm] | Split MN1 Furnace with DX Cooling OA Rate [cfm] | 109.9824 | 109.9824 | 109.9824 | 109.9824 | [6 empty] | 2021-05-06
NJ_MA_Split MN2 Furnace with DX Cooling OA Rate [cfm] | Split MN2 Furnace with DX Cooling OA Rate [cfm] | 109.9824 | 109.9824 | 109.9824 | 109.9824 | [6 empty] | 2021-05-06
NJ_MA_Split MNE Furnace with DX Cooling OA Rate [cfm] | Split MNE Furnace with DX Cooling OA Rate [cfm] | 109.9824 | 109.9824 | 109.9824 | 109.9824 | [6 empty] | 2021-05-06
NJ_MA_Split MNW Furnace with DX Cooling OA Rate [cfm] | Split MNW Furnace with DX Cooling OA Rate [cfm] | 109.9824 | 109.9824 | 109.9824 | 109.9824 | [6 empty] | 2021-05-06
NJ_MA_Split MS1 Furnace with DX Cooling OA Rate [cfm] | Split MS1 Furnace with DX Cooling OA Rate [cfm] | 109.9824 | 109.9824 | 109.9824 | 109.9824 | [6 empty] | 2021-05-06
NJ_MA_Split MS2 Furnace with DX Cooling OA Rate [cfm] | Split MS2 Furnace with DX Cooling OA Rate [cfm] | 109.9824 | 109.9824 | 109.9824 | 109.9824 | [6 empty] | 2021-05-06
NJ_MA_Split MSE Furnace with DX Cooling OA Rate [cfm] | Split MSE Furnace with DX Cooling OA Rate [cfm] | 109.9824 | 109.9824 | 109.9824 | 109.9824 | [6 empty] | 2021-05-06
NJ_MA_Split MSW Furnace with DX Cooling OA Rate [cfm] | Split MSW Furnace with DX Cooling OA Rate [cfm] | 109.9824 | 109.9824 | 109.9824 | 109.9824 | [6 empty] | 2021-05-06
NJ_MA_Split Office Furnace with DX Cooling OA Rate [cfm] | Split Office Furnace with DX Cooling OA Rate [cfm] | 80.7372 | 80.7372 | 80.7372 | 80.7372 | [6 empty] | 2021-05-06
NJ_MA_Split TN1 Furnace with DX Cooling OA Rate [cfm] | Split TN1 Furnace with DX Cooling OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | [6 empty] | 2021-05-06
NJ_MA_Split TN2 Furnace with DX Cooling OA Rate [cfm] | Split TN2 Furnace with DX Cooling OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | [6 empty] | 2021-05-06
NJ_MA_Split TNE Furnace with DX Cooling OA Rate [cfm] | Split TNE Furnace with DX Cooling OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | [6 empty] | 2021-05-06
NJ_MA_Split TNW Furnace with DX Cooling OA Rate [cfm] | Split TNW Furnace with DX Cooling OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | [6 empty] | 2021-05-06
NJ_MA_Split TS1 Furnace with DX Cooling OA Rate [cfm] | Split TS1 Furnace with DX Cooling OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | [6 empty] | 2021-05-06
NJ_MA_Split TS2 Furnace with DX Cooling OA Rate [cfm] | Split TS2 Furnace with DX Cooling OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | [6 empty] | 2021-05-06
NJ_MA_Split TSE Furnace with DX Cooling OA Rate [cfm] | Split TSE Furnace with DX Cooling OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | [6 empty] | 2021-05-06
NJ_MA_Split TSW Furnace with DX Cooling OA Rate [cfm] | Split TSW Furnace with DX Cooling OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | [6 empty] | 2021-05-06
NJ_MA_SPLIT GSW HEATING COIL Heating Capacity [kBtu/hr] | SPLIT GSW HEATING COIL Heating Capacity [kBtu/hr] | 9.5029 | 9.5607 | 9.2154 | 9.2743 | [6 empty] | 2021-05-06
NJ_MA_SPLIT GNW HEATING COIL Heating Capacity [kBtu/hr] | SPLIT GNW HEATING COIL Heating Capacity [kBtu/hr] | 9.4405 | 9.4984 | 9.1461 | 9.2051 | [6 empty] | 2021-05-06
NJ_MA_SPLIT OFFICE HEATING COIL Heating Capacity [kBtu/hr] | SPLIT OFFICE HEATING COIL Heating Capacity [kBtu/hr] | 22.0538 | 22.144 | 21.8207 | 21.9104 | [6 empty] | 2021-05-06
NJ_MA_SPLIT GNE HEATING COIL Heating Capacity [kBtu/hr] | SPLIT GNE HEATING COIL Heating Capacity [kBtu/hr] | 9.4192 | 9.4771 | 9.1252 | 9.1842 | [6 empty] | 2021-05-06
NJ_MA_SPLIT GN1 HEATING COIL Heating Capacity [kBtu/hr] | SPLIT GN1 HEATING COIL Heating Capacity [kBtu/hr] | 6.7887 | 6.8467 | 6.7163 | 6.7753 | [6 empty] | 2021-05-06
NJ_MA_SPLIT GN2 HEATING COIL Heating Capacity [kBtu/hr] | SPLIT GN2 HEATING COIL Heating Capacity [kBtu/hr] | 6.7881 | 6.846 | 6.7156 | 6.7747 | [6 empty] | 2021-05-06
NJ_MA_SPLIT GS1 HEATING COIL Heating Capacity [kBtu/hr] | SPLIT GS1 HEATING COIL Heating Capacity [kBtu/hr] | 6.7394 | 6.7972 | 6.6669 | 6.7258 | [6 empty] | 2021-05-06
NJ_MA_SPLIT GS2 HEATING COIL Heating Capacity [kBtu/hr] | SPLIT GS2 HEATING COIL Heating Capacity [kBtu/hr] | 7.2372 | 7.2964 | 7.164 | 7.2242 | [6 empty] | 2021-05-06
NJ_MA_SPLIT MSW HEATING COIL Heating Capacity [kBtu/hr] | SPLIT MSW HEATING COIL Heating Capacity [kBtu/hr] | 17.8851 | 18.0143 | 16.4173 | 16.5467 | [6 empty] | 2021-05-06
NJ_MA_SPLIT MNW HEATING COIL Heating Capacity [kBtu/hr] | SPLIT MNW HEATING COIL Heating Capacity [kBtu/hr] | 17.9715 | 18.1005 | 16.5024 | 16.6317 | [6 empty] | 2021-05-06
NJ_MA_SPLIT MSE HEATING COIL Heating Capacity [kBtu/hr] | SPLIT MSE HEATING COIL Heating Capacity [kBtu/hr] | 17.835 | 17.9641 | 16.3679 | 16.4973 | [6 empty] | 2021-05-06
NJ_MA_SPLIT MNE HEATING COIL Heating Capacity [kBtu/hr] | SPLIT MNE HEATING COIL Heating Capacity [kBtu/hr] | 17.9213 | 18.0503 | 16.453 | 16.5823 | [6 empty] | 2021-05-06
NJ_MA_SPLIT MN1 HEATING COIL Heating Capacity [kBtu/hr] | SPLIT MN1 HEATING COIL Heating Capacity [kBtu/hr] | 12.1497 | 12.274 | 11.3971 | 11.5222 | [6 empty] | 2021-05-06
NJ_MA_SPLIT MN2 HEATING COIL Heating Capacity [kBtu/hr] | SPLIT MN2 HEATING COIL Heating Capacity [kBtu/hr] | 12.1484 | 12.2727 | 11.3957 | 11.5209 | [6 empty] | 2021-05-06
NJ_MA_SPLIT MS1 HEATING COIL Heating Capacity [kBtu/hr] | SPLIT MS1 HEATING COIL Heating Capacity [kBtu/hr] | 12.0717 | 12.1958 | 11.3904 | 11.4458 | [6 empty] | 2021-05-06
NJ_MA_SPLIT MS2 HEATING COIL Heating Capacity [kBtu/hr] | SPLIT MS2 HEATING COIL Heating Capacity [kBtu/hr] | 12.0703 | 12.1945 | 11.3904 | 11.4445 | [6 empty] | 2021-05-06
NJ_MA_SPLIT TSW HEATING COIL Heating Capacity [kBtu/hr] | SPLIT TSW HEATING COIL Heating Capacity [kBtu/hr] | 12.511 | 12.5724 | 11.6789 | 11.7407 | [6 empty] | 2021-05-06
NJ_MA_SPLIT TNW HEATING COIL Heating Capacity [kBtu/hr] | SPLIT TNW HEATING COIL Heating Capacity [kBtu/hr] | 12.5618 | 12.6234 | 11.7301 | 11.792 | [6 empty] | 2021-05-06
NJ_MA_SPLIT TSE HEATING COIL Heating Capacity [kBtu/hr] | SPLIT TSE HEATING COIL Heating Capacity [kBtu/hr] | 12.4848 | 12.5463 | 11.6528 | 11.7146 | [6 empty] | 2021-05-06
NJ_MA_SPLIT TNE HEATING COIL Heating Capacity [kBtu/hr] | SPLIT TNE HEATING COIL Heating Capacity [kBtu/hr] | 12.5356 | 12.5972 | 11.704 | 11.7659 | [6 empty] | 2021-05-06
NJ_MA_SPLIT TN1 HEATING COIL Heating Capacity [kBtu/hr] | SPLIT TN1 HEATING COIL Heating Capacity [kBtu/hr] | 9.322 | 9.3834 | 8.9608 | 9.0225 | [6 empty] | 2021-05-06
NJ_MA_SPLIT TN2 HEATING COIL Heating Capacity [kBtu/hr] | SPLIT TN2 HEATING COIL Heating Capacity [kBtu/hr] | 9.3213 | 9.3826 | 8.9601 | 9.0218 | [6 empty] | 2021-05-06
NJ_MA_SPLIT TS1 HEATING COIL Heating Capacity [kBtu/hr] | SPLIT TS1 HEATING COIL Heating Capacity [kBtu/hr] | 9.2639 | 9.3252 | 8.9026 | 8.9642 | [6 empty] | 2021-05-06
NJ_MA_SPLIT TS2 HEATING COIL Heating Capacity [kBtu/hr] | SPLIT TS2 HEATING COIL Heating Capacity [kBtu/hr] | 9.2631 | 9.3244 | 8.9018 | 8.9635 | [6 empty] | 2021-05-06
NJ_MA_Split_GSW ERV Flag | Split_GSW ERV Flag | Yes | Yes | Yes | Yes | [6 empty] | 2021-05-06
NJ_MA_Split_GNW ERV Flag | Split_GNW ERV Flag | Yes | Yes | Yes | Yes | [6 empty] | 2021-05-06
NJ_MA_Split_GNE ERV Flag | Split_GNE ERV Flag | Yes | Yes | Yes | Yes | [6 empty] | 2021-05-06
NJ_MA_Split_GN1 ERV Flag | Split_GN1 ERV Flag | Yes | Yes | Yes | Yes | [6 empty] | 2021-05-06
NJ_MA_Split_GN2 ERV Flag | Split_GN2 ERV Flag | Yes | Yes | Yes | Yes | [6 empty] | 2021-05-06
NJ_MA_Split_GS1 ERV Flag | Split_GS1 ERV Flag | Yes | Yes | Yes | Yes | [6 empty] | 2021-05-06
NJ_MA_Split_GS2 ERV Flag | Split_GS2 ERV Flag | Yes | Yes | Yes | Yes | [6 empty] | 2021-05-06
NJ_MA_Split_MSW ERV Flag | Split_MSW ERV Flag | Yes | Yes | Yes | Yes | [6 empty] | 2021-05-06
NJ_MA_Split_MNW ERV Flag | Split_MNW ERV Flag | Yes | Yes | Yes | Yes | [6 empty] | 2021-05-06
NJ_MA_Split_MSE ERV Flag | Split_MSE ERV Flag | Yes | Yes | Yes | Yes | [6 empty] | 2021-05-06
NJ_MA_Split_MNE ERV Flag | Split_MNE ERV Flag | Yes | Yes | Yes | Yes | [6 empty] | 2021-05-06
NJ_MA_Split_MN1 ERV Flag | Split_MN1 ERV Flag | Yes | Yes | Yes | Yes | [6 empty] | 2021-05-06
NJ_MA_Split_MN2 ERV Flag | Split_MN2 ERV Flag | Yes | Yes | Yes | Yes | [6 empty] | 2021-05-06
NJ_MA_Split_MS1 ERV Flag | Split_MS1 ERV Flag | Yes | Yes | Yes | Yes | [6 empty] | 2021-05-06
NJ_MA_Split_MS2 ERV Flag | Split_MS2 ERV Flag | Yes | Yes | Yes | Yes | [6 empty] | 2021-05-06
NJ_MA_Split_TSW ERV Flag | Split_TSW ERV Flag | Yes | Yes | Yes | Yes | [6 empty] | 2021-05-06
NJ_MA_Split_TNW ERV Flag | Split_TNW ERV Flag | Yes | Yes | Yes | Yes | [6 empty] | 2021-05-06
NJ_MA_Split_TSE ERV Flag | Split_TSE ERV Flag | Yes | Yes | Yes | Yes | [6 empty] | 2021-05-06
NJ_MA_Split_TNE ERV Flag | Split_TNE ERV Flag | Yes | Yes | Yes | Yes | [6 empty] | 2021-05-06
NJ_MA_Split_TN1 ERV Flag | Split_TN1 ERV Flag | Yes | Yes | Yes | Yes | [6 empty] | 2021-05-06
NJ_MA_Split_TN2 ERV Flag | Split_TN2 ERV Flag | Yes | Yes | Yes | Yes | [6 empty] | 2021-05-06
NJ_MA_Split_TS1 ERV Flag | Split_TS1 ERV Flag | Yes | Yes | Yes | Yes | [6 empty] | 2021-05-06
NJ_MA_Split_TS2 ERV Flag | Split_TS2 ERV Flag | Yes | Yes | Yes | Yes | [6 empty] | 2021-05-06
id | item | Zone3B(NM-Roswell-NM) ASHRAE901-state_STD2016 | Zone3B(NM-Roswell-NM) ASHRAE901-state_STD2019 | Zone4B(NM-Albuquerque-NM) ASHRAE901-state_STD2016 | Zone4B(NM-Albuquerque-NM) ASHRAE901-state_STD2019 | Zone5B(NM-Gallup-NM) ASHRAE901-state_STD2016 | Zone5B(NM-Gallup-NM) ASHRAE901-state_STD2019 |  |  |  |  | 2021-05-06
NM_SO_PSZ-AC:1 Cooling Capacity [ton] | PSZ-AC:1 Cooling Capacity [ton] | 1.812 | 1.7094 | 1.7472 | 1.629 | 1.7691 | 1.6436 |  |  |  |  | 2021-05-06
NM_SO_PSZ-AC:2 Cooling Capacity [ton] | PSZ-AC:2 Cooling Capacity [ton] | 1.6711 | 1.5786 | 1.5622 | 1.481 | 1.4307 | 1.3449 |  |  |  |  | 2021-05-06
NM_SO_PSZ-AC:3 Cooling Capacity [ton] | PSZ-AC:3 Cooling Capacity [ton] | 1.1507 | 1.1013 | 1.2228 | 1.1715 | 1.1844 | 1.1309 |  |  |  |  | 2021-05-06
NM_SO_PSZ-AC:4 Cooling Capacity [ton] | PSZ-AC:4 Cooling Capacity [ton] | 1.6537 | 1.5732 | 1.5286 | 1.4405 | 1.4132 | 1.3075 |  |  |  |  | 2021-05-06
NM_SO_PSZ-AC:5 Cooling Capacity [ton] | PSZ-AC:5 Cooling Capacity [ton] | 1.4429 | 1.3889 | 1.4888 | 1.4358 | 1.5035 | 1.4475 |  |  |  |  | 2021-05-06
NM_SO_PSZ-AC:1 Supply Flow Rate [cfm] | PSZ-AC:1 Supply Flow Rate [cfm] | 783.9856 | 720.4192 | 783.9856 | 741.608 | 805.1744 | 741.608 |  |  |  |  | 2021-05-06
NM_SO_PSZ-AC:2 Supply Flow Rate [cfm] | PSZ-AC:2 Supply Flow Rate [cfm] | 741.608 | 678.0416 | 699.2304 | 656.8528 | 635.664 | 614.4752 |  |  |  |  | 2021-05-06
NM_SO_PSZ-AC:3 Supply Flow Rate [cfm] | PSZ-AC:3 Supply Flow Rate [cfm] | 508.5312 | 487.3424 | 550.9088 | 529.72 | 529.72 | 508.5312 |  |  |  |  | 2021-05-06
NM_SO_PSZ-AC:4 Supply Flow Rate [cfm] | PSZ-AC:4 Supply Flow Rate [cfm] | 720.4192 | 678.0416 | 678.0416 | 656.8528 | 635.664 | 593.2864 |  |  |  |  | 2021-05-06
NM_SO_PSZ-AC:5 Supply Flow Rate [cfm] | PSZ-AC:5 Supply Flow Rate [cfm] | 656.8528 | 635.664 | 678.0416 | 656.8528 | 678.0416 | 656.8528 |  |  |  |  | 2021-05-06
NM_SO_PSZ-AC:1 OA Rate [cfm] | PSZ-AC:1 OA Rate [cfm] | 136.9178 | 136.9178 | 136.9178 | 136.9178 | 136.9178 | 136.9178 |  |  |  |  | 2021-05-06
NM_SO_PSZ-AC:2 OA Rate [cfm] | PSZ-AC:2 OA Rate [cfm] | 103.7925 | 103.7925 | 103.7925 | 103.7925 | 103.7925 | 103.7925 |  |  |  |  | 2021-05-06
NM_SO_PSZ-AC:3 OA Rate [cfm] | PSZ-AC:3 OA Rate [cfm] | 61.5711 | 61.5711 | 61.5711 | 61.5711 | 61.5711 | 61.5711 |  |  |  |  | 2021-05-06
NM_SO_PSZ-AC:4 OA Rate [cfm] | PSZ-AC:4 OA Rate [cfm] | 103.7925 | 103.7925 | 103.7925 | 103.7925 | 103.7925 | 103.7925 |  |  |  |  | 2021-05-06
NM_SO_PSZ-AC:5 OA Rate [cfm] | PSZ-AC:5 OA Rate [cfm] | 61.5711 | 61.5711 | 61.5711 | 61.5711 | 61.5711 | 61.5711 |  |  |  |  | 2021-05-06
NM_SO_PSZ-AC:1 heating Capacity [kBtu/hr] | PSZ-AC:1 heating Capacity [kBtu/hr] | 11.3701 | 11.3701 | 10.5108 | 10.5108 | 12.3338 | 12.3053 |  |  |  |  | 2021-05-06
NM_SO_PSZ-AC:2 heating Capacity [kBtu/hr] | PSZ-AC:2 heating Capacity [kBtu/hr] | 16.6017 | 16.3476 | 14.1036 | 13.9348 | 16.8792 | 16.6588 |  |  |  |  | 2021-05-06
NM_SO_PSZ-AC:3 heating Capacity [kBtu/hr] | PSZ-AC:3 heating Capacity [kBtu/hr] | 10.1302 | 9.9897 | 8.6197 | 8.5225 | 10.1731 | 10.0513 |  |  |  |  | 2021-05-06
NM_SO_PSZ-AC:4 heating Capacity [kBtu/hr] | PSZ-AC:4 heating Capacity [kBtu/hr] | 16.2464 | 16.0471 | 14.0101 | 13.8664 | 16.6442 | 16.4677 |  |  |  |  | 2021-05-06
NM_SO_PSZ-AC:5 heating Capacity [kBtu/hr] | PSZ-AC:5 heating Capacity [kBtu/hr] | 10.1302 | 9.9897 | 8.6197 | 8.5225 | 10.1468 | 10.0275 |  |  |  |  | 2021-05-06
id | item | Zone3B(NM-Roswell-NM) ASHRAE901-state_STD2016 | Zone3B(NM-Roswell-NM) ASHRAE901-state_STD2019 | Zone4B(NM-Albuquerque-NM) ASHRAE901-state_STD2016 | Zone4B(NM-Albuquerque-NM) ASHRAE901-state_STD2019 | Zone5B(NM-Gallup-NM) ASHRAE901-state_STD2016 | Zone5B(NM-Gallup-NM) ASHRAE901-state_STD2019 |  |  |  |  | 2021-05-06
NM_LO_CAV_BAS Supply Flow Rate [cfm] | CAV_BAS Supply Flow Rate [cfm] | 13137.056 | 12162.3712 | 14196.496 | 13158.2448 | 14577.8944 | 13476.0768 |  |  |  |  | 2021-05-06
NM_LO_VAV_BOT WITH REHEAT Supply Flow Rate [cfm] | VAV_BOT WITH REHEAT Supply Flow Rate [cfm] | 21866.8416 | 20807.4016 | 23625.512 | 22502.5056 | 23943.344 | 22799.1488 |  |  |  |  | 2021-05-06
NM_LO_VAV_MID WITH REHEAT Supply Flow Rate [cfm] | VAV_MID WITH REHEAT Supply Flow Rate [cfm] | 203370.1027 | 193284.2339 | 219325.2691 | 208603.7363 | 220702.5411 | 209578.4211 |  |  |  |  | 2021-05-06
NM_LO_VAV_TOP WITH REHEAT Supply Flow Rate [cfm] | VAV_TOP WITH REHEAT Supply Flow Rate [cfm] | 21803.2752 | 20849.7792 | 23561.9456 | 22608.4496 | 23922.1552 | 22926.2816 |  |  |  |  | 2021-05-06
NM_LO_Supply Air Temp. Reset Flag | Supply Air Temp. Reset Flag | Yes | Yes | Yes | Yes | Yes | Yes |  |  |  |  | 2021-05-06
NM_LO_CAV_BAS OA Rate [cfm] | CAV_BAS OA Rate [cfm] | 2542.8255 | 2542.8255 | 2542.8255 | 2542.8255 | 2542.8255 | 2542.8255 |  |  |  |  | 2021-05-06
NM_LO_VAV_BOT WITH REHEAT OA Rate [cfm] | VAV_BOT WITH REHEAT OA Rate [cfm] | 5377.8022 | 4302.174 | 5377.8022 | 4302.174 | 5377.8022 | 4302.174 |  |  |  |  | 2021-05-06
NM_LO_VAV_MID WITH REHEAT OA Rate [cfm] | VAV_MID WITH REHEAT OA Rate [cfm] | 53777.9373 | 43021.7396 | 53777.9373 | 43021.7396 | 53777.9373 | 43021.7396 |  |  |  |  | 2021-05-06
NM_LO_VAV_TOP WITH REHEAT OA Rate [cfm] | VAV_TOP WITH REHEAT OA Rate [cfm] | 5377.8022 | 4302.174 | 5377.8022 | 4302.174 | 5377.8022 | 4302.174 |  |  |  |  | 2021-05-06
NM_LO_AIRLOOP DATACENTER BASEMENT OA Rate [cfm] | AIRLOOP DATACENTER BASEMENT OA Rate [cfm] | 716.9654 | 716.9654 | 716.9654 | 716.9654 | 716.9654 | 716.9654 |  |  |  |  | 2021-05-06
NM_LO_VAV_bot_WITH_REHEAT ERV Flag | VAV_bot_WITH_REHEAT ERV Flag | No | No | No | No | No | No |  |  |  |  | 2021-05-06
NM_LO_VAV_mid_WITH_REHEAT ERV Flag | VAV_mid_WITH_REHEAT ERV Flag | No | No | No | No | No | No |  |  |  |  | 2021-05-06
NM_LO_VAV_top_WITH_REHEAT ERV Flag | VAV_top_WITH_REHEAT ERV Flag | No | No | No | No | No | No |  |  |  |  | 2021-05-06
NM_LO_COOLSYS1 CHILLER1 Capacity [ton] | COOLSYS1 CHILLER1 Capacity [ton] | 344.5235 | 317.7086 | 312.7197 | 289.9706 | 291.6229 | 270.5693 |  |  |  |  | 2021-05-06
NM_LO_COOLSYS1 CHILLER2 Capacity [ton] | COOLSYS1 CHILLER2 Capacity [ton] | 344.5235 | 317.7086 | 312.7197 | 289.9706 | 291.6229 | 270.5693 |  |  |  |  | 2021-05-06
NM_LO_TOWERWATERSYS COOLTOWER 1 Capacity [ton] | TOWERWATERSYS COOLTOWER 1 Capacity [ton] | 327.2717 | 301.7988 | 297.1997 | 275.5787 | 277.1559 | 257.1384 |  |  |  |  | 2021-05-06
NM_LO_TOWERWATERSYS COOLTOWER 2 Capacity [ton] | TOWERWATERSYS COOLTOWER 2 Capacity [ton] | 327.2717 | 301.7988 | 297.1997 | 275.5787 | 277.1559 | 257.1384 |  |  |  |  | 2021-05-06
NM_LO_HEATSYS1 BOILER Capacity [MMBTU/h] | HEATSYS1 BOILER Capacity [MMBTU/h] | 3743.7108 | 3327.4217 | 3382.3294 | 3018.5934 | 4030.4415 | 3562.4946 |  |  |  |  | 2021-05-06
NM_LO_COOLSYS1 PUMP Flow Rate [gal/min] | COOLSYS1 PUMP Flow Rate [gal/min] | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 2021-05-06
NM_LO_COOLSYS1 CHILLER1 PUMP Flow Rate [gal/min] | COOLSYS1 CHILLER1 PUMP Flow Rate [gal/min] | 538.7889 | 496.7412 | 487.6463 | 452.289 | 457.686 | 421.5203 |  |  |  |  | 2021-05-06
NM_LO_COOLSYS1 CHILLER2 PUMP Flow Rate [gal/min] | COOLSYS1 CHILLER2 PUMP Flow Rate [gal/min] | 538.7889 | 496.7412 | 487.6463 | 452.289 | 457.686 | 421.5203 |  |  |  |  | 2021-05-06
NM_LO_COOLSYS1 PUMP SECONDARY Flow Rate [gal/min] | COOLSYS1 PUMP SECONDARY Flow Rate [gal/min] | 1077.5779 | 993.4824 | 975.291 | 904.5764 | 915.372 | 843.0406 |  |  |  |  | 2021-05-06
NM_LO_HEATSYS1 PUMP Flow Rate [gal/min] | HEATSYS1 PUMP Flow Rate [gal/min] | 768.4459 | 682.9968 | 694.2679 | 619.6066 | 827.3013 | 731.2483 |  |  |  |  | 2021-05-06
NM_LO_TOWERWATERSYS PUMP Flow Rate [gal/min] | TOWERWATERSYS PUMP Flow Rate [gal/min] | 1900.7708 | 1752.8872 | 1725.3077 | 1638.9234 | 1648.2751 | 1529.2915 |  |  |  |  | 2021-05-06
NM_LO_PLANT CIRC PUMP Flow Rate [gal/min] | PLANT CIRC PUMP Flow Rate [gal/min] | 222.6447 | 221.7413 | 229.2385 | 228.3081 | 233.5006 | 232.548 |  |  |  |  | 2021-05-06
NM_LO_COOLSYS1 PUMP SECONDARY Pressure setpoint reset [yes,no] | COOLSYS1 PUMP SECONDARY Pressure setpoint reset [yes,no] | pump_ride_on_curve | pump_ride_on_curve | pump_ride_on_curve | pump_ride_on_curve | pump_ride_on_curve | pump_ride_on_curve |  |  |  |  | 2021-05-06
NM_LO_COOLSYS1 CHILLER1 PUMP Pump Power [hp] | COOLSYS1 CHILLER1 PUMP Pump Power [hp] | 2.9066 | 2.6532 | 2.6307 | 2.4158 | 2.469 | 2.2514 |  |  |  |  | 2021-05-06
NM_LO_COOLSYS1 CHILLER2 PUMP Pump Power [hp] | COOLSYS1 CHILLER2 PUMP Pump Power [hp] | 2.9066 | 2.6532 | 2.6307 | 2.4158 | 2.469 | 2.2514 |  |  |  |  | 2021-05-06
NM_LO_COOLSYS1 PUMP SECONDARY Pump Power [hp] | COOLSYS1 PUMP SECONDARY Pump Power [hp] | 17.4395 | 15.9193 | 15.7841 | 14.4947 | 14.8143 | 13.5086 |  |  |  |  | 2021-05-06
NM_LO_HEATSYS1 PUMP Pump Power [hp] | HEATSYS1 PUMP Pump Power [hp] | 16.6104 | 14.6172 | 15.007 | 13.2605 | 17.8826 | 15.6499 |  |  |  |  | 2021-05-06
NM_LO_TOWERWATERSYS PUMP Pump Power [hp] | TOWERWATERSYS PUMP Pump Power [hp] | 34.0313 | 31.0719 | 30.8898 | 29.0534 | 29.5112 | 27.1095 |  |  |  |  | 2021-05-06
NM_LO_PLANT CIRC PUMP Pump Power [hp] | PLANT CIRC PUMP Pump Power [hp] | 4.8043 | 4.7375 | 4.9466 | 4.8778 | 5.0386 | 4.9684 |  |  |  |  | 2021-05-06
NM_LO_Datacenter PLANT CIRC PUMP Pump Power [hp] | Datacenter PLANT CIRC PUMP Pump Power [hp] | 4.8043 | 4.7375 | 4.9466 | 4.8778 | 5.0386 | 4.9684 |  |  |  |  | 2021-05-06
NM_LO_ZN_VAV_BOXes_Max_Reheat_Water_Flow_GPM | ZN_VAV_BOXes_Max_Reheat_Water_Flow_GPM | 438.5715 | 417.9591 | 394.5202 | 375.7351 | 435.3121 | 415.7291 |  |  |  |  | 2021-05-06
NM_LO_COOLSYS1 PUMP SECONDARY VSD | COOLSYS1 PUMP SECONDARY VSD | No | No | No | No | No | No |  |  |  |  | 2021-05-06
NM_LO_HEATSYS1 PUMP VSD | HEATSYS1 PUMP VSD | No | No | No | No | No | No |  |  |  |  | 2021-05-06
NM_LO_DATACENTER BASEMENT Cooling Capacity [ton] | DATACENTER BASEMENT Cooling Capacity [ton] | 131.1602 | 130.7723 | 134.4776 | 134.0753 | 136.4638 | 136.0551 |  |  |  |  | 2021-05-06
NM_LO_DATACENTER BOT Cooling Capacity [ton] | DATACENTER BOT Cooling Capacity [ton] | 2.7793 | 2.75 | 2.8983 | 2.8721 | 2.9921 | 2.9651 |  |  |  |  | 2021-05-06
NM_LO_DATACENTER MID Cooling Capacity [ton] | DATACENTER MID Cooling Capacity [ton] | 26.4517 | 26.2294 | 27.7175 | 27.4868 | 28.6669 | 28.4271 |  |  |  |  | 2021-05-06
NM_LO_DATACENTER TOP Cooling Capacity [ton] | DATACENTER TOP Cooling Capacity [ton] | 2.7004 | 2.6786 | 2.8282 | 2.8058 | 2.9216 | 2.8985 |  |  |  |  | 2021-05-06
id | item | Zone3B(NM-Roswell-NM) ASHRAE901-state_STD2016 | Zone3B(NM-Roswell-NM) ASHRAE901-state_STD2019 | Zone4B(NM-Albuquerque-NM) ASHRAE901-state_STD2016 | Zone4B(NM-Albuquerque-NM) ASHRAE901-state_STD2019 | Zone5B(NM-Gallup-NM) ASHRAE901-state_STD2016 | Zone5B(NM-Gallup-NM) ASHRAE901-state_STD2019 |  |  |  |  | 2021-05-06
NM_RS_PSZ-AC:1 Cooling Capacity [ton] | PSZ-AC:1 Cooling Capacity [ton] | 10.2731 | 9.7492 | 10.5159 | 9.8639 | 9.6267 | 8.7706 |  |  |  |  | 2021-05-06
NM_RS_PSZ-AC:2 Cooling Capacity [ton] | PSZ-AC:2 Cooling Capacity [ton] | 47.7437 | 45.722 | 42.9356 | 41.1755 | 40.3316 | 37.7736 |  |  |  |  | 2021-05-06
NM_RS_PSZ-AC:3 Cooling Capacity [ton] | PSZ-AC:3 Cooling Capacity [ton] | 6.5359 | 6.3635 | 5.9883 | 5.8203 | 5.567 | 5.3842 |  |  |  |  | 2021-05-06
NM_RS_PSZ-AC:4 Cooling Capacity [ton] | PSZ-AC:4 Cooling Capacity [ton] | 5.1731 | 4.9944 | 4.6731 | 4.5154 | 4.189 | 3.9989 |  |  |  |  | 2021-05-06
NM_RS_PSZ-AC:1 Supply Flow Rate [cfm] | PSZ-AC:1 Supply Flow Rate [cfm] | 4619.1584 | 4343.704 | 4725.1024 | 4449.648 | 4343.704 | 3941.1168 |  |  |  |  | 2021-05-06
NM_RS_PSZ-AC:2 Supply Flow Rate [cfm] | PSZ-AC:2 Supply Flow Rate [cfm] | 17247.6832 | 16272.9984 | 18179.9904 | 17290.0608 | 18158.8016 | 17014.6064 |  |  |  |  | 2021-05-06
NM_RS_PSZ-AC:3 Supply Flow Rate [cfm] | PSZ-AC:3 Supply Flow Rate [cfm] | 2585.0336 | 2500.2784 | 2690.9776 | 2606.2224 | 2500.2784 | 2415.5232 |  |  |  |  | 2021-05-06
NM_RS_PSZ-AC:4 Supply Flow Rate [cfm] | PSZ-AC:4 Supply Flow Rate [cfm] | 1970.5584 | 1885.8032 | 2055.3136 | 1970.5584 | 1885.8032 | 1801.048 |  |  |  |  | 2021-05-06
NM_RS_PSZ-AC:1 OA Rate [cfm] | PSZ-AC:1 OA Rate [cfm] | 490.669 | 490.669 | 490.669 | 490.669 | 490.669 | 490.669 |  |  |  |  | 2021-05-06
NM_RS_PSZ-AC:2 OA Rate [cfm] | PSZ-AC:2 OA Rate [cfm] | 4005.1282 | 4005.1282 | 4005.1282 | 4005.1282 | 4005.1282 | 4005.1282 |  |  |  |  | 2021-05-06
NM_RS_PSZ-AC:3 OA Rate [cfm] | PSZ-AC:3 OA Rate [cfm] | 377.3937 | 377.3937 | 377.3937 | 377.3937 | 377.3937 | 377.3937 |  |  |  |  | 2021-05-06
NM_RS_PSZ-AC:4 OA Rate [cfm] | PSZ-AC:4 OA Rate [cfm] | 377.3937 | 377.3937 | 377.3937 | 377.3937 | 377.3937 | 377.3937 |  |  |  |  | 2021-05-06
NM_RS_PSZ-AC:1 OA Damper [gravity, motorized] | PSZ-AC:1 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | motorized | motorized |  |  |  |  | 2021-05-06
NM_RS_PSZ-AC:2 OA Damper [gravity, motorized] | PSZ-AC:2 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | motorized | motorized |  |  |  |  | 2021-05-06
NM_RS_PSZ-AC:3 OA Damper [gravity, motorized] | PSZ-AC:3 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | motorized | motorized |  |  |  |  | 2021-05-06
NM_RS_PSZ-AC:4 OA Damper [gravity, motorized] | PSZ-AC:4 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | motorized | motorized |  |  |  |  | 2021-05-06
NM_RS_PSZ-AC:1 Heating Capacity [kBtu/hr] | PSZ-AC:1 Heating Capacity [kBtu/hr] | 175.3236 | 165.3447 | 167.1263 | 157.4494 | 153.4469 | 140.2664 |  |  |  |  | 2021-05-06
NM_RS_PSZ-AC:2 Heating Capacity [kBtu/hr] | PSZ-AC:2 Heating Capacity [kBtu/hr] | 754.067 | 717.6564 | 731.7825 | 700.5336 | 755.1017 | 716.8587 |  |  |  |  | 2021-05-06
NM_RS_PSZ-AC:3 Heating Capacity [kBtu/hr] | PSZ-AC:3 Heating Capacity [kBtu/hr] | 102.9416 | 100.314 | 99.6925 | 97.2038 | 95.4223 | 92.8637 |  |  |  |  | 2021-05-06
NM_RS_PSZ-AC:4 Heating Capacity [kBtu/hr] | PSZ-AC:4 Heating Capacity [kBtu/hr] | 82.8543 | 80.0853 | 79.4425 | 76.8918 | 77.3011 | 74.801 |  |  |  |  | 2021-05-06
id | item | Zone3B(NM-Roswell-NM) ASHRAE901-state_STD2016 | Zone3B(NM-Roswell-NM) ASHRAE901-state_STD2019 | Zone4B(NM-Albuquerque-NM) ASHRAE901-state_STD2016 | Zone4B(NM-Albuquerque-NM) ASHRAE901-state_STD2019 | Zone5B(NM-Gallup-NM) ASHRAE901-state_STD2016 | Zone5B(NM-Gallup-NM) ASHRAE901-state_STD2019 |  |  |  |  | 2021-05-06
NM_PS_VAV_POD_1 Cooling Capacity [ton] | VAV_POD_1 Cooling Capacity [ton] | 21.7716 | 20.3691 | 23.0796 | 21.4662 | 19.2948 | 18.073 |  |  |  |  | 2021-05-06
NM_PS_VAV_POD_2 Cooling Capacity [ton] | VAV_POD_2 Cooling Capacity [ton] | 21.8468 | 20.2748 | 22.8197 | 21.27 | 19.2245 | 17.77 |  |  |  |  | 2021-05-06
NM_PS_VAV_POD_3 Cooling Capacity [ton] | VAV_POD_3 Cooling Capacity [ton] | 19.818 | 18.554 | 21.1565 | 19.2496 | 17.6333 | 16.4769 |  |  |  |  | 2021-05-06
NM_PS_VAV_OTHER Cooling Capacity [ton] | VAV_OTHER Cooling Capacity [ton] | 26.5691 | 23.9748 | 24.084 | 21.9104 | 21.6849 | 20.2201 |  |  |  |  | 2021-05-06
NM_PS_PSZ-AC_1:6 Cooling Capacity [ton] | PSZ-AC_1:6 Cooling Capacity [ton] | 8.3751 | 8.077 | 7.9695 | 7.6833 | 7.6011 | 7.3191 |  |  |  |  | 2021-05-06
NM_PS_PSZ-AC_2:5 Cooling Capacity [ton] | PSZ-AC_2:5 Cooling Capacity [ton] | 6.0453 | 5.8383 | 5.5649 | 5.5508 | 5.0956 | 5.0823 |  |  |  |  | 2021-05-06
NM_PS_PSZ-AC_2:7 Cooling Capacity [ton] | PSZ-AC_2:7 Cooling Capacity [ton] | 10.5074 | 10.5074 | 10.4336 | 10.4336 | 9.3685 | 9.3685 |  |  |  |  | 2021-05-06
NM_PS_VAV_POD_1 Supply Flow Rate [cfm] | VAV_POD_1 Supply Flow Rate [cfm] | 6526.1504 | 6102.3744 | 6949.9264 | 6526.1504 | 6632.0944 | 6229.5072 |  |  |  |  | 2021-05-06
NM_PS_VAV_POD_2 Supply Flow Rate [cfm] | VAV_POD_2 Supply Flow Rate [cfm] | 6547.3392 | 6081.1856 | 6886.36 | 6420.2064 | 6610.9056 | 6123.5632 |  |  |  |  | 2021-05-06
NM_PS_VAV_POD_3 Supply Flow Rate [cfm] | VAV_POD_3 Supply Flow Rate [cfm] | 5954.0528 | 5572.6544 | 6377.8288 | 5996.4304 | 6123.5632 | 5699.7872 |  |  |  |  | 2021-05-06
NM_PS_VAV_OTHER Supply Flow Rate [cfm] | VAV_OTHER Supply Flow Rate [cfm] | 9068.8064 | 8517.8976 | 9852.792 | 9280.6944 | 9704.4704 | 9111.184 |  |  |  |  | 2021-05-06
NM_PS_PSZ-AC_2:5 Supply Flow Rate [cfm] | PSZ-AC_2:5 Supply Flow Rate [cfm] | 1822.2368 | 1758.6704 | 2034.1248 | 2012.936 | 2055.3136 | 2034.1248 |  |  |  |  | 2021-05-06
NM_PS_PSZ-AC_1:6 Supply Flow Rate [cfm] | PSZ-AC_1:6 Supply Flow Rate [cfm] | 2860.488 | 2733.3552 | 3072.376 | 2945.2432 | 3178.32 | 3029.9984 |  |  |  |  | 2021-05-06
NM_PS_PSZ-AC_2:7 Supply Flow Rate [cfm] | PSZ-AC_2:7 Supply Flow Rate [cfm] | 3157.1312 | 3157.1312 | 3157.1312 | 3157.1312 | 3157.1312 | 3157.1312 |  |  |  |  | 2021-05-06
NM_PS_Supply Air Temp. Reset Flag | Supply Air Temp. Reset Flag | Yes | Yes | Yes | Yes | Yes | Yes |  |  |  |  | 2021-05-06
NM_PS_VAV_POD_1 OA Rate [cfm] | VAV_POD_1 OA Rate [cfm] | 6533.3122 | 6112.4179 | 6953.4861 | 6282.2673 | 6639.9978 | 6221.4343 |  |  |  |  | 2021-05-06
NM_PS_VAV_POD_2 OA Rate [cfm] | VAV_POD_2 OA Rate [cfm] | 6554.2679 | 6084.152 | 6876.4437 | 6282.2673 | 6617.8132 | 6117.1218 |  |  |  |  | 2021-05-06
NM_PS_VAV_POD_3 OA Rate [cfm] | VAV_POD_3 OA Rate [cfm] | 5945.5773 | 5422.002 | 6369.3109 | 5422.002 | 6121.296 | 5422.002 |  |  |  |  | 2021-05-06
NM_PS_VAV_OTHER OA Rate [cfm] | VAV_OTHER OA Rate [cfm] | 3736.1787 | 2988.8921 | 3736.1787 | 2988.8921 | 3736.1787 | 2988.8921 |  |  |  |  | 2021-05-06
NM_PS_PSZ-AC_2:5 OA Rate [cfm] | PSZ-AC_2:5 OA Rate [cfm] | 1152.7343 | 1152.7343 | 1152.7343 | 1152.7343 | 1152.7343 | 1152.7343 |  |  |  |  | 2021-05-06
NM_PS_PSZ-AC_1:6 OA Rate [cfm] | PSZ-AC_1:6 OA Rate [cfm] | 539.9118 | 539.9118 | 539.9118 | 539.9118 | 539.9118 | 539.9118 |  |  |  |  | 2021-05-06
NM_PS_PSZ-AC_2:7 OA Rate [cfm] | PSZ-AC_2:7 OA Rate [cfm] | 3153.0841 | 3153.0841 | 3153.0841 | 3153.0841 | 3153.0841 | 3153.0841 |  |  |  |  | 2021-05-06
NM_PS_VAV_POD_1 OA Damper [gravity, motorized] | VAV_POD_1 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | motorized | motorized |  |  |  |  | 2021-05-06
NM_PS_VAV_POD_2 OA Damper [gravity, motorized] | VAV_POD_2 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | motorized | motorized |  |  |  |  | 2021-05-06
NM_PS_VAV_POD_3 OA Damper [gravity, motorized] | VAV_POD_3 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | motorized | motorized |  |  |  |  | 2021-05-06
NM_PS_VAV_OTHER OA Damper [gravity, motorized] | VAV_OTHER OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | motorized | motorized |  |  |  |  | 2021-05-06
NM_PS_PSZ-AC_2:5 OA Damper [gravity, motorized] | PSZ-AC_2:5 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | motorized | motorized |  |  |  |  | 2021-05-06
NM_PS_PSZ-AC_1:6 OA Damper [gravity, motorized] | PSZ-AC_1:6 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | motorized | motorized |  |  |  |  | 2021-05-06
NM_PS_PSZ-AC_2:7 OA Damper [gravity, motorized] | PSZ-AC_2:7 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | motorized | motorized |  |  |  |  | 2021-05-06
NM_PS_VAV_POD_1 (economizer) | VAV_POD_1 (economizer) | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb |  |  |  |  | 2021-05-06
NM_PS_VAV_POD_2 (economizer) | VAV_POD_2 (economizer) | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb |  |  |  |  | 2021-05-06
NM_PS_VAV_POD_3 (economizer) | VAV_POD_3 (economizer) | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb |  |  |  |  | 2021-05-06
NM_PS_VAV_OTHER (economizer) | VAV_OTHER (economizer) | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb |  |  |  |  | 2021-05-06
NM_PS_PSZ-AC_2:5 (economizer) | PSZ-AC_2:5 (economizer) | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb |  |  |  |  | 2021-05-06
NM_PS_PSZ-AC_1:6 (economizer) | PSZ-AC_1:6 (economizer) | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb |  |  |  |  | 2021-05-06
NM_PS_PSZ-AC_2:7 (economizer) | PSZ-AC_2:7 (economizer) | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb |  |  |  |  | 2021-05-06
NM_PS_VAV_Pod_1_ERV Flag | VAV_Pod_1_ERV Flag | No | No | No | No | No | No |  |  |  |  | 2021-05-06
NM_PS_VAV_Pod_2_ERV Flag | VAV_Pod_2_ERV Flag | No | No | No | No | No | No |  |  |  |  | 2021-05-06
NM_PS_VAV_Pod_3_ERV Flag | VAV_Pod_3_ERV Flag | No | No | No | No | No | No |  |  |  |  | 2021-05-06
NM_PS_VAV_OTHER_ERV Flag | VAV_OTHER_ERV Flag | No | No | No | No | No | No |  |  |  |  | 2021-05-06
NM_PS_PSZ_AC_2_5_ERV Flag | PSZ_AC_2_5_ERV Flag | No | No | No | No | No | No |  |  |  |  | 2021-05-06
NM_PS_PSZ_AC_2_7_ERV Flag | PSZ_AC_2_7_ERV Flag | No | No | No | No | No | No |  |  |  |  | 2021-05-06
NM_PS_HEATSYS1 Capacity [MMBTU/h] | HEATSYS1 Capacity [MMBTU/h] | 0.96408 | 0.89688 | 0.89029 | 0.82154 | 1.0503 | 0.98115 |  |  |  |  | 2021-05-06
NM_PS_HEATSYS1 Flow Rate [gal/min] | HEATSYS1 Flow Rate [gal/min] | 98.9445 | 92.0481 | 91.3724 | 84.3163 | 107.7923 | 100.6973 |  |  |  |  | 2021-05-06
NM_PS_VAV_POD_1 Fan Power [hp] | VAV_POD_1 Fan Power [hp] | 9.6386 | 9.0177 | 10.1826 | 9.6232 | 9.799 | 9.1785 |  |  |  |  | 2021-05-06
NM_PS_VAV_POD_2 Fan Power [hp] | VAV_POD_2 Fan Power [hp] | 9.6719 | 8.9759 | 10.068 | 9.4759 | 9.7633 | 9.0246 |  |  |  |  | 2021-05-06
NM_PS_VAV_POD_3 Fan Power [hp] | VAV_POD_3 Fan Power [hp] | 8.7737 | 8.2141 | 9.3983 | 8.8403 | 9.0308 | 8.4241 |  |  |  |  | 2021-05-06
NM_PS_VAV_OTHER Fan Power [hp] | VAV_OTHER Fan Power [hp] | 13.2806 | 12.4853 | 14.4361 | 13.5897 | 14.2125 | 13.3269 |  |  |  |  | 2021-05-06
NM_PS_HEATSYS1 Pump Power [hp] | HEATSYS1 Pump Power [hp] | 2.1387 | 1.97 | 1.9751 | 1.8045 | 2.33 | 2.1551 |  |  |  |  | 2021-05-06
NM_PS_PSZ-AC_1:6 Heating Capacity [kBtu/hr] | PSZ-AC_1:6 Heating Capacity [kBtu/hr] | 202.6448 | 194.0063 | 204.2977 | 195.8893 | 209.3004 | 200.9264 |  |  |  |  | 2021-05-06
NM_PS_PSZ-AC_2:5 Heating Capacity [kBtu/hr] | PSZ-AC_2:5 Heating Capacity [kBtu/hr] | 117.155 | 115.142 | 115.2082 | 114.9843 | 127.6765 | 127.4693 |  |  |  |  | 2021-05-06
NM_PS_PSZ-AC_2:7 Heating Capacity [kBtu/hr] | PSZ-AC_2:7 Heating Capacity [kBtu/hr] | 261.8431 | 261.8431 | 242.0539 | 242.0539 | 277.7147 | 277.7147 |  |  |  |  | 2021-05-06
NM_PS_ZN_VAV_BOXes_Max_Reheat_Water_Flow_GPM | ZN_VAV_BOXes_Max_Reheat_Water_Flow_GPM | 67.2175 | 62.3699 | 60.6663 | 55.4913 | 66.2894 | 61.9586 |  |  |  |  | 2021-05-06
id | item | Zone3B(NM-Roswell-NM) ASHRAE901-state_STD2016 | Zone3B(NM-Roswell-NM) ASHRAE901-state_STD2019 | Zone4B(NM-Albuquerque-NM) ASHRAE901-state_STD2016 | Zone4B(NM-Albuquerque-NM) ASHRAE901-state_STD2019 | Zone5B(NM-Gallup-NM) ASHRAE901-state_STD2016 | Zone5B(NM-Gallup-NM) ASHRAE901-state_STD2019 |  |  |  |  | 2021-05-06
NM_SH_SAC_FRONTOFFICE Cooling Capacity [ton] | SAC_FRONTOFFICE Cooling Capacity [ton] | 2.3806 | 2.2449 | 2.1203 | 1.9921 | 2.0572 | 1.8911 |  |  |  |  | 2021-05-06
NM_SH_SAC_FRONTLOUNGE Cooling Capacity [ton] | SAC_FRONTLOUNGE Cooling Capacity [ton] | 6.1439 | 5.8966 | 5.5188 | 5.261 | 5.0878 | 4.8308 |  |  |  |  | 2021-05-06
NM_SH_SAC_MEETINGROOM Cooling Capacity [ton] | SAC_MEETINGROOM Cooling Capacity [ton] | 3.1925 | 3.1002 | 2.8702 | 2.7992 | 2.6864 | 2.6119 |  |  |  |  | 2021-05-06
NM_SH_SAC_EXC_EMPLGE_RESTRM Cooling Capacity [ton] | SAC_EXC_EMPLGE_RESTRM Cooling Capacity [ton] | 6.0968 | 6.0519 | 5.8854 | 5.8405 | 6.0396 | 5.988 |  |  |  |  | 2021-05-06
NM_SH_SAC_FO_ADDAQ SUPPLY FAN Supply Flow Rate [cfm] | SAC_FO_ADDAQ SUPPLY FAN Supply Flow Rate [cfm] | 932.3072 | 868.7408 | 932.3072 | 868.7408 | 932.3072 | 847.552 |  |  |  |  | 2021-05-06
NM_SH_SAC_FL_ADDAQ SUPPLY FAN Supply Flow Rate [cfm] | SAC_FL_ADDAQ SUPPLY FAN Supply Flow Rate [cfm] | 2140.0688 | 2034.1248 | 2224.824 | 2097.6912 | 2224.824 | 2097.6912 |  |  |  |  | 2021-05-06
NM_SH_SAC_MR_ADDAQ SUPPLY FAN Supply Flow Rate [cfm] | SAC_MR_ADDAQ SUPPLY FAN Supply Flow Rate [cfm] | 1017.0624 | 974.6848 | 1059.44 | 1017.0624 | 1059.44 | 1038.2512 |  |  |  |  | 2021-05-06
NM_SH_SAC_EXC_ADDAQ SUPPLY FAN Supply Flow Rate [cfm] | SAC_EXC_ADDAQ SUPPLY FAN Supply Flow Rate [cfm] | 2479.0896 | 2457.9008 | 2648.6 | 2627.4112 | 2712.1664 | 2690.9776 |  |  |  |  | 2021-05-06
NM_SH_SAC_Exc_EmpLge_RestRm OA Rate [cfm] | SAC_Exc_EmpLge_RestRm OA Rate [cfm] | 199.9928 | 199.9928 | 199.9928 | 199.9928 | 199.9928 | 199.9928 |  |  |  |  | 2021-05-06
NM_SH_SAC_FrontLounge OA Rate [cfm] | SAC_FrontLounge OA Rate [cfm] | 500.0133 | 500.0133 | 500.0133 | 500.0133 | 500.0133 | 500.0133 |  |  |  |  | 2021-05-06
NM_SH_SAC_FrontOffice OA Rate [cfm] | SAC_FrontOffice OA Rate [cfm] | 119.2938 | 119.2938 | 119.2938 | 119.2938 | 119.2938 | 119.2938 |  |  |  |  | 2021-05-06
NM_SH_SAC_MeetingRoom OA Rate [cfm] | SAC_MeetingRoom OA Rate [cfm] | 267.7629 | 267.7629 | 267.7629 | 267.7629 | 267.7629 | 267.7629 |  |  |  |  | 2021-05-06
NM_SH_SAC_FrontLounge OA Damper [gravity, motorized] | SAC_FrontLounge OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | motorized | motorized |  |  |  |  | 2021-05-06
NM_SH_SAC_FrontOffice (economizer) | SAC_FrontOffice (economizer) | No | No | No | No | No | No |  |  |  |  | 2021-05-06
NM_SH_SAC_FrontLounge (economizer) | SAC_FrontLounge (economizer) | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb |  |  |  |  | 2021-05-06
NM_SH_SAC_MeetingRoom (economizer) | SAC_MeetingRoom (economizer) | No | No | No | No | No | No |  |  |  |  | 2021-05-06
NM_SH_SAC_Exc_EmpLge_RestRm (economizer) | SAC_Exc_EmpLge_RestRm (economizer) | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb |  |  |  |  | 2021-05-06
NM_SH_SAC_FRONTOFFICE Heating Capacity [kBtu/hr] | SAC_FRONTOFFICE Heating Capacity [kBtu/hr] | 36.185 | 34.2138 | 33.9283 | 32.0566 | 33.8903 | 31.7237 |  |  |  |  | 2021-05-06
NM_SH_SAC_FRONTLOUNGE Heating Capacity [kBtu/hr] | SAC_FRONTLOUNGE Heating Capacity [kBtu/hr] | 94.4211 | 91.0102 | 90.3434 | 86.9512 | 94.0087 | 90.6474 |  |  |  |  | 2021-05-06
NM_SH_SAC_MEETINGROOM Heating Capacity [kBtu/hr] | SAC_MEETINGROOM Heating Capacity [kBtu/hr] | 46.5273 | 45.3219 | 44.2422 | 43.2929 | 46.705 | 45.6996 |  |  |  |  | 2021-05-06
NM_SH_SAC_EXC_EMPLGE_RESTRM Heating Capacity [kBtu/hr] | SAC_EXC_EMPLGE_RESTRM Heating Capacity [kBtu/hr] | 89.8073 | 89.1556 | 89.3938 | 88.7328 | 90.6157 | 89.9432 |  |  |  |  | 2021-05-06
id | item | Zone3B(NM-Roswell-NM) ASHRAE901-state_STD2016 | Zone3B(NM-Roswell-NM) ASHRAE901-state_STD2019 | Zone4B(NM-Albuquerque-NM) ASHRAE901-state_STD2016 | Zone4B(NM-Albuquerque-NM) ASHRAE901-state_STD2019 | Zone5B(NM-Gallup-NM) ASHRAE901-state_STD2016 | Zone5B(NM-Gallup-NM) ASHRAE901-state_STD2019 |  |  |  |  | 2021-05-06
NM_MA_SPLIT GSW COOLING COIL Cooling Capacity [ton] | SPLIT GSW COOLING COIL Cooling Capacity [ton] | 0.83622 | 0.82336 | 0.85077 | 0.83303 | 0.76937 | 0.75029 |  |  |  |  | 2021-05-06
NM_MA_SPLIT GNW COOLING COIL Cooling Capacity [ton] | SPLIT GNW COOLING COIL Cooling Capacity [ton] | 0.82949 | 0.81662 | 0.82914 | 0.81153 | 0.74874 | 0.72968 |  |  |  |  | 2021-05-06
NM_MA_SPLIT OFFICE COOLING COIL Cooling Capacity [ton] | SPLIT OFFICE COOLING COIL Cooling Capacity [ton] | 1.7727 | 1.6559 | 1.9383 | 1.754 | 1.7224 | 1.5214 |  |  |  |  | 2021-05-06
NM_MA_SPLIT GNE COOLING COIL Cooling Capacity [ton] | SPLIT GNE COOLING COIL Cooling Capacity [ton] | 0.70943 | 0.69768 | 0.69177 | 0.67663 | 0.59488 | 0.57871 |  |  |  |  | 2021-05-06
NM_MA_SPLIT GN1 COOLING COIL Cooling Capacity [ton] | SPLIT GN1 COOLING COIL Cooling Capacity [ton] | 0.59363 | 0.58325 | 0.57553 | 0.56344 | 0.50222 | 0.48948 |  |  |  |  | 2021-05-06
NM_MA_SPLIT GN2 COOLING COIL Cooling Capacity [ton] | SPLIT GN2 COOLING COIL Cooling Capacity [ton] | 0.59144 | 0.58108 | 0.57284 | 0.56082 | 0.49901 | 0.48637 |  |  |  |  | 2021-05-06
NM_MA_SPLIT GS1 COOLING COIL Cooling Capacity [ton] | SPLIT GS1 COOLING COIL Cooling Capacity [ton] | 0.59677 | 0.58613 | 0.59543 | 0.58276 | 0.52379 | 0.51041 |  |  |  |  | 2021-05-06
NM_MA_SPLIT GS2 COOLING COIL Cooling Capacity [ton] | SPLIT GS2 COOLING COIL Cooling Capacity [ton] | 0.6428 | 0.62703 | 0.64297 | 0.62441 | 0.56836 | 0.54849 |  |  |  |  | 2021-05-06
NM_MA_SPLIT MSW COOLING COIL Cooling Capacity [ton] | SPLIT MSW COOLING COIL Cooling Capacity [ton] | 1.9324 | 1.9054 | 2.0695 | 2.0294 | 2.0657 | 2.0226 |  |  |  |  | 2021-05-06
NM_MA_SPLIT MNW COOLING COIL Cooling Capacity [ton] | SPLIT MNW COOLING COIL Cooling Capacity [ton] | 1.9112 | 1.8854 | 2.0264 | 1.9868 | 2.0303 | 1.9873 |  |  |  |  | 2021-05-06
NM_MA_SPLIT MSE COOLING COIL Cooling Capacity [ton] | SPLIT MSE COOLING COIL Cooling Capacity [ton] | 1.6483 | 1.6251 | 1.6462 | 1.6136 | 1.5589 | 1.525 |  |  |  |  | 2021-05-06
NM_MA_SPLIT MNE COOLING COIL Cooling Capacity [ton] | SPLIT MNE COOLING COIL Cooling Capacity [ton] | 1.5688 | 1.5453 | 1.5863 | 1.5575 | 1.4998 | 1.4695 |  |  |  |  | 2021-05-06
NM_MA_SPLIT MN1 COOLING COIL Cooling Capacity [ton] | SPLIT MN1 COOLING COIL Cooling Capacity [ton] | 1.2615 | 1.2412 | 1.2704 | 1.2474 | 1.2153 | 1.191 |  |  |  |  | 2021-05-06
NM_MA_SPLIT MN2 COOLING COIL Cooling Capacity [ton] | SPLIT MN2 COOLING COIL Cooling Capacity [ton] | 1.2559 | 1.2356 | 1.2629 | 1.2401 | 1.2062 | 1.1822 |  |  |  |  | 2021-05-06
NM_MA_SPLIT MS1 COOLING COIL Cooling Capacity [ton] | SPLIT MS1 COOLING COIL Cooling Capacity [ton] | 1.2631 | 1.2425 | 1.3019 | 1.2782 | 1.2423 | 1.2178 |  |  |  |  | 2021-05-06
NM_MA_SPLIT MS2 COOLING COIL Cooling Capacity [ton] | SPLIT MS2 COOLING COIL Cooling Capacity [ton] | 1.2577 | 1.2371 | 1.2947 | 1.2713 | 1.2344 | 1.2101 |  |  |  |  | 2021-05-06
NM_MA_SPLIT TSW COOLING COIL Cooling Capacity [ton] | SPLIT TSW COOLING COIL Cooling Capacity [ton] | 1.2402 | 1.226 | 1.3447 | 1.3228 | 1.3362 | 1.3128 |  |  |  |  | 2021-05-06
NM_MA_SPLIT TNW COOLING COIL Cooling Capacity [ton] | SPLIT TNW COOLING COIL Cooling Capacity [ton] | 1.2168 | 1.2032 | 1.3173 | 1.2954 | 1.3148 | 1.2913 |  |  |  |  | 2021-05-06
NM_MA_SPLIT TSE COOLING COIL Cooling Capacity [ton] | SPLIT TSE COOLING COIL Cooling Capacity [ton] | 1.068 | 1.0562 | 1.1308 | 1.1139 | 1.0728 | 1.0552 |  |  |  |  | 2021-05-06
NM_MA_SPLIT TNE COOLING COIL Cooling Capacity [ton] | SPLIT TNE COOLING COIL Cooling Capacity [ton] | 1.0266 | 1.015 | 1.0652 | 1.0492 | 1.014 | 0.99709 |  |  |  |  | 2021-05-06
NM_MA_SPLIT TN1 COOLING COIL Cooling Capacity [ton] | SPLIT TN1 COOLING COIL Cooling Capacity [ton] | 0.8175 | 0.80723 | 0.84743 | 0.83526 | 0.81237 | 0.79962 |  |  |  |  | 2021-05-06
NM_MA_SPLIT TN2 COOLING COIL Cooling Capacity [ton] | SPLIT TN2 COOLING COIL Cooling Capacity [ton] | 0.81106 | 0.80082 | 0.84539 | 0.83294 | 0.80646 | 0.79338 |  |  |  |  | 2021-05-06
NM_MA_SPLIT TS1 COOLING COIL Cooling Capacity [ton] | SPLIT TS1 COOLING COIL Cooling Capacity [ton] | 0.87427 | 0.86417 | 0.91245 | 0.89883 | 0.86939 | 0.85521 |  |  |  |  | 2021-05-06
NM_MA_SPLIT TS2 COOLING COIL Cooling Capacity [ton] | SPLIT TS2 COOLING COIL Cooling Capacity [ton] | 0.87516 | 0.86507 | 0.91314 | 0.89957 | 0.86976 | 0.85567 |  |  |  |  | 2021-05-06
NM_MA_Split GN1 Furnace with DX Cooling OA Rate [cfm] | Split GN1 Furnace with DX Cooling OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 |  |  |  |  | 2021-05-06
NM_MA_Split GN2 Furnace with DX Cooling OA Rate [cfm] | Split GN2 Furnace with DX Cooling OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 |  |  |  |  | 2021-05-06
NM_MA_Split GNE Furnace with DX Cooling OA Rate [cfm] | Split GNE Furnace with DX Cooling OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 |  |  |  |  | 2021-05-06
NM_MA_Split GNW Furnace with DX Cooling OA Rate [cfm] | Split GNW Furnace with DX Cooling OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 |  |  |  |  | 2021-05-06
NM_MA_Split GS1 Furnace with DX Cooling OA Rate [cfm] | Split GS1 Furnace with DX Cooling OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 |  |  |  |  | 2021-05-06
NM_MA_Split GS2 Furnace with DX Cooling OA Rate [cfm] | Split GS2 Furnace with DX Cooling OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 |  |  |  |  | 2021-05-06
NM_MA_Split GSW Furnace with DX Cooling OA Rate [cfm] | Split GSW Furnace with DX Cooling OA Rate [cfm] | 56.9945 | 56.9945 | 56.9945 | 56.9945 | 56.9945 | 56.9945 |  |  |  |  | 2021-05-06
NM_MA_Split MN1 Furnace with DX Cooling OA Rate [cfm] | Split MN1 Furnace with DX Cooling OA Rate [cfm] | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824 |  |  |  |  | 2021-05-06
NM_MA_Split MN2 Furnace with DX Cooling OA Rate [cfm] | Split MN2 Furnace with DX Cooling OA Rate [cfm] | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824 |  |  |  |  | 2021-05-06
NM_MA_Split MNE Furnace with DX Cooling OA Rate [cfm] | Split MNE Furnace with DX Cooling OA Rate [cfm] | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824 |  |  |  |  | 2021-05-06
NM_MA_Split MNW Furnace with DX Cooling OA Rate [cfm] | Split MNW Furnace with DX Cooling OA Rate [cfm] | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824 |  |  |  |  | 2021-05-06
NM_MA_Split MS1 Furnace with DX Cooling OA Rate [cfm] | Split MS1 Furnace with DX Cooling OA Rate [cfm] | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824 |  |  |  |  | 2021-05-06
NM_MA_Split MS2 Furnace with DX Cooling OA Rate [cfm] | Split MS2 Furnace with DX Cooling OA Rate [cfm] | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824 |  |  |  |  | 2021-05-06
NM_MA_Split MSE Furnace with DX Cooling OA Rate [cfm] | Split MSE Furnace with DX Cooling OA Rate [cfm] | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824 |  |  |  |  | 2021-05-06
NM_MA_Split MSW Furnace with DX Cooling OA Rate [cfm] | Split MSW Furnace with DX Cooling OA Rate [cfm] | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824 |  |  |  |  | 2021-05-06
NM_MA_Split Office Furnace with DX Cooling OA Rate [cfm] | Split Office Furnace with DX Cooling OA Rate [cfm] | 80.7372 | 80.7372 | 80.7372 | 80.7372 | 80.7372 | 80.7372 |  |  |  |  | 2021-05-06
NM_MA_Split TN1 Furnace with DX Cooling OA Rate [cfm] | Split TN1 Furnace with DX Cooling OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 |  |  |  |  | 2021-05-06
NM_MA_Split TN2 Furnace with DX Cooling OA Rate [cfm] | Split TN2 Furnace with DX Cooling OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 |  |  |  |  | 2021-05-06
NM_MA_Split TNE Furnace with DX Cooling OA Rate [cfm] | Split TNE Furnace with DX Cooling OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 |  |  |  |  | 2021-05-06
NM_MA_Split TNW Furnace with DX Cooling OA Rate [cfm] | Split TNW Furnace with DX Cooling OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 |  |  |  |  | 2021-05-06
NM_MA_Split TS1 Furnace with DX Cooling OA Rate [cfm] | Split TS1 Furnace with DX Cooling OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 |  |  |  |  | 2021-05-06
NM_MA_Split TS2 Furnace with DX Cooling OA Rate [cfm] | Split TS2 Furnace with DX Cooling OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 |  |  |  |  | 2021-05-06 | AL
NM_MA_Split TSE Furnace with DX Cooling OA Rate [cfm] | Split TSE Furnace with DX Cooling OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 |  |  |  |  | 2021-05-06 | AR
NM_MA_Split TSW Furnace with DX Cooling OA Rate [cfm] | Split TSW Furnace with DX Cooling OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 |  |  |  |  | 2021-05-06 | CO
NM_MA_SPLIT GSW HEATING COIL Heating Capacity [kBtu/hr] | SPLIT GSW HEATING COIL Heating Capacity [kBtu/hr] | 6.8096 | 6.7096 | 5.9561 | 6.003 | 7.5862 | 7.6465 |  |  |  |  | 2021-05-06 | CT
NM_MA_SPLIT GNW HEATING COIL Heating Capacity [kBtu/hr] | SPLIT GNW HEATING COIL Heating Capacity [kBtu/hr] | 6.6944 | 6.5988 | 5.9012 | 5.9484 | 7.4829 | 7.5435 |  |  |  |  | 2021-05-06 | DC
NM_MA_SPLIT OFFICE HEATING COIL Heating Capacity [kBtu/hr] | SPLIT OFFICE HEATING COIL Heating Capacity [kBtu/hr] | 17.8162 | 17.6312 | 16.1439 | 16.2331 | 19.2366 | 19.3694 |  |  |  |  | 2021-05-06 | DE
NM_MA_SPLIT GNE HEATING COIL Heating Capacity [kBtu/hr] | SPLIT GNE HEATING COIL Heating Capacity [kBtu/hr] | 6.6944 | 6.5988 | 5.9012 | 5.9484 | 7.494 | 7.5545 |  |  |  |  | 2021-05-06 | GA
NM_MA_SPLIT GN1 HEATING COIL Heating Capacity [kBtu/hr] | SPLIT GN1 HEATING COIL Heating Capacity [kBtu/hr] | 4.7468 | 4.704 | 4.2215 | 4.2215 | 5.5124 | 5.573 |  |  |  |  | 2021-05-06 | IA
NM_MA_SPLIT GN2 HEATING COIL Heating Capacity [kBtu/hr] | SPLIT GN2 HEATING COIL Heating Capacity [kBtu/hr] | 4.7468 | 4.704 | 4.2215 | 4.2215 | 5.5128 | 5.5734 |  |  |  |  | 2021-05-06 | KY
NM_MA_SPLIT GS1 HEATING COIL Heating Capacity [kBtu/hr] | SPLIT GS1 HEATING COIL Heating Capacity [kBtu/hr] | 4.7742 | 4.7266 | 4.2215 | 4.2215 | 5.513 | 5.5734 |  |  |  |  | 2021-05-06 | MA
NM_MA_SPLIT GS2 HEATING COIL Heating Capacity [kBtu/hr] | SPLIT GS2 HEATING COIL Heating Capacity [kBtu/hr] | 5.2404 | 5.1881 | 4.552 | 4.5953 | 5.9849 | 6.0488 |  |  |  |  | 2021-05-06 | MT
NM_MA_SPLIT MSW HEATING COIL Heating Capacity [kBtu/hr] | SPLIT MSW HEATING COIL Heating Capacity [kBtu/hr] | 12.902 | 12.705 | 11.1088 | 11.2381 | 12.7789 | 12.9111 |  |  |  |  | 2021-05-06 | NC
NM_MA_SPLIT MNW HEATING COIL Heating Capacity [kBtu/hr] | SPLIT MNW HEATING COIL Heating Capacity [kBtu/hr] | 12.8322 | 12.6449 | 11.1635 | 11.2922 | 12.75 | 12.8818 |  |  |  |  | 2021-05-06 | NE
NM_MA_SPLIT MSE HEATING COIL Heating Capacity [kBtu/hr] | SPLIT MSE HEATING COIL Heating Capacity [kBtu/hr] | 12.902 | 12.705 | 11.1088 | 11.2381 | 12.8058 | 12.938 |  |  |  |  | 2021-05-06 | NJ
NM_MA_SPLIT MNE HEATING COIL Heating Capacity [kBtu/hr] | SPLIT MNE HEATING COIL Heating Capacity [kBtu/hr] | 12.8322 | 12.6449 | 11.1635 | 11.2922 | 12.777 | 12.9088 |  |  |  |  | 2021-05-06 | NY
NM_MA_SPLIT MN1 HEATING COIL Heating Capacity [kBtu/hr] | SPLIT MN1 HEATING COIL Heating Capacity [kBtu/hr] | 9.1333 | 9.1333 | 8.443 | 8.443 | 9.6869 | 9.6869 |  |  |  |  | 2021-05-06 | OK
NM_MA_SPLIT MN2 HEATING COIL Heating Capacity [kBtu/hr] | SPLIT MN2 HEATING COIL Heating Capacity [kBtu/hr] | 9.1333 | 9.1333 | 8.443 | 8.443 | 9.6869 | 9.6869 |  |  |  |  | 2021-05-06 | RI
NM_MA_SPLIT MS1 HEATING COIL Heating Capacity [kBtu/hr] | SPLIT MS1 HEATING COIL Heating Capacity [kBtu/hr] | 9.1333 | 9.1333 | 8.443 | 8.443 | 9.6869 | 9.6869 |  |  |  |  | 2021-05-06 | SC
NM_MA_SPLIT MS2 HEATING COIL Heating Capacity [kBtu/hr] | SPLIT MS2 HEATING COIL Heating Capacity [kBtu/hr] | 9.1333 | 9.1333 | 8.443 | 8.443 | 9.6869 | 9.6869 |  |  |  |  | 2021-05-06 | TX
NM_MA_SPLIT TSW HEATING COIL Heating Capacity [kBtu/hr] | SPLIT TSW HEATING COIL Heating Capacity [kBtu/hr] | 9.7755 | 9.6787 | 8.3279 | 8.3894 | 9.6477 | 9.7097 |  |  |  |  | 2021-05-06 | UT
NM_MA_SPLIT TNW HEATING COIL Heating Capacity [kBtu/hr] | SPLIT TNW HEATING COIL Heating Capacity [kBtu/hr] | 9.7442 | 9.6533 | 8.3622 | 8.4237 | 9.6382 | 9.7003 |  |  |  |  | 2021-05-06 | VA
NM_MA_SPLIT TSE HEATING COIL Heating Capacity [kBtu/hr] | SPLIT TSE HEATING COIL Heating Capacity [kBtu/hr] | 9.7755 | 9.6787 | 8.3279 | 8.3894 | 9.6624 | 9.7243 |  |  |  |  | 2021-05-06 | WI
NM_MA_SPLIT TNE HEATING COIL Heating Capacity [kBtu/hr] | SPLIT TNE HEATING COIL Heating Capacity [kBtu/hr] | 9.7442 | 9.6533 | 8.3622 | 8.4237 | 9.6529 | 9.715 |  |  |  |  | 2021-05-06
NM_MA_SPLIT TN1 HEATING COIL Heating Capacity [kBtu/hr] | SPLIT TN1 HEATING COIL Heating Capacity [kBtu/hr] | 7.4655 | 7.4301 | 6.2935 | 6.3549 | 7.6678 | 7.7299 |  |  |  |  | 2021-05-06
NM_MA_SPLIT TN2 HEATING COIL Heating Capacity [kBtu/hr] | SPLIT TN2 HEATING COIL Heating Capacity [kBtu/hr] | 7.4655 | 7.4301 | 6.2935 | 6.3549 | 7.6682 | 7.7303 |  |  |  |  | 2021-05-06
NM_MA_SPLIT TS1 HEATING COIL Heating Capacity [kBtu/hr] | SPLIT TS1 HEATING COIL Heating Capacity [kBtu/hr] | 7.4913 | 7.4498 | 6.2519 | 6.3132 | 7.6712 | 7.7332 |  |  |  |  | 2021-05-06
NM_MA_SPLIT TS2 HEATING COIL Heating Capacity [kBtu/hr] | SPLIT TS2 HEATING COIL Heating Capacity [kBtu/hr] | 7.4913 | 7.4498 | 6.2519 | 6.3132 | 7.6717 | 7.7337 |  |  |  |  | 2021-05-06
NM_MA_Split_GSW ERV Flag | Split_GSW ERV Flag | No | Yes | No | Yes | No | Yes |  |  |  |  | 2021-05-06 | AL
NM_MA_Split_GNW ERV Flag | Split_GNW ERV Flag | No | Yes | No | Yes | No | Yes |  |  |  |  | 2021-05-06 | AR
NM_MA_Split_GNE ERV Flag | Split_GNE ERV Flag | No | Yes | No | Yes | No | Yes |  |  |  |  | 2021-05-06 | CO
NM_MA_Split_GN1 ERV Flag | Split_GN1 ERV Flag | No | Yes | No | Yes | No | Yes |  |  |  |  | 2021-05-06 | CT
NM_MA_Split_GN2 ERV Flag | Split_GN2 ERV Flag | No | Yes | No | Yes | No | Yes |  |  |  |  | 2021-05-06 | DC
NM_MA_Split_GS1 ERV Flag | Split_GS1 ERV Flag | No | Yes | No | Yes | No | Yes |  |  |  |  | 2021-05-06 | DE
NM_MA_Split_GS2 ERV Flag | Split_GS2 ERV Flag | No | Yes | No | Yes | No | Yes |  |  |  |  | 2021-05-06 | GA
NM_MA_Split_MSW ERV Flag | Split_MSW ERV Flag | No | Yes | No | Yes | No | Yes |  |  |  |  | 2021-05-06 | IA
NM_MA_Split_MNW ERV Flag | Split_MNW ERV Flag | No | Yes | No | Yes | No | Yes |  |  |  |  | 2021-05-06 | KY
NM_MA_Split_MSE ERV Flag | Split_MSE ERV Flag | No | Yes | No | Yes | No | Yes |  |  |  |  | 2021-05-06 | MA
NM_MA_Split_MNE ERV Flag | Split_MNE ERV Flag | No | Yes | No | Yes | No | Yes |  |  |  |  | 2021-05-06 | MT
NM_MA_Split_MN1 ERV Flag | Split_MN1 ERV Flag | No | Yes | No | Yes | No | Yes |  |  |  |  | 2021-05-06 | NC
NM_MA_Split_MN2 ERV Flag | Split_MN2 ERV Flag | No | Yes | No | Yes | No | Yes |  |  |  |  | 2021-05-06 | NE
NM_MA_Split_MS1 ERV Flag | Split_MS1 ERV Flag | No | Yes | No | Yes | No | Yes |  |  |  |  | 2021-05-06 | NJ
NM_MA_Split_MS2 ERV Flag | Split_MS2 ERV Flag | No | Yes | No | Yes | No | Yes |  |  |  |  | 2021-05-06 | NY
NM_MA_Split_TSW ERV Flag | Split_TSW ERV Flag | No | No | No | No | No | No |  |  |  |  | 2021-05-06 | OK
NM_MA_Split_TNW ERV Flag | Split_TNW ERV Flag | No | No | No | No | No | No |  |  |  |  | 2021-05-06 | RI
NM_MA_Split_TSE ERV Flag | Split_TSE ERV Flag | No | Yes | No | Yes | No | Yes |  |  |  |  | 2021-05-06 | SC
NM_MA_Split_TNE ERV Flag | Split_TNE ERV Flag | No | Yes | No | Yes | No | Yes |  |  |  |  | 2021-05-06 | TX
NM_MA_Split_TN1 ERV Flag | Split_TN1 ERV Flag | No | Yes | No | Yes | No | Yes |  |  |  |  | 2021-05-06 | UT
NM_MA_Split_TN2 ERV Flag | Split_TN2 ERV Flag | No | Yes | No | Yes | No | Yes |  |  |  |  | 2021-05-06 | VA
NM_MA_Split_TS1 ERV Flag | Split_TS1 ERV Flag | No | Yes | No | Yes | No | Yes |  |  |  |  | 2021-05-06 | WI
NM_MA_Split_TS2 ERV Flag | Split_TS2 ERV Flag | No | Yes | No | Yes | No | Yes |  |  |  |  | 2021-05-06
id | item | Zone3B(NV-LasVegas-NV) ASHRAE901-state_STD2016 | Zone3B(NV-LasVegas-NV) ASHRAE901-state_STD2019 | Zone4B(NV-Tonopah-NV) ASHRAE901-state_STD2016 | Zone4B(NV-Tonopah-NV) ASHRAE901-state_STD2019 | Zone5B(NV-Winnermucca-NV) ASHRAE901-state_STD2016 | Zone5B(NV-Winnermucca-NV) ASHRAE901-state_STD2019 |  |  |  |  | 2021-05-06
NV_SO_PSZ-AC:1 Cooling Capacity [ton] | PSZ-AC:1 Cooling Capacity [ton] | 2.0293 | 1.929 | 1.7222 | 1.6034 | 1.6619 | 1.5476 |  |  |  |  | 2021-05-06
NV_SO_PSZ-AC:2 Cooling Capacity [ton] | PSZ-AC:2 Cooling Capacity [ton] | 2.0337 | 1.9577 | 1.517 | 1.4359 | 1.4865 | 1.4081 |  |  |  |  | 2021-05-06
NV_SO_PSZ-AC:3 Cooling Capacity [ton] | PSZ-AC:3 Cooling Capacity [ton] | 1.2193 | 1.1746 | 1.1008 | 1.0505 | 1.0972 | 1.049 |  |  |  |  | 2021-05-06
NV_SO_PSZ-AC:4 Cooling Capacity [ton] | PSZ-AC:4 Cooling Capacity [ton] | 1.9972 | 1.9024 | 1.4526 | 1.3689 | 1.4 | 1.3161 |  |  |  |  | 2021-05-06
NV_SO_PSZ-AC:5 Cooling Capacity [ton] | PSZ-AC:5 Cooling Capacity [ton] | 1.5523 | 1.5017 | 1.4281 | 1.3749 | 1.4191 | 1.3674 |  |  |  |  | 2021-05-06
NV_SO_PSZ-AC:1 Supply Flow Rate [cfm] | PSZ-AC:1 Supply Flow Rate [cfm] | 762.7968 | 720.4192 | 783.9856 | 720.4192 | 741.608 | 699.2304 |  |  |  |  | 2021-05-06
NV_SO_PSZ-AC:2 Supply Flow Rate [cfm] | PSZ-AC:2 Supply Flow Rate [cfm] | 805.1744 | 762.7968 | 678.0416 | 656.8528 | 678.0416 | 635.664 |  |  |  |  | 2021-05-06
NV_SO_PSZ-AC:3 Supply Flow Rate [cfm] | PSZ-AC:3 Supply Flow Rate [cfm] | 550.9088 | 529.72 | 487.3424 | 466.1536 | 487.3424 | 466.1536 |  |  |  |  | 2021-05-06
NV_SO_PSZ-AC:4 Supply Flow Rate [cfm] | PSZ-AC:4 Supply Flow Rate [cfm] | 783.9856 | 741.608 | 656.8528 | 614.4752 | 635.664 | 593.2864 |  |  |  |  | 2021-05-06
NV_SO_PSZ-AC:5 Supply Flow Rate [cfm] | PSZ-AC:5 Supply Flow Rate [cfm] | 656.8528 | 635.664 | 635.664 | 614.4752 | 635.664 | 614.4752 |  |  |  |  | 2021-05-06
NV_SO_PSZ-AC:1 OA Rate [cfm] | PSZ-AC:1 OA Rate [cfm] | 136.9178 | 136.9178 | 136.9178 | 136.9178 | 136.9178 | 136.9178 |  |  |  |  | 2021-05-06
NV_SO_PSZ-AC:2 OA Rate [cfm] | PSZ-AC:2 OA Rate [cfm] | 103.7925 | 103.7925 | 103.7925 | 103.7925 | 103.7925 | 103.7925 |  |  |  |  | 2021-05-06
NV_SO_PSZ-AC:3 OA Rate [cfm] | PSZ-AC:3 OA Rate [cfm] | 61.5711 | 61.5711 | 61.5711 | 61.5711 | 61.5711 | 61.5711 |  |  |  |  | 2021-05-06
NV_SO_PSZ-AC:4 OA Rate [cfm] | PSZ-AC:4 OA Rate [cfm] | 103.7925 | 103.7925 | 103.7925 | 103.7925 | 103.7925 | 103.7925 |  |  |  |  | 2021-05-06
NV_SO_PSZ-AC:5 OA Rate [cfm] | PSZ-AC:5 OA Rate [cfm] | 61.5711 | 61.5711 | 61.5711 | 61.5711 | 61.5711 | 61.5711 |  |  |  |  | 2021-05-06
NV_SO_PSZ-AC:1 heating Capacity [kBtu/hr] | PSZ-AC:1 heating Capacity [kBtu/hr] | 10.0756 | 10.0756 | 11.4692 | 11.4692 | 12.8538 | 12.8538 |  |  |  |  | 2021-05-06
NV_SO_PSZ-AC:2 heating Capacity [kBtu/hr] | PSZ-AC:2 heating Capacity [kBtu/hr] | 11.9396 | 11.7502 | 16.717 | 16.5212 | 17.6945 | 17.4708 |  |  |  |  | 2021-05-06
NV_SO_PSZ-AC:3 heating Capacity [kBtu/hr] | PSZ-AC:3 heating Capacity [kBtu/hr] | 7.2186 | 7.118 | 10.2525 | 10.1393 | 10.6978 | 10.5741 |  |  |  |  | 2021-05-06
NV_SO_PSZ-AC:4 heating Capacity [kBtu/hr] | PSZ-AC:4 heating Capacity [kBtu/hr] | 11.6844 | 11.5358 | 16.6258 | 16.4584 | 17.427 | 17.2502 |  |  |  |  | 2021-05-06
NV_SO_PSZ-AC:5 heating Capacity [kBtu/hr] | PSZ-AC:5 heating Capacity [kBtu/hr] | 7.2447 | 7.1398 | 10.2525 | 10.1393 | 10.6553 | 10.5357 |  |  |  |  | 2021-05-06
id | item | Zone3B(NV-LasVegas-NV) ASHRAE901-state_STD2016 | Zone3B(NV-LasVegas-NV) ASHRAE901-state_STD2019 | Zone4B(NV-Tonopah-NV) ASHRAE901-state_STD2016 | Zone4B(NV-Tonopah-NV) ASHRAE901-state_STD2019 | Zone5B(NV-Winnermucca-NV) ASHRAE901-state_STD2016 | Zone5B(NV-Winnermucca-NV) ASHRAE901-state_STD2019 |  |  |  |  | 2021-05-06
NV_LO_CAV_BAS Supply Flow Rate [cfm] | CAV_BAS Supply Flow Rate [cfm] | 12649.7136 | 11717.4064 | 14111.7408 | 13052.3008 | 13539.6432 | 12522.5808 |  |  |  |  | 2021-05-06
NV_LO_VAV_BOT WITH REHEAT Supply Flow Rate [cfm] | VAV_BOT WITH REHEAT Supply Flow Rate [cfm] | 21824.464 | 20807.4016 | 23180.5472 | 22057.5408 | 22375.3728 | 21315.9328 |  |  |  |  | 2021-05-06
NV_LO_VAV_MID WITH REHEAT Supply Flow Rate [cfm] | VAV_MID WITH REHEAT Supply Flow Rate [cfm] | 205467.7939 | 195636.1907 | 214176.3907 | 203560.8019 | 207162.8979 | 197013.4627 |  |  |  |  | 2021-05-06
NV_LO_VAV_TOP WITH REHEAT Supply Flow Rate [cfm] | VAV_TOP WITH REHEAT Supply Flow Rate [cfm] | 22227.0512 | 21294.744 | 23519.568 | 22544.8832 | 23032.2256 | 22099.9184 |  |  |  |  | 2021-05-06
NV_LO_Supply Air Temp. Reset Flag | Supply Air Temp. Reset Flag | Yes | Yes | Yes | Yes | Yes | Yes |  |  |  |  | 2021-05-06
NV_LO_CAV_BAS OA Rate [cfm] | CAV_BAS OA Rate [cfm] | 2542.8255 | 2542.8255 | 2542.8255 | 2542.8255 | 2542.8255 | 2542.8255 |  |  |  |  | 2021-05-06
NV_LO_VAV_BOT WITH REHEAT OA Rate [cfm] | VAV_BOT WITH REHEAT OA Rate [cfm] | 5377.8022 | 4302.174 | 5377.8022 | 4302.174 | 5377.8022 | 4302.174 |  |  |  |  | 2021-05-06
NV_LO_VAV_MID WITH REHEAT OA Rate [cfm] | VAV_MID WITH REHEAT OA Rate [cfm] | 53777.9373 | 43021.7396 | 53777.9373 | 43021.7396 | 53777.9373 | 43021.7396 |  |  |  |  | 2021-05-06
NV_LO_VAV_TOP WITH REHEAT OA Rate [cfm] | VAV_TOP WITH REHEAT OA Rate [cfm] | 5377.8022 | 4302.174 | 5377.8022 | 4302.174 | 5377.8022 | 4302.174 |  |  |  |  | 2021-05-06
NV_LO_AIRLOOP DATACENTER BASEMENT OA Rate [cfm] | AIRLOOP DATACENTER BASEMENT OA Rate [cfm] | 716.9654 | 716.9654 | 716.9654 | 716.9654 | 716.9654 | 716.9654 |  |  |  |  | 2021-05-06
NV_LO_VAV_bot_WITH_REHEAT ERV Flag | VAV_bot_WITH_REHEAT ERV Flag | No | No | No | No | No | No |  |  |  |  | 2021-05-06
NV_LO_VAV_mid_WITH_REHEAT ERV Flag | VAV_mid_WITH_REHEAT ERV Flag | No | No | No | No | No | No |  |  |  |  | 2021-05-06
NV_LO_VAV_top_WITH_REHEAT ERV Flag | VAV_top_WITH_REHEAT ERV Flag | No | No | No | No | No | No |  |  |  |  | 2021-05-06
NV_LO_COOLSYS1 CHILLER1 Capacity [ton] | COOLSYS1 CHILLER1 Capacity [ton] | 380.6749 | 349.4741 | 307.7797 | 283.0963 | 322.432 | 298.9751 |  |  |  |  | 2021-05-06
NV_LO_COOLSYS1 CHILLER2 Capacity [ton] | COOLSYS1 CHILLER2 Capacity [ton] | 380.6749 | 349.4741 | 307.7797 | 283.0963 | 322.432 | 298.9751 |  |  |  |  | 2021-05-06
NV_LO_TOWERWATERSYS COOLTOWER 1 Capacity [ton] | TOWERWATERSYS COOLTOWER 1 Capacity [ton] | 361.4841 | 331.8573 | 292.5075 | 269.0464 | 306.4264 | 284.1351 |  |  |  |  | 2021-05-06
NV_LO_TOWERWATERSYS COOLTOWER 2 Capacity [ton] | TOWERWATERSYS COOLTOWER 2 Capacity [ton] | 361.4841 | 331.8573 | 292.5075 | 269.0464 | 306.4264 | 284.1351 |  |  |  |  | 2021-05-06
NV_LO_HEATSYS1 BOILER Capacity [MMBTU/h] | HEATSYS1 BOILER Capacity [MMBTU/h] | 2952.8407 | 2611.3774 | 3861.7351 | 3433.4661 | 4181.3373 | 3697.073 |  |  |  |  | 2021-05-06
NV_LO_COOLSYS1 PUMP Flow Rate [gal/min] | COOLSYS1 PUMP Flow Rate [gal/min] | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 2021-05-06
NV_LO_COOLSYS1 CHILLER1 PUMP Flow Rate [gal/min] | COOLSYS1 CHILLER1 PUMP Flow Rate [gal/min] | 595.9896 | 546.9899 | 479.9668 | 441.5393 | 506.7126 | 469.4993 |  |  |  |  | 2021-05-06
NV_LO_COOLSYS1 CHILLER2 PUMP Flow Rate [gal/min] | COOLSYS1 CHILLER2 PUMP Flow Rate [gal/min] | 595.9896 | 546.9899 | 479.9668 | 441.5393 | 506.7126 | 469.4993 |  |  |  |  | 2021-05-06
NV_LO_COOLSYS1 PUMP SECONDARY Flow Rate [gal/min] | COOLSYS1 PUMP SECONDARY Flow Rate [gal/min] | 1191.9792 | 1093.9782 | 959.9336 | 883.0801 | 1013.4253 | 939.0001 |  |  |  |  | 2021-05-06
NV_LO_HEATSYS1 PUMP Flow Rate [gal/min] | HEATSYS1 PUMP Flow Rate [gal/min] | 606.11 | 536.0199 | 792.6715 | 704.764 | 858.2744 | 758.8723 |  |  |  |  | 2021-05-06
NV_LO_TOWERWATERSYS PUMP Flow Rate [gal/min] | TOWERWATERSYS PUMP Flow Rate [gal/min] | 2100.1678 | 1928.0333 | 1698.0451 | 1600.0901 | 1778.8818 | 1689.803 |  |  |  |  | 2021-05-06
NV_LO_PLANT CIRC PUMP Flow Rate [gal/min] | PLANT CIRC PUMP Flow Rate [gal/min] | 219.4556 | 218.4951 | 229.1846 | 228.2557 | 226.2871 | 225.3662 |  |  |  |  | 2021-05-06
NV_LO_COOLSYS1 PUMP SECONDARY Pressure setpoint reset [yes,no] | COOLSYS1 PUMP SECONDARY Pressure setpoint reset [yes,no] | pump_ride_on_curve | pump_ride_on_curve | pump_ride_on_curve | pump_ride_on_curve | pump_ride_on_curve | pump_ride_on_curve |  |  |  |  | 2021-05-06
NV_LO_COOLSYS1 CHILLER1 PUMP Pump Power [hp] | COOLSYS1 CHILLER1 PUMP Pump Power [hp] | 3.2152 | 2.9216 | 2.5892 | 2.3584 | 2.7335 | 2.5077 |  |  |  |  | 2021-05-06
NV_LO_COOLSYS1 CHILLER2 PUMP Pump Power [hp] | COOLSYS1 CHILLER2 PUMP Pump Power [hp] | 3.2152 | 2.9216 | 2.5892 | 2.3584 | 2.7335 | 2.5077 |  |  |  |  | 2021-05-06
NV_LO_COOLSYS1 PUMP SECONDARY Pump Power [hp] | COOLSYS1 PUMP SECONDARY Pump Power [hp] | 19.2909 | 17.5296 | 15.5355 | 14.1502 | 16.4012 | 15.0463 |  |  |  |  | 2021-05-06
NV_LO_HEATSYS1 PUMP Pump Power [hp] | HEATSYS1 PUMP Pump Power [hp] | 13.1014 | 11.4717 | 17.1341 | 15.0831 | 18.5521 | 16.2411 |  |  |  |  | 2021-05-06
NV_LO_TOWERWATERSYS PUMP Pump Power [hp] | TOWERWATERSYS PUMP Pump Power [hp] | 37.6023 | 34.1785 | 30.4018 | 28.3647 | 31.8492 | 29.9556 |  |  |  |  | 2021-05-06
NV_LO_PLANT CIRC PUMP Pump Power [hp] | PLANT CIRC PUMP Pump Power [hp] | 4.7355 | 4.6682 | 4.9455 | 4.8767 | 4.883 | 4.8149 |  |  |  |  | 2021-05-06
NV_LO_Datacenter PLANT CIRC PUMP Pump Power [hp] | Datacenter PLANT CIRC PUMP Pump Power [hp] | 4.7355 | 4.6682 | 4.9455 | 4.8767 | 4.883 | 4.8149 |  |  |  |  | 2021-05-06
NV_LO_ZN_VAV_BOXes_Max_Reheat_Water_Flow_GPM | ZN_VAV_BOXes_Max_Reheat_Water_Flow_GPM | 362.3061 | 343.765 | 439.6759 | 420.3209 | 446.8856 | 427.916 |  |  |  |  | 2021-05-06
NV_LO_COOLSYS1 PUMP SECONDARY VSD | COOLSYS1 PUMP SECONDARY VSD | No | No | No | No | No | No |  |  |  |  | 2021-05-06
NV_LO_HEATSYS1 PUMP VSD | HEATSYS1 PUMP VSD | No | No | No | No | No | No |  |  |  |  | 2021-05-06
NV_LO_DATACENTER BASEMENT Cooling Capacity [ton] | DATACENTER BASEMENT Cooling Capacity [ton] | 128.9357 | 128.5548 | 134.609 | 134.206 | 132.4826 | 132.0867 |  |  |  |  | 2021-05-06
NV_LO_DATACENTER BOT Cooling Capacity [ton] | DATACENTER BOT Cooling Capacity [ton] | 2.7701 | 2.7406 | 2.8863 | 2.8602 | 2.8799 | 2.8539 |  |  |  |  | 2021-05-06
NV_LO_DATACENTER MID Cooling Capacity [ton] | DATACENTER MID Cooling Capacity [ton] | 26.3798 | 26.1089 | 27.5726 | 27.3427 | 27.5798 | 27.349 |  |  |  |  | 2021-05-06
NV_LO_DATACENTER TOP Cooling Capacity [ton] | DATACENTER TOP Cooling Capacity [ton] | 2.6699 | 2.6482 | 2.815 | 2.7927 | 2.8178 | 2.7955 |  |  |  |  | 2021-05-06
id | item | Zone3B(NV-LasVegas-NV) ASHRAE901-state_STD2016 | Zone3B(NV-LasVegas-NV) ASHRAE901-state_STD2019 | Zone4B(NV-Tonopah-NV) ASHRAE901-state_STD2016 | Zone4B(NV-Tonopah-NV) ASHRAE901-state_STD2019 | Zone5B(NV-Winnermucca-NV) ASHRAE901-state_STD2016 | Zone5B(NV-Winnermucca-NV) ASHRAE901-state_STD2019 |  |  |  |  | 2021-05-06
NV_RS_PSZ-AC:1 Cooling Capacity [ton] | PSZ-AC:1 Cooling Capacity [ton] | 11.7687 | 11.2424 | 10.0713 | 9.3289 | 10.2201 | 9.4539 |  |  |  |  | 2021-05-06
NV_RS_PSZ-AC:2 Cooling Capacity [ton] | PSZ-AC:2 Cooling Capacity [ton] | 54.9513 | 52.5914 | 42.2271 | 40.1781 | 43.9728 | 41.9165 |  |  |  |  | 2021-05-06
NV_RS_PSZ-AC:3 Cooling Capacity [ton] | PSZ-AC:3 Cooling Capacity [ton] | 7.8369 | 7.6477 | 5.7242 | 5.5384 | 5.9323 | 5.7747 |  |  |  |  | 2021-05-06
NV_RS_PSZ-AC:4 Cooling Capacity [ton] | PSZ-AC:4 Cooling Capacity [ton] | 6.4744 | 6.2729 | 4.5186 | 4.3531 | 4.7692 | 4.5951 |  |  |  |  | 2021-05-06
NV_RS_PSZ-AC:1 Supply Flow Rate [cfm] | PSZ-AC:1 Supply Flow Rate [cfm] | 4936.9904 | 4640.3472 | 4428.4592 | 4047.0608 | 4195.3824 | 3835.1728 |  |  |  |  | 2021-05-06
NV_RS_PSZ-AC:2 Supply Flow Rate [cfm] | PSZ-AC:2 Supply Flow Rate [cfm] | 17353.6272 | 16378.9424 | 17862.1584 | 16866.2848 | 17120.5504 | 16124.6768 |  |  |  |  | 2021-05-06
NV_RS_PSZ-AC:3 Supply Flow Rate [cfm] | PSZ-AC:3 Supply Flow Rate [cfm] | 2775.7328 | 2690.9776 | 2585.0336 | 2500.2784 | 2500.2784 | 2415.5232 |  |  |  |  | 2021-05-06
NV_RS_PSZ-AC:4 Supply Flow Rate [cfm] | PSZ-AC:4 Supply Flow Rate [cfm] | 2203.6352 | 2118.88 | 1970.5584 | 1885.8032 | 1928.1808 | 1843.4256 |  |  |  |  | 2021-05-06
NV_RS_PSZ-AC:1 OA Rate [cfm] | PSZ-AC:1 OA Rate [cfm] | 490.669 | 490.669 | 490.669 | 490.669 | 490.669 | 490.669 |  |  |  |  | 2021-05-06
NV_RS_PSZ-AC:2 OA Rate [cfm] | PSZ-AC:2 OA Rate [cfm] | 4005.1282 | 4005.1282 | 4005.1282 | 4005.1282 | 4005.1282 | 4005.1282 |  |  |  |  | 2021-05-06
NV_RS_PSZ-AC:3 OA Rate [cfm] | PSZ-AC:3 OA Rate [cfm] | 377.3937 | 377.3937 | 377.3937 | 377.3937 | 377.3937 | 377.3937 |  |  |  |  | 2021-05-06
NV_RS_PSZ-AC:4 OA Rate [cfm] | PSZ-AC:4 OA Rate [cfm] | 377.3937 | 377.3937 | 377.3937 | 377.3937 | 377.3937 | 377.3937 |  |  |  |  | 2021-05-06
NV_RS_PSZ-AC:1 OA Damper [gravity, motorized] | PSZ-AC:1 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | motorized | motorized |  |  |  |  | 2021-05-06
NV_RS_PSZ-AC:2 OA Damper [gravity, motorized] | PSZ-AC:2 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | motorized | motorized |  |  |  |  | 2021-05-06
NV_RS_PSZ-AC:3 OA Damper [gravity, motorized] | PSZ-AC:3 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | motorized | motorized |  |  |  |  | 2021-05-06
NV_RS_PSZ-AC:4 OA Damper [gravity, motorized] | PSZ-AC:4 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | motorized | motorized |  |  |  |  | 2021-05-06
NV_RS_PSZ-AC:1 Heating Capacity [kBtu/hr] | PSZ-AC:1 Heating Capacity [kBtu/hr] | 189.2293 | 179.5293 | 159.6554 | 146.8598 | 161.9946 | 148.756 |  |  |  |  | 2021-05-06
NV_RS_PSZ-AC:2 Heating Capacity [kBtu/hr] | PSZ-AC:2 Heating Capacity [kBtu/hr] | 744.7461 | 709.7124 | 744.1336 | 710.6591 | 778.5832 | 742.7497 |  |  |  |  | 2021-05-06
NV_RS_PSZ-AC:3 Heating Capacity [kBtu/hr] | PSZ-AC:3 Heating Capacity [kBtu/hr] | 110.129 | 107.3793 | 98.4181 | 95.7984 | 101.5724 | 98.8633 |  |  |  |  | 2021-05-06
NV_RS_PSZ-AC:4 Heating Capacity [kBtu/hr] | PSZ-AC:4 Heating Capacity [kBtu/hr] | 90.8738 | 88.0014 | 80.2196 | 77.7035 | 84.738 | 82.0921 |  |  |  |  | 2021-05-06
id | item | Zone3B(NV-LasVegas-NV) ASHRAE901-state_STD2016 | Zone3B(NV-LasVegas-NV) ASHRAE901-state_STD2019 | Zone4B(NV-Tonopah-NV) ASHRAE901-state_STD2016 | Zone4B(NV-Tonopah-NV) ASHRAE901-state_STD2019 | Zone5B(NV-Winnermucca-NV) ASHRAE901-state_STD2016 | Zone5B(NV-Winnermucca-NV) ASHRAE901-state_STD2019 |  |  |  |  | 2021-05-06
NV_PS_VAV_POD_1 Cooling Capacity [ton] | VAV_POD_1 Cooling Capacity [ton] | 23.3081 | 22.0879 | 22.5806 | 21.1382 | 22.2793 | 20.8811 |  |  |  |  | 2021-05-06
NV_PS_VAV_POD_2 Cooling Capacity [ton] | VAV_POD_2 Cooling Capacity [ton] | 23.1982 | 21.8602 | 22.248 | 20.7728 | 21.9519 | 20.5271 |  |  |  |  | 2021-05-06
NV_PS_VAV_POD_3 Cooling Capacity [ton] | VAV_POD_3 Cooling Capacity [ton] | 21.2471 | 20.0392 | 20.7122 | 18.9711 | 20.4459 | 19.259 |  |  |  |  | 2021-05-06
NV_PS_VAV_OTHER Cooling Capacity [ton] | VAV_OTHER Cooling Capacity [ton] | 31.5268 | 28.3894 | 23.6196 | 21.4529 | 24.8986 | 22.5471 |  |  |  |  | 2021-05-06
NV_PS_PSZ-AC_1:6 Cooling Capacity [ton] | PSZ-AC_1:6 Cooling Capacity [ton] | 9.1141 | 8.7991 | 7.8534 | 7.568 | 8.0404 | 7.755 |  |  |  |  | 2021-05-06
NV_PS_PSZ-AC_2:5 Cooling Capacity [ton] | PSZ-AC_2:5 Cooling Capacity [ton] | 6.0504 | 5.9187 | 5.3919 | 5.4549 | 5.6767 | 5.6596 |  |  |  |  | 2021-05-06
NV_PS_PSZ-AC_2:7 Cooling Capacity [ton] | PSZ-AC_2:7 Cooling Capacity [ton] | 10.5074 | 10.5074 | 10.4702 | 10.4702 | 10.5074 | 10.5074 |  |  |  |  | 2021-05-06
NV_PS_VAV_POD_1 Supply Flow Rate [cfm] | VAV_POD_1 Supply Flow Rate [cfm] | 6992.304 | 6632.0944 | 6801.6048 | 6356.64 | 6695.6608 | 6271.8848 |  |  |  |  | 2021-05-06
NV_PS_VAV_POD_2 Supply Flow Rate [cfm] | VAV_POD_2 Supply Flow Rate [cfm] | 6971.1152 | 6568.528 | 6695.6608 | 6250.696 | 6589.7168 | 6165.9408 |  |  |  |  | 2021-05-06
NV_PS_VAV_POD_3 Supply Flow Rate [cfm] | VAV_POD_3 Supply Flow Rate [cfm] | 6377.8288 | 6017.6192 | 6229.5072 | 5869.2976 | 6144.752 | 5784.5424 |  |  |  |  | 2021-05-06
NV_PS_VAV_OTHER Supply Flow Rate [cfm] | VAV_OTHER Supply Flow Rate [cfm] | 9471.3936 | 8941.6736 | 9619.7152 | 9047.6176 | 9429.016 | 8878.1072 |  |  |  |  | 2021-05-06
NV_PS_PSZ-AC_2:5 Supply Flow Rate [cfm] | PSZ-AC_2:5 Supply Flow Rate [cfm] | 1822.2368 | 1779.8592 | 1928.1808 | 1970.5584 | 1928.1808 | 1906.992 |  |  |  |  | 2021-05-06
NV_PS_PSZ-AC_1:6 Supply Flow Rate [cfm] | PSZ-AC_1:6 Supply Flow Rate [cfm] | 2754.544 | 2648.6 | 3072.376 | 2924.0544 | 2945.2432 | 2818.1104 |  |  |  |  | 2021-05-06
NV_PS_PSZ-AC_2:7 Supply Flow Rate [cfm] | PSZ-AC_2:7 Supply Flow Rate [cfm] | 3157.1312 | 3157.1312 | 3157.1312 | 3157.1312 | 3157.1312 | 3157.1312 |  |  |  |  | 2021-05-06
NV_PS_Supply Air Temp. Reset Flag | Supply Air Temp. Reset Flag | Yes | Yes | Yes | Yes | Yes | Yes |  |  |  |  | 2021-05-06
NV_PS_VAV_POD_1 OA Rate [cfm] | VAV_POD_1 OA Rate [cfm] | 6993.3846 | 6282.2673 | 6802.071 | 6282.2673 | 6684.1553 | 6266.0791 |  |  |  |  | 2021-05-06
NV_PS_VAV_POD_2 OA Rate [cfm] | VAV_POD_2 OA Rate [cfm] | 6961.3896 | 6282.2673 | 6696.2965 | 6252.7725 | 6584.6951 | 6159.8384 |  |  |  |  | 2021-05-06
NV_PS_VAV_POD_3 OA Rate [cfm] | VAV_POD_3 OA Rate [cfm] | 6374.3115 | 5422.002 | 6234.529 | 5422.002 | 6135.4925 | 5422.002 |  |  |  |  | 2021-05-06
NV_PS_VAV_OTHER OA Rate [cfm] | VAV_OTHER OA Rate [cfm] | 3736.1787 | 2988.8921 | 3736.1787 | 2988.8921 | 3736.1787 | 2988.8921 |  |  |  |  | 2021-05-06
NV_PS_PSZ-AC_2:5 OA Rate [cfm] | PSZ-AC_2:5 OA Rate [cfm] | 1152.7343 | 1152.7343 | 1152.7343 | 1152.7343 | 1152.7343 | 1152.7343 |  |  |  |  | 2021-05-06
NV_PS_PSZ-AC_1:6 OA Rate [cfm] | PSZ-AC_1:6 OA Rate [cfm] | 539.9118 | 539.9118 | 539.9118 | 539.9118 | 539.9118 | 539.9118 |  |  |  |  | 2021-05-06
NV_PS_PSZ-AC_2:7 OA Rate [cfm] | PSZ-AC_2:7 OA Rate [cfm] | 3153.0841 | 3153.0841 | 3153.0841 | 3153.0841 | 3153.0841 | 3153.0841 |  |  |  |  | 2021-05-06
NV_PS_VAV_POD_1 OA Damper [gravity, motorized] | VAV_POD_1 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | motorized | motorized |  |  |  |  | 2021-05-06
NV_PS_VAV_POD_2 OA Damper [gravity, motorized] | VAV_POD_2 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | motorized | motorized |  |  |  |  | 2021-05-06
NV_PS_VAV_POD_3 OA Damper [gravity, motorized] | VAV_POD_3 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | motorized | motorized |  |  |  |  | 2021-05-06
NV_PS_VAV_OTHER OA Damper [gravity, motorized] | VAV_OTHER OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | motorized | motorized |  |  |  |  | 2021-05-06
NV_PS_PSZ-AC_2:5 OA Damper [gravity, motorized] | PSZ-AC_2:5 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | motorized | motorized |  |  |  |  | 2021-05-06
NV_PS_PSZ-AC_1:6 OA Damper [gravity, motorized] | PSZ-AC_1:6 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | motorized | motorized |  |  |  |  | 2021-05-06
NV_PS_PSZ-AC_2:7 OA Damper [gravity, motorized] | PSZ-AC_2:7 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | motorized | motorized |  |  |  |  | 2021-05-06
NV_PS_VAV_POD_1 (economizer) | VAV_POD_1 (economizer) | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb |  |  |  |  | 2021-05-06
NV_PS_VAV_POD_2 (economizer) | VAV_POD_2 (economizer) | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb |  |  |  |  | 2021-05-06
NV_PS_VAV_POD_3 (economizer) | VAV_POD_3 (economizer) | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb |  |  |  |  | 2021-05-06
NV_PS_VAV_OTHER (economizer) | VAV_OTHER (economizer) | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb |  |  |  |  | 2021-05-06
NV_PS_PSZ-AC_2:5 (economizer) | PSZ-AC_2:5 (economizer) | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb |  |  |  |  | 2021-05-06
NV_PS_PSZ-AC_1:6 (economizer) | PSZ-AC_1:6 (economizer) | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb |  |  |  |  | 2021-05-06
NV_PS_PSZ-AC_2:7 (economizer) | PSZ-AC_2:7 (economizer) | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb |  |  |  |  | 2021-05-06
NV_PS_VAV_Pod_1_ERV Flag | VAV_Pod_1_ERV Flag | No | No | No | No | No | No |  |  |  |  | 2021-05-06
NV_PS_VAV_Pod_2_ERV Flag | VAV_Pod_2_ERV Flag | No | No | No | No | No | No |  |  |  |  | 2021-05-06
NV_PS_VAV_Pod_3_ERV Flag | VAV_Pod_3_ERV Flag | No | No | No | No | No | No |  |  |  |  | 2021-05-06
NV_PS_VAV_OTHER_ERV Flag | VAV_OTHER_ERV Flag | No | No | No | No | No | No |  |  |  |  | 2021-05-06
NV_PS_PSZ_AC_2_5_ERV Flag | PSZ_AC_2_5_ERV Flag | No | No | No | No | No | No |  |  |  |  | 2021-05-06
NV_PS_PSZ_AC_2_7_ERV Flag | PSZ_AC_2_7_ERV Flag | No | No | No | No | No | No |  |  |  |  | 2021-05-06
NV_PS_HEATSYS1 Capacity [MMBTU/h] | HEATSYS1 Capacity [MMBTU/h] | 0.79794 | 0.72762 | 1.0029 | 0.93366 | 1.0958 | 1.0228 |  |  |  |  | 2021-05-06
NV_PS_HEATSYS1 Flow Rate [gal/min] | HEATSYS1 Flow Rate [gal/min] | 81.894 | 74.6772 | 102.9304 | 95.8231 | 112.4603 | 104.974 |  |  |  |  | 2021-05-06
NV_PS_VAV_POD_1 Fan Power [hp] | VAV_POD_1 Fan Power [hp] | 10.2406 | 9.7786 | 9.9591 | 9.392 | 9.8633 | 9.2443 |  |  |  |  | 2021-05-06
NV_PS_VAV_POD_2 Fan Power [hp] | VAV_POD_2 Fan Power [hp] | 10.1923 | 9.6778 | 9.8798 | 9.2247 | 9.7184 | 9.0876 |  |  |  |  | 2021-05-06
NV_PS_VAV_POD_3 Fan Power [hp] | VAV_POD_3 Fan Power [hp] | 9.4064 | 8.8716 | 9.1978 | 8.6496 | 9.0517 | 8.5262 |  |  |  |  | 2021-05-06
NV_PS_VAV_OTHER Fan Power [hp] | VAV_OTHER Fan Power [hp] | 13.8528 | 13.0888 | 14.0984 | 13.2619 | 13.7938 | 12.9837 |  |  |  |  | 2021-05-06
NV_PS_HEATSYS1 Pump Power [hp] | HEATSYS1 Pump Power [hp] | 1.7702 | 1.5982 | 2.2249 | 2.0508 | 2.4309 | 2.2466 |  |  |  |  | 2021-05-06
NV_PS_PSZ-AC_1:6 Heating Capacity [kBtu/hr] | PSZ-AC_1:6 Heating Capacity [kBtu/hr] | 200.0914 | 191.3944 | 206.211 | 197.8171 | 211.3057 | 202.8779 |  |  |  |  | 2021-05-06
NV_PS_PSZ-AC_2:5 Heating Capacity [kBtu/hr] | PSZ-AC_2:5 Heating Capacity [kBtu/hr] | 107.5458 | 106.1912 | 120.3205 | 121.2728 | 132.5886 | 132.3161 |  |  |  |  | 2021-05-06
NV_PS_PSZ-AC_2:7 Heating Capacity [kBtu/hr] | PSZ-AC_2:7 Heating Capacity [kBtu/hr] | 232.032 | 232.032 | 264.126 | 264.126 | 296.0123 | 296.0123 |  |  |  |  | 2021-05-06
NV_PS_ZN_VAV_BOXes_Max_Reheat_Water_Flow_GPM | ZN_VAV_BOXes_Max_Reheat_Water_Flow_GPM | 59.3926 | 53.4234 | 66.4354 | 61.5938 | 69.3163 | 64.4587 |  |  |  |  | 2021-05-06
id | item | Zone3B(NV-LasVegas-NV) ASHRAE901-state_STD2016 | Zone3B(NV-LasVegas-NV) ASHRAE901-state_STD2019 | Zone4B(NV-Tonopah-NV) ASHRAE901-state_STD2016 | Zone4B(NV-Tonopah-NV) ASHRAE901-state_STD2019 | Zone5B(NV-Winnermucca-NV) ASHRAE901-state_STD2016 | Zone5B(NV-Winnermucca-NV) ASHRAE901-state_STD2019 |  |  |  |  | 2021-05-06
NV_SH_SAC_FRONTOFFICE Cooling Capacity [ton] | SAC_FRONTOFFICE Cooling Capacity [ton] | 2.7159 | 2.5535 | 2.0757 | 1.9565 | 2.1448 | 2.0242 |  |  |  |  | 2021-05-06
NV_SH_SAC_FRONTLOUNGE Cooling Capacity [ton] | SAC_FRONTLOUNGE Cooling Capacity [ton] | 6.8572 | 6.5791 | 5.4279 | 5.189 | 5.633 | 5.394 |  |  |  |  | 2021-05-06
NV_SH_SAC_MEETINGROOM Cooling Capacity [ton] | SAC_MEETINGROOM Cooling Capacity [ton] | 3.33 | 3.2357 | 2.8328 | 2.7715 | 2.9415 | 2.8727 |  |  |  |  | 2021-05-06
NV_SH_SAC_EXC_EMPLGE_RESTRM Cooling Capacity [ton] | SAC_EXC_EMPLGE_RESTRM Cooling Capacity [ton] | 6.5996 | 6.5506 | 5.8635 | 5.8145 | 5.9215 | 5.8763 |  |  |  |  | 2021-05-06
NV_SH_SAC_FO_ADDAQ SUPPLY FAN Supply Flow Rate [cfm] | SAC_FO_ADDAQ SUPPLY FAN Supply Flow Rate [cfm] | 953.496 | 889.9296 | 911.1184 | 868.7408 | 889.9296 | 826.3632 |  |  |  |  | 2021-05-06
NV_SH_SAC_FL_ADDAQ SUPPLY FAN Supply Flow Rate [cfm] | SAC_FL_ADDAQ SUPPLY FAN Supply Flow Rate [cfm] | 2140.0688 | 2034.1248 | 2203.6352 | 2097.6912 | 2118.88 | 2012.936 |  |  |  |  | 2021-05-06
NV_SH_SAC_MR_ADDAQ SUPPLY FAN Supply Flow Rate [cfm] | SAC_MR_ADDAQ SUPPLY FAN Supply Flow Rate [cfm] | 995.8736 | 974.6848 | 1038.2512 | 1017.0624 | 995.8736 | 974.6848 |  |  |  |  | 2021-05-06
NV_SH_SAC_EXC_ADDAQ SUPPLY FAN Supply Flow Rate [cfm] | SAC_EXC_ADDAQ SUPPLY FAN Supply Flow Rate [cfm] | 2394.3344 | 2373.1456 | 2648.6 | 2627.4112 | 2542.656 | 2521.4672 |  |  |  |  | 2021-05-06
NV_SH_SAC_Exc_EmpLge_RestRm OA Rate [cfm] | SAC_Exc_EmpLge_RestRm OA Rate [cfm] | 199.9928 | 199.9928 | 199.9928 | 199.9928 | 199.9928 | 199.9928 |  |  |  |  | 2021-05-06
NV_SH_SAC_FrontLounge OA Rate [cfm] | SAC_FrontLounge OA Rate [cfm] | 500.0133 | 500.0133 | 500.0133 | 500.0133 | 500.0133 | 500.0133 |  |  |  |  | 2021-05-06
NV_SH_SAC_FrontOffice OA Rate [cfm] | SAC_FrontOffice OA Rate [cfm] | 119.2938 | 119.2938 | 119.2938 | 119.2938 | 119.2938 | 119.2938 |  |  |  |  | 2021-05-06
NV_SH_SAC_MeetingRoom OA Rate [cfm] | SAC_MeetingRoom OA Rate [cfm] | 267.7629 | 267.7629 | 267.7629 | 267.7629 | 267.7629 | 267.7629 |  |  |  |  | 2021-05-06
NV_SH_SAC_FrontLounge OA Damper [gravity, motorized] | SAC_FrontLounge OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | motorized | motorized |  |  |  |  | 2021-05-06
NV_SH_SAC_FrontOffice (economizer) | SAC_FrontOffice (economizer) | No | No | No | No | No | No |  |  |  |  | 2021-05-06
NV_SH_SAC_FrontLounge (economizer) | SAC_FrontLounge (economizer) | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb |  |  |  |  | 2021-05-06
NV_SH_SAC_MeetingRoom (economizer) | SAC_MeetingRoom (economizer) | No | No | No | No | No | No |  |  |  |  | 2021-05-06
NV_SH_SAC_Exc_EmpLge_RestRm (economizer) | SAC_Exc_EmpLge_RestRm (economizer) | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb |  |  |  |  | 2021-05-06
NV_SH_SAC_FRONTOFFICE Heating Capacity [kBtu/hr] | SAC_FRONTOFFICE Heating Capacity [kBtu/hr] | 37.5183 | 35.2481 | 34.1629 | 32.4097 | 35.3275 | 33.5503 |  |  |  |  | 2021-05-06
NV_SH_SAC_FRONTLOUNGE Heating Capacity [kBtu/hr] | SAC_FRONTLOUNGE Heating Capacity [kBtu/hr] | 92.5153 | 89.0822 | 93.0895 | 89.7318 | 97.5263 | 94.1818 |  |  |  |  | 2021-05-06
NV_SH_SAC_MEETINGROOM Heating Capacity [kBtu/hr] | SAC_MEETINGROOM Heating Capacity [kBtu/hr] | 44.6263 | 43.6624 | 45.6571 | 44.8445 | 48.1269 | 47.2274 |  |  |  |  | 2021-05-06
NV_SH_SAC_EXC_EMPLGE_RESTRM Heating Capacity [kBtu/hr] | SAC_EXC_EMPLGE_RESTRM Heating Capacity [kBtu/hr] | 89.6535 | 88.9884 | 90.2725 | 89.6087 | 92.486 | 91.8232 |  |  |  |  | 2021-05-06
id | item | Zone3B(NV-LasVegas-NV) ASHRAE901-state_STD2016 | Zone3B(NV-LasVegas-NV) ASHRAE901-state_STD2019 | Zone4B(NV-Tonopah-NV) ASHRAE901-state_STD2016 | Zone4B(NV-Tonopah-NV) ASHRAE901-state_STD2019 | Zone5B(NV-Winnermucca-NV) ASHRAE901-state_STD2016 | Zone5B(NV-Winnermucca-NV) ASHRAE901-state_STD2019 |  |  |  |  | 2021-05-06
NV_MA_SPLIT GSW COOLING COIL Cooling Capacity [ton] | SPLIT GSW COOLING COIL Cooling Capacity [ton] | 1.0266 | 1.0117 | 0.7942 | 0.77581 | 0.79266 | 0.77454 |  |  |  |  | 2021-05-06
NV_MA_SPLIT GNW COOLING COIL Cooling Capacity [ton] | SPLIT GNW COOLING COIL Cooling Capacity [ton] | 0.9842 | 0.97025 | 0.75987 | 0.74195 | 0.74923 | 0.73186 |  |  |  |  | 2021-05-06
NV_MA_SPLIT OFFICE COOLING COIL Cooling Capacity [ton] | SPLIT OFFICE COOLING COIL Cooling Capacity [ton] | 2.0012 | 1.8967 | 1.7631 | 1.571 | 1.7292 | 1.5436 |  |  |  |  | 2021-05-06
NV_MA_SPLIT GNE COOLING COIL Cooling Capacity [ton] | SPLIT GNE COOLING COIL Cooling Capacity [ton] | 0.88989 | 0.87693 | 0.63142 | 0.61613 | 0.61655 | 0.60173 |  |  |  |  | 2021-05-06
NV_MA_SPLIT GN1 COOLING COIL Cooling Capacity [ton] | SPLIT GN1 COOLING COIL Cooling Capacity [ton] | 0.73381 | 0.7231 | 0.53181 | 0.51953 | 0.51188 | 0.50005 |  |  |  |  | 2021-05-06
NV_MA_SPLIT GN2 COOLING COIL Cooling Capacity [ton] | SPLIT GN2 COOLING COIL Cooling Capacity [ton] | 0.73218 | 0.72148 | 0.52917 | 0.51697 | 0.50918 | 0.49743 |  |  |  |  | 2021-05-06
NV_MA_SPLIT GS1 COOLING COIL Cooling Capacity [ton] | SPLIT GS1 COOLING COIL Cooling Capacity [ton] | 0.75198 | 0.74096 | 0.5653 | 0.55216 | 0.55525 | 0.54235 |  |  |  |  | 2021-05-06
NV_MA_SPLIT GS2 COOLING COIL Cooling Capacity [ton] | SPLIT GS2 COOLING COIL Cooling Capacity [ton] | 0.78984 | 0.77579 | 0.60939 | 0.59009 | 0.59795 | 0.57913 |  |  |  |  | 2021-05-06
NV_MA_SPLIT MSW COOLING COIL Cooling Capacity [ton] | SPLIT MSW COOLING COIL Cooling Capacity [ton] | 2.2712 | 2.2389 | 2.0424 | 2.0014 | 2.0338 | 1.993 |  |  |  |  | 2021-05-06
NV_MA_SPLIT MNW COOLING COIL Cooling Capacity [ton] | SPLIT MNW COOLING COIL Cooling Capacity [ton] | 2.1793 | 2.1492 | 1.9676 | 1.9276 | 1.9413 | 1.9022 |  |  |  |  | 2021-05-06
NV_MA_SPLIT MSE COOLING COIL Cooling Capacity [ton] | SPLIT MSE COOLING COIL Cooling Capacity [ton] | 2.0964 | 2.0653 | 1.6553 | 1.6216 | 1.6286 | 1.5959 |  |  |  |  | 2021-05-06
NV_MA_SPLIT MNE COOLING COIL Cooling Capacity [ton] | SPLIT MNE COOLING COIL Cooling Capacity [ton] | 1.8914 | 1.8643 | 1.5443 | 1.5154 | 1.4927 | 1.4648 |  |  |  |  | 2021-05-06
NV_MA_SPLIT MN1 COOLING COIL Cooling Capacity [ton] | SPLIT MN1 COOLING COIL Cooling Capacity [ton] | 1.5153 | 1.493 | 1.2408 | 1.2173 | 1.1882 | 1.1657 |  |  |  |  | 2021-05-06
NV_MA_SPLIT MN2 COOLING COIL Cooling Capacity [ton] | SPLIT MN2 COOLING COIL Cooling Capacity [ton] | 1.511 | 1.4887 | 1.2334 | 1.2101 | 1.1805 | 1.1582 |  |  |  |  | 2021-05-06
NV_MA_SPLIT MS1 COOLING COIL Cooling Capacity [ton] | SPLIT MS1 COOLING COIL Cooling Capacity [ton] | 1.5515 | 1.5285 | 1.2972 | 1.273 | 1.2649 | 1.2411 |  |  |  |  | 2021-05-06
NV_MA_SPLIT MS2 COOLING COIL Cooling Capacity [ton] | SPLIT MS2 COOLING COIL Cooling Capacity [ton] | 1.5471 | 1.5242 | 1.2899 | 1.2658 | 1.2574 | 1.2338 |  |  |  |  | 2021-05-06
NV_MA_SPLIT TSW COOLING COIL Cooling Capacity [ton] | SPLIT TSW COOLING COIL Cooling Capacity [ton] | 1.4583 | 1.4417 | 1.3426 | 1.3198 | 1.3366 | 1.3143 |  |  |  |  | 2021-05-06
NV_MA_SPLIT TNW COOLING COIL Cooling Capacity [ton] | SPLIT TNW COOLING COIL Cooling Capacity [ton] | 1.4087 | 1.3927 | 1.2899 | 1.2678 | 1.2768 | 1.2553 |  |  |  |  | 2021-05-06
NV_MA_SPLIT TSE COOLING COIL Cooling Capacity [ton] | SPLIT TSE COOLING COIL Cooling Capacity [ton] | 1.3559 | 1.3402 | 1.13 | 1.1124 | 1.1173 | 1.0999 |  |  |  |  | 2021-05-06
NV_MA_SPLIT TNE COOLING COIL Cooling Capacity [ton] | SPLIT TNE COOLING COIL Cooling Capacity [ton] | 1.2892 | 1.2741 | 1.043 | 1.0267 | 1.0211 | 1.0054 |  |  |  |  | 2021-05-06
NV_MA_SPLIT TN1 COOLING COIL Cooling Capacity [ton] | SPLIT TN1 COOLING COIL Cooling Capacity [ton] | 1.0364 | 1.024 | 0.83241 | 0.81956 | 0.80864 | 0.79637 |  |  |  |  | 2021-05-06
NV_MA_SPLIT TN2 COOLING COIL Cooling Capacity [ton] | SPLIT TN2 COOLING COIL Cooling Capacity [ton] | 1.0419 | 1.0295 | 0.83103 | 0.8183 | 0.80749 | 0.7953 |  |  |  |  | 2021-05-06
NV_MA_SPLIT TS1 COOLING COIL Cooling Capacity [ton] | SPLIT TS1 COOLING COIL Cooling Capacity [ton] | 1.1078 | 1.0947 | 0.91762 | 0.90334 | 0.90191 | 0.88804 |  |  |  |  | 2021-05-06
NV_MA_SPLIT TS2 COOLING COIL Cooling Capacity [ton] | SPLIT TS2 COOLING COIL Cooling Capacity [ton] | 1.109 | 1.096 | 0.91776 | 0.90358 | 0.90179 | 0.88795 |  |  |  |  | 2021-05-06
NV_MA_Split GN1 Furnace with DX Cooling OA Rate [cfm] | Split GN1 Furnace with DX Cooling OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 |  |  |  |  | 2021-05-06
NV_MA_Split GN2 Furnace with DX Cooling OA Rate [cfm] | Split GN2 Furnace with DX Cooling OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 |  |  |  |  | 2021-05-06
NV_MA_Split GNE Furnace with DX Cooling OA Rate [cfm] | Split GNE Furnace with DX Cooling OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 |  |  |  |  | 2021-05-06
NV_MA_Split GNW Furnace with DX Cooling OA Rate [cfm] | Split GNW Furnace with DX Cooling OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 |  |  |  |  | 2021-05-06
NV_MA_Split GS1 Furnace with DX Cooling OA Rate [cfm] | Split GS1 Furnace with DX Cooling OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 |  |  |  |  | 2021-05-06
NV_MA_Split GS2 Furnace with DX Cooling OA Rate [cfm] | Split GS2 Furnace with DX Cooling OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 |  |  |  |  | 2021-05-06
NV_MA_Split GSW Furnace with DX Cooling OA Rate [cfm] | Split GSW Furnace with DX Cooling OA Rate [cfm] | 56.9945 | 56.9945 | 56.9945 | 56.9945 | 56.9945 | 56.9945 |  |  |  |  | 2021-05-06
NV_MA_Split MN1 Furnace with DX Cooling OA Rate [cfm] | Split MN1 Furnace with DX Cooling OA Rate [cfm] | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824 |  |  |  |  | 2021-05-06
NV_MA_Split MN2 Furnace with DX Cooling OA Rate [cfm] | Split MN2 Furnace with DX Cooling OA Rate [cfm] | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824 |  |  |  |  | 2021-05-06
NV_MA_Split MNE Furnace with DX Cooling OA Rate [cfm] | Split MNE Furnace with DX Cooling OA Rate [cfm] | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824 |  |  |  |  | 2021-05-06
NV_MA_Split MNW Furnace with DX Cooling OA Rate [cfm] | Split MNW Furnace with DX Cooling OA Rate [cfm] | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824 |  |  |  |  | 2021-05-06
NV_MA_Split MS1 Furnace with DX Cooling OA Rate [cfm] | Split MS1 Furnace with DX Cooling OA Rate [cfm] | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824 |  |  |  |  | 2021-05-06
NV_MA_Split MS2 Furnace with DX Cooling OA Rate [cfm] | Split MS2 Furnace with DX Cooling OA Rate [cfm] | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824 |  |  |  |  | 2021-05-06
NV_MA_Split MSE Furnace with DX Cooling OA Rate [cfm] | Split MSE Furnace with DX Cooling OA Rate [cfm] | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824 |  |  |  |  | 2021-05-06
NV_MA_Split MSW Furnace with DX Cooling OA Rate [cfm] | Split MSW Furnace with DX Cooling OA Rate [cfm] | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824 |  |  |  |  | 2021-05-06
NV_MA_Split Office Furnace with DX Cooling OA Rate [cfm] | Split Office Furnace with DX Cooling OA Rate [cfm] | 80.7372 | 80.7372 | 80.7372 | 80.7372 | 80.7372 | 80.7372 |  |  |  |  | 2021-05-06
NV_MA_Split TN1 Furnace with DX Cooling OA Rate [cfm] | Split TN1 Furnace with DX Cooling OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 |  |  |  |  | 2021-05-06
NV_MA_Split TN2 Furnace with DX Cooling OA Rate [cfm] | Split TN2 Furnace with DX Cooling OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 |  |  |  |  | 2021-05-06
NV_MA_Split TNE Furnace with DX Cooling OA Rate [cfm] | Split TNE Furnace with DX Cooling OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 |  |  |  |  | 2021-05-06
NV_MA_Split TNW Furnace with DX Cooling OA Rate [cfm] | Split TNW Furnace with DX Cooling OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 |  |  |  |  | 2021-05-06
NV_MA_Split TS1 Furnace with DX Cooling OA Rate [cfm] | Split TS1 Furnace with DX Cooling OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 |  |  |  |  | 2021-05-06
NV_MA_Split TS2 Furnace with DX Cooling OA Rate [cfm] | Split TS2 Furnace with DX Cooling OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 |  |  |  |  | 2021-05-06
NV_MA_Split TSE Furnace with DX Cooling OA Rate [cfm] | Split TSE Furnace with DX Cooling OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 |  |  |  |  | 2021-05-06
NV_MA_Split TSW Furnace with DX Cooling OA Rate [cfm] | Split TSW Furnace with DX Cooling OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 |  |  |  |  | 2021-05-06
NV_MA_SPLIT GSW HEATING COIL Heating Capacity [kBtu/hr] | SPLIT GSW HEATING COIL Heating Capacity [kBtu/hr] | 4.2447 | 4.1942 | 7.6034 | 7.6632 | 8.1847 | 8.2446 |  |  |  |  | 2021-05-06
NV_MA_SPLIT GNW HEATING COIL Heating Capacity [kBtu/hr] | SPLIT GNW HEATING COIL Heating Capacity [kBtu/hr] | 4.1608 | 4.101 | 7.5545 | 7.6144 | 8.0651 | 8.1252 |  |  |  |  | 2021-05-06
NV_MA_SPLIT OFFICE HEATING COIL Heating Capacity [kBtu/hr] | SPLIT OFFICE HEATING COIL Heating Capacity [kBtu/hr] | 12.5544 | 12.4477 | 19.318 | 19.4426 | 20.234 | 20.3519 |  |  |  |  | 2021-05-06
NV_MA_SPLIT GNE HEATING COIL Heating Capacity [kBtu/hr] | SPLIT GNE HEATING COIL Heating Capacity [kBtu/hr] | 4.1486 | 4.0908 | 7.5545 | 7.6144 | 8.083 | 8.1431 |  |  |  |  | 2021-05-06
NV_MA_SPLIT GN1 HEATING COIL Heating Capacity [kBtu/hr] | SPLIT GN1 HEATING COIL Heating Capacity [kBtu/hr] | 4.0467 | 4.0467 | 5.3626 | 5.4225 | 5.9396 | 5.9998 |  |  |  |  | 2021-05-06
NV_MA_SPLIT GN2 HEATING COIL Heating Capacity [kBtu/hr] | SPLIT GN2 HEATING COIL Heating Capacity [kBtu/hr] | 4.0467 | 4.0467 | 5.3626 | 5.4225 | 5.9401 | 6.0004 |  |  |  |  | 2021-05-06
NV_MA_SPLIT GS1 HEATING COIL Heating Capacity [kBtu/hr] | SPLIT GS1 HEATING COIL Heating Capacity [kBtu/hr] | 4.0467 | 4.0467 | 5.3192 | 5.379 | 5.9506 | 6.0106 |  |  |  |  | 2021-05-06
NV_MA_SPLIT GS2 HEATING COIL Heating Capacity [kBtu/hr] | SPLIT GS2 HEATING COIL Heating Capacity [kBtu/hr] | 4.0467 | 4.0467 | 5.8115 | 5.8735 | 6.4344 | 6.4971 |  |  |  |  | 2021-05-06
NV_MA_SPLIT MSW HEATING COIL Heating Capacity [kBtu/hr] | SPLIT MSW HEATING COIL Heating Capacity [kBtu/hr] | 8.6241 | 8.5081 | 14.1885 | 14.3166 | 14.344 | 14.4735 |  |  |  |  | 2021-05-06
NV_MA_SPLIT MNW HEATING COIL Heating Capacity [kBtu/hr] | SPLIT MNW HEATING COIL Heating Capacity [kBtu/hr] | 8.5855 | 8.4767 | 14.2654 | 14.3934 | 14.2908 | 14.4197 |  |  |  |  | 2021-05-06
NV_MA_SPLIT MSE HEATING COIL Heating Capacity [kBtu/hr] | SPLIT MSE HEATING COIL Heating Capacity [kBtu/hr] | 8.5946 | 8.4835 | 14.1885 | 14.3166 | 14.3866 | 14.5162 |  |  |  |  | 2021-05-06
NV_MA_SPLIT MNE HEATING COIL Heating Capacity [kBtu/hr] | SPLIT MNE HEATING COIL Heating Capacity [kBtu/hr] | 8.556 | 8.4521 | 14.2654 | 14.3934 | 14.3335 | 14.4625 |  |  |  |  | 2021-05-06
NV_MA_SPLIT MN1 HEATING COIL Heating Capacity [kBtu/hr] | SPLIT MN1 HEATING COIL Heating Capacity [kBtu/hr] | 8.0935 | 8.0935 | 9.4638 | 9.5894 | 10.3252 | 10.3252 |  |  |  |  | 2021-05-06
NV_MA_SPLIT MN2 HEATING COIL Heating Capacity [kBtu/hr] | SPLIT MN2 HEATING COIL Heating Capacity [kBtu/hr] | 8.0935 | 8.0935 | 9.4638 | 9.5894 | 10.3252 | 10.3252 |  |  |  |  | 2021-05-06
NV_MA_SPLIT MS1 HEATING COIL Heating Capacity [kBtu/hr] | SPLIT MS1 HEATING COIL Heating Capacity [kBtu/hr] | 8.0935 | 8.0935 | 9.3949 | 9.5204 | 10.3252 | 10.3252 |  |  |  |  | 2021-05-06
NV_MA_SPLIT MS2 HEATING COIL Heating Capacity [kBtu/hr] | SPLIT MS2 HEATING COIL Heating Capacity [kBtu/hr] | 8.0935 | 8.0935 | 9.3949 | 9.5204 | 10.3252 | 10.3252 |  |  |  |  | 2021-05-06
NV_MA_SPLIT TSW HEATING COIL Heating Capacity [kBtu/hr] | SPLIT TSW HEATING COIL Heating Capacity [kBtu/hr] | 6.9497 | 6.892 | 10.3093 | 10.3709 | 10.5099 | 10.5718 |  |  |  |  | 2021-05-06
NV_MA_SPLIT TNW HEATING COIL Heating Capacity [kBtu/hr] | SPLIT TNW HEATING COIL Heating Capacity [kBtu/hr] | 6.9355 | 6.8822 | 10.3555 | 10.4172 | 10.4877 | 10.5497 |  |  |  |  | 2021-05-06
NV_MA_SPLIT TSE HEATING COIL Heating Capacity [kBtu/hr] | SPLIT TSE HEATING COIL Heating Capacity [kBtu/hr] | 6.9343 | 6.8792 | 10.3093 | 10.3709 | 10.5328 | 10.5947 |  |  |  |  | 2021-05-06
NV_MA_SPLIT TNE HEATING COIL Heating Capacity [kBtu/hr] | SPLIT TNE HEATING COIL Heating Capacity [kBtu/hr] | 6.9201 | 6.8694 | 10.3555 | 10.4172 | 10.5106 | 10.5726 |  |  |  |  | 2021-05-06
NV_MA_SPLIT TN1 HEATING COIL Heating Capacity [kBtu/hr] | SPLIT TN1 HEATING COIL Heating Capacity [kBtu/hr] | 5.2101 | 5.1981 | 7.8043 | 7.8659 | 8.1978 | 8.2598 |  |  |  |  | 2021-05-06
NV_MA_SPLIT TN2 HEATING COIL Heating Capacity [kBtu/hr] | SPLIT TN2 HEATING COIL Heating Capacity [kBtu/hr] | 5.2096 | 5.1977 | 7.8043 | 7.8659 | 8.1985 | 8.2605 |  |  |  |  | 2021-05-06
NV_MA_SPLIT TS1 HEATING COIL Heating Capacity [kBtu/hr] | SPLIT TS1 HEATING COIL Heating Capacity [kBtu/hr] | 5.2179 | 5.2013 | 7.751 | 7.8125 | 8.2141 | 8.2759 |  |  |  |  | 2021-05-06
NV_MA_SPLIT TS2 HEATING COIL Heating Capacity [kBtu/hr] | SPLIT TS2 HEATING COIL Heating Capacity [kBtu/hr] | 5.2175 | 5.2009 | 7.751 | 7.8125 | 8.2148 | 8.2766 |  |  |  |  | 2021-05-06
NV_MA_Split_GSW ERV Flag | Split_GSW ERV Flag | No | Yes | No | Yes | No | Yes |  |  |  |  | 2021-05-06
NV_MA_Split_GNW ERV Flag | Split_GNW ERV Flag | No | Yes | No | Yes | No | Yes |  |  |  |  | 2021-05-06
NV_MA_Split_GNE ERV Flag | Split_GNE ERV Flag | No | Yes | No | Yes | No | Yes |  |  |  |  | 2021-05-06
NV_MA_Split_GN1 ERV Flag | Split_GN1 ERV Flag | No | Yes | No | Yes | No | Yes |  |  |  |  | 2021-05-06
NV_MA_Split_GN2 ERV Flag | Split_GN2 ERV Flag | No | Yes | No | Yes | No | Yes |  |  |  |  | 2021-05-06
NV_MA_Split_GS1 ERV Flag | Split_GS1 ERV Flag | No | Yes | No | Yes | No | Yes |  |  |  |  | 2021-05-06
NV_MA_Split_GS2 ERV Flag | Split_GS2 ERV Flag | No | Yes | No | Yes | No | Yes |  |  |  |  | 2021-05-06
NV_MA_Split_MSW ERV Flag | Split_MSW ERV Flag | No | Yes | No | Yes | No | Yes |  |  |  |  | 2021-05-06
NV_MA_Split_MNW ERV Flag | Split_MNW ERV Flag | No | Yes | No | Yes | No | Yes |  |  |  |  | 2021-05-06
NV_MA_Split_MSE ERV Flag | Split_MSE ERV Flag | No | Yes | No | Yes | No | Yes |  |  |  |  | 2021-05-06
NV_MA_Split_MNE ERV Flag | Split_MNE ERV Flag | No | Yes | No | Yes | No | Yes |  |  |  |  | 2021-05-06
NV_MA_Split_MN1 ERV Flag | Split_MN1 ERV Flag | No | Yes | No | Yes | No | Yes |  |  |  |  | 2021-05-06
NV_MA_Split_MN2 ERV Flag | Split_MN2 ERV Flag | No | Yes | No | Yes | No | Yes |  |  |  |  | 2021-05-06
NV_MA_Split_MS1 ERV Flag | Split_MS1 ERV Flag | No | Yes | No | Yes | No | Yes |  |  |  |  | 2021-05-06
NV_MA_Split_MS2 ERV Flag | Split_MS2 ERV Flag | No | Yes | No | Yes | No | Yes |  |  |  |  | 2021-05-06
NV_MA_Split_TSW ERV Flag | Split_TSW ERV Flag | No | No | No | No | No | No |  |  |  |  | 2021-05-06
NV_MA_Split_TNW ERV Flag | Split_TNW ERV Flag | No | No | No | No | No | No |  |  |  |  | 2021-05-06
NV_MA_Split_TSE ERV Flag | Split_TSE ERV Flag | No | Yes | No | Yes | No | Yes |  |  |  |  | 2021-05-06
NV_MA_Split_TNE ERV Flag | Split_TNE ERV Flag | No | Yes | No | Yes | No | Yes |  |  |  |  | 2021-05-06
NV_MA_Split_TN1 ERV Flag | Split_TN1 ERV Flag | No | Yes | No | Yes | No | Yes |  |  |  |  | 2021-05-06
NV_MA_Split_TN2 ERV Flag | Split_TN2 ERV Flag | No | Yes | No | Yes | No | Yes |  |  |  |  | 2021-05-06
NV_MA_Split_TS1 ERV Flag | Split_TS1 ERV Flag | No | Yes | No | Yes | No | Yes |  |  |  |  | 2021-05-06
NV_MA_Split_TS2 ERV Flag | Split_TS2 ERV Flag | No | Yes | No | Yes | No | Yes |  |  |  |  | 2021-05-06
id | item | Zone4A(NY-NewYork-NY) ASHRAE901-state_STD2016 | Zone4A(NY-NewYork-NY) ASHRAE901-state_STD2019 | Zone5A(NY-Albany-NY) ASHRAE901-state_STD2016 | Zone5A(NY-Albany-NY) ASHRAE901-state_STD2019 | Zone6A(NY-Massena-NY) ASHRAE901-state_STD2016 | Zone6A(NY-Massena-NY) ASHRAE901-state_STD2019 |  |  |  |  | 2021-05-06
NY_SO_PSZ-AC:1 Cooling Capacity [ton] | PSZ-AC:1 Cooling Capacity [ton] | 1.8064 | 1.7147 | 1.764 | 1.6724 | 1.7365 | 1.6413 |  |  |  |  | 2021-05-06
NY_SO_PSZ-AC:2 Cooling Capacity [ton] | PSZ-AC:2 Cooling Capacity [ton] | 1.5723 | 1.5112 | 1.5068 | 1.4459 | 1.4903 | 1.413 |  |  |  |  | 2021-05-06
NY_SO_PSZ-AC:3 Cooling Capacity [ton] | PSZ-AC:3 Cooling Capacity [ton] | 1.0937 | 1.0556 | 1.0238 | 0.98688 | 1.0415 | 0.97671 |  |  |  |  | 2021-05-06
NY_SO_PSZ-AC:4 Cooling Capacity [ton] | PSZ-AC:4 Cooling Capacity [ton] | 1.4997 | 1.4318 | 1.4292 | 1.3493 | 1.3819 | 1.2926 |  |  |  |  | 2021-05-06
NY_SO_PSZ-AC:5 Cooling Capacity [ton] | PSZ-AC:5 Cooling Capacity [ton] | 1.2695 | 1.2306 | 1.2455 | 1.2064 | 1.2546 | 1.1897 |  |  |  |  | 2021-05-06
NY_SO_PSZ-AC:1 Supply Flow Rate [cfm] | PSZ-AC:1 Supply Flow Rate [cfm] | 635.664 | 593.2864 | 635.664 | 593.2864 | 635.664 | 593.2864 |  |  |  |  | 2021-05-06
NY_SO_PSZ-AC:2 Supply Flow Rate [cfm] | PSZ-AC:2 Supply Flow Rate [cfm] | 572.0976 | 550.9088 | 550.9088 | 529.72 | 550.9088 | 508.5312 |  |  |  |  | 2021-05-06
NY_SO_PSZ-AC:3 Supply Flow Rate [cfm] | PSZ-AC:3 Supply Flow Rate [cfm] | 444.9648 | 423.776 | 423.776 | 402.5872 | 444.9648 | 402.5872 |  |  |  |  | 2021-05-06
NY_SO_PSZ-AC:4 Supply Flow Rate [cfm] | PSZ-AC:4 Supply Flow Rate [cfm] | 529.72 | 508.5312 | 508.5312 | 487.3424 | 508.5312 | 466.1536 |  |  |  |  | 2021-05-06
NY_SO_PSZ-AC:5 Supply Flow Rate [cfm] | PSZ-AC:5 Supply Flow Rate [cfm] | 508.5312 | 487.3424 | 508.5312 | 487.3424 | 529.72 | 487.3424 |  |  |  |  | 2021-05-06
NY_SO_PSZ-AC:1 OA Rate [cfm] | PSZ-AC:1 OA Rate [cfm] | 136.9178 | 136.9178 | 136.9178 | 136.9178 | 136.9178 | 136.9178 |  |  |  |  | 2021-05-06
NY_SO_PSZ-AC:2 OA Rate [cfm] | PSZ-AC:2 OA Rate [cfm] | 103.7925 | 103.7925 | 103.7925 | 103.7925 | 103.7925 | 103.7925 |  |  |  |  | 2021-05-06
NY_SO_PSZ-AC:3 OA Rate [cfm] | PSZ-AC:3 OA Rate [cfm] | 61.5711 | 61.5711 | 61.5711 | 61.5711 | 61.5711 | 61.5711 |  |  |  |  | 2021-05-06
NY_SO_PSZ-AC:4 OA Rate [cfm] | PSZ-AC:4 OA Rate [cfm] | 103.7925 | 103.7925 | 103.7925 | 103.7925 | 103.7925 | 103.7925 |  |  |  |  | 2021-05-06
NY_SO_PSZ-AC:5 OA Rate [cfm] | PSZ-AC:5 OA Rate [cfm] | 61.5711 | 61.5711 | 61.5711 | 61.5711 | 61.5711 | 61.5711 |  |  |  |  | 2021-05-06
NY_SO_PSZ-AC:1 heating Capacity [kBtu/hr] | PSZ-AC:1 heating Capacity [kBtu/hr] | 13.5199 | 13.5199 | 15.5336 | 15.5336 | 17.4701 | 17.4486 |  |  |  |  | 2021-05-06
NY_SO_PSZ-AC:2 heating Capacity [kBtu/hr] | PSZ-AC:2 heating Capacity [kBtu/hr] | 19.4071 | 19.214 | 20.9891 | 20.7541 | 23.8275 | 23.5392 |  |  |  |  | 2021-05-06
NY_SO_PSZ-AC:3 heating Capacity [kBtu/hr] | PSZ-AC:3 heating Capacity [kBtu/hr] | 11.9544 | 11.8476 | 12.7488 | 12.6189 | 14.3906 | 14.2365 |  |  |  |  | 2021-05-06
NY_SO_PSZ-AC:4 heating Capacity [kBtu/hr] | PSZ-AC:4 heating Capacity [kBtu/hr] | 19.3271 | 19.1604 | 20.8775 | 20.6777 | 23.6327 | 23.3971 |  |  |  |  | 2021-05-06
NY_SO_PSZ-AC:5 heating Capacity [kBtu/hr] | PSZ-AC:5 heating Capacity [kBtu/hr] | 12.0082 | 11.8954 | 12.8031 | 12.6681 | 14.4459 | 14.2866 |  |  |  |  | 2021-05-06
id | item | Zone4A(NY-NewYork-NY) ASHRAE901-state_STD2016 | Zone4A(NY-NewYork-NY) ASHRAE901-state_STD2019 | Zone5A(NY-Albany-NY) ASHRAE901-state_STD2016 | Zone5A(NY-Albany-NY) ASHRAE901-state_STD2019 | Zone6A(NY-Massena-NY) ASHRAE901-state_STD2016 | Zone6A(NY-Massena-NY) ASHRAE901-state_STD2019 |  |  |  |  | 2021-05-06
NY_LO_CAV_BAS Supply Flow Rate [cfm] | CAV_BAS Supply Flow Rate [cfm] | 11611.4624 | 10742.7216 | 11653.84 | 10785.0992 | 11653.84 | 10763.9104 |  |  |  |  | 2021-05-06
NY_LO_VAV_BOT WITH REHEAT Supply Flow Rate [cfm] | VAV_BOT WITH REHEAT Supply Flow Rate [cfm] | 19620.8288 | 18688.5216 | 19557.2624 | 18624.9552 | 19642.0176 | 18561.3888 |  |  |  |  | 2021-05-06
NY_LO_VAV_MID WITH REHEAT Supply Flow Rate [cfm] | VAV_MID WITH REHEAT Supply Flow Rate [cfm] | 182986.4771 | 174129.5587 | 181672.7715 | 172837.0419 | 182541.5123 | 172010.6787 |  |  |  |  | 2021-05-06
NY_LO_VAV_TOP WITH REHEAT Supply Flow Rate [cfm] | VAV_TOP WITH REHEAT Supply Flow Rate [cfm] | 18985.1648 | 18201.1792 | 19112.2976 | 18349.5008 | 19154.6752 | 18137.6128 |  |  |  |  | 2021-05-06
NY_LO_Supply Air Temp. Reset Flag | Supply Air Temp. Reset Flag | Yes | Yes | Yes | Yes | Yes | Yes |  |  |  |  | 2021-05-06
NY_LO_CAV_BAS OA Rate [cfm] | CAV_BAS OA Rate [cfm] | 2542.8255 | 2542.8255 | 2542.8255 | 2542.8255 | 2542.8255 | 2542.8255 |  |  |  |  | 2021-05-06
NY_LO_VAV_BOT WITH REHEAT OA Rate [cfm] | VAV_BOT WITH REHEAT OA Rate [cfm] | 5377.8022 | 4302.174 | 5377.8022 | 4302.174 | 5377.8022 | 4302.174 |  |  |  |  | 2021-05-06
NY_LO_VAV_MID WITH REHEAT OA Rate [cfm] | VAV_MID WITH REHEAT OA Rate [cfm] | 53777.9373 | 43021.7396 | 53777.9373 | 43021.7396 | 53777.9373 | 43021.7396 |  |  |  |  | 2021-05-06
NY_LO_VAV_TOP WITH REHEAT OA Rate [cfm] | VAV_TOP WITH REHEAT OA Rate [cfm] | 5377.8022 | 4302.174 | 5377.8022 | 4302.174 | 5377.8022 | 4302.174 |  |  |  |  | 2021-05-06
NY_LO_AIRLOOP DATACENTER BASEMENT OA Rate [cfm] | AIRLOOP DATACENTER BASEMENT OA Rate [cfm] | 716.9654 | 716.9654 | 716.9654 | 716.9654 | 716.9654 | 716.9654 |  |  |  |  | 2021-05-06
NY_LO_VAV_bot_WITH_REHEAT ERV Flag | VAV_bot_WITH_REHEAT ERV Flag | Yes | Yes | Yes | Yes | Yes | Yes |  |  |  |  | 2021-05-06
NY_LO_VAV_mid_WITH_REHEAT ERV Flag | VAV_mid_WITH_REHEAT ERV Flag | Yes | Yes | Yes | Yes | Yes | Yes |  |  |  |  | 2021-05-06
NY_LO_VAV_top_WITH_REHEAT ERV Flag | VAV_top_WITH_REHEAT ERV Flag | Yes | Yes | Yes | Yes | Yes | Yes |  |  |  |  | 2021-05-06
NY_LO_COOLSYS1 CHILLER1 Capacity [ton] | COOLSYS1 CHILLER1 Capacity [ton] | 402.5147 | 336.332 | 393.3227 | 356.7205 | 390.6177 | 352.6177 |  |  |  |  | 2021-05-06
NY_LO_COOLSYS1 CHILLER2 Capacity [ton] | COOLSYS1 CHILLER2 Capacity [ton] | 402.5147 | 336.332 | 393.3227 | 356.7205 | 390.6177 | 352.6177 |  |  |  |  | 2021-05-06
NY_LO_TOWERWATERSYS COOLTOWER 1 Capacity [ton] | TOWERWATERSYS COOLTOWER 1 Capacity [ton] | 382.0618 | 319.2359 | 373.3323 | 338.5982 | 370.7725 | 334.6995 |  |  |  |  | 2021-05-06
NY_LO_TOWERWATERSYS COOLTOWER 2 Capacity [ton] | TOWERWATERSYS COOLTOWER 2 Capacity [ton] | 382.0618 | 319.2359 | 373.3323 | 338.5982 | 370.7725 | 334.6995 |  |  |  |  | 2021-05-06
NY_LO_HEATSYS1 BOILER Capacity [MMBTU/h] | HEATSYS1 BOILER Capacity [MMBTU/h] | 4228.6442 | 3766.2372 | 4822.1577 | 4250.2619 | 5419.0216 | 4758.0533 |  |  |  |  | 2021-05-06
NY_LO_COOLSYS1 PUMP Flow Rate [gal/min] | COOLSYS1 PUMP Flow Rate [gal/min] | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 2021-05-06
NY_LO_COOLSYS1 CHILLER1 PUMP Flow Rate [gal/min] | COOLSYS1 CHILLER1 PUMP Flow Rate [gal/min] | 634.2253 | 526.8568 | 619.6842 | 561.9098 | 615.3936 | 555.4254 |  |  |  |  | 2021-05-06
NY_LO_COOLSYS1 CHILLER2 PUMP Flow Rate [gal/min] | COOLSYS1 CHILLER2 PUMP Flow Rate [gal/min] | 634.2253 | 526.8568 | 619.6842 | 561.9098 | 615.3936 | 555.4254 |  |  |  |  | 2021-05-06
NY_LO_COOLSYS1 PUMP SECONDARY Flow Rate [gal/min] | COOLSYS1 PUMP SECONDARY Flow Rate [gal/min] | 1268.4491 | 1053.7136 | 1239.3685 | 1123.818 | 1230.7871 | 1110.8509 |  |  |  |  | 2021-05-06
NY_LO_HEATSYS1 PUMP Flow Rate [gal/min] | HEATSYS1 PUMP Flow Rate [gal/min] | 867.9843 | 773.0694 | 989.8115 | 872.4224 | 1112.325 | 976.6525 |  |  |  |  | 2021-05-06
NY_LO_TOWERWATERSYS PUMP Flow Rate [gal/min] | TOWERWATERSYS PUMP Flow Rate [gal/min] | 2220.6303 | 1855.5973 | 2169.9092 | 1967.9761 | 2155.0099 | 1945.4687 |  |  |  |  | 2021-05-06
NY_LO_PLANT CIRC PUMP Flow Rate [gal/min] | PLANT CIRC PUMP Flow Rate [gal/min] | 207.4427 | 206.6137 | 208.4 | 207.5647 | 208.706 | 207.5584 |  |  |  |  | 2021-05-06
NY_LO_COOLSYS1 PUMP SECONDARY Pressure setpoint reset [yes,no] | COOLSYS1 PUMP SECONDARY Pressure setpoint reset [yes,no] | pump_ride_on_curve | pump_ride_on_curve | pump_ride_on_curve | pump_ride_on_curve | pump_ride_on_curve | pump_ride_on_curve |  |  |  |  | 2021-05-06
NY_LO_COOLSYS1 CHILLER1 PUMP Pump Power [hp] | COOLSYS1 CHILLER1 PUMP Pump Power [hp] | 3.4214 | 2.8141 | 3.343 | 3.0013 | 3.3198 | 2.9667 |  |  |  |  | 2021-05-06
NY_LO_COOLSYS1 CHILLER2 PUMP Pump Power [hp] | COOLSYS1 CHILLER2 PUMP Pump Power [hp] | 3.4214 | 2.8141 | 3.343 | 3.0013 | 3.3198 | 2.9667 |  |  |  |  | 2021-05-06
NY_LO_COOLSYS1 PUMP SECONDARY Pump Power [hp] | COOLSYS1 PUMP SECONDARY Pump Power [hp] | 20.5285 | 16.8844 | 20.0579 | 18.0077 | 19.919 | 17.8 |  |  |  |  | 2021-05-06
NY_LO_HEATSYS1 PUMP Pump Power [hp] | HEATSYS1 PUMP Pump Power [hp] | 18.762 | 16.5449 | 21.3954 | 18.6712 | 24.0436 | 20.9019 |  |  |  |  | 2021-05-06
NY_LO_TOWERWATERSYS PUMP Pump Power [hp] | TOWERWATERSYS PUMP Pump Power [hp] | 39.7596 | 32.8932 | 38.8516 | 34.8873 | 38.5844 | 34.486 |  |  |  |  | 2021-05-06
NY_LO_PLANT CIRC PUMP Pump Power [hp] | PLANT CIRC PUMP Pump Power [hp] | 4.4763 | 4.4143 | 4.497 | 4.4346 | 4.5036 | 4.4345 |  |  |  |  | 2021-05-06
NY_LO_Datacenter PLANT CIRC PUMP Pump Power [hp] | Datacenter PLANT CIRC PUMP Pump Power [hp] | 4.4763 | 4.4143 | 4.497 | 4.4346 | 4.5036 | 4.4345 |  |  |  |  | 2021-05-06
NY_LO_ZN_VAV_BOXes_Max_Reheat_Water_Flow_GPM | ZN_VAV_BOXes_Max_Reheat_Water_Flow_GPM | 468.5491 | 451.3242 | 485.4275 | 467.0627 | 513.0147 | 492.9639 |  |  |  |  | 2021-05-06
NY_LO_COOLSYS1 PUMP SECONDARY VSD | COOLSYS1 PUMP SECONDARY VSD | No | No | No | No | No | No |  |  |  |  | 2021-05-06
NY_LO_HEATSYS1 PUMP VSD | HEATSYS1 PUMP VSD | No | No | No | No | No | No |  |  |  |  | 2021-05-06
NY_LO_DATACENTER BASEMENT Cooling Capacity [ton] | DATACENTER BASEMENT Cooling Capacity [ton] | 121.5038 | 121.1433 | 121.7896 | 121.4284 | 121.6621 | 121.2915 |  |  |  |  | 2021-05-06
NY_LO_DATACENTER BOT Cooling Capacity [ton] | DATACENTER BOT Cooling Capacity [ton] | 2.6392 | 2.616 | 2.6717 | 2.6482 | 2.7002 | 2.6599 |  |  |  |  | 2021-05-06
NY_LO_DATACENTER MID Cooling Capacity [ton] | DATACENTER MID Cooling Capacity [ton] | 25.2433 | 25.04 | 25.5918 | 25.3848 | 25.8861 | 25.4952 |  |  |  |  | 2021-05-06
NY_LO_DATACENTER TOP Cooling Capacity [ton] | DATACENTER TOP Cooling Capacity [ton] | 2.5697 | 2.55 | 2.6042 | 2.5841 | 2.6332 | 2.5946 |  |  |  |  | 2021-05-06
id | item | Zone4A(NY-NewYork-NY) ASHRAE901-state_STD2016 | Zone4A(NY-NewYork-NY) ASHRAE901-state_STD2019 | Zone5A(NY-Albany-NY) ASHRAE901-state_STD2016 | Zone5A(NY-Albany-NY) ASHRAE901-state_STD2019 | Zone6A(NY-Massena-NY) ASHRAE901-state_STD2016 | Zone6A(NY-Massena-NY) ASHRAE901-state_STD2019 |  |  |  |  | 2021-05-06
NY_RS_PSZ-AC:1 Cooling Capacity [ton] | PSZ-AC:1 Cooling Capacity [ton] | 10.4496 | 10.1122 | 9.8265 | 9.3896 | 9.5464 | 9.0897 |  |  |  |  | 2021-05-06
NY_RS_PSZ-AC:2 Cooling Capacity [ton] | PSZ-AC:2 Cooling Capacity [ton] | 48.0421 | 46.2727 | 46.6509 | 44.9186 | 46.1881 | 44.3917 |  |  |  |  | 2021-05-06
NY_RS_PSZ-AC:3 Cooling Capacity [ton] | PSZ-AC:3 Cooling Capacity [ton] | 6.3704 | 6.2117 | 6.052 | 5.8918 | 5.8584 | 5.7036 |  |  |  |  | 2021-05-06
NY_RS_PSZ-AC:4 Cooling Capacity [ton] | PSZ-AC:4 Cooling Capacity [ton] | 5.1962 | 5.0405 | 4.8567 | 4.6777 | 4.7396 | 4.5453 |  |  |  |  | 2021-05-06
NY_RS_PSZ-AC:1 Supply Flow Rate [cfm] | PSZ-AC:1 Supply Flow Rate [cfm] | 3983.4944 | 3729.2288 | 3792.7952 | 3496.152 | 3686.8512 | 3369.0192 |  |  |  |  | 2021-05-06
NY_RS_PSZ-AC:2 Supply Flow Rate [cfm] | PSZ-AC:2 Supply Flow Rate [cfm] | 15298.3136 | 14493.1392 | 15065.2368 | 14238.8736 | 14980.4816 | 14175.3072 |  |  |  |  | 2021-05-06
NY_RS_PSZ-AC:3 Supply Flow Rate [cfm] | PSZ-AC:3 Supply Flow Rate [cfm] | 2309.5792 | 2224.824 | 2224.824 | 2140.0688 | 2182.4464 | 2097.6912 |  |  |  |  | 2021-05-06
NY_RS_PSZ-AC:4 Supply Flow Rate [cfm] | PSZ-AC:4 Supply Flow Rate [cfm] | 1758.6704 | 1695.104 | 1673.9152 | 1589.16 | 1652.7264 | 1567.9712 |  |  |  |  | 2021-05-06
NY_RS_PSZ-AC:1 OA Rate [cfm] | PSZ-AC:1 OA Rate [cfm] | 490.669 | 490.669 | 490.669 | 490.669 | 490.669 | 490.669 |  |  |  |  | 2021-05-06
NY_RS_PSZ-AC:2 OA Rate [cfm] | PSZ-AC:2 OA Rate [cfm] | 4005.1282 | 4005.1282 | 4005.1282 | 4005.1282 | 4005.1282 | 4005.1282 |  |  |  |  | 2021-05-06
NY_RS_PSZ-AC:3 OA Rate [cfm] | PSZ-AC:3 OA Rate [cfm] | 377.3937 | 377.3937 | 377.3937 | 377.3937 | 377.3937 | 377.3937 |  |  |  |  | 2021-05-06
NY_RS_PSZ-AC:4 OA Rate [cfm] | PSZ-AC:4 OA Rate [cfm] | 377.3937 | 377.3937 | 377.3937 | 377.3937 | 377.3937 | 377.3937 |  |  |  |  | 2021-05-06
NY_RS_PSZ-AC:1 OA Damper [gravity, motorized] | PSZ-AC:1 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | motorized | motorized |  |  |  |  | 2021-05-06
NY_RS_PSZ-AC:2 OA Damper [gravity, motorized] | PSZ-AC:2 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | motorized | motorized |  |  |  |  | 2021-05-06
NY_RS_PSZ-AC:3 OA Damper [gravity, motorized] | PSZ-AC:3 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | motorized | motorized |  |  |  |  | 2021-05-06
NY_RS_PSZ-AC:4 OA Damper [gravity, motorized] | PSZ-AC:4 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | motorized | motorized |  |  |  |  | 2021-05-06
NY_RS_PSZ-AC:1 Heating Capacity [kBtu/hr] | PSZ-AC:1 Heating Capacity [kBtu/hr] | 177.1602 | 166.5832 | 175.0115 | 162.5932 | 177.4435 | 164.672 |  |  |  |  | 2021-05-06
NY_RS_PSZ-AC:2 Heating Capacity [kBtu/hr] | PSZ-AC:2 Heating Capacity [kBtu/hr] | 799.5648 | 766.0535 | 846.1788 | 810.5853 | 897.4426 | 865.176 |  |  |  |  | 2021-05-06
NY_RS_PSZ-AC:3 Heating Capacity [kBtu/hr] | PSZ-AC:3 Heating Capacity [kBtu/hr] | 108.8975 | 106.1929 | 110.4006 | 107.6787 | 114.5356 | 111.5459 |  |  |  |  | 2021-05-06
NY_RS_PSZ-AC:4 Heating Capacity [kBtu/hr] | PSZ-AC:4 Heating Capacity [kBtu/hr] | 88.8873 | 85.9836 | 89.6277 | 86.3075 | 93.5239 | 89.8558 |  |  |  |  | 2021-05-06
id | item | Zone4A(NY-NewYork-NY) ASHRAE901-state_STD2016 | Zone4A(NY-NewYork-NY) ASHRAE901-state_STD2019 | Zone5A(NY-Albany-NY) ASHRAE901-state_STD2016 | Zone5A(NY-Albany-NY) ASHRAE901-state_STD2019 | Zone6A(NY-Massena-NY) ASHRAE901-state_STD2016 | Zone6A(NY-Massena-NY) ASHRAE901-state_STD2019 |  |  |  |  | 2021-05-06
NY_PS_VAV_POD_1 Cooling Capacity [ton] | VAV_POD_1 Cooling Capacity [ton] | 18.7359 | 18.219 | 18.8198 | 18.2826 | 18.7722 | 18.1525 |  |  |  |  | 2021-05-06
NY_PS_VAV_POD_2 Cooling Capacity [ton] | VAV_POD_2 Cooling Capacity [ton] | 18.519 | 18.1663 | 18.596 | 18.2308 | 18.5933 | 18.104 |  |  |  |  | 2021-05-06
NY_PS_VAV_POD_3 Cooling Capacity [ton] | VAV_POD_3 Cooling Capacity [ton] | 16.9741 | 16.2042 | 17.0829 | 16.2826 | 17.0385 | 16.055 |  |  |  |  | 2021-05-06
NY_PS_VAV_OTHER Cooling Capacity [ton] | VAV_OTHER Cooling Capacity [ton] | 25.786 | 24.281 | 25.943 | 24.3746 | 25.7524 | 23.8402 |  |  |  |  | 2021-05-06
NY_PS_PSZ-AC_1:6 Cooling Capacity [ton] | PSZ-AC_1:6 Cooling Capacity [ton] | 8.1353 | 7.8741 | 8.0228 | 7.7623 | 7.9293 | 7.6506 |  |  |  |  | 2021-05-06
NY_PS_PSZ-AC_2:5 Cooling Capacity [ton] | PSZ-AC_2:5 Cooling Capacity [ton] | 5.2085 | 5.2924 | 5.3011 | 5.2744 | 5.266 | 5.1847 |  |  |  |  | 2021-05-06
NY_PS_PSZ-AC_2:7 Cooling Capacity [ton] | PSZ-AC_2:7 Cooling Capacity [ton] | 10.5074 | 10.5074 | 10.5074 | 10.5074 | 10.5074 | 10.5074 |  |  |  |  | 2021-05-06
NY_PS_VAV_POD_1 Supply Flow Rate [cfm] | VAV_POD_1 Supply Flow Rate [cfm] | 5615.032 | 5466.7104 | 5657.4096 | 5487.8992 | 5636.2208 | 5445.5216 |  |  |  |  | 2021-05-06
NY_PS_VAV_POD_2 Supply Flow Rate [cfm] | VAV_POD_2 Supply Flow Rate [cfm] | 5551.4656 | 5445.5216 | 5572.6544 | 5466.7104 | 5572.6544 | 5424.3328 |  |  |  |  | 2021-05-06
NY_PS_VAV_POD_3 Supply Flow Rate [cfm] | VAV_POD_3 Supply Flow Rate [cfm] | 5085.312 | 4852.2352 | 5127.6896 | 4894.6128 | 5106.5008 | 4809.8576 |  |  |  |  | 2021-05-06
NY_PS_VAV_OTHER Supply Flow Rate [cfm] | VAV_OTHER Supply Flow Rate [cfm] | 7733.912 | 7288.9472 | 7776.2896 | 7310.136 | 7733.912 | 7161.8144 |  |  |  |  | 2021-05-06
NY_PS_PSZ-AC_2:5 Supply Flow Rate [cfm] | PSZ-AC_2:5 Supply Flow Rate [cfm] | 1567.9712 | 1589.16 | 1589.16 | 1589.16 | 1589.16 | 1546.7824 |  |  |  |  | 2021-05-06
NY_PS_PSZ-AC_1:6 Supply Flow Rate [cfm] | PSZ-AC_1:6 Supply Flow Rate [cfm] | 2521.4672 | 2415.5232 | 2542.656 | 2436.712 | 2542.656 | 2415.5232 |  |  |  |  | 2021-05-06
NY_PS_PSZ-AC_2:7 Supply Flow Rate [cfm] | PSZ-AC_2:7 Supply Flow Rate [cfm] | 3157.1312 | 3157.1312 | 3157.1312 | 3157.1312 | 3157.1312 | 3157.1312 |  |  |  |  | 2021-05-06
NY_PS_Supply Air Temp. Reset Flag | Supply Air Temp. Reset Flag | Yes | Yes | Yes | Yes | Yes | Yes |  |  |  |  | 2021-05-06
NY_PS_VAV_POD_1 OA Rate [cfm] | VAV_POD_1 OA Rate [cfm] | 5622.321 | 5467.2189 | 5646.4974 | 5486.31 | 5633.212 | 5447.2803 |  |  |  |  | 2021-05-06
NY_PS_VAV_POD_2 OA Rate [cfm] | VAV_POD_2 OA Rate [cfm] | 5556.6569 | 5451.3909 | 5580.3671 | 5470.7575 | 5578.5237 | 5432.7236 |  |  |  |  | 2021-05-06
NY_PS_VAV_POD_3 OA Rate [cfm] | VAV_POD_3 OA Rate [cfm] | 5093.6604 | 4862.6177 | 5126.3123 | 4886.1585 | 5112.9634 | 4817.8458 |  |  |  |  | 2021-05-06
NY_PS_VAV_OTHER OA Rate [cfm] | VAV_OTHER OA Rate [cfm] | 3736.1787 | 2988.8921 | 3736.1787 | 2988.8921 | 3736.1787 | 2988.8921 |  |  |  |  | 2021-05-06
NY_PS_PSZ-AC_2:5 OA Rate [cfm] | PSZ-AC_2:5 OA Rate [cfm] | 1152.7343 | 1152.7343 | 1152.7343 | 1152.7343 | 1152.7343 | 1152.7343 |  |  |  |  | 2021-05-06
NY_PS_PSZ-AC_1:6 OA Rate [cfm] | PSZ-AC_1:6 OA Rate [cfm] | 539.9118 | 539.9118 | 539.9118 | 539.9118 | 539.9118 | 539.9118 |  |  |  |  | 2021-05-06
NY_PS_PSZ-AC_2:7 OA Rate [cfm] | PSZ-AC_2:7 OA Rate [cfm] | 3153.0841 | 3153.0841 | 3153.0841 | 3153.0841 | 3153.0841 | 3153.0841 |  |  |  |  | 2021-05-06
NY_PS_VAV_POD_1 OA Damper [gravity, motorized] | VAV_POD_1 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | motorized | motorized |  |  |  |  | 2021-05-06
NY_PS_VAV_POD_2 OA Damper [gravity, motorized] | VAV_POD_2 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | motorized | motorized |  |  |  |  | 2021-05-06
NY_PS_VAV_POD_3 OA Damper [gravity, motorized] | VAV_POD_3 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | motorized | motorized |  |  |  |  | 2021-05-06
NY_PS_VAV_OTHER OA Damper [gravity, motorized] | VAV_OTHER OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | motorized | motorized |  |  |  |  | 2021-05-06
NY_PS_PSZ-AC_2:5 OA Damper [gravity, motorized] | PSZ-AC_2:5 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | motorized | motorized |  |  |  |  | 2021-05-06
NY_PS_PSZ-AC_1:6 OA Damper [gravity, motorized] | PSZ-AC_1:6 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | motorized | motorized |  |  |  |  | 2021-05-06
NY_PS_PSZ-AC_2:7 OA Damper [gravity, motorized] | PSZ-AC_2:7 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | motorized | motorized |  |  |  |  | 2021-05-06
NY_PS_VAV_POD_1 (economizer) | VAV_POD_1 (economizer) | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb |  |  |  |  | 2021-05-06
NY_PS_VAV_POD_2 (economizer) | VAV_POD_2 (economizer) | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb |  |  |  |  | 2021-05-06
NY_PS_VAV_POD_3 (economizer) | VAV_POD_3 (economizer) | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb |  |  |  |  | 2021-05-06
NY_PS_VAV_OTHER (economizer) | VAV_OTHER (economizer) | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb |  |  |  |  | 2021-05-06
NY_PS_PSZ-AC_2:5 (economizer) | PSZ-AC_2:5 (economizer) | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb |  |  |  |  | 2021-05-06
NY_PS_PSZ-AC_1:6 (economizer) | PSZ-AC_1:6 (economizer) | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb |  |  |  |  | 2021-05-06
NY_PS_PSZ-AC_2:7 (economizer) | PSZ-AC_2:7 (economizer) | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb |  |  |  |  | 2021-05-06
NY_PS_VAV_Pod_1_ERV Flag | VAV_Pod_1_ERV Flag | Yes | Yes | Yes | Yes | Yes | Yes |  |  |  |  | 2021-05-06
NY_PS_VAV_Pod_2_ERV Flag | VAV_Pod_2_ERV Flag | Yes | Yes | Yes | Yes | Yes | Yes |  |  |  |  | 2021-05-06
NY_PS_VAV_Pod_3_ERV Flag | VAV_Pod_3_ERV Flag | Yes | Yes | Yes | Yes | Yes | Yes |  |  |  |  | 2021-05-06
NY_PS_VAV_OTHER_ERV Flag | VAV_OTHER_ERV Flag | Yes | Yes | Yes | Yes | Yes | Yes |  |  |  |  | 2021-05-06
NY_PS_PSZ_AC_2_5_ERV Flag | PSZ_AC_2_5_ERV Flag | Yes | Yes | Yes | Yes | Yes | Yes |  |  |  |  | 2021-05-06
NY_PS_PSZ_AC_2_7_ERV Flag | PSZ_AC_2_7_ERV Flag | Yes | Yes | Yes | Yes | Yes | Yes |  |  |  |  | 2021-05-06
NY_PS_HEATSYS1 Capacity [MMBTU/h] | HEATSYS1 Capacity [MMBTU/h] | 1.0176 | 0.97622 | 1.1632 | 1.12 | 1.3128 | 1.2624 |  |  |  |  | 2021-05-06
NY_PS_HEATSYS1 Flow Rate [gal/min] | HEATSYS1 Flow Rate [gal/min] | 104.4345 | 100.1915 | 119.3792 | 114.9499 | 134.7301 | 129.5601 |  |  |  |  | 2021-05-06
NY_PS_VAV_POD_1 Fan Power [hp] | VAV_POD_1 Fan Power [hp] | 8.2946 | 8.0658 | 8.3318 | 8.094 | 8.3107 | 8.0364 |  |  |  |  | 2021-05-06
NY_PS_VAV_POD_2 Fan Power [hp] | VAV_POD_2 Fan Power [hp] | 8.1986 | 8.0424 | 8.2327 | 8.071 | 8.2315 | 8.0149 |  |  |  |  | 2021-05-06
NY_PS_VAV_POD_3 Fan Power [hp] | VAV_POD_3 Fan Power [hp] | 7.5147 | 7.1738 | 7.5628 | 7.2085 | 7.5432 | 7.1078 |  |  |  |  | 2021-05-06
NY_PS_VAV_OTHER Fan Power [hp] | VAV_OTHER Fan Power [hp] | 11.3293 | 10.6681 | 11.3983 | 10.7092 | 11.3146 | 10.4744 |  |  |  |  | 2021-05-06
NY_PS_HEATSYS1 Pump Power [hp] | HEATSYS1 Pump Power [hp] | 2.2574 | 2.1443 | 2.5804 | 2.4601 | 2.9123 | 2.7728 |  |  |  |  | 2021-05-06
NY_PS_PSZ-AC_1:6 Heating Capacity [kBtu/hr] | PSZ-AC_1:6 Heating Capacity [kBtu/hr] | 207.8693 | 199.3028 | 215.4467 | 206.8729 | 222.94 | 213.6814 |  |  |  |  | 2021-05-06
NY_PS_PSZ-AC_2:5 Heating Capacity [kBtu/hr] | PSZ-AC_2:5 Heating Capacity [kBtu/hr] | 129.009 | 129.9401 | 146.8392 | 146.5456 | 162.6113 | 161.7142 |  |  |  |  | 2021-05-06
NY_PS_PSZ-AC_2:7 Heating Capacity [kBtu/hr] | PSZ-AC_2:7 Heating Capacity [kBtu/hr] | 311.351 | 311.351 | 357.7238 | 357.7238 | 401.824 | 401.824 |  |  |  |  | 2021-05-06
NY_PS_ZN_VAV_BOXes_Max_Reheat_Water_Flow_GPM | ZN_VAV_BOXes_Max_Reheat_Water_Flow_GPM | 70.5975 | 67.6844 | 74.0638 | 71.4771 | 79.3049 | 76.9038 |  |  |  |  | 2021-05-06
id | item | Zone4A(NY-NewYork-NY) ASHRAE901-state_STD2016 | Zone4A(NY-NewYork-NY) ASHRAE901-state_STD2019 | Zone5A(NY-Albany-NY) ASHRAE901-state_STD2016 | Zone5A(NY-Albany-NY) ASHRAE901-state_STD2019 | Zone6A(NY-Massena-NY) ASHRAE901-state_STD2016 | Zone6A(NY-Massena-NY) ASHRAE901-state_STD2019 |  |  |  |  | 2021-05-06
NY_SH_SAC_FRONTOFFICE Cooling Capacity [ton] | SAC_FRONTOFFICE Cooling Capacity [ton] | 2.2647 | 2.1507 | 2.1772 | 2.0709 | 2.1297 | 2.0197 |  |  |  |  | 2021-05-06
NY_SH_SAC_FRONTLOUNGE Cooling Capacity [ton] | SAC_FRONTLOUNGE Cooling Capacity [ton] | 6.0281 | 5.7245 | 5.9387 | 5.6346 | 5.8704 | 5.5588 |  |  |  |  | 2021-05-06
NY_SH_SAC_MEETINGROOM Cooling Capacity [ton] | SAC_MEETINGROOM Cooling Capacity [ton] | 2.8412 | 2.7723 | 2.8317 | 2.75 | 2.8123 | 2.7209 |  |  |  |  | 2021-05-06
NY_SH_SAC_EXC_EMPLGE_RESTRM Cooling Capacity [ton] | SAC_EXC_EMPLGE_RESTRM Cooling Capacity [ton] | 5.8181 | 5.7778 | 5.752 | 5.7113 | 5.6665 | 5.621 |  |  |  |  | 2021-05-06
NY_SH_SAC_FO_ADDAQ SUPPLY FAN Supply Flow Rate [cfm] | SAC_FO_ADDAQ SUPPLY FAN Supply Flow Rate [cfm] | 762.7968 | 720.4192 | 741.608 | 699.2304 | 741.608 | 678.0416 |  |  |  |  | 2021-05-06
NY_SH_SAC_FL_ADDAQ SUPPLY FAN Supply Flow Rate [cfm] | SAC_FL_ADDAQ SUPPLY FAN Supply Flow Rate [cfm] | 1801.048 | 1716.2928 | 1779.8592 | 1695.104 | 1758.6704 | 1673.9152 |  |  |  |  | 2021-05-06
NY_SH_SAC_MR_ADDAQ SUPPLY FAN Supply Flow Rate [cfm] | SAC_MR_ADDAQ SUPPLY FAN Supply Flow Rate [cfm] | 847.552 | 826.3632 | 847.552 | 826.3632 | 847.552 | 826.3632 |  |  |  |  | 2021-05-06
NY_SH_SAC_EXC_ADDAQ SUPPLY FAN Supply Flow Rate [cfm] | SAC_EXC_ADDAQ SUPPLY FAN Supply Flow Rate [cfm] | 2161.2576 | 2140.0688 | 2182.4464 | 2161.2576 | 2161.2576 | 2140.0688 |  |  |  |  | 2021-05-06
NY_SH_SAC_Exc_EmpLge_RestRm OA Rate [cfm] | SAC_Exc_EmpLge_RestRm OA Rate [cfm] | 199.9928 | 199.9928 | 199.9928 | 199.9928 | 199.9928 | 199.9928 |  |  |  |  | 2021-05-06
NY_SH_SAC_FrontLounge OA Rate [cfm] | SAC_FrontLounge OA Rate [cfm] | 500.0133 | 500.0133 | 500.0133 | 500.0133 | 500.0133 | 500.0133 |  |  |  |  | 2021-05-06
NY_SH_SAC_FrontOffice OA Rate [cfm] | SAC_FrontOffice OA Rate [cfm] | 119.2938 | 119.2938 | 119.2938 | 119.2938 | 119.2938 | 119.2938 |  |  |  |  | 2021-05-06
NY_SH_SAC_MeetingRoom OA Rate [cfm] | SAC_MeetingRoom OA Rate [cfm] | 267.7629 | 267.7629 | 267.7629 | 267.7629 | 267.7629 | 267.7629 |  |  |  |  | 2021-05-06
NY_SH_SAC_FrontLounge OA Damper [gravity, motorized] | SAC_FrontLounge OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | motorized | motorized |  |  |  |  | 2021-05-06
NY_SH_SAC_FrontOffice (economizer) | SAC_FrontOffice (economizer) | No | No | No | No | No | No |  |  |  |  | 2021-05-06
NY_SH_SAC_FrontLounge (economizer) | SAC_FrontLounge (economizer) | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb |  |  |  |  | 2021-05-06
NY_SH_SAC_MeetingRoom (economizer) | SAC_MeetingRoom (economizer) | No | No | No | No | No | No |  |  |  |  | 2021-05-06
NY_SH_SAC_Exc_EmpLge_RestRm (economizer) | SAC_Exc_EmpLge_RestRm (economizer) | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb |  |  |  |  | 2021-05-06
NY_SH_SAC_FRONTOFFICE Heating Capacity [kBtu/hr] | SAC_FRONTOFFICE Heating Capacity [kBtu/hr] | 35.5725 | 33.8488 | 36.4161 | 34.6947 | 37.7406 | 35.9538 |  |  |  |  | 2021-05-06
NY_SH_SAC_FRONTLOUNGE Heating Capacity [kBtu/hr] | SAC_FRONTLOUNGE Heating Capacity [kBtu/hr] | 97.527 | 94.176 | 103.4541 | 100.1284 | 109.8567 | 106.3893 |  |  |  |  | 2021-05-06
NY_SH_SAC_MEETINGROOM Heating Capacity [kBtu/hr] | SAC_MEETINGROOM Heating Capacity [kBtu/hr] | 47.9553 | 47.1949 | 51.588 | 50.6951 | 55.169 | 54.1671 |  |  |  |  | 2021-05-06
NY_SH_SAC_EXC_EMPLGE_RESTRM Heating Capacity [kBtu/hr] | SAC_EXC_EMPLGE_RESTRM Heating Capacity [kBtu/hr] | 91.7409 | 91.0924 | 94.6976 | 94.0443 | 97.3545 | 96.6025 |  |  |  |  | 2021-05-06
id | item | Zone4A(NY-NewYork-NY) ASHRAE901-state_STD2016 | Zone4A(NY-NewYork-NY) ASHRAE901-state_STD2019 | Zone5A(NY-Albany-NY) ASHRAE901-state_STD2016 | Zone5A(NY-Albany-NY) ASHRAE901-state_STD2019 | Zone6A(NY-Massena-NY) ASHRAE901-state_STD2016 | Zone6A(NY-Massena-NY) ASHRAE901-state_STD2019 |  |  |  |  | 2021-05-06
NY_MA_SPLIT GSW COOLING COIL Cooling Capacity [ton] | SPLIT GSW COOLING COIL Cooling Capacity [ton] | 0.83701 | 0.82335 | 0.78261 | 0.76857 | 0.78678 | 0.75698 |  |  |  |  | 2021-05-06
NY_MA_SPLIT GNW COOLING COIL Cooling Capacity [ton] | SPLIT GNW COOLING COIL Cooling Capacity [ton] | 0.79979 | 0.7866 | 0.73923 | 0.72583 | 0.73427 | 0.70754 |  |  |  |  | 2021-05-06
NY_MA_SPLIT OFFICE COOLING COIL Cooling Capacity [ton] | SPLIT OFFICE COOLING COIL Cooling Capacity [ton] | 1.6547 | 1.5255 | 1.595 | 1.4605 | 1.6649 | 1.5167 |  |  |  |  | 2021-05-06
NY_MA_SPLIT GNE COOLING COIL Cooling Capacity [ton] | SPLIT GNE COOLING COIL Cooling Capacity [ton] | 0.70352 | 0.69193 | 0.63578 | 0.62411 | 0.62582 | 0.60411 |  |  |  |  | 2021-05-06
NY_MA_SPLIT GN1 COOLING COIL Cooling Capacity [ton] | SPLIT GN1 COOLING COIL Cooling Capacity [ton] | 0.60246 | 0.59323 | 0.54425 | 0.53522 | 0.52821 | 0.51416 |  |  |  |  | 2021-05-06
NY_MA_SPLIT GN2 COOLING COIL Cooling Capacity [ton] | SPLIT GN2 COOLING COIL Cooling Capacity [ton] | 0.6006 | 0.59142 | 0.54211 | 0.53313 | 0.52592 | 0.51204 |  |  |  |  | 2021-05-06
NY_MA_SPLIT GS1 COOLING COIL Cooling Capacity [ton] | SPLIT GS1 COOLING COIL Cooling Capacity [ton] | 0.64157 | 0.63145 | 0.59503 | 0.5847 | 0.58999 | 0.57209 |  |  |  |  | 2021-05-06
NY_MA_SPLIT GS2 COOLING COIL Cooling Capacity [ton] | SPLIT GS2 COOLING COIL Cooling Capacity [ton] | 0.6741 | 0.6595 | 0.62993 | 0.61488 | 0.62496 | 0.60223 |  |  |  |  | 2021-05-06
NY_MA_SPLIT MSW COOLING COIL Cooling Capacity [ton] | SPLIT MSW COOLING COIL Cooling Capacity [ton] | 2.0117 | 1.9811 | 1.9288 | 1.8975 | 1.9446 | 1.8692 |  |  |  |  | 2021-05-06
NY_MA_SPLIT MNW COOLING COIL Cooling Capacity [ton] | SPLIT MNW COOLING COIL Cooling Capacity [ton] | 1.9394 | 1.9102 | 1.8454 | 1.8156 | 1.8414 | 1.7767 |  |  |  |  | 2021-05-06
NY_MA_SPLIT MSE COOLING COIL Cooling Capacity [ton] | SPLIT MSE COOLING COIL Cooling Capacity [ton] | 1.768 | 1.7423 | 1.6776 | 1.6491 | 1.7044 | 1.6407 |  |  |  |  | 2021-05-06
NY_MA_SPLIT MNE COOLING COIL Cooling Capacity [ton] | SPLIT MNE COOLING COIL Cooling Capacity [ton] | 1.6288 | 1.5973 | 1.4763 | 1.4429 | 1.4785 | 1.4112 |  |  |  |  | 2021-05-06
NY_MA_SPLIT MN1 COOLING COIL Cooling Capacity [ton] | SPLIT MN1 COOLING COIL Cooling Capacity [ton] | 1.344 | 1.3263 | 1.2384 | 1.2211 | 1.208 | 1.1803 |  |  |  |  | 2021-05-06
NY_MA_SPLIT MN2 COOLING COIL Cooling Capacity [ton] | SPLIT MN2 COOLING COIL Cooling Capacity [ton] | 1.3388 | 1.3212 | 1.2325 | 1.2154 | 1.2016 | 1.1743 |  |  |  |  | 2021-05-06
NY_MA_SPLIT MS1 COOLING COIL Cooling Capacity [ton] | SPLIT MS1 COOLING COIL Cooling Capacity [ton] | 1.4129 | 1.3938 | 1.3299 | 1.3107 | 1.3177 | 1.2838 |  |  |  |  | 2021-05-06
NY_MA_SPLIT MS2 COOLING COIL Cooling Capacity [ton] | SPLIT MS2 COOLING COIL Cooling Capacity [ton] | 1.4076 | 1.3887 | 1.324 | 1.305 | 1.3116 | 1.2781 |  |  |  |  | 2021-05-06
NY_MA_SPLIT TSW COOLING COIL Cooling Capacity [ton] | SPLIT TSW COOLING COIL Cooling Capacity [ton] | 1.2504 | 1.2336 | 1.2059 | 1.1888 | 1.207 | 1.1667 |  |  |  |  | 2021-05-06
NY_MA_SPLIT TNW COOLING COIL Cooling Capacity [ton] | SPLIT TNW COOLING COIL Cooling Capacity [ton] | 1.1996 | 1.1836 | 1.1493 | 1.133 | 1.1426 | 1.1057 |  |  |  |  | 2021-05-06
NY_MA_SPLIT TSE COOLING COIL Cooling Capacity [ton] | SPLIT TSE COOLING COIL Cooling Capacity [ton] | 1.1294 | 1.1151 | 1.074 | 1.0604 | 1.0861 | 1.05 |  |  |  |  | 2021-05-06
NY_MA_SPLIT TNE COOLING COIL Cooling Capacity [ton] | SPLIT TNE COOLING COIL Cooling Capacity [ton] | 1.0473 | 1.0348 | 0.98297 | 0.97049 | 0.96455 | 0.93968 |  |  |  |  | 2021-05-06
NY_MA_SPLIT TN1 COOLING COIL Cooling Capacity [ton] | SPLIT TN1 COOLING COIL Cooling Capacity [ton] | 0.85357 | 0.82411 | 0.78125 | 0.77053 | 0.76179 | 0.7468 |  |  |  |  | 2021-05-06
NY_MA_SPLIT TN2 COOLING COIL Cooling Capacity [ton] | SPLIT TN2 COOLING COIL Cooling Capacity [ton] | 0.85496 | 0.84524 | 0.81024 | 0.80049 | 0.78909 | 0.77275 |  |  |  |  | 2021-05-06
NY_MA_SPLIT TS1 COOLING COIL Cooling Capacity [ton] | SPLIT TS1 COOLING COIL Cooling Capacity [ton] | 0.93217 | 0.92112 | 0.89704 | 0.88535 | 0.90058 | 0.87454 |  |  |  |  | 2021-05-06
NY_MA_SPLIT TS2 COOLING COIL Cooling Capacity [ton] | SPLIT TS2 COOLING COIL Cooling Capacity [ton] | 0.93434 | 0.9232 | 0.89974 | 0.88789 | 0.90293 | 0.8778 |  |  |  |  | 2021-05-06
NY_MA_Split GN1 Furnace with DX Cooling OA Rate [cfm] | Split GN1 Furnace with DX Cooling OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 |  |  |  |  | 2021-05-06
NY_MA_Split GN2 Furnace with DX Cooling OA Rate [cfm] | Split GN2 Furnace with DX Cooling OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 |  |  |  |  | 2021-05-06
NY_MA_Split GNE Furnace with DX Cooling OA Rate [cfm] | Split GNE Furnace with DX Cooling OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 |  |  |  |  | 2021-05-06
NY_MA_Split GNW Furnace with DX Cooling OA Rate [cfm] | Split GNW Furnace with DX Cooling OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 |  |  |  |  | 2021-05-06
NY_MA_Split GS1 Furnace with DX Cooling OA Rate [cfm] | Split GS1 Furnace with DX Cooling OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 |  |  |  |  | 2021-05-06
NY_MA_Split GS2 Furnace with DX Cooling OA Rate [cfm] | Split GS2 Furnace with DX Cooling OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 |  |  |  |  | 2021-05-06
NY_MA_Split GSW Furnace with DX Cooling OA Rate [cfm] | Split GSW Furnace with DX Cooling OA Rate [cfm] | 56.9945 | 56.9945 | 56.9945 | 56.9945 | 56.9945 | 56.9945 |  |  |  |  | 2021-05-06
NY_MA_Split MN1 Furnace with DX Cooling OA Rate [cfm] | Split MN1 Furnace with DX Cooling OA Rate [cfm] | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824 |  |  |  |  | 2021-05-06
NY_MA_Split MN2 Furnace with DX Cooling OA Rate [cfm] | Split MN2 Furnace with DX Cooling OA Rate [cfm] | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824 |  |  |  |  | 2021-05-06
NY_MA_Split MNE Furnace with DX Cooling OA Rate [cfm] | Split MNE Furnace with DX Cooling OA Rate [cfm] | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824 |  |  |  |  | 2021-05-06
NY_MA_Split MNW Furnace with DX Cooling OA Rate [cfm] | Split MNW Furnace with DX Cooling OA Rate [cfm] | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824 |  |  |  |  | 2021-05-06
NY_MA_Split MS1 Furnace with DX Cooling OA Rate [cfm] | Split MS1 Furnace with DX Cooling OA Rate [cfm] | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824 |  |  |  |  | 2021-05-06
NY_MA_Split MS2 Furnace with DX Cooling OA Rate [cfm] | Split MS2 Furnace with DX Cooling OA Rate [cfm] | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824 |  |  |  |  | 2021-05-06
NY_MA_Split MSE Furnace with DX Cooling OA Rate [cfm] | Split MSE Furnace with DX Cooling OA Rate [cfm] | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824 |  |  |  |  | 2021-05-06
NY_MA_Split MSW Furnace with DX Cooling OA Rate [cfm] | Split MSW Furnace with DX Cooling OA Rate [cfm] | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824 |  |  |  |  | 2021-05-06
NY_MA_Split Office Furnace with DX Cooling OA Rate [cfm] | Split Office Furnace with DX Cooling OA Rate [cfm] | 80.7372 | 80.7372 | 80.7372 | 80.7372 | 80.7372 | 80.7372 |  |  |  |  | 2021-05-06
NY_MA_Split TN1 Furnace with DX Cooling OA Rate [cfm] | Split TN1 Furnace with DX Cooling OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 |  |  |  |  | 2021-05-06
NY_MA_Split TN2 Furnace with DX Cooling OA Rate [cfm] | Split TN2 Furnace with DX Cooling OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 |  |  |  |  | 2021-05-06
NY_MA_Split TNE Furnace with DX Cooling OA Rate [cfm] | Split TNE Furnace with DX Cooling OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 |  |  |  |  | 2021-05-06
NY_MA_Split TNW Furnace with DX Cooling OA Rate [cfm] | Split TNW Furnace with DX Cooling OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 |  |  |  |  | 2021-05-06
NY_MA_Split TS1 Furnace with DX Cooling OA Rate [cfm] | Split TS1 Furnace with DX Cooling OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 |  |  |  |  | 2021-05-06
NY_MA_Split TS2 Furnace with DX Cooling OA Rate [cfm] | Split TS2 Furnace with DX Cooling OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 |  |  |  |  | 2021-05-06
NY_MA_Split TSE Furnace with DX Cooling OA Rate [cfm] | Split TSE Furnace with DX Cooling OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 |  |  |  |  | 2021-05-06
NY_MA_Split TSW Furnace with DX Cooling OA Rate [cfm] | Split TSW Furnace with DX Cooling OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 |  |  |  |  | 2021-05-06
NY_MA_SPLIT GSW HEATING COIL Heating Capacity [kBtu/hr] | SPLIT GSW HEATING COIL Heating Capacity [kBtu/hr] | 9.5475 | 9.6059 | 10.4729 | 10.532 | 11.8718 | 11.9313 |  |  |  |  | 2021-05-06
NY_MA_SPLIT GNW HEATING COIL Heating Capacity [kBtu/hr] | SPLIT GNW HEATING COIL Heating Capacity [kBtu/hr] | 9.4886 | 9.5469 | 10.3894 | 10.4485 | 11.729 | 11.7886 |  |  |  |  | 2021-05-06
NY_MA_SPLIT OFFICE HEATING COIL Heating Capacity [kBtu/hr] | SPLIT OFFICE HEATING COIL Heating Capacity [kBtu/hr] | 22.0183 | 22.0991 | 23.7972 | 23.8787 | 25.6155 | 25.6989 |  |  |  |  | 2021-05-06
NY_MA_SPLIT GNE HEATING COIL Heating Capacity [kBtu/hr] | SPLIT GNE HEATING COIL Heating Capacity [kBtu/hr] | 9.4671 | 9.5255 | 10.3664 | 10.4255 | 11.7055 | 11.7652 |  |  |  |  | 2021-05-06
NY_MA_SPLIT GN1 HEATING COIL Heating Capacity [kBtu/hr] | SPLIT GN1 HEATING COIL Heating Capacity [kBtu/hr] | 6.7588 | 6.8172 | 7.7966 | 7.8558 | 9.0318 | 9.0915 |  |  |  |  | 2021-05-06
NY_MA_SPLIT GN2 HEATING COIL Heating Capacity [kBtu/hr] | SPLIT GN2 HEATING COIL Heating Capacity [kBtu/hr] | 6.7582 | 6.8166 | 7.796 | 7.8552 | 9.0312 | 9.0909 |  |  |  |  | 2021-05-06
NY_MA_SPLIT GS1 HEATING COIL Heating Capacity [kBtu/hr] | SPLIT GS1 HEATING COIL Heating Capacity [kBtu/hr] | 6.7098 | 6.7681 | 7.7423 | 7.8013 | 9.0098 | 9.0693 |  |  |  |  | 2021-05-06
NY_MA_SPLIT GS2 HEATING COIL Heating Capacity [kBtu/hr] | SPLIT GS2 HEATING COIL Heating Capacity [kBtu/hr] | 7.207 | 7.2661 | 8.2535 | 8.3134 | 9.5334 | 9.5939 |  |  |  |  | 2021-05-06
NY_MA_SPLIT MSW HEATING COIL Heating Capacity [kBtu/hr] | SPLIT MSW HEATING COIL Heating Capacity [kBtu/hr] | 18.452 | 18.5812 | 17.9423 | 18.0707 | 19.9102 | 20.0386 |  |  |  |  | 2021-05-06
NY_MA_SPLIT MNW HEATING COIL Heating Capacity [kBtu/hr] | SPLIT MNW HEATING COIL Heating Capacity [kBtu/hr] | 18.5383 | 18.6674 | 18.036 | 18.1644 | 19.9232 | 20.0516 |  |  |  |  | 2021-05-06
NY_MA_SPLIT MSE HEATING COIL Heating Capacity [kBtu/hr] | SPLIT MSE HEATING COIL Heating Capacity [kBtu/hr] | 18.4017 | 18.531 | 17.8878 | 18.0162 | 19.8546 | 19.983 |  |  |  |  | 2021-05-06
NY_MA_SPLIT MNE HEATING COIL Heating Capacity [kBtu/hr] | SPLIT MNE HEATING COIL Heating Capacity [kBtu/hr] | 18.488 | 18.6171 | 17.9813 | 18.1098 | 19.8675 | 19.996 |  |  |  |  | 2021-05-06
NY_MA_SPLIT MN1 HEATING COIL Heating Capacity [kBtu/hr] | SPLIT MN1 HEATING COIL Heating Capacity [kBtu/hr] | 12.4145 | 12.5385 | 12.7795 | 12.9059 | 14.5411 | 14.6688 |  |  |  |  | 2021-05-06
NY_MA_SPLIT MN2 HEATING COIL Heating Capacity [kBtu/hr] | SPLIT MN2 HEATING COIL Heating Capacity [kBtu/hr] | 12.4131 | 12.5371 | 12.778 | 12.9045 | 14.5397 | 14.6674 |  |  |  |  | 2021-05-06
NY_MA_SPLIT MS1 HEATING COIL Heating Capacity [kBtu/hr] | SPLIT MS1 HEATING COIL Heating Capacity [kBtu/hr] | 12.3363 | 12.4602 | 12.6953 | 12.8217 | 14.5384 | 14.6661 |  |  |  |  | 2021-05-06
NY_MA_SPLIT MS2 HEATING COIL Heating Capacity [kBtu/hr] | SPLIT MS2 HEATING COIL Heating Capacity [kBtu/hr] | 12.335 | 12.4588 | 12.6938 | 12.8203 | 14.537 | 14.6647 |  |  |  |  | 2021-05-06
NY_MA_SPLIT TSW HEATING COIL Heating Capacity [kBtu/hr] | SPLIT TSW HEATING COIL Heating Capacity [kBtu/hr] | 12.8829 | 12.9443 | 12.6567 | 12.7187 | 14.0593 | 14.1216 |  |  |  |  | 2021-05-06
NY_MA_SPLIT TNW HEATING COIL Heating Capacity [kBtu/hr] | SPLIT TNW HEATING COIL Heating Capacity [kBtu/hr] | 12.9334 | 12.9949 | 12.7132 | 12.7752 | 14.0736 | 14.136 |  |  |  |  | 2021-05-06
NY_MA_SPLIT TSE HEATING COIL Heating Capacity [kBtu/hr] | SPLIT TSE HEATING COIL Heating Capacity [kBtu/hr] | 12.8568 | 12.9182 | 12.6276 | 12.6896 | 14.0294 | 14.0917 |  |  |  |  | 2021-05-06
NY_MA_SPLIT TNE HEATING COIL Heating Capacity [kBtu/hr] | SPLIT TNE HEATING COIL Heating Capacity [kBtu/hr] | 12.9074 | 12.9688 | 12.6841 | 12.7461 | 14.0436 | 14.106 |  |  |  |  | 2021-05-06
NY_MA_SPLIT TN1 HEATING COIL Heating Capacity [kBtu/hr] | SPLIT TN1 HEATING COIL Heating Capacity [kBtu/hr] | 9.4772 | 9.5384 | 9.932 | 9.9939 | 11.2713 | 11.3336 |  |  |  |  | 2021-05-06
NY_MA_SPLIT TN2 HEATING COIL Heating Capacity [kBtu/hr] | SPLIT TN2 HEATING COIL Heating Capacity [kBtu/hr] | 9.4764 | 9.5377 | 9.9312 | 9.9931 | 11.2705 | 11.3327 |  |  |  |  | 2021-05-06
NY_MA_SPLIT TS1 HEATING COIL Heating Capacity [kBtu/hr] | SPLIT TS1 HEATING COIL Heating Capacity [kBtu/hr] | 9.4193 | 9.4804 | 9.8689 | 9.9307 | 11.2512 | 11.3134 |  |  |  |  | 2021-05-06
NY_MA_SPLIT TS2 HEATING COIL Heating Capacity [kBtu/hr] | SPLIT TS2 HEATING COIL Heating Capacity [kBtu/hr] | 9.4185 | 9.4797 | 9.8681 | 9.9299 | 11.2504 | 11.3126 |  |  |  |  | 2021-05-06
NY_MA_Split_GSW ERV Flag | Split_GSW ERV Flag | Yes | Yes | Yes | Yes | Yes | Yes |  |  |  |  | 2021-05-06
NY_MA_Split_GNW ERV Flag | Split_GNW ERV Flag | Yes | Yes | Yes | Yes | Yes | Yes |  |  |  |  | 2021-05-06
NY_MA_Split_GNE ERV Flag | Split_GNE ERV Flag | Yes | Yes | Yes | Yes | Yes | Yes |  |  |  |  | 2021-05-06
NY_MA_Split_GN1 ERV Flag | Split_GN1 ERV Flag | Yes | Yes | Yes | Yes | Yes | Yes |  |  |  |  | 2021-05-06
NY_MA_Split_GN2 ERV Flag | Split_GN2 ERV Flag | Yes | Yes | Yes | Yes | Yes | Yes |  |  |  |  | 2021-05-06
NY_MA_Split_GS1 ERV Flag | Split_GS1 ERV Flag | Yes | Yes | Yes | Yes | Yes | Yes |  |  |  |  | 2021-05-06
NY_MA_Split_GS2 ERV Flag | Split_GS2 ERV Flag | Yes | Yes | Yes | Yes | Yes | Yes |  |  |  |  | 2021-05-06
NY_MA_Split_MSW ERV Flag | Split_MSW ERV Flag | Yes | Yes | Yes | Yes | Yes | Yes |  |  |  |  | 2021-05-06
NY_MA_Split_MNW ERV Flag | Split_MNW ERV Flag | Yes | Yes | Yes | Yes | Yes | Yes |  |  |  |  | 2021-05-06
NY_MA_Split_MSE ERV Flag | Split_MSE ERV Flag | Yes | Yes | Yes | Yes | Yes | Yes |  |  |  |  | 2021-05-06
NY_MA_Split_MNE ERV Flag | Split_MNE ERV Flag | Yes | Yes | Yes | Yes | Yes | Yes |  |  |  |  | 2021-05-06
NY_MA_Split_MN1 ERV Flag | Split_MN1 ERV Flag | Yes | Yes | Yes | Yes | Yes | Yes |  |  |  |  | 2021-05-06
NY_MA_Split_MN2 ERV Flag | Split_MN2 ERV Flag | Yes | Yes | Yes | Yes | Yes | Yes |  |  |  |  | 2021-05-06
NY_MA_Split_MS1 ERV Flag | Split_MS1 ERV Flag | Yes | Yes | Yes | Yes | Yes | Yes |  |  |  |  | 2021-05-06
NY_MA_Split_MS2 ERV Flag | Split_MS2 ERV Flag | Yes | Yes | Yes | Yes | Yes | Yes |  |  |  |  | 2021-05-06
NY_MA_Split_TSW ERV Flag | Split_TSW ERV Flag | Yes | Yes | Yes | Yes | Yes | Yes |  |  |  |  | 2021-05-06
NY_MA_Split_TNW ERV Flag | Split_TNW ERV Flag | Yes | Yes | Yes | Yes | Yes | Yes |  |  |  |  | 2021-05-06
NY_MA_Split_TSE ERV Flag | Split_TSE ERV Flag | Yes | Yes | Yes | Yes | Yes | Yes |  |  |  |  | 2021-05-06
NY_MA_Split_TNE ERV Flag | Split_TNE ERV Flag | Yes | Yes | Yes | Yes | Yes | Yes |  |  |  |  | 2021-05-06
NY_MA_Split_TN1 ERV Flag | Split_TN1 ERV Flag | Yes | Yes | Yes | Yes | Yes | Yes |  |  |  |  | 2021-05-06
NY_MA_Split_TN2 ERV Flag | Split_TN2 ERV Flag | Yes | Yes | Yes | Yes | Yes | Yes |  |  |  |  | 2021-05-06
NY_MA_Split_TS1 ERV Flag | Split_TS1 ERV Flag | Yes | Yes | Yes | Yes | Yes | Yes |  |  |  |  | 2021-05-06
NY_MA_Split_TS2 ERV Flag | Split_TS2 ERV Flag | Yes | Yes | Yes | Yes | Yes | Yes |  |  |  |  | 2021-05-06
id | item | Zone4A(OH-Columbus-OH) ASHRAE901-state_STD2016 | Zone4A(OH-Columbus-OH) ASHRAE901-state_STD2019 | Zone5A(OH-Cleveland-OH) ASHRAE901-state_STD2016 | Zone5A(OH-Cleveland-OH) ASHRAE901-state_STD2019 | [6 empty] | 2021-05-06
OH_SO_PSZ-AC:1 Cooling Capacity [ton] | PSZ-AC:1 Cooling Capacity [ton] | 1.8376 | 1.7405 | 1.8248 | 1.7324 | [6 empty] | 2021-05-06
OH_SO_PSZ-AC:2 Cooling Capacity [ton] | PSZ-AC:2 Cooling Capacity [ton] | 1.5947 | 1.5323 | 1.5561 | 1.4945 | [6 empty] | 2021-05-06
OH_SO_PSZ-AC:3 Cooling Capacity [ton] | PSZ-AC:3 Cooling Capacity [ton] | 1.1226 | 1.0837 | 1.1151 | 1.0766 | [6 empty] | 2021-05-06
OH_SO_PSZ-AC:4 Cooling Capacity [ton] | PSZ-AC:4 Cooling Capacity [ton] | 1.5433 | 1.456 | 1.4967 | 1.4155 | [6 empty] | 2021-05-06
OH_SO_PSZ-AC:5 Cooling Capacity [ton] | PSZ-AC:5 Cooling Capacity [ton] | 1.3082 | 1.2687 | 1.291 | 1.2518 | [6 empty] | 2021-05-06
OH_SO_PSZ-AC:1 Supply Flow Rate [cfm] | PSZ-AC:1 Supply Flow Rate [cfm] | 656.8528 | 614.4752 | 656.8528 | 614.4752 | [6 empty] | 2021-05-06
OH_SO_PSZ-AC:2 Supply Flow Rate [cfm] | PSZ-AC:2 Supply Flow Rate [cfm] | 593.2864 | 550.9088 | 572.0976 | 529.72 | [6 empty] | 2021-05-06
OH_SO_PSZ-AC:3 Supply Flow Rate [cfm] | PSZ-AC:3 Supply Flow Rate [cfm] | 466.1536 | 444.9648 | 466.1536 | 444.9648 | [6 empty] | 2021-05-06
OH_SO_PSZ-AC:4 Supply Flow Rate [cfm] | PSZ-AC:4 Supply Flow Rate [cfm] | 550.9088 | 529.72 | 529.72 | 508.5312 | [6 empty] | 2021-05-06
OH_SO_PSZ-AC:5 Supply Flow Rate [cfm] | PSZ-AC:5 Supply Flow Rate [cfm] | 550.9088 | 529.72 | 529.72 | 508.5312 | [6 empty] | 2021-05-06
OH_SO_PSZ-AC:1 OA Rate [cfm] | PSZ-AC:1 OA Rate [cfm] | 136.9178 | 136.9178 | 136.9178 | 136.9178 | [6 empty] | 2021-05-06
OH_SO_PSZ-AC:2 OA Rate [cfm] | PSZ-AC:2 OA Rate [cfm] | 103.7925 | 103.7925 | 103.7925 | 103.7925 | [6 empty] | 2021-05-06
OH_SO_PSZ-AC:3 OA Rate [cfm] | PSZ-AC:3 OA Rate [cfm] | 61.5711 | 61.5711 | 61.5711 | 61.5711 | [6 empty] | 2021-05-06
OH_SO_PSZ-AC:4 OA Rate [cfm] | PSZ-AC:4 OA Rate [cfm] | 103.7925 | 103.7925 | 103.7925 | 103.7925 | [6 empty] | 2021-05-06
OH_SO_PSZ-AC:5 OA Rate [cfm] | PSZ-AC:5 OA Rate [cfm] | 61.5711 | 61.5711 | 61.5711 | 61.5711 | [6 empty] | 2021-05-06
OH_SO_PSZ-AC:1 heating Capacity [kBtu/hr] | PSZ-AC:1 heating Capacity [kBtu/hr] | 14.5097 | 14.5097 | 14.6342 | 14.6342 | [6 empty] | 2021-05-06
OH_SO_PSZ-AC:2 heating Capacity [kBtu/hr] | PSZ-AC:2 heating Capacity [kBtu/hr] | 20.5226 | 20.2936 | 20.6605 | 20.426 | [6 empty] | 2021-05-06
OH_SO_PSZ-AC:3 heating Capacity [kBtu/hr] | PSZ-AC:3 heating Capacity [kBtu/hr] | 12.4927 | 12.3713 | 12.5371 | 12.4134 | [6 empty] | 2021-05-06
OH_SO_PSZ-AC:4 heating Capacity [kBtu/hr] | PSZ-AC:4 heating Capacity [kBtu/hr] | 20.321 | 20.1338 | 20.3525 | 20.1695 | [6 empty] | 2021-05-06
OH_SO_PSZ-AC:5 heating Capacity [kBtu/hr] | PSZ-AC:5 heating Capacity [kBtu/hr] | 12.5478 | 12.421 | 12.5973 | 12.4675 | [6 empty] | 2021-05-06
id | item | Zone4A(OH-Columbus-OH) ASHRAE901-state_STD2016 | Zone4A(OH-Columbus-OH) ASHRAE901-state_STD2019 | Zone5A(OH-Cleveland-OH) ASHRAE901-state_STD2016 | Zone5A(OH-Cleveland-OH) ASHRAE901-state_STD2019 | [6 empty] | 2021-05-06
OH_LO_CAV_BAS Supply Flow Rate [cfm] | CAV_BAS Supply Flow Rate [cfm] | 11950.4832 | 11060.5536 | 11865.728 | 10975.7984 | [6 empty] | 2021-05-06
OH_LO_VAV_BOT WITH REHEAT Supply Flow Rate [cfm] | VAV_BOT WITH REHEAT Supply Flow Rate [cfm] | 19769.1504 | 18815.6544 | 19896.2832 | 18942.7872 | [6 empty] | 2021-05-06
OH_LO_VAV_MID WITH REHEAT Supply Flow Rate [cfm] | VAV_MID WITH REHEAT Supply Flow Rate [cfm] | 183028.8547 | 173917.6707 | 184575.6371 | 175506.8307 | [6 empty] | 2021-05-06
OH_LO_VAV_TOP WITH REHEAT Supply Flow Rate [cfm] | VAV_TOP WITH REHEAT Supply Flow Rate [cfm] | 19514.8848 | 18709.7104 | 19514.8848 | 18730.8992 | [6 empty] | 2021-05-06
OH_LO_Supply Air Temp. Reset Flag | Supply Air Temp. Reset Flag | Yes | Yes | Yes | Yes | [6 empty] | 2021-05-06
OH_LO_CAV_BAS OA Rate [cfm] | CAV_BAS OA Rate [cfm] | 2542.8255 | 2542.8255 | 2542.8255 | 2542.8255 | [6 empty] | 2021-05-06
OH_LO_VAV_BOT WITH REHEAT OA Rate [cfm] | VAV_BOT WITH REHEAT OA Rate [cfm] | 5377.8022 | 4302.174 | 5377.8022 | 4302.174 | [6 empty] | 2021-05-06
OH_LO_VAV_MID WITH REHEAT OA Rate [cfm] | VAV_MID WITH REHEAT OA Rate [cfm] | 53777.9373 | 43021.7396 | 53777.9373 | 43021.7396 | [6 empty] | 2021-05-06
OH_LO_VAV_TOP WITH REHEAT OA Rate [cfm] | VAV_TOP WITH REHEAT OA Rate [cfm] | 5377.8022 | 4302.174 | 5377.8022 | 4302.174 | [6 empty] | 2021-05-06
OH_LO_AIRLOOP DATACENTER BASEMENT OA Rate [cfm] | AIRLOOP DATACENTER BASEMENT OA Rate [cfm] | 716.9654 | 716.9654 | 716.9654 | 716.9654 | [6 empty] | 2021-05-06
OH_LO_VAV_bot_WITH_REHEAT ERV Flag | VAV_bot_WITH_REHEAT ERV Flag | Yes | Yes | Yes | Yes | [6 empty] | 2021-05-06
OH_LO_VAV_mid_WITH_REHEAT ERV Flag | VAV_mid_WITH_REHEAT ERV Flag | Yes | Yes | Yes | Yes | [6 empty] | 2021-05-06
OH_LO_VAV_top_WITH_REHEAT ERV Flag | VAV_top_WITH_REHEAT ERV Flag | Yes | Yes | Yes | Yes | [6 empty] | 2021-05-06
OH_LO_COOLSYS1 CHILLER1 Capacity [ton] | COOLSYS1 CHILLER1 Capacity [ton] | 400.4706 | 362.4133 | 405.6645 | 367.1235 | [6 empty] | 2021-05-06
OH_LO_COOLSYS1 CHILLER2 Capacity [ton] | COOLSYS1 CHILLER2 Capacity [ton] | 400.4706 | 362.4133 | 405.6645 | 367.1235 | [6 empty] | 2021-05-06
OH_LO_TOWERWATERSYS COOLTOWER 1 Capacity [ton] | TOWERWATERSYS COOLTOWER 1 Capacity [ton] | 380.119 | 343.9934 | 385.0547 | 348.4697 | [6 empty] | 2021-05-06
OH_LO_TOWERWATERSYS COOLTOWER 2 Capacity [ton] | TOWERWATERSYS COOLTOWER 2 Capacity [ton] | 380.119 | 343.9934 | 385.0547 | 348.4697 | [6 empty] | 2021-05-06
OH_LO_HEATSYS1 BOILER Capacity [MMBTU/h] | HEATSYS1 BOILER Capacity [MMBTU/h] | 4587.2433 | 4067.0037 | 4621.7834 | 4092.0542 | [6 empty] | 2021-05-06
OH_LO_COOLSYS1 PUMP Flow Rate [gal/min] | COOLSYS1 PUMP Flow Rate [gal/min] | 0 | 0 | 0 | 0 | [6 empty] | 2021-05-06
OH_LO_COOLSYS1 CHILLER1 PUMP Flow Rate [gal/min] | COOLSYS1 CHILLER1 PUMP Flow Rate [gal/min] | 630.9586 | 568.1073 | 639.169 | 578.3292 | [6 empty] | 2021-05-06
OH_LO_COOLSYS1 CHILLER2 PUMP Flow Rate [gal/min] | COOLSYS1 CHILLER2 PUMP Flow Rate [gal/min] | 630.9586 | 568.1073 | 639.169 | 578.3292 | [6 empty] | 2021-05-06
OH_LO_COOLSYS1 PUMP SECONDARY Flow Rate [gal/min] | COOLSYS1 PUMP SECONDARY Flow Rate [gal/min] | 1261.9171 | 1136.2161 | 1278.3381 | 1156.6583 | [6 empty] | 2021-05-06
OH_LO_HEATSYS1 PUMP Flow Rate [gal/min] | HEATSYS1 PUMP Flow Rate [gal/min] | 941.5916 | 834.8064 | 948.6815 | 839.9482 | [6 empty] | 2021-05-06
OH_LO_TOWERWATERSYS PUMP Flow Rate [gal/min] | TOWERWATERSYS PUMP Flow Rate [gal/min] | 2209.3765 | 1999.5183 | 2238.0656 | 2025.5128 | [6 empty] | 2021-05-06
OH_LO_PLANT CIRC PUMP Flow Rate [gal/min] | PLANT CIRC PUMP Flow Rate [gal/min] | 210.0723 | 209.2322 | 210.3956 | 209.554 | [6 empty] | 2021-05-06
OH_LO_COOLSYS1 PUMP SECONDARY Pressure setpoint reset [yes,no] | COOLSYS1 PUMP SECONDARY Pressure setpoint reset [yes,no] | pump_ride_on_curve | pump_ride_on_curve | pump_ride_on_curve | pump_ride_on_curve | [6 empty] | 2021-05-06
OH_LO_COOLSYS1 CHILLER1 PUMP Pump Power [hp] | COOLSYS1 CHILLER1 PUMP Pump Power [hp] | 3.4038 | 3.0344 | 3.4481 | 3.089 | [6 empty] | 2021-05-06
OH_LO_COOLSYS1 CHILLER2 PUMP Pump Power [hp] | COOLSYS1 CHILLER2 PUMP Pump Power [hp] | 3.4038 | 3.0344 | 3.4481 | 3.089 | [6 empty] | 2021-05-06
OH_LO_COOLSYS1 PUMP SECONDARY Pump Power [hp] | COOLSYS1 PUMP SECONDARY Pump Power [hp] | 20.4228 | 18.2064 | 20.6886 | 18.5339 | [6 empty] | 2021-05-06
OH_LO_HEATSYS1 PUMP Pump Power [hp] | HEATSYS1 PUMP Pump Power [hp] | 20.3531 | 17.8662 | 20.5063 | 17.9762 | [6 empty] | 2021-05-06
OH_LO_TOWERWATERSYS PUMP Pump Power [hp] | TOWERWATERSYS PUMP Pump Power [hp] | 39.5577 | 35.444 | 40.0707 | 35.9047 | [6 empty] | 2021-05-06
OH_LO_PLANT CIRC PUMP Pump Power [hp] | PLANT CIRC PUMP Pump Power [hp] | 4.533 | 4.4702 | 4.54 | 4.4771 | [6 empty] | 2021-05-06
OH_LO_Datacenter PLANT CIRC PUMP Pump Power [hp] | Datacenter PLANT CIRC PUMP Pump Power [hp] | 4.533 | 4.4702 | 4.54 | 4.4771 | [6 empty] | 2021-05-06
OH_LO_ZN_VAV_BOXes_Max_Reheat_Water_Flow_GPM | ZN_VAV_BOXes_Max_Reheat_Water_Flow_GPM | 482.3606 | 464.4346 | 483.996 | 465.8202 | [6 empty] | 2021-05-06
OH_LO_COOLSYS1 PUMP SECONDARY VSD | COOLSYS1 PUMP SECONDARY VSD | No | No | No | No | [6 empty] | 2021-05-06
OH_LO_HEATSYS1 PUMP VSD | HEATSYS1 PUMP VSD | No | No | No | No | [6 empty] | 2021-05-06
OH_LO_DATACENTER BASEMENT Cooling Capacity [ton] | DATACENTER BASEMENT Cooling Capacity [ton] | 122.8759 | 122.5122 | 122.8136 | 122.4501 | [6 empty] | 2021-05-06
OH_LO_DATACENTER BOT Cooling Capacity [ton] | DATACENTER BOT Cooling Capacity [ton] | 2.6852 | 2.6615 | 2.7083 | 2.6846 | [6 empty] | 2021-05-06
OH_LO_DATACENTER MID Cooling Capacity [ton] | DATACENTER MID Cooling Capacity [ton] | 25.7026 | 25.4947 | 25.9558 | 25.7466 | [6 empty] | 2021-05-06
OH_LO_DATACENTER TOP Cooling Capacity [ton] | DATACENTER TOP Cooling Capacity [ton] | 2.6181 | 2.598 | 2.6417 | 2.6215 | [6 empty] | 2021-05-06
id | item | Zone4A(OH-Columbus-OH) ASHRAE901-state_STD2016 | Zone4A(OH-Columbus-OH) ASHRAE901-state_STD2019 | Zone5A(OH-Cleveland-OH) ASHRAE901-state_STD2016 | Zone5A(OH-Cleveland-OH) ASHRAE901-state_STD2019 | [6 empty] | 2021-05-06
OH_RS_PSZ-AC:1 Cooling Capacity [ton] | PSZ-AC:1 Cooling Capacity [ton] | 10.1856 | 9.8506 | 10.1809 | 9.7791 | [6 empty] | 2021-05-06
OH_RS_PSZ-AC:2 Cooling Capacity [ton] | PSZ-AC:2 Cooling Capacity [ton] | 47.4054 | 45.8317 | 48.28 | 46.3281 | [6 empty] | 2021-05-06
OH_RS_PSZ-AC:3 Cooling Capacity [ton] | PSZ-AC:3 Cooling Capacity [ton] | 6.2671 | 6.1135 | 6.2356 | 6.0754 | [6 empty] | 2021-05-06
OH_RS_PSZ-AC:4 Cooling Capacity [ton] | PSZ-AC:4 Cooling Capacity [ton] | 5.0555 | 4.8998 | 5.0285 | 4.8565 | [6 empty] | 2021-05-06
OH_RS_PSZ-AC:1 Supply Flow Rate [cfm] | PSZ-AC:1 Supply Flow Rate [cfm] | 3983.4944 | 3708.04 | 3919.928 | 3623.2848 | [6 empty] | 2021-05-06
OH_RS_PSZ-AC:2 Supply Flow Rate [cfm] | PSZ-AC:2 Supply Flow Rate [cfm] | 15149.992 | 14366.0064 | 15383.0688 | 14471.9504 | [6 empty] | 2021-05-06
OH_RS_PSZ-AC:3 Supply Flow Rate [cfm] | PSZ-AC:3 Supply Flow Rate [cfm] | 2267.2016 | 2203.6352 | 2267.2016 | 2182.4464 | [6 empty] | 2021-05-06
OH_RS_PSZ-AC:4 Supply Flow Rate [cfm] | PSZ-AC:4 Supply Flow Rate [cfm] | 1716.2928 | 1652.7264 | 1716.2928 | 1631.5376 | [6 empty] | 2021-05-06
OH_RS_PSZ-AC:1 OA Rate [cfm] | PSZ-AC:1 OA Rate [cfm] | 490.669 | 490.669 | 490.669 | 490.669 | [6 empty] | 2021-05-06
OH_RS_PSZ-AC:2 OA Rate [cfm] | PSZ-AC:2 OA Rate [cfm] | 4005.1282 | 4005.1282 | 4005.1282 | 4005.1282 | [6 empty] | 2021-05-06
OH_RS_PSZ-AC:3 OA Rate [cfm] | PSZ-AC:3 OA Rate [cfm] | 377.3937 | 377.3937 | 377.3937 | 377.3937 | [6 empty] | 2021-05-06
OH_RS_PSZ-AC:4 OA Rate [cfm] | PSZ-AC:4 OA Rate [cfm] | 377.3937 | 377.3937 | 377.3937 | 377.3937 | [6 empty] | 2021-05-06
OH_RS_PSZ-AC:1 OA Damper [gravity, motorized] | PSZ-AC:1 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2021-05-06
OH_RS_PSZ-AC:2 OA Damper [gravity, motorized] | PSZ-AC:2 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2021-05-06
OH_RS_PSZ-AC:3 OA Damper [gravity, motorized] | PSZ-AC:3 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2021-05-06
OH_RS_PSZ-AC:4 OA Damper [gravity, motorized] | PSZ-AC:4 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2021-05-06
OH_RS_PSZ-AC:1 Heating Capacity [kBtu/hr] | PSZ-AC:1 Heating Capacity [kBtu/hr] | 176.2795 | 165.6427 | 174.436 | 162.7834 | [6 empty] | 2021-05-06
OH_RS_PSZ-AC:2 Heating Capacity [kBtu/hr] | PSZ-AC:2 Heating Capacity [kBtu/hr] | 808.3992 | 777.1507 | 825.1127 | 787.4361 | [6 empty] | 2021-05-06
OH_RS_PSZ-AC:3 Heating Capacity [kBtu/hr] | PSZ-AC:3 Heating Capacity [kBtu/hr] | 108.233 | 105.6395 | 108.2177 | 105.514 | [6 empty] | 2021-05-06
OH_RS_PSZ-AC:4 Heating Capacity [kBtu/hr] | PSZ-AC:4 Heating Capacity [kBtu/hr] | 88.1201 | 85.2809 | 87.8979 | 84.7874 | [6 empty] | 2021-05-06
id | item | Zone4A(OH-Columbus-OH) ASHRAE901-state_STD2016 | Zone4A(OH-Columbus-OH) ASHRAE901-state_STD2019 | Zone5A(OH-Cleveland-OH) ASHRAE901-state_STD2016 | Zone5A(OH-Cleveland-OH) ASHRAE901-state_STD2019 | [6 empty] | 2021-05-06
OH_PS_VAV_POD_1 Cooling Capacity [ton] | VAV_POD_1 Cooling Capacity [ton] | 19.254 | 18.5521 | 19.1092 | 18.4393 | [6 empty] | 2021-05-06
OH_PS_VAV_POD_2 Cooling Capacity [ton] | VAV_POD_2 Cooling Capacity [ton] | 19.0362 | 18.445 | 18.855 | 18.3872 | [6 empty] | 2021-05-06
OH_PS_VAV_POD_3 Cooling Capacity [ton] | VAV_POD_3 Cooling Capacity [ton] | 17.5525 | 16.7125 | 17.3906 | 16.5641 | [6 empty] | 2021-05-06
OH_PS_VAV_OTHER Cooling Capacity [ton] | VAV_OTHER Cooling Capacity [ton] | 27.0945 | 25.4172 | 26.7297 | 25.1001 | [6 empty] | 2021-05-06
OH_PS_PSZ-AC_1:6 Cooling Capacity [ton] | PSZ-AC_1:6 Cooling Capacity [ton] | 8.3052 | 8.0408 | 8.285 | 8.0224 | [6 empty] | 2021-05-06
OH_PS_PSZ-AC_2:5 Cooling Capacity [ton] | PSZ-AC_2:5 Cooling Capacity [ton] | 5.5551 | 5.5315 | 5.5014 | 5.4786 | [6 empty] | 2021-05-06
OH_PS_PSZ-AC_2:7 Cooling Capacity [ton] | PSZ-AC_2:7 Cooling Capacity [ton] | 10.5074 | 10.5074 | 10.5074 | 10.5074 | [6 empty] | 2021-05-06
OH_PS_VAV_POD_1 Supply Flow Rate [cfm] | VAV_POD_1 Supply Flow Rate [cfm] | 5784.5424 | 5572.6544 | 5742.1648 | 5530.2768 | [6 empty] | 2021-05-06
OH_PS_VAV_POD_2 Supply Flow Rate [cfm] | VAV_POD_2 Supply Flow Rate [cfm] | 5720.976 | 5530.2768 | 5657.4096 | 5509.088 | [6 empty] | 2021-05-06
OH_PS_VAV_POD_3 Supply Flow Rate [cfm] | VAV_POD_3 Supply Flow Rate [cfm] | 5276.0112 | 5021.7456 | 5212.4448 | 4979.368 | [6 empty] | 2021-05-06
OH_PS_VAV_OTHER Supply Flow Rate [cfm] | VAV_OTHER Supply Flow Rate [cfm] | 8136.4992 | 7627.968 | 8030.5552 | 7522.024 | [6 empty] | 2021-05-06
OH_PS_PSZ-AC_2:5 Supply Flow Rate [cfm] | PSZ-AC_2:5 Supply Flow Rate [cfm] | 1673.9152 | 1652.7264 | 1652.7264 | 1652.7264 | [6 empty] | 2021-05-06
OH_PS_PSZ-AC_1:6 Supply Flow Rate [cfm] | PSZ-AC_1:6 Supply Flow Rate [cfm] | 2606.2224 | 2500.2784 | 2585.0336 | 2479.0896 | [6 empty] | 2021-05-06
OH_PS_PSZ-AC_2:7 Supply Flow Rate [cfm] | PSZ-AC_2:7 Supply Flow Rate [cfm] | 3157.1312 | 3157.1312 | 3157.1312 | 3157.1312 | [6 empty] | 2021-05-06
OH_PS_Supply Air Temp. Reset Flag | Supply Air Temp. Reset Flag | Yes | Yes | Yes | Yes | [6 empty] | 2021-05-06
OH_PS_VAV_POD_1 OA Rate [cfm] | VAV_POD_1 OA Rate [cfm] | 5776.0881 | 5567.1665 | 5732.0366 | 5533.328 | [6 empty] | 2021-05-06
OH_PS_VAV_POD_2 OA Rate [cfm] | VAV_POD_2 OA Rate [cfm] | 5712.4581 | 5535.0443 | 5657.0494 | 5517.7118 | [6 empty] | 2021-05-06
OH_PS_VAV_POD_3 OA Rate [cfm] | VAV_POD_3 OA Rate [cfm] | 5265.1625 | 5015.1559 | 5218.6319 | 4970.5958 | [6 empty] | 2021-05-06
OH_PS_VAV_OTHER OA Rate [cfm] | VAV_OTHER OA Rate [cfm] | 3736.1787 | 2988.8921 | 3736.1787 | 2988.8921 | [6 empty] | 2021-05-06
OH_PS_PSZ-AC_2:5 OA Rate [cfm] | PSZ-AC_2:5 OA Rate [cfm] | 1152.7343 | 1152.7343 | 1152.7343 | 1152.7343 | [6 empty] | 2021-05-06
OH_PS_PSZ-AC_1:6 OA Rate [cfm] | PSZ-AC_1:6 OA Rate [cfm] | 539.9118 | 539.9118 | 539.9118 | 539.9118 | [6 empty] | 2021-05-06
OH_PS_PSZ-AC_2:7 OA Rate [cfm] | PSZ-AC_2:7 OA Rate [cfm] | 3153.0841 | 3153.0841 | 3153.0841 | 3153.0841 | [6 empty] | 2021-05-06
OH_PS_VAV_POD_1 OA Damper [gravity, motorized] | VAV_POD_1 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2021-05-06
OH_PS_VAV_POD_2 OA Damper [gravity, motorized] | VAV_POD_2 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2021-05-06
OH_PS_VAV_POD_3 OA Damper [gravity, motorized] | VAV_POD_3 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2021-05-06
OH_PS_VAV_OTHER OA Damper [gravity, motorized] | VAV_OTHER OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2021-05-06
OH_PS_PSZ-AC_2:5 OA Damper [gravity, motorized] | PSZ-AC_2:5 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2021-05-06
OH_PS_PSZ-AC_1:6 OA Damper [gravity, motorized] | PSZ-AC_1:6 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2021-05-06
OH_PS_PSZ-AC_2:7 OA Damper [gravity, motorized] | PSZ-AC_2:7 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2021-05-06
OH_PS_VAV_POD_1 (economizer) | VAV_POD_1 (economizer) | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialDryBulb | DifferentialDryBulb | [6 empty] | 2021-05-06
OH_PS_VAV_POD_2 (economizer) | VAV_POD_2 (economizer) | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialDryBulb | DifferentialDryBulb | [6 empty] | 2021-05-06
OH_PS_VAV_POD_3 (economizer) | VAV_POD_3 (economizer) | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialDryBulb | DifferentialDryBulb | [6 empty] | 2021-05-06
OH_PS_VAV_OTHER (economizer) | VAV_OTHER (economizer) | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialDryBulb | DifferentialDryBulb | [6 empty] | 2021-05-06
OH_PS_PSZ-AC_2:5 (economizer) | PSZ-AC_2:5 (economizer) | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialDryBulb | DifferentialDryBulb | [6 empty] | 2021-05-06
OH_PS_PSZ-AC_1:6 (economizer) | PSZ-AC_1:6 (economizer) | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialDryBulb | DifferentialDryBulb | [6 empty] | 2021-05-06
OH_PS_PSZ-AC_2:7 (economizer) | PSZ-AC_2:7 (economizer) | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialDryBulb | DifferentialDryBulb | [6 empty] | 2021-05-06
OH_PS_VAV_Pod_1_ERV Flag | VAV_Pod_1_ERV Flag | Yes | Yes | Yes | Yes | [6 empty] | 2021-05-06
OH_PS_VAV_Pod_2_ERV Flag | VAV_Pod_2_ERV Flag | Yes | Yes | Yes | Yes | [6 empty] | 2021-05-06
OH_PS_VAV_Pod_3_ERV Flag | VAV_Pod_3_ERV Flag | Yes | Yes | Yes | Yes | [6 empty] | 2021-05-06
OH_PS_VAV_OTHER_ERV Flag | VAV_OTHER_ERV Flag | Yes | Yes | Yes | Yes | [6 empty] | 2021-05-06
OH_PS_PSZ_AC_2_5_ERV Flag | PSZ_AC_2_5_ERV Flag | No | No | No | No | [6 empty] | 2021-05-06
OH_PS_PSZ_AC_2_7_ERV Flag | PSZ_AC_2_7_ERV Flag | Yes | Yes | Yes | Yes | [6 empty] | 2021-05-06
OH_PS_HEATSYS1 Capacity [MMBTU/h] | HEATSYS1 Capacity [MMBTU/h] | 1.1172 | 1.0709 | 1.1249 | 1.0803 | [6 empty] | 2021-05-06
OH_PS_HEATSYS1 Flow Rate [gal/min] | HEATSYS1 Flow Rate [gal/min] | 114.657 | 109.9065 | 115.4495 | 110.876 | [6 empty] | 2021-05-06
OH_PS_VAV_POD_1 Fan Power [hp] | VAV_POD_1 Fan Power [hp] | 8.524 | 8.2132 | 8.4599 | 8.1633 | [6 empty] | 2021-05-06
OH_PS_VAV_POD_2 Fan Power [hp] | VAV_POD_2 Fan Power [hp] | 8.4276 | 8.1658 | 8.3474 | 8.1403 | [6 empty] | 2021-05-06
OH_PS_VAV_POD_3 Fan Power [hp] | VAV_POD_3 Fan Power [hp] | 7.7707 | 7.3989 | 7.6991 | 7.3331 | [6 empty] | 2021-05-06
OH_PS_VAV_OTHER Fan Power [hp] | VAV_OTHER Fan Power [hp] | 11.9042 | 11.1673 | 11.744 | 11.0279 | [6 empty] | 2021-05-06
OH_PS_HEATSYS1 Pump Power [hp] | HEATSYS1 Pump Power [hp] | 2.4784 | 2.3522 | 2.4955 | 2.3729 | [6 empty] | 2021-05-06
OH_PS_PSZ-AC_1:6 Heating Capacity [kBtu/hr] | PSZ-AC_1:6 Heating Capacity [kBtu/hr] | 213.3703 | 204.8132 | 213.4954 | 204.9419 | [6 empty] | 2021-05-06
OH_PS_PSZ-AC_2:5 Heating Capacity [kBtu/hr] | PSZ-AC_2:5 Heating Capacity [kBtu/hr] | 140.6511 | 140.396 | 141.1456 | 140.8991 | [6 empty] | 2021-05-06
OH_PS_PSZ-AC_2:7 Heating Capacity [kBtu/hr] | PSZ-AC_2:7 Heating Capacity [kBtu/hr] | 334.1444 | 334.1444 | 337.0129 | 337.0129 | [6 empty] | 2021-05-06
OH_PS_ZN_VAV_BOXes_Max_Reheat_Water_Flow_GPM | ZN_VAV_BOXes_Max_Reheat_Water_Flow_GPM | 72.8935 | 70.0618 | 73.4814 | 70.7453 | [6 empty] | 2021-05-06
id | item | Zone4A(OH-Columbus-OH) ASHRAE901-state_STD2016 | Zone4A(OH-Columbus-OH) ASHRAE901-state_STD2019 | Zone5A(OH-Cleveland-OH) ASHRAE901-state_STD2016 | Zone5A(OH-Cleveland-OH) ASHRAE901-state_STD2019 | [6 empty] | 2021-05-06
OH_SH_SAC_FRONTOFFICE Cooling Capacity [ton] | SAC_FRONTOFFICE Cooling Capacity [ton] | 2.303 | 2.1744 | 2.2653 | 2.1507 | [6 empty] | 2021-05-06
OH_SH_SAC_FRONTLOUNGE Cooling Capacity [ton] | SAC_FRONTLOUNGE Cooling Capacity [ton] | 6.1697 | 5.855 | 6.1043 | 5.7911 | [6 empty] | 2021-05-06
OH_SH_SAC_MEETINGROOM Cooling Capacity [ton] | SAC_MEETINGROOM Cooling Capacity [ton] | 2.9389 | 2.8453 | 2.9103 | 2.819 | [6 empty] | 2021-05-06
OH_SH_SAC_EXC_EMPLGE_RESTRM Cooling Capacity [ton] | SAC_EXC_EMPLGE_RESTRM Cooling Capacity [ton] | 5.9304 | 5.8794 | 5.8727 | 5.8221 | [6 empty] | 2021-05-06
OH_SH_SAC_FO_ADDAQ SUPPLY FAN Supply Flow Rate [cfm] | SAC_FO_ADDAQ SUPPLY FAN Supply Flow Rate [cfm] | 783.9856 | 741.608 | 762.7968 | 720.4192 | [6 empty] | 2021-05-06
OH_SH_SAC_FL_ADDAQ SUPPLY FAN Supply Flow Rate [cfm] | SAC_FL_ADDAQ SUPPLY FAN Supply Flow Rate [cfm] | 1843.4256 | 1758.6704 | 1822.2368 | 1737.4816 | [6 empty] | 2021-05-06
OH_SH_SAC_MR_ADDAQ SUPPLY FAN Supply Flow Rate [cfm] | SAC_MR_ADDAQ SUPPLY FAN Supply Flow Rate [cfm] | 889.9296 | 847.552 | 868.7408 | 847.552 | [6 empty] | 2021-05-06
OH_SH_SAC_EXC_ADDAQ SUPPLY FAN Supply Flow Rate [cfm] | SAC_EXC_ADDAQ SUPPLY FAN Supply Flow Rate [cfm] | 2224.824 | 2203.6352 | 2224.824 | 2203.6352 | [6 empty] | 2021-05-06
OH_SH_SAC_Exc_EmpLge_RestRm OA Rate [cfm] | SAC_Exc_EmpLge_RestRm OA Rate [cfm] | 199.9928 | 199.9928 | 199.9928 | 199.9928 | [6 empty] | 2021-05-06
OH_SH_SAC_FrontLounge OA Rate [cfm] | SAC_FrontLounge OA Rate [cfm] | 500.0133 | 500.0133 | 500.0133 | 500.0133 | [6 empty] | 2021-05-06
OH_SH_SAC_FrontOffice OA Rate [cfm] | SAC_FrontOffice OA Rate [cfm] | 119.2938 | 119.2938 | 119.2938 | 119.2938 | [6 empty] | 2021-05-06
OH_SH_SAC_MeetingRoom OA Rate [cfm] | SAC_MeetingRoom OA Rate [cfm] | 267.7629 | 267.7629 | 267.7629 | 267.7629 | [6 empty] | 2021-05-06
OH_SH_SAC_FrontLounge OA Damper [gravity, motorized] | SAC_FrontLounge OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2021-05-06
OH_SH_SAC_FrontOffice (economizer) | SAC_FrontOffice (economizer) | No | No | No | No | [6 empty] | 2021-05-06
OH_SH_SAC_FrontLounge (economizer) | SAC_FrontLounge (economizer) | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialDryBulb | DifferentialDryBulb | [6 empty] | 2021-05-06
OH_SH_SAC_MeetingRoom (economizer) | SAC_MeetingRoom (economizer) | No | No | No | No | [6 empty] | 2021-05-06
OH_SH_SAC_Exc_EmpLge_RestRm (economizer) | SAC_Exc_EmpLge_RestRm (economizer) | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialDryBulb | DifferentialDryBulb | [6 empty] | 2021-05-06
OH_SH_SAC_FRONTOFFICE Heating Capacity [kBtu/hr] | SAC_FRONTOFFICE Heating Capacity [kBtu/hr] | 36.3652 | 34.5748 | 35.9714 | 34.2063 | [6 empty] | 2021-05-06
OH_SH_SAC_FRONTLOUNGE Heating Capacity [kBtu/hr] | SAC_FRONTLOUNGE Heating Capacity [kBtu/hr] | 101.2952 | 97.9199 | 101.117 | 97.7518 | [6 empty] | 2021-05-06
OH_SH_SAC_MEETINGROOM Heating Capacity [kBtu/hr] | SAC_MEETINGROOM Heating Capacity [kBtu/hr] | 50.328 | 49.3248 | 50.2959 | 49.3155 | [6 empty] | 2021-05-06
OH_SH_SAC_EXC_EMPLGE_RESTRM Heating Capacity [kBtu/hr] | SAC_EXC_EMPLGE_RESTRM Heating Capacity [kBtu/hr] | 93.7278 | 93.0697 | 93.522 | 92.8661 | [6 empty] | 2021-05-06
id | item | Zone4A(OH-Columbus-OH) ASHRAE901-state_STD2016 | Zone4A(OH-Columbus-OH) ASHRAE901-state_STD2019 | Zone5A(OH-Cleveland-OH) ASHRAE901-state_STD2016 | Zone5A(OH-Cleveland-OH) ASHRAE901-state_STD2019 | [6 empty] | 2021-05-06
OH_MA_SPLIT GSW COOLING COIL Cooling Capacity [ton] | SPLIT GSW COOLING COIL Cooling Capacity [ton] | 0.85307 | 0.83904 | 0.84311 | 0.82896 | [6 empty] | 2021-05-06
OH_MA_SPLIT GNW COOLING COIL Cooling Capacity [ton] | SPLIT GNW COOLING COIL Cooling Capacity [ton] | 0.81132 | 0.79775 | 0.80117 | 0.78748 | [6 empty] | 2021-05-06
OH_MA_SPLIT OFFICE COOLING COIL Cooling Capacity [ton] | SPLIT OFFICE COOLING COIL Cooling Capacity [ton] | 1.7249 | 1.5961 | 1.7303 | 1.6015 | [6 empty] | 2021-05-06
OH_MA_SPLIT GNE COOLING COIL Cooling Capacity [ton] | SPLIT GNE COOLING COIL Cooling Capacity [ton] | 0.70766 | 0.69546 | 0.69392 | 0.6818 | [6 empty] | 2021-05-06
OH_MA_SPLIT GN1 COOLING COIL Cooling Capacity [ton] | SPLIT GN1 COOLING COIL Cooling Capacity [ton] | 0.59632 | 0.58668 | 0.59443 | 0.57705 | [6 empty] | 2021-05-06
OH_MA_SPLIT GN2 COOLING COIL Cooling Capacity [ton] | SPLIT GN2 COOLING COIL Cooling Capacity [ton] | 0.59416 | 0.58457 | 0.59232 | 0.57484 | [6 empty] | 2021-05-06
OH_MA_SPLIT GS1 COOLING COIL Cooling Capacity [ton] | SPLIT GS1 COOLING COIL Cooling Capacity [ton] | 0.64389 | 0.63346 | 0.63619 | 0.62576 | [6 empty] | 2021-05-06
OH_MA_SPLIT GS2 COOLING COIL Cooling Capacity [ton] | SPLIT GS2 COOLING COIL Cooling Capacity [ton] | 0.67637 | 0.65935 | 0.66899 | 0.65345 | [6 empty] | 2021-05-06
OH_MA_SPLIT MSW COOLING COIL Cooling Capacity [ton] | SPLIT MSW COOLING COIL Cooling Capacity [ton] | 2.0403 | 2.0088 | 2.0604 | 2.0287 | [6 empty] | 2021-05-06
OH_MA_SPLIT MNW COOLING COIL Cooling Capacity [ton] | SPLIT MNW COOLING COIL Cooling Capacity [ton] | 1.9705 | 1.94 | 1.986 | 1.9553 | [6 empty] | 2021-05-06
OH_MA_SPLIT MSE COOLING COIL Cooling Capacity [ton] | SPLIT MSE COOLING COIL Cooling Capacity [ton] | 1.7575 | 1.7305 | 1.7728 | 1.7447 | [6 empty] | 2021-05-06
OH_MA_SPLIT MNE COOLING COIL Cooling Capacity [ton] | SPLIT MNE COOLING COIL Cooling Capacity [ton] | 1.6178 | 1.5879 | 1.6448 | 1.6148 | [6 empty] | 2021-05-06
OH_MA_SPLIT MN1 COOLING COIL Cooling Capacity [ton] | SPLIT MN1 COOLING COIL Cooling Capacity [ton] | 1.3235 | 1.305 | 1.3261 | 1.3086 | [6 empty] | 2021-05-06
OH_MA_SPLIT MN2 COOLING COIL Cooling Capacity [ton] | SPLIT MN2 COOLING COIL Cooling Capacity [ton] | 1.3176 | 1.2993 | 1.3198 | 1.3025 | [6 empty] | 2021-05-06
OH_MA_SPLIT MS1 COOLING COIL Cooling Capacity [ton] | SPLIT MS1 COOLING COIL Cooling Capacity [ton] | 1.4128 | 1.3931 | 1.4181 | 1.3986 | [6 empty] | 2021-05-06
OH_MA_SPLIT MS2 COOLING COIL Cooling Capacity [ton] | SPLIT MS2 COOLING COIL Cooling Capacity [ton] | 1.4078 | 1.3883 | 1.4127 | 1.3934 | [6 empty] | 2021-05-06
OH_MA_SPLIT TSW COOLING COIL Cooling Capacity [ton] | SPLIT TSW COOLING COIL Cooling Capacity [ton] | 1.2673 | 1.2504 | 1.2728 | 1.2558 | [6 empty] | 2021-05-06
OH_MA_SPLIT TNW COOLING COIL Cooling Capacity [ton] | SPLIT TNW COOLING COIL Cooling Capacity [ton] | 1.2254 | 1.2088 | 1.2309 | 1.2124 | [6 empty] | 2021-05-06
OH_MA_SPLIT TSE COOLING COIL Cooling Capacity [ton] | SPLIT TSE COOLING COIL Cooling Capacity [ton] | 1.1311 | 1.1171 | 1.1354 | 1.1207 | [6 empty] | 2021-05-06
OH_MA_SPLIT TNE COOLING COIL Cooling Capacity [ton] | SPLIT TNE COOLING COIL Cooling Capacity [ton] | 1.0572 | 1.0445 | 1.0515 | 1.0388 | [6 empty] | 2021-05-06
OH_MA_SPLIT TN1 COOLING COIL Cooling Capacity [ton] | SPLIT TN1 COOLING COIL Cooling Capacity [ton] | 0.85359 | 0.84397 | 0.84693 | 0.83756 | [6 empty] | 2021-05-06
OH_MA_SPLIT TN2 COOLING COIL Cooling Capacity [ton] | SPLIT TN2 COOLING COIL Cooling Capacity [ton] | 0.84752 | 0.83806 | 0.84041 | 0.83121 | [6 empty] | 2021-05-06
OH_MA_SPLIT TS1 COOLING COIL Cooling Capacity [ton] | SPLIT TS1 COOLING COIL Cooling Capacity [ton] | 0.93367 | 0.92284 | 0.93453 | 0.92322 | [6 empty] | 2021-05-06
OH_MA_SPLIT TS2 COOLING COIL Cooling Capacity [ton] | SPLIT TS2 COOLING COIL Cooling Capacity [ton] | 0.93608 | 0.92526 | 0.93734 | 0.92586 | [6 empty] | 2021-05-06
OH_MA_Split GN1 Furnace with DX Cooling OA Rate [cfm] | Split GN1 Furnace with DX Cooling OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | [6 empty] | 2021-05-06
OH_MA_Split GN2 Furnace with DX Cooling OA Rate [cfm] | Split GN2 Furnace with DX Cooling OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | [6 empty] | 2021-05-06
OH_MA_Split GNE Furnace with DX Cooling OA Rate [cfm] | Split GNE Furnace with DX Cooling OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | [6 empty] | 2021-05-06
OH_MA_Split GNW Furnace with DX Cooling OA Rate [cfm] | Split GNW Furnace with DX Cooling OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | [6 empty] | 2021-05-06
OH_MA_Split GS1 Furnace with DX Cooling OA Rate [cfm] | Split GS1 Furnace with DX Cooling OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | [6 empty] | 2021-05-06
OH_MA_Split GS2 Furnace with DX Cooling OA Rate [cfm] | Split GS2 Furnace with DX Cooling OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | [6 empty] | 2021-05-06
OH_MA_Split GSW Furnace with DX Cooling OA Rate [cfm] | Split GSW Furnace with DX Cooling OA Rate [cfm] | 56.9945 | 56.9945 | 56.9945 | 56.9945 | [6 empty] | 2021-05-06
OH_MA_Split MN1 Furnace with DX Cooling OA Rate [cfm] | Split MN1 Furnace with DX Cooling OA Rate [cfm] | 109.9824 | 109.9824 | 109.9824 | 109.9824 | [6 empty] | 2021-05-06
OH_MA_Split MN2 Furnace with DX Cooling OA Rate [cfm] | Split MN2 Furnace with DX Cooling OA Rate [cfm] | 109.9824 | 109.9824 | 109.9824 | 109.9824 | [6 empty] | 2021-05-06
OH_MA_Split MNE Furnace with DX Cooling OA Rate [cfm] | Split MNE Furnace with DX Cooling OA Rate [cfm] | 109.9824 | 109.9824 | 109.9824 | 109.9824 | [6 empty] | 2021-05-06
OH_MA_Split MNW Furnace with DX Cooling OA Rate [cfm] | Split MNW Furnace with DX Cooling OA Rate [cfm] | 109.9824 | 109.9824 | 109.9824 | 109.9824 | [6 empty] | 2021-05-06
OH_MA_Split MS1 Furnace with DX Cooling OA Rate [cfm] | Split MS1 Furnace with DX Cooling OA Rate [cfm] | 109.9824 | 109.9824 | 109.9824 | 109.9824 | [6 empty] | 2021-05-06
OH_MA_Split MS2 Furnace with DX Cooling OA Rate [cfm] | Split MS2 Furnace with DX Cooling OA Rate [cfm] | 109.9824 | 109.9824 | 109.9824 | 109.9824 | [6 empty] | 2021-05-06
OH_MA_Split MSE Furnace with DX Cooling OA Rate [cfm] | Split MSE Furnace with DX Cooling OA Rate [cfm] | 109.9824 | 109.9824 | 109.9824 | 109.9824 | [6 empty] | 2021-05-06
OH_MA_Split MSW Furnace with DX Cooling OA Rate [cfm] | Split MSW Furnace with DX Cooling OA Rate [cfm] | 109.9824 | 109.9824 | 109.9824 | 109.9824 | [6 empty] | 2021-05-06
OH_MA_Split Office Furnace with DX Cooling OA Rate [cfm] | Split Office Furnace with DX Cooling OA Rate [cfm] | 80.7372 | 80.7372 | 80.7372 | 80.7372 | [6 empty] | 2021-05-06
OH_MA_Split TN1 Furnace with DX Cooling OA Rate [cfm] | Split TN1 Furnace with DX Cooling OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | [6 empty] | 2021-05-06
OH_MA_Split TN2 Furnace with DX Cooling OA Rate [cfm] | Split TN2 Furnace with DX Cooling OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | [6 empty] | 2021-05-06
OH_MA_Split TNE Furnace with DX Cooling OA Rate [cfm] | Split TNE Furnace with DX Cooling OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | [6 empty] | 2021-05-06
OH_MA_Split TNW Furnace with DX Cooling OA Rate [cfm] | Split TNW Furnace with DX Cooling OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | [6 empty] | 2021-05-06
OH_MA_Split TS1 Furnace with DX Cooling OA Rate [cfm] | Split TS1 Furnace with DX Cooling OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | [6 empty] | 2021-05-06
OH_MA_Split TS2 Furnace with DX Cooling OA Rate [cfm] | Split TS2 Furnace with DX Cooling OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | [6 empty] | 2021-05-06
OH_MA_Split TSE Furnace with DX Cooling OA Rate [cfm] | Split TSE Furnace with DX Cooling OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | [6 empty] | 2021-05-06
OH_MA_Split TSW Furnace with DX Cooling OA Rate [cfm] | Split TSW Furnace with DX Cooling OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | [6 empty] | 2021-05-06
OH_MA_SPLIT GSW HEATING COIL Heating Capacity [kBtu/hr] | SPLIT GSW HEATING COIL Heating Capacity [kBtu/hr] | 10.1241 | 10.1862 | 10.2914 | 10.3487 | [6 empty] | 2021-05-06
OH_MA_SPLIT GNW HEATING COIL Heating Capacity [kBtu/hr] | SPLIT GNW HEATING COIL Heating Capacity [kBtu/hr] | 10.0182 | 10.0804 | 10.1459 | 10.2033 | [6 empty] | 2021-05-06
OH_MA_SPLIT OFFICE HEATING COIL Heating Capacity [kBtu/hr] | SPLIT OFFICE HEATING COIL Heating Capacity [kBtu/hr] | 23.0382 | 23.1191 | 23.163 | 23.2411 | [6 empty] | 2021-05-06
OH_MA_SPLIT GNE HEATING COIL Heating Capacity [kBtu/hr] | SPLIT GNE HEATING COIL Heating Capacity [kBtu/hr] | 9.9956 | 10.0579 | 10.1208 | 10.1781 | [6 empty] | 2021-05-06
OH_MA_SPLIT GN1 HEATING COIL Heating Capacity [kBtu/hr] | SPLIT GN1 HEATING COIL Heating Capacity [kBtu/hr] | 7.3729 | 7.435 | 7.4439 | 7.5013 | [6 empty] | 2021-05-06
OH_MA_SPLIT GN2 HEATING COIL Heating Capacity [kBtu/hr] | SPLIT GN2 HEATING COIL Heating Capacity [kBtu/hr] | 7.3722 | 7.4343 | 7.4432 | 7.5006 | [6 empty] | 2021-05-06
OH_MA_SPLIT GS1 HEATING COIL Heating Capacity [kBtu/hr] | SPLIT GS1 HEATING COIL Heating Capacity [kBtu/hr] | 7.3547 | 7.4166 | 7.4646 | 7.5218 | [6 empty] | 2021-05-06
OH_MA_SPLIT GS2 HEATING COIL Heating Capacity [kBtu/hr] | SPLIT GS2 HEATING COIL Heating Capacity [kBtu/hr] | 7.862 | 7.9247 | 7.9717 | 8.0296 | [6 empty] | 2021-05-06
OH_MA_SPLIT MSW HEATING COIL Heating Capacity [kBtu/hr] | SPLIT MSW HEATING COIL Heating Capacity [kBtu/hr] | 17.8663 | 17.9948 | 18.6535 | 18.7827 | [6 empty] | 2021-05-06
OH_MA_SPLIT MNW HEATING COIL Heating Capacity [kBtu/hr] | SPLIT MNW HEATING COIL Heating Capacity [kBtu/hr] | 17.8773 | 18.0058 | 18.5751 | 18.7044 | [6 empty] | 2021-05-06
OH_MA_SPLIT MSE HEATING COIL Heating Capacity [kBtu/hr] | SPLIT MSE HEATING COIL Heating Capacity [kBtu/hr] | 17.8129 | 17.9413 | 18.5944 | 18.7237 | [6 empty] | 2021-05-06
OH_MA_SPLIT MNE HEATING COIL Heating Capacity [kBtu/hr] | SPLIT MNE HEATING COIL Heating Capacity [kBtu/hr] | 17.8238 | 17.9523 | 18.516 | 18.6452 | [6 empty] | 2021-05-06
OH_MA_SPLIT MN1 HEATING COIL Heating Capacity [kBtu/hr] | SPLIT MN1 HEATING COIL Heating Capacity [kBtu/hr] | 12.401 | 12.5267 | 12.8094 | 12.9345 | [6 empty] | 2021-05-06
OH_MA_SPLIT MN2 HEATING COIL Heating Capacity [kBtu/hr] | SPLIT MN2 HEATING COIL Heating Capacity [kBtu/hr] | 12.3996 | 12.5253 | 12.8078 | 12.933 | [6 empty] | 2021-05-06
OH_MA_SPLIT MS1 HEATING COIL Heating Capacity [kBtu/hr] | SPLIT MS1 HEATING COIL Heating Capacity [kBtu/hr] | 12.3986 | 12.5243 | 12.8961 | 13.0213 | [6 empty] | 2021-05-06
OH_MA_SPLIT MS2 HEATING COIL Heating Capacity [kBtu/hr] | SPLIT MS2 HEATING COIL Heating Capacity [kBtu/hr] | 12.3972 | 12.5229 | 12.8945 | 13.0198 | [6 empty] | 2021-05-06
OH_MA_SPLIT TSW HEATING COIL Heating Capacity [kBtu/hr] | SPLIT TSW HEATING COIL Heating Capacity [kBtu/hr] | 12.5054 | 12.5671 | 13.1179 | 13.1797 | [6 empty] | 2021-05-06
OH_MA_SPLIT TNW HEATING COIL Heating Capacity [kBtu/hr] | SPLIT TNW HEATING COIL Heating Capacity [kBtu/hr] | 12.5171 | 12.579 | 13.083 | 13.1449 | [6 empty] | 2021-05-06
OH_MA_SPLIT TSE HEATING COIL Heating Capacity [kBtu/hr] | SPLIT TSE HEATING COIL Heating Capacity [kBtu/hr] | 12.4771 | 12.5389 | 13.0868 | 13.1486 | [6 empty] | 2021-05-06
OH_MA_SPLIT TNE HEATING COIL Heating Capacity [kBtu/hr] | SPLIT TNE HEATING COIL Heating Capacity [kBtu/hr] | 12.4888 | 12.5507 | 13.0518 | 13.1137 | [6 empty] | 2021-05-06
OH_MA_SPLIT TN1 HEATING COIL Heating Capacity [kBtu/hr] | SPLIT TN1 HEATING COIL Heating Capacity [kBtu/hr] | 9.5886 | 9.6503 | 9.9233 | 9.985 | [6 empty] | 2021-05-06
OH_MA_SPLIT TN2 HEATING COIL Heating Capacity [kBtu/hr] | SPLIT TN2 HEATING COIL Heating Capacity [kBtu/hr] | 9.5877 | 9.6495 | 9.9224 | 9.9841 | [6 empty] | 2021-05-06
OH_MA_SPLIT TS1 HEATING COIL Heating Capacity [kBtu/hr] | SPLIT TS1 HEATING COIL Heating Capacity [kBtu/hr] | 9.5705 | 9.6321 | 9.9524 | 10.0141 | [6 empty] | 2021-05-06
OH_MA_SPLIT TS2 HEATING COIL Heating Capacity [kBtu/hr] | SPLIT TS2 HEATING COIL Heating Capacity [kBtu/hr] | 9.5697 | 9.6313 | 9.9515 | 10.0132 | [6 empty] | 2021-05-06
OH_MA_Split_GSW ERV Flag | Split_GSW ERV Flag | Yes | Yes | Yes | Yes | [6 empty] | 2021-05-06
OH_MA_Split_GNW ERV Flag | Split_GNW ERV Flag | Yes | Yes | Yes | Yes | [6 empty] | 2021-05-06
OH_MA_Split_GNE ERV Flag | Split_GNE ERV Flag | Yes | Yes | Yes | Yes | [6 empty] | 2021-05-06
OH_MA_Split_GN1 ERV Flag | Split_GN1 ERV Flag | Yes | Yes | Yes | Yes | [6 empty] | 2021-05-06
OH_MA_Split_GN2 ERV Flag | Split_GN2 ERV Flag | Yes | Yes | Yes | Yes | [6 empty] | 2021-05-06
OH_MA_Split_GS1 ERV Flag | Split_GS1 ERV Flag | Yes | Yes | Yes | Yes | [6 empty] | 2021-05-06
OH_MA_Split_GS2 ERV Flag | Split_GS2 ERV Flag | Yes | Yes | Yes | Yes | [6 empty] | 2021-05-06
OH_MA_Split_MSW ERV Flag | Split_MSW ERV Flag | Yes | Yes | Yes | Yes | [6 empty] | 2021-05-06
OH_MA_Split_MNW ERV Flag | Split_MNW ERV Flag | Yes | Yes | Yes | Yes | [6 empty] | 2021-05-06
OH_MA_Split_MSE ERV Flag | Split_MSE ERV Flag | Yes | Yes | Yes | Yes | [6 empty] | 2021-05-06
OH_MA_Split_MNE ERV Flag | Split_MNE ERV Flag | Yes | Yes | Yes | Yes | [6 empty] | 2021-05-06
OH_MA_Split_MN1 ERV Flag | Split_MN1 ERV Flag | Yes | Yes | Yes | Yes | [6 empty] | 2021-05-06
OH_MA_Split_MN2 ERV Flag | Split_MN2 ERV Flag | Yes | Yes | Yes | Yes | [6 empty] | 2021-05-06
OH_MA_Split_MS1 ERV Flag | Split_MS1 ERV Flag | Yes | Yes | Yes | Yes | [6 empty] | 2021-05-06
OH_MA_Split_MS2 ERV Flag | Split_MS2 ERV Flag | Yes | Yes | Yes | Yes | [6 empty] | 2021-05-06
OH_MA_Split_TSW ERV Flag | Split_TSW ERV Flag | Yes | Yes | Yes | Yes | [6 empty] | 2021-05-06
OH_MA_Split_TNW ERV Flag | Split_TNW ERV Flag | Yes | Yes | Yes | Yes | [6 empty] | 2021-05-06
OH_MA_Split_TSE ERV Flag | Split_TSE ERV Flag | Yes | Yes | Yes | Yes | [6 empty] | 2021-05-06
OH_MA_Split_TNE ERV Flag | Split_TNE ERV Flag | Yes | Yes | Yes | Yes | [6 empty] | 2021-05-06
OH_MA_Split_TN1 ERV Flag | Split_TN1 ERV Flag | Yes | Yes | Yes | Yes | [6 empty] | 2021-05-06
OH_MA_Split_TN2 ERV Flag | Split_TN2 ERV Flag | Yes | Yes | Yes | Yes | [6 empty] | 2021-05-06
OH_MA_Split_TS1 ERV Flag | Split_TS1 ERV Flag | Yes | Yes | Yes | Yes | [6 empty] | 2021-05-06
OH_MA_Split_TS2 ERV Flag | Split_TS2 ERV Flag | Yes | Yes | Yes | Yes | [6 empty] | 2021-05-06
id | item | Zone3A(OK-Oklahoma-OK) ASHRAE901-state_STD2016 | Zone3A(OK-Oklahoma-OK) ASHRAE901-state_STD2019 | Zone4A(OK-PoncaCity-OK) ASHRAE901-state_STD2016 | Zone4A(OK-PoncaCity-OK) ASHRAE901-state_STD2019 | Zone4B(OK-Amarillo-TX) ASHRAE901-state_STD2016 | Zone4B(OK-Amarillo-TX) ASHRAE901-state_STD2019 |  |  |  |  | 2021-05-06
OK_SO_PSZ-AC:1 Cooling Capacity [ton] | PSZ-AC:1 Cooling Capacity [ton] | 2.0226 | 1.9231 | 2.0052 | 1.9067 | 1.7186 | 1.6204 |  |  |  |  | 2021-05-06
OK_SO_PSZ-AC:2 Cooling Capacity [ton] | PSZ-AC:2 Cooling Capacity [ton] | 1.8561 | 1.7718 | 1.8421 | 1.7675 | 1.5571 | 1.4873 |  |  |  |  | 2021-05-06
OK_SO_PSZ-AC:3 Cooling Capacity [ton] | PSZ-AC:3 Cooling Capacity [ton] | 1.2381 | 1.1959 | 1.2858 | 1.2443 | 1.221 | 1.1716 |  |  |  |  | 2021-05-06
OK_SO_PSZ-AC:4 Cooling Capacity [ton] | PSZ-AC:4 Cooling Capacity [ton] | 1.8289 | 1.7413 | 1.8037 | 1.7239 | 1.5312 | 1.4519 |  |  |  |  | 2021-05-06
OK_SO_PSZ-AC:5 Cooling Capacity [ton] | PSZ-AC:5 Cooling Capacity [ton] | 1.4512 | 1.4062 | 1.5157 | 1.4727 | 1.4573 | 1.4067 |  |  |  |  | 2021-05-06
OK_SO_PSZ-AC:1 Supply Flow Rate [cfm] | PSZ-AC:1 Supply Flow Rate [cfm] | 720.4192 | 656.8528 | 678.0416 | 635.664 | 741.608 | 699.2304 |  |  |  |  | 2021-05-06
OK_SO_PSZ-AC:2 Supply Flow Rate [cfm] | PSZ-AC:2 Supply Flow Rate [cfm] | 678.0416 | 635.664 | 656.8528 | 614.4752 | 678.0416 | 635.664 |  |  |  |  | 2021-05-06
OK_SO_PSZ-AC:3 Supply Flow Rate [cfm] | PSZ-AC:3 Supply Flow Rate [cfm] | 508.5312 | 487.3424 | 529.72 | 508.5312 | 550.9088 | 529.72 |  |  |  |  | 2021-05-06
OK_SO_PSZ-AC:4 Supply Flow Rate [cfm] | PSZ-AC:4 Supply Flow Rate [cfm] | 678.0416 | 635.664 | 635.664 | 593.2864 | 678.0416 | 635.664 |  |  |  |  | 2021-05-06
OK_SO_PSZ-AC:5 Supply Flow Rate [cfm] | PSZ-AC:5 Supply Flow Rate [cfm] | 593.2864 | 572.0976 | 614.4752 | 593.2864 | 656.8528 | 635.664 |  |  |  |  | 2021-05-06
OK_SO_PSZ-AC:1 OA Rate [cfm] | PSZ-AC:1 OA Rate [cfm] | 136.9178 | 136.9178 | 136.9178 | 136.9178 | 136.9178 | 136.9178 |  |  |  |  | 2021-05-06
OK_SO_PSZ-AC:2 OA Rate [cfm] | PSZ-AC:2 OA Rate [cfm] | 103.7925 | 103.7925 | 103.7925 | 103.7925 | 103.7925 | 103.7925 |  |  |  |  | 2021-05-06
OK_SO_PSZ-AC:3 OA Rate [cfm] | PSZ-AC:3 OA Rate [cfm] | 61.5711 | 61.5711 | 61.5711 | 61.5711 | 61.5711 | 61.5711 |  |  |  |  | 2021-05-06
OK_SO_PSZ-AC:4 OA Rate [cfm] | PSZ-AC:4 OA Rate [cfm] | 103.7925 | 103.7925 | 103.7925 | 103.7925 | 103.7925 | 103.7925 |  |  |  |  | 2021-05-06
OK_SO_PSZ-AC:5 OA Rate [cfm] | PSZ-AC:5 OA Rate [cfm] | 61.5711 | 61.5711 | 61.5711 | 61.5711 | 61.5711 | 61.5711 |  |  |  |  | 2021-05-06
OK_SO_PSZ-AC:1 heating Capacity [kBtu/hr] | PSZ-AC:1 heating Capacity [kBtu/hr] | 13.0798 | 13.0798 | 13.4881 | 13.4881 | 12.6282 | 12.6282 |  |  |  |  | 2021-05-06
OK_SO_PSZ-AC:2 heating Capacity [kBtu/hr] | PSZ-AC:2 heating Capacity [kBtu/hr] | 20.6599 | 20.3856 | 18.4413 | 18.2423 | 18.1995 | 17.9931 |  |  |  |  | 2021-05-06
OK_SO_PSZ-AC:3 heating Capacity [kBtu/hr] | PSZ-AC:3 heating Capacity [kBtu/hr] | 12.7985 | 12.638 | 11.3244 | 11.2095 | 11.1792 | 11.0593 |  |  |  |  | 2021-05-06
OK_SO_PSZ-AC:4 heating Capacity [kBtu/hr] | PSZ-AC:4 heating Capacity [kBtu/hr] | 20.4919 | 20.2542 | 18.3447 | 18.1748 | 18.1104 | 17.9332 |  |  |  |  | 2021-05-06
OK_SO_PSZ-AC:5 heating Capacity [kBtu/hr] | PSZ-AC:5 heating Capacity [kBtu/hr] | 12.7985 | 12.638 | 11.3244 | 11.2095 | 11.124 | 11.0098 |  |  |  |  | 2021-05-06
id | item | Zone3A(OK-Oklahoma-OK) ASHRAE901-state_STD2016 | Zone3A(OK-Oklahoma-OK) ASHRAE901-state_STD2019 | Zone4A(OK-PoncaCity-OK) ASHRAE901-state_STD2016 | Zone4A(OK-PoncaCity-OK) ASHRAE901-state_STD2019 | Zone4B(OK-Amarillo-TX) ASHRAE901-state_STD2016 | Zone4B(OK-Amarillo-TX) ASHRAE901-state_STD2019 |  |  |  |  | 2021-05-06
OK_LO_CAV_BAS Supply Flow Rate [cfm] | CAV_BAS Supply Flow Rate [cfm] | 11992.8608 | 11081.7424 | 12204.7488 | 11314.8192 | 13327.7552 | 12353.0704 |  |  |  |  | 2021-05-06
OK_LO_VAV_BOT WITH REHEAT Supply Flow Rate [cfm] | VAV_BOT WITH REHEAT Supply Flow Rate [cfm] | 20214.1152 | 19218.2416 | 20786.2128 | 19811.528 | 21909.2192 | 20849.7792 |  |  |  |  | 2021-05-06
OK_LO_VAV_MID WITH REHEAT Supply Flow Rate [cfm] | VAV_MID WITH REHEAT Supply Flow Rate [cfm] | 188453.1875 | 178981.7939 | 194195.3523 | 184914.6579 | 202670.8723 | 192521.4371 |  |  |  |  | 2021-05-06
OK_LO_VAV_TOP WITH REHEAT Supply Flow Rate [cfm] | VAV_TOP WITH REHEAT Supply Flow Rate [cfm] | 19959.8496 | 19112.2976 | 20828.5904 | 20002.2272 | 22205.8624 | 21315.9328 |  |  |  |  | 2021-05-06
OK_LO_Supply Air Temp. Reset Flag | Supply Air Temp. Reset Flag | No | Yes | Yes | Yes | Yes | Yes |  |  |  |  | 2021-05-06
OK_LO_CAV_BAS OA Rate [cfm] | CAV_BAS OA Rate [cfm] | 2542.8255 | 2542.8255 | 2542.8255 | 2542.8255 | 2542.8255 | 2542.8255 |  |  |  |  | 2021-05-06
OK_LO_VAV_BOT WITH REHEAT OA Rate [cfm] | VAV_BOT WITH REHEAT OA Rate [cfm] | 5377.8022 | 4302.174 | 5377.8022 | 4302.174 | 5377.8022 | 4302.174 |  |  |  |  | 2021-05-06
OK_LO_VAV_MID WITH REHEAT OA Rate [cfm] | VAV_MID WITH REHEAT OA Rate [cfm] | 53777.9373 | 43021.7396 | 53777.9373 | 43021.7396 | 53777.9373 | 43021.7396 |  |  |  |  | 2021-05-06
OK_LO_VAV_TOP WITH REHEAT OA Rate [cfm] | VAV_TOP WITH REHEAT OA Rate [cfm] | 5377.8022 | 4302.174 | 5377.8022 | 4302.174 | 5377.8022 | 4302.174 |  |  |  |  | 2021-05-06
OK_LO_AIRLOOP DATACENTER BASEMENT OA Rate [cfm] | AIRLOOP DATACENTER BASEMENT OA Rate [cfm] | 716.9654 | 716.9654 | 716.9654 | 716.9654 | 716.9654 | 716.9654 |  |  |  |  | 2021-05-06
OK_LO_VAV_bot_WITH_REHEAT ERV Flag | VAV_bot_WITH_REHEAT ERV Flag | Yes | Yes | Yes | Yes | No | No |  |  |  |  | 2021-05-06
OK_LO_VAV_mid_WITH_REHEAT ERV Flag | VAV_mid_WITH_REHEAT ERV Flag | Yes | Yes | Yes | Yes | No | No |  |  |  |  | 2021-05-06
OK_LO_VAV_top_WITH_REHEAT ERV Flag | VAV_top_WITH_REHEAT ERV Flag | Yes | Yes | Yes | Yes | No | No |  |  |  |  | 2021-05-06
OK_LO_COOLSYS1 CHILLER1 Capacity [ton] | COOLSYS1 CHILLER1 Capacity [ton] | 415.1183 | 375.1034 | 428.1264 | 387.6011 | 349.8538 | 321.1757 |  |  |  |  | 2021-05-06
OK_LO_COOLSYS1 CHILLER2 Capacity [ton] | COOLSYS1 CHILLER2 Capacity [ton] | 415.1183 | 375.1034 | 428.1264 | 387.6011 | 349.8538 | 321.1757 |  |  |  |  | 2021-05-06
OK_LO_TOWERWATERSYS COOLTOWER 1 Capacity [ton] | TOWERWATERSYS COOLTOWER 1 Capacity [ton] | 394.0205 | 356.044 | 406.373 | 367.8977 | 332.3081 | 305.0635 |  |  |  |  | 2021-05-06
OK_LO_TOWERWATERSYS COOLTOWER 2 Capacity [ton] | TOWERWATERSYS COOLTOWER 2 Capacity [ton] | 394.0205 | 356.044 | 406.373 | 367.8977 | 332.3081 | 305.0635 |  |  |  |  | 2021-05-06
OK_LO_HEATSYS1 BOILER Capacity [MMBTU/h] | HEATSYS1 BOILER Capacity [MMBTU/h] | 4340.5239 | 3874.4344 | 4184.6074 | 3709.3453 | 4188.4619 | 3701.4559 |  |  |  |  | 2021-05-06
OK_LO_COOLSYS1 PUMP Flow Rate [gal/min] | COOLSYS1 PUMP Flow Rate [gal/min] | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 2021-05-06
OK_LO_COOLSYS1 CHILLER1 PUMP Flow Rate [gal/min] | COOLSYS1 CHILLER1 PUMP Flow Rate [gal/min] | 653.5532 | 588.0613 | 674.5343 | 607.6586 | 549.6163 | 502.2207 |  |  |  |  | 2021-05-06
OK_LO_COOLSYS1 CHILLER2 PUMP Flow Rate [gal/min] | COOLSYS1 CHILLER2 PUMP Flow Rate [gal/min] | 653.5532 | 588.0613 | 674.5343 | 607.6586 | 549.6163 | 502.2207 |  |  |  |  | 2021-05-06
OK_LO_COOLSYS1 PUMP SECONDARY Flow Rate [gal/min] | COOLSYS1 PUMP SECONDARY Flow Rate [gal/min] | 1307.108 | 1176.1209 | 1349.0686 | 1215.3172 | 1099.2342 | 1004.4429 |  |  |  |  | 2021-05-06
OK_LO_HEATSYS1 PUMP Flow Rate [gal/min] | HEATSYS1 PUMP Flow Rate [gal/min] | 890.9498 | 795.2789 | 858.9464 | 761.3925 | 859.7374 | 759.7726 |  |  |  |  | 2021-05-06
OK_LO_TOWERWATERSYS PUMP Flow Rate [gal/min] | TOWERWATERSYS PUMP Flow Rate [gal/min] | 2290.2132 | 2069.4182 | 2362.0152 | 2138.3671 | 1930.0938 | 1771.9076 |  |  |  |  | 2021-05-06
OK_LO_PLANT CIRC PUMP Flow Rate [gal/min] | PLANT CIRC PUMP Flow Rate [gal/min] | 210.3512 | 209.5096 | 212.0329 | 211.1786 | 224.8559 | 223.9429 |  |  |  |  | 2021-05-06
OK_LO_COOLSYS1 PUMP SECONDARY Pressure setpoint reset [yes,no] | COOLSYS1 PUMP SECONDARY Pressure setpoint reset [yes,no] | pump_ride_on_curve | pump_ride_on_curve | pump_ride_on_curve | pump_ride_on_curve | pump_ride_on_curve | pump_ride_on_curve |  |  |  |  | 2021-05-06
OK_LO_COOLSYS1 CHILLER1 PUMP Pump Power [hp] | COOLSYS1 CHILLER1 PUMP Pump Power [hp] | 3.5257 | 3.141 | 3.6389 | 3.2456 | 2.965 | 2.6825 |  |  |  |  | 2021-05-06
OK_LO_COOLSYS1 CHILLER2 PUMP Pump Power [hp] | COOLSYS1 CHILLER2 PUMP Pump Power [hp] | 3.5257 | 3.141 | 3.6389 | 3.2456 | 2.965 | 2.6825 |  |  |  |  | 2021-05-06
OK_LO_COOLSYS1 PUMP SECONDARY Pump Power [hp] | COOLSYS1 PUMP SECONDARY Pump Power [hp] | 21.1542 | 18.8458 | 21.8333 | 19.4739 | 17.7899 | 16.0949 |  |  |  |  | 2021-05-06
OK_LO_HEATSYS1 PUMP Pump Power [hp] | HEATSYS1 PUMP Pump Power [hp] | 19.2584 | 17.0202 | 18.5666 | 16.295 | 18.5837 | 16.2603 |  |  |  |  | 2021-05-06
OK_LO_TOWERWATERSYS PUMP Pump Power [hp] | TOWERWATERSYS PUMP Pump Power [hp] | 41.0045 | 36.6851 | 42.2895 | 37.9074 | 34.5578 | 31.411 |  |  |  |  | 2021-05-06
OK_LO_PLANT CIRC PUMP Pump Power [hp] | PLANT CIRC PUMP Pump Power [hp] | 4.5391 | 4.4761 | 4.5754 | 4.5118 | 4.8521 | 4.7845 |  |  |  |  | 2021-05-06
OK_LO_Datacenter PLANT CIRC PUMP Pump Power [hp] | Datacenter PLANT CIRC PUMP Pump Power [hp] | 4.5391 | 4.4761 | 4.5754 | 4.5118 | 4.8521 | 4.7845 |  |  |  |  | 2021-05-06
OK_LO_ZN_VAV_BOXes_Max_Reheat_Water_Flow_GPM | ZN_VAV_BOXes_Max_Reheat_Water_Flow_GPM | 499.8085 | 480.1827 | 451.8831 | 433.2029 | 466.3917 | 447.9014 |  |  |  |  | 2021-05-06
OK_LO_COOLSYS1 PUMP SECONDARY VSD | COOLSYS1 PUMP SECONDARY VSD | No | No | No | No | No | No |  |  |  |  | 2021-05-06
OK_LO_HEATSYS1 PUMP VSD | HEATSYS1 PUMP VSD | No | No | No | No | No | No |  |  |  |  | 2021-05-06
OK_LO_DATACENTER BASEMENT Cooling Capacity [ton] | DATACENTER BASEMENT Cooling Capacity [ton] | 123.4373 | 123.0753 | 123.5983 | 123.233 | 131.4853 | 131.0935 |  |  |  |  | 2021-05-06
OK_LO_DATACENTER BOT Cooling Capacity [ton] | DATACENTER BOT Cooling Capacity [ton] | 2.6583 | 2.6344 | 2.7429 | 2.7187 | 2.8765 | 2.8507 |  |  |  |  | 2021-05-06
OK_LO_DATACENTER MID Cooling Capacity [ton] | DATACENTER MID Cooling Capacity [ton] | 25.4019 | 25.1917 | 26.2921 | 26.0771 | 27.5392 | 27.3102 |  |  |  |  | 2021-05-06
OK_LO_DATACENTER TOP Cooling Capacity [ton] | DATACENTER TOP Cooling Capacity [ton] | 2.5888 | 2.5684 | 2.6852 | 2.6644 | 2.8104 | 2.7883 |  |  |  |  | 2021-05-06
id | item | Zone3A(OK-Oklahoma-OK) ASHRAE901-state_STD2016 | Zone3A(OK-Oklahoma-OK) ASHRAE901-state_STD2019 | Zone4A(OK-PoncaCity-OK) ASHRAE901-state_STD2016 | Zone4A(OK-PoncaCity-OK) ASHRAE901-state_STD2019 | Zone4B(OK-Amarillo-TX) ASHRAE901-state_STD2016 | Zone4B(OK-Amarillo-TX) ASHRAE901-state_STD2019 |  |  |  |  | 2021-05-06
OK_RS_PSZ-AC:1 Cooling Capacity [ton] | PSZ-AC:1 Cooling Capacity [ton] | 10.8437 | 10.4382 | 11.1627 | 10.6698 | 10.0639 | 10.8533 |  |  |  |  | 2021-05-06
OK_RS_PSZ-AC:2 Cooling Capacity [ton] | PSZ-AC:2 Cooling Capacity [ton] | 52.0366 | 49.7451 | 53.6761 | 51.3055 | 47.692 | 45.4221 |  |  |  |  | 2021-05-06
OK_RS_PSZ-AC:3 Cooling Capacity [ton] | PSZ-AC:3 Cooling Capacity [ton] | 6.8358 | 6.677 | 7.152 | 6.9823 | 6.4065 | 6.2384 |  |  |  |  | 2021-05-06
OK_RS_PSZ-AC:4 Cooling Capacity [ton] | PSZ-AC:4 Cooling Capacity [ton] | 5.5564 | 5.3842 | 5.8751 | 5.6886 | 5.1513 | 4.9938 |  |  |  |  | 2021-05-06
OK_RS_PSZ-AC:1 Supply Flow Rate [cfm] | PSZ-AC:1 Supply Flow Rate [cfm] | 4343.704 | 4089.4384 | 4407.2704 | 4153.0048 | 4513.2144 | 4216.5712 |  |  |  |  | 2021-05-06
OK_RS_PSZ-AC:2 Supply Flow Rate [cfm] | PSZ-AC:2 Supply Flow Rate [cfm] | 16145.8656 | 15128.8032 | 16421.32 | 15425.4464 | 17184.1168 | 16145.8656 |  |  |  |  | 2021-05-06
OK_RS_PSZ-AC:3 Supply Flow Rate [cfm] | PSZ-AC:3 Supply Flow Rate [cfm] | 2415.5232 | 2330.768 | 2479.0896 | 2415.5232 | 2521.4672 | 2457.9008 |  |  |  |  | 2021-05-06
OK_RS_PSZ-AC:4 Supply Flow Rate [cfm] | PSZ-AC:4 Supply Flow Rate [cfm] | 1843.4256 | 1779.8592 | 1928.1808 | 1843.4256 | 1949.3696 | 1864.6144 |  |  |  |  | 2021-05-06
OK_RS_PSZ-AC:1 OA Rate [cfm] | PSZ-AC:1 OA Rate [cfm] | 490.669 | 490.669 | 490.669 | 490.669 | 490.669 | 490.669 |  |  |  |  | 2021-05-06
OK_RS_PSZ-AC:2 OA Rate [cfm] | PSZ-AC:2 OA Rate [cfm] | 4005.1282 | 4005.1282 | 4005.1282 | 4005.1282 | 4005.1282 | 4005.1282 |  |  |  |  | 2021-05-06
OK_RS_PSZ-AC:3 OA Rate [cfm] | PSZ-AC:3 OA Rate [cfm] | 377.3937 | 377.3937 | 377.3937 | 377.3937 | 377.3937 | 377.3937 |  |  |  |  | 2021-05-06
OK_RS_PSZ-AC:4 OA Rate [cfm] | PSZ-AC:4 OA Rate [cfm] | 377.3937 | 377.3937 | 377.3937 | 377.3937 | 377.3937 | 377.3937 |  |  |  |  | 2021-05-06
OK_RS_PSZ-AC:1 OA Damper [gravity, motorized] | PSZ-AC:1 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | motorized | motorized |  |  |  |  | 2021-05-06
OK_RS_PSZ-AC:2 OA Damper [gravity, motorized] | PSZ-AC:2 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | motorized | motorized |  |  |  |  | 2021-05-06
OK_RS_PSZ-AC:3 OA Damper [gravity, motorized] | PSZ-AC:3 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | motorized | motorized |  |  |  |  | 2021-05-06
OK_RS_PSZ-AC:4 OA Damper [gravity, motorized] | PSZ-AC:4 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | motorized | motorized |  |  |  |  | 2021-05-06
OK_RS_PSZ-AC:1 Heating Capacity [kBtu/hr] | PSZ-AC:1 Heating Capacity [kBtu/hr] | 183.0226 | 173.1428 | 188.6838 | 178.5964 | 176.2373 | 166.0563 |  |  |  |  | 2021-05-06
OK_RS_PSZ-AC:2 Heating Capacity [kBtu/hr] | PSZ-AC:2 Heating Capacity [kBtu/hr] | 799.0578 | 760.9335 | 824.7089 | 786.6045 | 788.1234 | 752.7394 |  |  |  |  | 2021-05-06
OK_RS_PSZ-AC:3 Heating Capacity [kBtu/hr] | PSZ-AC:3 Heating Capacity [kBtu/hr] | 108.0068 | 105.4095 | 112.5793 | 109.8807 | 104.9879 | 102.4156 |  |  |  |  | 2021-05-06
OK_RS_PSZ-AC:4 Heating Capacity [kBtu/hr] | PSZ-AC:4 Heating Capacity [kBtu/hr] | 88.2016 | 85.4745 | 92.7052 | 89.8567 | 85.0107 | 82.2116 |  |  |  |  | 2021-05-06
id | item | Zone3A(OK-Oklahoma-OK) ASHRAE901-state_STD2016 | Zone3A(OK-Oklahoma-OK) ASHRAE901-state_STD2019 | Zone4A(OK-PoncaCity-OK) ASHRAE901-state_STD2016 | Zone4A(OK-PoncaCity-OK) ASHRAE901-state_STD2019 | Zone4B(OK-Amarillo-TX) ASHRAE901-state_STD2016 | Zone4B(OK-Amarillo-TX) ASHRAE901-state_STD2019 |  |  |  |  | 2021-05-06
OK_PS_VAV_POD_1 Cooling Capacity [ton] | VAV_POD_1 Cooling Capacity [ton] | 20.2183 | 18.8425 | 21.0209 | 19.9414 | 22.1671 | 20.9191 |  |  |  |  | 2021-05-06
OK_PS_VAV_POD_2 Cooling Capacity [ton] | VAV_POD_2 Cooling Capacity [ton] | 20.287 | 18.8542 | 20.9713 | 19.73 | 22.1077 | 20.6836 |  |  |  |  | 2021-05-06
OK_PS_VAV_POD_3 Cooling Capacity [ton] | VAV_POD_3 Cooling Capacity [ton] | 18.4341 | 17.146 | 19.2575 | 18.1682 | 20.3218 | 19.0853 |  |  |  |  | 2021-05-06
OK_PS_VAV_OTHER Cooling Capacity [ton] | VAV_OTHER Cooling Capacity [ton] | 28.1204 | 26.3196 | 29.3984 | 27.8148 | 28.129 | 25.3792 |  |  |  |  | 2021-05-06
OK_PS_PSZ-AC_1:6 Cooling Capacity [ton] | PSZ-AC_1:6 Cooling Capacity [ton] | 8.6759 | 8.3887 | 8.9166 | 8.5358 | 8.4716 | 8.1858 |  |  |  |  | 2021-05-06
OK_PS_PSZ-AC_2:5 Cooling Capacity [ton] | PSZ-AC_2:5 Cooling Capacity [ton] | 5.5891 | 5.401 | 6.0419 | 6.0146 | 6.4717 | 6.4454 |  |  |  |  | 2021-05-06
OK_PS_PSZ-AC_2:7 Cooling Capacity [ton] | PSZ-AC_2:7 Cooling Capacity [ton] | 10.5074 | 10.5074 | 10.5074 | 10.5074 | 10.5074 | 10.5074 |  |  |  |  | 2021-05-06
OK_PS_VAV_POD_1 Supply Flow Rate [cfm] | VAV_POD_1 Supply Flow Rate [cfm] | 6059.9968 | 5657.4096 | 6314.2624 | 5975.2416 | 6653.2832 | 6271.8848 |  |  |  |  | 2021-05-06
OK_PS_VAV_POD_2 Supply Flow Rate [cfm] | VAV_POD_2 Supply Flow Rate [cfm] | 6081.1856 | 5657.4096 | 6293.0736 | 5911.6752 | 6632.0944 | 6208.3184 |  |  |  |  | 2021-05-06
OK_PS_VAV_POD_3 Supply Flow Rate [cfm] | VAV_POD_3 Supply Flow Rate [cfm] | 5530.2768 | 5148.8784 | 5784.5424 | 5445.5216 | 6102.3744 | 5720.976 |  |  |  |  | 2021-05-06
OK_PS_VAV_OTHER Supply Flow Rate [cfm] | VAV_OTHER Supply Flow Rate [cfm] | 8433.1424 | 7903.4224 | 8814.5408 | 8348.3872 | 9407.8272 | 8878.1072 |  |  |  |  | 2021-05-06
OK_PS_PSZ-AC_2:5 Supply Flow Rate [cfm] | PSZ-AC_2:5 Supply Flow Rate [cfm] | 1673.9152 | 1610.3488 | 1822.2368 | 1801.048 | 1949.3696 | 1928.1808 |  |  |  |  | 2021-05-06
OK_PS_PSZ-AC_1:6 Supply Flow Rate [cfm] | PSZ-AC_1:6 Supply Flow Rate [cfm] | 2627.4112 | 2521.4672 | 2669.7888 | 2563.8448 | 2902.8656 | 2775.7328 |  |  |  |  | 2021-05-06
OK_PS_PSZ-AC_2:7 Supply Flow Rate [cfm] | PSZ-AC_2:7 Supply Flow Rate [cfm] | 3157.1312 | 3157.1312 | 3157.1312 | 3157.1312 | 3157.1312 | 3157.1312 |  |  |  |  | 2021-05-06
OK_PS_Supply Air Temp. Reset Flag | Supply Air Temp. Reset Flag | No | No | Yes | Yes | Yes | Yes |  |  |  |  | 2021-05-06
OK_PS_VAV_POD_1 OA Rate [cfm] | VAV_POD_1 OA Rate [cfm] | 6067.1798 | 5654.316 | 6308.0329 | 5984.0985 | 6649.1514 | 6277.4787 |  |  |  |  | 2021-05-06
OK_PS_VAV_POD_2 OA Rate [cfm] | VAV_POD_2 OA Rate [cfm] | 6087.7965 | 5657.8334 | 6293.1584 | 5920.6381 | 6634.1497 | 6206.814 |  |  |  |  | 2021-05-06
OK_PS_VAV_POD_3 OA Rate [cfm] | VAV_POD_3 OA Rate [cfm] | 5531.76 | 5145.2339 | 5778.8426 | 5422.002 | 6098.2426 | 5422.002 |  |  |  |  | 2021-05-06
OK_PS_VAV_OTHER OA Rate [cfm] | VAV_OTHER OA Rate [cfm] | 3736.1787 | 2988.8921 | 3736.1787 | 2988.8921 | 3736.1787 | 2988.8921 |  |  |  |  | 2021-05-06
OK_PS_PSZ-AC_2:5 OA Rate [cfm] | PSZ-AC_2:5 OA Rate [cfm] | 1152.7343 | 1152.7343 | 1152.7343 | 1152.7343 | 1152.7343 | 1152.7343 |  |  |  |  | 2021-05-06
OK_PS_PSZ-AC_1:6 OA Rate [cfm] | PSZ-AC_1:6 OA Rate [cfm] | 539.9118 | 539.9118 | 539.9118 | 539.9118 | 539.9118 | 539.9118 |  |  |  |  | 2021-05-06
OK_PS_PSZ-AC_2:7 OA Rate [cfm] | PSZ-AC_2:7 OA Rate [cfm] | 3153.0841 | 3153.0841 | 3153.0841 | 3153.0841 | 3153.0841 | 3153.0841 |  |  |  |  | 2021-05-06
OK_PS_VAV_POD_1 OA Damper [gravity, motorized] | VAV_POD_1 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | motorized | motorized |  |  |  |  | 2021-05-06
OK_PS_VAV_POD_2 OA Damper [gravity, motorized] | VAV_POD_2 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | motorized | motorized |  |  |  |  | 2021-05-06
OK_PS_VAV_POD_3 OA Damper [gravity, motorized] | VAV_POD_3 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | motorized | motorized |  |  |  |  | 2021-05-06
OK_PS_VAV_OTHER OA Damper [gravity, motorized] | VAV_OTHER OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | motorized | motorized |  |  |  |  | 2021-05-06
OK_PS_PSZ-AC_2:5 OA Damper [gravity, motorized] | PSZ-AC_2:5 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | motorized | motorized |  |  |  |  | 2021-05-06
OK_PS_PSZ-AC_1:6 OA Damper [gravity, motorized] | PSZ-AC_1:6 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | motorized | motorized |  |  |  |  | 2021-05-06
OK_PS_PSZ-AC_2:7 OA Damper [gravity, motorized] | PSZ-AC_2:7 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | motorized | motorized |  |  |  |  | 2021-05-06
OK_PS_VAV_POD_1 (economizer) | VAV_POD_1 (economizer) | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialDryBulb | DifferentialDryBulb |  |  |  |  | 2021-05-06
OK_PS_VAV_POD_2 (economizer) | VAV_POD_2 (economizer) | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialDryBulb | DifferentialDryBulb |  |  |  |  | 2021-05-06
OK_PS_VAV_POD_3 (economizer) | VAV_POD_3 (economizer) | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialDryBulb | DifferentialDryBulb |  |  |  |  | 2021-05-06
OK_PS_VAV_OTHER (economizer) | VAV_OTHER (economizer) | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialDryBulb | DifferentialDryBulb |  |  |  |  | 2021-05-06
OK_PS_PSZ-AC_2:5 (economizer) | PSZ-AC_2:5 (economizer) | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialDryBulb | DifferentialDryBulb |  |  |  |  | 2021-05-06
OK_PS_PSZ-AC_1:6 (economizer) | PSZ-AC_1:6 (economizer) | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialDryBulb | DifferentialDryBulb |  |  |  |  | 2021-05-06
OK_PS_PSZ-AC_2:7 (economizer) | PSZ-AC_2:7 (economizer) | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialDryBulb | DifferentialDryBulb |  |  |  |  | 2021-05-06
OK_PS_VAV_Pod_1_ERV Flag | VAV_Pod_1_ERV Flag | Yes | Yes | Yes | Yes | No | No |  |  |  |  | 2021-05-06
OK_PS_VAV_Pod_2_ERV Flag | VAV_Pod_2_ERV Flag | Yes | Yes | Yes | Yes | No | No |  |  |  |  | 2021-05-06
OK_PS_VAV_Pod_3_ERV Flag | VAV_Pod_3_ERV Flag | Yes | Yes | Yes | Yes | No | No |  |  |  |  | 2021-05-06
OK_PS_VAV_OTHER_ERV Flag | VAV_OTHER_ERV Flag | Yes | Yes | Yes | Yes | No | No |  |  |  |  | 2021-05-06
OK_PS_PSZ_AC_2_5_ERV Flag | PSZ_AC_2_5_ERV Flag | No | Yes | No | No | No | No |  |  |  |  | 2021-05-06
OK_PS_PSZ_AC_2_7_ERV Flag | PSZ_AC_2_7_ERV Flag | Yes | Yes | Yes | Yes | No | No |  |  |  |  | 2021-05-06
OK_PS_HEATSYS1 Capacity [MMBTU/h] | HEATSYS1 Capacity [MMBTU/h] | 1.0943 | 1.0352 | 1.0762 | 1.0149 | 1.0852 | 1.0157 |  |  |  |  | 2021-05-06
OK_PS_HEATSYS1 Flow Rate [gal/min] | HEATSYS1 Flow Rate [gal/min] | 112.3132 | 106.2434 | 110.4571 | 104.1556 | 111.3804 | 104.2409 |  |  |  |  | 2021-05-06
OK_PS_VAV_POD_1 Fan Power [hp] | VAV_POD_1 Fan Power [hp] | 8.9509 | 8.3418 | 9.3063 | 8.8283 | 9.8137 | 9.2612 |  |  |  |  | 2021-05-06
OK_PS_VAV_POD_2 Fan Power [hp] | VAV_POD_2 Fan Power [hp] | 8.9813 | 8.347 | 9.2843 | 8.7347 | 9.7874 | 9.1569 |  |  |  |  | 2021-05-06
OK_PS_VAV_POD_3 Fan Power [hp] | VAV_POD_3 Fan Power [hp] | 8.161 | 7.5908 | 8.5255 | 8.0433 | 8.9968 | 8.4493 |  |  |  |  | 2021-05-06
OK_PS_VAV_OTHER Fan Power [hp] | VAV_OTHER Fan Power [hp] | 12.355 | 11.5637 | 12.9165 | 12.2207 | 13.7732 | 12.988 |  |  |  |  | 2021-05-06
OK_PS_HEATSYS1 Pump Power [hp] | HEATSYS1 Pump Power [hp] | 2.4277 | 2.2738 | 2.3876 | 2.2291 | 2.4076 | 2.2309 |  |  |  |  | 2021-05-06
OK_PS_PSZ-AC_1:6 Heating Capacity [kBtu/hr] | PSZ-AC_1:6 Heating Capacity [kBtu/hr] | 207.3326 | 198.5822 | 213.4952 | 204.9176 | 211.1704 | 202.726 |  |  |  |  | 2021-05-06
OK_PS_PSZ-AC_2:5 Heating Capacity [kBtu/hr] | PSZ-AC_2:5 Heating Capacity [kBtu/hr] | 128.6417 | 126.6483 | 137.1017 | 136.8099 | 132.0303 | 131.7727 |  |  |  |  | 2021-05-06
OK_PS_PSZ-AC_2:7 Heating Capacity [kBtu/hr] | PSZ-AC_2:7 Heating Capacity [kBtu/hr] | 301.2154 | 301.2154 | 310.6177 | 310.6177 | 290.8152 | 290.8152 |  |  |  |  | 2021-05-06
OK_PS_ZN_VAV_BOXes_Max_Reheat_Water_Flow_GPM | ZN_VAV_BOXes_Max_Reheat_Water_Flow_GPM | 76.1343 | 72.5154 | 70.6964 | 66.5854 | 70.9556 | 66.2159 |  |  |  |  | 2021-05-06
id | item | Zone3A(OK-Oklahoma-OK) ASHRAE901-state_STD2016 | Zone3A(OK-Oklahoma-OK) ASHRAE901-state_STD2019 | Zone4A(OK-PoncaCity-OK) ASHRAE901-state_STD2016 | Zone4A(OK-PoncaCity-OK) ASHRAE901-state_STD2019 | Zone4B(OK-Amarillo-TX) ASHRAE901-state_STD2016 | Zone4B(OK-Amarillo-TX) ASHRAE901-state_STD2019 |  |  |  |  | 2021-05-06
OK_SH_SAC_FRONTOFFICE Cooling Capacity [ton] | SAC_FRONTOFFICE Cooling Capacity [ton] | 2.6477 | 2.5032 | 2.6557 | 2.5067 | 2.3543 | 2.2122 |  |  |  |  | 2021-05-06
OK_SH_SAC_FRONTLOUNGE Cooling Capacity [ton] | SAC_FRONTLOUNGE Cooling Capacity [ton] | 6.578 | 6.2553 | 6.5731 | 6.2535 | 6.1667 | 5.9049 |  |  |  |  | 2021-05-06
OK_SH_SAC_MEETINGROOM Cooling Capacity [ton] | SAC_MEETINGROOM Cooling Capacity [ton] | 3.1341 | 3.049 | 3.1042 | 3.0085 | 3.1679 | 3.0934 |  |  |  |  | 2021-05-06
OK_SH_SAC_EXC_EMPLGE_RESTRM Cooling Capacity [ton] | SAC_EXC_EMPLGE_RESTRM Cooling Capacity [ton] | 6.3458 | 6.302 | 6.4617 | 6.4171 | 6.0379 | 5.9926 |  |  |  |  | 2021-05-06
OK_SH_SAC_FO_ADDAQ SUPPLY FAN Supply Flow Rate [cfm] | SAC_FO_ADDAQ SUPPLY FAN Supply Flow Rate [cfm] | 868.7408 | 826.3632 | 868.7408 | 805.1744 | 932.3072 | 868.7408 |  |  |  |  | 2021-05-06
OK_SH_SAC_FL_ADDAQ SUPPLY FAN Supply Flow Rate [cfm] | SAC_FL_ADDAQ SUPPLY FAN Supply Flow Rate [cfm] | 1970.5584 | 1885.8032 | 1970.5584 | 1885.8032 | 2140.0688 | 2034.1248 |  |  |  |  | 2021-05-06
OK_SH_SAC_MR_ADDAQ SUPPLY FAN Supply Flow Rate [cfm] | SAC_MR_ADDAQ SUPPLY FAN Supply Flow Rate [cfm] | 932.3072 | 911.1184 | 932.3072 | 911.1184 | 1017.0624 | 974.6848 |  |  |  |  | 2021-05-06
OK_SH_SAC_EXC_ADDAQ SUPPLY FAN Supply Flow Rate [cfm] | SAC_EXC_ADDAQ SUPPLY FAN Supply Flow Rate [cfm] | 2267.2016 | 2246.0128 | 2288.3904 | 2267.2016 | 2479.0896 | 2457.9008 |  |  |  |  | 2021-05-06
OK_SH_SAC_Exc_EmpLge_RestRm OA Rate [cfm] | SAC_Exc_EmpLge_RestRm OA Rate [cfm] | 199.9928 | 199.9928 | 199.9928 | 199.9928 | 199.9928 | 199.9928 |  |  |  |  | 2021-05-06
OK_SH_SAC_FrontLounge OA Rate [cfm] | SAC_FrontLounge OA Rate [cfm] | 500.0133 | 500.0133 | 500.0133 | 500.0133 | 500.0133 | 500.0133 |  |  |  |  | 2021-05-06
OK_SH_SAC_FrontOffice OA Rate [cfm] | SAC_FrontOffice OA Rate [cfm] | 119.2938 | 119.2938 | 119.2938 | 119.2938 | 119.2938 | 119.2938 |  |  |  |  | 2021-05-06
OK_SH_SAC_MeetingRoom OA Rate [cfm] | SAC_MeetingRoom OA Rate [cfm] | 267.7629 | 267.7629 | 267.7629 | 267.7629 | 267.7629 | 267.7629 |  |  |  |  | 2021-05-06
OK_SH_SAC_FrontLounge OA Damper [gravity, motorized] | SAC_FrontLounge OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | motorized | motorized |  |  |  |  | 2021-05-06
OK_SH_SAC_FrontOffice (economizer) | SAC_FrontOffice (economizer) | No | No | No | No | No | No |  |  |  |  | 2021-05-06
OK_SH_SAC_FrontLounge (economizer) | SAC_FrontLounge (economizer) | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialDryBulb | DifferentialDryBulb |  |  |  |  | 2021-05-06
OK_SH_SAC_MeetingRoom (economizer) | SAC_MeetingRoom (economizer) | No | No | No | No | No | No |  |  |  |  | 2021-05-06
OK_SH_SAC_Exc_EmpLge_RestRm (economizer) | SAC_Exc_EmpLge_RestRm (economizer) | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialDryBulb | DifferentialDryBulb |  |  |  |  | 2021-05-06
OK_SH_SAC_FRONTOFFICE Heating Capacity [kBtu/hr] | SAC_FRONTOFFICE Heating Capacity [kBtu/hr] | 38.0178 | 35.8851 | 38.2517 | 36.0555 | 37.1539 | 34.956 |  |  |  |  | 2021-05-06
OK_SH_SAC_FRONTLOUNGE Heating Capacity [kBtu/hr] | SAC_FRONTLOUNGE Heating Capacity [kBtu/hr] | 99.5114 | 96.1118 | 101.4469 | 98.0483 | 99.2461 | 95.8254 |  |  |  |  | 2021-05-06
OK_SH_SAC_MEETINGROOM Heating Capacity [kBtu/hr] | SAC_MEETINGROOM Heating Capacity [kBtu/hr] | 49.1957 | 48.2992 | 49.903 | 48.8853 | 48.6762 | 47.69 |  |  |  |  | 2021-05-06
OK_SH_SAC_EXC_EMPLGE_RESTRM Heating Capacity [kBtu/hr] | SAC_EXC_EMPLGE_RESTRM Heating Capacity [kBtu/hr] | 91.7917 | 91.1361 | 93.718 | 93.0471 | 92.1588 | 91.486 |  |  |  |  | 2021-05-06
id | item | Zone3A(OK-Oklahoma-OK) ASHRAE901-state_STD2016 | Zone3A(OK-Oklahoma-OK) ASHRAE901-state_STD2019 | Zone4A(OK-PoncaCity-OK) ASHRAE901-state_STD2016 | Zone4A(OK-PoncaCity-OK) ASHRAE901-state_STD2019 | Zone4B(OK-Amarillo-TX) ASHRAE901-state_STD2016 | Zone4B(OK-Amarillo-TX) ASHRAE901-state_STD2019 |  |  |  |  | 2021-05-06
OK_MA_SPLIT GSW COOLING COIL Cooling Capacity [ton] | SPLIT GSW COOLING COIL Cooling Capacity [ton] | 0.96643 | 0.95465 | 1.0269 | 1.013 | 0.86775 | 0.85134 |  |  |  |  | 2021-05-06
OK_MA_SPLIT GNW COOLING COIL Cooling Capacity [ton] | SPLIT GNW COOLING COIL Cooling Capacity [ton] | 0.93709 | 0.92561 | 0.99986 | 0.9861 | 0.84889 | 0.83243 |  |  |  |  | 2021-05-06
OK_MA_SPLIT OFFICE COOLING COIL Cooling Capacity [ton] | SPLIT OFFICE COOLING COIL Cooling Capacity [ton] | 1.7554 | 1.6864 | 1.8453 | 1.7453 | 1.8017 | 1.6369 |  |  |  |  | 2021-05-06
OK_MA_SPLIT GNE COOLING COIL Cooling Capacity [ton] | SPLIT GNE COOLING COIL Cooling Capacity [ton] | 0.8226 | 0.80885 | 0.879 | 0.86697 | 0.71398 | 0.69955 |  |  |  |  | 2021-05-06
OK_MA_SPLIT GN1 COOLING COIL Cooling Capacity [ton] | SPLIT GN1 COOLING COIL Cooling Capacity [ton] | 0.69864 | 0.68943 | 0.71828 | 0.70916 | 0.57437 | 0.56309 |  |  |  |  | 2021-05-06
OK_MA_SPLIT GN2 COOLING COIL Cooling Capacity [ton] | SPLIT GN2 COOLING COIL Cooling Capacity [ton] | 0.69669 | 0.68748 | 0.71578 | 0.70672 | 0.57197 | 0.56069 |  |  |  |  | 2021-05-06
OK_MA_SPLIT GS1 COOLING COIL Cooling Capacity [ton] | SPLIT GS1 COOLING COIL Cooling Capacity [ton] | 0.71966 | 0.71015 | 0.753 | 0.74326 | 0.59724 | 0.58701 |  |  |  |  | 2021-05-06
OK_MA_SPLIT GS2 COOLING COIL Cooling Capacity [ton] | SPLIT GS2 COOLING COIL Cooling Capacity [ton] | 0.7547 | 0.74114 | 0.78824 | 0.77514 | 0.64296 | 0.62574 |  |  |  |  | 2021-05-06
OK_MA_SPLIT MSW COOLING COIL Cooling Capacity [ton] | SPLIT MSW COOLING COIL Cooling Capacity [ton] | 2.19 | 2.1658 | 2.3658 | 2.3334 | 2.0966 | 2.059 |  |  |  |  | 2021-05-06
OK_MA_SPLIT MNW COOLING COIL Cooling Capacity [ton] | SPLIT MNW COOLING COIL Cooling Capacity [ton] | 2.1439 | 2.1204 | 2.3228 | 2.2906 | 2.0561 | 2.0185 |  |  |  |  | 2021-05-06
OK_MA_SPLIT MSE COOLING COIL Cooling Capacity [ton] | SPLIT MSE COOLING COIL Cooling Capacity [ton] | 1.963 | 1.9382 | 2.0431 | 1.9428 | 1.6931 | 1.6665 |  |  |  |  | 2021-05-06
OK_MA_SPLIT MNE COOLING COIL Cooling Capacity [ton] | SPLIT MNE COOLING COIL Cooling Capacity [ton] | 1.8299 | 1.8084 | 1.9059 | 1.8747 | 1.6229 | 1.5879 |  |  |  |  | 2021-05-06
OK_MA_SPLIT MN1 COOLING COIL Cooling Capacity [ton] | SPLIT MN1 COOLING COIL Cooling Capacity [ton] | 1.4836 | 1.4654 | 1.5235 | 1.5052 | 1.2536 | 1.232 |  |  |  |  | 2021-05-06
OK_MA_SPLIT MN2 COOLING COIL Cooling Capacity [ton] | SPLIT MN2 COOLING COIL Cooling Capacity [ton] | 1.4785 | 1.4603 | 1.5168 | 1.4987 | 1.2472 | 1.2257 |  |  |  |  | 2021-05-06
OK_MA_SPLIT MS1 COOLING COIL Cooling Capacity [ton] | SPLIT MS1 COOLING COIL Cooling Capacity [ton] | 1.5354 | 1.5164 | 1.6002 | 1.5809 | 1.2956 | 1.2736 |  |  |  |  | 2021-05-06
OK_MA_SPLIT MS2 COOLING COIL Cooling Capacity [ton] | SPLIT MS2 COOLING COIL Cooling Capacity [ton] | 1.5312 | 1.5122 | 1.5945 | 1.5754 | 1.2901 | 1.2683 |  |  |  |  | 2021-05-06
OK_MA_SPLIT TSW COOLING COIL Cooling Capacity [ton] | SPLIT TSW COOLING COIL Cooling Capacity [ton] | 1.3528 | 1.3406 | 1.4833 | 1.4658 | 1.3618 | 1.3414 |  |  |  |  | 2021-05-06
OK_MA_SPLIT TNW COOLING COIL Cooling Capacity [ton] | SPLIT TNW COOLING COIL Cooling Capacity [ton] | 1.3253 | 1.3137 | 1.4542 | 1.4368 | 1.3409 | 1.3205 |  |  |  |  | 2021-05-06
OK_MA_SPLIT TSE COOLING COIL Cooling Capacity [ton] | SPLIT TSE COOLING COIL Cooling Capacity [ton] | 1.2444 | 1.2319 | 1.3282 | 1.3146 | 1.1359 | 1.1206 |  |  |  |  | 2021-05-06
OK_MA_SPLIT TNE COOLING COIL Cooling Capacity [ton] | SPLIT TNE COOLING COIL Cooling Capacity [ton] | 1.1917 | 1.1798 | 1.2765 | 1.2634 | 1.0842 | 1.0694 |  |  |  |  | 2021-05-06
OK_MA_SPLIT TN1 COOLING COIL Cooling Capacity [ton] | SPLIT TN1 COOLING COIL Cooling Capacity [ton] | 0.94469 | 0.93561 | 1.0036 | 0.99395 | 0.86405 | 0.85276 |  |  |  |  | 2021-05-06
OK_MA_SPLIT TN2 COOLING COIL Cooling Capacity [ton] | SPLIT TN2 COOLING COIL Cooling Capacity [ton] | 0.93957 | 0.9305 | 0.99679 | 0.98731 | 0.85698 | 0.84591 |  |  |  |  | 2021-05-06
OK_MA_SPLIT TS1 COOLING COIL Cooling Capacity [ton] | SPLIT TS1 COOLING COIL Cooling Capacity [ton] | 1.0159 | 1.0034 | 1.0825 | 1.0716 | 0.90204 | 0.88975 |  |  |  |  | 2021-05-06
OK_MA_SPLIT TS2 COOLING COIL Cooling Capacity [ton] | SPLIT TS2 COOLING COIL Cooling Capacity [ton] | 1.0198 | 1.0093 | 1.0851 | 1.0743 | 0.90575 | 0.89484 |  |  |  |  | 2021-05-06
OK_MA_Split GN1 Furnace with DX Cooling OA Rate [cfm] | Split GN1 Furnace with DX Cooling OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 |  |  |  |  | 2021-05-06
OK_MA_Split GN2 Furnace with DX Cooling OA Rate [cfm] | Split GN2 Furnace with DX Cooling OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 |  |  |  |  | 2021-05-06
OK_MA_Split GNE Furnace with DX Cooling OA Rate [cfm] | Split GNE Furnace with DX Cooling OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 |  |  |  |  | 2021-05-06
OK_MA_Split GNW Furnace with DX Cooling OA Rate [cfm] | Split GNW Furnace with DX Cooling OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 |  |  |  |  | 2021-05-06
OK_MA_Split GS1 Furnace with DX Cooling OA Rate [cfm] | Split GS1 Furnace with DX Cooling OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 |  |  |  |  | 2021-05-06
OK_MA_Split GS2 Furnace with DX Cooling OA Rate [cfm] | Split GS2 Furnace with DX Cooling OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 |  |  |  |  | 2021-05-06
OK_MA_Split GSW Furnace with DX Cooling OA Rate [cfm] | Split GSW Furnace with DX Cooling OA Rate [cfm] | 56.9945 | 56.9945 | 56.9945 | 56.9945 | 56.9945 | 56.9945 |  |  |  |  | 2021-05-06
OK_MA_Split MN1 Furnace with DX Cooling OA Rate [cfm] | Split MN1 Furnace with DX Cooling OA Rate [cfm] | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824 |  |  |  |  | 2021-05-06
OK_MA_Split MN2 Furnace with DX Cooling OA Rate [cfm] | Split MN2 Furnace with DX Cooling OA Rate [cfm] | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824 |  |  |  |  | 2021-05-06
OK_MA_Split MNE Furnace with DX Cooling OA Rate [cfm] | Split MNE Furnace with DX Cooling OA Rate [cfm] | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824 |  |  |  |  | 2021-05-06
OK_MA_Split MNW Furnace with DX Cooling OA Rate [cfm] | Split MNW Furnace with DX Cooling OA Rate [cfm] | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824 |  |  |  |  | 2021-05-06
OK_MA_Split MS1 Furnace with DX Cooling OA Rate [cfm] | Split MS1 Furnace with DX Cooling OA Rate [cfm] | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824 |  |  |  |  | 2021-05-06
OK_MA_Split MS2 Furnace with DX Cooling OA Rate [cfm] | Split MS2 Furnace with DX Cooling OA Rate [cfm] | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824 |  |  |  |  | 2021-05-06
OK_MA_Split MSE Furnace with DX Cooling OA Rate [cfm] | Split MSE Furnace with DX Cooling OA Rate [cfm] | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824 |  |  |  |  | 2021-05-06
OK_MA_Split MSW Furnace with DX Cooling OA Rate [cfm] | Split MSW Furnace with DX Cooling OA Rate [cfm] | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824 |  |  |  |  | 2021-05-06
OK_MA_Split Office Furnace with DX Cooling OA Rate [cfm] | Split Office Furnace with DX Cooling OA Rate [cfm] | 80.7372 | 80.7372 | 80.7372 | 80.7372 | 80.7372 | 80.7372 |  |  |  |  | 2021-05-06
OK_MA_Split TN1 Furnace with DX Cooling OA Rate [cfm] | Split TN1 Furnace with DX Cooling OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 |  |  |  |  | 2021-05-06
OK_MA_Split TN2 Furnace with DX Cooling OA Rate [cfm] | Split TN2 Furnace with DX Cooling OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 |  |  |  |  | 2021-05-06
OK_MA_Split TNE Furnace with DX Cooling OA Rate [cfm] | Split TNE Furnace with DX Cooling OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 |  |  |  |  | 2021-05-06
OK_MA_Split TNW Furnace with DX Cooling OA Rate [cfm] | Split TNW Furnace with DX Cooling OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 |  |  |  |  | 2021-05-06
OK_MA_Split TS1 Furnace with DX Cooling OA Rate [cfm] | Split TS1 Furnace with DX Cooling OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 |  |  |  |  | 2021-05-06
OK_MA_Split TS2 Furnace with DX Cooling OA Rate [cfm] | Split TS2 Furnace with DX Cooling OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 |  |  |  |  | 2021-05-06
OK_MA_Split TSE Furnace with DX Cooling OA Rate [cfm] | Split TSE Furnace with DX Cooling OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 |  |  |  |  | 2021-05-06
OK_MA_Split TSW Furnace with DX Cooling OA Rate [cfm] | Split TSW Furnace with DX Cooling OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 |  |  |  |  | 2021-05-06
OK_MA_SPLIT GSW HEATING COIL Heating Capacity [kBtu/hr] | SPLIT GSW HEATING COIL Heating Capacity [kBtu/hr] | 9.4534 | 9.3382 | 8.8031 | 8.862 | 8.5714 | 8.6307 |  |  |  |  | 2021-05-06
OK_MA_SPLIT GNW HEATING COIL Heating Capacity [kBtu/hr] | SPLIT GNW HEATING COIL Heating Capacity [kBtu/hr] | 9.4153 | 9.2941 | 8.738 | 8.797 | 8.5165 | 8.5758 |  |  |  |  | 2021-05-06
OK_MA_SPLIT OFFICE HEATING COIL Heating Capacity [kBtu/hr] | SPLIT OFFICE HEATING COIL Heating Capacity [kBtu/hr] | 21.8549 | 21.7266 | 21.2528 | 21.347 | 20.7227 | 20.8187 |  |  |  |  | 2021-05-06
OK_MA_SPLIT GNE HEATING COIL Heating Capacity [kBtu/hr] | SPLIT GNE HEATING COIL Heating Capacity [kBtu/hr] | 9.4153 | 9.2941 | 8.738 | 8.797 | 8.5389 | 8.5983 |  |  |  |  | 2021-05-06
OK_MA_SPLIT GN1 HEATING COIL Heating Capacity [kBtu/hr] | SPLIT GN1 HEATING COIL Heating Capacity [kBtu/hr] | 6.7027 | 6.6429 | 6.3556 | 6.4147 | 6.1344 | 6.1939 |  |  |  |  | 2021-05-06
OK_MA_SPLIT GN2 HEATING COIL Heating Capacity [kBtu/hr] | SPLIT GN2 HEATING COIL Heating Capacity [kBtu/hr] | 6.7027 | 6.6429 | 6.3556 | 6.4147 | 6.1351 | 6.1946 |  |  |  |  | 2021-05-06
OK_MA_SPLIT GS1 HEATING COIL Heating Capacity [kBtu/hr] | SPLIT GS1 HEATING COIL Heating Capacity [kBtu/hr] | 6.6357 | 6.5819 | 6.31 | 6.3689 | 6.0853 | 6.1446 |  |  |  |  | 2021-05-06
OK_MA_SPLIT GS2 HEATING COIL Heating Capacity [kBtu/hr] | SPLIT GS2 HEATING COIL Heating Capacity [kBtu/hr] | 7.1331 | 7.0793 | 6.8033 | 6.8639 | 6.5772 | 6.6382 |  |  |  |  | 2021-05-06
OK_MA_SPLIT MSW HEATING COIL Heating Capacity [kBtu/hr] | SPLIT MSW HEATING COIL Heating Capacity [kBtu/hr] | 18.2794 | 18.049 | 15.6316 | 15.7599 | 16.7023 | 16.8311 |  |  |  |  | 2021-05-06
OK_MA_SPLIT MNW HEATING COIL Heating Capacity [kBtu/hr] | SPLIT MNW HEATING COIL Heating Capacity [kBtu/hr] | 18.4114 | 18.1661 | 15.7088 | 15.8373 | 16.7927 | 16.9213 |  |  |  |  | 2021-05-06
OK_MA_SPLIT MSE HEATING COIL Heating Capacity [kBtu/hr] | SPLIT MSE HEATING COIL Heating Capacity [kBtu/hr] | 18.2794 | 18.049 | 15.6316 | 15.7599 | 16.755 | 16.8837 |  |  |  |  | 2021-05-06
OK_MA_SPLIT MNE HEATING COIL Heating Capacity [kBtu/hr] | SPLIT MNE HEATING COIL Heating Capacity [kBtu/hr] | 18.4114 | 18.1661 | 15.7088 | 15.8373 | 16.8453 | 16.974 |  |  |  |  | 2021-05-06
OK_MA_SPLIT MN1 HEATING COIL Heating Capacity [kBtu/hr] | SPLIT MN1 HEATING COIL Heating Capacity [kBtu/hr] | 12.3123 | 12.1985 | 10.8346 | 10.8706 | 11.314 | 11.4391 |  |  |  |  | 2021-05-06
OK_MA_SPLIT MN2 HEATING COIL Heating Capacity [kBtu/hr] | SPLIT MN2 HEATING COIL Heating Capacity [kBtu/hr] | 12.3123 | 12.1985 | 10.8346 | 10.8706 | 11.3154 | 11.4405 |  |  |  |  | 2021-05-06
OK_MA_SPLIT MS1 HEATING COIL Heating Capacity [kBtu/hr] | SPLIT MS1 HEATING COIL Heating Capacity [kBtu/hr] | 12.1876 | 12.0888 | 10.8346 | 10.8346 | 11.232 | 11.357 |  |  |  |  | 2021-05-06
OK_MA_SPLIT MS2 HEATING COIL Heating Capacity [kBtu/hr] | SPLIT MS2 HEATING COIL Heating Capacity [kBtu/hr] | 12.1876 | 12.0888 | 10.8346 | 10.8346 | 11.2335 | 11.3585 |  |  |  |  | 2021-05-06
OK_MA_SPLIT TSW HEATING COIL Heating Capacity [kBtu/hr] | SPLIT TSW HEATING COIL Heating Capacity [kBtu/hr] | 13.1584 | 13.0449 | 11.0963 | 11.1579 | 11.8673 | 11.9289 |  |  |  |  | 2021-05-06
OK_MA_SPLIT TNW HEATING COIL Heating Capacity [kBtu/hr] | SPLIT TNW HEATING COIL Heating Capacity [kBtu/hr] | 13.233 | 13.112 | 11.143 | 11.2047 | 11.9204 | 11.9821 |  |  |  |  | 2021-05-06
OK_MA_SPLIT TSE HEATING COIL Heating Capacity [kBtu/hr] | SPLIT TSE HEATING COIL Heating Capacity [kBtu/hr] | 13.1584 | 13.0449 | 11.0963 | 11.1579 | 11.8949 | 11.9565 |  |  |  |  | 2021-05-06
OK_MA_SPLIT TNE HEATING COIL Heating Capacity [kBtu/hr] | SPLIT TNE HEATING COIL Heating Capacity [kBtu/hr] | 13.233 | 13.112 | 11.143 | 11.2047 | 11.948 | 12.0097 |  |  |  |  | 2021-05-06
OK_MA_SPLIT TN1 HEATING COIL Heating Capacity [kBtu/hr] | SPLIT TN1 HEATING COIL Heating Capacity [kBtu/hr] | 9.8928 | 9.8364 | 8.4857 | 8.5473 | 8.9412 | 9.0028 |  |  |  |  | 2021-05-06
OK_MA_SPLIT TN2 HEATING COIL Heating Capacity [kBtu/hr] | SPLIT TN2 HEATING COIL Heating Capacity [kBtu/hr] | 9.8928 | 9.8364 | 8.4857 | 8.5473 | 8.9421 | 9.0036 |  |  |  |  | 2021-05-06
OK_MA_SPLIT TS1 HEATING COIL Heating Capacity [kBtu/hr] | SPLIT TS1 HEATING COIL Heating Capacity [kBtu/hr] | 9.8115 | 9.7624 | 8.4318 | 8.4934 | 8.8811 | 8.9425 |  |  |  |  | 2021-05-06
OK_MA_SPLIT TS2 HEATING COIL Heating Capacity [kBtu/hr] | SPLIT TS2 HEATING COIL Heating Capacity [kBtu/hr] | 9.8115 | 9.7624 | 8.4318 | 8.4934 | 8.8819 | 8.9434 |  |  |  |  | 2021-05-06
OK_MA_Split_GSW ERV Flag | Split_GSW ERV Flag | No | Yes | Yes | Yes | No | Yes |  |  |  |  | 2021-05-06
OK_MA_Split_GNW ERV Flag | Split_GNW ERV Flag | No | Yes | Yes | Yes | No | Yes |  |  |  |  | 2021-05-06
OK_MA_Split_GNE ERV Flag | Split_GNE ERV Flag | No | Yes | Yes | Yes | No | Yes |  |  |  |  | 2021-05-06
OK_MA_Split_GN1 ERV Flag | Split_GN1 ERV Flag | No | Yes | Yes | Yes | No | Yes |  |  |  |  | 2021-05-06
OK_MA_Split_GN2 ERV Flag | Split_GN2 ERV Flag | No | Yes | Yes | Yes | No | Yes |  |  |  |  | 2021-05-06
OK_MA_Split_GS1 ERV Flag | Split_GS1 ERV Flag | No | Yes | Yes | Yes | No | Yes |  |  |  |  | 2021-05-06
OK_MA_Split_GS2 ERV Flag | Split_GS2 ERV Flag | No | Yes | Yes | Yes | No | Yes |  |  |  |  | 2021-05-06
OK_MA_Split_MSW ERV Flag | Split_MSW ERV Flag | No | Yes | Yes | Yes | No | Yes |  |  |  |  | 2021-05-06
OK_MA_Split_MNW ERV Flag | Split_MNW ERV Flag | No | Yes | Yes | Yes | No | Yes |  |  |  |  | 2021-05-06
OK_MA_Split_MSE ERV Flag | Split_MSE ERV Flag | No | Yes | Yes | Yes | No | Yes |  |  |  |  | 2021-05-06
OK_MA_Split_MNE ERV Flag | Split_MNE ERV Flag | No | Yes | Yes | Yes | No | Yes |  |  |  |  | 2021-05-06
OK_MA_Split_MN1 ERV Flag | Split_MN1 ERV Flag | No | Yes | Yes | Yes | No | Yes |  |  |  |  | 2021-05-06
OK_MA_Split_MN2 ERV Flag | Split_MN2 ERV Flag | No | Yes | Yes | Yes | No | Yes |  |  |  |  | 2021-05-06
OK_MA_Split_MS1 ERV Flag | Split_MS1 ERV Flag | No | Yes | Yes | Yes | No | Yes |  |  |  |  | 2021-05-06
OK_MA_Split_MS2 ERV Flag | Split_MS2 ERV Flag | No | Yes | Yes | Yes | No | Yes |  |  |  |  | 2021-05-06
OK_MA_Split_TSW ERV Flag | Split_TSW ERV Flag | No | Yes | No | No | No | No |  |  |  |  | 2021-05-06
OK_MA_Split_TNW ERV Flag | Split_TNW ERV Flag | No | Yes | No | No | No | No |  |  |  |  | 2021-05-06
OK_MA_Split_TSE ERV Flag | Split_TSE ERV Flag | No | Yes | Yes | Yes | No | Yes |  |  |  |  | 2021-05-06
OK_MA_Split_TNE ERV Flag | Split_TNE ERV Flag | No | Yes | Yes | Yes | No | Yes |  |  |  |  | 2021-05-06
OK_MA_Split_TN1 ERV Flag | Split_TN1 ERV Flag | No | Yes | Yes | Yes | No | Yes |  |  |  |  | 2021-05-06
OK_MA_Split_TN2 ERV Flag | Split_TN2 ERV Flag | No | Yes | Yes | Yes | No | Yes |  |  |  |  | 2021-05-06
OK_MA_Split_TS1 ERV Flag | Split_TS1 ERV Flag | No | Yes | Yes | Yes | No | Yes |  |  |  |  | 2021-05-06
OK_MA_Split_TS2 ERV Flag | Split_TS2 ERV Flag | No | Yes | Yes | Yes | No | Yes |  |  |  |  | 2021-05-06
id | item | Zone4C(OR-Portland-OR) ASHRAE901-state_STD2016 | Zone4C(OR-Portland-OR) ASHRAE901-state_STD2019 | Zone5B(OR-Redmond-OR) ASHRAE901-state_STD2016 | Zone5B(OR-Redmond-OR) ASHRAE901-state_STD2019 | [6 empty] | 2021-05-06
OR_SO_PSZ-AC:1 Cooling Capacity [ton] | PSZ-AC:1 Cooling Capacity [ton] | 1.5768 | 1.48 | 1.5548 | 1.4447 | [6 empty] | 2021-05-06
OR_SO_PSZ-AC:2 Cooling Capacity [ton] | PSZ-AC:2 Cooling Capacity [ton] | 1.6595 | 1.5962 | 1.3396 | 1.2634 | [6 empty] | 2021-05-06
OR_SO_PSZ-AC:3 Cooling Capacity [ton] | PSZ-AC:3 Cooling Capacity [ton] | 1.0426 | 0.99983 | 1.0558 | 1.0092 | [6 empty] | 2021-05-06
OR_SO_PSZ-AC:4 Cooling Capacity [ton] | PSZ-AC:4 Cooling Capacity [ton] | 1.303 | 1.2236 | 1.2452 | 1.159 | [6 empty] | 2021-05-06
OR_SO_PSZ-AC:5 Cooling Capacity [ton] | PSZ-AC:5 Cooling Capacity [ton] | 1.2749 | 1.2302 | 1.3749 | 1.3248 | [6 empty] | 2021-05-06
OR_SO_PSZ-AC:1 Supply Flow Rate [cfm] | PSZ-AC:1 Supply Flow Rate [cfm] | 635.664 | 593.2864 | 699.2304 | 656.8528 | [6 empty] | 2021-05-06
OR_SO_PSZ-AC:2 Supply Flow Rate [cfm] | PSZ-AC:2 Supply Flow Rate [cfm] | 699.2304 | 656.8528 | 593.2864 | 572.0976 | [6 empty] | 2021-05-06
OR_SO_PSZ-AC:3 Supply Flow Rate [cfm] | PSZ-AC:3 Supply Flow Rate [cfm] | 466.1536 | 444.9648 | 466.1536 | 444.9648 | [6 empty] | 2021-05-06
OR_SO_PSZ-AC:4 Supply Flow Rate [cfm] | PSZ-AC:4 Supply Flow Rate [cfm] | 529.72 | 487.3424 | 550.9088 | 529.72 | [6 empty] | 2021-05-06
OR_SO_PSZ-AC:5 Supply Flow Rate [cfm] | PSZ-AC:5 Supply Flow Rate [cfm] | 572.0976 | 550.9088 | 614.4752 | 593.2864 | [6 empty] | 2021-05-06
OR_SO_PSZ-AC:1 OA Rate [cfm] | PSZ-AC:1 OA Rate [cfm] | 136.9178 | 136.9178 | 136.9178 | 136.9178 | [6 empty] | 2021-05-06
OR_SO_PSZ-AC:2 OA Rate [cfm] | PSZ-AC:2 OA Rate [cfm] | 103.7925 | 103.7925 | 103.7925 | 103.7925 | [6 empty] | 2021-05-06
OR_SO_PSZ-AC:3 OA Rate [cfm] | PSZ-AC:3 OA Rate [cfm] | 61.5711 | 61.5711 | 61.5711 | 61.5711 | [6 empty] | 2021-05-06
OR_SO_PSZ-AC:4 OA Rate [cfm] | PSZ-AC:4 OA Rate [cfm] | 103.7925 | 103.7925 | 103.7925 | 103.7925 | [6 empty] | 2021-05-06
OR_SO_PSZ-AC:5 OA Rate [cfm] | PSZ-AC:5 OA Rate [cfm] | 61.5711 | 61.5711 | 61.5711 | 61.5711 | [6 empty] | 2021-05-06
OR_SO_PSZ-AC:1 heating Capacity [kBtu/hr] | PSZ-AC:1 heating Capacity [kBtu/hr] | 11.8652 | 11.8652 | 13.0753 | 13.0753 | [6 empty] | 2021-05-06
OR_SO_PSZ-AC:2 heating Capacity [kBtu/hr] | PSZ-AC:2 heating Capacity [kBtu/hr] | 14.6902 | 14.5287 | 17.2794 | 17.0719 | [6 empty] | 2021-05-06
OR_SO_PSZ-AC:3 heating Capacity [kBtu/hr] | PSZ-AC:3 heating Capacity [kBtu/hr] | 8.9887 | 8.8993 | 10.4537 | 10.3391 | [6 empty] | 2021-05-06
OR_SO_PSZ-AC:4 heating Capacity [kBtu/hr] | PSZ-AC:4 heating Capacity [kBtu/hr] | 14.4912 | 14.365 | 17.1635 | 16.9883 | [6 empty] | 2021-05-06
OR_SO_PSZ-AC:5 heating Capacity [kBtu/hr] | PSZ-AC:5 heating Capacity [kBtu/hr] | 8.9589 | 8.8735 | 10.4909 | 10.3724 | [6 empty] | 2021-05-06
id | item | Zone4C(OR-Portland-OR) ASHRAE901-state_STD2016 | Zone4C(OR-Portland-OR) ASHRAE901-state_STD2019 | Zone5B(OR-Redmond-OR) ASHRAE901-state_STD2016 | Zone5B(OR-Redmond-OR) ASHRAE901-state_STD2019 | [6 empty] | 2021-05-06
OR_LO_CAV_BAS Supply Flow Rate [cfm] | CAV_BAS Supply Flow Rate [cfm] | 11675.0288 | 10806.288 | 12861.6016 | 11908.1056 | [6 empty] | 2021-05-06
OR_LO_VAV_BOT WITH REHEAT Supply Flow Rate [cfm] | VAV_BOT WITH REHEAT Supply Flow Rate [cfm] | 19408.9408 | 18497.8224 | 21231.1776 | 20235.304 | [6 empty] | 2021-05-06
OR_LO_VAV_MID WITH REHEAT Supply Flow Rate [cfm] | VAV_MID WITH REHEAT Supply Flow Rate [cfm] | 179723.4019 | 170908.8611 | 196250.6659 | 186609.7619 | [6 empty] | 2021-05-06
OR_LO_VAV_TOP WITH REHEAT Supply Flow Rate [cfm] | VAV_TOP WITH REHEAT Supply Flow Rate [cfm] | 18963.976 | 18179.9904 | 21188.8 | 20298.8704 | [6 empty] | 2021-05-06
OR_LO_Supply Air Temp. Reset Flag | Supply Air Temp. Reset Flag | Yes | Yes | Yes | Yes | [6 empty] | 2021-05-06
OR_LO_CAV_BAS OA Rate [cfm] | CAV_BAS OA Rate [cfm] | 2542.8255 | 2542.8255 | 2542.8255 | 2542.8255 | [6 empty] | 2021-05-06
OR_LO_VAV_BOT WITH REHEAT OA Rate [cfm] | VAV_BOT WITH REHEAT OA Rate [cfm] | 5377.8022 | 4302.174 | 5377.8022 | 4302.174 | [6 empty] | 2021-05-06
OR_LO_VAV_MID WITH REHEAT OA Rate [cfm] | VAV_MID WITH REHEAT OA Rate [cfm] | 53777.9373 | 43021.7396 | 53777.9373 | 43021.7396 | [6 empty] | 2021-05-06
OR_LO_VAV_TOP WITH REHEAT OA Rate [cfm] | VAV_TOP WITH REHEAT OA Rate [cfm] | 5377.8022 | 4302.174 | 5377.8022 | 4302.174 | [6 empty] | 2021-05-06
OR_LO_AIRLOOP DATACENTER BASEMENT OA Rate [cfm] | AIRLOOP DATACENTER BASEMENT OA Rate [cfm] | 716.9654 | 716.9654 | 716.9654 | 716.9654 | [6 empty] | 2021-05-06
OR_LO_VAV_bot_WITH_REHEAT ERV Flag | VAV_bot_WITH_REHEAT ERV Flag | No | No | No | No | [6 empty] | 2021-05-06
OR_LO_VAV_mid_WITH_REHEAT ERV Flag | VAV_mid_WITH_REHEAT ERV Flag | No | No | No | No | [6 empty] | 2021-05-06
OR_LO_VAV_top_WITH_REHEAT ERV Flag | VAV_top_WITH_REHEAT ERV Flag | No | No | No | No | [6 empty] | 2021-05-06
OR_LO_COOLSYS1 CHILLER1 Capacity [ton] | COOLSYS1 CHILLER1 Capacity [ton] | 324.1278 | 300.919 | 304.6141 | 282.1304 | [6 empty] | 2021-05-06
OR_LO_COOLSYS1 CHILLER2 Capacity [ton] | COOLSYS1 CHILLER2 Capacity [ton] | 324.1278 | 300.919 | 304.6141 | 282.1304 | [6 empty] | 2021-05-06
OR_LO_TOWERWATERSYS COOLTOWER 1 Capacity [ton] | TOWERWATERSYS COOLTOWER 1 Capacity [ton] | 307.9638 | 285.9147 | 289.4976 | 268.1264 | [6 empty] | 2021-05-06
OR_LO_TOWERWATERSYS COOLTOWER 2 Capacity [ton] | TOWERWATERSYS COOLTOWER 2 Capacity [ton] | 307.9638 | 285.9147 | 289.4976 | 268.1264 | [6 empty] | 2021-05-06
OR_LO_HEATSYS1 BOILER Capacity [MMBTU/h] | HEATSYS1 BOILER Capacity [MMBTU/h] | 3448.8522 | 3068.3844 | 4111.8326 | 3621.5818 | [6 empty] | 2021-05-06
OR_LO_COOLSYS1 PUMP Flow Rate [gal/min] | COOLSYS1 PUMP Flow Rate [gal/min] | 0 | 0 | 0 | 0 | [6 empty] | 2021-05-06
OR_LO_COOLSYS1 CHILLER1 PUMP Flow Rate [gal/min] | COOLSYS1 CHILLER1 PUMP Flow Rate [gal/min] | 509.6735 | 470.8766 | 478.9603 | 443.0704 | [6 empty] | 2021-05-06
OR_LO_COOLSYS1 CHILLER2 PUMP Flow Rate [gal/min] | COOLSYS1 CHILLER2 PUMP Flow Rate [gal/min] | 509.6735 | 470.8766 | 478.9603 | 443.0704 | [6 empty] | 2021-05-06
OR_LO_COOLSYS1 PUMP SECONDARY Flow Rate [gal/min] | COOLSYS1 PUMP SECONDARY Flow Rate [gal/min] | 1019.3485 | 941.7517 | 957.919 | 886.1424 | [6 empty] | 2021-05-06
OR_LO_HEATSYS1 PUMP Flow Rate [gal/min] | HEATSYS1 PUMP Flow Rate [gal/min] | 707.923 | 629.8269 | 844.0075 | 743.377 | [6 empty] | 2021-05-06
OR_LO_TOWERWATERSYS PUMP Flow Rate [gal/min] | TOWERWATERSYS PUMP Flow Rate [gal/min] | 1788.2335 | 1660.1628 | 1680.6098 | 1594.701 | [6 empty] | 2021-05-06
OR_LO_PLANT CIRC PUMP Flow Rate [gal/min] | PLANT CIRC PUMP Flow Rate [gal/min] | 206.9783 | 206.1113 | 223.1012 | 222.1882 | [6 empty] | 2021-05-06
OR_LO_COOLSYS1 PUMP SECONDARY Pressure setpoint reset [yes,no] | COOLSYS1 PUMP SECONDARY Pressure setpoint reset [yes,no] | pump_ride_on_curve | pump_ride_on_curve | pump_ride_on_curve | pump_ride_on_curve | [6 empty] | 2021-05-06
OR_LO_COOLSYS1 CHILLER1 PUMP Pump Power [hp] | COOLSYS1 CHILLER1 PUMP Pump Power [hp] | 2.7495 | 2.5151 | 2.5838 | 2.3665 | [6 empty] | 2021-05-06
OR_LO_COOLSYS1 CHILLER2 PUMP Pump Power [hp] | COOLSYS1 CHILLER2 PUMP Pump Power [hp] | 2.7495 | 2.5151 | 2.5838 | 2.3665 | [6 empty] | 2021-05-06
OR_LO_COOLSYS1 PUMP SECONDARY Pump Power [hp] | COOLSYS1 PUMP SECONDARY Pump Power [hp] | 16.4971 | 15.0904 | 15.5029 | 14.1993 | [6 empty] | 2021-05-06
OR_LO_HEATSYS1 PUMP Pump Power [hp] | HEATSYS1 PUMP Pump Power [hp] | 15.3021 | 13.4793 | 18.2437 | 15.9094 | [6 empty] | 2021-05-06
OR_LO_TOWERWATERSYS PUMP Pump Power [hp] | TOWERWATERSYS PUMP Pump Power [hp] | 32.0167 | 29.4299 | 30.0892 | 28.2679 | [6 empty] | 2021-05-06
OR_LO_PLANT CIRC PUMP Pump Power [hp] | PLANT CIRC PUMP Pump Power [hp] | 4.4663 | 4.4036 | 4.8142 | 4.747 | [6 empty] | 2021-05-06
OR_LO_Datacenter PLANT CIRC PUMP Pump Power [hp] | Datacenter PLANT CIRC PUMP Pump Power [hp] | 4.4663 | 4.4036 | 4.8142 | 4.747 | [6 empty] | 2021-05-06
OR_LO_ZN_VAV_BOXes_Max_Reheat_Water_Flow_GPM | ZN_VAV_BOXes_Max_Reheat_Water_Flow_GPM | 389.4763 | 373.3618 | 434.6289 | 416.6844 | [6 empty] | 2021-05-06
OR_LO_COOLSYS1 PUMP SECONDARY VSD | COOLSYS1 PUMP SECONDARY VSD | No | No | No | No | [6 empty] | 2021-05-06
OR_LO_HEATSYS1 PUMP VSD | HEATSYS1 PUMP VSD | No | No | No | No | [6 empty] | 2021-05-06
OR_LO_DATACENTER BASEMENT Cooling Capacity [ton] | DATACENTER BASEMENT Cooling Capacity [ton] | 120.323 | 119.963 | 129.9118 | 129.5229 | [6 empty] | 2021-05-06
OR_LO_DATACENTER BOT Cooling Capacity [ton] | DATACENTER BOT Cooling Capacity [ton] | 2.7066 | 2.6823 | 2.8957 | 2.8697 | [6 empty] | 2021-05-06
OR_LO_DATACENTER MID Cooling Capacity [ton] | DATACENTER MID Cooling Capacity [ton] | 25.9484 | 25.7179 | 27.7902 | 27.5583 | [6 empty] | 2021-05-06
OR_LO_DATACENTER TOP Cooling Capacity [ton] | DATACENTER TOP Cooling Capacity [ton] | 2.6383 | 2.6174 | 2.8287 | 2.8063 | [6 empty] | 2021-05-06
id | item | Zone4C(OR-Portland-OR) ASHRAE901-state_STD2016 | Zone4C(OR-Portland-OR) ASHRAE901-state_STD2019 | Zone5B(OR-Redmond-OR) ASHRAE901-state_STD2016 | Zone5B(OR-Redmond-OR) ASHRAE901-state_STD2019 | [6 empty] | 2021-05-06
OR_RS_PSZ-AC:1 Cooling Capacity [ton] | PSZ-AC:1 Cooling Capacity [ton] | 8.7639 | 8.31 | 9.0853 | 8.372 | [6 empty] | 2021-05-06
OR_RS_PSZ-AC:2 Cooling Capacity [ton] | PSZ-AC:2 Cooling Capacity [ton] | 40.0066 | 38.0544 | 40.5305 | 38.1353 | [6 empty] | 2021-05-06
OR_RS_PSZ-AC:3 Cooling Capacity [ton] | PSZ-AC:3 Cooling Capacity [ton] | 5.9014 | 5.771 | 5.3354 | 5.194 | [6 empty] | 2021-05-06
OR_RS_PSZ-AC:4 Cooling Capacity [ton] | PSZ-AC:4 Cooling Capacity [ton] | 4.9274 | 4.7826 | 4.1877 | 4.0282 | [6 empty] | 2021-05-06
OR_RS_PSZ-AC:1 Supply Flow Rate [cfm] | PSZ-AC:1 Supply Flow Rate [cfm] | 3708.04 | 3432.5856 | 3771.6064 | 3432.5856 | [6 empty] | 2021-05-06
OR_RS_PSZ-AC:2 Supply Flow Rate [cfm] | PSZ-AC:2 Supply Flow Rate [cfm] | 14874.5376 | 14005.7968 | 16272.9984 | 15171.1808 | [6 empty] | 2021-05-06
OR_RS_PSZ-AC:3 Supply Flow Rate [cfm] | PSZ-AC:3 Supply Flow Rate [cfm] | 2436.712 | 2373.1456 | 2288.3904 | 2224.824 | [6 empty] | 2021-05-06
OR_RS_PSZ-AC:4 Supply Flow Rate [cfm] | PSZ-AC:4 Supply Flow Rate [cfm] | 1970.5584 | 1906.992 | 1737.4816 | 1652.7264 | [6 empty] | 2021-05-06
OR_RS_PSZ-AC:1 OA Rate [cfm] | PSZ-AC:1 OA Rate [cfm] | 490.669 | 490.669 | 490.669 | 490.669 | [6 empty] | 2021-05-06
OR_RS_PSZ-AC:2 OA Rate [cfm] | PSZ-AC:2 OA Rate [cfm] | 4005.1282 | 4005.1282 | 4005.1282 | 4005.1282 | [6 empty] | 2021-05-06
OR_RS_PSZ-AC:3 OA Rate [cfm] | PSZ-AC:3 OA Rate [cfm] | 377.3937 | 377.3937 | 377.3937 | 377.3937 | [6 empty] | 2021-05-06
OR_RS_PSZ-AC:4 OA Rate [cfm] | PSZ-AC:4 OA Rate [cfm] | 377.3937 | 377.3937 | 377.3937 | 377.3937 | [6 empty] | 2021-05-06
OR_RS_PSZ-AC:1 OA Damper [gravity, motorized] | PSZ-AC:1 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2021-05-06
OR_RS_PSZ-AC:2 OA Damper [gravity, motorized] | PSZ-AC:2 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2021-05-06
OR_RS_PSZ-AC:3 OA Damper [gravity, motorized] | PSZ-AC:3 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2021-05-06
OR_RS_PSZ-AC:4 OA Damper [gravity, motorized] | PSZ-AC:4 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2021-05-06
OR_RS_PSZ-AC:1 Heating Capacity [kBtu/hr] | PSZ-AC:1 Heating Capacity [kBtu/hr] | 159.7574 | 147.4912 | 152.844 | 144.9699 | [6 empty] | 2021-05-06
OR_RS_PSZ-AC:2 Heating Capacity [kBtu/hr] | PSZ-AC:2 Heating Capacity [kBtu/hr] | 737.346 | 701.4797 | 772.7148 | 733.9299 | [6 empty] | 2021-05-06
OR_RS_PSZ-AC:3 Heating Capacity [kBtu/hr] | PSZ-AC:3 Heating Capacity [kBtu/hr] | 109.5382 | 107.0413 | 98.9188 | 96.3191 | [6 empty] | 2021-05-06
OR_RS_PSZ-AC:4 Heating Capacity [kBtu/hr] | PSZ-AC:4 Heating Capacity [kBtu/hr] | 92.2179 | 89.6817 | 81.0774 | 78.5366 | [6 empty] | 2021-05-06
id | item | Zone4C(OR-Portland-OR) ASHRAE901-state_STD2016 | Zone4C(OR-Portland-OR) ASHRAE901-state_STD2019 | Zone5B(OR-Redmond-OR) ASHRAE901-state_STD2016 | Zone5B(OR-Redmond-OR) ASHRAE901-state_STD2019 | [6 empty] | 2021-05-06
OR_PS_VAV_POD_1 Cooling Capacity [ton] | VAV_POD_1 Cooling Capacity [ton] | 19.6256 | 18.9074 | 20.1574 | 19.2587 | [6 empty] | 2021-05-06
OR_PS_VAV_POD_2 Cooling Capacity [ton] | VAV_POD_2 Cooling Capacity [ton] | 19.5457 | 18.7408 | 20.1361 | 19.1062 | [6 empty] | 2021-05-06
OR_PS_VAV_POD_3 Cooling Capacity [ton] | VAV_POD_3 Cooling Capacity [ton] | 17.9684 | 17.1129 | 18.5118 | 17.5522 | [6 empty] | 2021-05-06
OR_PS_VAV_OTHER Cooling Capacity [ton] | VAV_OTHER Cooling Capacity [ton] | 23.1387 | 21.0815 | 22.5779 | 20.4795 | [6 empty] | 2021-05-06
OR_PS_PSZ-AC_1:6 Cooling Capacity [ton] | PSZ-AC_1:6 Cooling Capacity [ton] | 7.2283 | 6.9692 | 7.4937 | 7.2193 | [6 empty] | 2021-05-06
OR_PS_PSZ-AC_2:5 Cooling Capacity [ton] | PSZ-AC_2:5 Cooling Capacity [ton] | 4.8524 | 4.9401 | 5.0656 | 5.0484 | [6 empty] | 2021-05-06
OR_PS_PSZ-AC_2:7 Cooling Capacity [ton] | PSZ-AC_2:7 Cooling Capacity [ton] | 10.5074 | 10.5074 | 10.3303 | 10.3303 | [6 empty] | 2021-05-06
OR_PS_VAV_POD_1 Supply Flow Rate [cfm] | VAV_POD_1 Supply Flow Rate [cfm] | 5890.4864 | 5678.5984 | 6038.808 | 5784.5424 | [6 empty] | 2021-05-06
OR_PS_VAV_POD_2 Supply Flow Rate [cfm] | VAV_POD_2 Supply Flow Rate [cfm] | 5869.2976 | 5615.032 | 6038.808 | 5742.1648 | [6 empty] | 2021-05-06
OR_PS_VAV_POD_3 Supply Flow Rate [cfm] | VAV_POD_3 Supply Flow Rate [cfm] | 5381.9552 | 5127.6896 | 5551.4656 | 5276.0112 | [6 empty] | 2021-05-06
OR_PS_VAV_OTHER Supply Flow Rate [cfm] | VAV_OTHER Supply Flow Rate [cfm] | 7924.6112 | 7437.2688 | 8623.8416 | 8115.3104 | [6 empty] | 2021-05-06
OR_PS_PSZ-AC_2:5 Supply Flow Rate [cfm] | PSZ-AC_2:5 Supply Flow Rate [cfm] | 1525.5936 | 1567.9712 | 1779.8592 | 1758.6704 | [6 empty] | 2021-05-06
OR_PS_PSZ-AC_1:6 Supply Flow Rate [cfm] | PSZ-AC_1:6 Supply Flow Rate [cfm] | 2521.4672 | 2394.3344 | 2796.9216 | 2669.7888 | [6 empty] | 2021-05-06
OR_PS_PSZ-AC_2:7 Supply Flow Rate [cfm] | PSZ-AC_2:7 Supply Flow Rate [cfm] | 3157.1312 | 3157.1312 | 3157.1312 | 3157.1312 | [6 empty] | 2021-05-06
OR_PS_Supply Air Temp. Reset Flag | Supply Air Temp. Reset Flag | Yes | Yes | Yes | Yes | [6 empty] | 2021-05-06
OR_PS_VAV_POD_1 OA Rate [cfm] | VAV_POD_1 OA Rate [cfm] | 5886.3546 | 5673.7886 | 6048.0675 | 5779.224 | [6 empty] | 2021-05-06
OR_PS_VAV_POD_2 OA Rate [cfm] | VAV_POD_2 OA Rate [cfm] | 5862.6655 | 5623.783 | 6042.516 | 5733.4774 | [6 empty] | 2021-05-06
OR_PS_VAV_POD_3 OA Rate [cfm] | VAV_POD_3 OA Rate [cfm] | 5390.3884 | 5135.2964 | 5554.7075 | 5267.1331 | [6 empty] | 2021-05-06
OR_PS_VAV_OTHER OA Rate [cfm] | VAV_OTHER OA Rate [cfm] | 3736.1787 | 2988.8921 | 3736.1787 | 2988.8921 | [6 empty] | 2021-05-06
OR_PS_PSZ-AC_2:5 OA Rate [cfm] | PSZ-AC_2:5 OA Rate [cfm] | 1152.7343 | 1152.7343 | 1152.7343 | 1152.7343 | [6 empty] | 2021-05-06
OR_PS_PSZ-AC_1:6 OA Rate [cfm] | PSZ-AC_1:6 OA Rate [cfm] | 539.9118 | 539.9118 | 539.9118 | 539.9118 | [6 empty] | 2021-05-06
OR_PS_PSZ-AC_2:7 OA Rate [cfm] | PSZ-AC_2:7 OA Rate [cfm] | 3153.0841 | 3153.0841 | 3153.0841 | 3153.0841 | [6 empty] | 2021-05-06
OR_PS_VAV_POD_1 OA Damper [gravity, motorized] | VAV_POD_1 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2021-05-06
OR_PS_VAV_POD_2 OA Damper [gravity, motorized] | VAV_POD_2 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2021-05-06
OR_PS_VAV_POD_3 OA Damper [gravity, motorized] | VAV_POD_3 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2021-05-06
OR_PS_VAV_OTHER OA Damper [gravity, motorized] | VAV_OTHER OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2021-05-06
OR_PS_PSZ-AC_2:5 OA Damper [gravity, motorized] | PSZ-AC_2:5 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2021-05-06
OR_PS_PSZ-AC_1:6 OA Damper [gravity, motorized] | PSZ-AC_1:6 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2021-05-06
OR_PS_PSZ-AC_2:7 OA Damper [gravity, motorized] | PSZ-AC_2:7 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2021-05-06
OR_PS_VAV_POD_1 (economizer) | VAV_POD_1 (economizer) | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | [6 empty] | 2021-05-06
OR_PS_VAV_POD_2 (economizer) | VAV_POD_2 (economizer) | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | [6 empty] | 2021-05-06
OR_PS_VAV_POD_3 (economizer) | VAV_POD_3 (economizer) | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | [6 empty] | 2021-05-06
OR_PS_VAV_OTHER (economizer) | VAV_OTHER (economizer) | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | [6 empty] | 2021-05-06
OR_PS_PSZ-AC_2:5 (economizer) | PSZ-AC_2:5 (economizer) | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | [6 empty] | 2021-05-06
OR_PS_PSZ-AC_1:6 (economizer) | PSZ-AC_1:6 (economizer) | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | [6 empty] | 2021-05-06
OR_PS_PSZ-AC_2:7 (economizer) | PSZ-AC_2:7 (economizer) | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | [6 empty] | 2021-05-06
OR_PS_VAV_Pod_1_ERV Flag | VAV_Pod_1_ERV Flag | No | No | No | No | [6 empty] | 2021-05-06
OR_PS_VAV_Pod_2_ERV Flag | VAV_Pod_2_ERV Flag | No | No | No | No | [6 empty] | 2021-05-06
OR_PS_VAV_Pod_3_ERV Flag | VAV_Pod_3_ERV Flag | No | No | No | No | [6 empty] | 2021-05-06
OR_PS_VAV_OTHER_ERV Flag | VAV_OTHER_ERV Flag | No | No | No | No | [6 empty] | 2021-05-06
OR_PS_PSZ_AC_2_5_ERV Flag | PSZ_AC_2_5_ERV Flag | No | No | No | No | [6 empty] | 2021-05-06
OR_PS_PSZ_AC_2_7_ERV Flag | PSZ_AC_2_7_ERV Flag | No | No | No | No | [6 empty] | 2021-05-06
OR_PS_HEATSYS1 Capacity [MMBTU/h] | HEATSYS1 Capacity [MMBTU/h] | 0.84734 | 0.80806 | 1.0216 | 0.96744 | [6 empty] | 2021-05-06
OR_PS_HEATSYS1 Flow Rate [gal/min] | HEATSYS1 Flow Rate [gal/min] | 86.9641 | 82.9327 | 104.8448 | 99.2901 | [6 empty] | 2021-05-06
OR_PS_VAV_POD_1 Fan Power [hp] | VAV_POD_1 Fan Power [hp] | 8.6885 | 8.3706 | 8.924 | 8.5261 | [6 empty] | 2021-05-06
OR_PS_VAV_POD_2 Fan Power [hp] | VAV_POD_2 Fan Power [hp] | 8.6531 | 8.2968 | 8.9145 | 8.4586 | [6 empty] | 2021-05-06
OR_PS_VAV_POD_3 Fan Power [hp] | VAV_POD_3 Fan Power [hp] | 7.9549 | 7.5761 | 8.1954 | 7.7706 | [6 empty] | 2021-05-06
OR_PS_VAV_OTHER Fan Power [hp] | VAV_OTHER Fan Power [hp] | 11.6016 | 10.8817 | 12.6395 | 11.8701 | [6 empty] | 2021-05-06
OR_PS_HEATSYS1 Pump Power [hp] | HEATSYS1 Pump Power [hp] | 1.8798 | 1.7749 | 2.2663 | 2.125 | [6 empty] | 2021-05-06
OR_PS_PSZ-AC_1:6 Heating Capacity [kBtu/hr] | PSZ-AC_1:6 Heating Capacity [kBtu/hr] | 200.4156 | 191.8446 | 208.9537 | 200.4923 | [6 empty] | 2021-05-06
OR_PS_PSZ-AC_2:5 Heating Capacity [kBtu/hr] | PSZ-AC_2:5 Heating Capacity [kBtu/hr] | 113.7362 | 115.0824 | 130.7816 | 130.4868 | [6 empty] | 2021-05-06
OR_PS_PSZ-AC_2:7 Heating Capacity [kBtu/hr] | PSZ-AC_2:7 Heating Capacity [kBtu/hr] | 273.2442 | 273.2442 | 301.1113 | 301.1113 | [6 empty] | 2021-05-06
OR_PS_ZN_VAV_BOXes_Max_Reheat_Water_Flow_GPM | ZN_VAV_BOXes_Max_Reheat_Water_Flow_GPM | 60.9583 | 58.1775 | 65.9281 | 62.435 | [6 empty] | 2021-05-06
id | item | Zone4C(OR-Portland-OR) ASHRAE901-state_STD2016 | Zone4C(OR-Portland-OR) ASHRAE901-state_STD2019 | Zone5B(OR-Redmond-OR) ASHRAE901-state_STD2016 | Zone5B(OR-Redmond-OR) ASHRAE901-state_STD2019 | [6 empty] | 2021-05-06
OR_SH_SAC_FRONTOFFICE Cooling Capacity [ton] | SAC_FRONTOFFICE Cooling Capacity [ton] | 2.1561 | 2.0417 | 1.9884 | 1.8502 | [6 empty] | 2021-05-06
OR_SH_SAC_FRONTLOUNGE Cooling Capacity [ton] | SAC_FRONTLOUNGE Cooling Capacity [ton] | 5.3437 | 5.119 | 5.0628 | 4.8379 | [6 empty] | 2021-05-06
OR_SH_SAC_MEETINGROOM Cooling Capacity [ton] | SAC_MEETINGROOM Cooling Capacity [ton] | 2.8086 | 2.7299 | 2.6926 | 2.6067 | [6 empty] | 2021-05-06
OR_SH_SAC_EXC_EMPLGE_RESTRM Cooling Capacity [ton] | SAC_EXC_EMPLGE_RESTRM Cooling Capacity [ton] | 5.589 | 5.5482 | 5.491 | 5.4473 | [6 empty] | 2021-05-06
OR_SH_SAC_FO_ADDAQ SUPPLY FAN Supply Flow Rate [cfm] | SAC_FO_ADDAQ SUPPLY FAN Supply Flow Rate [cfm] | 826.3632 | 762.7968 | 847.552 | 783.9856 | [6 empty] | 2021-05-06
OR_SH_SAC_FL_ADDAQ SUPPLY FAN Supply Flow Rate [cfm] | SAC_FL_ADDAQ SUPPLY FAN Supply Flow Rate [cfm] | 1779.8592 | 1695.104 | 1970.5584 | 1864.6144 | [6 empty] | 2021-05-06
OR_SH_SAC_MR_ADDAQ SUPPLY FAN Supply Flow Rate [cfm] | SAC_MR_ADDAQ SUPPLY FAN Supply Flow Rate [cfm] | 868.7408 | 847.552 | 953.496 | 911.1184 | [6 empty] | 2021-05-06
OR_SH_SAC_EXC_ADDAQ SUPPLY FAN Supply Flow Rate [cfm] | SAC_EXC_ADDAQ SUPPLY FAN Supply Flow Rate [cfm] | 2203.6352 | 2182.4464 | 2415.5232 | 2394.3344 | [6 empty] | 2021-05-06
OR_SH_SAC_Exc_EmpLge_RestRm OA Rate [cfm] | SAC_Exc_EmpLge_RestRm OA Rate [cfm] | 199.9928 | 199.9928 | 199.9928 | 199.9928 | [6 empty] | 2021-05-06
OR_SH_SAC_FrontLounge OA Rate [cfm] | SAC_FrontLounge OA Rate [cfm] | 500.0133 | 500.0133 | 500.0133 | 500.0133 | [6 empty] | 2021-05-06
OR_SH_SAC_FrontOffice OA Rate [cfm] | SAC_FrontOffice OA Rate [cfm] | 119.2938 | 119.2938 | 119.2938 | 119.2938 | [6 empty] | 2021-05-06
OR_SH_SAC_MeetingRoom OA Rate [cfm] | SAC_MeetingRoom OA Rate [cfm] | 267.7629 | 267.7629 | 267.7629 | 267.7629 | [6 empty] | 2021-05-06
OR_SH_SAC_FrontLounge OA Damper [gravity, motorized] | SAC_FrontLounge OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2021-05-06
OR_SH_SAC_FrontOffice (economizer) | SAC_FrontOffice (economizer) | No | No | No | No | [6 empty] | 2021-05-06
OR_SH_SAC_FrontLounge (economizer) | SAC_FrontLounge (economizer) | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | [6 empty] | 2021-05-06
OR_SH_SAC_MeetingRoom (economizer) | SAC_MeetingRoom (economizer) | No | No | No | No | [6 empty] | 2021-05-06
OR_SH_SAC_Exc_EmpLge_RestRm (economizer) | SAC_Exc_EmpLge_RestRm (economizer) | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | [6 empty] | 2021-05-06
OR_SH_SAC_FRONTOFFICE Heating Capacity [kBtu/hr] | SAC_FRONTOFFICE Heating Capacity [kBtu/hr] | 36.1052 | 34.2518 | 35.3033 | 33.1697 | [6 empty] | 2021-05-06
OR_SH_SAC_FRONTLOUNGE Heating Capacity [kBtu/hr] | SAC_FRONTLOUNGE Heating Capacity [kBtu/hr] | 90.7886 | 87.3727 | 95.9304 | 92.6226 | [6 empty] | 2021-05-06
OR_SH_SAC_MEETINGROOM Heating Capacity [kBtu/hr] | SAC_MEETINGROOM Heating Capacity [kBtu/hr] | 45.3706 | 44.24 | 48.0371 | 46.8465 | [6 empty] | 2021-05-06
OR_SH_SAC_EXC_EMPLGE_RESTRM Heating Capacity [kBtu/hr] | SAC_EXC_EMPLGE_RESTRM Heating Capacity [kBtu/hr] | 90.8509 | 90.1859 | 91.8659 | 91.1894 | [6 empty] | 2021-05-06
id | item | Zone4C(OR-Portland-OR) ASHRAE901-state_STD2016 | Zone4C(OR-Portland-OR) ASHRAE901-state_STD2019 | Zone5B(OR-Redmond-OR) ASHRAE901-state_STD2016 | Zone5B(OR-Redmond-OR) ASHRAE901-state_STD2019 | [6 empty] | 2021-05-06
OR_MA_SPLIT GSW COOLING COIL Cooling Capacity [ton] | SPLIT GSW COOLING COIL Cooling Capacity [ton] | 0.7884 | 0.77005 | 0.73294 | 0.71511 | [6 empty] | 2021-05-06
OR_MA_SPLIT GNW COOLING COIL Cooling Capacity [ton] | SPLIT GNW COOLING COIL Cooling Capacity [ton] | 0.67215 | 0.65883 | 0.67682 | 0.65992 | [6 empty] | 2021-05-06
OR_MA_SPLIT OFFICE COOLING COIL Cooling Capacity [ton] | SPLIT OFFICE COOLING COIL Cooling Capacity [ton] | 1.6526 | 1.5019 | 1.5696 | 1.3912 | [6 empty] | 2021-05-06
OR_MA_SPLIT GNE COOLING COIL Cooling Capacity [ton] | SPLIT GNE COOLING COIL Cooling Capacity [ton] | 0.55096 | 0.53978 | 0.53012 | 0.51592 | [6 empty] | 2021-05-06
OR_MA_SPLIT GN1 COOLING COIL Cooling Capacity [ton] | SPLIT GN1 COOLING COIL Cooling Capacity [ton] | 0.4592 | 0.45088 | 0.44172 | 0.43036 | [6 empty] | 2021-05-06
OR_MA_SPLIT GN2 COOLING COIL Cooling Capacity [ton] | SPLIT GN2 COOLING COIL Cooling Capacity [ton] | 0.45688 | 0.44862 | 0.43917 | 0.42789 | [6 empty] | 2021-05-06
OR_MA_SPLIT GS1 COOLING COIL Cooling Capacity [ton] | SPLIT GS1 COOLING COIL Cooling Capacity [ton] | 0.60757 | 0.56539 | 0.49866 | 0.4861 | [6 empty] | 2021-05-06
OR_MA_SPLIT GS2 COOLING COIL Cooling Capacity [ton] | SPLIT GS2 COOLING COIL Cooling Capacity [ton] | 0.65079 | 0.63092 | 0.53828 | 0.51997 | [6 empty] | 2021-05-06
OR_MA_SPLIT MSW COOLING COIL Cooling Capacity [ton] | SPLIT MSW COOLING COIL Cooling Capacity [ton] | 1.8888 | 1.8528 | 1.9423 | 1.9021 | [6 empty] | 2021-05-06
OR_MA_SPLIT MNW COOLING COIL Cooling Capacity [ton] | SPLIT MNW COOLING COIL Cooling Capacity [ton] | 1.6407 | 1.6103 | 1.829 | 1.7907 | [6 empty] | 2021-05-06
OR_MA_SPLIT MSE COOLING COIL Cooling Capacity [ton] | SPLIT MSE COOLING COIL Cooling Capacity [ton] | 1.7515 | 1.7119 | 1.5043 | 1.4695 | [6 empty] | 2021-05-06
OR_MA_SPLIT MNE COOLING COIL Cooling Capacity [ton] | SPLIT MNE COOLING COIL Cooling Capacity [ton] | 1.2406 | 1.2098 | 1.3244 | 1.298 | [6 empty] | 2021-05-06
OR_MA_SPLIT MN1 COOLING COIL Cooling Capacity [ton] | SPLIT MN1 COOLING COIL Cooling Capacity [ton] | 1.0085 | 0.98747 | 1.0686 | 1.0473 | [6 empty] | 2021-05-06
OR_MA_SPLIT MN2 COOLING COIL Cooling Capacity [ton] | SPLIT MN2 COOLING COIL Cooling Capacity [ton] | 1.0021 | 0.98656 | 1.0599 | 1.0388 | [6 empty] | 2021-05-06
OR_MA_SPLIT MS1 COOLING COIL Cooling Capacity [ton] | SPLIT MS1 COOLING COIL Cooling Capacity [ton] | 1.4142 | 1.3812 | 1.1698 | 1.1467 | [6 empty] | 2021-05-06
OR_MA_SPLIT MS2 COOLING COIL Cooling Capacity [ton] | SPLIT MS2 COOLING COIL Cooling Capacity [ton] | 1.419 | 1.3859 | 1.1623 | 1.1395 | [6 empty] | 2021-05-06
OR_MA_SPLIT TSW COOLING COIL Cooling Capacity [ton] | SPLIT TSW COOLING COIL Cooling Capacity [ton] | 1.166 | 1.1452 | 1.2402 | 1.2186 | [6 empty] | 2021-05-06
OR_MA_SPLIT TNW COOLING COIL Cooling Capacity [ton] | SPLIT TNW COOLING COIL Cooling Capacity [ton] | 1.0281 | 1.0115 | 1.1756 | 1.1548 | [6 empty] | 2021-05-06
OR_MA_SPLIT TSE COOLING COIL Cooling Capacity [ton] | SPLIT TSE COOLING COIL Cooling Capacity [ton] | 1.1144 | 1.0926 | 1.0149 | 0.99672 | [6 empty] | 2021-05-06
OR_MA_SPLIT TNE COOLING COIL Cooling Capacity [ton] | SPLIT TNE COOLING COIL Cooling Capacity [ton] | 0.84282 | 0.83099 | 0.89318 | 0.87856 | [6 empty] | 2021-05-06
OR_MA_SPLIT TN1 COOLING COIL Cooling Capacity [ton] | SPLIT TN1 COOLING COIL Cooling Capacity [ton] | 0.64694 | 0.63828 | 0.71195 | 0.70099 | [6 empty] | 2021-05-06
OR_MA_SPLIT TN2 COOLING COIL Cooling Capacity [ton] | SPLIT TN2 COOLING COIL Cooling Capacity [ton] | 0.67749 | 0.66839 | 0.70933 | 0.69802 | [6 empty] | 2021-05-06
OR_MA_SPLIT TS1 COOLING COIL Cooling Capacity [ton] | SPLIT TS1 COOLING COIL Cooling Capacity [ton] | 0.93897 | 0.92031 | 0.81708 | 0.80295 | [6 empty] | 2021-05-06
OR_MA_SPLIT TS2 COOLING COIL Cooling Capacity [ton] | SPLIT TS2 COOLING COIL Cooling Capacity [ton] | 0.94282 | 0.92411 | 0.82096 | 0.80659 | [6 empty] | 2021-05-06
OR_MA_Split GN1 Furnace with DX Cooling OA Rate [cfm] | Split GN1 Furnace with DX Cooling OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | [6 empty] | 2021-05-06
OR_MA_Split GN2 Furnace with DX Cooling OA Rate [cfm] | Split GN2 Furnace with DX Cooling OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | [6 empty] | 2021-05-06
OR_MA_Split GNE Furnace with DX Cooling OA Rate [cfm] | Split GNE Furnace with DX Cooling OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | [6 empty] | 2021-05-06
OR_MA_Split GNW Furnace with DX Cooling OA Rate [cfm] | Split GNW Furnace with DX Cooling OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | [6 empty] | 2021-05-06
OR_MA_Split GS1 Furnace with DX Cooling OA Rate [cfm] | Split GS1 Furnace with DX Cooling OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | [6 empty] | 2021-05-06
OR_MA_Split GS2 Furnace with DX Cooling OA Rate [cfm] | Split GS2 Furnace with DX Cooling OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | [6 empty] | 2021-05-06
OR_MA_Split GSW Furnace with DX Cooling OA Rate [cfm] | Split GSW Furnace with DX Cooling OA Rate [cfm] | 56.9945 | 56.9945 | 56.9945 | 56.9945 | [6 empty] | 2021-05-06
OR_MA_Split MN1 Furnace with DX Cooling OA Rate [cfm] | Split MN1 Furnace with DX Cooling OA Rate [cfm] | 109.9824 | 109.9824 | 109.9824 | 109.9824 | [6 empty] | 2021-05-06
OR_MA_Split MN2 Furnace with DX Cooling OA Rate [cfm] | Split MN2 Furnace with DX Cooling OA Rate [cfm] | 109.9824 | 109.9824 | 109.9824 | 109.9824 | [6 empty] | 2021-05-06
OR_MA_Split MNE Furnace with DX Cooling OA Rate [cfm] | Split MNE Furnace with DX Cooling OA Rate [cfm] | 109.9824 | 109.9824 | 109.9824 | 109.9824 | [6 empty] | 2021-05-06
OR_MA_Split MNW Furnace with DX Cooling OA Rate [cfm] | Split MNW Furnace with DX Cooling OA Rate [cfm] | 109.9824 | 109.9824 | 109.9824 | 109.9824 | [6 empty] | 2021-05-06
OR_MA_Split MS1 Furnace with DX Cooling OA Rate [cfm] | Split MS1 Furnace with DX Cooling OA Rate [cfm] | 109.9824 | 109.9824 | 109.9824 | 109.9824 | [6 empty] | 2021-05-06
OR_MA_Split MS2 Furnace with DX Cooling OA Rate [cfm] | Split MS2 Furnace with DX Cooling OA Rate [cfm] | 109.9824 | 109.9824 | 109.9824 | 109.9824 | [6 empty] | 2021-05-06
OR_MA_Split MSE Furnace with DX Cooling OA Rate [cfm] | Split MSE Furnace with DX Cooling OA Rate [cfm] | 109.9824 | 109.9824 | 109.9824 | 109.9824 | [6 empty] | 2021-05-06
OR_MA_Split MSW Furnace with DX Cooling OA Rate [cfm] | Split MSW Furnace with DX Cooling OA Rate [cfm] | 109.9824 | 109.9824 | 109.9824 | 109.9824 | [6 empty] | 2021-05-06
OR_MA_Split Office Furnace with DX Cooling OA Rate [cfm] | Split Office Furnace with DX Cooling OA Rate [cfm] | 80.7372 | 80.7372 | 80.7372 | 80.7372 | [6 empty] | 2021-05-06
OR_MA_Split TN1 Furnace with DX Cooling OA Rate [cfm] | Split TN1 Furnace with DX Cooling OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | [6 empty] | 2021-05-06
OR_MA_Split TN2 Furnace with DX Cooling OA Rate [cfm] | Split TN2 Furnace with DX Cooling OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | [6 empty] | 2021-05-06
OR_MA_Split TNE Furnace with DX Cooling OA Rate [cfm] | Split TNE Furnace with DX Cooling OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | [6 empty] | 2021-05-06
OR_MA_Split TNW Furnace with DX Cooling OA Rate [cfm] | Split TNW Furnace with DX Cooling OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | [6 empty] | 2021-05-06
OR_MA_Split TS1 Furnace with DX Cooling OA Rate [cfm] | Split TS1 Furnace with DX Cooling OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | [6 empty] | 2021-05-06
OR_MA_Split TS2 Furnace with DX Cooling OA Rate [cfm] | Split TS2 Furnace with DX Cooling OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | [6 empty] | 2021-05-06
OR_MA_Split TSE Furnace with DX Cooling OA Rate [cfm] | Split TSE Furnace with DX Cooling OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | [6 empty] | 2021-05-06
OR_MA_Split TSW Furnace with DX Cooling OA Rate [cfm] | Split TSW Furnace with DX Cooling OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | [6 empty] | 2021-05-06
OR_MA_SPLIT GSW HEATING COIL Heating Capacity [kBtu/hr] | SPLIT GSW HEATING COIL Heating Capacity [kBtu/hr] | 6.4343 | 6.492 | 7.9705 | 8.0304 | [6 empty] | 2021-05-06
OR_MA_SPLIT GNW HEATING COIL Heating Capacity [kBtu/hr] | SPLIT GNW HEATING COIL Heating Capacity [kBtu/hr] | 6.3378 | 6.3958 | 7.9007 | 7.9608 | [6 empty] | 2021-05-06
OR_MA_SPLIT OFFICE HEATING COIL Heating Capacity [kBtu/hr] | SPLIT OFFICE HEATING COIL Heating Capacity [kBtu/hr] | 16.8497 | 17.1798 | 19.8224 | 19.9548 | [6 empty] | 2021-05-06
OR_MA_SPLIT GNE HEATING COIL Heating Capacity [kBtu/hr] | SPLIT GNE HEATING COIL Heating Capacity [kBtu/hr] | 6.349 | 6.407 | 7.8852 | 7.9453 | [6 empty] | 2021-05-06
OR_MA_SPLIT GN1 HEATING COIL Heating Capacity [kBtu/hr] | SPLIT GN1 HEATING COIL Heating Capacity [kBtu/hr] | 4.7655 | 4.7655 | 5.829 | 5.8893 | [6 empty] | 2021-05-06
OR_MA_SPLIT GN2 HEATING COIL Heating Capacity [kBtu/hr] | SPLIT GN2 HEATING COIL Heating Capacity [kBtu/hr] | 4.7655 | 4.7655 | 5.8286 | 5.8888 | [6 empty] | 2021-05-06
OR_MA_SPLIT GS1 HEATING COIL Heating Capacity [kBtu/hr] | SPLIT GS1 HEATING COIL Heating Capacity [kBtu/hr] | 4.7655 | 4.7655 | 5.7886 | 5.8487 | [6 empty] | 2021-05-06
OR_MA_SPLIT GS2 HEATING COIL Heating Capacity [kBtu/hr] | SPLIT GS2 HEATING COIL Heating Capacity [kBtu/hr] | 4.9189 | 4.9805 | 6.2595 | 6.3231 | [6 empty] | 2021-05-06
OR_MA_SPLIT MSW HEATING COIL Heating Capacity [kBtu/hr] | SPLIT MSW HEATING COIL Heating Capacity [kBtu/hr] | 12.063 | 12.1946 | 13.6115 | 13.7424 | [6 empty] | 2021-05-06
OR_MA_SPLIT MNW HEATING COIL Heating Capacity [kBtu/hr] | SPLIT MNW HEATING COIL Heating Capacity [kBtu/hr] | 12.03 | 12.1615 | 13.6784 | 13.8088 | [6 empty] | 2021-05-06
OR_MA_SPLIT MSE HEATING COIL Heating Capacity [kBtu/hr] | SPLIT MSE HEATING COIL Heating Capacity [kBtu/hr] | 12.09 | 12.2216 | 13.5744 | 13.7052 | [6 empty] | 2021-05-06
OR_MA_SPLIT MNE HEATING COIL Heating Capacity [kBtu/hr] | SPLIT MNE HEATING COIL Heating Capacity [kBtu/hr] | 12.0571 | 12.1885 | 13.6412 | 13.7716 | [6 empty] | 2021-05-06
OR_MA_SPLIT MN1 HEATING COIL Heating Capacity [kBtu/hr] | SPLIT MN1 HEATING COIL Heating Capacity [kBtu/hr] | 9.531 | 9.531 | 10.503 | 10.503 | [6 empty] | 2021-05-06
OR_MA_SPLIT MN2 HEATING COIL Heating Capacity [kBtu/hr] | SPLIT MN2 HEATING COIL Heating Capacity [kBtu/hr] | 9.531 | 9.531 | 10.503 | 10.503 | [6 empty] | 2021-05-06
OR_MA_SPLIT MS1 HEATING COIL Heating Capacity [kBtu/hr] | SPLIT MS1 HEATING COIL Heating Capacity [kBtu/hr] | 9.531 | 9.531 | 10.503 | 10.503 | [6 empty] | 2021-05-06
OR_MA_SPLIT MS2 HEATING COIL Heating Capacity [kBtu/hr] | SPLIT MS2 HEATING COIL Heating Capacity [kBtu/hr] | 9.531 | 9.531 | 10.503 | 10.503 | [6 empty] | 2021-05-06
OR_MA_SPLIT TSW HEATING COIL Heating Capacity [kBtu/hr] | SPLIT TSW HEATING COIL Heating Capacity [kBtu/hr] | 8.7933 | 8.8546 | 10.0027 | 10.0646 | [6 empty] | 2021-05-06
OR_MA_SPLIT TNW HEATING COIL Heating Capacity [kBtu/hr] | SPLIT TNW HEATING COIL Heating Capacity [kBtu/hr] | 8.782 | 8.8434 | 10.0447 | 10.1066 | [6 empty] | 2021-05-06
OR_MA_SPLIT TSE HEATING COIL Heating Capacity [kBtu/hr] | SPLIT TSE HEATING COIL Heating Capacity [kBtu/hr] | 8.8074 | 8.8686 | 9.9828 | 10.0446 | [6 empty] | 2021-05-06
OR_MA_SPLIT TNE HEATING COIL Heating Capacity [kBtu/hr] | SPLIT TNE HEATING COIL Heating Capacity [kBtu/hr] | 8.7961 | 8.8574 | 10.0247 | 10.0867 | [6 empty] | 2021-05-06
OR_MA_SPLIT TN1 HEATING COIL Heating Capacity [kBtu/hr] | SPLIT TN1 HEATING COIL Heating Capacity [kBtu/hr] | 6.4972 | 6.5583 | 7.8838 | 7.9457 | [6 empty] | 2021-05-06
OR_MA_SPLIT TN2 HEATING COIL Heating Capacity [kBtu/hr] | SPLIT TN2 HEATING COIL Heating Capacity [kBtu/hr] | 6.4976 | 6.5588 | 7.8832 | 7.9451 | [6 empty] | 2021-05-06
OR_MA_SPLIT TS1 HEATING COIL Heating Capacity [kBtu/hr] | SPLIT TS1 HEATING COIL Heating Capacity [kBtu/hr] | 6.5017 | 6.5627 | 7.835 | 7.8968 | [6 empty] | 2021-05-06
OR_MA_SPLIT TS2 HEATING COIL Heating Capacity [kBtu/hr] | SPLIT TS2 HEATING COIL Heating Capacity [kBtu/hr] | 6.5021 | 6.5631 | 7.8344 | 7.8962 | [6 empty] | 2021-05-06
OR_MA_Split_GSW ERV Flag | Split_GSW ERV Flag | No | Yes | No | Yes | [6 empty] | 2021-05-06
OR_MA_Split_GNW ERV Flag | Split_GNW ERV Flag | No | Yes | No | Yes | [6 empty] | 2021-05-06
OR_MA_Split_GNE ERV Flag | Split_GNE ERV Flag | No | Yes | No | Yes | [6 empty] | 2021-05-06
OR_MA_Split_GN1 ERV Flag | Split_GN1 ERV Flag | No | Yes | No | Yes | [6 empty] | 2021-05-06
OR_MA_Split_GN2 ERV Flag | Split_GN2 ERV Flag | No | Yes | No | Yes | [6 empty] | 2021-05-06
OR_MA_Split_GS1 ERV Flag | Split_GS1 ERV Flag | No | Yes | No | Yes | [6 empty] | 2021-05-06
OR_MA_Split_GS2 ERV Flag | Split_GS2 ERV Flag | No | Yes | No | Yes | [6 empty] | 2021-05-06
OR_MA_Split_MSW ERV Flag | Split_MSW ERV Flag | No | Yes | No | Yes | [6 empty] | 2021-05-06
OR_MA_Split_MNW ERV Flag | Split_MNW ERV Flag | No | Yes | No | Yes | [6 empty] | 2021-05-06
OR_MA_Split_MSE ERV Flag | Split_MSE ERV Flag | No | Yes | No | Yes | [6 empty] | 2021-05-06
OR_MA_Split_MNE ERV Flag | Split_MNE ERV Flag | No | Yes | No | Yes | [6 empty] | 2021-05-06
OR_MA_Split_MN1 ERV Flag | Split_MN1 ERV Flag | No | Yes | No | Yes | [6 empty] | 2021-05-06
OR_MA_Split_MN2 ERV Flag | Split_MN2 ERV Flag | No | Yes | No | Yes | [6 empty] | 2021-05-06
OR_MA_Split_MS1 ERV Flag | Split_MS1 ERV Flag | No | Yes | No | Yes | [6 empty] | 2021-05-06
OR_MA_Split_MS2 ERV Flag | Split_MS2 ERV Flag | No | Yes | No | Yes | [6 empty] | 2021-05-06
OR_MA_Split_TSW ERV Flag | Split_TSW ERV Flag | No | Yes | No | No | [6 empty] | 2021-05-06
OR_MA_Split_TNW ERV Flag | Split_TNW ERV Flag | No | Yes | No | Yes | [6 empty] | 2021-05-06
OR_MA_Split_TSE ERV Flag | Split_TSE ERV Flag | No | Yes | No | Yes | [6 empty] | 2021-05-06
OR_MA_Split_TNE ERV Flag | Split_TNE ERV Flag | No | Yes | No | Yes | [6 empty] | 2021-05-06
OR_MA_Split_TN1 ERV Flag | Split_TN1 ERV Flag | No | Yes | No | Yes | [6 empty] | 2021-05-06
OR_MA_Split_TN2 ERV Flag | Split_TN2 ERV Flag | No | Yes | No | Yes | [6 empty] | 2021-05-06
OR_MA_Split_TS1 ERV Flag | Split_TS1 ERV Flag | No | Yes | No | Yes | [6 empty] | 2021-05-06
OR_MA_Split_TS2 ERV Flag | Split_TS2 ERV Flag | No | Yes | No | Yes | [6 empty] | 2021-05-06
id | item | Zone4A(PA-Philadelphia-PA) ASHRAE901-state_STD2016 | Zone4A(PA-Philadelphia-PA) ASHRAE901-state_STD2019 | Zone5A(PA-Pittsburgh-PA) ASHRAE901-state_STD2016 | Zone5A(PA-Pittsburgh-PA) ASHRAE901-state_STD2019 | [6 empty] | 2021-05-06
PA_SO_PSZ-AC:1 Cooling Capacity [ton] | PSZ-AC:1 Cooling Capacity [ton] | 1.9081 | 1.815 | 1.7871 | 1.6908 | [6 empty] | 2021-05-06
PA_SO_PSZ-AC:2 Cooling Capacity [ton] | PSZ-AC:2 Cooling Capacity [ton] | 1.6937 | 1.6308 | 1.5246 | 1.463 | [6 empty] | 2021-05-06
PA_SO_PSZ-AC:3 Cooling Capacity [ton] | PSZ-AC:3 Cooling Capacity [ton] | 1.1414 | 1.1027 | 1.0865 | 1.0481 | [6 empty] | 2021-05-06
PA_SO_PSZ-AC:4 Cooling Capacity [ton] | PSZ-AC:4 Cooling Capacity [ton] | 1.6228 | 1.5539 | 1.4683 | 1.3872 | [6 empty] | 2021-05-06
PA_SO_PSZ-AC:5 Cooling Capacity [ton] | PSZ-AC:5 Cooling Capacity [ton] | 1.342 | 1.2995 | 1.2735 | 1.2342 | [6 empty] | 2021-05-06
PA_SO_PSZ-AC:1 Supply Flow Rate [cfm] | PSZ-AC:1 Supply Flow Rate [cfm] | 635.664 | 593.2864 | 656.8528 | 614.4752 | [6 empty] | 2021-05-06
PA_SO_PSZ-AC:2 Supply Flow Rate [cfm] | PSZ-AC:2 Supply Flow Rate [cfm] | 593.2864 | 572.0976 | 572.0976 | 550.9088 | [6 empty] | 2021-05-06
PA_SO_PSZ-AC:3 Supply Flow Rate [cfm] | PSZ-AC:3 Supply Flow Rate [cfm] | 444.9648 | 423.776 | 466.1536 | 444.9648 | [6 empty] | 2021-05-06
PA_SO_PSZ-AC:4 Supply Flow Rate [cfm] | PSZ-AC:4 Supply Flow Rate [cfm] | 572.0976 | 529.72 | 550.9088 | 508.5312 | [6 empty] | 2021-05-06
PA_SO_PSZ-AC:5 Supply Flow Rate [cfm] | PSZ-AC:5 Supply Flow Rate [cfm] | 529.72 | 508.5312 | 550.9088 | 529.72 | [6 empty] | 2021-05-06
PA_SO_PSZ-AC:1 OA Rate [cfm] | PSZ-AC:1 OA Rate [cfm] | 136.9178 | 136.9178 | 136.9178 | 136.9178 | [6 empty] | 2021-05-06
PA_SO_PSZ-AC:2 OA Rate [cfm] | PSZ-AC:2 OA Rate [cfm] | 103.7925 | 103.7925 | 103.7925 | 103.7925 | [6 empty] | 2021-05-06
PA_SO_PSZ-AC:3 OA Rate [cfm] | PSZ-AC:3 OA Rate [cfm] | 61.5711 | 61.5711 | 61.5711 | 61.5711 | [6 empty] | 2021-05-06
PA_SO_PSZ-AC:4 OA Rate [cfm] | PSZ-AC:4 OA Rate [cfm] | 103.7925 | 103.7925 | 103.7925 | 103.7925 | [6 empty] | 2021-05-06
PA_SO_PSZ-AC:5 OA Rate [cfm] | PSZ-AC:5 OA Rate [cfm] | 61.5711 | 61.5711 | 61.5711 | 61.5711 | [6 empty] | 2021-05-06
PA_SO_PSZ-AC:1 heating Capacity [kBtu/hr] | PSZ-AC:1 heating Capacity [kBtu/hr] | 13.5514 | 13.5514 | 14.2556 | 14.2556 | [6 empty] | 2021-05-06
PA_SO_PSZ-AC:2 heating Capacity [kBtu/hr] | PSZ-AC:2 heating Capacity [kBtu/hr] | 18.5751 | 18.3836 | 19.7423 | 19.5151 | [6 empty] | 2021-05-06
PA_SO_PSZ-AC:3 heating Capacity [kBtu/hr] | PSZ-AC:3 heating Capacity [kBtu/hr] | 11.3978 | 11.292 | 11.9643 | 11.844 | [6 empty] | 2021-05-06
PA_SO_PSZ-AC:4 heating Capacity [kBtu/hr] | PSZ-AC:4 heating Capacity [kBtu/hr] | 18.4867 | 18.3224 | 19.4546 | 19.2767 | [6 empty] | 2021-05-06
PA_SO_PSZ-AC:5 heating Capacity [kBtu/hr] | PSZ-AC:5 heating Capacity [kBtu/hr] | 11.4455 | 11.3344 | 12.0169 | 11.8913 | [6 empty] | 2021-05-06
id | item | Zone4A(PA-Philadelphia-PA) ASHRAE901-state_STD2016 | Zone4A(PA-Philadelphia-PA) ASHRAE901-state_STD2019 | Zone5A(PA-Pittsburgh-PA) ASHRAE901-state_STD2016 | Zone5A(PA-Pittsburgh-PA) ASHRAE901-state_STD2019 | [6 empty] | 2021-05-06
PA_LO_CAV_BAS Supply Flow Rate [cfm] | CAV_BAS Supply Flow Rate [cfm] | 11653.84 | 10785.0992 | 12056.4272 | 11166.4976 | [6 empty] | 2021-05-06
PA_LO_VAV_BOT WITH REHEAT Supply Flow Rate [cfm] | VAV_BOT WITH REHEAT Supply Flow Rate [cfm] | 19642.0176 | 18709.7104 | 20150.5488 | 19175.864 | [6 empty] | 2021-05-06
PA_LO_VAV_MID WITH REHEAT Supply Flow Rate [cfm] | VAV_MID WITH REHEAT Supply Flow Rate [cfm] | 183007.6659 | 174129.5587 | 186779.2723 | 177583.3331 | [6 empty] | 2021-05-06
PA_LO_VAV_TOP WITH REHEAT Supply Flow Rate [cfm] | VAV_TOP WITH REHEAT Supply Flow Rate [cfm] | 19324.1856 | 18540.2 | 19811.528 | 19006.3536 | [6 empty] | 2021-05-06
PA_LO_Supply Air Temp. Reset Flag | Supply Air Temp. Reset Flag | Yes | Yes | Yes | Yes | [6 empty] | 2021-05-06
PA_LO_CAV_BAS OA Rate [cfm] | CAV_BAS OA Rate [cfm] | 2542.8255 | 2542.8255 | 2542.8255 | 2542.8255 | [6 empty] | 2021-05-06
PA_LO_VAV_BOT WITH REHEAT OA Rate [cfm] | VAV_BOT WITH REHEAT OA Rate [cfm] | 5377.8022 | 4302.174 | 5377.8022 | 4302.174 | [6 empty] | 2021-05-06
PA_LO_VAV_MID WITH REHEAT OA Rate [cfm] | VAV_MID WITH REHEAT OA Rate [cfm] | 53777.9373 | 43021.7396 | 53777.9373 | 43021.7396 | [6 empty] | 2021-05-06
PA_LO_VAV_TOP WITH REHEAT OA Rate [cfm] | VAV_TOP WITH REHEAT OA Rate [cfm] | 5377.8022 | 4302.174 | 5377.8022 | 4302.174 | [6 empty] | 2021-05-06
PA_LO_AIRLOOP DATACENTER BASEMENT OA Rate [cfm] | AIRLOOP DATACENTER BASEMENT OA Rate [cfm] | 716.9654 | 716.9654 | 716.9654 | 716.9654 | [6 empty] | 2021-05-06
PA_LO_VAV_bot_WITH_REHEAT ERV Flag | VAV_bot_WITH_REHEAT ERV Flag | Yes | Yes | Yes | Yes | [6 empty] | 2021-05-06
PA_LO_VAV_mid_WITH_REHEAT ERV Flag | VAV_mid_WITH_REHEAT ERV Flag | Yes | Yes | Yes | Yes | [6 empty] | 2021-05-06
PA_LO_VAV_top_WITH_REHEAT ERV Flag | VAV_top_WITH_REHEAT ERV Flag | Yes | Yes | Yes | Yes | [6 empty] | 2021-05-06
PA_LO_COOLSYS1 CHILLER1 Capacity [ton] | COOLSYS1 CHILLER1 Capacity [ton] | 425.6481 | 383.6217 | 389.5913 | 353.3461 | [6 empty] | 2021-05-06
PA_LO_COOLSYS1 CHILLER2 Capacity [ton] | COOLSYS1 CHILLER2 Capacity [ton] | 425.6481 | 383.6217 | 389.5913 | 353.3461 | [6 empty] | 2021-05-06
PA_LO_TOWERWATERSYS COOLTOWER 1 Capacity [ton] | TOWERWATERSYS COOLTOWER 1 Capacity [ton] | 404.0232 | 364.1303 | 369.788 | 335.3952 | [6 empty] | 2021-05-06
PA_LO_TOWERWATERSYS COOLTOWER 2 Capacity [ton] | TOWERWATERSYS COOLTOWER 2 Capacity [ton] | 404.0232 | 364.1303 | 369.788 | 335.3952 | [6 empty] | 2021-05-06
PA_LO_HEATSYS1 BOILER Capacity [MMBTU/h] | HEATSYS1 BOILER Capacity [MMBTU/h] | 4152.6254 | 3690.0492 | 4462.6288 | 3946.5572 | [6 empty] | 2021-05-06
PA_LO_COOLSYS1 PUMP Flow Rate [gal/min] | COOLSYS1 PUMP Flow Rate [gal/min] | 0 | 0 | 0 | 0 | [6 empty] | 2021-05-06
PA_LO_COOLSYS1 CHILLER1 PUMP Flow Rate [gal/min] | COOLSYS1 CHILLER1 PUMP Flow Rate [gal/min] | 670.8348 | 601.6973 | 613.6896 | 556.4842 | [6 empty] | 2021-05-06
PA_LO_COOLSYS1 CHILLER2 PUMP Flow Rate [gal/min] | COOLSYS1 CHILLER2 PUMP Flow Rate [gal/min] | 670.8348 | 601.6973 | 613.6896 | 556.4842 | [6 empty] | 2021-05-06
PA_LO_COOLSYS1 PUMP SECONDARY Flow Rate [gal/min] | COOLSYS1 PUMP SECONDARY Flow Rate [gal/min] | 1341.668 | 1203.3946 | 1227.3777 | 1112.9701 | [6 empty] | 2021-05-06
PA_LO_HEATSYS1 PUMP Flow Rate [gal/min] | HEATSYS1 PUMP Flow Rate [gal/min] | 852.3812 | 757.4315 | 916.0139 | 810.0831 | [6 empty] | 2021-05-06
PA_LO_TOWERWATERSYS PUMP Flow Rate [gal/min] | TOWERWATERSYS PUMP Flow Rate [gal/min] | 2348.3839 | 2116.4936 | 2149.4623 | 1949.4312 | [6 empty] | 2021-05-06
PA_LO_PLANT CIRC PUMP Flow Rate [gal/min] | PLANT CIRC PUMP Flow Rate [gal/min] | 208.2098 | 207.3809 | 210.7839 | 209.9391 | [6 empty] | 2021-05-06
PA_LO_COOLSYS1 PUMP SECONDARY Pressure setpoint reset [yes,no] | COOLSYS1 PUMP SECONDARY Pressure setpoint reset [yes,no] | pump_ride_on_curve | pump_ride_on_curve | pump_ride_on_curve | pump_ride_on_curve | [6 empty] | 2021-05-06
PA_LO_COOLSYS1 CHILLER1 PUMP Pump Power [hp] | COOLSYS1 CHILLER1 PUMP Pump Power [hp] | 3.6189 | 3.2138 | 3.3106 | 2.9723 | [6 empty] | 2021-05-06
PA_LO_COOLSYS1 CHILLER2 PUMP Pump Power [hp] | COOLSYS1 CHILLER2 PUMP Pump Power [hp] | 3.6189 | 3.2138 | 3.3106 | 2.9723 | [6 empty] | 2021-05-06
PA_LO_COOLSYS1 PUMP SECONDARY Pump Power [hp] | COOLSYS1 PUMP SECONDARY Pump Power [hp] | 21.7135 | 19.2829 | 19.8638 | 17.8339 | [6 empty] | 2021-05-06
PA_LO_HEATSYS1 PUMP Pump Power [hp] | HEATSYS1 PUMP Pump Power [hp] | 18.4247 | 16.2102 | 19.8002 | 17.337 | [6 empty] | 2021-05-06
PA_LO_TOWERWATERSYS PUMP Pump Power [hp] | TOWERWATERSYS PUMP Pump Power [hp] | 42.0446 | 37.5182 | 38.483 | 34.5572 | [6 empty] | 2021-05-06
PA_LO_PLANT CIRC PUMP Pump Power [hp] | PLANT CIRC PUMP Pump Power [hp] | 4.4929 | 4.4307 | 4.5484 | 4.4853 | [6 empty] | 2021-05-06
PA_LO_Datacenter PLANT CIRC PUMP Pump Power [hp] | Datacenter PLANT CIRC PUMP Pump Power [hp] | 4.4929 | 4.4307 | 4.5484 | 4.4853 | [6 empty] | 2021-05-06
PA_LO_ZN_VAV_BOXes_Max_Reheat_Water_Flow_GPM | ZN_VAV_BOXes_Max_Reheat_Water_Flow_GPM | 451.1736 | 434.6526 | 466.1073 | 447.9179 | [6 empty] | 2021-05-06
PA_LO_COOLSYS1 PUMP SECONDARY VSD | COOLSYS1 PUMP SECONDARY VSD | No | No | No | No | [6 empty] | 2021-05-06
PA_LO_HEATSYS1 PUMP VSD | HEATSYS1 PUMP VSD | No | No | No | No | [6 empty] | 2021-05-06
PA_LO_DATACENTER BASEMENT Cooling Capacity [ton] | DATACENTER BASEMENT Cooling Capacity [ton] | 121.9095 | 121.5491 | 123.1812 | 122.8159 | [6 empty] | 2021-05-06
PA_LO_DATACENTER BOT Cooling Capacity [ton] | DATACENTER BOT Cooling Capacity [ton] | 2.6523 | 2.629 | 2.7023 | 2.6785 | [6 empty] | 2021-05-06
PA_LO_DATACENTER MID Cooling Capacity [ton] | DATACENTER MID Cooling Capacity [ton] | 25.371 | 25.1669 | 25.8844 | 25.6746 | [6 empty] | 2021-05-06
PA_LO_DATACENTER TOP Cooling Capacity [ton] | DATACENTER TOP Cooling Capacity [ton] | 2.5858 | 2.566 | 2.6357 | 2.6155 | [6 empty] | 2021-05-06
id | item | Zone4A(PA-Philadelphia-PA) ASHRAE901-state_STD2016 | Zone4A(PA-Philadelphia-PA) ASHRAE901-state_STD2019 | Zone5A(PA-Pittsburgh-PA) ASHRAE901-state_STD2016 | Zone5A(PA-Pittsburgh-PA) ASHRAE901-state_STD2019 | [6 empty] | 2021-05-06
PA_RS_PSZ-AC:1 Cooling Capacity [ton] | PSZ-AC:1 Cooling Capacity [ton] | 10.7497 | 10.4069 | 9.9665 | 9.5661 | [6 empty] | 2021-05-06
PA_RS_PSZ-AC:2 Cooling Capacity [ton] | PSZ-AC:2 Cooling Capacity [ton] | 50.9909 | 48.4938 | 46.8162 | 44.9445 | [6 empty] | 2021-05-06
PA_RS_PSZ-AC:3 Cooling Capacity [ton] | PSZ-AC:3 Cooling Capacity [ton] | 6.7017 | 6.5406 | 6.1009 | 5.9405 | [6 empty] | 2021-05-06
PA_RS_PSZ-AC:4 Cooling Capacity [ton] | PSZ-AC:4 Cooling Capacity [ton] | 5.4966 | 5.3395 | 4.8966 | 4.7223 | [6 empty] | 2021-05-06
PA_RS_PSZ-AC:1 Supply Flow Rate [cfm] | PSZ-AC:1 Supply Flow Rate [cfm] | 4047.0608 | 3792.7952 | 3962.3056 | 3665.6624 | [6 empty] | 2021-05-06
PA_RS_PSZ-AC:2 Supply Flow Rate [cfm] | PSZ-AC:2 Supply Flow Rate [cfm] | 15340.6912 | 14556.7056 | 15552.5792 | 14662.6496 | [6 empty] | 2021-05-06
PA_RS_PSZ-AC:3 Supply Flow Rate [cfm] | PSZ-AC:3 Supply Flow Rate [cfm] | 2330.768 | 2246.0128 | 2288.3904 | 2203.6352 | [6 empty] | 2021-05-06
PA_RS_PSZ-AC:4 Supply Flow Rate [cfm] | PSZ-AC:4 Supply Flow Rate [cfm] | 1801.048 | 1716.2928 | 1716.2928 | 1652.7264 | [6 empty] | 2021-05-06
PA_RS_PSZ-AC:1 OA Rate [cfm] | PSZ-AC:1 OA Rate [cfm] | 490.669 | 490.669 | 490.669 | 490.669 | [6 empty] | 2021-05-06
PA_RS_PSZ-AC:2 OA Rate [cfm] | PSZ-AC:2 OA Rate [cfm] | 4005.1282 | 4005.1282 | 4005.1282 | 4005.1282 | [6 empty] | 2021-05-06
PA_RS_PSZ-AC:3 OA Rate [cfm] | PSZ-AC:3 OA Rate [cfm] | 377.3937 | 377.3937 | 377.3937 | 377.3937 | [6 empty] | 2021-05-06
PA_RS_PSZ-AC:4 OA Rate [cfm] | PSZ-AC:4 OA Rate [cfm] | 377.3937 | 377.3937 | 377.3937 | 377.3937 | [6 empty] | 2021-05-06
PA_RS_PSZ-AC:1 OA Damper [gravity, motorized] | PSZ-AC:1 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2021-05-06
PA_RS_PSZ-AC:2 OA Damper [gravity, motorized] | PSZ-AC:2 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2021-05-06
PA_RS_PSZ-AC:3 OA Damper [gravity, motorized] | PSZ-AC:3 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2021-05-06
PA_RS_PSZ-AC:4 OA Damper [gravity, motorized] | PSZ-AC:4 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2021-05-06
PA_RS_PSZ-AC:1 Heating Capacity [kBtu/hr] | PSZ-AC:1 Heating Capacity [kBtu/hr] | 179.6858 | 169.3694 | 173.2632 | 161.598 | [6 empty] | 2021-05-06
PA_RS_PSZ-AC:2 Heating Capacity [kBtu/hr] | PSZ-AC:2 Heating Capacity [kBtu/hr] | 802.6376 | 769.3517 | 814.7737 | 778.0039 | [6 empty] | 2021-05-06
PA_RS_PSZ-AC:3 Heating Capacity [kBtu/hr] | PSZ-AC:3 Heating Capacity [kBtu/hr] | 109.8796 | 107.1884 | 107.171 | 104.471 | [6 empty] | 2021-05-06
PA_RS_PSZ-AC:4 Heating Capacity [kBtu/hr] | PSZ-AC:4 Heating Capacity [kBtu/hr] | 89.9351 | 87.0942 | 86.8284 | 83.6636 | [6 empty] | 2021-05-06
id | item | Zone4A(PA-Philadelphia-PA) ASHRAE901-state_STD2016 | Zone4A(PA-Philadelphia-PA) ASHRAE901-state_STD2019 | Zone5A(PA-Pittsburgh-PA) ASHRAE901-state_STD2016 | Zone5A(PA-Pittsburgh-PA) ASHRAE901-state_STD2019 | [6 empty] | 2021-05-06
PA_PS_VAV_POD_1 Cooling Capacity [ton] | VAV_POD_1 Cooling Capacity [ton] | 19.1675 | 18.5146 | 19.2922 | 18.5917 | [6 empty] | 2021-05-06
PA_PS_VAV_POD_2 Cooling Capacity [ton] | VAV_POD_2 Cooling Capacity [ton] | 18.8719 | 18.3687 | 19.0113 | 18.4805 | [6 empty] | 2021-05-06
PA_PS_VAV_POD_3 Cooling Capacity [ton] | VAV_POD_3 Cooling Capacity [ton] | 17.4084 | 16.6295 | 17.5728 | 16.7439 | [6 empty] | 2021-05-06
PA_PS_VAV_OTHER Cooling Capacity [ton] | VAV_OTHER Cooling Capacity [ton] | 26.5357 | 25.0248 | 27.1456 | 25.5085 | [6 empty] | 2021-05-06
PA_PS_PSZ-AC_1:6 Cooling Capacity [ton] | PSZ-AC_1:6 Cooling Capacity [ton] | 8.4566 | 8.09 | 8.1327 | 7.87 | [6 empty] | 2021-05-06
PA_PS_PSZ-AC_2:5 Cooling Capacity [ton] | PSZ-AC_2:5 Cooling Capacity [ton] | 5.325 | 5.4084 | 5.5896 | 5.5665 | [6 empty] | 2021-05-06
PA_PS_PSZ-AC_2:7 Cooling Capacity [ton] | PSZ-AC_2:7 Cooling Capacity [ton] | 10.5074 | 10.5074 | 10.5074 | 10.5074 | [6 empty] | 2021-05-06
PA_PS_VAV_POD_1 Supply Flow Rate [cfm] | VAV_POD_1 Supply Flow Rate [cfm] | 5742.1648 | 5551.4656 | 5784.5424 | 5572.6544 | [6 empty] | 2021-05-06
PA_PS_VAV_POD_2 Supply Flow Rate [cfm] | VAV_POD_2 Supply Flow Rate [cfm] | 5657.4096 | 5509.088 | 5699.7872 | 5551.4656 | [6 empty] | 2021-05-06
PA_PS_VAV_POD_3 Supply Flow Rate [cfm] | VAV_POD_3 Supply Flow Rate [cfm] | 5233.6336 | 5000.5568 | 5276.0112 | 5021.7456 | [6 empty] | 2021-05-06
PA_PS_VAV_OTHER Supply Flow Rate [cfm] | VAV_OTHER Supply Flow Rate [cfm] | 7966.9888 | 7500.8352 | 8136.4992 | 7649.1568 | [6 empty] | 2021-05-06
PA_PS_PSZ-AC_2:5 Supply Flow Rate [cfm] | PSZ-AC_2:5 Supply Flow Rate [cfm] | 1589.16 | 1631.5376 | 1673.9152 | 1673.9152 | [6 empty] | 2021-05-06
PA_PS_PSZ-AC_1:6 Supply Flow Rate [cfm] | PSZ-AC_1:6 Supply Flow Rate [cfm] | 2542.656 | 2436.712 | 2627.4112 | 2521.4672 | [6 empty] | 2021-05-06
PA_PS_PSZ-AC_2:7 Supply Flow Rate [cfm] | PSZ-AC_2:7 Supply Flow Rate [cfm] | 3157.1312 | 3157.1312 | 3157.1312 | 3157.1312 | [6 empty] | 2021-05-06
PA_PS_Supply Air Temp. Reset Flag | Supply Air Temp. Reset Flag | Yes | Yes | Yes | Yes | [6 empty] | 2021-05-06
PA_PS_VAV_POD_1 OA Rate [cfm] | VAV_POD_1 OA Rate [cfm] | 5751.8693 | 5555.9153 | 5789.2887 | 5579.0534 | [6 empty] | 2021-05-06
PA_PS_VAV_POD_2 OA Rate [cfm] | VAV_POD_2 OA Rate [cfm] | 5663.1306 | 5512.1392 | 5704.9997 | 5545.7023 | [6 empty] | 2021-05-06
PA_PS_VAV_POD_3 OA Rate [cfm] | VAV_POD_3 OA Rate [cfm] | 5222.4247 | 4990.2591 | 5273.3202 | 5024.5637 | [6 empty] | 2021-05-06
PA_PS_VAV_OTHER OA Rate [cfm] | VAV_OTHER OA Rate [cfm] | 3736.1787 | 2988.8921 | 3736.1787 | 2988.8921 | [6 empty] | 2021-05-06
PA_PS_PSZ-AC_2:5 OA Rate [cfm] | PSZ-AC_2:5 OA Rate [cfm] | 1152.7343 | 1152.7343 | 1152.7343 | 1152.7343 | [6 empty] | 2021-05-06
PA_PS_PSZ-AC_1:6 OA Rate [cfm] | PSZ-AC_1:6 OA Rate [cfm] | 539.9118 | 539.9118 | 539.9118 | 539.9118 | [6 empty] | 2021-05-06
PA_PS_PSZ-AC_2:7 OA Rate [cfm] | PSZ-AC_2:7 OA Rate [cfm] | 3153.0841 | 3153.0841 | 3153.0841 | 3153.0841 | [6 empty] | 2021-05-06
PA_PS_VAV_POD_1 OA Damper [gravity, motorized] | VAV_POD_1 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2021-05-06
PA_PS_VAV_POD_2 OA Damper [gravity, motorized] | VAV_POD_2 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2021-05-06
PA_PS_VAV_POD_3 OA Damper [gravity, motorized] | VAV_POD_3 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2021-05-06
PA_PS_VAV_OTHER OA Damper [gravity, motorized] | VAV_OTHER OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2021-05-06
PA_PS_PSZ-AC_2:5 OA Damper [gravity, motorized] | PSZ-AC_2:5 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2021-05-06
PA_PS_PSZ-AC_1:6 OA Damper [gravity, motorized] | PSZ-AC_1:6 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2021-05-06
PA_PS_PSZ-AC_2:7 OA Damper [gravity, motorized] | PSZ-AC_2:7 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2021-05-06
PA_PS_VAV_POD_1 (economizer) | VAV_POD_1 (economizer) | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialDryBulb | DifferentialDryBulb | [6 empty] | 2021-05-06
PA_PS_VAV_POD_2 (economizer) | VAV_POD_2 (economizer) | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialDryBulb | DifferentialDryBulb | [6 empty] | 2021-05-06
PA_PS_VAV_POD_3 (economizer) | VAV_POD_3 (economizer) | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialDryBulb | DifferentialDryBulb | [6 empty] | 2021-05-06
PA_PS_VAV_OTHER (economizer) | VAV_OTHER (economizer) | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialDryBulb | DifferentialDryBulb | [6 empty] | 2021-05-06
PA_PS_PSZ-AC_2:5 (economizer) | PSZ-AC_2:5 (economizer) | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialDryBulb | DifferentialDryBulb | [6 empty] | 2021-05-06
PA_PS_PSZ-AC_1:6 (economizer) | PSZ-AC_1:6 (economizer) | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialDryBulb | DifferentialDryBulb | [6 empty] | 2021-05-06
PA_PS_PSZ-AC_2:7 (economizer) | PSZ-AC_2:7 (economizer) | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialDryBulb | DifferentialDryBulb | [6 empty] | 2021-05-06
PA_PS_VAV_Pod_1_ERV Flag | VAV_Pod_1_ERV Flag | Yes | Yes | Yes | Yes | [6 empty] | 2021-05-06
PA_PS_VAV_Pod_2_ERV Flag | VAV_Pod_2_ERV Flag | Yes | Yes | Yes | Yes | [6 empty] | 2021-05-06
PA_PS_VAV_Pod_3_ERV Flag | VAV_Pod_3_ERV Flag | Yes | Yes | Yes | Yes | [6 empty] | 2021-05-06
PA_PS_VAV_OTHER_ERV Flag | VAV_OTHER_ERV Flag | Yes | Yes | Yes | Yes | [6 empty] | 2021-05-06
PA_PS_PSZ_AC_2_5_ERV Flag | PSZ_AC_2_5_ERV Flag | Yes | Yes | No | No | [6 empty] | 2021-05-06
PA_PS_PSZ_AC_2_7_ERV Flag | PSZ_AC_2_7_ERV Flag | Yes | Yes | Yes | Yes | [6 empty] | 2021-05-06
PA_PS_HEATSYS1 Capacity [MMBTU/h] | HEATSYS1 Capacity [MMBTU/h] | 1.0116 | 0.96671 | 1.0921 | 1.0467 | [6 empty] | 2021-05-06
PA_PS_HEATSYS1 Flow Rate [gal/min] | HEATSYS1 Flow Rate [gal/min] | 103.8193 | 99.2151 | 112.0814 | 107.4286 | [6 empty] | 2021-05-06
PA_PS_VAV_POD_1 Fan Power [hp] | VAV_POD_1 Fan Power [hp] | 8.4857 | 8.1966 | 8.5409 | 8.2308 | [6 empty] | 2021-05-06
PA_PS_VAV_POD_2 Fan Power [hp] | VAV_POD_2 Fan Power [hp] | 8.3548 | 8.1321 | 8.4166 | 8.1816 | [6 empty] | 2021-05-06
PA_PS_VAV_POD_3 Fan Power [hp] | VAV_POD_3 Fan Power [hp] | 7.7069 | 7.3621 | 7.7797 | 7.4127 | [6 empty] | 2021-05-06
PA_PS_VAV_OTHER Fan Power [hp] | VAV_OTHER Fan Power [hp] | 11.6587 | 10.9949 | 11.9267 | 11.2074 | [6 empty] | 2021-05-06
PA_PS_HEATSYS1 Pump Power [hp] | HEATSYS1 Pump Power [hp] | 2.2441 | 2.1234 | 2.4227 | 2.2991 | [6 empty] | 2021-05-06
PA_PS_PSZ-AC_1:6 Heating Capacity [kBtu/hr] | PSZ-AC_1:6 Heating Capacity [kBtu/hr] | 209.1295 | 200.557 | 212.5855 | 204.0379 | [6 empty] | 2021-05-06
PA_PS_PSZ-AC_2:5 Heating Capacity [kBtu/hr] | PSZ-AC_2:5 Heating Capacity [kBtu/hr] | 130.5737 | 131.4999 | 138.653 | 138.4071 | [6 empty] | 2021-05-06
PA_PS_PSZ-AC_2:7 Heating Capacity [kBtu/hr] | PSZ-AC_2:7 Heating Capacity [kBtu/hr] | 312.0761 | 312.0761 | 328.2932 | 328.2932 | [6 empty] | 2021-05-06
PA_PS_ZN_VAV_BOXes_Max_Reheat_Water_Flow_GPM | ZN_VAV_BOXes_Max_Reheat_Water_Flow_GPM | 68.9902 | 65.8499 | 71.2163 | 68.3833 | [6 empty] | 2021-05-06
id | item | Zone4A(PA-Philadelphia-PA) ASHRAE901-state_STD2016 | Zone4A(PA-Philadelphia-PA) ASHRAE901-state_STD2019 | Zone5A(PA-Pittsburgh-PA) ASHRAE901-state_STD2016 | Zone5A(PA-Pittsburgh-PA) ASHRAE901-state_STD2019 | [6 empty] | 2021-05-06
PA_SH_SAC_FRONTOFFICE Cooling Capacity [ton] | SAC_FRONTOFFICE Cooling Capacity [ton] | 2.4071 | 2.2921 | 2.2155 | 2.1042 | [6 empty] | 2021-05-06
PA_SH_SAC_FRONTLOUNGE Cooling Capacity [ton] | SAC_FRONTLOUNGE Cooling Capacity [ton] | 6.1159 | 5.8111 | 6.1066 | 5.8648 | [6 empty] | 2021-05-06
PA_SH_SAC_MEETINGROOM Cooling Capacity [ton] | SAC_MEETINGROOM Cooling Capacity [ton] | 2.8749 | 2.8042 | 2.9467 | 2.8554 | [6 empty] | 2021-05-06
PA_SH_SAC_EXC_EMPLGE_RESTRM Cooling Capacity [ton] | SAC_EXC_EMPLGE_RESTRM Cooling Capacity [ton] | 6.0703 | 6.0293 | 5.8241 | 5.7835 | [6 empty] | 2021-05-06
PA_SH_SAC_FO_ADDAQ SUPPLY FAN Supply Flow Rate [cfm] | SAC_FO_ADDAQ SUPPLY FAN Supply Flow Rate [cfm] | 783.9856 | 741.608 | 783.9856 | 720.4192 | [6 empty] | 2021-05-06
PA_SH_SAC_FL_ADDAQ SUPPLY FAN Supply Flow Rate [cfm] | SAC_FL_ADDAQ SUPPLY FAN Supply Flow Rate [cfm] | 1843.4256 | 1737.4816 | 1864.6144 | 1758.6704 | [6 empty] | 2021-05-06
PA_SH_SAC_MR_ADDAQ SUPPLY FAN Supply Flow Rate [cfm] | SAC_MR_ADDAQ SUPPLY FAN Supply Flow Rate [cfm] | 868.7408 | 847.552 | 889.9296 | 847.552 | [6 empty] | 2021-05-06
PA_SH_SAC_EXC_ADDAQ SUPPLY FAN Supply Flow Rate [cfm] | SAC_EXC_ADDAQ SUPPLY FAN Supply Flow Rate [cfm] | 2182.4464 | 2161.2576 | 2246.0128 | 2224.824 | [6 empty] | 2021-05-06
PA_SH_SAC_Exc_EmpLge_RestRm OA Rate [cfm] | SAC_Exc_EmpLge_RestRm OA Rate [cfm] | 199.9928 | 199.9928 | 199.9928 | 199.9928 | [6 empty] | 2021-05-06
PA_SH_SAC_FrontLounge OA Rate [cfm] | SAC_FrontLounge OA Rate [cfm] | 500.0133 | 500.0133 | 500.0133 | 500.0133 | [6 empty] | 2021-05-06
PA_SH_SAC_FrontOffice OA Rate [cfm] | SAC_FrontOffice OA Rate [cfm] | 119.2938 | 119.2938 | 119.2938 | 119.2938 | [6 empty] | 2021-05-06
PA_SH_SAC_MeetingRoom OA Rate [cfm] | SAC_MeetingRoom OA Rate [cfm] | 267.7629 | 267.7629 | 267.7629 | 267.7629 | [6 empty] | 2021-05-06
PA_SH_SAC_FrontLounge OA Damper [gravity, motorized] | SAC_FrontLounge OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2021-05-06
PA_SH_SAC_FrontOffice (economizer) | SAC_FrontOffice (economizer) | No | No | No | No | [6 empty] | 2021-05-06
PA_SH_SAC_FrontLounge (economizer) | SAC_FrontLounge (economizer) | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialDryBulb | DifferentialDryBulb | [6 empty] | 2021-05-06
PA_SH_SAC_MeetingRoom (economizer) | SAC_MeetingRoom (economizer) | No | No | No | No | [6 empty] | 2021-05-06
PA_SH_SAC_Exc_EmpLge_RestRm (economizer) | SAC_Exc_EmpLge_RestRm (economizer) | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialDryBulb | DifferentialDryBulb | [6 empty] | 2021-05-06
PA_SH_SAC_FRONTOFFICE Heating Capacity [kBtu/hr] | SAC_FRONTOFFICE Heating Capacity [kBtu/hr] | 36.171 | 34.437 | 35.6069 | 33.8275 | [6 empty] | 2021-05-06
PA_SH_SAC_FRONTLOUNGE Heating Capacity [kBtu/hr] | SAC_FRONTLOUNGE Heating Capacity [kBtu/hr] | 98.6298 | 95.263 | 99.913 | 96.5469 | [6 empty] | 2021-05-06
PA_SH_SAC_MEETINGROOM Heating Capacity [kBtu/hr] | SAC_MEETINGROOM Heating Capacity [kBtu/hr] | 48.396 | 47.6157 | 49.6459 | 48.6789 | [6 empty] | 2021-05-06
PA_SH_SAC_EXC_EMPLGE_RESTRM Heating Capacity [kBtu/hr] | SAC_EXC_EMPLGE_RESTRM Heating Capacity [kBtu/hr] | 92.4676 | 91.8167 | 93.208 | 92.5514 | [6 empty] | 2021-05-06
id | item | Zone4A(PA-Philadelphia-PA) ASHRAE901-state_STD2016 | Zone4A(PA-Philadelphia-PA) ASHRAE901-state_STD2019 | Zone5A(PA-Pittsburgh-PA) ASHRAE901-state_STD2016 | Zone5A(PA-Pittsburgh-PA) ASHRAE901-state_STD2019 | [6 empty] | 2021-05-06
PA_MA_SPLIT GSW COOLING COIL Cooling Capacity [ton] | SPLIT GSW COOLING COIL Cooling Capacity [ton] | 0.90518 | 0.89127 | 0.81155 | 0.7974 | [6 empty] | 2021-05-06
PA_MA_SPLIT GNW COOLING COIL Cooling Capacity [ton] | SPLIT GNW COOLING COIL Cooling Capacity [ton] | 0.86821 | 0.85478 | 0.77387 | 0.76018 | [6 empty] | 2021-05-06
PA_MA_SPLIT OFFICE COOLING COIL Cooling Capacity [ton] | SPLIT OFFICE COOLING COIL Cooling Capacity [ton] | 1.7277 | 1.6024 | 1.6816 | 1.5507 | [6 empty] | 2021-05-06
PA_MA_SPLIT GNE COOLING COIL Cooling Capacity [ton] | SPLIT GNE COOLING COIL Cooling Capacity [ton] | 0.7701 | 0.75821 | 0.66787 | 0.65572 | [6 empty] | 2021-05-06
PA_MA_SPLIT GN1 COOLING COIL Cooling Capacity [ton] | SPLIT GN1 COOLING COIL Cooling Capacity [ton] | 0.65198 | 0.64233 | 0.56386 | 0.55475 | [6 empty] | 2021-05-06
PA_MA_SPLIT GN2 COOLING COIL Cooling Capacity [ton] | SPLIT GN2 COOLING COIL Cooling Capacity [ton] | 0.65009 | 0.64049 | 0.56164 | 0.55258 | [6 empty] | 2021-05-06
PA_MA_SPLIT GS1 COOLING COIL Cooling Capacity [ton] | SPLIT GS1 COOLING COIL Cooling Capacity [ton] | 0.69442 | 0.68405 | 0.61029 | 0.59984 | [6 empty] | 2021-05-06
PA_MA_SPLIT GS2 COOLING COIL Cooling Capacity [ton] | SPLIT GS2 COOLING COIL Cooling Capacity [ton] | 0.72571 | 0.71161 | 0.6426 | 0.62707 | [6 empty] | 2021-05-06
PA_MA_SPLIT MSW COOLING COIL Cooling Capacity [ton] | SPLIT MSW COOLING COIL Cooling Capacity [ton] | 2.1286 | 2.0978 | 1.9708 | 1.9392 | [6 empty] | 2021-05-06
PA_MA_SPLIT MNW COOLING COIL Cooling Capacity [ton] | SPLIT MNW COOLING COIL Cooling Capacity [ton] | 2.0606 | 2.0307 | 1.9055 | 1.8749 | [6 empty] | 2021-05-06
PA_MA_SPLIT MSE COOLING COIL Cooling Capacity [ton] | SPLIT MSE COOLING COIL Cooling Capacity [ton] | 1.891 | 1.8639 | 1.6869 | 1.6594 | [6 empty] | 2021-05-06
PA_MA_SPLIT MNE COOLING COIL Cooling Capacity [ton] | SPLIT MNE COOLING COIL Cooling Capacity [ton] | 1.7093 | 1.725 | 1.5553 | 1.5256 | [6 empty] | 2021-05-06
PA_MA_SPLIT MN1 COOLING COIL Cooling Capacity [ton] | SPLIT MN1 COOLING COIL Cooling Capacity [ton] | 1.4274 | 1.4089 | 1.2676 | 1.2501 | [6 empty] | 2021-05-06
PA_MA_SPLIT MN2 COOLING COIL Cooling Capacity [ton] | SPLIT MN2 COOLING COIL Cooling Capacity [ton] | 1.4221 | 1.4037 | 1.2615 | 1.2442 | [6 empty] | 2021-05-06
PA_MA_SPLIT MS1 COOLING COIL Cooling Capacity [ton] | SPLIT MS1 COOLING COIL Cooling Capacity [ton] | 1.5041 | 1.4845 | 1.3518 | 1.3322 | [6 empty] | 2021-05-06
PA_MA_SPLIT MS2 COOLING COIL Cooling Capacity [ton] | SPLIT MS2 COOLING COIL Cooling Capacity [ton] | 1.4989 | 1.4794 | 1.3464 | 1.3269 | [6 empty] | 2021-05-06
PA_MA_SPLIT TSW COOLING COIL Cooling Capacity [ton] | SPLIT TSW COOLING COIL Cooling Capacity [ton] | 1.3332 | 1.3161 | 1.2264 | 1.2092 | [6 empty] | 2021-05-06
PA_MA_SPLIT TNW COOLING COIL Cooling Capacity [ton] | SPLIT TNW COOLING COIL Cooling Capacity [ton] | 1.28 | 1.2639 | 1.1847 | 1.1681 | [6 empty] | 2021-05-06
PA_MA_SPLIT TSE COOLING COIL Cooling Capacity [ton] | SPLIT TSE COOLING COIL Cooling Capacity [ton] | 1.2103 | 1.1961 | 1.0881 | 1.0739 | [6 empty] | 2021-05-06
PA_MA_SPLIT TNE COOLING COIL Cooling Capacity [ton] | SPLIT TNE COOLING COIL Cooling Capacity [ton] | 1.1335 | 1.1208 | 1.0125 | 0.9998 | [6 empty] | 2021-05-06
PA_MA_SPLIT TN1 COOLING COIL Cooling Capacity [ton] | SPLIT TN1 COOLING COIL Cooling Capacity [ton] | 0.8975 | 0.88803 | 0.81287 | 0.80329 | [6 empty] | 2021-05-06
PA_MA_SPLIT TN2 COOLING COIL Cooling Capacity [ton] | SPLIT TN2 COOLING COIL Cooling Capacity [ton] | 0.92624 | 0.9163 | 0.80627 | 0.79686 | [6 empty] | 2021-05-06
PA_MA_SPLIT TS1 COOLING COIL Cooling Capacity [ton] | SPLIT TS1 COOLING COIL Cooling Capacity [ton] | 1.0008 | 0.98967 | 0.89672 | 0.88583 | [6 empty] | 2021-05-06
PA_MA_SPLIT TS2 COOLING COIL Cooling Capacity [ton] | SPLIT TS2 COOLING COIL Cooling Capacity [ton] | 1.0025 | 0.99136 | 0.90159 | 0.8905 | [6 empty] | 2021-05-06
PA_MA_Split GN1 Furnace with DX Cooling OA Rate [cfm] | Split GN1 Furnace with DX Cooling OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | [6 empty] | 2021-05-06
PA_MA_Split GN2 Furnace with DX Cooling OA Rate [cfm] | Split GN2 Furnace with DX Cooling OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | [6 empty] | 2021-05-06
PA_MA_Split GNE Furnace with DX Cooling OA Rate [cfm] | Split GNE Furnace with DX Cooling OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | [6 empty] | 2021-05-06
PA_MA_Split GNW Furnace with DX Cooling OA Rate [cfm] | Split GNW Furnace with DX Cooling OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | [6 empty] | 2021-05-06
PA_MA_Split GS1 Furnace with DX Cooling OA Rate [cfm] | Split GS1 Furnace with DX Cooling OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | [6 empty] | 2021-05-06
PA_MA_Split GS2 Furnace with DX Cooling OA Rate [cfm] | Split GS2 Furnace with DX Cooling OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | [6 empty] | 2021-05-06
PA_MA_Split GSW Furnace with DX Cooling OA Rate [cfm] | Split GSW Furnace with DX Cooling OA Rate [cfm] | 56.9945 | 56.9945 | 56.9945 | 56.9945 | [6 empty] | 2021-05-06
PA_MA_Split MN1 Furnace with DX Cooling OA Rate [cfm] | Split MN1 Furnace with DX Cooling OA Rate [cfm] | 109.9824 | 109.9824 | 109.9824 | 109.9824 | [6 empty] | 2021-05-06
PA_MA_Split MN2 Furnace with DX Cooling OA Rate [cfm] | Split MN2 Furnace with DX Cooling OA Rate [cfm] | 109.9824 | 109.9824 | 109.9824 | 109.9824 | [6 empty] | 2021-05-06
PA_MA_Split MNE Furnace with DX Cooling OA Rate [cfm] | Split MNE Furnace with DX Cooling OA Rate [cfm] | 109.9824 | 109.9824 | 109.9824 | 109.9824 | [6 empty] | 2021-05-06
PA_MA_Split MNW Furnace with DX Cooling OA Rate [cfm] | Split MNW Furnace with DX Cooling OA Rate [cfm] | 109.9824 | 109.9824 | 109.9824 | 109.9824 | [6 empty] | 2021-05-06
PA_MA_Split MS1 Furnace with DX Cooling OA Rate [cfm] | Split MS1 Furnace with DX Cooling OA Rate [cfm] | 109.9824 | 109.9824 | 109.9824 | 109.9824 | [6 empty] | 2021-05-06
PA_MA_Split MS2 Furnace with DX Cooling OA Rate [cfm] | Split MS2 Furnace with DX Cooling OA Rate [cfm] | 109.9824 | 109.9824 | 109.9824 | 109.9824 | [6 empty] | 2021-05-06
PA_MA_Split MSE Furnace with DX Cooling OA Rate [cfm] | Split MSE Furnace with DX Cooling OA Rate [cfm] | 109.9824 | 109.9824 | 109.9824 | 109.9824 | [6 empty] | 2021-05-06
PA_MA_Split MSW Furnace with DX Cooling OA Rate [cfm] | Split MSW Furnace with DX Cooling OA Rate [cfm] | 109.9824 | 109.9824 | 109.9824 | 109.9824 | [6 empty] | 2021-05-06
PA_MA_Split Office Furnace with DX Cooling OA Rate [cfm] | Split Office Furnace with DX Cooling OA Rate [cfm] | 80.7372 | 80.7372 | 80.7372 | 80.7372 | [6 empty] | 2021-05-06
PA_MA_Split TN1 Furnace with DX Cooling OA Rate [cfm] | Split TN1 Furnace with DX Cooling OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | [6 empty] | 2021-05-06
PA_MA_Split TN2 Furnace with DX Cooling OA Rate [cfm] | Split TN2 Furnace with DX Cooling OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | [6 empty] | 2021-05-06
PA_MA_Split TNE Furnace with DX Cooling OA Rate [cfm] | Split TNE Furnace with DX Cooling OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | [6 empty] | 2021-05-06
PA_MA_Split TNW Furnace with DX Cooling OA Rate [cfm] | Split TNW Furnace with DX Cooling OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | [6 empty] | 2021-05-06
PA_MA_Split TS1 Furnace with DX Cooling OA Rate [cfm] | Split TS1 Furnace with DX Cooling OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | [6 empty] | 2021-05-06
PA_MA_Split TS2 Furnace with DX Cooling OA Rate [cfm] | Split TS2 Furnace with DX Cooling OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | [6 empty] | 2021-05-06
PA_MA_Split TSE Furnace with DX Cooling OA Rate [cfm] | Split TSE Furnace with DX Cooling OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | [6 empty] | 2021-05-06
PA_MA_Split TSW Furnace with DX Cooling OA Rate [cfm] | Split TSW Furnace with DX Cooling OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | [6 empty] | 2021-05-06
PA_MA_SPLIT GSW HEATING COIL Heating Capacity [kBtu/hr] | SPLIT GSW HEATING COIL Heating Capacity [kBtu/hr] | 8.9489 | 9.0073 | 9.6661 | 9.7243 | [6 empty] | 2021-05-06
PA_MA_SPLIT GNW HEATING COIL Heating Capacity [kBtu/hr] | SPLIT GNW HEATING COIL Heating Capacity [kBtu/hr] | 8.886 | 8.9445 | 9.53 | 9.5884 | [6 empty] | 2021-05-06
PA_MA_SPLIT OFFICE HEATING COIL Heating Capacity [kBtu/hr] | SPLIT OFFICE HEATING COIL Heating Capacity [kBtu/hr] | 21.3675 | 21.4569 | 22.4236 | 22.5057 | [6 empty] | 2021-05-06
PA_MA_SPLIT GNE HEATING COIL Heating Capacity [kBtu/hr] | SPLIT GNE HEATING COIL Heating Capacity [kBtu/hr] | 8.8669 | 8.9254 | 9.5081 | 9.5664 | [6 empty] | 2021-05-06
PA_MA_SPLIT GN1 HEATING COIL Heating Capacity [kBtu/hr] | SPLIT GN1 HEATING COIL Heating Capacity [kBtu/hr] | 6.4023 | 6.4609 | 7.0072 | 7.0657 | [6 empty] | 2021-05-06
PA_MA_SPLIT GN2 HEATING COIL Heating Capacity [kBtu/hr] | SPLIT GN2 HEATING COIL Heating Capacity [kBtu/hr] | 6.4017 | 6.4603 | 7.0066 | 7.065 | [6 empty] | 2021-05-06
PA_MA_SPLIT GS1 HEATING COIL Heating Capacity [kBtu/hr] | SPLIT GS1 HEATING COIL Heating Capacity [kBtu/hr] | 6.3565 | 6.4149 | 7.0228 | 7.0811 | [6 empty] | 2021-05-06
PA_MA_SPLIT GS2 HEATING COIL Heating Capacity [kBtu/hr] | SPLIT GS2 HEATING COIL Heating Capacity [kBtu/hr] | 6.8492 | 6.9089 | 7.5269 | 7.5861 | [6 empty] | 2021-05-06
PA_MA_SPLIT MSW HEATING COIL Heating Capacity [kBtu/hr] | SPLIT MSW HEATING COIL Heating Capacity [kBtu/hr] | 16.38 | 16.5092 | 16.8486 | 16.9775 | [6 empty] | 2021-05-06
PA_MA_SPLIT MNW HEATING COIL Heating Capacity [kBtu/hr] | SPLIT MNW HEATING COIL Heating Capacity [kBtu/hr] | 16.4583 | 16.5874 | 16.7806 | 16.9097 | [6 empty] | 2021-05-06
PA_MA_SPLIT MSE HEATING COIL Heating Capacity [kBtu/hr] | SPLIT MSE HEATING COIL Heating Capacity [kBtu/hr] | 16.3349 | 16.4641 | 16.7965 | 16.9255 | [6 empty] | 2021-05-06
PA_MA_SPLIT MNE HEATING COIL Heating Capacity [kBtu/hr] | SPLIT MNE HEATING COIL Heating Capacity [kBtu/hr] | 16.4132 | 16.5423 | 16.7285 | 16.8575 | [6 empty] | 2021-05-06
PA_MA_SPLIT MN1 HEATING COIL Heating Capacity [kBtu/hr] | SPLIT MN1 HEATING COIL Heating Capacity [kBtu/hr] | 11.153 | 11.2774 | 11.6142 | 11.7398 | [6 empty] | 2021-05-06
PA_MA_SPLIT MN2 HEATING COIL Heating Capacity [kBtu/hr] | SPLIT MN2 HEATING COIL Heating Capacity [kBtu/hr] | 11.1518 | 11.2761 | 11.6128 | 11.7384 | [6 empty] | 2021-05-06
PA_MA_SPLIT MS1 HEATING COIL Heating Capacity [kBtu/hr] | SPLIT MS1 HEATING COIL Heating Capacity [kBtu/hr] | 11.0828 | 11.2071 | 11.6902 | 11.8159 | [6 empty] | 2021-05-06
PA_MA_SPLIT MS2 HEATING COIL Heating Capacity [kBtu/hr] | SPLIT MS2 HEATING COIL Heating Capacity [kBtu/hr] | 11.0816 | 11.2059 | 11.6888 | 11.8145 | [6 empty] | 2021-05-06
PA_MA_SPLIT TSW HEATING COIL Heating Capacity [kBtu/hr] | SPLIT TSW HEATING COIL Heating Capacity [kBtu/hr] | 11.5446 | 11.6062 | 11.9759 | 12.0378 | [6 empty] | 2021-05-06
PA_MA_SPLIT TNW HEATING COIL Heating Capacity [kBtu/hr] | SPLIT TNW HEATING COIL Heating Capacity [kBtu/hr] | 11.5914 | 11.653 | 11.9464 | 12.0084 | [6 empty] | 2021-05-06
PA_MA_SPLIT TSE HEATING COIL Heating Capacity [kBtu/hr] | SPLIT TSE HEATING COIL Heating Capacity [kBtu/hr] | 11.521 | 11.5825 | 11.9484 | 12.0102 | [6 empty] | 2021-05-06
PA_MA_SPLIT TNE HEATING COIL Heating Capacity [kBtu/hr] | SPLIT TNE HEATING COIL Heating Capacity [kBtu/hr] | 11.5678 | 11.6294 | 11.9188 | 11.9807 | [6 empty] | 2021-05-06
PA_MA_SPLIT TN1 HEATING COIL Heating Capacity [kBtu/hr] | SPLIT TN1 HEATING COIL Heating Capacity [kBtu/hr] | 8.676 | 8.7374 | 9.1686 | 9.2305 | [6 empty] | 2021-05-06
PA_MA_SPLIT TN2 HEATING COIL Heating Capacity [kBtu/hr] | SPLIT TN2 HEATING COIL Heating Capacity [kBtu/hr] | 8.6753 | 8.7367 | 9.1678 | 9.2296 | [6 empty] | 2021-05-06
PA_MA_SPLIT TS1 HEATING COIL Heating Capacity [kBtu/hr] | SPLIT TS1 HEATING COIL Heating Capacity [kBtu/hr] | 8.6219 | 8.6832 | 9.1922 | 9.254 | [6 empty] | 2021-05-06
PA_MA_SPLIT TS2 HEATING COIL Heating Capacity [kBtu/hr] | SPLIT TS2 HEATING COIL Heating Capacity [kBtu/hr] | 8.6212 | 8.6825 | 9.1915 | 9.2532 | [6 empty] | 2021-05-06
PA_MA_Split_GSW ERV Flag | Split_GSW ERV Flag | Yes | Yes | Yes | Yes | [6 empty] | 2021-05-06
PA_MA_Split_GNW ERV Flag | Split_GNW ERV Flag | Yes | Yes | Yes | Yes | [6 empty] | 2021-05-06
PA_MA_Split_GNE ERV Flag | Split_GNE ERV Flag | Yes | Yes | Yes | Yes | [6 empty] | 2021-05-06
PA_MA_Split_GN1 ERV Flag | Split_GN1 ERV Flag | Yes | Yes | Yes | Yes | [6 empty] | 2021-05-06
PA_MA_Split_GN2 ERV Flag | Split_GN2 ERV Flag | Yes | Yes | Yes | Yes | [6 empty] | 2021-05-06
PA_MA_Split_GS1 ERV Flag | Split_GS1 ERV Flag | Yes | Yes | Yes | Yes | [6 empty] | 2021-05-06
PA_MA_Split_GS2 ERV Flag | Split_GS2 ERV Flag | Yes | Yes | Yes | Yes | [6 empty] | 2021-05-06
PA_MA_Split_MSW ERV Flag | Split_MSW ERV Flag | Yes | Yes | Yes | Yes | [6 empty] | 2021-05-06
PA_MA_Split_MNW ERV Flag | Split_MNW ERV Flag | Yes | Yes | Yes | Yes | [6 empty] | 2021-05-06
PA_MA_Split_MSE ERV Flag | Split_MSE ERV Flag | Yes | Yes | Yes | Yes | [6 empty] | 2021-05-06
PA_MA_Split_MNE ERV Flag | Split_MNE ERV Flag | Yes | Yes | Yes | Yes | [6 empty] | 2021-05-06
PA_MA_Split_MN1 ERV Flag | Split_MN1 ERV Flag | Yes | Yes | Yes | Yes | [6 empty] | 2021-05-06
PA_MA_Split_MN2 ERV Flag | Split_MN2 ERV Flag | Yes | Yes | Yes | Yes | [6 empty] | 2021-05-06
PA_MA_Split_MS1 ERV Flag | Split_MS1 ERV Flag | Yes | Yes | Yes | Yes | [6 empty] | 2021-05-06
PA_MA_Split_MS2 ERV Flag | Split_MS2 ERV Flag | Yes | Yes | Yes | Yes | [6 empty] | 2021-05-06
PA_MA_Split_TSW ERV Flag | Split_TSW ERV Flag | Yes | Yes | Yes | Yes | [6 empty] | 2021-05-06
PA_MA_Split_TNW ERV Flag | Split_TNW ERV Flag | Yes | Yes | Yes | Yes | [6 empty] | 2021-05-06
PA_MA_Split_TSE ERV Flag | Split_TSE ERV Flag | Yes | Yes | Yes | Yes | [6 empty] | 2021-05-06
PA_MA_Split_TNE ERV Flag | Split_TNE ERV Flag | Yes | Yes | Yes | Yes | [6 empty] | 2021-05-06
PA_MA_Split_TN1 ERV Flag | Split_TN1 ERV Flag | Yes | Yes | Yes | Yes | [6 empty] | 2021-05-06
PA_MA_Split_TN2 ERV Flag | Split_TN2 ERV Flag | Yes | Yes | Yes | Yes | [6 empty] | 2021-05-06
PA_MA_Split_TS1 ERV Flag | Split_TS1 ERV Flag | Yes | Yes | Yes | Yes | [6 empty] | 2021-05-06
PA_MA_Split_TS2 ERV Flag | Split_TS2 ERV Flag | Yes | Yes | Yes | Yes | [6 empty] | 2021-05-06
id | item | Zone5A(RI-Providence-RI) ASHRAE901-state_STD2016 | Zone5A(RI-Providence-RI) ASHRAE901-state_STD2019 | [8 empty] | 2021-05-06
RI_SO_PSZ-AC:1 Cooling Capacity [ton] | PSZ-AC:1 Cooling Capacity [ton] | 1.786 | 1.6942 | [8 empty] | 2021-05-06
RI_SO_PSZ-AC:2 Cooling Capacity [ton] | PSZ-AC:2 Cooling Capacity [ton] | 1.5288 | 1.4674 | [8 empty] | 2021-05-06
RI_SO_PSZ-AC:3 Cooling Capacity [ton] | PSZ-AC:3 Cooling Capacity [ton] | 1.052 | 1.0142 | [8 empty] | 2021-05-06
RI_SO_PSZ-AC:4 Cooling Capacity [ton] | PSZ-AC:4 Cooling Capacity [ton] | 1.4484 | 1.38 | [8 empty] | 2021-05-06
RI_SO_PSZ-AC:5 Cooling Capacity [ton] | PSZ-AC:5 Cooling Capacity [ton] | 1.2571 | 1.2179 | [8 empty] | 2021-05-06
RI_SO_PSZ-AC:1 Supply Flow Rate [cfm] | PSZ-AC:1 Supply Flow Rate [cfm] | 635.664 | 593.2864 | [8 empty] | 2021-05-06
RI_SO_PSZ-AC:2 Supply Flow Rate [cfm] | PSZ-AC:2 Supply Flow Rate [cfm] | 550.9088 | 529.72 | [8 empty] | 2021-05-06
RI_SO_PSZ-AC:3 Supply Flow Rate [cfm] | PSZ-AC:3 Supply Flow Rate [cfm] | 423.776 | 423.776 | [8 empty] | 2021-05-06
RI_SO_PSZ-AC:4 Supply Flow Rate [cfm] | PSZ-AC:4 Supply Flow Rate [cfm] | 508.5312 | 487.3424 | [8 empty] | 2021-05-06
RI_SO_PSZ-AC:5 Supply Flow Rate [cfm] | PSZ-AC:5 Supply Flow Rate [cfm] | 508.5312 | 487.3424 | [8 empty] | 2021-05-06
RI_SO_PSZ-AC:1 OA Rate [cfm] | PSZ-AC:1 OA Rate [cfm] | 136.9178 | 136.9178 | [8 empty] | 2021-05-06
RI_SO_PSZ-AC:2 OA Rate [cfm] | PSZ-AC:2 OA Rate [cfm] | 103.7925 | 103.7925 | [8 empty] | 2021-05-06
RI_SO_PSZ-AC:3 OA Rate [cfm] | PSZ-AC:3 OA Rate [cfm] | 61.5711 | 61.5711 | [8 empty] | 2021-05-06
RI_SO_PSZ-AC:4 OA Rate [cfm] | PSZ-AC:4 OA Rate [cfm] | 103.7925 | 103.7925 | [8 empty] | 2021-05-06
RI_SO_PSZ-AC:5 OA Rate [cfm] | PSZ-AC:5 OA Rate [cfm] | 61.5711 | 61.5711 | [8 empty] | 2021-05-06
RI_SO_PSZ-AC:1 heating Capacity [kBtu/hr] | PSZ-AC:1 heating Capacity [kBtu/hr] | 14.3279 | 14.3279 | [8 empty] | 2021-05-06
RI_SO_PSZ-AC:2 heating Capacity [kBtu/hr] | PSZ-AC:2 heating Capacity [kBtu/hr] | 19.569 | 19.3597 | [8 empty] | 2021-05-06
RI_SO_PSZ-AC:3 heating Capacity [kBtu/hr] | PSZ-AC:3 heating Capacity [kBtu/hr] | 11.9485 | 11.8327 | [8 empty] | 2021-05-06
RI_SO_PSZ-AC:4 heating Capacity [kBtu/hr] | PSZ-AC:4 heating Capacity [kBtu/hr] | 19.4798 | 19.3002 | [8 empty] | 2021-05-06
RI_SO_PSZ-AC:5 heating Capacity [kBtu/hr] | PSZ-AC:5 heating Capacity [kBtu/hr] | 12.003 | 11.8815 | [8 empty] | 2021-05-06
id | item | Zone5A(RI-Providence-RI) ASHRAE901-state_STD2016 | Zone5A(RI-Providence-RI) ASHRAE901-state_STD2019 | [8 empty] | 2021-05-06
RI_LO_CAV_BAS Supply Flow Rate [cfm] | CAV_BAS Supply Flow Rate [cfm] | 11547.896 | 10700.344 | [8 empty] | 2021-05-06
RI_LO_VAV_BOT WITH REHEAT Supply Flow Rate [cfm] | VAV_BOT WITH REHEAT Supply Flow Rate [cfm] | 19663.2064 | 18752.088 | [8 empty] | 2021-05-06
RI_LO_VAV_MID WITH REHEAT Supply Flow Rate [cfm] | VAV_MID WITH REHEAT Supply Flow Rate [cfm] | 183622.1411 | 174828.7891 | [8 empty] | 2021-05-06
RI_LO_VAV_TOP WITH REHEAT Supply Flow Rate [cfm] | VAV_TOP WITH REHEAT Supply Flow Rate [cfm] | 19175.864 | 18413.0672 | [8 empty] | 2021-05-06
RI_LO_Supply Air Temp. Reset Flag | Supply Air Temp. Reset Flag | Yes | Yes | [8 empty] | 2021-05-06
RI_LO_CAV_BAS OA Rate [cfm] | CAV_BAS OA Rate [cfm] | 2542.8255 | 2542.8255 | [8 empty] | 2021-05-06
RI_LO_VAV_BOT WITH REHEAT OA Rate [cfm] | VAV_BOT WITH REHEAT OA Rate [cfm] | 5377.8022 | 4302.174 | [8 empty] | 2021-05-06
RI_LO_VAV_MID WITH REHEAT OA Rate [cfm] | VAV_MID WITH REHEAT OA Rate [cfm] | 53777.9373 | 43021.7396 | [8 empty] | 2021-05-06
RI_LO_VAV_TOP WITH REHEAT OA Rate [cfm] | VAV_TOP WITH REHEAT OA Rate [cfm] | 5377.8022 | 4302.174 | [8 empty] | 2021-05-06
RI_LO_AIRLOOP DATACENTER BASEMENT OA Rate [cfm] | AIRLOOP DATACENTER BASEMENT OA Rate [cfm] | 716.9654 | 716.9654 | [8 empty] | 2021-05-06
RI_LO_VAV_bot_WITH_REHEAT ERV Flag | VAV_bot_WITH_REHEAT ERV Flag | Yes | Yes | [8 empty] | 2021-05-06
RI_LO_VAV_mid_WITH_REHEAT ERV Flag | VAV_mid_WITH_REHEAT ERV Flag | Yes | Yes | [8 empty] | 2021-05-06
RI_LO_VAV_top_WITH_REHEAT ERV Flag | VAV_top_WITH_REHEAT ERV Flag | Yes | Yes | [8 empty] | 2021-05-06
RI_LO_COOLSYS1 CHILLER1 Capacity [ton] | COOLSYS1 CHILLER1 Capacity [ton] | 401.3113 | 364.1185 | [8 empty] | 2021-05-06
RI_LO_COOLSYS1 CHILLER2 Capacity [ton] | COOLSYS1 CHILLER2 Capacity [ton] | 401.3113 | 364.1185 | [8 empty] | 2021-05-06
RI_LO_TOWERWATERSYS COOLTOWER 1 Capacity [ton] | TOWERWATERSYS COOLTOWER 1 Capacity [ton] | 380.9197 | 345.608 | [8 empty] | 2021-05-06
RI_LO_TOWERWATERSYS COOLTOWER 2 Capacity [ton] | TOWERWATERSYS COOLTOWER 2 Capacity [ton] | 380.9197 | 345.608 | [8 empty] | 2021-05-06
RI_LO_HEATSYS1 BOILER Capacity [MMBTU/h] | HEATSYS1 BOILER Capacity [MMBTU/h] | 4415.7608 | 3910.2055 | [8 empty] | 2021-05-06
RI_LO_COOLSYS1 PUMP Flow Rate [gal/min] | COOLSYS1 PUMP Flow Rate [gal/min] | 0 | 0 | [8 empty] | 2021-05-06
RI_LO_COOLSYS1 CHILLER1 PUMP Flow Rate [gal/min] | COOLSYS1 CHILLER1 PUMP Flow Rate [gal/min] | 632.3154 | 573.6042 | [8 empty] | 2021-05-06
RI_LO_COOLSYS1 CHILLER2 PUMP Flow Rate [gal/min] | COOLSYS1 CHILLER2 PUMP Flow Rate [gal/min] | 632.3154 | 573.6042 | [8 empty] | 2021-05-06
RI_LO_COOLSYS1 PUMP SECONDARY Flow Rate [gal/min] | COOLSYS1 PUMP SECONDARY Flow Rate [gal/min] | 1264.6307 | 1147.2099 | [8 empty] | 2021-05-06
RI_LO_HEATSYS1 PUMP Flow Rate [gal/min] | HEATSYS1 PUMP Flow Rate [gal/min] | 906.3928 | 802.6207 | [8 empty] | 2021-05-06
RI_LO_TOWERWATERSYS PUMP Flow Rate [gal/min] | TOWERWATERSYS PUMP Flow Rate [gal/min] | 2214.1316 | 2008.87 | [8 empty] | 2021-05-06
RI_LO_PLANT CIRC PUMP Flow Rate [gal/min] | PLANT CIRC PUMP Flow Rate [gal/min] | 207.8279 | 206.9957 | [8 empty] | 2021-05-06
RI_LO_COOLSYS1 PUMP SECONDARY Pressure setpoint reset [yes,no] | COOLSYS1 PUMP SECONDARY Pressure setpoint reset [yes,no] | pump_ride_on_curve | pump_ride_on_curve | [8 empty] | 2021-05-06
RI_LO_COOLSYS1 CHILLER1 PUMP Pump Power [hp] | COOLSYS1 CHILLER1 PUMP Pump Power [hp] | 3.4111 | 3.0638 | [8 empty] | 2021-05-06
RI_LO_COOLSYS1 CHILLER2 PUMP Pump Power [hp] | COOLSYS1 CHILLER2 PUMP Pump Power [hp] | 3.4111 | 3.0638 | [8 empty] | 2021-05-06
RI_LO_COOLSYS1 PUMP SECONDARY Pump Power [hp] | COOLSYS1 PUMP SECONDARY Pump Power [hp] | 20.4667 | 18.3826 | [8 empty] | 2021-05-06
RI_LO_HEATSYS1 PUMP Pump Power [hp] | HEATSYS1 PUMP Pump Power [hp] | 19.5922 | 17.1774 | [8 empty] | 2021-05-06
RI_LO_TOWERWATERSYS PUMP Pump Power [hp] | TOWERWATERSYS PUMP Pump Power [hp] | 39.6407 | 35.6108 | [8 empty] | 2021-05-06
RI_LO_PLANT CIRC PUMP Pump Power [hp] | PLANT CIRC PUMP Pump Power [hp] | 4.4846 | 4.4225 | [8 empty] | 2021-05-06
RI_LO_Datacenter PLANT CIRC PUMP Pump Power [hp] | Datacenter PLANT CIRC PUMP Pump Power [hp] | 4.4846 | 4.4225 | [8 empty] | 2021-05-06
RI_LO_ZN_VAV_BOXes_Max_Reheat_Water_Flow_GPM | ZN_VAV_BOXes_Max_Reheat_Water_Flow_GPM | 466.7536 | 448.7245 | [8 empty] | 2021-05-06
RI_LO_COOLSYS1 PUMP SECONDARY VSD | COOLSYS1 PUMP SECONDARY VSD | No | No | [8 empty] | 2021-05-06
RI_LO_HEATSYS1 PUMP VSD | HEATSYS1 PUMP VSD | No | No | [8 empty] | 2021-05-06
RI_LO_DATACENTER BASEMENT Cooling Capacity [ton] | DATACENTER BASEMENT Cooling Capacity [ton] | 121.4724 | 121.1121 | [8 empty] | 2021-05-06
RI_LO_DATACENTER BOT Cooling Capacity [ton] | DATACENTER BOT Cooling Capacity [ton] | 2.6632 | 2.6397 | [8 empty] | 2021-05-06
RI_LO_DATACENTER MID Cooling Capacity [ton] | DATACENTER MID Cooling Capacity [ton] | 25.5064 | 25.3005 | [8 empty] | 2021-05-06
RI_LO_DATACENTER TOP Cooling Capacity [ton] | DATACENTER TOP Cooling Capacity [ton] | 2.5968 | 2.5768 | [8 empty] | 2021-05-06
id | item | Zone5A(RI-Providence-RI) ASHRAE901-state_STD2016 | Zone5A(RI-Providence-RI) ASHRAE901-state_STD2019 | [8 empty] | 2021-05-06
RI_RS_PSZ-AC:1 Cooling Capacity [ton] | PSZ-AC:1 Cooling Capacity [ton] | 10.0754 | 9.6727 | [8 empty] | 2021-05-06
RI_RS_PSZ-AC:2 Cooling Capacity [ton] | PSZ-AC:2 Cooling Capacity [ton] | 47.3457 | 45.7477 | [8 empty] | 2021-05-06
RI_RS_PSZ-AC:3 Cooling Capacity [ton] | PSZ-AC:3 Cooling Capacity [ton] | 6.2454 | 6.0861 | [8 empty] | 2021-05-06
RI_RS_PSZ-AC:4 Cooling Capacity [ton] | PSZ-AC:4 Cooling Capacity [ton] | 5.0695 | 4.9008 | [8 empty] | 2021-05-06
RI_RS_PSZ-AC:1 Supply Flow Rate [cfm] | PSZ-AC:1 Supply Flow Rate [cfm] | 3856.3616 | 3580.9072 | [8 empty] | 2021-05-06
RI_RS_PSZ-AC:2 Supply Flow Rate [cfm] | PSZ-AC:2 Supply Flow Rate [cfm] | 15192.3696 | 14387.1952 | [8 empty] | 2021-05-06
RI_RS_PSZ-AC:3 Supply Flow Rate [cfm] | PSZ-AC:3 Supply Flow Rate [cfm] | 2267.2016 | 2182.4464 | [8 empty] | 2021-05-06
RI_RS_PSZ-AC:4 Supply Flow Rate [cfm] | PSZ-AC:4 Supply Flow Rate [cfm] | 1716.2928 | 1652.7264 | [8 empty] | 2021-05-06
RI_RS_PSZ-AC:1 OA Rate [cfm] | PSZ-AC:1 OA Rate [cfm] | 490.669 | 490.669 | [8 empty] | 2021-05-06
RI_RS_PSZ-AC:2 OA Rate [cfm] | PSZ-AC:2 OA Rate [cfm] | 4005.1282 | 4005.1282 | [8 empty] | 2021-05-06
RI_RS_PSZ-AC:3 OA Rate [cfm] | PSZ-AC:3 OA Rate [cfm] | 377.3937 | 377.3937 | [8 empty] | 2021-05-06
RI_RS_PSZ-AC:4 OA Rate [cfm] | PSZ-AC:4 OA Rate [cfm] | 377.3937 | 377.3937 | [8 empty] | 2021-05-06
RI_RS_PSZ-AC:1 OA Damper [gravity, motorized] | PSZ-AC:1 OA Damper [gravity, motorized] | motorized | motorized | [8 empty] | 2021-05-06
RI_RS_PSZ-AC:2 OA Damper [gravity, motorized] | PSZ-AC:2 OA Damper [gravity, motorized] | motorized | motorized | [8 empty] | 2021-05-06
RI_RS_PSZ-AC:3 OA Damper [gravity, motorized] | PSZ-AC:3 OA Damper [gravity, motorized] | motorized | motorized | [8 empty] | 2021-05-06
RI_RS_PSZ-AC:4 OA Damper [gravity, motorized] | PSZ-AC:4 OA Damper [gravity, motorized] | motorized | motorized | [8 empty] | 2021-05-06
RI_RS_PSZ-AC:1 Heating Capacity [kBtu/hr] | PSZ-AC:1 Heating Capacity [kBtu/hr] | 174.453 | 162.7113 | [8 empty] | 2021-05-06
RI_RS_PSZ-AC:2 Heating Capacity [kBtu/hr] | PSZ-AC:2 Heating Capacity [kBtu/hr] | 817.2479 | 783.8687 | [8 empty] | 2021-05-06
RI_RS_PSZ-AC:3 Heating Capacity [kBtu/hr] | PSZ-AC:3 Heating Capacity [kBtu/hr] | 109.391 | 106.6696 | [8 empty] | 2021-05-06
RI_RS_PSZ-AC:4 Heating Capacity [kBtu/hr] | PSZ-AC:4 Heating Capacity [kBtu/hr] | 89.0981 | 85.9598 | [8 empty] | 2021-05-06
id | item | Zone5A(RI-Providence-RI) ASHRAE901-state_STD2016 | Zone5A(RI-Providence-RI) ASHRAE901-state_STD2019 | [8 empty] | 2021-05-06
RI_PS_VAV_POD_1 Cooling Capacity [ton] | VAV_POD_1 Cooling Capacity [ton] | 18.8414 | 18.295 | [8 empty] | 2021-05-06
RI_PS_VAV_POD_2 Cooling Capacity [ton] | VAV_POD_2 Cooling Capacity [ton] | 18.613 | 18.2422 | [8 empty] | 2021-05-06
RI_PS_VAV_POD_3 Cooling Capacity [ton] | VAV_POD_3 Cooling Capacity [ton] | 17.0999 | 16.3041 | [8 empty] | 2021-05-06
RI_PS_VAV_OTHER Cooling Capacity [ton] | VAV_OTHER Cooling Capacity [ton] | 26.0186 | 24.4623 | [8 empty] | 2021-05-06
RI_PS_PSZ-AC_1:6 Cooling Capacity [ton] | PSZ-AC_1:6 Cooling Capacity [ton] | 8.0948 | 7.8329 | [8 empty] | 2021-05-06
RI_PS_PSZ-AC_2:5 Cooling Capacity [ton] | PSZ-AC_2:5 Cooling Capacity [ton] | 5.3145 | 5.287 | [8 empty] | 2021-05-06
RI_PS_PSZ-AC_2:7 Cooling Capacity [ton] | PSZ-AC_2:7 Cooling Capacity [ton] | 10.5074 | 10.5074 | [8 empty] | 2021-05-06
RI_PS_VAV_POD_1 Supply Flow Rate [cfm] | VAV_POD_1 Supply Flow Rate [cfm] | 5657.4096 | 5487.8992 | [8 empty] | 2021-05-06
RI_PS_VAV_POD_2 Supply Flow Rate [cfm] | VAV_POD_2 Supply Flow Rate [cfm] | 5593.8432 | 5466.7104 | [8 empty] | 2021-05-06
RI_PS_VAV_POD_3 Supply Flow Rate [cfm] | VAV_POD_3 Supply Flow Rate [cfm] | 5127.6896 | 4894.6128 | [8 empty] | 2021-05-06
RI_PS_VAV_OTHER Supply Flow Rate [cfm] | VAV_OTHER Supply Flow Rate [cfm] | 7797.4784 | 7331.3248 | [8 empty] | 2021-05-06
RI_PS_PSZ-AC_2:5 Supply Flow Rate [cfm] | PSZ-AC_2:5 Supply Flow Rate [cfm] | 1589.16 | 1589.16 | [8 empty] | 2021-05-06
RI_PS_PSZ-AC_1:6 Supply Flow Rate [cfm] | PSZ-AC_1:6 Supply Flow Rate [cfm] | 2521.4672 | 2415.5232 | [8 empty] | 2021-05-06
RI_PS_PSZ-AC_2:7 Supply Flow Rate [cfm] | PSZ-AC_2:7 Supply Flow Rate [cfm] | 3157.1312 | 3157.1312 | [8 empty] | 2021-05-06
RI_PS_Supply Air Temp. Reset Flag | Supply Air Temp. Reset Flag | Yes | Yes | [8 empty] | 2021-05-06
RI_PS_VAV_POD_1 OA Rate [cfm] | VAV_POD_1 OA Rate [cfm] | 5653.6592 | 5490.0393 | [8 empty] | 2021-05-06
RI_PS_VAV_POD_2 OA Rate [cfm] | VAV_POD_2 OA Rate [cfm] | 5583.0581 | 5474.1689 | [8 empty] | 2021-05-06
RI_PS_VAV_POD_3 OA Rate [cfm] | VAV_POD_3 OA Rate [cfm] | 5131.3976 | 4892.5999 | [8 empty] | 2021-05-06
RI_PS_VAV_OTHER OA Rate [cfm] | VAV_OTHER OA Rate [cfm] | 3736.1787 | 2988.8921 | [8 empty] | 2021-05-06
RI_PS_PSZ-AC_2:5 OA Rate [cfm] | PSZ-AC_2:5 OA Rate [cfm] | 1152.7343 | 1152.7343 | [8 empty] | 2021-05-06
RI_PS_PSZ-AC_1:6 OA Rate [cfm] | PSZ-AC_1:6 OA Rate [cfm] | 539.9118 | 539.9118 | [8 empty] | 2021-05-06
RI_PS_PSZ-AC_2:7 OA Rate [cfm] | PSZ-AC_2:7 OA Rate [cfm] | 3153.0841 | 3153.0841 | [8 empty] | 2021-05-06
RI_PS_VAV_POD_1 OA Damper [gravity, motorized] | VAV_POD_1 OA Damper [gravity, motorized] | motorized | motorized | [8 empty] | 2021-05-06
RI_PS_VAV_POD_2 OA Damper [gravity, motorized] | VAV_POD_2 OA Damper [gravity, motorized] | motorized | motorized | [8 empty] | 2021-05-06
RI_PS_VAV_POD_3 OA Damper [gravity, motorized] | VAV_POD_3 OA Damper [gravity, motorized] | motorized | motorized | [8 empty] | 2021-05-06
RI_PS_VAV_OTHER OA Damper [gravity, motorized] | VAV_OTHER OA Damper [gravity, motorized] | motorized | motorized | [8 empty] | 2021-05-06
RI_PS_PSZ-AC_2:5 OA Damper [gravity, motorized] | PSZ-AC_2:5 OA Damper [gravity, motorized] | motorized | motorized | [8 empty] | 2021-05-06
RI_PS_PSZ-AC_1:6 OA Damper [gravity, motorized] | PSZ-AC_1:6 OA Damper [gravity, motorized] | motorized | motorized | [8 empty] | 2021-05-06
RI_PS_PSZ-AC_2:7 OA Damper [gravity, motorized] | PSZ-AC_2:7 OA Damper [gravity, motorized] | motorized | motorized | [8 empty] | 2021-05-06
RI_PS_VAV_POD_1 (economizer) | VAV_POD_1 (economizer) | DifferentialDryBulb | DifferentialDryBulb | [8 empty] | 2021-05-06
RI_PS_VAV_POD_2 (economizer) | VAV_POD_2 (economizer) | DifferentialDryBulb | DifferentialDryBulb | [8 empty] | 2021-05-06
RI_PS_VAV_POD_3 (economizer) | VAV_POD_3 (economizer) | DifferentialDryBulb | DifferentialDryBulb | [8 empty] | 2021-05-06
RI_PS_VAV_OTHER (economizer) | VAV_OTHER (economizer) | DifferentialDryBulb | DifferentialDryBulb | [8 empty] | 2021-05-06
RI_PS_PSZ-AC_2:5 (economizer) | PSZ-AC_2:5 (economizer) | DifferentialDryBulb | DifferentialDryBulb | [8 empty] | 2021-05-06
RI_PS_PSZ-AC_1:6 (economizer) | PSZ-AC_1:6 (economizer) | DifferentialDryBulb | DifferentialDryBulb | [8 empty] | 2021-05-06
RI_PS_PSZ-AC_2:7 (economizer) | PSZ-AC_2:7 (economizer) | DifferentialDryBulb | DifferentialDryBulb | [8 empty] | 2021-05-06
RI_PS_VAV_Pod_1_ERV Flag | VAV_Pod_1_ERV Flag | Yes | Yes | [8 empty] | 2021-05-06
RI_PS_VAV_Pod_2_ERV Flag | VAV_Pod_2_ERV Flag | Yes | Yes | [8 empty] | 2021-05-06
RI_PS_VAV_Pod_3_ERV Flag | VAV_Pod_3_ERV Flag | Yes | Yes | [8 empty] | 2021-05-06
RI_PS_VAV_OTHER_ERV Flag | VAV_OTHER_ERV Flag | Yes | Yes | [8 empty] | 2021-05-06
RI_PS_PSZ_AC_2_5_ERV Flag | PSZ_AC_2_5_ERV Flag | Yes | Yes | [8 empty] | 2021-05-06
RI_PS_PSZ_AC_2_7_ERV Flag | PSZ_AC_2_7_ERV Flag | Yes | Yes | [8 empty] | 2021-05-06
RI_PS_HEATSYS1 Capacity [MMBTU/h] | HEATSYS1 Capacity [MMBTU/h] | 1.0696 | 1.0261 | [8 empty] | 2021-05-06
RI_PS_HEATSYS1 Flow Rate [gal/min] | HEATSYS1 Flow Rate [gal/min] | 109.7703 | 105.3141 | [8 empty] | 2021-05-06
RI_PS_VAV_POD_1 Fan Power [hp] | VAV_POD_1 Fan Power [hp] | 8.3414 | 8.0995 | [8 empty] | 2021-05-06
RI_PS_VAV_POD_2 Fan Power [hp] | VAV_POD_2 Fan Power [hp] | 8.2402 | 8.0761 | [8 empty] | 2021-05-06
RI_PS_VAV_POD_3 Fan Power [hp] | VAV_POD_3 Fan Power [hp] | 7.5703 | 7.2181 | [8 empty] | 2021-05-06
RI_PS_VAV_OTHER Fan Power [hp] | VAV_OTHER Fan Power [hp] | 11.4315 | 10.7478 | [8 empty] | 2021-05-06
RI_PS_HEATSYS1 Pump Power [hp] | HEATSYS1 Pump Power [hp] | 2.3728 | 2.2539 | [8 empty] | 2021-05-06
RI_PS_PSZ-AC_1:6 Heating Capacity [kBtu/hr] | PSZ-AC_1:6 Heating Capacity [kBtu/hr] | 210.9343 | 202.3452 | [8 empty] | 2021-05-06
RI_PS_PSZ-AC_2:5 Heating Capacity [kBtu/hr] | PSZ-AC_2:5 Heating Capacity [kBtu/hr] | 136.9666 | 136.6621 | [8 empty] | 2021-05-06
RI_PS_PSZ-AC_2:7 Heating Capacity [kBtu/hr] | PSZ-AC_2:7 Heating Capacity [kBtu/hr] | 329.9576 | 329.9576 | [8 empty] | 2021-05-06
RI_PS_ZN_VAV_BOXes_Max_Reheat_Water_Flow_GPM | ZN_VAV_BOXes_Max_Reheat_Water_Flow_GPM | 71.2531 | 68.3598 | [8 empty] | 2021-05-06
id | item | Zone5A(RI-Providence-RI) ASHRAE901-state_STD2016 | Zone5A(RI-Providence-RI) ASHRAE901-state_STD2019 | [8 empty] | 2021-05-06
RI_SH_SAC_FRONTOFFICE Cooling Capacity [ton] | SAC_FRONTOFFICE Cooling Capacity [ton] | 2.2316 | 2.1186 | [8 empty] | 2021-05-06
RI_SH_SAC_FRONTLOUNGE Cooling Capacity [ton] | SAC_FRONTLOUNGE Cooling Capacity [ton] | 5.9736 | 5.6713 | [8 empty] | 2021-05-06
RI_SH_SAC_MEETINGROOM Cooling Capacity [ton] | SAC_MEETINGROOM Cooling Capacity [ton] | 2.8275 | 2.7522 | [8 empty] | 2021-05-06
RI_SH_SAC_EXC_EMPLGE_RESTRM Cooling Capacity [ton] | SAC_EXC_EMPLGE_RESTRM Cooling Capacity [ton] | 5.8027 | 5.7616 | [8 empty] | 2021-05-06
RI_SH_SAC_FO_ADDAQ SUPPLY FAN Supply Flow Rate [cfm] | SAC_FO_ADDAQ SUPPLY FAN Supply Flow Rate [cfm] | 762.7968 | 699.2304 | [8 empty] | 2021-05-06
RI_SH_SAC_FL_ADDAQ SUPPLY FAN Supply Flow Rate [cfm] | SAC_FL_ADDAQ SUPPLY FAN Supply Flow Rate [cfm] | 1801.048 | 1695.104 | [8 empty] | 2021-05-06
RI_SH_SAC_MR_ADDAQ SUPPLY FAN Supply Flow Rate [cfm] | SAC_MR_ADDAQ SUPPLY FAN Supply Flow Rate [cfm] | 847.552 | 826.3632 | [8 empty] | 2021-05-06
RI_SH_SAC_EXC_ADDAQ SUPPLY FAN Supply Flow Rate [cfm] | SAC_EXC_ADDAQ SUPPLY FAN Supply Flow Rate [cfm] | 2161.2576 | 2140.0688 | [8 empty] | 2021-05-06
RI_SH_SAC_Exc_EmpLge_RestRm OA Rate [cfm] | SAC_Exc_EmpLge_RestRm OA Rate [cfm] | 199.9928 | 199.9928 | [8 empty] | 2021-05-06
RI_SH_SAC_FrontLounge OA Rate [cfm] | SAC_FrontLounge OA Rate [cfm] | 500.0133 | 500.0133 | [8 empty] | 2021-05-06
RI_SH_SAC_FrontOffice OA Rate [cfm] | SAC_FrontOffice OA Rate [cfm] | 119.2938 | 119.2938 | [8 empty] | 2021-05-06
RI_SH_SAC_MeetingRoom OA Rate [cfm] | SAC_MeetingRoom OA Rate [cfm] | 267.7629 | 267.7629 | [8 empty] | 2021-05-06
RI_SH_SAC_FrontLounge OA Damper [gravity, motorized] | SAC_FrontLounge OA Damper [gravity, motorized] | motorized | motorized | [8 empty] | 2021-05-06
RI_SH_SAC_FrontOffice (economizer) | SAC_FrontOffice (economizer) | No | No | [8 empty] | 2021-05-06
RI_SH_SAC_FrontLounge (economizer) | SAC_FrontLounge (economizer) | DifferentialDryBulb | DifferentialDryBulb | [8 empty] | 2021-05-06
RI_SH_SAC_MeetingRoom (economizer) | SAC_MeetingRoom (economizer) | No | No | [8 empty] | 2021-05-06
RI_SH_SAC_Exc_EmpLge_RestRm (economizer) | SAC_Exc_EmpLge_RestRm (economizer) | DifferentialDryBulb | DifferentialDryBulb | [8 empty] | 2021-05-06
RI_SH_SAC_FRONTOFFICE Heating Capacity [kBtu/hr] | SAC_FRONTOFFICE Heating Capacity [kBtu/hr] | 35.8007 | 34.0557 | [8 empty] | 2021-05-06
RI_SH_SAC_FRONTLOUNGE Heating Capacity [kBtu/hr] | SAC_FRONTLOUNGE Heating Capacity [kBtu/hr] | 99.8148 | 96.4811 | [8 empty] | 2021-05-06
RI_SH_SAC_MEETINGROOM Heating Capacity [kBtu/hr] | SAC_MEETINGROOM Heating Capacity [kBtu/hr] | 49.3561 | 48.5253 | [8 empty] | 2021-05-06
RI_SH_SAC_EXC_EMPLGE_RESTRM Heating Capacity [kBtu/hr] | SAC_EXC_EMPLGE_RESTRM Heating Capacity [kBtu/hr] | 92.7626 | 92.107 | [8 empty] | 2021-05-06
id | item | Zone5A(RI-Providence-RI) ASHRAE901-state_STD2016 | Zone5A(RI-Providence-RI) ASHRAE901-state_STD2019 | [8 empty] | 2021-05-06
RI_MA_SPLIT GSW COOLING COIL Cooling Capacity [ton] | SPLIT GSW COOLING COIL Cooling Capacity [ton] | 0.80771 | 0.79376 | [8 empty] | 2021-05-06
RI_MA_SPLIT GNW COOLING COIL Cooling Capacity [ton] | SPLIT GNW COOLING COIL Cooling Capacity [ton] | 0.76686 | 0.75357 | [8 empty] | 2021-05-06
RI_MA_SPLIT OFFICE COOLING COIL Cooling Capacity [ton] | SPLIT OFFICE COOLING COIL Cooling Capacity [ton] | 1.7131 | 1.5848 | [8 empty] | 2021-05-06
RI_MA_SPLIT GNE COOLING COIL Cooling Capacity [ton] | SPLIT GNE COOLING COIL Cooling Capacity [ton] | 0.66865 | 0.65705 | [8 empty] | 2021-05-06
RI_MA_SPLIT GN1 COOLING COIL Cooling Capacity [ton] | SPLIT GN1 COOLING COIL Cooling Capacity [ton] | 0.57147 | 0.56244 | [8 empty] | 2021-05-06
RI_MA_SPLIT GN2 COOLING COIL Cooling Capacity [ton] | SPLIT GN2 COOLING COIL Cooling Capacity [ton] | 0.56952 | 0.56054 | [8 empty] | 2021-05-06
RI_MA_SPLIT GS1 COOLING COIL Cooling Capacity [ton] | SPLIT GS1 COOLING COIL Cooling Capacity [ton] | 0.6155 | 0.60529 | [8 empty] | 2021-05-06
RI_MA_SPLIT GS2 COOLING COIL Cooling Capacity [ton] | SPLIT GS2 COOLING COIL Cooling Capacity [ton] | 0.64748 | 0.63223 | [8 empty] | 2021-05-06
RI_MA_SPLIT MSW COOLING COIL Cooling Capacity [ton] | SPLIT MSW COOLING COIL Cooling Capacity [ton] | 1.997 | 1.9657 | [8 empty] | 2021-05-06
RI_MA_SPLIT MNW COOLING COIL Cooling Capacity [ton] | SPLIT MNW COOLING COIL Cooling Capacity [ton] | 1.9169 | 1.8872 | [8 empty] | 2021-05-06
RI_MA_SPLIT MSE COOLING COIL Cooling Capacity [ton] | SPLIT MSE COOLING COIL Cooling Capacity [ton] | 1.7482 | 1.7204 | [8 empty] | 2021-05-06
RI_MA_SPLIT MNE COOLING COIL Cooling Capacity [ton] | SPLIT MNE COOLING COIL Cooling Capacity [ton] | 1.5719 | 1.5427 | [8 empty] | 2021-05-06
RI_MA_SPLIT MN1 COOLING COIL Cooling Capacity [ton] | SPLIT MN1 COOLING COIL Cooling Capacity [ton] | 1.3019 | 1.2846 | [8 empty] | 2021-05-06
RI_MA_SPLIT MN2 COOLING COIL Cooling Capacity [ton] | SPLIT MN2 COOLING COIL Cooling Capacity [ton] | 1.2963 | 1.2791 | [8 empty] | 2021-05-06
RI_MA_SPLIT MS1 COOLING COIL Cooling Capacity [ton] | SPLIT MS1 COOLING COIL Cooling Capacity [ton] | 1.3777 | 1.3587 | [8 empty] | 2021-05-06
RI_MA_SPLIT MS2 COOLING COIL Cooling Capacity [ton] | SPLIT MS2 COOLING COIL Cooling Capacity [ton] | 1.3719 | 1.3531 | [8 empty] | 2021-05-06
RI_MA_SPLIT TSW COOLING COIL Cooling Capacity [ton] | SPLIT TSW COOLING COIL Cooling Capacity [ton] | 1.2502 | 1.2331 | [8 empty] | 2021-05-06
RI_MA_SPLIT TNW COOLING COIL Cooling Capacity [ton] | SPLIT TNW COOLING COIL Cooling Capacity [ton] | 1.1922 | 1.176 | [8 empty] | 2021-05-06
RI_MA_SPLIT TSE COOLING COIL Cooling Capacity [ton] | SPLIT TSE COOLING COIL Cooling Capacity [ton] | 1.1184 | 1.1039 | [8 empty] | 2021-05-06
RI_MA_SPLIT TNE COOLING COIL Cooling Capacity [ton] | SPLIT TNE COOLING COIL Cooling Capacity [ton] | 1.0339 | 1.0213 | [8 empty] | 2021-05-06
RI_MA_SPLIT TN1 COOLING COIL Cooling Capacity [ton] | SPLIT TN1 COOLING COIL Cooling Capacity [ton] | 0.84309 | 0.83336 | [8 empty] | 2021-05-06
RI_MA_SPLIT TN2 COOLING COIL Cooling Capacity [ton] | SPLIT TN2 COOLING COIL Cooling Capacity [ton] | 0.84434 | 0.83462 | [8 empty] | 2021-05-06
RI_MA_SPLIT TS1 COOLING COIL Cooling Capacity [ton] | SPLIT TS1 COOLING COIL Cooling Capacity [ton] | 0.92369 | 0.91243 | [8 empty] | 2021-05-06
RI_MA_SPLIT TS2 COOLING COIL Cooling Capacity [ton] | SPLIT TS2 COOLING COIL Cooling Capacity [ton] | 0.92513 | 0.91469 | [8 empty] | 2021-05-06
RI_MA_Split GN1 Furnace with DX Cooling OA Rate [cfm] | Split GN1 Furnace with DX Cooling OA Rate [cfm] | 54.9913 | 54.9913 | [8 empty] | 2021-05-06
RI_MA_Split GN2 Furnace with DX Cooling OA Rate [cfm] | Split GN2 Furnace with DX Cooling OA Rate [cfm] | 54.9913 | 54.9913 | [8 empty] | 2021-05-06
RI_MA_Split GNE Furnace with DX Cooling OA Rate [cfm] | Split GNE Furnace with DX Cooling OA Rate [cfm] | 54.9913 | 54.9913 | [8 empty] | 2021-05-06
RI_MA_Split GNW Furnace with DX Cooling OA Rate [cfm] | Split GNW Furnace with DX Cooling OA Rate [cfm] | 54.9913 | 54.9913 | [8 empty] | 2021-05-06
RI_MA_Split GS1 Furnace with DX Cooling OA Rate [cfm] | Split GS1 Furnace with DX Cooling OA Rate [cfm] | 54.9913 | 54.9913 | [8 empty] | 2021-05-06
RI_MA_Split GS2 Furnace with DX Cooling OA Rate [cfm] | Split GS2 Furnace with DX Cooling OA Rate [cfm] | 54.9913 | 54.9913 | [8 empty] | 2021-05-06
RI_MA_Split GSW Furnace with DX Cooling OA Rate [cfm] | Split GSW Furnace with DX Cooling OA Rate [cfm] | 56.9945 | 56.9945 | [8 empty] | 2021-05-06
RI_MA_Split MN1 Furnace with DX Cooling OA Rate [cfm] | Split MN1 Furnace with DX Cooling OA Rate [cfm] | 109.9824 | 109.9824 | [8 empty] | 2021-05-06
RI_MA_Split MN2 Furnace with DX Cooling OA Rate [cfm] | Split MN2 Furnace with DX Cooling OA Rate [cfm] | 109.9824 | 109.9824 | [8 empty] | 2021-05-06
RI_MA_Split MNE Furnace with DX Cooling OA Rate [cfm] | Split MNE Furnace with DX Cooling OA Rate [cfm] | 109.9824 | 109.9824 | [8 empty] | 2021-05-06
RI_MA_Split MNW Furnace with DX Cooling OA Rate [cfm] | Split MNW Furnace with DX Cooling OA Rate [cfm] | 109.9824 | 109.9824 | [8 empty] | 2021-05-06
RI_MA_Split MS1 Furnace with DX Cooling OA Rate [cfm] | Split MS1 Furnace with DX Cooling OA Rate [cfm] | 109.9824 | 109.9824 | [8 empty] | 2021-05-06
RI_MA_Split MS2 Furnace with DX Cooling OA Rate [cfm] | Split MS2 Furnace with DX Cooling OA Rate [cfm] | 109.9824 | 109.9824 | [8 empty] | 2021-05-06
RI_MA_Split MSE Furnace with DX Cooling OA Rate [cfm] | Split MSE Furnace with DX Cooling OA Rate [cfm] | 109.9824 | 109.9824 | [8 empty] | 2021-05-06
RI_MA_Split MSW Furnace with DX Cooling OA Rate [cfm] | Split MSW Furnace with DX Cooling OA Rate [cfm] | 109.9824 | 109.9824 | [8 empty] | 2021-05-06
RI_MA_Split Office Furnace with DX Cooling OA Rate [cfm] | Split Office Furnace with DX Cooling OA Rate [cfm] | 80.7372 | 80.7372 | [8 empty] | 2021-05-06
RI_MA_Split TN1 Furnace with DX Cooling OA Rate [cfm] | Split TN1 Furnace with DX Cooling OA Rate [cfm] | 54.9913 | 54.9913 | [8 empty] | 2021-05-06
RI_MA_Split TN2 Furnace with DX Cooling OA Rate [cfm] | Split TN2 Furnace with DX Cooling OA Rate [cfm] | 54.9913 | 54.9913 | [8 empty] | 2021-05-06
RI_MA_Split TNE Furnace with DX Cooling OA Rate [cfm] | Split TNE Furnace with DX Cooling OA Rate [cfm] | 54.9913 | 54.9913 | [8 empty] | 2021-05-06
RI_MA_Split TNW Furnace with DX Cooling OA Rate [cfm] | Split TNW Furnace with DX Cooling OA Rate [cfm] | 54.9913 | 54.9913 | [8 empty] | 2021-05-06
RI_MA_Split TS1 Furnace with DX Cooling OA Rate [cfm] | Split TS1 Furnace with DX Cooling OA Rate [cfm] | 54.9913 | 54.9913 | [8 empty] | 2021-05-06
RI_MA_Split TS2 Furnace with DX Cooling OA Rate [cfm] | Split TS2 Furnace with DX Cooling OA Rate [cfm] | 54.9913 | 54.9913 | [8 empty] | 2021-05-06
RI_MA_Split TSE Furnace with DX Cooling OA Rate [cfm] | Split TSE Furnace with DX Cooling OA Rate [cfm] | 54.9913 | 54.9913 | [8 empty] | 2021-05-06
RI_MA_Split TSW Furnace with DX Cooling OA Rate [cfm] | Split TSW Furnace with DX Cooling OA Rate [cfm] | 54.9913 | 54.9913 | [8 empty] | 2021-05-06
RI_MA_SPLIT GSW HEATING COIL Heating Capacity [kBtu/hr] | SPLIT GSW HEATING COIL Heating Capacity [kBtu/hr] | 9.6362 | 9.6949 | [8 empty] | 2021-05-06
RI_MA_SPLIT GNW HEATING COIL Heating Capacity [kBtu/hr] | SPLIT GNW HEATING COIL Heating Capacity [kBtu/hr] | 9.5683 | 9.6272 | [8 empty] | 2021-05-06
RI_MA_SPLIT OFFICE HEATING COIL Heating Capacity [kBtu/hr] | SPLIT OFFICE HEATING COIL Heating Capacity [kBtu/hr] | 22.337 | 22.4203 | [8 empty] | 2021-05-06
RI_MA_SPLIT GNE HEATING COIL Heating Capacity [kBtu/hr] | SPLIT GNE HEATING COIL Heating Capacity [kBtu/hr] | 9.5457 | 9.6046 | [8 empty] | 2021-05-06
RI_MA_SPLIT GN1 HEATING COIL Heating Capacity [kBtu/hr] | SPLIT GN1 HEATING COIL Heating Capacity [kBtu/hr] | 6.9912 | 7.0501 | [8 empty] | 2021-05-06
RI_MA_SPLIT GN2 HEATING COIL Heating Capacity [kBtu/hr] | SPLIT GN2 HEATING COIL Heating Capacity [kBtu/hr] | 6.9905 | 7.0494 | [8 empty] | 2021-05-06
RI_MA_SPLIT GS1 HEATING COIL Heating Capacity [kBtu/hr] | SPLIT GS1 HEATING COIL Heating Capacity [kBtu/hr] | 6.9393 | 6.998 | [8 empty] | 2021-05-06
RI_MA_SPLIT GS2 HEATING COIL Heating Capacity [kBtu/hr] | SPLIT GS2 HEATING COIL Heating Capacity [kBtu/hr] | 7.4399 | 7.4997 | [8 empty] | 2021-05-06
RI_MA_SPLIT MSW HEATING COIL Heating Capacity [kBtu/hr] | SPLIT MSW HEATING COIL Heating Capacity [kBtu/hr] | 17.539 | 17.6686 | [8 empty] | 2021-05-06
RI_MA_SPLIT MNW HEATING COIL Heating Capacity [kBtu/hr] | SPLIT MNW HEATING COIL Heating Capacity [kBtu/hr] | 17.6298 | 17.7593 | [8 empty] | 2021-05-06
RI_MA_SPLIT MSE HEATING COIL Heating Capacity [kBtu/hr] | SPLIT MSE HEATING COIL Heating Capacity [kBtu/hr] | 17.486 | 17.6156 | [8 empty] | 2021-05-06
RI_MA_SPLIT MNE HEATING COIL Heating Capacity [kBtu/hr] | SPLIT MNE HEATING COIL Heating Capacity [kBtu/hr] | 17.5767 | 17.7062 | [8 empty] | 2021-05-06
RI_MA_SPLIT MN1 HEATING COIL Heating Capacity [kBtu/hr] | SPLIT MN1 HEATING COIL Heating Capacity [kBtu/hr] | 12.1129 | 12.2377 | [8 empty] | 2021-05-06
RI_MA_SPLIT MN2 HEATING COIL Heating Capacity [kBtu/hr] | SPLIT MN2 HEATING COIL Heating Capacity [kBtu/hr] | 12.1115 | 12.2362 | [8 empty] | 2021-05-06
RI_MA_SPLIT MS1 HEATING COIL Heating Capacity [kBtu/hr] | SPLIT MS1 HEATING COIL Heating Capacity [kBtu/hr] | 12.0311 | 12.1557 | [8 empty] | 2021-05-06
RI_MA_SPLIT MS2 HEATING COIL Heating Capacity [kBtu/hr] | SPLIT MS2 HEATING COIL Heating Capacity [kBtu/hr] | 12.0296 | 12.1543 | [8 empty] | 2021-05-06
RI_MA_SPLIT TSW HEATING COIL Heating Capacity [kBtu/hr] | SPLIT TSW HEATING COIL Heating Capacity [kBtu/hr] | 12.3865 | 12.4482 | [8 empty] | 2021-05-06
RI_MA_SPLIT TNW HEATING COIL Heating Capacity [kBtu/hr] | SPLIT TNW HEATING COIL Heating Capacity [kBtu/hr] | 12.4405 | 12.5023 | [8 empty] | 2021-05-06
RI_MA_SPLIT TSE HEATING COIL Heating Capacity [kBtu/hr] | SPLIT TSE HEATING COIL Heating Capacity [kBtu/hr] | 12.3586 | 12.4203 | [8 empty] | 2021-05-06
RI_MA_SPLIT TNE HEATING COIL Heating Capacity [kBtu/hr] | SPLIT TNE HEATING COIL Heating Capacity [kBtu/hr] | 12.4126 | 12.4744 | [8 empty] | 2021-05-06
RI_MA_SPLIT TN1 HEATING COIL Heating Capacity [kBtu/hr] | SPLIT TN1 HEATING COIL Heating Capacity [kBtu/hr] | 9.3985 | 9.4602 | [8 empty] | 2021-05-06
RI_MA_SPLIT TN2 HEATING COIL Heating Capacity [kBtu/hr] | SPLIT TN2 HEATING COIL Heating Capacity [kBtu/hr] | 9.3978 | 9.4594 | [8 empty] | 2021-05-06
RI_MA_SPLIT TS1 HEATING COIL Heating Capacity [kBtu/hr] | SPLIT TS1 HEATING COIL Heating Capacity [kBtu/hr] | 9.3376 | 9.3991 | [8 empty] | 2021-05-06
RI_MA_SPLIT TS2 HEATING COIL Heating Capacity [kBtu/hr] | SPLIT TS2 HEATING COIL Heating Capacity [kBtu/hr] | 9.3367 | 9.3983 | [8 empty] | 2021-05-06
RI_MA_Split_GSW ERV Flag | Split_GSW ERV Flag | Yes | Yes | [8 empty] | 2021-05-06
RI_MA_Split_GNW ERV Flag | Split_GNW ERV Flag | Yes | Yes | [8 empty] | 2021-05-06
RI_MA_Split_GNE ERV Flag | Split_GNE ERV Flag | Yes | Yes | [8 empty] | 2021-05-06
RI_MA_Split_GN1 ERV Flag | Split_GN1 ERV Flag | Yes | Yes | [8 empty] | 2021-05-06
RI_MA_Split_GN2 ERV Flag | Split_GN2 ERV Flag | Yes | Yes | [8 empty] | 2021-05-06
RI_MA_Split_GS1 ERV Flag | Split_GS1 ERV Flag | Yes | Yes | [8 empty] | 2021-05-06
RI_MA_Split_GS2 ERV Flag | Split_GS2 ERV Flag | Yes | Yes | [8 empty] | 2021-05-06
RI_MA_Split_MSW ERV Flag | Split_MSW ERV Flag | Yes | Yes | [8 empty] | 2021-05-06
RI_MA_Split_MNW ERV Flag | Split_MNW ERV Flag | Yes | Yes | [8 empty] | 2021-05-06
RI_MA_Split_MSE ERV Flag | Split_MSE ERV Flag | Yes | Yes | [8 empty] | 2021-05-06
RI_MA_Split_MNE ERV Flag | Split_MNE ERV Flag | Yes | Yes | [8 empty] | 2021-05-06
RI_MA_Split_MN1 ERV Flag | Split_MN1 ERV Flag | Yes | Yes | [8 empty] | 2021-05-06
RI_MA_Split_MN2 ERV Flag | Split_MN2 ERV Flag | Yes | Yes | [8 empty] | 2021-05-06
RI_MA_Split_MS1 ERV Flag | Split_MS1 ERV Flag | Yes | Yes | [8 empty] | 2021-05-06
RI_MA_Split_MS2 ERV Flag | Split_MS2 ERV Flag | Yes | Yes | [8 empty] | 2021-05-06
RI_MA_Split_TSW ERV Flag | Split_TSW ERV Flag | Yes | Yes | [8 empty] | 2021-05-06
RI_MA_Split_TNW ERV Flag | Split_TNW ERV Flag | Yes | Yes | [8 empty] | 2021-05-06
RI_MA_Split_TSE ERV Flag | Split_TSE ERV Flag | Yes | Yes | [8 empty] | 2021-05-06
RI_MA_Split_TNE ERV Flag | Split_TNE ERV Flag | Yes | Yes | [8 empty] | 2021-05-06
RI_MA_Split_TN1 ERV Flag | Split_TN1 ERV Flag | Yes | Yes | [8 empty] | 2021-05-06
RI_MA_Split_TN2 ERV Flag | Split_TN2 ERV Flag | Yes | Yes | [8 empty] | 2021-05-06
RI_MA_Split_TS1 ERV Flag | Split_TS1 ERV Flag | Yes | Yes | [8 empty] | 2021-05-06
RI_MA_Split_TS2 ERV Flag | Split_TS2 ERV Flag | Yes | Yes | [8 empty] | 2021-05-06
id | item | Zone2A(SC-Beaufort-SC) ASHRAE901-state_STD2016 | Zone2A(SC-Beaufort-SC) ASHRAE901-state_STD2019 | Zone3A(SC-Columbia-SC) ASHRAE901-state_STD2016 | Zone3A(SC-Columbia-SC) ASHRAE901-state_STD2019 | [6 empty] | 2021-05-06
SC_SO_PSZ-AC:1 Cooling Capacity [ton] | PSZ-AC:1 Cooling Capacity [ton] | 2.0968 | 1.9992 | 2.0011 | 1.9047 | [6 empty] | 2021-05-06
SC_SO_PSZ-AC:2 Cooling Capacity [ton] | PSZ-AC:2 Cooling Capacity [ton] | 1.853 | 1.7763 | 1.7848 | 1.723 | [6 empty] | 2021-05-06
SC_SO_PSZ-AC:3 Cooling Capacity [ton] | PSZ-AC:3 Cooling Capacity [ton] | 1.2494 | 1.2017 | 1.1753 | 1.1343 | [6 empty] | 2021-05-06
SC_SO_PSZ-AC:4 Cooling Capacity [ton] | PSZ-AC:4 Cooling Capacity [ton] | 1.8527 | 1.7673 | 1.7812 | 1.7077 | [6 empty] | 2021-05-06
SC_SO_PSZ-AC:5 Cooling Capacity [ton] | PSZ-AC:5 Cooling Capacity [ton] | 1.4278 | 1.3764 | 1.3682 | 1.325 | [6 empty] | 2021-05-06
SC_SO_PSZ-AC:1 Supply Flow Rate [cfm] | PSZ-AC:1 Supply Flow Rate [cfm] | 678.0416 | 635.664 | 678.0416 | 635.664 | [6 empty] | 2021-05-06
SC_SO_PSZ-AC:2 Supply Flow Rate [cfm] | PSZ-AC:2 Supply Flow Rate [cfm] | 635.664 | 593.2864 | 635.664 | 593.2864 | [6 empty] | 2021-05-06
SC_SO_PSZ-AC:3 Supply Flow Rate [cfm] | PSZ-AC:3 Supply Flow Rate [cfm] | 466.1536 | 444.9648 | 444.9648 | 444.9648 | [6 empty] | 2021-05-06
SC_SO_PSZ-AC:4 Supply Flow Rate [cfm] | PSZ-AC:4 Supply Flow Rate [cfm] | 635.664 | 593.2864 | 635.664 | 593.2864 | [6 empty] | 2021-05-06
SC_SO_PSZ-AC:5 Supply Flow Rate [cfm] | PSZ-AC:5 Supply Flow Rate [cfm] | 529.72 | 508.5312 | 529.72 | 508.5312 | [6 empty] | 2021-05-06
SC_SO_PSZ-AC:1 OA Rate [cfm] | PSZ-AC:1 OA Rate [cfm] | 136.9178 | 136.9178 | 136.9178 | 136.9178 | [6 empty] | 2021-05-06
SC_SO_PSZ-AC:2 OA Rate [cfm] | PSZ-AC:2 OA Rate [cfm] | 103.7925 | 103.7925 | 103.7925 | 103.7925 | [6 empty] | 2021-05-06
SC_SO_PSZ-AC:3 OA Rate [cfm] | PSZ-AC:3 OA Rate [cfm] | 61.5711 | 61.5711 | 61.5711 | 61.5711 | [6 empty] | 2021-05-06
SC_SO_PSZ-AC:4 OA Rate [cfm] | PSZ-AC:4 OA Rate [cfm] | 103.7925 | 103.7925 | 103.7925 | 103.7925 | [6 empty] | 2021-05-06
SC_SO_PSZ-AC:5 OA Rate [cfm] | PSZ-AC:5 OA Rate [cfm] | 61.5711 | 61.5711 | 61.5711 | 61.5711 | [6 empty] | 2021-05-06
SC_SO_PSZ-AC:1 heating Capacity [kBtu/hr] | PSZ-AC:1 heating Capacity [kBtu/hr] | 11.3265 | 11.3265 | 12.0472 | 12.0472 | [6 empty] | 2021-05-06
SC_SO_PSZ-AC:2 heating Capacity [kBtu/hr] | PSZ-AC:2 heating Capacity [kBtu/hr] | 14.5809 | 14.09 | 15.8687 | 15.6418 | [6 empty] | 2021-05-06
SC_SO_PSZ-AC:3 heating Capacity [kBtu/hr] | PSZ-AC:3 heating Capacity [kBtu/hr] | 8.9093 | 8.6266 | 9.6586 | 9.5376 | [6 empty] | 2021-05-06
SC_SO_PSZ-AC:4 heating Capacity [kBtu/hr] | PSZ-AC:4 heating Capacity [kBtu/hr] | 14.3298 | 13.9112 | 15.6227 | 15.4371 | [6 empty] | 2021-05-06
SC_SO_PSZ-AC:5 heating Capacity [kBtu/hr] | PSZ-AC:5 heating Capacity [kBtu/hr] | 8.9093 | 8.6266 | 9.6924 | 9.5668 | [6 empty] | 2021-05-06
id | item | Zone2A(SC-Beaufort-SC) ASHRAE901-state_STD2016 | Zone2A(SC-Beaufort-SC) ASHRAE901-state_STD2019 | Zone3A(SC-Columbia-SC) ASHRAE901-state_STD2016 | Zone3A(SC-Columbia-SC) ASHRAE901-state_STD2019 | [6 empty] | 2021-05-06
SC_LO_CAV_BAS Supply Flow Rate [cfm] | CAV_BAS Supply Flow Rate [cfm] | 11569.0848 | 10700.344 | 11569.0848 | 10700.344 | [6 empty] | 2021-05-06
SC_LO_VAV_BOT WITH REHEAT Supply Flow Rate [cfm] | VAV_BOT WITH REHEAT Supply Flow Rate [cfm] | 19091.1088 | 18158.8016 | 19048.7312 | 18095.2352 | [6 empty] | 2021-05-06
SC_LO_VAV_MID WITH REHEAT Supply Flow Rate [cfm] | VAV_MID WITH REHEAT Supply Flow Rate [cfm] | 177477.3891 | 168450.9603 | 176778.1587 | 167730.5411 | [6 empty] | 2021-05-06
SC_LO_VAV_TOP WITH REHEAT Supply Flow Rate [cfm] | VAV_TOP WITH REHEAT Supply Flow Rate [cfm] | 18730.8992 | 17862.1584 | 18815.6544 | 18010.48 | [6 empty] | 2021-05-06
SC_LO_Supply Air Temp. Reset Flag | Supply Air Temp. Reset Flag | No | No | No | Yes | [6 empty] | 2021-05-06
SC_LO_CAV_BAS OA Rate [cfm] | CAV_BAS OA Rate [cfm] | 2542.8255 | 2542.8255 | 2542.8255 | 2542.8255 | [6 empty] | 2021-05-06
SC_LO_VAV_BOT WITH REHEAT OA Rate [cfm] | VAV_BOT WITH REHEAT OA Rate [cfm] | 5377.8022 | 4302.174 | 5377.8022 | 4302.174 | [6 empty] | 2021-05-06
SC_LO_VAV_MID WITH REHEAT OA Rate [cfm] | VAV_MID WITH REHEAT OA Rate [cfm] | 53777.9373 | 43021.7396 | 53777.9373 | 43021.7396 | [6 empty] | 2021-05-06
SC_LO_VAV_TOP WITH REHEAT OA Rate [cfm] | VAV_TOP WITH REHEAT OA Rate [cfm] | 5377.8022 | 4302.174 | 5377.8022 | 4302.174 | [6 empty] | 2021-05-06
SC_LO_AIRLOOP DATACENTER BASEMENT OA Rate [cfm] | AIRLOOP DATACENTER BASEMENT OA Rate [cfm] | 716.9654 | 716.9654 | 716.9654 | 716.9654 | [6 empty] | 2021-05-06
SC_LO_VAV_bot_WITH_REHEAT ERV Flag | VAV_bot_WITH_REHEAT ERV Flag | Yes | Yes | Yes | Yes | [6 empty] | 2021-05-06
SC_LO_VAV_mid_WITH_REHEAT ERV Flag | VAV_mid_WITH_REHEAT ERV Flag | Yes | Yes | Yes | Yes | [6 empty] | 2021-05-06
SC_LO_VAV_top_WITH_REHEAT ERV Flag | VAV_top_WITH_REHEAT ERV Flag | Yes | Yes | Yes | Yes | [6 empty] | 2021-05-06
SC_LO_COOLSYS1 CHILLER1 Capacity [ton] | COOLSYS1 CHILLER1 Capacity [ton] | 456.7596 | 407.337 | 417.0536 | 375.3111 | [6 empty] | 2021-05-06
SC_LO_COOLSYS1 CHILLER2 Capacity [ton] | COOLSYS1 CHILLER2 Capacity [ton] | 456.7596 | 407.337 | 417.0536 | 375.3111 | [6 empty] | 2021-05-06
SC_LO_TOWERWATERSYS COOLTOWER 1 Capacity [ton] | TOWERWATERSYS COOLTOWER 1 Capacity [ton] | 433.5459 | 386.6431 | 395.8582 | 356.2409 | [6 empty] | 2021-05-06
SC_LO_TOWERWATERSYS COOLTOWER 2 Capacity [ton] | TOWERWATERSYS COOLTOWER 2 Capacity [ton] | 433.5459 | 386.6431 | 395.8582 | 356.2409 | [6 empty] | 2021-05-06
SC_LO_HEATSYS1 BOILER Capacity [MMBTU/h] | HEATSYS1 BOILER Capacity [MMBTU/h] | 3423.4432 | 3006.3634 | 3573.554 | 3189.8072 | [6 empty] | 2021-05-06
SC_LO_COOLSYS1 PUMP Flow Rate [gal/min] | COOLSYS1 PUMP Flow Rate [gal/min] | 0 | 0 | 0 | 0 | [6 empty] | 2021-05-06
SC_LO_COOLSYS1 CHILLER1 PUMP Flow Rate [gal/min] | COOLSYS1 CHILLER1 PUMP Flow Rate [gal/min] | 717.3191 | 639.3957 | 657.3034 | 588.7175 | [6 empty] | 2021-05-06
SC_LO_COOLSYS1 CHILLER2 PUMP Flow Rate [gal/min] | COOLSYS1 CHILLER2 PUMP Flow Rate [gal/min] | 717.3191 | 639.3957 | 657.3034 | 588.7175 | [6 empty] | 2021-05-06
SC_LO_COOLSYS1 PUMP SECONDARY Flow Rate [gal/min] | COOLSYS1 PUMP SECONDARY Flow Rate [gal/min] | 1434.6381 | 1278.7914 | 1314.6084 | 1177.4365 | [6 empty] | 2021-05-06
SC_LO_HEATSYS1 PUMP Flow Rate [gal/min] | HEATSYS1 PUMP Flow Rate [gal/min] | 702.7066 | 617.0959 | 733.5197 | 654.7499 | [6 empty] | 2021-05-06
SC_LO_TOWERWATERSYS PUMP Flow Rate [gal/min] | TOWERWATERSYS PUMP Flow Rate [gal/min] | 2520.0429 | 2247.2588 | 2300.8329 | 2070.6862 | [6 empty] | 2021-05-06
SC_LO_PLANT CIRC PUMP Flow Rate [gal/min] | PLANT CIRC PUMP Flow Rate [gal/min] | 208.6013 | 207.7153 | 207.5822 | 206.6882 | [6 empty] | 2021-05-06
SC_LO_COOLSYS1 PUMP SECONDARY Pressure setpoint reset [yes,no] | COOLSYS1 PUMP SECONDARY Pressure setpoint reset [yes,no] | pump_ride_on_curve | pump_ride_on_curve | pump_ride_on_curve | pump_ride_on_curve | [6 empty] | 2021-05-06
SC_LO_COOLSYS1 CHILLER1 PUMP Pump Power [hp] | COOLSYS1 CHILLER1 PUMP Pump Power [hp] | 3.8697 | 3.4152 | 3.5459 | 3.1445 | [6 empty] | 2021-05-06
SC_LO_COOLSYS1 CHILLER2 PUMP Pump Power [hp] | COOLSYS1 CHILLER2 PUMP Pump Power [hp] | 3.8697 | 3.4152 | 3.5459 | 3.1445 | [6 empty] | 2021-05-06
SC_LO_COOLSYS1 PUMP SECONDARY Pump Power [hp] | COOLSYS1 PUMP SECONDARY Pump Power [hp] | 23.2181 | 20.491 | 21.2755 | 18.8669 | [6 empty] | 2021-05-06
SC_LO_HEATSYS1 PUMP Pump Power [hp] | HEATSYS1 PUMP Pump Power [hp] | 15.1894 | 13.2068 | 15.8554 | 14.0127 | [6 empty] | 2021-05-06
SC_LO_TOWERWATERSYS PUMP Pump Power [hp] | TOWERWATERSYS PUMP Pump Power [hp] | 45.1178 | 39.8375 | 41.1957 | 36.7054 | [6 empty] | 2021-05-06
SC_LO_PLANT CIRC PUMP Pump Power [hp] | PLANT CIRC PUMP Pump Power [hp] | 4.5013 | 4.4378 | 4.4793 | 4.4159 | [6 empty] | 2021-05-06
SC_LO_Datacenter PLANT CIRC PUMP Pump Power [hp] | Datacenter PLANT CIRC PUMP Pump Power [hp] | 4.5013 | 4.4378 | 4.4793 | 4.4159 | [6 empty] | 2021-05-06
SC_LO_ZN_VAV_BOXes_Max_Reheat_Water_Flow_GPM | ZN_VAV_BOXes_Max_Reheat_Water_Flow_GPM | 413.507 | 384.9405 | 407.2459 | 389.1437 | [6 empty] | 2021-05-06
SC_LO_COOLSYS1 PUMP SECONDARY VSD | COOLSYS1 PUMP SECONDARY VSD | No | No | No | No | [6 empty] | 2021-05-06
SC_LO_HEATSYS1 PUMP VSD | HEATSYS1 PUMP VSD | No | No | No | No | [6 empty] | 2021-05-06
SC_LO_DATACENTER BASEMENT Cooling Capacity [ton] | DATACENTER BASEMENT Cooling Capacity [ton] | 122.3052 | 121.9491 | 121.9213 | 121.5644 | [6 empty] | 2021-05-06
SC_LO_DATACENTER BOT Cooling Capacity [ton] | DATACENTER BOT Cooling Capacity [ton] | 2.6558 | 2.6291 | 2.6262 | 2.5988 | [6 empty] | 2021-05-06
SC_LO_DATACENTER MID Cooling Capacity [ton] | DATACENTER MID Cooling Capacity [ton] | 25.2942 | 25.049 | 24.9929 | 24.7418 | [6 empty] | 2021-05-06
SC_LO_DATACENTER TOP Cooling Capacity [ton] | DATACENTER TOP Cooling Capacity [ton] | 2.5493 | 2.5285 | 2.5179 | 2.4983 | [6 empty] | 2021-05-06
id | item | Zone2A(SC-Beaufort-SC) ASHRAE901-state_STD2016 | Zone2A(SC-Beaufort-SC) ASHRAE901-state_STD2019 | Zone3A(SC-Columbia-SC) ASHRAE901-state_STD2016 | Zone3A(SC-Columbia-SC) ASHRAE901-state_STD2019 | [6 empty] | 2021-05-06
SC_RS_PSZ-AC:1 Cooling Capacity [ton] | PSZ-AC:1 Cooling Capacity [ton] | 11.3855 | 10.9759 | 10.7135 | 10.372 | [6 empty] | 2021-05-06
SC_RS_PSZ-AC:2 Cooling Capacity [ton] | PSZ-AC:2 Cooling Capacity [ton] | 50.947 | 48.0341 | 50.5517 | 47.6547 | [6 empty] | 2021-05-06
SC_RS_PSZ-AC:3 Cooling Capacity [ton] | PSZ-AC:3 Cooling Capacity [ton] | 7.0039 | 6.8617 | 6.6751 | 6.5138 | [6 empty] | 2021-05-06
SC_RS_PSZ-AC:4 Cooling Capacity [ton] | PSZ-AC:4 Cooling Capacity [ton] | 5.7779 | 5.6369 | 5.4431 | 5.2886 | [6 empty] | 2021-05-06
SC_RS_PSZ-AC:1 Supply Flow Rate [cfm] | PSZ-AC:1 Supply Flow Rate [cfm] | 4153.0048 | 3898.7392 | 4089.4384 | 3856.3616 | [6 empty] | 2021-05-06
SC_RS_PSZ-AC:2 Supply Flow Rate [cfm] | PSZ-AC:2 Supply Flow Rate [cfm] | 15298.3136 | 14408.384 | 15171.1808 | 14302.44 | [6 empty] | 2021-05-06
SC_RS_PSZ-AC:3 Supply Flow Rate [cfm] | PSZ-AC:3 Supply Flow Rate [cfm] | 2309.5792 | 2224.824 | 2288.3904 | 2203.6352 | [6 empty] | 2021-05-06
SC_RS_PSZ-AC:4 Supply Flow Rate [cfm] | PSZ-AC:4 Supply Flow Rate [cfm] | 1779.8592 | 1716.2928 | 1758.6704 | 1673.9152 | [6 empty] | 2021-05-06
SC_RS_PSZ-AC:1 OA Rate [cfm] | PSZ-AC:1 OA Rate [cfm] | 490.669 | 490.669 | 490.669 | 490.669 | [6 empty] | 2021-05-06
SC_RS_PSZ-AC:2 OA Rate [cfm] | PSZ-AC:2 OA Rate [cfm] | 4005.1282 | 4005.1282 | 4005.1282 | 4005.1282 | [6 empty] | 2021-05-06
SC_RS_PSZ-AC:3 OA Rate [cfm] | PSZ-AC:3 OA Rate [cfm] | 377.3937 | 377.3937 | 377.3937 | 377.3937 | [6 empty] | 2021-05-06
SC_RS_PSZ-AC:4 OA Rate [cfm] | PSZ-AC:4 OA Rate [cfm] | 377.3937 | 377.3937 | 377.3937 | 377.3937 | [6 empty] | 2021-05-06
SC_RS_PSZ-AC:1 OA Damper [gravity, motorized] | PSZ-AC:1 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2021-05-06
SC_RS_PSZ-AC:2 OA Damper [gravity, motorized] | PSZ-AC:2 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2021-05-06
SC_RS_PSZ-AC:3 OA Damper [gravity, motorized] | PSZ-AC:3 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2021-05-06
SC_RS_PSZ-AC:4 OA Damper [gravity, motorized] | PSZ-AC:4 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2021-05-06
SC_RS_PSZ-AC:1 Heating Capacity [kBtu/hr] | PSZ-AC:1 Heating Capacity [kBtu/hr] | 175.6194 | 165.6393 | 175.3671 | 165.3533 | [6 empty] | 2021-05-06
SC_RS_PSZ-AC:2 Heating Capacity [kBtu/hr] | PSZ-AC:2 Heating Capacity [kBtu/hr] | 737.8409 | 700.4527 | 751.2963 | 714.6601 | [6 empty] | 2021-05-06
SC_RS_PSZ-AC:3 Heating Capacity [kBtu/hr] | PSZ-AC:3 Heating Capacity [kBtu/hr] | 102.6196 | 100.0744 | 103.6313 | 100.9562 | [6 empty] | 2021-05-06
SC_RS_PSZ-AC:4 Heating Capacity [kBtu/hr] | PSZ-AC:4 Heating Capacity [kBtu/hr] | 83.0089 | 80.3155 | 83.8749 | 81.0901 | [6 empty] | 2021-05-06
id | item | Zone2A(SC-Beaufort-SC) ASHRAE901-state_STD2016 | Zone2A(SC-Beaufort-SC) ASHRAE901-state_STD2019 | Zone3A(SC-Columbia-SC) ASHRAE901-state_STD2016 | Zone3A(SC-Columbia-SC) ASHRAE901-state_STD2019 | [6 empty] | 2021-05-06
SC_PS_VAV_POD_1 Cooling Capacity [ton] | VAV_POD_1 Cooling Capacity [ton] | 18.7517 | 18.2054 | 18.7843 | 18.2093 | [6 empty] | 2021-05-06
SC_PS_VAV_POD_2 Cooling Capacity [ton] | VAV_POD_2 Cooling Capacity [ton] | 18.7423 | 18.1732 | 18.7378 | 18.1746 | [6 empty] | 2021-05-06
SC_PS_VAV_POD_3 Cooling Capacity [ton] | VAV_POD_3 Cooling Capacity [ton] | 17.1209 | 16.1958 | 17.1451 | 16.2787 | [6 empty] | 2021-05-06
SC_PS_VAV_OTHER Cooling Capacity [ton] | VAV_OTHER Cooling Capacity [ton] | 26.1862 | 24.527 | 26.2236 | 24.6515 | [6 empty] | 2021-05-06
SC_PS_PSZ-AC_1:6 Cooling Capacity [ton] | PSZ-AC_1:6 Cooling Capacity [ton] | 8.3662 | 7.988 | 8.3959 | 8.0194 | [6 empty] | 2021-05-06
SC_PS_PSZ-AC_2:5 Cooling Capacity [ton] | PSZ-AC_2:5 Cooling Capacity [ton] | 5.2657 | 5.0889 | 5.2041 | 5.0345 | [6 empty] | 2021-05-06
SC_PS_PSZ-AC_2:7 Cooling Capacity [ton] | PSZ-AC_2:7 Cooling Capacity [ton] | 10.5074 | 10.5074 | 10.5074 | 10.5074 | [6 empty] | 2021-05-06
SC_PS_VAV_POD_1 Supply Flow Rate [cfm] | VAV_POD_1 Supply Flow Rate [cfm] | 5636.2208 | 5466.7104 | 5636.2208 | 5466.7104 | [6 empty] | 2021-05-06
SC_PS_VAV_POD_2 Supply Flow Rate [cfm] | VAV_POD_2 Supply Flow Rate [cfm] | 5615.032 | 5445.5216 | 5615.032 | 5445.5216 | [6 empty] | 2021-05-06
SC_PS_VAV_POD_3 Supply Flow Rate [cfm] | VAV_POD_3 Supply Flow Rate [cfm] | 5127.6896 | 4852.2352 | 5148.8784 | 4894.6128 | [6 empty] | 2021-05-06
SC_PS_VAV_OTHER Supply Flow Rate [cfm] | VAV_OTHER Supply Flow Rate [cfm] | 7861.0448 | 7352.5136 | 7861.0448 | 7394.8912 | [6 empty] | 2021-05-06
SC_PS_PSZ-AC_2:5 Supply Flow Rate [cfm] | PSZ-AC_2:5 Supply Flow Rate [cfm] | 1589.16 | 1525.5936 | 1567.9712 | 1504.4048 | [6 empty] | 2021-05-06
SC_PS_PSZ-AC_1:6 Supply Flow Rate [cfm] | PSZ-AC_1:6 Supply Flow Rate [cfm] | 2500.2784 | 2394.3344 | 2521.4672 | 2415.5232 | [6 empty] | 2021-05-06
SC_PS_PSZ-AC_2:7 Supply Flow Rate [cfm] | PSZ-AC_2:7 Supply Flow Rate [cfm] | 3157.1312 | 3157.1312 | 3157.1312 | 3157.1312 | [6 empty] | 2021-05-06
SC_PS_Supply Air Temp. Reset Flag | Supply Air Temp. Reset Flag | No | No | No | No | [6 empty] | 2021-05-06
SC_PS_VAV_POD_1 OA Rate [cfm] | VAV_POD_1 OA Rate [cfm] | 5625.6476 | 5463.1507 | 5636.8777 | 5464.3161 | [6 empty] | 2021-05-06
SC_PS_VAV_POD_2 OA Rate [cfm] | VAV_POD_2 OA Rate [cfm] | 5621.6429 | 5453.4674 | 5621.1344 | 5453.9124 | [6 empty] | 2021-05-06
SC_PS_VAV_POD_3 OA Rate [cfm] | VAV_POD_3 OA Rate [cfm] | 5137.6907 | 4860.0963 | 5144.2804 | 4884.9719 | [6 empty] | 2021-05-06
SC_PS_VAV_OTHER OA Rate [cfm] | VAV_OTHER OA Rate [cfm] | 3736.1787 | 2988.8921 | 3736.1787 | 2988.8921 | [6 empty] | 2021-05-06
SC_PS_PSZ-AC_2:5 OA Rate [cfm] | PSZ-AC_2:5 OA Rate [cfm] | 1152.7343 | 1152.7343 | 1152.7343 | 1152.7343 | [6 empty] | 2021-05-06
SC_PS_PSZ-AC_1:6 OA Rate [cfm] | PSZ-AC_1:6 OA Rate [cfm] | 539.9118 | 539.9118 | 539.9118 | 539.9118 | [6 empty] | 2021-05-06
SC_PS_PSZ-AC_2:7 OA Rate [cfm] | PSZ-AC_2:7 OA Rate [cfm] | 3153.0841 | 3153.0841 | 3153.0841 | 3153.0841 | [6 empty] | 2021-05-06
SC_PS_VAV_POD_1 OA Damper [gravity, motorized] | VAV_POD_1 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2021-05-06
SC_PS_VAV_POD_2 OA Damper [gravity, motorized] | VAV_POD_2 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2021-05-06
SC_PS_VAV_POD_3 OA Damper [gravity, motorized] | VAV_POD_3 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2021-05-06
SC_PS_VAV_OTHER OA Damper [gravity, motorized] | VAV_OTHER OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2021-05-06
SC_PS_PSZ-AC_2:5 OA Damper [gravity, motorized] | PSZ-AC_2:5 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2021-05-06
SC_PS_PSZ-AC_1:6 OA Damper [gravity, motorized] | PSZ-AC_1:6 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2021-05-06
SC_PS_PSZ-AC_2:7 OA Damper [gravity, motorized] | PSZ-AC_2:7 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2021-05-06
SC_PS_VAV_POD_1 (economizer) | VAV_POD_1 (economizer) | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialEnthalpy | [6 empty] | 2021-05-06
SC_PS_VAV_POD_2 (economizer) | VAV_POD_2 (economizer) | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialEnthalpy | [6 empty] | 2021-05-06
SC_PS_VAV_POD_3 (economizer) | VAV_POD_3 (economizer) | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialEnthalpy | [6 empty] | 2021-05-06
SC_PS_VAV_OTHER (economizer) | VAV_OTHER (economizer) | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialEnthalpy | [6 empty] | 2021-05-06
SC_PS_PSZ-AC_2:5 (economizer) | PSZ-AC_2:5 (economizer) | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialEnthalpy | [6 empty] | 2021-05-06
SC_PS_PSZ-AC_1:6 (economizer) | PSZ-AC_1:6 (economizer) | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialEnthalpy | [6 empty] | 2021-05-06
SC_PS_PSZ-AC_2:7 (economizer) | PSZ-AC_2:7 (economizer) | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialEnthalpy | [6 empty] | 2021-05-06
SC_PS_VAV_Pod_1_ERV Flag | VAV_Pod_1_ERV Flag | Yes | Yes | Yes | Yes | [6 empty] | 2021-05-06
SC_PS_VAV_Pod_2_ERV Flag | VAV_Pod_2_ERV Flag | Yes | Yes | Yes | Yes | [6 empty] | 2021-05-06
SC_PS_VAV_Pod_3_ERV Flag | VAV_Pod_3_ERV Flag | Yes | Yes | Yes | Yes | [6 empty] | 2021-05-06
SC_PS_VAV_OTHER_ERV Flag | VAV_OTHER_ERV Flag | Yes | Yes | Yes | Yes | [6 empty] | 2021-05-06
SC_PS_PSZ_AC_2_5_ERV Flag | PSZ_AC_2_5_ERV Flag | Yes | Yes | Yes | Yes | [6 empty] | 2021-05-06
SC_PS_PSZ_AC_2_7_ERV Flag | PSZ_AC_2_7_ERV Flag | Yes | Yes | Yes | Yes | [6 empty] | 2021-05-06
SC_PS_HEATSYS1 Capacity [MMBTU/h] | HEATSYS1 Capacity [MMBTU/h] | 0.81551 | 0.7614 | 0.87425 | 0.82892 | [6 empty] | 2021-05-06
SC_PS_HEATSYS1 Flow Rate [gal/min] | HEATSYS1 Flow Rate [gal/min] | 83.6973 | 78.1442 | 89.726 | 85.0736 | [6 empty] | 2021-05-06
SC_PS_VAV_POD_1 Fan Power [hp] | VAV_POD_1 Fan Power [hp] | 8.3016 | 8.0598 | 8.3161 | 8.0615 | [6 empty] | 2021-05-06
SC_PS_VAV_POD_2 Fan Power [hp] | VAV_POD_2 Fan Power [hp] | 8.2975 | 8.0455 | 8.2955 | 8.0462 | [6 empty] | 2021-05-06
SC_PS_VAV_POD_3 Fan Power [hp] | VAV_POD_3 Fan Power [hp] | 7.5796 | 7.1701 | 7.5904 | 7.2068 | [6 empty] | 2021-05-06
SC_PS_VAV_OTHER Fan Power [hp] | VAV_OTHER Fan Power [hp] | 11.5052 | 10.7762 | 11.5216 | 10.8309 | [6 empty] | 2021-05-06
SC_PS_HEATSYS1 Pump Power [hp] | HEATSYS1 Pump Power [hp] | 1.8092 | 1.6724 | 1.9395 | 1.8207 | [6 empty] | 2021-05-06
SC_PS_PSZ-AC_1:6 Heating Capacity [kBtu/hr] | PSZ-AC_1:6 Heating Capacity [kBtu/hr] | 198.097 | 189.2604 | 200.6294 | 191.8914 | [6 empty] | 2021-05-06
SC_PS_PSZ-AC_2:5 Heating Capacity [kBtu/hr] | PSZ-AC_2:5 Heating Capacity [kBtu/hr] | 111.1677 | 109.2053 | 116.4531 | 114.5829 | [6 empty] | 2021-05-06
SC_PS_PSZ-AC_2:7 Heating Capacity [kBtu/hr] | PSZ-AC_2:7 Heating Capacity [kBtu/hr] | 260.8398 | 260.8398 | 277.4354 | 277.4354 | [6 empty] | 2021-05-06
SC_PS_ZN_VAV_BOXes_Max_Reheat_Water_Flow_GPM | ZN_VAV_BOXes_Max_Reheat_Water_Flow_GPM | 61.4641 | 56.929 | 63.277 | 59.794 | [6 empty] | 2021-05-06
id | item | Zone2A(SC-Beaufort-SC) ASHRAE901-state_STD2016 | Zone2A(SC-Beaufort-SC) ASHRAE901-state_STD2019 | Zone3A(SC-Columbia-SC) ASHRAE901-state_STD2016 | Zone3A(SC-Columbia-SC) ASHRAE901-state_STD2019 | [6 empty] | 2021-05-06
SC_SH_SAC_FRONTOFFICE Cooling Capacity [ton] | SAC_FRONTOFFICE Cooling Capacity [ton] | 2.5556 | 2.4225 | 2.5105 | 2.3674 | [6 empty] | 2021-05-06
SC_SH_SAC_FRONTLOUNGE Cooling Capacity [ton] | SAC_FRONTLOUNGE Cooling Capacity [ton] | 6.1498 | 5.8343 | 6.2239 | 5.9136 | [6 empty] | 2021-05-06
SC_SH_SAC_MEETINGROOM Cooling Capacity [ton] | SAC_MEETINGROOM Cooling Capacity [ton] | 2.9183 | 2.8269 | 2.9476 | 2.8608 | [6 empty] | 2021-05-06
SC_SH_SAC_EXC_EMPLGE_RESTRM Cooling Capacity [ton] | SAC_EXC_EMPLGE_RESTRM Cooling Capacity [ton] | 6.2439 | 6.2104 | 6.1821 | 6.1402 | [6 empty] | 2021-05-06
SC_SH_SAC_FO_ADDAQ SUPPLY FAN Supply Flow Rate [cfm] | SAC_FO_ADDAQ SUPPLY FAN Supply Flow Rate [cfm] | 805.1744 | 741.608 | 805.1744 | 741.608 | [6 empty] | 2021-05-06
SC_SH_SAC_FL_ADDAQ SUPPLY FAN Supply Flow Rate [cfm] | SAC_FL_ADDAQ SUPPLY FAN Supply Flow Rate [cfm] | 1843.4256 | 1758.6704 | 1864.6144 | 1779.8592 | [6 empty] | 2021-05-06
SC_SH_SAC_MR_ADDAQ SUPPLY FAN Supply Flow Rate [cfm] | SAC_MR_ADDAQ SUPPLY FAN Supply Flow Rate [cfm] | 868.7408 | 847.552 | 889.9296 | 868.7408 | [6 empty] | 2021-05-06
SC_SH_SAC_EXC_ADDAQ SUPPLY FAN Supply Flow Rate [cfm] | SAC_EXC_ADDAQ SUPPLY FAN Supply Flow Rate [cfm] | 2161.2576 | 2140.0688 | 2182.4464 | 2161.2576 | [6 empty] | 2021-05-06
SC_SH_SAC_Exc_EmpLge_RestRm OA Rate [cfm] | SAC_Exc_EmpLge_RestRm OA Rate [cfm] | 199.9928 | 199.9928 | 199.9928 | 199.9928 | [6 empty] | 2021-05-06
SC_SH_SAC_FrontLounge OA Rate [cfm] | SAC_FrontLounge OA Rate [cfm] | 500.0133 | 500.0133 | 500.0133 | 500.0133 | [6 empty] | 2021-05-06
SC_SH_SAC_FrontOffice OA Rate [cfm] | SAC_FrontOffice OA Rate [cfm] | 119.2938 | 119.2938 | 119.2938 | 119.2938 | [6 empty] | 2021-05-06
SC_SH_SAC_MeetingRoom OA Rate [cfm] | SAC_MeetingRoom OA Rate [cfm] | 267.7629 | 267.7629 | 267.7629 | 267.7629 | [6 empty] | 2021-05-06
SC_SH_SAC_FrontLounge OA Damper [gravity, motorized] | SAC_FrontLounge OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2021-05-06
SC_SH_SAC_FrontOffice (economizer) | SAC_FrontOffice (economizer) | No | No | No | No | [6 empty] | 2021-05-06
SC_SH_SAC_FrontLounge (economizer) | SAC_FrontLounge (economizer) | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialEnthalpy | [6 empty] | 2021-05-06
SC_SH_SAC_MeetingRoom (economizer) | SAC_MeetingRoom (economizer) | No | No | No | No | [6 empty] | 2021-05-06
SC_SH_SAC_Exc_EmpLge_RestRm (economizer) | SAC_Exc_EmpLge_RestRm (economizer) | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialEnthalpy | [6 empty] | 2021-05-06
SC_SH_SAC_FRONTOFFICE Heating Capacity [kBtu/hr] | SAC_FRONTOFFICE Heating Capacity [kBtu/hr] | 34.8771 | 32.8335 | 35.7913 | 33.6131 | [6 empty] | 2021-05-06
SC_SH_SAC_FRONTLOUNGE Heating Capacity [kBtu/hr] | SAC_FRONTLOUNGE Heating Capacity [kBtu/hr] | 90.831 | 87.3509 | 93.9534 | 90.5523 | [6 empty] | 2021-05-06
SC_SH_SAC_MEETINGROOM Heating Capacity [kBtu/hr] | SAC_MEETINGROOM Heating Capacity [kBtu/hr] | 44.5036 | 43.4956 | 46.089 | 45.1371 | [6 empty] | 2021-05-06
SC_SH_SAC_EXC_EMPLGE_RESTRM Heating Capacity [kBtu/hr] | SAC_EXC_EMPLGE_RESTRM Heating Capacity [kBtu/hr] | 88.5069 | 87.9801 | 89.9024 | 89.2509 | [6 empty] | 2021-05-06
id | item | Zone2A(SC-Beaufort-SC) ASHRAE901-state_STD2016 | Zone2A(SC-Beaufort-SC) ASHRAE901-state_STD2019 | Zone3A(SC-Columbia-SC) ASHRAE901-state_STD2016 | Zone3A(SC-Columbia-SC) ASHRAE901-state_STD2019 | [6 empty] | 2021-05-06
SC_MA_SPLIT GSW COOLING COIL Cooling Capacity [ton] | SPLIT GSW COOLING COIL Cooling Capacity [ton] | 0.93565 | 0.92425 | 0.90685 | 0.89601 | [6 empty] | 2021-05-06
SC_MA_SPLIT GNW COOLING COIL Cooling Capacity [ton] | SPLIT GNW COOLING COIL Cooling Capacity [ton] | 0.91934 | 0.90777 | 0.88667 | 0.87583 | [6 empty] | 2021-05-06
SC_MA_SPLIT OFFICE COOLING COIL Cooling Capacity [ton] | SPLIT OFFICE COOLING COIL Cooling Capacity [ton] | 1.7663 | 1.6887 | 1.6997 | 1.6274 | [6 empty] | 2021-05-06
SC_MA_SPLIT GNE COOLING COIL Cooling Capacity [ton] | SPLIT GNE COOLING COIL Cooling Capacity [ton] | 0.82171 | 0.81215 | 0.79161 | 0.78224 | [6 empty] | 2021-05-06
SC_MA_SPLIT GN1 COOLING COIL Cooling Capacity [ton] | SPLIT GN1 COOLING COIL Cooling Capacity [ton] | 0.72315 | 0.71393 | 0.68107 | 0.6721 | [6 empty] | 2021-05-06
SC_MA_SPLIT GN2 COOLING COIL Cooling Capacity [ton] | SPLIT GN2 COOLING COIL Cooling Capacity [ton] | 0.72154 | 0.71233 | 0.67953 | 0.67056 | [6 empty] | 2021-05-06
SC_MA_SPLIT GS1 COOLING COIL Cooling Capacity [ton] | SPLIT GS1 COOLING COIL Cooling Capacity [ton] | 0.73205 | 0.72122 | 0.70138 | 0.6899 | [6 empty] | 2021-05-06
SC_MA_SPLIT GS2 COOLING COIL Cooling Capacity [ton] | SPLIT GS2 COOLING COIL Cooling Capacity [ton] | 0.76831 | 0.75542 | 0.73328 | 0.7205 | [6 empty] | 2021-05-06
SC_MA_SPLIT MSW COOLING COIL Cooling Capacity [ton] | SPLIT MSW COOLING COIL Cooling Capacity [ton] | 2.076 | 2.0519 | 2.0132 | 1.991 | [6 empty] | 2021-05-06
SC_MA_SPLIT MNW COOLING COIL Cooling Capacity [ton] | SPLIT MNW COOLING COIL Cooling Capacity [ton] | 2.0598 | 2.0357 | 1.9853 | 1.9635 | [6 empty] | 2021-05-06
SC_MA_SPLIT MSE COOLING COIL Cooling Capacity [ton] | SPLIT MSE COOLING COIL Cooling Capacity [ton] | 1.8139 | 1.7923 | 1.7587 | 1.7384 | [6 empty] | 2021-05-06
SC_MA_SPLIT MNE COOLING COIL Cooling Capacity [ton] | SPLIT MNE COOLING COIL Cooling Capacity [ton] | 1.7848 | 1.7631 | 1.7306 | 1.7107 | [6 empty] | 2021-05-06
SC_MA_SPLIT MN1 COOLING COIL Cooling Capacity [ton] | SPLIT MN1 COOLING COIL Cooling Capacity [ton] | 1.5142 | 1.4913 | 1.4279 | 1.4104 | [6 empty] | 2021-05-06
SC_MA_SPLIT MN2 COOLING COIL Cooling Capacity [ton] | SPLIT MN2 COOLING COIL Cooling Capacity [ton] | 1.506 | 1.4873 | 1.424 | 1.4065 | [6 empty] | 2021-05-06
SC_MA_SPLIT MS1 COOLING COIL Cooling Capacity [ton] | SPLIT MS1 COOLING COIL Cooling Capacity [ton] | 1.5367 | 1.5179 | 1.4729 | 1.455 | [6 empty] | 2021-05-06
SC_MA_SPLIT MS2 COOLING COIL Cooling Capacity [ton] | SPLIT MS2 COOLING COIL Cooling Capacity [ton] | 1.5329 | 1.5141 | 1.4693 | 1.4513 | [6 empty] | 2021-05-06
SC_MA_SPLIT TSW COOLING COIL Cooling Capacity [ton] | SPLIT TSW COOLING COIL Cooling Capacity [ton] | 1.2663 | 1.2541 | 1.2449 | 1.2337 | [6 empty] | 2021-05-06
SC_MA_SPLIT TNW COOLING COIL Cooling Capacity [ton] | SPLIT TNW COOLING COIL Cooling Capacity [ton] | 1.2461 | 1.2342 | 1.2176 | 1.2069 | [6 empty] | 2021-05-06
SC_MA_SPLIT TSE COOLING COIL Cooling Capacity [ton] | SPLIT TSE COOLING COIL Cooling Capacity [ton] | 1.1613 | 1.1497 | 1.1562 | 1.1451 | [6 empty] | 2021-05-06
SC_MA_SPLIT TNE COOLING COIL Cooling Capacity [ton] | SPLIT TNE COOLING COIL Cooling Capacity [ton] | 1.1236 | 1.1122 | 1.1084 | 1.0976 | [6 empty] | 2021-05-06
SC_MA_SPLIT TN1 COOLING COIL Cooling Capacity [ton] | SPLIT TN1 COOLING COIL Cooling Capacity [ton] | 0.92909 | 0.91977 | 0.89633 | 0.8876 | [6 empty] | 2021-05-06
SC_MA_SPLIT TN2 COOLING COIL Cooling Capacity [ton] | SPLIT TN2 COOLING COIL Cooling Capacity [ton] | 0.92452 | 0.91521 | 0.8919 | 0.88318 | [6 empty] | 2021-05-06
SC_MA_SPLIT TS1 COOLING COIL Cooling Capacity [ton] | SPLIT TS1 COOLING COIL Cooling Capacity [ton] | 0.97107 | 0.96128 | 0.95861 | 0.94727 | [6 empty] | 2021-05-06
SC_MA_SPLIT TS2 COOLING COIL Cooling Capacity [ton] | SPLIT TS2 COOLING COIL Cooling Capacity [ton] | 0.97495 | 0.96499 | 0.96173 | 0.95215 | [6 empty] | 2021-05-06
SC_MA_Split GN1 Furnace with DX Cooling OA Rate [cfm] | Split GN1 Furnace with DX Cooling OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | [6 empty] | 2021-05-06
SC_MA_Split GN2 Furnace with DX Cooling OA Rate [cfm] | Split GN2 Furnace with DX Cooling OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | [6 empty] | 2021-05-06
SC_MA_Split GNE Furnace with DX Cooling OA Rate [cfm] | Split GNE Furnace with DX Cooling OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | [6 empty] | 2021-05-06
SC_MA_Split GNW Furnace with DX Cooling OA Rate [cfm] | Split GNW Furnace with DX Cooling OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | [6 empty] | 2021-05-06
SC_MA_Split GS1 Furnace with DX Cooling OA Rate [cfm] | Split GS1 Furnace with DX Cooling OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | [6 empty] | 2021-05-06
SC_MA_Split GS2 Furnace with DX Cooling OA Rate [cfm] | Split GS2 Furnace with DX Cooling OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | [6 empty] | 2021-05-06
SC_MA_Split GSW Furnace with DX Cooling OA Rate [cfm] | Split GSW Furnace with DX Cooling OA Rate [cfm] | 56.9945 | 56.9945 | 56.9945 | 56.9945 | [6 empty] | 2021-05-06
SC_MA_Split MN1 Furnace with DX Cooling OA Rate [cfm] | Split MN1 Furnace with DX Cooling OA Rate [cfm] | 109.9824 | 109.9824 | 109.9824 | 109.9824 | [6 empty] | 2021-05-06
SC_MA_Split MN2 Furnace with DX Cooling OA Rate [cfm] | Split MN2 Furnace with DX Cooling OA Rate [cfm] | 109.9824 | 109.9824 | 109.9824 | 109.9824 | [6 empty] | 2021-05-06
SC_MA_Split MNE Furnace with DX Cooling OA Rate [cfm] | Split MNE Furnace with DX Cooling OA Rate [cfm] | 109.9824 | 109.9824 | 109.9824 | 109.9824 | [6 empty] | 2021-05-06
SC_MA_Split MNW Furnace with DX Cooling OA Rate [cfm] | Split MNW Furnace with DX Cooling OA Rate [cfm] | 109.9824 | 109.9824 | 109.9824 | 109.9824 | [6 empty] | 2021-05-06
SC_MA_Split MS1 Furnace with DX Cooling OA Rate [cfm] | Split MS1 Furnace with DX Cooling OA Rate [cfm] | 109.9824 | 109.9824 | 109.9824 | 109.9824 | [6 empty] | 2021-05-06
SC_MA_Split MS2 Furnace with DX Cooling OA Rate [cfm] | Split MS2 Furnace with DX Cooling OA Rate [cfm] | 109.9824 | 109.9824 | 109.9824 | 109.9824 | [6 empty] | 2021-05-06
SC_MA_Split MSE Furnace with DX Cooling OA Rate [cfm] | Split MSE Furnace with DX Cooling OA Rate [cfm] | 109.9824 | 109.9824 | 109.9824 | 109.9824 | [6 empty] | 2021-05-06
SC_MA_Split MSW Furnace with DX Cooling OA Rate [cfm] | Split MSW Furnace with DX Cooling OA Rate [cfm] | 109.9824 | 109.9824 | 109.9824 | 109.9824 | [6 empty] | 2021-05-06
SC_MA_Split Office Furnace with DX Cooling OA Rate [cfm] | Split Office Furnace with DX Cooling OA Rate [cfm] | 80.7372 | 80.7372 | 80.7372 | 80.7372 | [6 empty] | 2021-05-06
SC_MA_Split TN1 Furnace with DX Cooling OA Rate [cfm] | Split TN1 Furnace with DX Cooling OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | [6 empty] | 2021-05-06
SC_MA_Split TN2 Furnace with DX Cooling OA Rate [cfm] | Split TN2 Furnace with DX Cooling OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | [6 empty] | 2021-05-06
SC_MA_Split TNE Furnace with DX Cooling OA Rate [cfm] | Split TNE Furnace with DX Cooling OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | [6 empty] | 2021-05-06
SC_MA_Split TNW Furnace with DX Cooling OA Rate [cfm] | Split TNW Furnace with DX Cooling OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | [6 empty] | 2021-05-06
SC_MA_Split TS1 Furnace with DX Cooling OA Rate [cfm] | Split TS1 Furnace with DX Cooling OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | [6 empty] | 2021-05-06
SC_MA_Split TS2 Furnace with DX Cooling OA Rate [cfm] | Split TS2 Furnace with DX Cooling OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | [6 empty] | 2021-05-06
SC_MA_Split TSE Furnace with DX Cooling OA Rate [cfm] | Split TSE Furnace with DX Cooling OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | [6 empty] | 2021-05-06
SC_MA_Split TSW Furnace with DX Cooling OA Rate [cfm] | Split TSW Furnace with DX Cooling OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | [6 empty] | 2021-05-06
SC_MA_SPLIT GSW HEATING COIL Heating Capacity [kBtu/hr] | SPLIT GSW HEATING COIL Heating Capacity [kBtu/hr] | 5.848 | 5.7498 | 6.3835 | 6.2999 | [6 empty] | 2021-05-06
SC_MA_SPLIT GNW HEATING COIL Heating Capacity [kBtu/hr] | SPLIT GNW HEATING COIL Heating Capacity [kBtu/hr] | 5.8049 | 5.7031 | 6.2998 | 6.2164 | [6 empty] | 2021-05-06
SC_MA_SPLIT OFFICE HEATING COIL Heating Capacity [kBtu/hr] | SPLIT OFFICE HEATING COIL Heating Capacity [kBtu/hr] | 15.8114 | 15.6538 | 16.8171 | 16.666 | [6 empty] | 2021-05-06
SC_MA_SPLIT GNE HEATING COIL Heating Capacity [kBtu/hr] | SPLIT GNE HEATING COIL Heating Capacity [kBtu/hr] | 5.8049 | 5.7031 | 6.2845 | 6.2032 | [6 empty] | 2021-05-06
SC_MA_SPLIT GN1 HEATING COIL Heating Capacity [kBtu/hr] | SPLIT GN1 HEATING COIL Heating Capacity [kBtu/hr] | 4.5492 | 4.5492 | 4.8386 | 4.8386 | [6 empty] | 2021-05-06
SC_MA_SPLIT GN2 HEATING COIL Heating Capacity [kBtu/hr] | SPLIT GN2 HEATING COIL Heating Capacity [kBtu/hr] | 4.5492 | 4.5492 | 4.8386 | 4.8386 | [6 empty] | 2021-05-06
SC_MA_SPLIT GS1 HEATING COIL Heating Capacity [kBtu/hr] | SPLIT GS1 HEATING COIL Heating Capacity [kBtu/hr] | 4.5492 | 4.5492 | 4.8386 | 4.8386 | [6 empty] | 2021-05-06
SC_MA_SPLIT GS2 HEATING COIL Heating Capacity [kBtu/hr] | SPLIT GS2 HEATING COIL Heating Capacity [kBtu/hr] | 4.5492 | 4.5492 | 4.9422 | 4.9017 | [6 empty] | 2021-05-06
SC_MA_SPLIT MSW HEATING COIL Heating Capacity [kBtu/hr] | SPLIT MSW HEATING COIL Heating Capacity [kBtu/hr] | 9.9014 | 9.7051 | 11.2397 | 11.0789 | [6 empty] | 2021-05-06
SC_MA_SPLIT MNW HEATING COIL Heating Capacity [kBtu/hr] | SPLIT MNW HEATING COIL Heating Capacity [kBtu/hr] | 9.9676 | 9.7613 | 11.2482 | 11.0871 | [6 empty] | 2021-05-06
SC_MA_SPLIT MSE HEATING COIL Heating Capacity [kBtu/hr] | SPLIT MSE HEATING COIL Heating Capacity [kBtu/hr] | 9.9014 | 9.7051 | 11.2025 | 11.0468 | [6 empty] | 2021-05-06
SC_MA_SPLIT MNE HEATING COIL Heating Capacity [kBtu/hr] | SPLIT MNE HEATING COIL Heating Capacity [kBtu/hr] | 9.9676 | 9.7613 | 11.211 | 11.055 | [6 empty] | 2021-05-06
SC_MA_SPLIT MN1 HEATING COIL Heating Capacity [kBtu/hr] | SPLIT MN1 HEATING COIL Heating Capacity [kBtu/hr] | 9.0983 | 9.0983 | 9.6772 | 9.6772 | [6 empty] | 2021-05-06
SC_MA_SPLIT MN2 HEATING COIL Heating Capacity [kBtu/hr] | SPLIT MN2 HEATING COIL Heating Capacity [kBtu/hr] | 9.0983 | 9.0983 | 9.6772 | 9.6772 | [6 empty] | 2021-05-06
SC_MA_SPLIT MS1 HEATING COIL Heating Capacity [kBtu/hr] | SPLIT MS1 HEATING COIL Heating Capacity [kBtu/hr] | 9.0983 | 9.0983 | 9.6772 | 9.6772 | [6 empty] | 2021-05-06
SC_MA_SPLIT MS2 HEATING COIL Heating Capacity [kBtu/hr] | SPLIT MS2 HEATING COIL Heating Capacity [kBtu/hr] | 9.0983 | 9.0983 | 9.6772 | 9.6772 | [6 empty] | 2021-05-06
SC_MA_SPLIT TSW HEATING COIL Heating Capacity [kBtu/hr] | SPLIT TSW HEATING COIL Heating Capacity [kBtu/hr] | 7.6811 | 7.5846 | 8.6148 | 8.5349 | [6 empty] | 2021-05-06
SC_MA_SPLIT TNW HEATING COIL Heating Capacity [kBtu/hr] | SPLIT TNW HEATING COIL Heating Capacity [kBtu/hr] | 7.7204 | 7.6193 | 8.6247 | 8.5452 | [6 empty] | 2021-05-06
SC_MA_SPLIT TSE HEATING COIL Heating Capacity [kBtu/hr] | SPLIT TSE HEATING COIL Heating Capacity [kBtu/hr] | 7.6811 | 7.5846 | 8.595 | 8.5178 | [6 empty] | 2021-05-06
SC_MA_SPLIT TNE HEATING COIL Heating Capacity [kBtu/hr] | SPLIT TNE HEATING COIL Heating Capacity [kBtu/hr] | 7.7204 | 7.6193 | 8.6049 | 8.5282 | [6 empty] | 2021-05-06
SC_MA_SPLIT TN1 HEATING COIL Heating Capacity [kBtu/hr] | SPLIT TN1 HEATING COIL Heating Capacity [kBtu/hr] | 5.9214 | 5.8771 | 6.6998 | 6.6699 | [6 empty] | 2021-05-06
SC_MA_SPLIT TN2 HEATING COIL Heating Capacity [kBtu/hr] | SPLIT TN2 HEATING COIL Heating Capacity [kBtu/hr] | 5.9214 | 5.8771 | 6.6992 | 6.6694 | [6 empty] | 2021-05-06
SC_MA_SPLIT TS1 HEATING COIL Heating Capacity [kBtu/hr] | SPLIT TS1 HEATING COIL Heating Capacity [kBtu/hr] | 5.875 | 5.8352 | 6.6834 | 6.6528 | [6 empty] | 2021-05-06
SC_MA_SPLIT TS2 HEATING COIL Heating Capacity [kBtu/hr] | SPLIT TS2 HEATING COIL Heating Capacity [kBtu/hr] | 5.875 | 5.8352 | 6.6828 | 6.6523 | [6 empty] | 2021-05-06
SC_MA_Split_GSW ERV Flag | Split_GSW ERV Flag | No | Yes | No | Yes | [6 empty] | 2021-05-06
SC_MA_Split_GNW ERV Flag | Split_GNW ERV Flag | No | Yes | No | Yes | [6 empty] | 2021-05-06
SC_MA_Split_GNE ERV Flag | Split_GNE ERV Flag | No | Yes | No | Yes | [6 empty] | 2021-05-06
SC_MA_Split_GN1 ERV Flag | Split_GN1 ERV Flag | No | Yes | No | Yes | [6 empty] | 2021-05-06
SC_MA_Split_GN2 ERV Flag | Split_GN2 ERV Flag | No | Yes | No | Yes | [6 empty] | 2021-05-06
SC_MA_Split_GS1 ERV Flag | Split_GS1 ERV Flag | No | Yes | No | Yes | [6 empty] | 2021-05-06
SC_MA_Split_GS2 ERV Flag | Split_GS2 ERV Flag | No | Yes | No | Yes | [6 empty] | 2021-05-06
SC_MA_Split_MSW ERV Flag | Split_MSW ERV Flag | No | Yes | No | Yes | [6 empty] | 2021-05-06
SC_MA_Split_MNW ERV Flag | Split_MNW ERV Flag | No | Yes | No | Yes | [6 empty] | 2021-05-06
SC_MA_Split_MSE ERV Flag | Split_MSE ERV Flag | No | Yes | No | Yes | [6 empty] | 2021-05-06
SC_MA_Split_MNE ERV Flag | Split_MNE ERV Flag | No | Yes | No | Yes | [6 empty] | 2021-05-06
SC_MA_Split_MN1 ERV Flag | Split_MN1 ERV Flag | No | Yes | No | Yes | [6 empty] | 2021-05-06
SC_MA_Split_MN2 ERV Flag | Split_MN2 ERV Flag | No | Yes | No | Yes | [6 empty] | 2021-05-06
SC_MA_Split_MS1 ERV Flag | Split_MS1 ERV Flag | No | Yes | No | Yes | [6 empty] | 2021-05-06
SC_MA_Split_MS2 ERV Flag | Split_MS2 ERV Flag | No | Yes | No | Yes | [6 empty] | 2021-05-06
SC_MA_Split_TSW ERV Flag | Split_TSW ERV Flag | No | Yes | No | Yes | [6 empty] | 2021-05-06
SC_MA_Split_TNW ERV Flag | Split_TNW ERV Flag | No | Yes | No | Yes | [6 empty] | 2021-05-06
SC_MA_Split_TSE ERV Flag | Split_TSE ERV Flag | No | Yes | No | Yes | [6 empty] | 2021-05-06
SC_MA_Split_TNE ERV Flag | Split_TNE ERV Flag | No | Yes | No | Yes | [6 empty] | 2021-05-06
SC_MA_Split_TN1 ERV Flag | Split_TN1 ERV Flag | No | Yes | No | Yes | [6 empty] | 2021-05-06
SC_MA_Split_TN2 ERV Flag | Split_TN2 ERV Flag | No | Yes | No | Yes | [6 empty] | 2021-05-06
SC_MA_Split_TS1 ERV Flag | Split_TS1 ERV Flag | No | Yes | No | Yes | [6 empty] | 2021-05-06
SC_MA_Split_TS2 ERV Flag | Split_TS2 ERV Flag | No | Yes | No | Yes | [6 empty] | 2021-05-06
id | item | Zone5A(SD-SiouxCity-IA) ASHRAE901-state_STD2016 | Zone5A(SD-SiouxCity-IA) ASHRAE901-state_STD2019 | Zone6A(SD-SiouxFalls-SD) ASHRAE901-state_STD2016 | Zone6A(SD-SiouxFalls-SD) ASHRAE901-state_STD2019 | [6 empty] | 2021-05-06
SD_SO_PSZ-AC:1 Cooling Capacity [ton] | PSZ-AC:1 Cooling Capacity [ton] | 1.918 | 1.8231 | 1.873 | 1.7745 | [6 empty] | 2021-05-06
SD_SO_PSZ-AC:2 Cooling Capacity [ton] | PSZ-AC:2 Cooling Capacity [ton] | 1.6857 | 1.6201 | 1.6436 | 1.5629 | [6 empty] | 2021-05-06
SD_SO_PSZ-AC:3 Cooling Capacity [ton] | PSZ-AC:3 Cooling Capacity [ton] | 1.2015 | 1.1623 | 1.1975 | 1.1284 | [6 empty] | 2021-05-06
SD_SO_PSZ-AC:4 Cooling Capacity [ton] | PSZ-AC:4 Cooling Capacity [ton] | 1.6121 | 1.536 | 1.5547 | 1.4777 | [6 empty] | 2021-05-06
SD_SO_PSZ-AC:5 Cooling Capacity [ton] | PSZ-AC:5 Cooling Capacity [ton] | 1.4125 | 1.3716 | 1.4079 | 1.3378 | [6 empty] | 2021-05-06
SD_SO_PSZ-AC:1 Supply Flow Rate [cfm] | PSZ-AC:1 Supply Flow Rate [cfm] | 678.0416 | 614.4752 | 678.0416 | 635.664 | [6 empty] | 2021-05-06
SD_SO_PSZ-AC:2 Supply Flow Rate [cfm] | PSZ-AC:2 Supply Flow Rate [cfm] | 593.2864 | 572.0976 | 614.4752 | 572.0976 | [6 empty] | 2021-05-06
SD_SO_PSZ-AC:3 Supply Flow Rate [cfm] | PSZ-AC:3 Supply Flow Rate [cfm] | 487.3424 | 466.1536 | 508.5312 | 466.1536 | [6 empty] | 2021-05-06
SD_SO_PSZ-AC:4 Supply Flow Rate [cfm] | PSZ-AC:4 Supply Flow Rate [cfm] | 572.0976 | 529.72 | 572.0976 | 529.72 | [6 empty] | 2021-05-06
SD_SO_PSZ-AC:5 Supply Flow Rate [cfm] | PSZ-AC:5 Supply Flow Rate [cfm] | 593.2864 | 572.0976 | 593.2864 | 572.0976 | [6 empty] | 2021-05-06
SD_SO_PSZ-AC:1 OA Rate [cfm] | PSZ-AC:1 OA Rate [cfm] | 136.9178 | 136.9178 | 136.9178 | 136.9178 | [6 empty] | 2021-05-06
SD_SO_PSZ-AC:2 OA Rate [cfm] | PSZ-AC:2 OA Rate [cfm] | 103.7925 | 103.7925 | 103.7925 | 103.7925 | [6 empty] | 2021-05-06
SD_SO_PSZ-AC:3 OA Rate [cfm] | PSZ-AC:3 OA Rate [cfm] | 61.5711 | 61.5711 | 61.5711 | 61.5711 | [6 empty] | 2021-05-06
SD_SO_PSZ-AC:4 OA Rate [cfm] | PSZ-AC:4 OA Rate [cfm] | 103.7925 | 103.7925 | 103.7925 | 103.7925 | [6 empty] | 2021-05-06
SD_SO_PSZ-AC:5 OA Rate [cfm] | PSZ-AC:5 OA Rate [cfm] | 61.5711 | 61.5711 | 61.5711 | 61.5711 | [6 empty] | 2021-05-06
SD_SO_PSZ-AC:1 heating Capacity [kBtu/hr] | PSZ-AC:1 heating Capacity [kBtu/hr] | 16.0798 | 16.0798 | 16.7352 | 16.7013 | [6 empty] | 2021-05-06
SD_SO_PSZ-AC:2 heating Capacity [kBtu/hr] | PSZ-AC:2 heating Capacity [kBtu/hr] | 24.1546 | 23.8934 | 24.5562 | 24.2763 | [6 empty] | 2021-05-06
SD_SO_PSZ-AC:3 heating Capacity [kBtu/hr] | PSZ-AC:3 heating Capacity [kBtu/hr] | 14.7572 | 14.6128 | 14.9846 | 14.83 | [6 empty] | 2021-05-06
SD_SO_PSZ-AC:4 heating Capacity [kBtu/hr] | PSZ-AC:4 heating Capacity [kBtu/hr] | 24.067 | 23.8424 | 24.4993 | 24.26 | [6 empty] | 2021-05-06
SD_SO_PSZ-AC:5 heating Capacity [kBtu/hr] | PSZ-AC:5 heating Capacity [kBtu/hr] | 14.8378 | 14.686 | 15.0594 | 14.8976 | [6 empty] | 2021-05-06
id | item | Zone5A(SD-SiouxCity-IA) ASHRAE901-state_STD2016 | Zone5A(SD-SiouxCity-IA) ASHRAE901-state_STD2019 | Zone6A(SD-SiouxFalls-SD) ASHRAE901-state_STD2016 | Zone6A(SD-SiouxFalls-SD) ASHRAE901-state_STD2019 | [6 empty] | 2021-05-06
SD_LO_CAV_BAS Supply Flow Rate [cfm] | CAV_BAS Supply Flow Rate [cfm] | 12077.616 | 11166.4976 | 12225.9376 | 11314.8192 | [6 empty] | 2021-05-06
SD_LO_VAV_BOT WITH REHEAT Supply Flow Rate [cfm] | VAV_BOT WITH REHEAT Supply Flow Rate [cfm] | 20510.7584 | 19536.0736 | 20913.3456 | 19769.1504 | [6 empty] | 2021-05-06
SD_LO_VAV_MID WITH REHEAT Supply Flow Rate [cfm] | VAV_MID WITH REHEAT Supply Flow Rate [cfm] | 190911.0883 | 181736.3379 | 194936.9603 | 183897.5955 | [6 empty] | 2021-05-06
SD_LO_VAV_TOP WITH REHEAT Supply Flow Rate [cfm] | VAV_TOP WITH REHEAT Supply Flow Rate [cfm] | 20256.4928 | 19451.3184 | 20637.8912 | 19557.2624 | [6 empty] | 2021-05-06
SD_LO_Supply Air Temp. Reset Flag | Supply Air Temp. Reset Flag | Yes | Yes | Yes | Yes | [6 empty] | 2021-05-06
SD_LO_CAV_BAS OA Rate [cfm] | CAV_BAS OA Rate [cfm] | 2542.8255 | 2542.8255 | 2542.8255 | 2542.8255 | [6 empty] | 2021-05-06
SD_LO_VAV_BOT WITH REHEAT OA Rate [cfm] | VAV_BOT WITH REHEAT OA Rate [cfm] | 5377.8022 | 4302.174 | 5377.8022 | 4302.174 | [6 empty] | 2021-05-06
SD_LO_VAV_MID WITH REHEAT OA Rate [cfm] | VAV_MID WITH REHEAT OA Rate [cfm] | 53777.9373 | 43021.7396 | 53777.9373 | 43021.7396 | [6 empty] | 2021-05-06
SD_LO_VAV_TOP WITH REHEAT OA Rate [cfm] | VAV_TOP WITH REHEAT OA Rate [cfm] | 5377.8022 | 4302.174 | 5377.8022 | 4302.174 | [6 empty] | 2021-05-06
SD_LO_AIRLOOP DATACENTER BASEMENT OA Rate [cfm] | AIRLOOP DATACENTER BASEMENT OA Rate [cfm] | 716.9654 | 716.9654 | 716.9654 | 716.9654 | [6 empty] | 2021-05-06
SD_LO_VAV_bot_WITH_REHEAT ERV Flag | VAV_bot_WITH_REHEAT ERV Flag | Yes | Yes | Yes | Yes | [6 empty] | 2021-05-06
SD_LO_VAV_mid_WITH_REHEAT ERV Flag | VAV_mid_WITH_REHEAT ERV Flag | Yes | Yes | Yes | Yes | [6 empty] | 2021-05-06
SD_LO_VAV_top_WITH_REHEAT ERV Flag | VAV_top_WITH_REHEAT ERV Flag | Yes | Yes | Yes | Yes | [6 empty] | 2021-05-06
SD_LO_COOLSYS1 CHILLER1 Capacity [ton] | COOLSYS1 CHILLER1 Capacity [ton] | 429.4464 | 388.0188 | 417.3794 | 376.9035 | [6 empty] | 2021-05-06
SD_LO_COOLSYS1 CHILLER2 Capacity [ton] | COOLSYS1 CHILLER2 Capacity [ton] | 429.4464 | 388.0188 | 417.3794 | 376.9035 | [6 empty] | 2021-05-06
SD_LO_TOWERWATERSYS COOLTOWER 1 Capacity [ton] | TOWERWATERSYS COOLTOWER 1 Capacity [ton] | 407.62 | 368.3046 | 396.1733 | 357.7505 | [6 empty] | 2021-05-06
SD_LO_TOWERWATERSYS COOLTOWER 2 Capacity [ton] | TOWERWATERSYS COOLTOWER 2 Capacity [ton] | 407.62 | 368.3046 | 396.1733 | 357.7505 | [6 empty] | 2021-05-06
SD_LO_HEATSYS1 BOILER Capacity [MMBTU/h] | HEATSYS1 BOILER Capacity [MMBTU/h] | 5277.6562 | 4675.4447 | 5361.825 | 4741.4905 | [6 empty] | 2021-05-06
SD_LO_COOLSYS1 PUMP Flow Rate [gal/min] | COOLSYS1 PUMP Flow Rate [gal/min] | 0 | 0 | 0 | 0 | [6 empty] | 2021-05-06
SD_LO_COOLSYS1 CHILLER1 PUMP Flow Rate [gal/min] | COOLSYS1 CHILLER1 PUMP Flow Rate [gal/min] | 676.6741 | 611.32 | 657.5158 | 593.6929 | [6 empty] | 2021-05-06
SD_LO_COOLSYS1 CHILLER2 PUMP Flow Rate [gal/min] | COOLSYS1 CHILLER2 PUMP Flow Rate [gal/min] | 676.6741 | 611.32 | 657.5158 | 593.6929 | [6 empty] | 2021-05-06
SD_LO_COOLSYS1 PUMP SECONDARY Flow Rate [gal/min] | COOLSYS1 PUMP SECONDARY Flow Rate [gal/min] | 1353.3466 | 1222.6385 | 1315.0332 | 1187.3857 | [6 empty] | 2021-05-06
SD_LO_HEATSYS1 PUMP Flow Rate [gal/min] | HEATSYS1 PUMP Flow Rate [gal/min] | 1083.3078 | 959.6959 | 1100.5846 | 973.2526 | [6 empty] | 2021-05-06
SD_LO_TOWERWATERSYS PUMP Flow Rate [gal/min] | TOWERWATERSYS PUMP Flow Rate [gal/min] | 2369.3063 | 2140.7446 | 2302.7349 | 2079.4039 | [6 empty] | 2021-05-06
SD_LO_PLANT CIRC PUMP Flow Rate [gal/min] | PLANT CIRC PUMP Flow Rate [gal/min] | 212.7193 | 211.8665 | 213.7511 | 212.5227 | [6 empty] | 2021-05-06
SD_LO_COOLSYS1 PUMP SECONDARY Pressure setpoint reset [yes,no] | COOLSYS1 PUMP SECONDARY Pressure setpoint reset [yes,no] | pump_ride_on_curve | pump_ride_on_curve | pump_ride_on_curve | pump_ride_on_curve | [6 empty] | 2021-05-06
SD_LO_COOLSYS1 CHILLER1 PUMP Pump Power [hp] | COOLSYS1 CHILLER1 PUMP Pump Power [hp] | 3.6504 | 3.2652 | 3.5471 | 3.171 | [6 empty] | 2021-05-06
SD_LO_COOLSYS1 CHILLER2 PUMP Pump Power [hp] | COOLSYS1 CHILLER2 PUMP Pump Power [hp] | 3.6504 | 3.2652 | 3.5471 | 3.171 | [6 empty] | 2021-05-06
SD_LO_COOLSYS1 PUMP SECONDARY Pump Power [hp] | COOLSYS1 PUMP SECONDARY Pump Power [hp] | 21.9025 | 19.5912 | 21.2824 | 19.0263 | [6 empty] | 2021-05-06
SD_LO_HEATSYS1 PUMP Pump Power [hp] | HEATSYS1 PUMP Pump Power [hp] | 23.4163 | 20.539 | 23.7898 | 20.8291 | [6 empty] | 2021-05-06
SD_LO_TOWERWATERSYS PUMP Pump Power [hp] | TOWERWATERSYS PUMP Pump Power [hp] | 42.4198 | 37.9482 | 41.2279 | 36.8611 | [6 empty] | 2021-05-06
SD_LO_PLANT CIRC PUMP Pump Power [hp] | PLANT CIRC PUMP Pump Power [hp] | 4.5902 | 4.5265 | 4.6125 | 4.5405 | [6 empty] | 2021-05-06
SD_LO_Datacenter PLANT CIRC PUMP Pump Power [hp] | Datacenter PLANT CIRC PUMP Pump Power [hp] | 4.5902 | 4.5265 | 4.6125 | 4.5405 | [6 empty] | 2021-05-06
SD_LO_ZN_VAV_BOXes_Max_Reheat_Water_Flow_GPM | ZN_VAV_BOXes_Max_Reheat_Water_Flow_GPM | 543.6479 | 523.9992 | 535.5212 | 514.7939 | [6 empty] | 2021-05-06
SD_LO_COOLSYS1 PUMP SECONDARY VSD | COOLSYS1 PUMP SECONDARY VSD | No | No | No | No | [6 empty] | 2021-05-06
SD_LO_HEATSYS1 PUMP VSD | HEATSYS1 PUMP VSD | No | No | No | No | [6 empty] | 2021-05-06
SD_LO_DATACENTER BASEMENT Cooling Capacity [ton] | DATACENTER BASEMENT Cooling Capacity [ton] | 123.684 | 123.3189 | 124.0247 | 123.6475 | [6 empty] | 2021-05-06
SD_LO_DATACENTER BOT Cooling Capacity [ton] | DATACENTER BOT Cooling Capacity [ton] | 2.776 | 2.7517 | 2.8089 | 2.7645 | [6 empty] | 2021-05-06
SD_LO_DATACENTER MID Cooling Capacity [ton] | DATACENTER MID Cooling Capacity [ton] | 26.6474 | 26.4328 | 26.9961 | 26.5608 | [6 empty] | 2021-05-06
SD_LO_DATACENTER TOP Cooling Capacity [ton] | DATACENTER TOP Cooling Capacity [ton] | 2.7143 | 2.6936 | 2.7477 | 2.7047 | [6 empty] | 2021-05-06
id | item | Zone5A(SD-SiouxCity-IA) ASHRAE901-state_STD2016 | Zone5A(SD-SiouxCity-IA) ASHRAE901-state_STD2019 | Zone6A(SD-SiouxFalls-SD) ASHRAE901-state_STD2016 | Zone6A(SD-SiouxFalls-SD) ASHRAE901-state_STD2019 | [6 empty] | 2021-05-06
SD_RS_PSZ-AC:1 Cooling Capacity [ton] | PSZ-AC:1 Cooling Capacity [ton] | 10.5395 | 10.1847 | 10.2468 | 9.8298 | [6 empty] | 2021-05-06
SD_RS_PSZ-AC:2 Cooling Capacity [ton] | PSZ-AC:2 Cooling Capacity [ton] | 51.5549 | 49.3144 | 49.5212 | 47.9633 | [6 empty] | 2021-05-06
SD_RS_PSZ-AC:3 Cooling Capacity [ton] | PSZ-AC:3 Cooling Capacity [ton] | 6.6531 | 6.4869 | 6.4692 | 6.3006 | [6 empty] | 2021-05-06
SD_RS_PSZ-AC:4 Cooling Capacity [ton] | PSZ-AC:4 Cooling Capacity [ton] | 5.3929 | 5.2222 | 5.2097 | 5.0268 | [6 empty] | 2021-05-06
SD_RS_PSZ-AC:1 Supply Flow Rate [cfm] | PSZ-AC:1 Supply Flow Rate [cfm] | 4068.2496 | 3792.7952 | 4025.872 | 3750.4176 | [6 empty] | 2021-05-06
SD_RS_PSZ-AC:2 Supply Flow Rate [cfm] | PSZ-AC:2 Supply Flow Rate [cfm] | 15891.6 | 14895.7264 | 15806.8448 | 15001.6704 | [6 empty] | 2021-05-06
SD_RS_PSZ-AC:3 Supply Flow Rate [cfm] | PSZ-AC:3 Supply Flow Rate [cfm] | 2351.9568 | 2267.2016 | 2351.9568 | 2267.2016 | [6 empty] | 2021-05-06
SD_RS_PSZ-AC:4 Supply Flow Rate [cfm] | PSZ-AC:4 Supply Flow Rate [cfm] | 1779.8592 | 1695.104 | 1779.8592 | 1695.104 | [6 empty] | 2021-05-06
SD_RS_PSZ-AC:1 OA Rate [cfm] | PSZ-AC:1 OA Rate [cfm] | 490.669 | 490.669 | 490.669 | 490.669 | [6 empty] | 2021-05-06
SD_RS_PSZ-AC:2 OA Rate [cfm] | PSZ-AC:2 OA Rate [cfm] | 4005.1282 | 4005.1282 | 4005.1282 | 4005.1282 | [6 empty] | 2021-05-06
SD_RS_PSZ-AC:3 OA Rate [cfm] | PSZ-AC:3 OA Rate [cfm] | 377.3937 | 377.3937 | 377.3937 | 377.3937 | [6 empty] | 2021-05-06
SD_RS_PSZ-AC:4 OA Rate [cfm] | PSZ-AC:4 OA Rate [cfm] | 377.3937 | 377.3937 | 377.3937 | 377.3937 | [6 empty] | 2021-05-06
SD_RS_PSZ-AC:1 OA Damper [gravity, motorized] | PSZ-AC:1 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2021-05-06
SD_RS_PSZ-AC:2 OA Damper [gravity, motorized] | PSZ-AC:2 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2021-05-06
SD_RS_PSZ-AC:3 OA Damper [gravity, motorized] | PSZ-AC:3 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2021-05-06
SD_RS_PSZ-AC:4 OA Damper [gravity, motorized] | PSZ-AC:4 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2021-05-06
SD_RS_PSZ-AC:1 Heating Capacity [kBtu/hr] | PSZ-AC:1 Heating Capacity [kBtu/hr] | 184.3134 | 173.2027 | 183.2906 | 171.7964 | [6 empty] | 2021-05-06
SD_RS_PSZ-AC:2 Heating Capacity [kBtu/hr] | PSZ-AC:2 Heating Capacity [kBtu/hr] | 878.6094 | 840.6347 | 885.204 | 854.6444 | [6 empty] | 2021-05-06
SD_RS_PSZ-AC:3 Heating Capacity [kBtu/hr] | PSZ-AC:3 Heating Capacity [kBtu/hr] | 114.5208 | 111.7895 | 115.242 | 112.3278 | [6 empty] | 2021-05-06
SD_RS_PSZ-AC:4 Heating Capacity [kBtu/hr] | PSZ-AC:4 Heating Capacity [kBtu/hr] | 94.2518 | 91.245 | 94.8875 | 91.5173 | [6 empty] | 2021-05-06
id | item | Zone5A(SD-SiouxCity-IA) ASHRAE901-state_STD2016 | Zone5A(SD-SiouxCity-IA) ASHRAE901-state_STD2019 | Zone6A(SD-SiouxFalls-SD) ASHRAE901-state_STD2016 | Zone6A(SD-SiouxFalls-SD) ASHRAE901-state_STD2019 | [6 empty] | 2021-05-06
SD_PS_VAV_POD_1 Cooling Capacity [ton] | VAV_POD_1 Cooling Capacity [ton] | 19.8111 | 19.1106 | 19.9623 | 19.0146 | [6 empty] | 2021-05-06
SD_PS_VAV_POD_2 Cooling Capacity [ton] | VAV_POD_2 Cooling Capacity [ton] | 19.7165 | 18.8633 | 19.8438 | 18.7853 | [6 empty] | 2021-05-06
SD_PS_VAV_POD_3 Cooling Capacity [ton] | VAV_POD_3 Cooling Capacity [ton] | 18.2372 | 17.3051 | 18.3547 | 17.2253 | [6 empty] | 2021-05-06
SD_PS_VAV_OTHER Cooling Capacity [ton] | VAV_OTHER Cooling Capacity [ton] | 28.0195 | 26.4059 | 28.2592 | 26.3151 | [6 empty] | 2021-05-06
SD_PS_PSZ-AC_1:6 Cooling Capacity [ton] | PSZ-AC_1:6 Cooling Capacity [ton] | 8.6604 | 8.3913 | 8.5123 | 8.2223 | [6 empty] | 2021-05-06
SD_PS_PSZ-AC_2:5 Cooling Capacity [ton] | PSZ-AC_2:5 Cooling Capacity [ton] | 5.7496 | 5.7221 | 5.8114 | 5.7255 | [6 empty] | 2021-05-06
SD_PS_PSZ-AC_2:7 Cooling Capacity [ton] | PSZ-AC_2:7 Cooling Capacity [ton] | 10.5074 | 10.5074 | 10.5074 | 10.5074 | [6 empty] | 2021-05-06
SD_PS_VAV_POD_1 Supply Flow Rate [cfm] | VAV_POD_1 Supply Flow Rate [cfm] | 5954.0528 | 5742.1648 | 5996.4304 | 5699.7872 | [6 empty] | 2021-05-06
SD_PS_VAV_POD_2 Supply Flow Rate [cfm] | VAV_POD_2 Supply Flow Rate [cfm] | 5911.6752 | 5657.4096 | 5954.0528 | 5636.2208 | [6 empty] | 2021-05-06
SD_PS_VAV_POD_3 Supply Flow Rate [cfm] | VAV_POD_3 Supply Flow Rate [cfm] | 5466.7104 | 5191.256 | 5509.088 | 5170.0672 | [6 empty] | 2021-05-06
SD_PS_VAV_OTHER Supply Flow Rate [cfm] | VAV_OTHER Supply Flow Rate [cfm] | 8411.9536 | 7924.6112 | 8475.52 | 7903.4224 | [6 empty] | 2021-05-06
SD_PS_PSZ-AC_2:5 Supply Flow Rate [cfm] | PSZ-AC_2:5 Supply Flow Rate [cfm] | 1716.2928 | 1716.2928 | 1737.4816 | 1716.2928 | [6 empty] | 2021-05-06
SD_PS_PSZ-AC_1:6 Supply Flow Rate [cfm] | PSZ-AC_1:6 Supply Flow Rate [cfm] | 2648.6 | 2521.4672 | 2669.7888 | 2542.656 | [6 empty] | 2021-05-06
SD_PS_PSZ-AC_2:7 Supply Flow Rate [cfm] | PSZ-AC_2:7 Supply Flow Rate [cfm] | 3157.1312 | 3157.1312 | 3157.1312 | 3157.1312 | [6 empty] | 2021-05-06
SD_PS_Supply Air Temp. Reset Flag | Supply Air Temp. Reset Flag | Yes | Yes | Yes | Yes | [6 empty] | 2021-05-06
SD_PS_VAV_POD_1 OA Rate [cfm] | VAV_POD_1 OA Rate [cfm] | 5944.984 | 5734.7699 | 5988.421 | 5705.9531 | [6 empty] | 2021-05-06
SD_PS_VAV_POD_2 OA Rate [cfm] | VAV_POD_2 OA Rate [cfm] | 5916.6122 | 5660.5667 | 5953.8833 | 5637.1531 | [6 empty] | 2021-05-06
SD_PS_VAV_POD_3 OA Rate [cfm] | VAV_POD_3 OA Rate [cfm] | 5470.3549 | 5192.9723 | 5505.8673 | 5169.029 | [6 empty] | 2021-05-06
SD_PS_VAV_OTHER OA Rate [cfm] | VAV_OTHER OA Rate [cfm] | 3736.1787 | 2988.8921 | 3736.1787 | 2988.8921 | [6 empty] | 2021-05-06
SD_PS_PSZ-AC_2:5 OA Rate [cfm] | PSZ-AC_2:5 OA Rate [cfm] | 1152.7343 | 1152.7343 | 1152.7343 | 1152.7343 | [6 empty] | 2021-05-06
SD_PS_PSZ-AC_1:6 OA Rate [cfm] | PSZ-AC_1:6 OA Rate [cfm] | 539.9118 | 539.9118 | 539.9118 | 539.9118 | [6 empty] | 2021-05-06
SD_PS_PSZ-AC_2:7 OA Rate [cfm] | PSZ-AC_2:7 OA Rate [cfm] | 3153.0841 | 3153.0841 | 3153.0841 | 3153.0841 | [6 empty] | 2021-05-06
SD_PS_VAV_POD_1 OA Damper [gravity, motorized] | VAV_POD_1 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2021-05-06
SD_PS_VAV_POD_2 OA Damper [gravity, motorized] | VAV_POD_2 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2021-05-06
SD_PS_VAV_POD_3 OA Damper [gravity, motorized] | VAV_POD_3 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2021-05-06
SD_PS_VAV_OTHER OA Damper [gravity, motorized] | VAV_OTHER OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2021-05-06
SD_PS_PSZ-AC_2:5 OA Damper [gravity, motorized] | PSZ-AC_2:5 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2021-05-06
SD_PS_PSZ-AC_1:6 OA Damper [gravity, motorized] | PSZ-AC_1:6 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2021-05-06
SD_PS_PSZ-AC_2:7 OA Damper [gravity, motorized] | PSZ-AC_2:7 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2021-05-06
SD_PS_VAV_POD_1 (economizer) | VAV_POD_1 (economizer) | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | [6 empty] | 2021-05-06
SD_PS_VAV_POD_2 (economizer) | VAV_POD_2 (economizer) | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | [6 empty] | 2021-05-06
SD_PS_VAV_POD_3 (economizer) | VAV_POD_3 (economizer) | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | [6 empty] | 2021-05-06
SD_PS_VAV_OTHER (economizer) | VAV_OTHER (economizer) | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | [6 empty] | 2021-05-06
SD_PS_PSZ-AC_2:5 (economizer) | PSZ-AC_2:5 (economizer) | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | [6 empty] | 2021-05-06
SD_PS_PSZ-AC_1:6 (economizer) | PSZ-AC_1:6 (economizer) | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | [6 empty] | 2021-05-06
SD_PS_PSZ-AC_2:7 (economizer) | PSZ-AC_2:7 (economizer) | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | [6 empty] | 2021-05-06
SD_PS_VAV_Pod_1_ERV Flag | VAV_Pod_1_ERV Flag | Yes | Yes | Yes | Yes | [6 empty] | 2021-05-06
SD_PS_VAV_Pod_2_ERV Flag | VAV_Pod_2_ERV Flag | Yes | Yes | Yes | Yes | [6 empty] | 2021-05-06
SD_PS_VAV_Pod_3_ERV Flag | VAV_Pod_3_ERV Flag | Yes | Yes | Yes | Yes | [6 empty] | 2021-05-06
SD_PS_VAV_OTHER_ERV Flag | VAV_OTHER_ERV Flag | Yes | Yes | Yes | Yes | [6 empty] | 2021-05-06
SD_PS_PSZ_AC_2_5_ERV Flag | PSZ_AC_2_5_ERV Flag | No | No | No | No | [6 empty] | 2021-05-06
SD_PS_PSZ_AC_2_7_ERV Flag | PSZ_AC_2_7_ERV Flag | Yes | Yes | Yes | Yes | [6 empty] | 2021-05-06
SD_PS_HEATSYS1 Capacity [MMBTU/h] | HEATSYS1 Capacity [MMBTU/h] | 1.3249 | 1.2714 | 1.3587 | 1.2962 | [6 empty] | 2021-05-06
SD_PS_HEATSYS1 Flow Rate [gal/min] | HEATSYS1 Flow Rate [gal/min] | 135.972 | 130.483 | 139.4502 | 133.0319 | [6 empty] | 2021-05-06
SD_PS_VAV_POD_1 Fan Power [hp] | VAV_POD_1 Fan Power [hp] | 8.7706 | 8.4605 | 8.8376 | 8.418 | [6 empty] | 2021-05-06
SD_PS_VAV_POD_2 Fan Power [hp] | VAV_POD_2 Fan Power [hp] | 8.7288 | 8.3511 | 8.7851 | 8.3165 | [6 empty] | 2021-05-06
SD_PS_VAV_POD_3 Fan Power [hp] | VAV_POD_3 Fan Power [hp] | 8.0739 | 7.6612 | 8.1259 | 7.6259 | [6 empty] | 2021-05-06
SD_PS_VAV_OTHER Fan Power [hp] | VAV_OTHER Fan Power [hp] | 12.3106 | 11.6017 | 12.416 | 11.5618 | [6 empty] | 2021-05-06
SD_PS_HEATSYS1 Pump Power [hp] | HEATSYS1 Pump Power [hp] | 2.9391 | 2.7925 | 3.0143 | 2.8471 | [6 empty] | 2021-05-06
SD_PS_PSZ-AC_1:6 Heating Capacity [kBtu/hr] | PSZ-AC_1:6 Heating Capacity [kBtu/hr] | 221.0746 | 212.5098 | 223.5519 | 214.2785 | [6 empty] | 2021-05-06
SD_PS_PSZ-AC_2:5 Heating Capacity [kBtu/hr] | PSZ-AC_2:5 Heating Capacity [kBtu/hr] | 155.7582 | 155.4646 | 160.3191 | 159.4129 | [6 empty] | 2021-05-06
SD_PS_PSZ-AC_2:7 Heating Capacity [kBtu/hr] | PSZ-AC_2:7 Heating Capacity [kBtu/hr] | 370.3023 | 370.3023 | 381.6565 | 381.6565 | [6 empty] | 2021-05-06
SD_PS_ZN_VAV_BOXes_Max_Reheat_Water_Flow_GPM | ZN_VAV_BOXes_Max_Reheat_Water_Flow_GPM | 83.2692 | 80.2988 | 82.9978 | 79.898 | [6 empty] | 2021-05-06
id | item | Zone5A(SD-SiouxCity-IA) ASHRAE901-state_STD2016 | Zone5A(SD-SiouxCity-IA) ASHRAE901-state_STD2019 | Zone6A(SD-SiouxFalls-SD) ASHRAE901-state_STD2016 | Zone6A(SD-SiouxFalls-SD) ASHRAE901-state_STD2019 | [6 empty] | 2021-05-06
SD_SH_SAC_FRONTOFFICE Cooling Capacity [ton] | SAC_FRONTOFFICE Cooling Capacity [ton] | 2.4552 | 2.3546 | 2.4312 | 2.2897 | [6 empty] | 2021-05-06
SD_SH_SAC_FRONTLOUNGE Cooling Capacity [ton] | SAC_FRONTLOUNGE Cooling Capacity [ton] | 6.3359 | 6.0188 | 6.3602 | 6.0268 | [6 empty] | 2021-05-06
SD_SH_SAC_MEETINGROOM Cooling Capacity [ton] | SAC_MEETINGROOM Cooling Capacity [ton] | 3.0275 | 2.9182 | 3.0509 | 2.9318 | [6 empty] | 2021-05-06
SD_SH_SAC_EXC_EMPLGE_RESTRM Cooling Capacity [ton] | SAC_EXC_EMPLGE_RESTRM Cooling Capacity [ton] | 6.1497 | 6.107 | 6.0796 | 6.0312 | [6 empty] | 2021-05-06
SD_SH_SAC_FO_ADDAQ SUPPLY FAN Supply Flow Rate [cfm] | SAC_FO_ADDAQ SUPPLY FAN Supply Flow Rate [cfm] | 826.3632 | 762.7968 | 826.3632 | 762.7968 | [6 empty] | 2021-05-06
SD_SH_SAC_FL_ADDAQ SUPPLY FAN Supply Flow Rate [cfm] | SAC_FL_ADDAQ SUPPLY FAN Supply Flow Rate [cfm] | 1906.992 | 1801.048 | 1906.992 | 1801.048 | [6 empty] | 2021-05-06
SD_SH_SAC_MR_ADDAQ SUPPLY FAN Supply Flow Rate [cfm] | SAC_MR_ADDAQ SUPPLY FAN Supply Flow Rate [cfm] | 911.1184 | 868.7408 | 911.1184 | 889.9296 | [6 empty] | 2021-05-06
SD_SH_SAC_EXC_ADDAQ SUPPLY FAN Supply Flow Rate [cfm] | SAC_EXC_ADDAQ SUPPLY FAN Supply Flow Rate [cfm] | 2246.0128 | 2246.0128 | 2288.3904 | 2267.2016 | [6 empty] | 2021-05-06
SD_SH_SAC_Exc_EmpLge_RestRm OA Rate [cfm] | SAC_Exc_EmpLge_RestRm OA Rate [cfm] | 199.9928 | 199.9928 | 199.9928 | 199.9928 | [6 empty] | 2021-05-06
SD_SH_SAC_FrontLounge OA Rate [cfm] | SAC_FrontLounge OA Rate [cfm] | 500.0133 | 500.0133 | 500.0133 | 500.0133 | [6 empty] | 2021-05-06
SD_SH_SAC_FrontOffice OA Rate [cfm] | SAC_FrontOffice OA Rate [cfm] | 119.2938 | 119.2938 | 119.2938 | 119.2938 | [6 empty] | 2021-05-06
SD_SH_SAC_MeetingRoom OA Rate [cfm] | SAC_MeetingRoom OA Rate [cfm] | 267.7629 | 267.7629 | 267.7629 | 267.7629 | [6 empty] | 2021-05-06
SD_SH_SAC_FrontLounge OA Damper [gravity, motorized] | SAC_FrontLounge OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2021-05-06
SD_SH_SAC_FrontOffice (economizer) | SAC_FrontOffice (economizer) | No | No | No | No | [6 empty] | 2021-05-06
SD_SH_SAC_FrontLounge (economizer) | SAC_FrontLounge (economizer) | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | [6 empty] | 2021-05-06
SD_SH_SAC_MeetingRoom (economizer) | SAC_MeetingRoom (economizer) | No | No | No | No | [6 empty] | 2021-05-06
SD_SH_SAC_Exc_EmpLge_RestRm (economizer) | SAC_Exc_EmpLge_RestRm (economizer) | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | [6 empty] | 2021-05-06
SD_SH_SAC_FRONTOFFICE Heating Capacity [kBtu/hr] | SAC_FRONTOFFICE Heating Capacity [kBtu/hr] | 38.7505 | 36.7268 | 38.8606 | 36.7661 | [6 empty] | 2021-05-06
SD_SH_SAC_FRONTLOUNGE Heating Capacity [kBtu/hr] | SAC_FRONTLOUNGE Heating Capacity [kBtu/hr] | 108.3004 | 104.9332 | 109.7667 | 106.2683 | [6 empty] | 2021-05-06
SD_SH_SAC_MEETINGROOM Heating Capacity [kBtu/hr] | SAC_MEETINGROOM Heating Capacity [kBtu/hr] | 54.1152 | 52.9553 | 55.0558 | 53.8061 | [6 empty] | 2021-05-06
SD_SH_SAC_EXC_EMPLGE_RESTRM Heating Capacity [kBtu/hr] | SAC_EXC_EMPLGE_RESTRM Heating Capacity [kBtu/hr] | 96.1707 | 95.5025 | 96.8839 | 96.1235 | [6 empty] | 2021-05-06
id | item | Zone5A(SD-SiouxCity-IA) ASHRAE901-state_STD2016 | Zone5A(SD-SiouxCity-IA) ASHRAE901-state_STD2019 | Zone6A(SD-SiouxFalls-SD) ASHRAE901-state_STD2016 | Zone6A(SD-SiouxFalls-SD) ASHRAE901-state_STD2019 | [6 empty] | 2021-05-06
SD_MA_SPLIT GSW COOLING COIL Cooling Capacity [ton] | SPLIT GSW COOLING COIL Cooling Capacity [ton] | 0.94998 | 0.93534 | 0.92917 | 0.90198 | [6 empty] | 2021-05-06
SD_MA_SPLIT GNW COOLING COIL Cooling Capacity [ton] | SPLIT GNW COOLING COIL Cooling Capacity [ton] | 0.90192 | 0.8879 | 0.88094 | 0.85277 | [6 empty] | 2021-05-06
SD_MA_SPLIT OFFICE COOLING COIL Cooling Capacity [ton] | SPLIT OFFICE COOLING COIL Cooling Capacity [ton] | 1.8562 | 1.6342 | 1.838 | 1.6909 | [6 empty] | 2021-05-06
SD_MA_SPLIT GNE COOLING COIL Cooling Capacity [ton] | SPLIT GNE COOLING COIL Cooling Capacity [ton] | 0.78275 | 0.77024 | 0.75985 | 0.73648 | [6 empty] | 2021-05-06
SD_MA_SPLIT GN1 COOLING COIL Cooling Capacity [ton] | SPLIT GN1 COOLING COIL Cooling Capacity [ton] | 0.65762 | 0.64815 | 0.63458 | 0.61968 | [6 empty] | 2021-05-06
SD_MA_SPLIT GN2 COOLING COIL Cooling Capacity [ton] | SPLIT GN2 COOLING COIL Cooling Capacity [ton] | 0.65526 | 0.64584 | 0.63476 | 0.61741 | [6 empty] | 2021-05-06
SD_MA_SPLIT GS1 COOLING COIL Cooling Capacity [ton] | SPLIT GS1 COOLING COIL Cooling Capacity [ton] | 0.70361 | 0.69287 | 0.68494 | 0.66685 | [6 empty] | 2021-05-06
SD_MA_SPLIT GS2 COOLING COIL Cooling Capacity [ton] | SPLIT GS2 COOLING COIL Cooling Capacity [ton] | 0.73345 | 0.71874 | 0.71789 | 0.69297 | [6 empty] | 2021-05-06
SD_MA_SPLIT MSW COOLING COIL Cooling Capacity [ton] | SPLIT MSW COOLING COIL Cooling Capacity [ton] | 2.2928 | 2.2596 | 2.2673 | 2.1926 | [6 empty] | 2021-05-06
SD_MA_SPLIT MNW COOLING COIL Cooling Capacity [ton] | SPLIT MNW COOLING COIL Cooling Capacity [ton] | 2.2125 | 2.1808 | 2.1715 | 2.1014 | [6 empty] | 2021-05-06
SD_MA_SPLIT MSE COOLING COIL Cooling Capacity [ton] | SPLIT MSE COOLING COIL Cooling Capacity [ton] | 1.9852 | 1.9557 | 1.9648 | 1.8998 | [6 empty] | 2021-05-06
SD_MA_SPLIT MNE COOLING COIL Cooling Capacity [ton] | SPLIT MNE COOLING COIL Cooling Capacity [ton] | 1.8152 | 1.7777 | 1.7836 | 1.7158 | [6 empty] | 2021-05-06
SD_MA_SPLIT MN1 COOLING COIL Cooling Capacity [ton] | SPLIT MN1 COOLING COIL Cooling Capacity [ton] | 1.4422 | 1.4234 | 1.394 | 1.3649 | [6 empty] | 2021-05-06
SD_MA_SPLIT MN2 COOLING COIL Cooling Capacity [ton] | SPLIT MN2 COOLING COIL Cooling Capacity [ton] | 1.435 | 1.4164 | 1.3864 | 1.3578 | [6 empty] | 2021-05-06
SD_MA_SPLIT MS1 COOLING COIL Cooling Capacity [ton] | SPLIT MS1 COOLING COIL Cooling Capacity [ton] | 1.5494 | 1.5291 | 1.5101 | 1.4755 | [6 empty] | 2021-05-06
SD_MA_SPLIT MS2 COOLING COIL Cooling Capacity [ton] | SPLIT MS2 COOLING COIL Cooling Capacity [ton] | 1.5434 | 1.5233 | 1.5039 | 1.4698 | [6 empty] | 2021-05-06
SD_MA_SPLIT TSW COOLING COIL Cooling Capacity [ton] | SPLIT TSW COOLING COIL Cooling Capacity [ton] | 1.4193 | 1.4015 | 1.4012 | 1.3597 | [6 empty] | 2021-05-06
SD_MA_SPLIT TNW COOLING COIL Cooling Capacity [ton] | SPLIT TNW COOLING COIL Cooling Capacity [ton] | 1.3732 | 1.3559 | 1.3542 | 1.3149 | [6 empty] | 2021-05-06
SD_MA_SPLIT TSE COOLING COIL Cooling Capacity [ton] | SPLIT TSE COOLING COIL Cooling Capacity [ton] | 1.2701 | 1.2547 | 1.2546 | 1.2211 | [6 empty] | 2021-05-06
SD_MA_SPLIT TNE COOLING COIL Cooling Capacity [ton] | SPLIT TNE COOLING COIL Cooling Capacity [ton] | 1.1804 | 1.1675 | 1.1497 | 1.1238 | [6 empty] | 2021-05-06
SD_MA_SPLIT TN1 COOLING COIL Cooling Capacity [ton] | SPLIT TN1 COOLING COIL Cooling Capacity [ton] | 0.93103 | 0.92137 | 0.90317 | 0.88734 | [6 empty] | 2021-05-06
SD_MA_SPLIT TN2 COOLING COIL Cooling Capacity [ton] | SPLIT TN2 COOLING COIL Cooling Capacity [ton] | 0.92387 | 0.91438 | 0.8957 | 0.8804 | [6 empty] | 2021-05-06
SD_MA_SPLIT TS1 COOLING COIL Cooling Capacity [ton] | SPLIT TS1 COOLING COIL Cooling Capacity [ton] | 1.0342 | 1.0225 | 1.0198 | 0.99561 | [6 empty] | 2021-05-06
SD_MA_SPLIT TS2 COOLING COIL Cooling Capacity [ton] | SPLIT TS2 COOLING COIL Cooling Capacity [ton] | 1.0373 | 1.0255 | 1.0233 | 0.99898 | [6 empty] | 2021-05-06
SD_MA_Split GN1 Furnace with DX Cooling OA Rate [cfm] | Split GN1 Furnace with DX Cooling OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | [6 empty] | 2021-05-06
SD_MA_Split GN2 Furnace with DX Cooling OA Rate [cfm] | Split GN2 Furnace with DX Cooling OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | [6 empty] | 2021-05-06
SD_MA_Split GNE Furnace with DX Cooling OA Rate [cfm] | Split GNE Furnace with DX Cooling OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | [6 empty] | 2021-05-06
SD_MA_Split GNW Furnace with DX Cooling OA Rate [cfm] | Split GNW Furnace with DX Cooling OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | [6 empty] | 2021-05-06
SD_MA_Split GS1 Furnace with DX Cooling OA Rate [cfm] | Split GS1 Furnace with DX Cooling OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | [6 empty] | 2021-05-06
SD_MA_Split GS2 Furnace with DX Cooling OA Rate [cfm] | Split GS2 Furnace with DX Cooling OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | [6 empty] | 2021-05-06
SD_MA_Split GSW Furnace with DX Cooling OA Rate [cfm] | Split GSW Furnace with DX Cooling OA Rate [cfm] | 56.9945 | 56.9945 | 56.9945 | 56.9945 | [6 empty] | 2021-05-06
SD_MA_Split MN1 Furnace with DX Cooling OA Rate [cfm] | Split MN1 Furnace with DX Cooling OA Rate [cfm] | 109.9824 | 109.9824 | 109.9824 | 109.9824 | [6 empty] | 2021-05-06
SD_MA_Split MN2 Furnace with DX Cooling OA Rate [cfm] | Split MN2 Furnace with DX Cooling OA Rate [cfm] | 109.9824 | 109.9824 | 109.9824 | 109.9824 | [6 empty] | 2021-05-06
SD_MA_Split MNE Furnace with DX Cooling OA Rate [cfm] | Split MNE Furnace with DX Cooling OA Rate [cfm] | 109.9824 | 109.9824 | 109.9824 | 109.9824 | [6 empty] | 2021-05-06
SD_MA_Split MNW Furnace with DX Cooling OA Rate [cfm] | Split MNW Furnace with DX Cooling OA Rate [cfm] | 109.9824 | 109.9824 | 109.9824 | 109.9824 | [6 empty] | 2021-05-06
SD_MA_Split MS1 Furnace with DX Cooling OA Rate [cfm] | Split MS1 Furnace with DX Cooling OA Rate [cfm] | 109.9824 | 109.9824 | 109.9824 | 109.9824 | [6 empty] | 2021-05-06
SD_MA_Split MS2 Furnace with DX Cooling OA Rate [cfm] | Split MS2 Furnace with DX Cooling OA Rate [cfm] | 109.9824 | 109.9824 | 109.9824 | 109.9824 | [6 empty] | 2021-05-06
SD_MA_Split MSE Furnace with DX Cooling OA Rate [cfm] | Split MSE Furnace with DX Cooling OA Rate [cfm] | 109.9824 | 109.9824 | 109.9824 | 109.9824 | [6 empty] | 2021-05-06
SD_MA_Split MSW Furnace with DX Cooling OA Rate [cfm] | Split MSW Furnace with DX Cooling OA Rate [cfm] | 109.9824 | 109.9824 | 109.9824 | 109.9824 | [6 empty] | 2021-05-06
SD_MA_Split Office Furnace with DX Cooling OA Rate [cfm] | Split Office Furnace with DX Cooling OA Rate [cfm] | 80.7372 | 80.7372 | 80.7372 | 80.7372 | [6 empty] | 2021-05-06
SD_MA_Split TN1 Furnace with DX Cooling OA Rate [cfm] | Split TN1 Furnace with DX Cooling OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | [6 empty] | 2021-05-06
SD_MA_Split TN2 Furnace with DX Cooling OA Rate [cfm] | Split TN2 Furnace with DX Cooling OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | [6 empty] | 2021-05-06
SD_MA_Split TNE Furnace with DX Cooling OA Rate [cfm] | Split TNE Furnace with DX Cooling OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | [6 empty] | 2021-05-06
SD_MA_Split TNW Furnace with DX Cooling OA Rate [cfm] | Split TNW Furnace with DX Cooling OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | [6 empty] | 2021-05-06
SD_MA_Split TS1 Furnace with DX Cooling OA Rate [cfm] | Split TS1 Furnace with DX Cooling OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | [6 empty] | 2021-05-06
SD_MA_Split TS2 Furnace with DX Cooling OA Rate [cfm] | Split TS2 Furnace with DX Cooling OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | [6 empty] | 2021-05-06
SD_MA_Split TSE Furnace with DX Cooling OA Rate [cfm] | Split TSE Furnace with DX Cooling OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | [6 empty] | 2021-05-06
SD_MA_Split TSW Furnace with DX Cooling OA Rate [cfm] | Split TSW Furnace with DX Cooling OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | [6 empty] | 2021-05-06
SD_MA_SPLIT GSW HEATING COIL Heating Capacity [kBtu/hr] | SPLIT GSW HEATING COIL Heating Capacity [kBtu/hr] | 12.6061 | 12.6652 | 12.4718 | 12.5316 | [6 empty] | 2021-05-06
SD_MA_SPLIT GNW HEATING COIL Heating Capacity [kBtu/hr] | SPLIT GNW HEATING COIL Heating Capacity [kBtu/hr] | 12.5309 | 12.59 | 12.3856 | 12.4455 | [6 empty] | 2021-05-06
SD_MA_SPLIT OFFICE HEATING COIL Heating Capacity [kBtu/hr] | SPLIT OFFICE HEATING COIL Heating Capacity [kBtu/hr] | 26.2258 | 26.3069 | 26.2129 | 26.295 | [6 empty] | 2021-05-06
SD_MA_SPLIT GNE HEATING COIL Heating Capacity [kBtu/hr] | SPLIT GNE HEATING COIL Heating Capacity [kBtu/hr] | 12.4965 | 12.5557 | 12.354 | 12.4139 | [6 empty] | 2021-05-06
SD_MA_SPLIT GN1 HEATING COIL Heating Capacity [kBtu/hr] | SPLIT GN1 HEATING COIL Heating Capacity [kBtu/hr] | 9.2727 | 9.332 | 9.2982 | 9.3581 | [6 empty] | 2021-05-06
SD_MA_SPLIT GN2 HEATING COIL Heating Capacity [kBtu/hr] | SPLIT GN2 HEATING COIL Heating Capacity [kBtu/hr] | 9.2717 | 9.331 | 9.2973 | 9.3572 | [6 empty] | 2021-05-06
SD_MA_SPLIT GS1 HEATING COIL Heating Capacity [kBtu/hr] | SPLIT GS1 HEATING COIL Heating Capacity [kBtu/hr] | 9.2 | 9.2591 | 9.2288 | 9.2886 | [6 empty] | 2021-05-06
SD_MA_SPLIT GS2 HEATING COIL Heating Capacity [kBtu/hr] | SPLIT GS2 HEATING COIL Heating Capacity [kBtu/hr] | 9.7193 | 9.7792 | 9.7518 | 9.8124 | [6 empty] | 2021-05-06
SD_MA_SPLIT MSW HEATING COIL Heating Capacity [kBtu/hr] | SPLIT MSW HEATING COIL Heating Capacity [kBtu/hr] | 23.0814 | 23.2106 | 22.3495 | 22.4791 | [6 empty] | 2021-05-06
SD_MA_SPLIT MNW HEATING COIL Heating Capacity [kBtu/hr] | SPLIT MNW HEATING COIL Heating Capacity [kBtu/hr] | 23.215 | 23.3442 | 22.4738 | 22.6033 | [6 empty] | 2021-05-06
SD_MA_SPLIT MSE HEATING COIL Heating Capacity [kBtu/hr] | SPLIT MSE HEATING COIL Heating Capacity [kBtu/hr] | 23.0015 | 23.1307 | 22.2758 | 22.4054 | [6 empty] | 2021-05-06
SD_MA_SPLIT MNE HEATING COIL Heating Capacity [kBtu/hr] | SPLIT MNE HEATING COIL Heating Capacity [kBtu/hr] | 23.135 | 23.2642 | 22.4001 | 22.5296 | [6 empty] | 2021-05-06
SD_MA_SPLIT MN1 HEATING COIL Heating Capacity [kBtu/hr] | SPLIT MN1 HEATING COIL Heating Capacity [kBtu/hr] | 16.1883 | 16.3143 | 15.8962 | 16.0226 | [6 empty] | 2021-05-06
SD_MA_SPLIT MN2 HEATING COIL Heating Capacity [kBtu/hr] | SPLIT MN2 HEATING COIL Heating Capacity [kBtu/hr] | 16.1862 | 16.3123 | 15.8943 | 16.0207 | [6 empty] | 2021-05-06
SD_MA_SPLIT MS1 HEATING COIL Heating Capacity [kBtu/hr] | SPLIT MS1 HEATING COIL Heating Capacity [kBtu/hr] | 16.065 | 16.1911 | 15.7829 | 15.9092 | [6 empty] | 2021-05-06
SD_MA_SPLIT MS2 HEATING COIL Heating Capacity [kBtu/hr] | SPLIT MS2 HEATING COIL Heating Capacity [kBtu/hr] | 16.063 | 16.189 | 15.781 | 15.9073 | [6 empty] | 2021-05-06
SD_MA_SPLIT TSW HEATING COIL Heating Capacity [kBtu/hr] | SPLIT TSW HEATING COIL Heating Capacity [kBtu/hr] | 15.9925 | 16.0545 | 15.6812 | 15.7434 | [6 empty] | 2021-05-06
SD_MA_SPLIT TNW HEATING COIL Heating Capacity [kBtu/hr] | SPLIT TNW HEATING COIL Heating Capacity [kBtu/hr] | 16.0694 | 16.1314 | 15.7543 | 15.8165 | [6 empty] | 2021-05-06
SD_MA_SPLIT TSE HEATING COIL Heating Capacity [kBtu/hr] | SPLIT TSE HEATING COIL Heating Capacity [kBtu/hr] | 15.9504 | 16.0123 | 15.6422 | 15.7044 | [6 empty] | 2021-05-06
SD_MA_SPLIT TNE HEATING COIL Heating Capacity [kBtu/hr] | SPLIT TNE HEATING COIL Heating Capacity [kBtu/hr] | 16.0272 | 16.0893 | 15.7152 | 15.7774 | [6 empty] | 2021-05-06
SD_MA_SPLIT TN1 HEATING COIL Heating Capacity [kBtu/hr] | SPLIT TN1 HEATING COIL Heating Capacity [kBtu/hr] | 12.1922 | 12.2541 | 12.1571 | 12.2192 | [6 empty] | 2021-05-06
SD_MA_SPLIT TN2 HEATING COIL Heating Capacity [kBtu/hr] | SPLIT TN2 HEATING COIL Heating Capacity [kBtu/hr] | 12.191 | 12.2529 | 12.156 | 12.2181 | [6 empty] | 2021-05-06
SD_MA_SPLIT TS1 HEATING COIL Heating Capacity [kBtu/hr] | SPLIT TS1 HEATING COIL Heating Capacity [kBtu/hr] | 12.109 | 12.1708 | 12.0779 | 12.1399 | [6 empty] | 2021-05-06
SD_MA_SPLIT TS2 HEATING COIL Heating Capacity [kBtu/hr] | SPLIT TS2 HEATING COIL Heating Capacity [kBtu/hr] | 12.1078 | 12.1696 | 12.0768 | 12.1388 | [6 empty] | 2021-05-06
SD_MA_Split_GSW ERV Flag | Split_GSW ERV Flag | Yes | Yes | Yes | Yes | [6 empty] | 2021-05-06
SD_MA_Split_GNW ERV Flag | Split_GNW ERV Flag | Yes | Yes | Yes | Yes | [6 empty] | 2021-05-06
SD_MA_Split_GNE ERV Flag | Split_GNE ERV Flag | Yes | Yes | Yes | Yes | [6 empty] | 2021-05-06
SD_MA_Split_GN1 ERV Flag | Split_GN1 ERV Flag | Yes | Yes | Yes | Yes | [6 empty] | 2021-05-06
SD_MA_Split_GN2 ERV Flag | Split_GN2 ERV Flag | Yes | Yes | Yes | Yes | [6 empty] | 2021-05-06
SD_MA_Split_GS1 ERV Flag | Split_GS1 ERV Flag | Yes | Yes | Yes | Yes | [6 empty] | 2021-05-06
SD_MA_Split_GS2 ERV Flag | Split_GS2 ERV Flag | Yes | Yes | Yes | Yes | [6 empty] | 2021-05-06
SD_MA_Split_MSW ERV Flag | Split_MSW ERV Flag | Yes | Yes | Yes | Yes | [6 empty] | 2021-05-06
SD_MA_Split_MNW ERV Flag | Split_MNW ERV Flag | Yes | Yes | Yes | Yes | [6 empty] | 2021-05-06
SD_MA_Split_MSE ERV Flag | Split_MSE ERV Flag | Yes | Yes | Yes | Yes | [6 empty] | 2021-05-06
SD_MA_Split_MNE ERV Flag | Split_MNE ERV Flag | Yes | Yes | Yes | Yes | [6 empty] | 2021-05-06
SD_MA_Split_MN1 ERV Flag | Split_MN1 ERV Flag | Yes | Yes | Yes | Yes | [6 empty] | 2021-05-06
SD_MA_Split_MN2 ERV Flag | Split_MN2 ERV Flag | Yes | Yes | Yes | Yes | [6 empty] | 2021-05-06
SD_MA_Split_MS1 ERV Flag | Split_MS1 ERV Flag | Yes | Yes | Yes | Yes | [6 empty] | 2021-05-06
SD_MA_Split_MS2 ERV Flag | Split_MS2 ERV Flag | Yes | Yes | Yes | Yes | [6 empty] | 2021-05-06
SD_MA_Split_TSW ERV Flag | Split_TSW ERV Flag | No | No | No | No | [6 empty] | 2021-05-06
SD_MA_Split_TNW ERV Flag | Split_TNW ERV Flag | Yes | Yes | Yes | Yes | [6 empty] | 2021-05-06
SD_MA_Split_TSE ERV Flag | Split_TSE ERV Flag | Yes | Yes | Yes | Yes | [6 empty] | 2021-05-06
SD_MA_Split_TNE ERV Flag | Split_TNE ERV Flag | Yes | Yes | Yes | Yes | [6 empty] | 2021-05-06
SD_MA_Split_TN1 ERV Flag | Split_TN1 ERV Flag | Yes | Yes | Yes | Yes | [6 empty] | 2021-05-06
SD_MA_Split_TN2 ERV Flag | Split_TN2 ERV Flag | Yes | Yes | Yes | Yes | [6 empty] | 2021-05-06
SD_MA_Split_TS1 ERV Flag | Split_TS1 ERV Flag | Yes | Yes | Yes | Yes | [6 empty] | 2021-05-06
SD_MA_Split_TS2 ERV Flag | Split_TS2 ERV Flag | Yes | Yes | Yes | Yes | [6 empty] | 2021-05-06
id | item | Zone3A(TN-Memphis-TN) ASHRAE901-state_STD2016 | Zone3A(TN-Memphis-TN) ASHRAE901-state_STD2019 | Zone4A(TN-Bristol-TN) ASHRAE901-state_STD2016 | Zone4A(TN-Bristol-TN) ASHRAE901-state_STD2019 | [6 empty] | 2021-05-06
TN_SO_PSZ-AC:1 Cooling Capacity [ton] | PSZ-AC:1 Cooling Capacity [ton] | 2.0998 | 2.0018 | 1.7879 | 1.6915 | [6 empty] | 2021-05-06
TN_SO_PSZ-AC:2 Cooling Capacity [ton] | PSZ-AC:2 Cooling Capacity [ton] | 1.8625 | 1.7879 | 1.5242 | 1.4627 | [6 empty] | 2021-05-06
TN_SO_PSZ-AC:3 Cooling Capacity [ton] | PSZ-AC:3 Cooling Capacity [ton] | 1.2349 | 1.1938 | 1.0621 | 1.0237 | [6 empty] | 2021-05-06
TN_SO_PSZ-AC:4 Cooling Capacity [ton] | PSZ-AC:4 Cooling Capacity [ton] | 1.8457 | 1.7674 | 1.4837 | 1.4167 | [6 empty] | 2021-05-06
TN_SO_PSZ-AC:5 Cooling Capacity [ton] | PSZ-AC:5 Cooling Capacity [ton] | 1.4414 | 1.3943 | 1.2493 | 1.2105 | [6 empty] | 2021-05-06
TN_SO_PSZ-AC:1 Supply Flow Rate [cfm] | PSZ-AC:1 Supply Flow Rate [cfm] | 678.0416 | 635.664 | 678.0416 | 635.664 | [6 empty] | 2021-05-06
TN_SO_PSZ-AC:2 Supply Flow Rate [cfm] | PSZ-AC:2 Supply Flow Rate [cfm] | 635.664 | 593.2864 | 593.2864 | 550.9088 | [6 empty] | 2021-05-06
TN_SO_PSZ-AC:3 Supply Flow Rate [cfm] | PSZ-AC:3 Supply Flow Rate [cfm] | 466.1536 | 444.9648 | 444.9648 | 423.776 | [6 empty] | 2021-05-06
TN_SO_PSZ-AC:4 Supply Flow Rate [cfm] | PSZ-AC:4 Supply Flow Rate [cfm] | 635.664 | 593.2864 | 572.0976 | 529.72 | [6 empty] | 2021-05-06
TN_SO_PSZ-AC:5 Supply Flow Rate [cfm] | PSZ-AC:5 Supply Flow Rate [cfm] | 550.9088 | 529.72 | 529.72 | 508.5312 | [6 empty] | 2021-05-06
TN_SO_PSZ-AC:1 OA Rate [cfm] | PSZ-AC:1 OA Rate [cfm] | 136.9178 | 136.9178 | 136.9178 | 136.9178 | [6 empty] | 2021-05-06
TN_SO_PSZ-AC:2 OA Rate [cfm] | PSZ-AC:2 OA Rate [cfm] | 103.7925 | 103.7925 | 103.7925 | 103.7925 | [6 empty] | 2021-05-06
TN_SO_PSZ-AC:3 OA Rate [cfm] | PSZ-AC:3 OA Rate [cfm] | 61.5711 | 61.5711 | 61.5711 | 61.5711 | [6 empty] | 2021-05-06
TN_SO_PSZ-AC:4 OA Rate [cfm] | PSZ-AC:4 OA Rate [cfm] | 103.7925 | 103.7925 | 103.7925 | 103.7925 | [6 empty] | 2021-05-06
TN_SO_PSZ-AC:5 OA Rate [cfm] | PSZ-AC:5 OA Rate [cfm] | 61.5711 | 61.5711 | 61.5711 | 61.5711 | [6 empty] | 2021-05-06
TN_SO_PSZ-AC:1 heating Capacity [kBtu/hr] | PSZ-AC:1 heating Capacity [kBtu/hr] | 12.7643 | 12.7643 | 13.013 | 13.013 | [6 empty] | 2021-05-06
TN_SO_PSZ-AC:2 heating Capacity [kBtu/hr] | PSZ-AC:2 heating Capacity [kBtu/hr] | 18.303 | 18.0567 | 17.0962 | 16.8992 | [6 empty] | 2021-05-06
TN_SO_PSZ-AC:3 heating Capacity [kBtu/hr] | PSZ-AC:3 heating Capacity [kBtu/hr] | 11.2873 | 11.1443 | 10.3788 | 10.2735 | [6 empty] | 2021-05-06
TN_SO_PSZ-AC:4 heating Capacity [kBtu/hr] | PSZ-AC:4 heating Capacity [kBtu/hr] | 18.1282 | 17.9165 | 16.9219 | 16.7608 | [6 empty] | 2021-05-06
TN_SO_PSZ-AC:5 heating Capacity [kBtu/hr] | PSZ-AC:5 heating Capacity [kBtu/hr] | 11.2873 | 11.1443 | 10.4137 | 10.3047 | [6 empty] | 2021-05-06
id | item | Zone3A(TN-Memphis-TN) ASHRAE901-state_STD2016 | Zone3A(TN-Memphis-TN) ASHRAE901-state_STD2019 | Zone4A(TN-Bristol-TN) ASHRAE901-state_STD2016 | Zone4A(TN-Bristol-TN) ASHRAE901-state_STD2019 | [6 empty] | 2021-05-06
TN_LO_CAV_BAS Supply Flow Rate [cfm] | CAV_BAS Supply Flow Rate [cfm] | 11569.0848 | 10700.344 | 12247.1264 | 11357.1968 | [6 empty] | 2021-05-06
TN_LO_VAV_BOT WITH REHEAT Supply Flow Rate [cfm] | VAV_BOT WITH REHEAT Supply Flow Rate [cfm] | 19557.2624 | 18603.7664 | 19896.2832 | 18942.7872 | [6 empty] | 2021-05-06
TN_LO_VAV_MID WITH REHEAT Supply Flow Rate [cfm] | VAV_MID WITH REHEAT Supply Flow Rate [cfm] | 182520.3235 | 173430.3283 | 183643.3299 | 174277.8803 | [6 empty] | 2021-05-06
TN_LO_VAV_TOP WITH REHEAT Supply Flow Rate [cfm] | VAV_TOP WITH REHEAT Supply Flow Rate [cfm] | 18985.1648 | 18179.9904 | 19769.1504 | 18942.7872 | [6 empty] | 2021-05-06
TN_LO_Supply Air Temp. Reset Flag | Supply Air Temp. Reset Flag | No | Yes | Yes | Yes | [6 empty] | 2021-05-06
TN_LO_CAV_BAS OA Rate [cfm] | CAV_BAS OA Rate [cfm] | 2542.8255 | 2542.8255 | 2542.8255 | 2542.8255 | [6 empty] | 2021-05-06
TN_LO_VAV_BOT WITH REHEAT OA Rate [cfm] | VAV_BOT WITH REHEAT OA Rate [cfm] | 5377.8022 | 4302.174 | 5377.8022 | 4302.174 | [6 empty] | 2021-05-06
TN_LO_VAV_MID WITH REHEAT OA Rate [cfm] | VAV_MID WITH REHEAT OA Rate [cfm] | 53777.9373 | 43021.7396 | 53777.9373 | 43021.7396 | [6 empty] | 2021-05-06
TN_LO_VAV_TOP WITH REHEAT OA Rate [cfm] | VAV_TOP WITH REHEAT OA Rate [cfm] | 5377.8022 | 4302.174 | 5377.8022 | 4302.174 | [6 empty] | 2021-05-06
TN_LO_AIRLOOP DATACENTER BASEMENT OA Rate [cfm] | AIRLOOP DATACENTER BASEMENT OA Rate [cfm] | 716.9654 | 716.9654 | 716.9654 | 716.9654 | [6 empty] | 2021-05-06
TN_LO_VAV_bot_WITH_REHEAT ERV Flag | VAV_bot_WITH_REHEAT ERV Flag | Yes | Yes | Yes | Yes | [6 empty] | 2021-05-06
TN_LO_VAV_mid_WITH_REHEAT ERV Flag | VAV_mid_WITH_REHEAT ERV Flag | Yes | Yes | Yes | Yes | [6 empty] | 2021-05-06
TN_LO_VAV_top_WITH_REHEAT ERV Flag | VAV_top_WITH_REHEAT ERV Flag | Yes | Yes | Yes | Yes | [6 empty] | 2021-05-06
TN_LO_COOLSYS1 CHILLER1 Capacity [ton] | COOLSYS1 CHILLER1 Capacity [ton] | 454.5843 | 406.7483 | 379.2722 | 343.6176 | [6 empty] | 2021-05-06
TN_LO_COOLSYS1 CHILLER2 Capacity [ton] | COOLSYS1 CHILLER2 Capacity [ton] | 454.5843 | 406.7483 | 379.2722 | 343.6176 | [6 empty] | 2021-05-06
TN_LO_TOWERWATERSYS COOLTOWER 1 Capacity [ton] | TOWERWATERSYS COOLTOWER 1 Capacity [ton] | 431.485 | 386.0786 | 359.9952 | 326.1538 | [6 empty] | 2021-05-06
TN_LO_TOWERWATERSYS COOLTOWER 2 Capacity [ton] | TOWERWATERSYS COOLTOWER 2 Capacity [ton] | 431.485 | 386.0786 | 359.9952 | 326.1538 | [6 empty] | 2021-05-06
TN_LO_HEATSYS1 BOILER Capacity [MMBTU/h] | HEATSYS1 BOILER Capacity [MMBTU/h] | 3989.7855 | 3545.0706 | 3993.4641 | 3515.1645 | [6 empty] | 2021-05-06
TN_LO_COOLSYS1 PUMP Flow Rate [gal/min] | COOLSYS1 PUMP Flow Rate [gal/min] | 0 | 0 | 0 | 0 | [6 empty] | 2021-05-06
TN_LO_COOLSYS1 CHILLER1 PUMP Flow Rate [gal/min] | COOLSYS1 CHILLER1 PUMP Flow Rate [gal/min] | 716.6502 | 638.3353 | 597.3733 | 538.3198 | [6 empty] | 2021-05-06
TN_LO_COOLSYS1 CHILLER2 PUMP Flow Rate [gal/min] | COOLSYS1 CHILLER2 PUMP Flow Rate [gal/min] | 716.6502 | 638.3353 | 597.3733 | 538.3198 | [6 empty] | 2021-05-06
TN_LO_COOLSYS1 PUMP SECONDARY Flow Rate [gal/min] | COOLSYS1 PUMP SECONDARY Flow Rate [gal/min] | 1433.2988 | 1276.6706 | 1194.7451 | 1076.6395 | [6 empty] | 2021-05-06
TN_LO_HEATSYS1 PUMP Flow Rate [gal/min] | HEATSYS1 PUMP Flow Rate [gal/min] | 818.9561 | 727.6725 | 819.7106 | 721.5337 | [6 empty] | 2021-05-06
TN_LO_TOWERWATERSYS PUMP Flow Rate [gal/min] | TOWERWATERSYS PUMP Flow Rate [gal/min] | 2507.9966 | 2244.0888 | 2092.4012 | 1895.6986 | [6 empty] | 2021-05-06
TN_LO_PLANT CIRC PUMP Flow Rate [gal/min] | PLANT CIRC PUMP Flow Rate [gal/min] | 208.8534 | 207.9547 | 210.9345 | 210.0929 | [6 empty] | 2021-05-06
TN_LO_COOLSYS1 PUMP SECONDARY Pressure setpoint reset [yes,no] | COOLSYS1 PUMP SECONDARY Pressure setpoint reset [yes,no] | pump_ride_on_curve | pump_ride_on_curve | pump_ride_on_curve | pump_ride_on_curve | [6 empty] | 2021-05-06
TN_LO_COOLSYS1 CHILLER1 PUMP Pump Power [hp] | COOLSYS1 CHILLER1 PUMP Pump Power [hp] | 3.8661 | 3.4095 | 3.2226 | 2.8753 | [6 empty] | 2021-05-06
TN_LO_COOLSYS1 CHILLER2 PUMP Pump Power [hp] | COOLSYS1 CHILLER2 PUMP Pump Power [hp] | 3.8661 | 3.4095 | 3.2226 | 2.8753 | [6 empty] | 2021-05-06
TN_LO_COOLSYS1 PUMP SECONDARY Pump Power [hp] | COOLSYS1 PUMP SECONDARY Pump Power [hp] | 23.1964 | 20.457 | 19.3357 | 17.2518 | [6 empty] | 2021-05-06
TN_LO_HEATSYS1 PUMP Pump Power [hp] | HEATSYS1 PUMP Pump Power [hp] | 17.7022 | 15.5733 | 17.7185 | 15.4419 | [6 empty] | 2021-05-06
TN_LO_TOWERWATERSYS PUMP Pump Power [hp] | TOWERWATERSYS PUMP Pump Power [hp] | 44.9029 | 39.78 | 37.4637 | 33.6058 | [6 empty] | 2021-05-06
TN_LO_PLANT CIRC PUMP Pump Power [hp] | PLANT CIRC PUMP Pump Power [hp] | 4.5068 | 4.443 | 4.5517 | 4.4886 | [6 empty] | 2021-05-06
TN_LO_Datacenter PLANT CIRC PUMP Pump Power [hp] | Datacenter PLANT CIRC PUMP Pump Power [hp] | 4.5068 | 4.443 | 4.5517 | 4.4886 | [6 empty] | 2021-05-06
TN_LO_ZN_VAV_BOXes_Max_Reheat_Water_Flow_GPM | ZN_VAV_BOXes_Max_Reheat_Water_Flow_GPM | 455.0206 | 435.773 | 426.8995 | 407.3979 | [6 empty] | 2021-05-06
TN_LO_COOLSYS1 PUMP SECONDARY VSD | COOLSYS1 PUMP SECONDARY VSD | No | No | No | No | [6 empty] | 2021-05-06
TN_LO_HEATSYS1 PUMP VSD | HEATSYS1 PUMP VSD | No | No | No | No | [6 empty] | 2021-05-06
TN_LO_DATACENTER BASEMENT Cooling Capacity [ton] | DATACENTER BASEMENT Cooling Capacity [ton] | 122.4493 | 122.092 | 123.7632 | 123.396 | [6 empty] | 2021-05-06
TN_LO_DATACENTER BOT Cooling Capacity [ton] | DATACENTER BOT Cooling Capacity [ton] | 2.6582 | 2.6307 | 2.6673 | 2.6437 | [6 empty] | 2021-05-06
TN_LO_DATACENTER MID Cooling Capacity [ton] | DATACENTER MID Cooling Capacity [ton] | 25.3207 | 25.0675 | 25.4864 | 25.2803 | [6 empty] | 2021-05-06
TN_LO_DATACENTER TOP Cooling Capacity [ton] | DATACENTER TOP Cooling Capacity [ton] | 2.5611 | 2.5413 | 2.5973 | 2.5773 | [6 empty] | 2021-05-06
id | item | Zone3A(TN-Memphis-TN) ASHRAE901-state_STD2016 | Zone3A(TN-Memphis-TN) ASHRAE901-state_STD2019 | Zone4A(TN-Bristol-TN) ASHRAE901-state_STD2016 | Zone4A(TN-Bristol-TN) ASHRAE901-state_STD2019 | [6 empty] | 2021-05-06
TN_RS_PSZ-AC:1 Cooling Capacity [ton] | PSZ-AC:1 Cooling Capacity [ton] | 11.384 | 11.0037 | 9.9298 | 9.5885 | [6 empty] | 2021-05-06
TN_RS_PSZ-AC:2 Cooling Capacity [ton] | PSZ-AC:2 Cooling Capacity [ton] | 51.9006 | 48.9007 | 46.5068 | 44.5397 | [6 empty] | 2021-05-06
TN_RS_PSZ-AC:3 Cooling Capacity [ton] | PSZ-AC:3 Cooling Capacity [ton] | 7.0894 | 6.924 | 6.0323 | 5.8713 | [6 empty] | 2021-05-06
TN_RS_PSZ-AC:4 Cooling Capacity [ton] | PSZ-AC:4 Cooling Capacity [ton] | 5.8565 | 5.6875 | 4.8263 | 4.6562 | [6 empty] | 2021-05-06
TN_RS_PSZ-AC:1 Supply Flow Rate [cfm] | PSZ-AC:1 Supply Flow Rate [cfm] | 4216.5712 | 3962.3056 | 4025.872 | 3729.2288 | [6 empty] | 2021-05-06
TN_RS_PSZ-AC:2 Supply Flow Rate [cfm] | PSZ-AC:2 Supply Flow Rate [cfm] | 15573.768 | 14683.8384 | 15594.9568 | 14705.0272 | [6 empty] | 2021-05-06
TN_RS_PSZ-AC:3 Supply Flow Rate [cfm] | PSZ-AC:3 Supply Flow Rate [cfm] | 2351.9568 | 2288.3904 | 2288.3904 | 2203.6352 | [6 empty] | 2021-05-06
TN_RS_PSZ-AC:4 Supply Flow Rate [cfm] | PSZ-AC:4 Supply Flow Rate [cfm] | 1822.2368 | 1737.4816 | 1716.2928 | 1631.5376 | [6 empty] | 2021-05-06
TN_RS_PSZ-AC:1 OA Rate [cfm] | PSZ-AC:1 OA Rate [cfm] | 490.669 | 490.669 | 490.669 | 490.669 | [6 empty] | 2021-05-06
TN_RS_PSZ-AC:2 OA Rate [cfm] | PSZ-AC:2 OA Rate [cfm] | 4005.1282 | 4005.1282 | 4005.1282 | 4005.1282 | [6 empty] | 2021-05-06
TN_RS_PSZ-AC:3 OA Rate [cfm] | PSZ-AC:3 OA Rate [cfm] | 377.3937 | 377.3937 | 377.3937 | 377.3937 | [6 empty] | 2021-05-06
TN_RS_PSZ-AC:4 OA Rate [cfm] | PSZ-AC:4 OA Rate [cfm] | 377.3937 | 377.3937 | 377.3937 | 377.3937 | [6 empty] | 2021-05-06
TN_RS_PSZ-AC:1 OA Damper [gravity, motorized] | PSZ-AC:1 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2021-05-06
TN_RS_PSZ-AC:2 OA Damper [gravity, motorized] | PSZ-AC:2 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2021-05-06
TN_RS_PSZ-AC:3 OA Damper [gravity, motorized] | PSZ-AC:3 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2021-05-06
TN_RS_PSZ-AC:4 OA Damper [gravity, motorized] | PSZ-AC:4 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2021-05-06
TN_RS_PSZ-AC:1 Heating Capacity [kBtu/hr] | PSZ-AC:1 Heating Capacity [kBtu/hr] | 182.3901 | 172.1883 | 169.2074 | 158.2812 | [6 empty] | 2021-05-06
TN_RS_PSZ-AC:2 Heating Capacity [kBtu/hr] | PSZ-AC:2 Heating Capacity [kBtu/hr] | 786.3374 | 748.2071 | 774.7281 | 738.8666 | [6 empty] | 2021-05-06
TN_RS_PSZ-AC:3 Heating Capacity [kBtu/hr] | PSZ-AC:3 Heating Capacity [kBtu/hr] | 108.1506 | 105.3786 | 102.8396 | 100.1738 | [6 empty] | 2021-05-06
TN_RS_PSZ-AC:4 Heating Capacity [kBtu/hr] | PSZ-AC:4 Heating Capacity [kBtu/hr] | 88.4535 | 85.576 | 82.5626 | 79.5067 | [6 empty] | 2021-05-06
id | item | Zone3A(TN-Memphis-TN) ASHRAE901-state_STD2016 | Zone3A(TN-Memphis-TN) ASHRAE901-state_STD2019 | Zone4A(TN-Bristol-TN) ASHRAE901-state_STD2016 | Zone4A(TN-Bristol-TN) ASHRAE901-state_STD2019 | [6 empty] | 2021-05-06
TN_PS_VAV_POD_1 Cooling Capacity [ton] | VAV_POD_1 Cooling Capacity [ton] | 18.9453 | 18.2722 | 19.3035 | 18.5874 | [6 empty] | 2021-05-06
TN_PS_VAV_POD_2 Cooling Capacity [ton] | VAV_POD_2 Cooling Capacity [ton] | 18.9361 | 18.2425 | 19.0036 | 18.4454 | [6 empty] | 2021-05-06
TN_PS_VAV_POD_3 Cooling Capacity [ton] | VAV_POD_3 Cooling Capacity [ton] | 17.2252 | 16.3627 | 17.6193 | 16.7255 | [6 empty] | 2021-05-06
TN_PS_VAV_OTHER Cooling Capacity [ton] | VAV_OTHER Cooling Capacity [ton] | 26.3812 | 24.7958 | 27.3865 | 25.4671 | [6 empty] | 2021-05-06
TN_PS_PSZ-AC_1:6 Cooling Capacity [ton] | PSZ-AC_1:6 Cooling Capacity [ton] | 8.4312 | 8.053 | 8.1302 | 7.8668 | [6 empty] | 2021-05-06
TN_PS_PSZ-AC_2:5 Cooling Capacity [ton] | PSZ-AC_2:5 Cooling Capacity [ton] | 5.2754 | 5.1016 | 5.5152 | 5.6073 | [6 empty] | 2021-05-06
TN_PS_PSZ-AC_2:7 Cooling Capacity [ton] | PSZ-AC_2:7 Cooling Capacity [ton] | 10.5074 | 10.5074 | 10.5074 | 10.5074 | [6 empty] | 2021-05-06
TN_PS_VAV_POD_1 Supply Flow Rate [cfm] | VAV_POD_1 Supply Flow Rate [cfm] | 5678.5984 | 5487.8992 | 5784.5424 | 5572.6544 | [6 empty] | 2021-05-06
TN_PS_VAV_POD_2 Supply Flow Rate [cfm] | VAV_POD_2 Supply Flow Rate [cfm] | 5678.5984 | 5466.7104 | 5699.7872 | 5530.2768 | [6 empty] | 2021-05-06
TN_PS_VAV_POD_3 Supply Flow Rate [cfm] | VAV_POD_3 Supply Flow Rate [cfm] | 5170.0672 | 4915.8016 | 5297.2 | 5021.7456 | [6 empty] | 2021-05-06
TN_PS_VAV_OTHER Supply Flow Rate [cfm] | VAV_OTHER Supply Flow Rate [cfm] | 7924.6112 | 7437.2688 | 8221.2544 | 7733.912 | [6 empty] | 2021-05-06
TN_PS_PSZ-AC_2:5 Supply Flow Rate [cfm] | PSZ-AC_2:5 Supply Flow Rate [cfm] | 1589.16 | 1525.5936 | 1652.7264 | 1673.9152 | [6 empty] | 2021-05-06
TN_PS_PSZ-AC_1:6 Supply Flow Rate [cfm] | PSZ-AC_1:6 Supply Flow Rate [cfm] | 2521.4672 | 2415.5232 | 2648.6 | 2542.656 | [6 empty] | 2021-05-06
TN_PS_PSZ-AC_2:7 Supply Flow Rate [cfm] | PSZ-AC_2:7 Supply Flow Rate [cfm] | 3157.1312 | 3157.1312 | 3157.1312 | 3157.1312 | [6 empty] | 2021-05-06
TN_PS_Supply Air Temp. Reset Flag | Supply Air Temp. Reset Flag | No | No | Yes | Yes | [6 empty] | 2021-05-06
TN_PS_VAV_POD_1 OA Rate [cfm] | VAV_POD_1 OA Rate [cfm] | 5683.5142 | 5483.1741 | 5792.6789 | 5577.7609 | [6 empty] | 2021-05-06
TN_PS_VAV_POD_2 OA Rate [cfm] | VAV_POD_2 OA Rate [cfm] | 5682.4124 | 5474.2748 | 5701.1221 | 5535.1714 | [6 empty] | 2021-05-06
TN_PS_VAV_POD_3 OA Rate [cfm] | VAV_POD_3 OA Rate [cfm] | 5168.9866 | 4910.1654 | 5286.8387 | 5019.0334 | [6 empty] | 2021-05-06
TN_PS_VAV_OTHER OA Rate [cfm] | VAV_OTHER OA Rate [cfm] | 3736.1787 | 2988.8921 | 3736.1787 | 2988.8921 | [6 empty] | 2021-05-06
TN_PS_PSZ-AC_2:5 OA Rate [cfm] | PSZ-AC_2:5 OA Rate [cfm] | 1152.7343 | 1152.7343 | 1152.7343 | 1152.7343 | [6 empty] | 2021-05-06
TN_PS_PSZ-AC_1:6 OA Rate [cfm] | PSZ-AC_1:6 OA Rate [cfm] | 539.9118 | 539.9118 | 539.9118 | 539.9118 | [6 empty] | 2021-05-06
TN_PS_PSZ-AC_2:7 OA Rate [cfm] | PSZ-AC_2:7 OA Rate [cfm] | 3153.0841 | 3153.0841 | 3153.0841 | 3153.0841 | [6 empty] | 2021-05-06
TN_PS_VAV_POD_1 OA Damper [gravity, motorized] | VAV_POD_1 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2021-05-06
TN_PS_VAV_POD_2 OA Damper [gravity, motorized] | VAV_POD_2 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2021-05-06
TN_PS_VAV_POD_3 OA Damper [gravity, motorized] | VAV_POD_3 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2021-05-06
TN_PS_VAV_OTHER OA Damper [gravity, motorized] | VAV_OTHER OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2021-05-06
TN_PS_PSZ-AC_2:5 OA Damper [gravity, motorized] | PSZ-AC_2:5 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2021-05-06
TN_PS_PSZ-AC_1:6 OA Damper [gravity, motorized] | PSZ-AC_1:6 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2021-05-06
TN_PS_PSZ-AC_2:7 OA Damper [gravity, motorized] | PSZ-AC_2:7 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2021-05-06
TN_PS_VAV_POD_1 (economizer) | VAV_POD_1 (economizer) | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialEnthalpy | [6 empty] | 2021-05-06
TN_PS_VAV_POD_2 (economizer) | VAV_POD_2 (economizer) | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialEnthalpy | [6 empty] | 2021-05-06
TN_PS_VAV_POD_3 (economizer) | VAV_POD_3 (economizer) | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialEnthalpy | [6 empty] | 2021-05-06
TN_PS_VAV_OTHER (economizer) | VAV_OTHER (economizer) | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialEnthalpy | [6 empty] | 2021-05-06
TN_PS_PSZ-AC_2:5 (economizer) | PSZ-AC_2:5 (economizer) | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialEnthalpy | [6 empty] | 2021-05-06
TN_PS_PSZ-AC_1:6 (economizer) | PSZ-AC_1:6 (economizer) | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialEnthalpy | [6 empty] | 2021-05-06
TN_PS_PSZ-AC_2:7 (economizer) | PSZ-AC_2:7 (economizer) | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialEnthalpy | [6 empty] | 2021-05-06
TN_PS_VAV_Pod_1_ERV Flag | VAV_Pod_1_ERV Flag | Yes | Yes | Yes | Yes | [6 empty] | 2021-05-06
TN_PS_VAV_Pod_2_ERV Flag | VAV_Pod_2_ERV Flag | Yes | Yes | Yes | Yes | [6 empty] | 2021-05-06
TN_PS_VAV_Pod_3_ERV Flag | VAV_Pod_3_ERV Flag | Yes | Yes | Yes | Yes | [6 empty] | 2021-05-06
TN_PS_VAV_OTHER_ERV Flag | VAV_OTHER_ERV Flag | Yes | Yes | Yes | Yes | [6 empty] | 2021-05-06
TN_PS_PSZ_AC_2_5_ERV Flag | PSZ_AC_2_5_ERV Flag | Yes | Yes | No | No | [6 empty] | 2021-05-06
TN_PS_PSZ_AC_2_7_ERV Flag | PSZ_AC_2_7_ERV Flag | Yes | Yes | Yes | Yes | [6 empty] | 2021-05-06
TN_PS_HEATSYS1 Capacity [MMBTU/h] | HEATSYS1 Capacity [MMBTU/h] | 0.9734 | 0.92735 | 0.96575 | 0.92052 | [6 empty] | 2021-05-06
TN_PS_HEATSYS1 Flow Rate [gal/min] | HEATSYS1 Flow Rate [gal/min] | 99.9021 | 95.175 | 99.1165 | 94.4739 | [6 empty] | 2021-05-06
TN_PS_VAV_POD_1 Fan Power [hp] | VAV_POD_1 Fan Power [hp] | 8.3873 | 8.0893 | 8.5459 | 8.2289 | [6 empty] | 2021-05-06
TN_PS_VAV_POD_2 Fan Power [hp] | VAV_POD_2 Fan Power [hp] | 8.3833 | 8.0762 | 8.4132 | 8.166 | [6 empty] | 2021-05-06
TN_PS_VAV_POD_3 Fan Power [hp] | VAV_POD_3 Fan Power [hp] | 7.6258 | 7.244 | 7.8003 | 7.4046 | [6 empty] | 2021-05-06
TN_PS_VAV_OTHER Fan Power [hp] | VAV_OTHER Fan Power [hp] | 11.5908 | 10.8943 | 12.0325 | 11.3162 | [6 empty] | 2021-05-06
TN_PS_HEATSYS1 Pump Power [hp] | HEATSYS1 Pump Power [hp] | 2.1594 | 2.0369 | 2.1425 | 2.0219 | [6 empty] | 2021-05-06
TN_PS_PSZ-AC_1:6 Heating Capacity [kBtu/hr] | PSZ-AC_1:6 Heating Capacity [kBtu/hr] | 203.9838 | 195.2217 | 207.7579 | 199.2303 | [6 empty] | 2021-05-06
TN_PS_PSZ-AC_2:5 Heating Capacity [kBtu/hr] | PSZ-AC_2:5 Heating Capacity [kBtu/hr] | 123.2467 | 121.3334 | 127.1721 | 128.1408 | [6 empty] | 2021-05-06
TN_PS_PSZ-AC_2:7 Heating Capacity [kBtu/hr] | PSZ-AC_2:7 Heating Capacity [kBtu/hr] | 293.9493 | 293.9493 | 299.6773 | 299.6773 | [6 empty] | 2021-05-06
TN_PS_ZN_VAV_BOXes_Max_Reheat_Water_Flow_GPM | ZN_VAV_BOXes_Max_Reheat_Water_Flow_GPM | 69.2394 | 65.9478 | 64.5962 | 61.5276 | [6 empty] | 2021-05-06
id | item | Zone3A(TN-Memphis-TN) ASHRAE901-state_STD2016 | Zone3A(TN-Memphis-TN) ASHRAE901-state_STD2019 | Zone4A(TN-Bristol-TN) ASHRAE901-state_STD2016 | Zone4A(TN-Bristol-TN) ASHRAE901-state_STD2019 | [6 empty] | 2021-05-06
TN_SH_SAC_FRONTOFFICE Cooling Capacity [ton] | SAC_FRONTOFFICE Cooling Capacity [ton] | 2.578 | 2.4464 | 2.2056 | 2.0812 | [6 empty] | 2021-05-06
TN_SH_SAC_FRONTLOUNGE Cooling Capacity [ton] | SAC_FRONTLOUNGE Cooling Capacity [ton] | 6.2075 | 5.8961 | 6.0878 | 5.8451 | [6 empty] | 2021-05-06
TN_SH_SAC_MEETINGROOM Cooling Capacity [ton] | SAC_MEETINGROOM Cooling Capacity [ton] | 2.972 | 2.8609 | 2.966 | 2.8897 | [6 empty] | 2021-05-06
TN_SH_SAC_EXC_EMPLGE_RESTRM Cooling Capacity [ton] | SAC_EXC_EMPLGE_RESTRM Cooling Capacity [ton] | 6.3079 | 6.2661 | 5.8595 | 5.8102 | [6 empty] | 2021-05-06
TN_SH_SAC_FO_ADDAQ SUPPLY FAN Supply Flow Rate [cfm] | SAC_FO_ADDAQ SUPPLY FAN Supply Flow Rate [cfm] | 805.1744 | 762.7968 | 783.9856 | 741.608 | [6 empty] | 2021-05-06
TN_SH_SAC_FL_ADDAQ SUPPLY FAN Supply Flow Rate [cfm] | SAC_FL_ADDAQ SUPPLY FAN Supply Flow Rate [cfm] | 1864.6144 | 1779.8592 | 1885.8032 | 1779.8592 | [6 empty] | 2021-05-06
TN_SH_SAC_MR_ADDAQ SUPPLY FAN Supply Flow Rate [cfm] | SAC_MR_ADDAQ SUPPLY FAN Supply Flow Rate [cfm] | 889.9296 | 868.7408 | 889.9296 | 868.7408 | [6 empty] | 2021-05-06
TN_SH_SAC_EXC_ADDAQ SUPPLY FAN Supply Flow Rate [cfm] | SAC_EXC_ADDAQ SUPPLY FAN Supply Flow Rate [cfm] | 2182.4464 | 2161.2576 | 2288.3904 | 2267.2016 | [6 empty] | 2021-05-06
TN_SH_SAC_Exc_EmpLge_RestRm OA Rate [cfm] | SAC_Exc_EmpLge_RestRm OA Rate [cfm] | 199.9928 | 199.9928 | 199.9928 | 199.9928 | [6 empty] | 2021-05-06
TN_SH_SAC_FrontLounge OA Rate [cfm] | SAC_FrontLounge OA Rate [cfm] | 500.0133 | 500.0133 | 500.0133 | 500.0133 | [6 empty] | 2021-05-06
TN_SH_SAC_FrontOffice OA Rate [cfm] | SAC_FrontOffice OA Rate [cfm] | 119.2938 | 119.2938 | 119.2938 | 119.2938 | [6 empty] | 2021-05-06
TN_SH_SAC_MeetingRoom OA Rate [cfm] | SAC_MeetingRoom OA Rate [cfm] | 267.7629 | 267.7629 | 267.7629 | 267.7629 | [6 empty] | 2021-05-06
TN_SH_SAC_FrontLounge OA Damper [gravity, motorized] | SAC_FrontLounge OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2021-05-06
TN_SH_SAC_FrontOffice (economizer) | SAC_FrontOffice (economizer) | No | No | No | No | [6 empty] | 2021-05-06
TN_SH_SAC_FrontLounge (economizer) | SAC_FrontLounge (economizer) | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialEnthalpy | [6 empty] | 2021-05-06
TN_SH_SAC_MeetingRoom (economizer) | SAC_MeetingRoom (economizer) | No | No | No | No | [6 empty] | 2021-05-06
TN_SH_SAC_Exc_EmpLge_RestRm (economizer) | SAC_Exc_EmpLge_RestRm (economizer) | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialEnthalpy | [6 empty] | 2021-05-06
TN_SH_SAC_FRONTOFFICE Heating Capacity [kBtu/hr] | SAC_FRONTOFFICE Heating Capacity [kBtu/hr] | 36.3576 | 34.3623 | 34.5057 | 32.7493 | [6 empty] | 2021-05-06
TN_SH_SAC_FRONTLOUNGE Heating Capacity [kBtu/hr] | SAC_FRONTLOUNGE Heating Capacity [kBtu/hr] | 96.2978 | 92.8911 | 95.6711 | 92.2901 | [6 empty] | 2021-05-06
TN_SH_SAC_MEETINGROOM Heating Capacity [kBtu/hr] | SAC_MEETINGROOM Heating Capacity [kBtu/hr] | 47.715 | 46.4995 | 47.1411 | 46.3423 | [6 empty] | 2021-05-06
TN_SH_SAC_EXC_EMPLGE_RESTRM Heating Capacity [kBtu/hr] | SAC_EXC_EMPLGE_RESTRM Heating Capacity [kBtu/hr] | 90.8977 | 90.2494 | 91.7194 | 91.0646 | [6 empty] | 2021-05-06
id | item | Zone3A(TN-Memphis-TN) ASHRAE901-state_STD2016 | Zone3A(TN-Memphis-TN) ASHRAE901-state_STD2019 | Zone4A(TN-Bristol-TN) ASHRAE901-state_STD2016 | Zone4A(TN-Bristol-TN) ASHRAE901-state_STD2019 | [6 empty] | 2021-05-06
TN_MA_SPLIT GSW COOLING COIL Cooling Capacity [ton] | SPLIT GSW COOLING COIL Cooling Capacity [ton] | 0.95082 | 0.93989 | 0.7901 | 0.7764 | [6 empty] | 2021-05-06
TN_MA_SPLIT GNW COOLING COIL Cooling Capacity [ton] | SPLIT GNW COOLING COIL Cooling Capacity [ton] | 0.9321 | 0.92112 | 0.76185 | 0.74835 | [6 empty] | 2021-05-06
TN_MA_SPLIT OFFICE COOLING COIL Cooling Capacity [ton] | SPLIT OFFICE COOLING COIL Cooling Capacity [ton] | 1.8214 | 1.7148 | 1.6333 | 1.501 | [6 empty] | 2021-05-06
TN_MA_SPLIT GNE COOLING COIL Cooling Capacity [ton] | SPLIT GNE COOLING COIL Cooling Capacity [ton] | 0.83422 | 0.8222 | 0.66414 | 0.65208 | [6 empty] | 2021-05-06
TN_MA_SPLIT GN1 COOLING COIL Cooling Capacity [ton] | SPLIT GN1 COOLING COIL Cooling Capacity [ton] | 0.72393 | 0.71484 | 0.5647 | 0.5556 | [6 empty] | 2021-05-06
TN_MA_SPLIT GN2 COOLING COIL Cooling Capacity [ton] | SPLIT GN2 COOLING COIL Cooling Capacity [ton] | 0.7223 | 0.71321 | 0.56272 | 0.55367 | [6 empty] | 2021-05-06
TN_MA_SPLIT GS1 COOLING COIL Cooling Capacity [ton] | SPLIT GS1 COOLING COIL Cooling Capacity [ton] | 0.7368 | 0.72808 | 0.60156 | 0.59133 | [6 empty] | 2021-05-06
TN_MA_SPLIT GS2 COOLING COIL Cooling Capacity [ton] | SPLIT GS2 COOLING COIL Cooling Capacity [ton] | 0.77323 | 0.76057 | 0.63209 | 0.61667 | [6 empty] | 2021-05-06
TN_MA_SPLIT MSW COOLING COIL Cooling Capacity [ton] | SPLIT MSW COOLING COIL Cooling Capacity [ton] | 2.1222 | 2.0998 | 1.8736 | 1.8431 | [6 empty] | 2021-05-06
TN_MA_SPLIT MNW COOLING COIL Cooling Capacity [ton] | SPLIT MNW COOLING COIL Cooling Capacity [ton] | 2.0907 | 2.0686 | 1.8269 | 1.7969 | [6 empty] | 2021-05-06
TN_MA_SPLIT MSE COOLING COIL Cooling Capacity [ton] | SPLIT MSE COOLING COIL Cooling Capacity [ton] | 1.9163 | 1.8941 | 1.559 | 1.5354 | [6 empty] | 2021-05-06
TN_MA_SPLIT MNE COOLING COIL Cooling Capacity [ton] | SPLIT MNE COOLING COIL Cooling Capacity [ton] | 1.8175 | 1.7711 | 1.513 | 1.4898 | [6 empty] | 2021-05-06
TN_MA_SPLIT MN1 COOLING COIL Cooling Capacity [ton] | SPLIT MN1 COOLING COIL Cooling Capacity [ton] | 1.5261 | 1.5092 | 1.2444 | 1.2269 | [6 empty] | 2021-05-06
TN_MA_SPLIT MN2 COOLING COIL Cooling Capacity [ton] | SPLIT MN2 COOLING COIL Cooling Capacity [ton] | 1.5218 | 1.5049 | 1.2391 | 1.2217 | [6 empty] | 2021-05-06
TN_MA_SPLIT MS1 COOLING COIL Cooling Capacity [ton] | SPLIT MS1 COOLING COIL Cooling Capacity [ton] | 1.5528 | 1.5346 | 1.3114 | 1.2922 | [6 empty] | 2021-05-06
TN_MA_SPLIT MS2 COOLING COIL Cooling Capacity [ton] | SPLIT MS2 COOLING COIL Cooling Capacity [ton] | 1.5486 | 1.5304 | 1.3067 | 1.2876 | [6 empty] | 2021-05-06
TN_MA_SPLIT TSW COOLING COIL Cooling Capacity [ton] | SPLIT TSW COOLING COIL Cooling Capacity [ton] | 1.3049 | 1.2935 | 1.1754 | 1.1587 | [6 empty] | 2021-05-06
TN_MA_SPLIT TNW COOLING COIL Cooling Capacity [ton] | SPLIT TNW COOLING COIL Cooling Capacity [ton] | 1.2726 | 1.2617 | 1.1453 | 1.1291 | [6 empty] | 2021-05-06
TN_MA_SPLIT TSE COOLING COIL Cooling Capacity [ton] | SPLIT TSE COOLING COIL Cooling Capacity [ton] | 1.2022 | 1.1912 | 1.0467 | 1.0333 | [6 empty] | 2021-05-06
TN_MA_SPLIT TNE COOLING COIL Cooling Capacity [ton] | SPLIT TNE COOLING COIL Cooling Capacity [ton] | 1.1497 | 1.1392 | 0.98837 | 0.97574 | [6 empty] | 2021-05-06
TN_MA_SPLIT TN1 COOLING COIL Cooling Capacity [ton] | SPLIT TN1 COOLING COIL Cooling Capacity [ton] | 0.93344 | 0.92462 | 0.8054 | 0.79572 | [6 empty] | 2021-05-06
TN_MA_SPLIT TN2 COOLING COIL Cooling Capacity [ton] | SPLIT TN2 COOLING COIL Cooling Capacity [ton] | 0.92842 | 0.91961 | 0.79962 | 0.79009 | [6 empty] | 2021-05-06
TN_MA_SPLIT TS1 COOLING COIL Cooling Capacity [ton] | SPLIT TS1 COOLING COIL Cooling Capacity [ton] | 1.0024 | 0.99281 | 0.8755 | 0.8647 | [6 empty] | 2021-05-06
TN_MA_SPLIT TS2 COOLING COIL Cooling Capacity [ton] | SPLIT TS2 COOLING COIL Cooling Capacity [ton] | 1.0041 | 0.99454 | 0.876 | 0.86525 | [6 empty] | 2021-05-06
TN_MA_Split GN1 Furnace with DX Cooling OA Rate [cfm] | Split GN1 Furnace with DX Cooling OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | [6 empty] | 2021-05-06
TN_MA_Split GN2 Furnace with DX Cooling OA Rate [cfm] | Split GN2 Furnace with DX Cooling OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | [6 empty] | 2021-05-06
TN_MA_Split GNE Furnace with DX Cooling OA Rate [cfm] | Split GNE Furnace with DX Cooling OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | [6 empty] | 2021-05-06
TN_MA_Split GNW Furnace with DX Cooling OA Rate [cfm] | Split GNW Furnace with DX Cooling OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | [6 empty] | 2021-05-06
TN_MA_Split GS1 Furnace with DX Cooling OA Rate [cfm] | Split GS1 Furnace with DX Cooling OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | [6 empty] | 2021-05-06
TN_MA_Split GS2 Furnace with DX Cooling OA Rate [cfm] | Split GS2 Furnace with DX Cooling OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | [6 empty] | 2021-05-06
TN_MA_Split GSW Furnace with DX Cooling OA Rate [cfm] | Split GSW Furnace with DX Cooling OA Rate [cfm] | 56.9945 | 56.9945 | 56.9945 | 56.9945 | [6 empty] | 2021-05-06
TN_MA_Split MN1 Furnace with DX Cooling OA Rate [cfm] | Split MN1 Furnace with DX Cooling OA Rate [cfm] | 109.9824 | 109.9824 | 109.9824 | 109.9824 | [6 empty] | 2021-05-06
TN_MA_Split MN2 Furnace with DX Cooling OA Rate [cfm] | Split MN2 Furnace with DX Cooling OA Rate [cfm] | 109.9824 | 109.9824 | 109.9824 | 109.9824 | [6 empty] | 2021-05-06
TN_MA_Split MNE Furnace with DX Cooling OA Rate [cfm] | Split MNE Furnace with DX Cooling OA Rate [cfm] | 109.9824 | 109.9824 | 109.9824 | 109.9824 | [6 empty] | 2021-05-06
TN_MA_Split MNW Furnace with DX Cooling OA Rate [cfm] | Split MNW Furnace with DX Cooling OA Rate [cfm] | 109.9824 | 109.9824 | 109.9824 | 109.9824 | [6 empty] | 2021-05-06
TN_MA_Split MS1 Furnace with DX Cooling OA Rate [cfm] | Split MS1 Furnace with DX Cooling OA Rate [cfm] | 109.9824 | 109.9824 | 109.9824 | 109.9824 | [6 empty] | 2021-05-06
TN_MA_Split MS2 Furnace with DX Cooling OA Rate [cfm] | Split MS2 Furnace with DX Cooling OA Rate [cfm] | 109.9824 | 109.9824 | 109.9824 | 109.9824 | [6 empty] | 2021-05-06
TN_MA_Split MSE Furnace with DX Cooling OA Rate [cfm] | Split MSE Furnace with DX Cooling OA Rate [cfm] | 109.9824 | 109.9824 | 109.9824 | 109.9824 | [6 empty] | 2021-05-06
TN_MA_Split MSW Furnace with DX Cooling OA Rate [cfm] | Split MSW Furnace with DX Cooling OA Rate [cfm] | 109.9824 | 109.9824 | 109.9824 | 109.9824 | [6 empty] | 2021-05-06
TN_MA_Split Office Furnace with DX Cooling OA Rate [cfm] | Split Office Furnace with DX Cooling OA Rate [cfm] | 80.7372 | 80.7372 | 80.7372 | 80.7372 | [6 empty] | 2021-05-06
TN_MA_Split TN1 Furnace with DX Cooling OA Rate [cfm] | Split TN1 Furnace with DX Cooling OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | [6 empty] | 2021-05-06
TN_MA_Split TN2 Furnace with DX Cooling OA Rate [cfm] | Split TN2 Furnace with DX Cooling OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | [6 empty] | 2021-05-06
TN_MA_Split TNE Furnace with DX Cooling OA Rate [cfm] | Split TNE Furnace with DX Cooling OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | [6 empty] | 2021-05-06
TN_MA_Split TNW Furnace with DX Cooling OA Rate [cfm] | Split TNW Furnace with DX Cooling OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | [6 empty] | 2021-05-06
TN_MA_Split TS1 Furnace with DX Cooling OA Rate [cfm] | Split TS1 Furnace with DX Cooling OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | [6 empty] | 2021-05-06
TN_MA_Split TS2 Furnace with DX Cooling OA Rate [cfm] | Split TS2 Furnace with DX Cooling OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | [6 empty] | 2021-05-06
TN_MA_Split TSE Furnace with DX Cooling OA Rate [cfm] | Split TSE Furnace with DX Cooling OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | [6 empty] | 2021-05-06
TN_MA_Split TSW Furnace with DX Cooling OA Rate [cfm] | Split TSW Furnace with DX Cooling OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | [6 empty] | 2021-05-06
TN_MA_SPLIT GSW HEATING COIL Heating Capacity [kBtu/hr] | SPLIT GSW HEATING COIL Heating Capacity [kBtu/hr] | 7.9381 | 7.84 | 7.8466 | 7.906 | [6 empty] | 2021-05-06
TN_MA_SPLIT GNW HEATING COIL Heating Capacity [kBtu/hr] | SPLIT GNW HEATING COIL Heating Capacity [kBtu/hr] | 7.8919 | 7.7891 | 7.7577 | 7.8173 | [6 empty] | 2021-05-06
TN_MA_SPLIT OFFICE HEATING COIL Heating Capacity [kBtu/hr] | SPLIT OFFICE HEATING COIL Heating Capacity [kBtu/hr] | 19.7517 | 19.5824 | 19.6507 | 19.7819 | [6 empty] | 2021-05-06
TN_MA_SPLIT GNE HEATING COIL Heating Capacity [kBtu/hr] | SPLIT GNE HEATING COIL Heating Capacity [kBtu/hr] | 7.8919 | 7.7891 | 7.7437 | 7.8033 | [6 empty] | 2021-05-06
TN_MA_SPLIT GN1 HEATING COIL Heating Capacity [kBtu/hr] | SPLIT GN1 HEATING COIL Heating Capacity [kBtu/hr] | 5.634 | 5.5857 | 5.6622 | 5.722 | [6 empty] | 2021-05-06
TN_MA_SPLIT GN2 HEATING COIL Heating Capacity [kBtu/hr] | SPLIT GN2 HEATING COIL Heating Capacity [kBtu/hr] | 5.634 | 5.5857 | 5.6617 | 5.7215 | [6 empty] | 2021-05-06
TN_MA_SPLIT GS1 HEATING COIL Heating Capacity [kBtu/hr] | SPLIT GS1 HEATING COIL Heating Capacity [kBtu/hr] | 5.5816 | 5.5378 | 5.6457 | 5.7053 | [6 empty] | 2021-05-06
TN_MA_SPLIT GS2 HEATING COIL Heating Capacity [kBtu/hr] | SPLIT GS2 HEATING COIL Heating Capacity [kBtu/hr] | 6.0855 | 6.0366 | 6.1132 | 6.176 | [6 empty] | 2021-05-06
TN_MA_SPLIT MSW HEATING COIL Heating Capacity [kBtu/hr] | SPLIT MSW HEATING COIL Heating Capacity [kBtu/hr] | 14.7563 | 14.5626 | 13.4214 | 13.5514 | [6 empty] | 2021-05-06
TN_MA_SPLIT MNW HEATING COIL Heating Capacity [kBtu/hr] | SPLIT MNW HEATING COIL Heating Capacity [kBtu/hr] | 14.8555 | 14.6504 | 13.4316 | 13.561 | [6 empty] | 2021-05-06
TN_MA_SPLIT MSE HEATING COIL Heating Capacity [kBtu/hr] | SPLIT MSE HEATING COIL Heating Capacity [kBtu/hr] | 14.7563 | 14.5626 | 13.3876 | 13.5175 | [6 empty] | 2021-05-06
TN_MA_SPLIT MNE HEATING COIL Heating Capacity [kBtu/hr] | SPLIT MNE HEATING COIL Heating Capacity [kBtu/hr] | 14.8555 | 14.6504 | 13.3977 | 13.5272 | [6 empty] | 2021-05-06
TN_MA_SPLIT MN1 HEATING COIL Heating Capacity [kBtu/hr] | SPLIT MN1 HEATING COIL Heating Capacity [kBtu/hr] | 10.2532 | 10.2532 | 10.453 | 10.453 | [6 empty] | 2021-05-06
TN_MA_SPLIT MN2 HEATING COIL Heating Capacity [kBtu/hr] | SPLIT MN2 HEATING COIL Heating Capacity [kBtu/hr] | 10.2532 | 10.2532 | 10.453 | 10.453 | [6 empty] | 2021-05-06
TN_MA_SPLIT MS1 HEATING COIL Heating Capacity [kBtu/hr] | SPLIT MS1 HEATING COIL Heating Capacity [kBtu/hr] | 10.2532 | 10.2532 | 10.453 | 10.453 | [6 empty] | 2021-05-06
TN_MA_SPLIT MS2 HEATING COIL Heating Capacity [kBtu/hr] | SPLIT MS2 HEATING COIL Heating Capacity [kBtu/hr] | 10.2532 | 10.2532 | 10.453 | 10.453 | [6 empty] | 2021-05-06
TN_MA_SPLIT TSW HEATING COIL Heating Capacity [kBtu/hr] | SPLIT TSW HEATING COIL Heating Capacity [kBtu/hr] | 10.8525 | 10.7577 | 9.7091 | 9.7707 | [6 empty] | 2021-05-06
TN_MA_SPLIT TNW HEATING COIL Heating Capacity [kBtu/hr] | SPLIT TNW HEATING COIL Heating Capacity [kBtu/hr] | 10.9103 | 10.8097 | 9.7202 | 9.782 | [6 empty] | 2021-05-06
TN_MA_SPLIT TSE HEATING COIL Heating Capacity [kBtu/hr] | SPLIT TSE HEATING COIL Heating Capacity [kBtu/hr] | 10.8525 | 10.7577 | 9.6911 | 9.7527 | [6 empty] | 2021-05-06
TN_MA_SPLIT TNE HEATING COIL Heating Capacity [kBtu/hr] | SPLIT TNE HEATING COIL Heating Capacity [kBtu/hr] | 10.9103 | 10.8097 | 9.7022 | 9.7639 | [6 empty] | 2021-05-06
TN_MA_SPLIT TN1 HEATING COIL Heating Capacity [kBtu/hr] | SPLIT TN1 HEATING COIL Heating Capacity [kBtu/hr] | 8.2916 | 8.2481 | 7.5389 | 7.6005 | [6 empty] | 2021-05-06
TN_MA_SPLIT TN2 HEATING COIL Heating Capacity [kBtu/hr] | SPLIT TN2 HEATING COIL Heating Capacity [kBtu/hr] | 8.2916 | 8.2481 | 7.5383 | 7.6 | [6 empty] | 2021-05-06
TN_MA_SPLIT TS1 HEATING COIL Heating Capacity [kBtu/hr] | SPLIT TS1 HEATING COIL Heating Capacity [kBtu/hr] | 8.2268 | 8.189 | 7.5209 | 7.5825 | [6 empty] | 2021-05-06
TN_MA_SPLIT TS2 HEATING COIL Heating Capacity [kBtu/hr] | SPLIT TS2 HEATING COIL Heating Capacity [kBtu/hr] | 8.2268 | 8.189 | 7.5204 | 7.582 | [6 empty] | 2021-05-06
TN_MA_Split_GSW ERV Flag | Split_GSW ERV Flag | No | Yes | Yes | Yes | [6 empty] | 2021-05-06
TN_MA_Split_GNW ERV Flag | Split_GNW ERV Flag | No | Yes | Yes | Yes | [6 empty] | 2021-05-06
TN_MA_Split_GNE ERV Flag | Split_GNE ERV Flag | No | Yes | Yes | Yes | [6 empty] | 2021-05-06
TN_MA_Split_GN1 ERV Flag | Split_GN1 ERV Flag | No | Yes | Yes | Yes | [6 empty] | 2021-05-06
TN_MA_Split_GN2 ERV Flag | Split_GN2 ERV Flag | No | Yes | Yes | Yes | [6 empty] | 2021-05-06
TN_MA_Split_GS1 ERV Flag | Split_GS1 ERV Flag | No | Yes | Yes | Yes | [6 empty] | 2021-05-06
TN_MA_Split_GS2 ERV Flag | Split_GS2 ERV Flag | No | Yes | Yes | Yes | [6 empty] | 2021-05-06
TN_MA_Split_MSW ERV Flag | Split_MSW ERV Flag | No | Yes | Yes | Yes | [6 empty] | 2021-05-06
TN_MA_Split_MNW ERV Flag | Split_MNW ERV Flag | No | Yes | Yes | Yes | [6 empty] | 2021-05-06
TN_MA_Split_MSE ERV Flag | Split_MSE ERV Flag | No | Yes | Yes | Yes | [6 empty] | 2021-05-06
TN_MA_Split_MNE ERV Flag | Split_MNE ERV Flag | No | Yes | Yes | Yes | [6 empty] | 2021-05-06
TN_MA_Split_MN1 ERV Flag | Split_MN1 ERV Flag | No | Yes | Yes | Yes | [6 empty] | 2021-05-06
TN_MA_Split_MN2 ERV Flag | Split_MN2 ERV Flag | No | Yes | Yes | Yes | [6 empty] | 2021-05-06
TN_MA_Split_MS1 ERV Flag | Split_MS1 ERV Flag | No | Yes | Yes | Yes | [6 empty] | 2021-05-06
TN_MA_Split_MS2 ERV Flag | Split_MS2 ERV Flag | No | Yes | Yes | Yes | [6 empty] | 2021-05-06
TN_MA_Split_TSW ERV Flag | Split_TSW ERV Flag | No | Yes | Yes | Yes | [6 empty] | 2021-05-06
TN_MA_Split_TNW ERV Flag | Split_TNW ERV Flag | No | Yes | Yes | Yes | [6 empty] | 2021-05-06
TN_MA_Split_TSE ERV Flag | Split_TSE ERV Flag | No | Yes | Yes | Yes | [6 empty] | 2021-05-06
TN_MA_Split_TNE ERV Flag | Split_TNE ERV Flag | No | Yes | Yes | Yes | [6 empty] | 2021-05-06
TN_MA_Split_TN1 ERV Flag | Split_TN1 ERV Flag | No | Yes | Yes | Yes | [6 empty] | 2021-05-06
TN_MA_Split_TN2 ERV Flag | Split_TN2 ERV Flag | No | Yes | Yes | Yes | [6 empty] | 2021-05-06
TN_MA_Split_TS1 ERV Flag | Split_TS1 ERV Flag | No | Yes | Yes | Yes | [6 empty] | 2021-05-06
TN_MA_Split_TS2 ERV Flag | Split_TS2 ERV Flag | No | Yes | Yes | Yes | [6 empty] | 2021-05-06
id | item | Zone1A(TX-Brownsville-TX) ASHRAE901-state_STD2016 | Zone1A(TX-Brownsville-TX) ASHRAE901-state_STD2019 | Zone2A(TX-Houston-TX) ASHRAE901-state_STD2016 | Zone2A(TX-Houston-TX) ASHRAE901-state_STD2019 | Zone2B(TX-Laredo-TX) ASHRAE901-state_STD2016 | Zone2B(TX-Laredo-TX) ASHRAE901-state_STD2019 | Zone3A(TX-WichitaFalls-TX) ASHRAE901-state_STD2016 | Zone3A(TX-WichitaFalls-TX) ASHRAE901-state_STD2019 | Zone3B(TX-ElPaso-TX) ASHRAE901-state_STD2016 | Zone3B(TX-ElPaso-TX) ASHRAE901-state_STD2019 | 2021-05-06
TX_SO_PSZ-AC:1 Cooling Capacity [ton] | PSZ-AC:1 Cooling Capacity [ton] | 2.0996 | 1.9988 | 2.0698 | 1.9705 | 2.0671 | 1.9644 | 2.0208 | 1.9199 | 1.8175 | 1.7153 | 2021-05-06
TX_SO_PSZ-AC:2 Cooling Capacity [ton] | PSZ-AC:2 Cooling Capacity [ton] | 2.0025 | 1.9052 | 1.891 | 1.7925 | 2.125 | 2.0155 | 1.9004 | 1.8124 | 1.7104 | 1.632 | 2021-05-06
TX_SO_PSZ-AC:3 Cooling Capacity [ton] | PSZ-AC:3 Cooling Capacity [ton] | 1.3336 | 1.2655 | 1.2505 | 1.2028 | 1.379 | 1.3262 | 1.2438 | 1.2009 | 1.1605 | 1.1103 | 2021-05-06
TX_SO_PSZ-AC:4 Cooling Capacity [ton] | PSZ-AC:4 Cooling Capacity [ton] | 1.9806 | 1.8782 | 1.8811 | 1.7953 | 2.0788 | 1.9724 | 1.8776 | 1.7926 | 1.712 | 1.6169 | 2021-05-06
TX_SO_PSZ-AC:5 Cooling Capacity [ton] | PSZ-AC:5 Cooling Capacity [ton] | 1.5606 | 1.4843 | 1.4666 | 1.4128 | 1.6179 | 1.5593 | 1.4718 | 1.4258 | 1.4012 | 1.3478 | 2021-05-06
TX_SO_PSZ-AC:1 Supply Flow Rate [cfm] | PSZ-AC:1 Supply Flow Rate [cfm] | 678.0416 | 635.664 | 678.0416 | 635.664 | 720.4192 | 656.8528 | 720.4192 | 678.0416 | 783.9856 | 741.608 | 2021-05-06
TX_SO_PSZ-AC:2 Supply Flow Rate [cfm] | PSZ-AC:2 Supply Flow Rate [cfm] | 699.2304 | 656.8528 | 656.8528 | 614.4752 | 783.9856 | 741.608 | 699.2304 | 656.8528 | 762.7968 | 720.4192 | 2021-05-06
TX_SO_PSZ-AC:3 Supply Flow Rate [cfm] | PSZ-AC:3 Supply Flow Rate [cfm] | 508.5312 | 466.1536 | 487.3424 | 466.1536 | 550.9088 | 529.72 | 508.5312 | 487.3424 | 529.72 | 508.5312 | 2021-05-06
TX_SO_PSZ-AC:4 Supply Flow Rate [cfm] | PSZ-AC:4 Supply Flow Rate [cfm] | 678.0416 | 635.664 | 656.8528 | 614.4752 | 762.7968 | 720.4192 | 699.2304 | 656.8528 | 762.7968 | 720.4192 | 2021-05-06
TX_SO_PSZ-AC:5 Supply Flow Rate [cfm] | PSZ-AC:5 Supply Flow Rate [cfm] | 593.2864 | 572.0976 | 572.0976 | 550.9088 | 656.8528 | 635.664 | 614.4752 | 593.2864 | 635.664 | 614.4752 | 2021-05-06
TX_SO_PSZ-AC:1 OA Rate [cfm] | PSZ-AC:1 OA Rate [cfm] | 136.9178 | 136.9178 | 136.9178 | 136.9178 | 136.9178 | 136.9178 | 136.9178 | 136.9178 | 136.9178 | 136.9178 | 2021-05-06
TX_SO_PSZ-AC:2 OA Rate [cfm] | PSZ-AC:2 OA Rate [cfm] | 103.7925 | 103.7925 | 103.7925 | 103.7925 | 103.7925 | 103.7925 | 103.7925 | 103.7925 | 103.7925 | 103.7925 | 2021-05-06
TX_SO_PSZ-AC:3 OA Rate [cfm] | PSZ-AC:3 OA Rate [cfm] | 61.5711 | 61.5711 | 61.5711 | 61.5711 | 61.5711 | 61.5711 | 61.5711 | 61.5711 | 61.5711 | 61.5711 | 2021-05-06
TX_SO_PSZ-AC:4 OA Rate [cfm] | PSZ-AC:4 OA Rate [cfm] | 103.7925 | 103.7925 | 103.7925 | 103.7925 | 103.7925 | 103.7925 | 103.7925 | 103.7925 | 103.7925 | 103.7925 | 2021-05-06
TX_SO_PSZ-AC:5 OA Rate [cfm] | PSZ-AC:5 OA Rate [cfm] | 61.5711 | 61.5711 | 61.5711 | 61.5711 | 61.5711 | 61.5711 | 61.5711 | 61.5711 | 61.5711 | 61.5711 | 2021-05-06
TX_SO_PSZ-AC:1 heating Capacity [kBtu/hr] | PSZ-AC:1 heating Capacity [kBtu/hr] | 10.0254 | 10.0254 | 11.0617 | 11.0617 | 10.2321 | 10.2321 | 12.672 | 12.672 | 10.4584 | 10.4584 | 2021-05-06
TX_SO_PSZ-AC:2 heating Capacity [kBtu/hr] | PSZ-AC:2 heating Capacity [kBtu/hr] | 12.0621 | 11.7206 | 14.0963 | 13.6198 | 12.4845 | 12.0571 | 19.1726 | 18.9162 | 14.1786 | 13.9649 | 2021-05-06
TX_SO_PSZ-AC:3 heating Capacity [kBtu/hr] | PSZ-AC:3 heating Capacity [kBtu/hr] | 7.3429 | 7.1535 | 8.6203 | 8.3442 | 7.6363 | 7.3868 | 11.8582 | 11.7084 | 8.6693 | 8.5464 | 2021-05-06
TX_SO_PSZ-AC:4 heating Capacity [kBtu/hr] | PSZ-AC:4 heating Capacity [kBtu/hr] | 11.8418 | 11.5443 | 13.8581 | 13.4493 | 12.2706 | 11.9014 | 19.0053 | 18.7835 | 14.0019 | 13.8201 | 2021-05-06
TX_SO_PSZ-AC:5 heating Capacity [kBtu/hr] | PSZ-AC:5 heating Capacity [kBtu/hr] | 7.3842 | 7.1831 | 8.6203 | 8.3442 | 7.6363 | 7.3868 | 11.8582 | 11.7084 | 8.635 | 8.5167 | 2021-05-06
id | item | Zone1A(TX-Brownsville-TX) ASHRAE901-state_STD2016 | Zone1A(TX-Brownsville-TX) ASHRAE901-state_STD2019 | Zone2A(TX-Houston-TX) ASHRAE901-state_STD2016 | Zone2A(TX-Houston-TX) ASHRAE901-state_STD2019 | Zone2B(TX-Laredo-TX) ASHRAE901-state_STD2016 | Zone2B(TX-Laredo-TX) ASHRAE901-state_STD2019 | Zone3A(TX-WichitaFalls-TX) ASHRAE901-state_STD2016 | Zone3A(TX-WichitaFalls-TX) ASHRAE901-state_STD2019 | Zone3B(TX-ElPaso-TX) ASHRAE901-state_STD2016 | Zone3B(TX-ElPaso-TX) ASHRAE901-state_STD2019 | 2021-05-06
TX_LO_CAV_BAS Supply Flow Rate [cfm] | CAV_BAS Supply Flow Rate [cfm] | 12077.616 | 11230.064 | 11696.2176 | 10848.6656 | 12395.448 | 11526.7072 | 11950.4832 | 11060.5536 | 13391.3216 | 12395.448 | 2021-05-06
TX_LO_VAV_BOT WITH REHEAT Supply Flow Rate [cfm] | VAV_BOT WITH REHEAT Supply Flow Rate [cfm] | 19642.0176 | 18603.7664 | 19281.808 | 18328.312 | 19726.7728 | 18752.088 | 20065.7936 | 19091.1088 | 22036.352 | 20955.7232 | 2021-05-06
TX_LO_VAV_MID WITH REHEAT Supply Flow Rate [cfm] | VAV_MID WITH REHEAT Supply Flow Rate [cfm] | 182647.4563 | 172879.4195 | 178981.7939 | 169934.1763 | 183177.1763 | 173578.6499 | 187266.6147 | 177858.7875 | 204683.8083 | 194364.8627 | 2021-05-06
TX_LO_VAV_TOP WITH REHEAT Supply Flow Rate [cfm] | VAV_TOP WITH REHEAT Supply Flow Rate [cfm] | 20277.6816 | 19218.2416 | 18985.1648 | 18095.2352 | 20192.9264 | 19218.2416 | 20129.36 | 19281.808 | 22142.296 | 21209.9888 | 2021-05-06
TX_LO_Supply Air Temp. Reset Flag | Supply Air Temp. Reset Flag | No | Yes | No | No | Yes | Yes | No | Yes | Yes | Yes | 2021-05-06
TX_LO_CAV_BAS OA Rate [cfm] | CAV_BAS OA Rate [cfm] | 2542.8255 | 2542.8255 | 2542.8255 | 2542.8255 | 2542.8255 | 2542.8255 | 2542.8255 | 2542.8255 | 2542.8255 | 2542.8255 | 2021-05-06
TX_LO_VAV_BOT WITH REHEAT OA Rate [cfm] | VAV_BOT WITH REHEAT OA Rate [cfm] | 5377.8022 | 4302.174 | 5377.8022 | 4302.174 | 5377.8022 | 4302.174 | 5377.8022 | 4302.174 | 5377.8022 | 4302.174 | 2021-05-06
TX_LO_VAV_MID WITH REHEAT OA Rate [cfm] | VAV_MID WITH REHEAT OA Rate [cfm] | 53777.9373 | 43021.7396 | 53777.9373 | 43021.7396 | 53777.9373 | 43021.7396 | 53777.9373 | 43021.7396 | 53777.9373 | 43021.7396 | 2021-05-06
TX_LO_VAV_TOP WITH REHEAT OA Rate [cfm] | VAV_TOP WITH REHEAT OA Rate [cfm] | 5377.8022 | 4302.174 | 5377.8022 | 4302.174 | 5377.8022 | 4302.174 | 5377.8022 | 4302.174 | 5377.8022 | 4302.174 | 2021-05-06
TX_LO_AIRLOOP DATACENTER BASEMENT OA Rate [cfm] | AIRLOOP DATACENTER BASEMENT OA Rate [cfm] | 716.9654 | 716.9654 | 716.9654 | 716.9654 | 716.9654 | 716.9654 | 716.9654 | 716.9654 | 716.9654 | 716.9654 | 2021-05-06
TX_LO_VAV_bot_WITH_REHEAT ERV Flag | VAV_bot_WITH_REHEAT ERV Flag | Yes | Yes | Yes | Yes | No | No | Yes | Yes | No | No | 2021-05-06
TX_LO_VAV_mid_WITH_REHEAT ERV Flag | VAV_mid_WITH_REHEAT ERV Flag | Yes | Yes | Yes | Yes | No | No | Yes | Yes | No | No | 2021-05-06
TX_LO_VAV_top_WITH_REHEAT ERV Flag | VAV_top_WITH_REHEAT ERV Flag | Yes | Yes | Yes | Yes | No | No | Yes | Yes | No | No | 2021-05-06
TX_LO_COOLSYS1 CHILLER1 Capacity [ton] | COOLSYS1 CHILLER1 Capacity [ton] | 450.7528 | 403.4985 | 438.6997 | 392.3391 | 402.8956 | 365.1673 | 401.436 | 363.8004 | 337.4605 | 311.9875 | 2021-05-06
TX_LO_COOLSYS1 CHILLER2 Capacity [ton] | COOLSYS1 CHILLER2 Capacity [ton] | 450.7528 | 403.4985 | 438.6997 | 392.3391 | 402.8956 | 365.1673 | 401.436 | 363.8004 | 337.4605 | 311.9875 | 2021-05-06
TX_LO_TOWERWATERSYS COOLTOWER 1 Capacity [ton] | TOWERWATERSYS COOLTOWER 1 Capacity [ton] | 427.8488 | 382.9938 | 416.402 | 372.4003 | 382.4162 | 346.6057 | 381.0378 | 345.3061 | 320.5792 | 296.3791 | 2021-05-06
TX_LO_TOWERWATERSYS COOLTOWER 2 Capacity [ton] | TOWERWATERSYS COOLTOWER 2 Capacity [ton] | 427.8488 | 382.9938 | 416.402 | 372.4003 | 382.4162 | 346.6057 | 381.0378 | 345.3061 | 320.5792 | 296.3791 | 2021-05-06
TX_LO_HEATSYS1 BOILER Capacity [MMBTU/h] | HEATSYS1 BOILER Capacity [MMBTU/h] | 3517.6514 | 3203.5882 | 3350.4414 | 2949.2388 | 3066.1213 | 2704.4284 | 4107.2248 | 3660.3035 | 3331.0417 | 2973.8208 | 2021-05-06
TX_LO_COOLSYS1 PUMP Flow Rate [gal/min] | COOLSYS1 PUMP Flow Rate [gal/min] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2021-05-06
TX_LO_COOLSYS1 CHILLER1 PUMP Flow Rate [gal/min] | COOLSYS1 CHILLER1 PUMP Flow Rate [gal/min] | 707.6107 | 633.1427 | 688.6791 | 615.6044 | 631.8272 | 572.4313 | 631.9096 | 570.1948 | 527.5495 | 487.632 | 2021-05-06
TX_LO_COOLSYS1 CHILLER2 PUMP Flow Rate [gal/min] | COOLSYS1 CHILLER2 PUMP Flow Rate [gal/min] | 707.6107 | 633.1427 | 688.6791 | 615.6044 | 631.8272 | 572.4313 | 631.9096 | 570.1948 | 527.5495 | 487.632 | 2021-05-06
TX_LO_COOLSYS1 PUMP SECONDARY Flow Rate [gal/min] | COOLSYS1 PUMP SECONDARY Flow Rate [gal/min] | 1415.2215 | 1266.2855 | 1377.3598 | 1231.2087 | 1263.6543 | 1144.8625 | 1263.8176 | 1140.3895 | 1055.1005 | 975.2656 | 2021-05-06
TX_LO_HEATSYS1 PUMP Flow Rate [gal/min] | HEATSYS1 PUMP Flow Rate [gal/min] | 722.044 | 657.5792 | 687.7217 | 605.3698 | 629.3624 | 555.1195 | 843.0613 | 751.3259 | 683.7401 | 610.4165 | 2021-05-06
TX_LO_TOWERWATERSYS PUMP Flow Rate [gal/min] | TOWERWATERSYS PUMP Flow Rate [gal/min] | 2486.7572 | 2226.1779 | 2420.3443 | 2164.5201 | 2222.8493 | 2014.5761 | 2214.7657 | 2007.1264 | 1861.779 | 1721.1866 | 2021-05-06
TX_LO_PLANT CIRC PUMP Flow Rate [gal/min] | PLANT CIRC PUMP Flow Rate [gal/min] | 209.4065 | 208.4159 | 208.1607 | 207.2731 | 208.622 | 207.7486 | 209.0784 | 208.2368 | 223.442 | 222.4688 | 2021-05-06
TX_LO_COOLSYS1 PUMP SECONDARY Pressure setpoint reset [yes,no] | COOLSYS1 PUMP SECONDARY Pressure setpoint reset [yes,no] | pump_ride_on_curve | pump_ride_on_curve | pump_ride_on_curve | pump_ride_on_curve | pump_ride_on_curve | pump_ride_on_curve | pump_ride_on_curve | pump_ride_on_curve | pump_ride_on_curve | pump_ride_on_curve | 2021-05-06
TX_LO_COOLSYS1 CHILLER1 PUMP Pump Power [hp] | COOLSYS1 CHILLER1 PUMP Pump Power [hp] | 3.8173 | 3.3818 | 3.7152 | 3.2881 | 3.4085 | 3.0575 | 3.4089 | 3.0455 | 2.8459 | 2.6046 | 2021-05-06
TX_LO_COOLSYS1 CHILLER2 PUMP Pump Power [hp] | COOLSYS1 CHILLER2 PUMP Pump Power [hp] | 3.8173 | 3.3818 | 3.7152 | 3.2881 | 3.4085 | 3.0575 | 3.4089 | 3.0455 | 2.8459 | 2.6046 | 2021-05-06
TX_LO_COOLSYS1 PUMP SECONDARY Pump Power [hp] | COOLSYS1 PUMP SECONDARY Pump Power [hp] | 22.9039 | 20.2906 | 22.2911 | 19.7285 | 20.4509 | 18.3449 | 20.4536 | 18.2733 | 17.0757 | 15.6274 | 2021-05-06
TX_LO_HEATSYS1 PUMP Pump Power [hp] | HEATSYS1 PUMP Pump Power [hp] | 15.6074 | 14.0732 | 14.8655 | 12.9559 | 13.604 | 11.8804 | 18.2233 | 16.0795 | 14.7794 | 13.0639 | 2021-05-06
TX_LO_TOWERWATERSYS PUMP Pump Power [hp] | TOWERWATERSYS PUMP Pump Power [hp] | 44.5244 | 39.4621 | 43.3339 | 38.3707 | 39.7972 | 35.7133 | 39.653 | 35.5797 | 33.3337 | 30.5124 | 2021-05-06
TX_LO_PLANT CIRC PUMP Pump Power [hp] | PLANT CIRC PUMP Pump Power [hp] | 4.5187 | 4.4528 | 4.4918 | 4.4284 | 4.5018 | 4.4386 | 4.5116 | 4.449 | 4.8216 | 4.753 | 2021-05-06
TX_LO_Datacenter PLANT CIRC PUMP Pump Power [hp] | Datacenter PLANT CIRC PUMP Pump Power [hp] | 4.5187 | 4.4528 | 4.4918 | 4.4284 | 4.5018 | 4.4386 | 4.5116 | 4.449 | 4.8216 | 4.753 | 2021-05-06
TX_LO_ZN_VAV_BOXes_Max_Reheat_Water_Flow_GPM | ZN_VAV_BOXes_Max_Reheat_Water_Flow_GPM | 494.3973 | 474.1443 | 408.7152 | 380.406 | 385.1674 | 359.8015 | 474.9848 | 455.3447 | 398.3272 | 378.7423 | 2021-05-06
TX_LO_COOLSYS1 PUMP SECONDARY VSD | COOLSYS1 PUMP SECONDARY VSD | No | No | No | No | No | No | No | No | No | No | 2021-05-06
TX_LO_HEATSYS1 PUMP VSD | HEATSYS1 PUMP VSD | No | No | No | No | No | No | No | No | No | No | 2021-05-06
TX_LO_DATACENTER BASEMENT Cooling Capacity [ton] | DATACENTER BASEMENT Cooling Capacity [ton] | 122.6007 | 122.2386 | 122.1531 | 121.7964 | 122.5574 | 122.1972 | 122.8104 | 122.4496 | 131.6564 | 131.2668 | 2021-05-06
TX_LO_DATACENTER BOT Cooling Capacity [ton] | DATACENTER BOT Cooling Capacity [ton] | 2.6718 | 2.6453 | 2.6407 | 2.6141 | 2.6331 | 2.606 | 2.6338 | 2.6086 | 2.7947 | 2.7651 | 2021-05-06
TX_LO_DATACENTER MID Cooling Capacity [ton] | DATACENTER MID Cooling Capacity [ton] | 25.5182 | 25.2176 | 25.1374 | 24.8923 | 25.0689 | 24.8398 | 25.1447 | 24.9348 | 26.5498 | 26.2782 | 2021-05-06
TX_LO_DATACENTER TOP Cooling Capacity [ton] | DATACENTER TOP Cooling Capacity [ton] | 2.6042 | 2.5674 | 2.5505 | 2.5292 | 2.5602 | 2.5377 | 2.5659 | 2.5454 | 2.6748 | 2.6533 | 2021-05-06
id | item | Zone1A(TX-Brownsville-TX) ASHRAE901-state_STD2016 | Zone1A(TX-Brownsville-TX) ASHRAE901-state_STD2019 | Zone2A(TX-Houston-TX) ASHRAE901-state_STD2016 | Zone2A(TX-Houston-TX) ASHRAE901-state_STD2019 | Zone2B(TX-Laredo-TX) ASHRAE901-state_STD2016 | Zone2B(TX-Laredo-TX) ASHRAE901-state_STD2019 | Zone3A(TX-WichitaFalls-TX) ASHRAE901-state_STD2016 | Zone3A(TX-WichitaFalls-TX) ASHRAE901-state_STD2019 | Zone3B(TX-ElPaso-TX) ASHRAE901-state_STD2016 | Zone3B(TX-ElPaso-TX) ASHRAE901-state_STD2019 | 2021-05-06
TX_RS_PSZ-AC:1 Cooling Capacity [ton] | PSZ-AC:1 Cooling Capacity [ton] | 12.9267 | 12.4645 | 11.2436 | 10.8852 | 11.3202 | 10.8324 | 10.7046 | 10.2665 | 10.54 | 9.9479 | 2021-05-06
TX_RS_PSZ-AC:2 Cooling Capacity [ton] | PSZ-AC:2 Cooling Capacity [ton] | 54.3279 | 51.1289 | 51.7246 | 48.554 | 52.4156 | 50.1708 | 51.6028 | 49.2393 | 47.5025 | 45.4234 | 2021-05-06
TX_RS_PSZ-AC:3 Cooling Capacity [ton] | PSZ-AC:3 Cooling Capacity [ton] | 7.7322 | 7.5717 | 6.9365 | 6.795 | 7.2192 | 7.073 | 6.8822 | 6.7176 | 6.6546 | 6.4818 | 2021-05-06
TX_RS_PSZ-AC:4 Cooling Capacity [ton] | PSZ-AC:4 Cooling Capacity [ton] | 6.9313 | 6.7364 | 5.6952 | 5.5511 | 6.0622 | 5.8594 | 5.5921 | 5.4165 | 5.3225 | 5.1393 | 2021-05-06
TX_RS_PSZ-AC:1 Supply Flow Rate [cfm] | PSZ-AC:1 Supply Flow Rate [cfm] | 4619.1584 | 4407.2704 | 4258.9488 | 4004.6832 | 4534.4032 | 4280.1376 | 4364.8928 | 4131.816 | 4746.2912 | 4449.648 | 2021-05-06
TX_RS_PSZ-AC:2 Supply Flow Rate [cfm] | PSZ-AC:2 Supply Flow Rate [cfm] | 16294.1872 | 15340.6912 | 15531.3904 | 14577.8944 | 16082.2992 | 15086.4256 | 16082.2992 | 15065.2368 | 17332.4384 | 16357.7536 | 2021-05-06
TX_RS_PSZ-AC:3 Supply Flow Rate [cfm] | PSZ-AC:3 Supply Flow Rate [cfm] | 2712.1664 | 2627.4112 | 2330.768 | 2246.0128 | 2542.656 | 2479.0896 | 2415.5232 | 2351.9568 | 2669.7888 | 2585.0336 | 2021-05-06
TX_RS_PSZ-AC:4 Supply Flow Rate [cfm] | PSZ-AC:4 Supply Flow Rate [cfm] | 2309.5792 | 2224.824 | 1801.048 | 1716.2928 | 2034.1248 | 1949.3696 | 1864.6144 | 1801.048 | 2055.3136 | 1970.5584 | 2021-05-06
TX_RS_PSZ-AC:1 OA Rate [cfm] | PSZ-AC:1 OA Rate [cfm] | 490.669 | 490.669 | 490.669 | 490.669 | 490.669 | 490.669 | 490.669 | 490.669 | 490.669 | 490.669 | 2021-05-06
TX_RS_PSZ-AC:2 OA Rate [cfm] | PSZ-AC:2 OA Rate [cfm] | 4005.1282 | 4005.1282 | 4005.1282 | 4005.1282 | 4005.1282 | 4005.1282 | 4005.1282 | 4005.1282 | 4005.1282 | 4005.1282 | 2021-05-06
TX_RS_PSZ-AC:3 OA Rate [cfm] | PSZ-AC:3 OA Rate [cfm] | 377.3937 | 377.3937 | 377.3937 | 377.3937 | 377.3937 | 377.3937 | 377.3937 | 377.3937 | 377.3937 | 377.3937 | 2021-05-06
TX_RS_PSZ-AC:4 OA Rate [cfm] | PSZ-AC:4 OA Rate [cfm] | 377.3937 | 377.3937 | 377.3937 | 377.3937 | 377.3937 | 377.3937 | 377.3937 | 377.3937 | 377.3937 | 377.3937 | 2021-05-06
TX_RS_PSZ-AC:1 OA Damper [gravity, motorized] | PSZ-AC:1 OA Damper [gravity, motorized] | gravity | gravity | motorized | motorized | motorized | motorized | motorized | motorized | motorized | motorized | 2021-05-06
TX_RS_PSZ-AC:2 OA Damper [gravity, motorized] | PSZ-AC:2 OA Damper [gravity, motorized] | gravity | gravity | motorized | motorized | motorized | motorized | motorized | motorized | motorized | motorized | 2021-05-06
TX_RS_PSZ-AC:3 OA Damper [gravity, motorized] | PSZ-AC:3 OA Damper [gravity, motorized] | gravity | gravity | motorized | motorized | motorized | motorized | motorized | motorized | motorized | motorized | 2021-05-06
TX_RS_PSZ-AC:4 OA Damper [gravity, motorized] | PSZ-AC:4 OA Damper [gravity, motorized] | gravity | gravity | motorized | motorized | motorized | motorized | motorized | motorized | motorized | motorized | 2021-05-06
TX_RS_PSZ-AC:1 Heating Capacity [kBtu/hr] | PSZ-AC:1 Heating Capacity [kBtu/hr] | 183.8121 | 181.6508 | 178.4428 | 168.5471 | 185.1214 | 175.3941 | 184.477 | 174.6212 | 174.7242 | 164.9075 | 2021-05-06
TX_RS_PSZ-AC:2 Heating Capacity [kBtu/hr] | PSZ-AC:2 Heating Capacity [kBtu/hr] | 734.7269 | 697.0172 | 737.4334 | 697.7724 | 729.4366 | 691.93 | 789.0484 | 750.7624 | 725.1638 | 691.081 | 2021-05-06
TX_RS_PSZ-AC:3 Heating Capacity [kBtu/hr] | PSZ-AC:3 Heating Capacity [kBtu/hr] | 113.9985 | 111.2346 | 102.6102 | 100.0888 | 107.1967 | 104.6376 | 108.1028 | 105.4575 | 102.3667 | 99.7647 | 2021-05-06
TX_RS_PSZ-AC:4 Heating Capacity [kBtu/hr] | PSZ-AC:4 Heating Capacity [kBtu/hr] | 99.2986 | 96.4013 | 82.8035 | 80.1206 | 87.5118 | 84.7957 | 88.3451 | 85.613 | 82.7921 | 80.0906 | 2021-05-06
id | item | Zone1A(TX-Brownsville-TX) ASHRAE901-state_STD2016 | Zone1A(TX-Brownsville-TX) ASHRAE901-state_STD2019 | Zone2A(TX-Houston-TX) ASHRAE901-state_STD2016 | Zone2A(TX-Houston-TX) ASHRAE901-state_STD2019 | Zone2B(TX-Laredo-TX) ASHRAE901-state_STD2016 | Zone2B(TX-Laredo-TX) ASHRAE901-state_STD2019 | Zone3A(TX-WichitaFalls-TX) ASHRAE901-state_STD2016 | Zone3A(TX-WichitaFalls-TX) ASHRAE901-state_STD2019 | Zone3B(TX-ElPaso-TX) ASHRAE901-state_STD2016 | Zone3B(TX-ElPaso-TX) ASHRAE901-state_STD2019 | 2021-05-06
TX_PS_VAV_POD_1 Cooling Capacity [ton] | VAV_POD_1 Cooling Capacity [ton] | 21.1677 | 19.6768 | 19.3581 | 18.4027 | 21.9984 | 20.5941 | 20.7296 | 19.3526 | 22.3782 | 21.113 | 2021-05-06
TX_PS_VAV_POD_2 Cooling Capacity [ton] | VAV_POD_2 Cooling Capacity [ton] | 21.269 | 19.669 | 19.4488 | 18.3797 | 22.0305 | 20.5133 | 20.8015 | 19.3594 | 22.3014 | 20.8323 | 2021-05-06
TX_PS_VAV_POD_3 Cooling Capacity [ton] | VAV_POD_3 Cooling Capacity [ton] | 19.3426 | 17.8933 | 17.604 | 16.5093 | 20.0525 | 18.6659 | 18.8871 | 17.5782 | 20.4519 | 19.1912 | 2021-05-06
TX_PS_VAV_OTHER Cooling Capacity [ton] | VAV_OTHER Cooling Capacity [ton] | 29.0021 | 26.9823 | 26.8527 | 25.1488 | 29.5708 | 27.6798 | 28.623 | 26.8198 | 26.2848 | 23.8215 | 2021-05-06
TX_PS_PSZ-AC_1:6 Cooling Capacity [ton] | PSZ-AC_1:6 Cooling Capacity [ton] | 8.5416 | 8.1329 | 8.4212 | 8.0408 | 8.6667 | 8.2776 | 8.6382 | 8.3494 | 8.4035 | 8.104 | 2021-05-06
TX_PS_PSZ-AC_2:5 Cooling Capacity [ton] | PSZ-AC_2:5 Cooling Capacity [ton] | 5.7667 | 5.495 | 5.3972 | 5.2113 | 5.7536 | 5.5698 | 5.657 | 5.4662 | 5.8864 | 5.8327 | 2021-05-06
TX_PS_PSZ-AC_2:7 Cooling Capacity [ton] | PSZ-AC_2:7 Cooling Capacity [ton] | 10.5074 | 10.5074 | 10.5074 | 10.5074 | 10.5074 | 10.5074 | 10.5074 | 10.5074 | 10.5074 | 10.5074 | 2021-05-06
TX_PS_VAV_POD_1 Supply Flow Rate [cfm] | VAV_POD_1 Supply Flow Rate [cfm] | 6356.64 | 5911.6752 | 5805.7312 | 5530.2768 | 6610.9056 | 6187.1296 | 6229.5072 | 5805.7312 | 6716.8496 | 6335.4512 | 2021-05-06
TX_PS_VAV_POD_2 Supply Flow Rate [cfm] | VAV_POD_2 Supply Flow Rate [cfm] | 6377.8288 | 5911.6752 | 5826.92 | 5509.088 | 6610.9056 | 6165.9408 | 6250.696 | 5805.7312 | 6695.6608 | 6250.696 | 2021-05-06
TX_PS_VAV_POD_3 Supply Flow Rate [cfm] | VAV_POD_3 Supply Flow Rate [cfm] | 5805.7312 | 5360.7664 | 5276.0112 | 4958.1792 | 6017.6192 | 5593.8432 | 5657.4096 | 5276.0112 | 6144.752 | 5763.3536 | 2021-05-06
TX_PS_VAV_OTHER Supply Flow Rate [cfm] | VAV_OTHER Supply Flow Rate [cfm] | 8708.5968 | 8094.1216 | 8051.744 | 7543.2128 | 8878.1072 | 8306.0096 | 8581.464 | 8051.744 | 9280.6944 | 8729.7856 | 2021-05-06
TX_PS_PSZ-AC_2:5 Supply Flow Rate [cfm] | PSZ-AC_2:5 Supply Flow Rate [cfm] | 1737.4816 | 1652.7264 | 1610.3488 | 1567.9712 | 1716.2928 | 1673.9152 | 1695.104 | 1631.5376 | 1801.048 | 1779.8592 | 2021-05-06
TX_PS_PSZ-AC_1:6 Supply Flow Rate [cfm] | PSZ-AC_1:6 Supply Flow Rate [cfm] | 2563.8448 | 2436.712 | 2521.4672 | 2415.5232 | 2606.2224 | 2479.0896 | 2627.4112 | 2500.2784 | 2881.6768 | 2754.544 | 2021-05-06
TX_PS_PSZ-AC_2:7 Supply Flow Rate [cfm] | PSZ-AC_2:7 Supply Flow Rate [cfm] | 3157.1312 | 3157.1312 | 3157.1312 | 3157.1312 | 3157.1312 | 3157.1312 | 3157.1312 | 3157.1312 | 3157.1312 | 3157.1312 | 2021-05-06
TX_PS_Supply Air Temp. Reset Flag | Supply Air Temp. Reset Flag | No | No | No | No | Yes | Yes | No | No | Yes | Yes | 2021-05-06
TX_PS_VAV_POD_1 OA Rate [cfm] | VAV_POD_1 OA Rate [cfm] | 6352.0844 | 5904.6617 | 5807.6806 | 5522.3522 | 6601.3495 | 6179.9466 | 6217.9381 | 5807.4051 | 6715.324 | 6282.2673 | 2021-05-06
TX_PS_VAV_POD_2 OA Rate [cfm] | VAV_POD_2 OA Rate [cfm] | 6382.3632 | 5902.3309 | 5833.8699 | 5515.4446 | 6609.825 | 6155.7278 | 6242.1781 | 5809.4392 | 6689.2618 | 6251.4376 | 2021-05-06
TX_PS_VAV_POD_3 OA Rate [cfm] | VAV_POD_3 OA Rate [cfm] | 5803.3157 | 5369.475 | 5281.3296 | 4954.1745 | 6017.4073 | 5422.002 | 5665.313 | 5274.9306 | 6137.2936 | 5422.002 | 2021-05-06
TX_PS_VAV_OTHER OA Rate [cfm] | VAV_OTHER OA Rate [cfm] | 3736.1787 | 2988.8921 | 3736.1787 | 2988.8921 | 3736.1787 | 2988.8921 | 3736.1787 | 2988.8921 | 3736.1787 | 2988.8921 | 2021-05-06
TX_PS_PSZ-AC_2:5 OA Rate [cfm] | PSZ-AC_2:5 OA Rate [cfm] | 1152.7343 | 1152.7343 | 1152.7343 | 1152.7343 | 1152.7343 | 1152.7343 | 1152.7343 | 1152.7343 | 1152.7343 | 1152.7343 | 2021-05-06
TX_PS_PSZ-AC_1:6 OA Rate [cfm] | PSZ-AC_1:6 OA Rate [cfm] | 539.9118 | 539.9118 | 539.9118 | 539.9118 | 539.9118 | 539.9118 | 539.9118 | 539.9118 | 539.9118 | 539.9118 | 2021-05-06
TX_PS_PSZ-AC_2:7 OA Rate [cfm] | PSZ-AC_2:7 OA Rate [cfm] | 3153.0841 | 3153.0841 | 3153.0841 | 3153.0841 | 3153.0841 | 3153.0841 | 3153.0841 | 3153.0841 | 3153.0841 | 3153.0841 | 2021-05-06
TX_PS_VAV_POD_1 OA Damper [gravity, motorized] | VAV_POD_1 OA Damper [gravity, motorized] | gravity | gravity | motorized | motorized | motorized | motorized | motorized | motorized | motorized | motorized | 2021-05-06
TX_PS_VAV_POD_2 OA Damper [gravity, motorized] | VAV_POD_2 OA Damper [gravity, motorized] | gravity | gravity | motorized | motorized | motorized | motorized | motorized | motorized | motorized | motorized | 2021-05-06
TX_PS_VAV_POD_3 OA Damper [gravity, motorized] | VAV_POD_3 OA Damper [gravity, motorized] | gravity | gravity | motorized | motorized | motorized | motorized | motorized | motorized | motorized | motorized | 2021-05-06
TX_PS_VAV_OTHER OA Damper [gravity, motorized] | VAV_OTHER OA Damper [gravity, motorized] | gravity | gravity | motorized | motorized | motorized | motorized | motorized | motorized | motorized | motorized | 2021-05-06
TX_PS_PSZ-AC_2:5 OA Damper [gravity, motorized] | PSZ-AC_2:5 OA Damper [gravity, motorized] | gravity | gravity | motorized | motorized | motorized | motorized | motorized | motorized | motorized | motorized | 2021-05-06
TX_PS_PSZ-AC_1:6 OA Damper [gravity, motorized] | PSZ-AC_1:6 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | motorized | motorized | motorized | motorized | motorized | motorized | 2021-05-06
TX_PS_PSZ-AC_2:7 OA Damper [gravity, motorized] | PSZ-AC_2:7 OA Damper [gravity, motorized] | gravity | gravity | motorized | motorized | motorized | motorized | motorized | motorized | motorized | motorized | 2021-05-06
TX_PS_VAV_POD_1 (economizer) | VAV_POD_1 (economizer) | No | No | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialDryBulb | DifferentialDryBulb | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialDryBulb | DifferentialDryBulb | 2021-05-06
TX_PS_VAV_POD_2 (economizer) | VAV_POD_2 (economizer) | No | No | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialDryBulb | DifferentialDryBulb | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialDryBulb | DifferentialDryBulb | 2021-05-06
TX_PS_VAV_POD_3 (economizer) | VAV_POD_3 (economizer) | No | No | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialDryBulb | DifferentialDryBulb | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialDryBulb | DifferentialDryBulb | 2021-05-06
TX_PS_VAV_OTHER (economizer) | VAV_OTHER (economizer) | No | No | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialDryBulb | DifferentialDryBulb | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialDryBulb | DifferentialDryBulb | 2021-05-06
TX_PS_PSZ-AC_2:5 (economizer) | PSZ-AC_2:5 (economizer) | No | No | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialDryBulb | DifferentialDryBulb | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialDryBulb | DifferentialDryBulb | 2021-05-06
TX_PS_PSZ-AC_1:6 (economizer) | PSZ-AC_1:6 (economizer) | No | No | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialDryBulb | DifferentialDryBulb | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialDryBulb | DifferentialDryBulb | 2021-05-06
TX_PS_PSZ-AC_2:7 (economizer) | PSZ-AC_2:7 (economizer) | No | No | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialDryBulb | DifferentialDryBulb | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialDryBulb | DifferentialDryBulb | 2021-05-06
TX_PS_VAV_Pod_1_ERV Flag | VAV_Pod_1_ERV Flag | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | No | 2021-05-06
TX_PS_VAV_Pod_2_ERV Flag | VAV_Pod_2_ERV Flag | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | No | 2021-05-06
TX_PS_VAV_Pod_3_ERV Flag | VAV_Pod_3_ERV Flag | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | No | 2021-05-06
TX_PS_VAV_OTHER_ERV Flag | VAV_OTHER_ERV Flag | Yes | Yes | Yes | Yes | No | No | Yes | Yes | No | No | 2021-05-06
TX_PS_PSZ_AC_2_5_ERV Flag | PSZ_AC_2_5_ERV Flag | No | No | Yes | Yes | No | No | No | Yes | No | No | 2021-05-06
TX_PS_PSZ_AC_2_7_ERV Flag | PSZ_AC_2_7_ERV Flag | Yes | Yes | Yes | Yes | No | No | Yes | Yes | No | No | 2021-05-06
TX_PS_HEATSYS1 Capacity [MMBTU/h] | HEATSYS1 Capacity [MMBTU/h] | 0.84437 | 0.77594 | 0.80637 | 0.74443 | 0.78617 | 0.7104 | 1.0486 | 0.98625 | 0.86641 | 0.80192 | 2021-05-06
TX_PS_HEATSYS1 Flow Rate [gal/min] | HEATSYS1 Flow Rate [gal/min] | 86.6586 | 79.6358 | 82.7595 | 76.4025 | 80.6856 | 72.9099 | 107.615 | 101.2208 | 88.9206 | 82.3025 | 2021-05-06
TX_PS_VAV_POD_1 Fan Power [hp] | VAV_POD_1 Fan Power [hp] | 9.3712 | 8.7112 | 8.5701 | 8.1471 | 9.739 | 9.1173 | 9.1773 | 8.5677 | 9.9071 | 9.347 | 2021-05-06
TX_PS_VAV_POD_2 Fan Power [hp] | VAV_POD_2 Fan Power [hp] | 9.4161 | 8.7077 | 8.6103 | 8.1369 | 9.7532 | 9.0815 | 9.2091 | 8.5707 | 9.8731 | 9.2227 | 2021-05-06
TX_PS_VAV_POD_3 Fan Power [hp] | VAV_POD_3 Fan Power [hp] | 8.5632 | 7.9216 | 7.7935 | 7.3089 | 8.8775 | 8.2636 | 8.3616 | 7.7821 | 9.0543 | 8.4962 | 2021-05-06
TX_PS_VAV_OTHER Fan Power [hp] | VAV_OTHER Fan Power [hp] | 12.0573 | 11.2176 | 11.798 | 11.0494 | 12.9922 | 11.5076 | 12.5758 | 11.7835 | 13.5794 | 12.7893 | 2021-05-06
TX_PS_HEATSYS1 Pump Power [hp] | HEATSYS1 Pump Power [hp] | 1.8732 | 1.7043 | 1.7889 | 1.6351 | 1.7441 | 1.5604 | 2.3262 | 2.1663 | 1.9221 | 1.7614 | 2021-05-06
TX_PS_PSZ-AC_1:6 Heating Capacity [kBtu/hr] | PSZ-AC_1:6 Heating Capacity [kBtu/hr] | 197.1388 | 187.5853 | 197.9896 | 189.1212 | 198.3056 | 189.3574 | 206.526 | 197.7534 | 199.9817 | 191.3792 | 2021-05-06
TX_PS_PSZ-AC_2:5 Heating Capacity [kBtu/hr] | PSZ-AC_2:5 Heating Capacity [kBtu/hr] | 105.784 | 102.7667 | 110.359 | 108.3 | 107.0383 | 105.0296 | 126.1228 | 124.0799 | 108.6488 | 107.9309 | 2021-05-06
TX_PS_PSZ-AC_2:7 Heating Capacity [kBtu/hr] | PSZ-AC_2:7 Heating Capacity [kBtu/hr] | 230.876 | 230.876 | 254.7413 | 254.7413 | 235.6357 | 235.6357 | 291.8242 | 291.8242 | 240.8457 | 240.8457 | 2021-05-06
TX_PS_ZN_VAV_BOXes_Max_Reheat_Water_Flow_GPM | ZN_VAV_BOXes_Max_Reheat_Water_Flow_GPM | 69.6711 | 63.8759 | 61.245 | 56.1341 | 61.1203 | 54.6398 | 73.4826 | 69.3621 | 61.9291 | 56.9392 | 2021-05-06
id | item | Zone1A(TX-Brownsville-TX) ASHRAE901-state_STD2016 | Zone1A(TX-Brownsville-TX) ASHRAE901-state_STD2019 | Zone2A(TX-Houston-TX) ASHRAE901-state_STD2016 | Zone2A(TX-Houston-TX) ASHRAE901-state_STD2019 | Zone2B(TX-Laredo-TX) ASHRAE901-state_STD2016 | Zone2B(TX-Laredo-TX) ASHRAE901-state_STD2019 | Zone3A(TX-WichitaFalls-TX) ASHRAE901-state_STD2016 | Zone3A(TX-WichitaFalls-TX) ASHRAE901-state_STD2019 | Zone3B(TX-ElPaso-TX) ASHRAE901-state_STD2016 | Zone3B(TX-ElPaso-TX) ASHRAE901-state_STD2019 | 2021-05-06
TX_SH_SAC_FRONTOFFICE Cooling Capacity [ton] | SAC_FRONTOFFICE Cooling Capacity [ton] | 2.8679 | 2.7238 | 2.5815 | 2.4378 | 2.8454 | 2.702 | 2.6823 | 2.5359 | 2.3837 | 2.2284 | 2021-05-06
TX_SH_SAC_FRONTLOUNGE Cooling Capacity [ton] | SAC_FRONTLOUNGE Cooling Capacity [ton] | 6.5833 | 6.2514 | 6.2574 | 5.9393 | 6.8248 | 6.4841 | 6.6375 | 6.3163 | 6.1369 | 5.8867 | 2021-05-06
TX_SH_SAC_MEETINGROOM Cooling Capacity [ton] | SAC_MEETINGROOM Cooling Capacity [ton] | 3.0954 | 3.0092 | 2.9888 | 2.8765 | 3.2038 | 3.1085 | 3.1493 | 3.058 | 3.1726 | 3.0952 | 2021-05-06
TX_SH_SAC_EXC_EMPLGE_RESTRM Cooling Capacity [ton] | SAC_EXC_EMPLGE_RESTRM Cooling Capacity [ton] | 6.3275 | 6.2841 | 6.2449 | 6.2099 | 6.4919 | 6.4536 | 6.4003 | 6.3453 | 6.1613 | 6.116 | 2021-05-06
TX_SH_SAC_FO_ADDAQ SUPPLY FAN Supply Flow Rate [cfm] | SAC_FO_ADDAQ SUPPLY FAN Supply Flow Rate [cfm] | 911.1184 | 847.552 | 826.3632 | 762.7968 | 932.3072 | 868.7408 | 889.9296 | 826.3632 | 953.496 | 868.7408 | 2021-05-06
TX_SH_SAC_FL_ADDAQ SUPPLY FAN Supply Flow Rate [cfm] | SAC_FL_ADDAQ SUPPLY FAN Supply Flow Rate [cfm] | 1970.5584 | 1885.8032 | 1885.8032 | 1779.8592 | 2055.3136 | 1949.3696 | 1991.7472 | 1885.8032 | 2161.2576 | 2055.3136 | 2021-05-06
TX_SH_SAC_MR_ADDAQ SUPPLY FAN Supply Flow Rate [cfm] | SAC_MR_ADDAQ SUPPLY FAN Supply Flow Rate [cfm] | 932.3072 | 911.1184 | 889.9296 | 868.7408 | 953.496 | 932.3072 | 953.496 | 911.1184 | 1017.0624 | 995.8736 | 2021-05-06
TX_SH_SAC_EXC_ADDAQ SUPPLY FAN Supply Flow Rate [cfm] | SAC_EXC_ADDAQ SUPPLY FAN Supply Flow Rate [cfm] | 2161.2576 | 2161.2576 | 2161.2576 | 2161.2576 | 2267.2016 | 2246.0128 | 2267.2016 | 2246.0128 | 2521.4672 | 2500.2784 | 2021-05-06
TX_SH_SAC_Exc_EmpLge_RestRm OA Rate [cfm] | SAC_Exc_EmpLge_RestRm OA Rate [cfm] | 199.9928 | 199.9928 | 199.9928 | 199.9928 | 199.9928 | 199.9928 | 199.9928 | 199.9928 | 199.9928 | 199.9928 | 2021-05-06
TX_SH_SAC_FrontLounge OA Rate [cfm] | SAC_FrontLounge OA Rate [cfm] | 500.0133 | 500.0133 | 500.0133 | 500.0133 | 500.0133 | 500.0133 | 500.0133 | 500.0133 | 500.0133 | 500.0133 | 2021-05-06
TX_SH_SAC_FrontOffice OA Rate [cfm] | SAC_FrontOffice OA Rate [cfm] | 119.2938 | 119.2938 | 119.2938 | 119.2938 | 119.2938 | 119.2938 | 119.2938 | 119.2938 | 119.2938 | 119.2938 | 2021-05-06
TX_SH_SAC_MeetingRoom OA Rate [cfm] | SAC_MeetingRoom OA Rate [cfm] | 267.7629 | 267.7629 | 267.7629 | 267.7629 | 267.7629 | 267.7629 | 267.7629 | 267.7629 | 267.7629 | 267.7629 | 2021-05-06
TX_SH_SAC_FrontLounge OA Damper [gravity, motorized] | SAC_FrontLounge OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | motorized | motorized | motorized | motorized | motorized | motorized | 2021-05-06
TX_SH_SAC_FrontOffice (economizer) | SAC_FrontOffice (economizer) | No | No | No | No | No | No | No | No | No | No | 2021-05-06
TX_SH_SAC_FrontLounge (economizer) | SAC_FrontLounge (economizer) | No | No | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialDryBulb | DifferentialDryBulb | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialDryBulb | DifferentialDryBulb | 2021-05-06
TX_SH_SAC_MeetingRoom (economizer) | SAC_MeetingRoom (economizer) | No | No | No | No | No | No | No | No | No | No | 2021-05-06
TX_SH_SAC_Exc_EmpLge_RestRm (economizer) | SAC_Exc_EmpLge_RestRm (economizer) | No | No | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialDryBulb | DifferentialDryBulb | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialDryBulb | DifferentialDryBulb | 2021-05-06
TX_SH_SAC_FRONTOFFICE Heating Capacity [kBtu/hr] | SAC_FRONTOFFICE Heating Capacity [kBtu/hr] | 37.7232 | 35.5221 | 35.4115 | 33.2225 | 38.5199 | 36.4028 | 38.3182 | 36.1817 | 35.4366 | 33.1977 | 2021-05-06
TX_SH_SAC_FRONTLOUNGE Heating Capacity [kBtu/hr] | SAC_FRONTLOUNGE Heating Capacity [kBtu/hr] | 90.8885 | 87.2249 | 90.9374 | 87.4362 | 93.3964 | 89.696 | 99.1778 | 95.7589 | 91.5452 | 88.1069 | 2021-05-06
TX_SH_SAC_MEETINGROOM Heating Capacity [kBtu/hr] | SAC_MEETINGROOM Heating Capacity [kBtu/hr] | 43.9251 | 42.9726 | 44.7112 | 43.4758 | 45.1168 | 44.0819 | 48.7983 | 47.8277 | 44.6253 | 43.6213 | 2021-05-06
TX_SH_SAC_EXC_EMPLGE_RESTRM Heating Capacity [kBtu/hr] | SAC_EXC_EMPLGE_RESTRM Heating Capacity [kBtu/hr] | 87.1728 | 86.4954 | 88.4239 | 87.8771 | 89.452 | 88.8808 | 91.6897 | 91.0326 | 89.096 | 88.4379 | 2021-05-06
id | item | Zone1A(TX-Brownsville-TX) ASHRAE901-state_STD2016 | Zone1A(TX-Brownsville-TX) ASHRAE901-state_STD2019 | Zone2A(TX-Houston-TX) ASHRAE901-state_STD2016 | Zone2A(TX-Houston-TX) ASHRAE901-state_STD2019 | Zone2B(TX-Laredo-TX) ASHRAE901-state_STD2016 | Zone2B(TX-Laredo-TX) ASHRAE901-state_STD2019 | Zone3A(TX-WichitaFalls-TX) ASHRAE901-state_STD2016 | Zone3A(TX-WichitaFalls-TX) ASHRAE901-state_STD2019 | Zone3B(TX-ElPaso-TX) ASHRAE901-state_STD2016 | Zone3B(TX-ElPaso-TX) ASHRAE901-state_STD2019 | 2021-05-06
TX_MA_SPLIT GSW COOLING COIL Cooling Capacity [ton] | SPLIT GSW COOLING COIL Cooling Capacity [ton] | 1.1977 | 1.1735 | 0.94789 | 0.93607 | 1.1178 | 1.104 | 0.98075 | 0.96834 | 0.83916 | 0.82611 | 2021-05-06
TX_MA_SPLIT GNW COOLING COIL Cooling Capacity [ton] | SPLIT GNW COOLING COIL Cooling Capacity [ton] | 1.1558 | 1.133 | 0.94063 | 0.92573 | 1.0812 | 1.0678 | 0.95409 | 0.94203 | 0.83255 | 0.81939 | 2021-05-06
TX_MA_SPLIT OFFICE COOLING COIL Cooling Capacity [ton] | SPLIT OFFICE COOLING COIL Cooling Capacity [ton] | 1.9853 | 1.89 | 1.7649 | 1.696 | 1.9068 | 1.813 | 1.746 | 1.693 | 1.8179 | 1.7193 | 2021-05-06
TX_MA_SPLIT GNE COOLING COIL Cooling Capacity [ton] | SPLIT GNE COOLING COIL Cooling Capacity [ton] | 1.0135 | 0.99509 | 0.83469 | 0.82371 | 0.96931 | 0.95709 | 0.8398 | 0.82878 | 0.73919 | 0.72695 | 2021-05-06
TX_MA_SPLIT GN1 COOLING COIL Cooling Capacity [ton] | SPLIT GN1 COOLING COIL Cooling Capacity [ton] | 0.82844 | 0.81577 | 0.72397 | 0.7153 | 0.78913 | 0.77909 | 0.70271 | 0.69326 | 0.61634 | 0.60559 | 2021-05-06
TX_MA_SPLIT GN2 COOLING COIL Cooling Capacity [ton] | SPLIT GN2 COOLING COIL Cooling Capacity [ton] | 0.82613 | 0.81359 | 0.72221 | 0.71356 | 0.78722 | 0.77718 | 0.70079 | 0.69135 | 0.61461 | 0.60388 | 2021-05-06
TX_MA_SPLIT GS1 COOLING COIL Cooling Capacity [ton] | SPLIT GS1 COOLING COIL Cooling Capacity [ton] | 0.87269 | 0.85844 | 0.72354 | 0.71401 | 0.82648 | 0.8155 | 0.72528 | 0.71546 | 0.62193 | 0.61061 | 2021-05-06
TX_MA_SPLIT GS2 COOLING COIL Cooling Capacity [ton] | SPLIT GS2 COOLING COIL Cooling Capacity [ton] | 0.90982 | 0.89277 | 0.75895 | 0.74844 | 0.86397 | 0.85006 | 0.75923 | 0.74589 | 0.66931 | 0.65389 | 2021-05-06
TX_MA_SPLIT MSW COOLING COIL Cooling Capacity [ton] | SPLIT MSW COOLING COIL Cooling Capacity [ton] | 2.5548 | 2.4891 | 2.0677 | 2.0424 | 2.2822 | 2.2513 | 2.1937 | 2.1678 | 1.8803 | 1.8525 | 2021-05-06
TX_MA_SPLIT MNW COOLING COIL Cooling Capacity [ton] | SPLIT MNW COOLING COIL Cooling Capacity [ton] | 2.4673 | 2.411 | 2.0701 | 2.045 | 2.2069 | 2.1774 | 2.1626 | 2.1373 | 1.8573 | 1.8301 | 2021-05-06
TX_MA_SPLIT MSE COOLING COIL Cooling Capacity [ton] | SPLIT MSE COOLING COIL Cooling Capacity [ton] | 2.2701 | 2.2165 | 1.7834 | 1.7606 | 2.0832 | 2.0514 | 1.8767 | 1.8531 | 1.6654 | 1.6416 | 2021-05-06
TX_MA_SPLIT MNE COOLING COIL Cooling Capacity [ton] | SPLIT MNE COOLING COIL Cooling Capacity [ton] | 2.0929 | 2.0445 | 1.7793 | 1.7568 | 1.8943 | 1.8676 | 1.8454 | 1.8223 | 1.5909 | 1.5663 | 2021-05-06
TX_MA_SPLIT MN1 COOLING COIL Cooling Capacity [ton] | SPLIT MN1 COOLING COIL Cooling Capacity [ton] | 1.6756 | 1.6484 | 1.4878 | 1.4696 | 1.532 | 1.5103 | 1.4707 | 1.4517 | 1.2765 | 1.2551 | 2021-05-06
TX_MA_SPLIT MN2 COOLING COIL Cooling Capacity [ton] | SPLIT MN2 COOLING COIL Cooling Capacity [ton] | 1.6754 | 1.6434 | 1.4834 | 1.4652 | 1.5276 | 1.506 | 1.4658 | 1.4468 | 1.2721 | 1.2508 | 2021-05-06
TX_MA_SPLIT MS1 COOLING COIL Cooling Capacity [ton] | SPLIT MS1 COOLING COIL Cooling Capacity [ton] | 1.7542 | 1.7238 | 1.4962 | 1.4768 | 1.5989 | 1.5762 | 1.5291 | 1.509 | 1.2842 | 1.2629 | 2021-05-06
TX_MA_SPLIT MS2 COOLING COIL Cooling Capacity [ton] | SPLIT MS2 COOLING COIL Cooling Capacity [ton] | 1.749 | 1.719 | 1.4921 | 1.4727 | 1.5945 | 1.5719 | 1.525 | 1.505 | 1.2799 | 1.2586 | 2021-05-06
TX_MA_SPLIT TSW COOLING COIL Cooling Capacity [ton] | SPLIT TSW COOLING COIL Cooling Capacity [ton] | 1.5415 | 1.5072 | 1.2737 | 1.2608 | 1.4233 | 1.4074 | 1.3687 | 1.3557 | 1.2155 | 1.2011 | 2021-05-06
TX_MA_SPLIT TNW COOLING COIL Cooling Capacity [ton] | SPLIT TNW COOLING COIL Cooling Capacity [ton] | 1.4943 | 1.4616 | 1.263 | 1.2505 | 1.3815 | 1.3662 | 1.3425 | 1.33 | 1.1935 | 1.1792 | 2021-05-06
TX_MA_SPLIT TSE COOLING COIL Cooling Capacity [ton] | SPLIT TSE COOLING COIL Cooling Capacity [ton] | 1.3985 | 1.3703 | 1.1532 | 1.141 | 1.3242 | 1.3081 | 1.2674 | 1.2541 | 1.0822 | 1.0701 | 2021-05-06
TX_MA_SPLIT TNE COOLING COIL Cooling Capacity [ton] | SPLIT TNE COOLING COIL Cooling Capacity [ton] | 1.3207 | 1.2964 | 1.1312 | 1.1191 | 1.2544 | 1.2394 | 1.2235 | 1.2106 | 1.0451 | 1.033 | 2021-05-06
TX_MA_SPLIT TN1 COOLING COIL Cooling Capacity [ton] | SPLIT TN1 COOLING COIL Cooling Capacity [ton] | 1.0253 | 1.0075 | 0.92551 | 0.91595 | 0.97456 | 0.96091 | 0.95692 | 0.94729 | 0.83166 | 0.82089 | 2021-05-06
TX_MA_SPLIT TN2 COOLING COIL Cooling Capacity [ton] | SPLIT TN2 COOLING COIL Cooling Capacity [ton] | 1.0464 | 1.0283 | 0.92059 | 0.91105 | 1.0071 | 0.99509 | 0.95189 | 0.94228 | 0.85134 | 0.84093 | 2021-05-06
TX_MA_SPLIT TS1 COOLING COIL Cooling Capacity [ton] | SPLIT TS1 COOLING COIL Cooling Capacity [ton] | 1.1186 | 1.1 | 0.95894 | 0.94874 | 1.0766 | 1.0635 | 1.0269 | 1.016 | 0.88811 | 0.87774 | 2021-05-06
TX_MA_SPLIT TS2 COOLING COIL Cooling Capacity [ton] | SPLIT TS2 COOLING COIL Cooling Capacity [ton] | 1.1231 | 1.1024 | 0.96061 | 0.95044 | 1.0783 | 1.0653 | 1.0303 | 1.0193 | 0.89086 | 0.88049 | 2021-05-06
TX_MA_Split GN1 Furnace with DX Cooling OA Rate [cfm] | Split GN1 Furnace with DX Cooling OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 2021-05-06
TX_MA_Split GN2 Furnace with DX Cooling OA Rate [cfm] | Split GN2 Furnace with DX Cooling OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 2021-05-06
TX_MA_Split GNE Furnace with DX Cooling OA Rate [cfm] | Split GNE Furnace with DX Cooling OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 2021-05-06
TX_MA_Split GNW Furnace with DX Cooling OA Rate [cfm] | Split GNW Furnace with DX Cooling OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 2021-05-06
TX_MA_Split GS1 Furnace with DX Cooling OA Rate [cfm] | Split GS1 Furnace with DX Cooling OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 2021-05-06
TX_MA_Split GS2 Furnace with DX Cooling OA Rate [cfm] | Split GS2 Furnace with DX Cooling OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 2021-05-06
TX_MA_Split GSW Furnace with DX Cooling OA Rate [cfm] | Split GSW Furnace with DX Cooling OA Rate [cfm] | 56.9945 | 56.9945 | 56.9945 | 56.9945 | 56.9945 | 56.9945 | 56.9945 | 56.9945 | 56.9945 | 56.9945 | 2021-05-06
TX_MA_Split MN1 Furnace with DX Cooling OA Rate [cfm] | Split MN1 Furnace with DX Cooling OA Rate [cfm] | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 2021-05-06
TX_MA_Split MN2 Furnace with DX Cooling OA Rate [cfm] | Split MN2 Furnace with DX Cooling OA Rate [cfm] | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 2021-05-06
TX_MA_Split MNE Furnace with DX Cooling OA Rate [cfm] | Split MNE Furnace with DX Cooling OA Rate [cfm] | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 2021-05-06
TX_MA_Split MNW Furnace with DX Cooling OA Rate [cfm] | Split MNW Furnace with DX Cooling OA Rate [cfm] | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 2021-05-06
TX_MA_Split MS1 Furnace with DX Cooling OA Rate [cfm] | Split MS1 Furnace with DX Cooling OA Rate [cfm] | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 2021-05-06
TX_MA_Split MS2 Furnace with DX Cooling OA Rate [cfm] | Split MS2 Furnace with DX Cooling OA Rate [cfm] | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 2021-05-06
TX_MA_Split MSE Furnace with DX Cooling OA Rate [cfm] | Split MSE Furnace with DX Cooling OA Rate [cfm] | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 2021-05-06
TX_MA_Split MSW Furnace with DX Cooling OA Rate [cfm] | Split MSW Furnace with DX Cooling OA Rate [cfm] | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 2021-05-06
TX_MA_Split Office Furnace with DX Cooling OA Rate [cfm] | Split Office Furnace with DX Cooling OA Rate [cfm] | 80.7372 | 80.7372 | 80.7372 | 80.7372 | 80.7372 | 80.7372 | 80.7372 | 80.7372 | 80.7372 | 80.7372 | 2021-05-06
TX_MA_Split TN1 Furnace with DX Cooling OA Rate [cfm] | Split TN1 Furnace with DX Cooling OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 2021-05-06
TX_MA_Split TN2 Furnace with DX Cooling OA Rate [cfm] | Split TN2 Furnace with DX Cooling OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 2021-05-06
TX_MA_Split TNE Furnace with DX Cooling OA Rate [cfm] | Split TNE Furnace with DX Cooling OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 2021-05-06
TX_MA_Split TNW Furnace with DX Cooling OA Rate [cfm] | Split TNW Furnace with DX Cooling OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 2021-05-06
TX_MA_Split TS1 Furnace with DX Cooling OA Rate [cfm] | Split TS1 Furnace with DX Cooling OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 2021-05-06
TX_MA_Split TS2 Furnace with DX Cooling OA Rate [cfm] | Split TS2 Furnace with DX Cooling OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 2021-05-06
TX_MA_Split TSE Furnace with DX Cooling OA Rate [cfm] | Split TSE Furnace with DX Cooling OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 2021-05-06
TX_MA_Split TSW Furnace with DX Cooling OA Rate [cfm] | Split TSW Furnace with DX Cooling OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 2021-05-06
TX_MA_SPLIT GSW HEATING COIL Heating Capacity [kBtu/hr] | SPLIT GSW HEATING COIL Heating Capacity [kBtu/hr] | 5.5553 | 5.4847 | 5.565 | 5.4673 | 4.6427 | 4.5593 | 8.5423 | 8.4378 | 5.4058 | 5.3304 | 2021-05-06
TX_MA_SPLIT GNW HEATING COIL Heating Capacity [kBtu/hr] | SPLIT GNW HEATING COIL Heating Capacity [kBtu/hr] | 5.5208 | 5.446 | 5.5261 | 5.4242 | 4.6025 | 4.5149 | 8.5032 | 8.3933 | 5.3571 | 5.2788 | 2021-05-06
TX_MA_SPLIT OFFICE HEATING COIL Heating Capacity [kBtu/hr] | SPLIT OFFICE HEATING COIL Heating Capacity [kBtu/hr] | 15.1423 | 15.0628 | 15.4284 | 15.2519 | 13.421 | 13.2599 | 20.6546 | 20.5157 | 15.0421 | 14.9007 | 2021-05-06
TX_MA_SPLIT GNE HEATING COIL Heating Capacity [kBtu/hr] | SPLIT GNE HEATING COIL Heating Capacity [kBtu/hr] | 5.5048 | 5.4331 | 5.5261 | 5.4242 | 4.6025 | 4.5149 | 8.5032 | 8.3933 | 5.3727 | 5.2921 | 2021-05-06
TX_MA_SPLIT GN1 HEATING COIL Heating Capacity [kBtu/hr] | SPLIT GN1 HEATING COIL Heating Capacity [kBtu/hr] | 4.0266 | 4.0266 | 4.4428 | 4.4428 | 4.1096 | 4.1096 | 6.0268 | 5.9741 | 4.2004 | 4.2004 | 2021-05-06
TX_MA_SPLIT GN2 HEATING COIL Heating Capacity [kBtu/hr] | SPLIT GN2 HEATING COIL Heating Capacity [kBtu/hr] | 4.0266 | 4.0266 | 4.4428 | 4.4428 | 4.1096 | 4.1096 | 6.0268 | 5.9741 | 4.2004 | 4.2004 | 2021-05-06
TX_MA_SPLIT GS1 HEATING COIL Heating Capacity [kBtu/hr] | SPLIT GS1 HEATING COIL Heating Capacity [kBtu/hr] | 4.0266 | 4.0266 | 4.4428 | 4.4428 | 4.1096 | 4.1096 | 5.9673 | 5.92 | 4.2004 | 4.2004 | 2021-05-06
TX_MA_SPLIT GS2 HEATING COIL Heating Capacity [kBtu/hr] | SPLIT GS2 HEATING COIL Heating Capacity [kBtu/hr] | 4.0826 | 4.0526 | 4.4428 | 4.4428 | 4.1096 | 4.1096 | 6.4862 | 6.4365 | 4.2004 | 4.2004 | 2021-05-06
TX_MA_SPLIT MSW HEATING COIL Heating Capacity [kBtu/hr] | SPLIT MSW HEATING COIL Heating Capacity [kBtu/hr] | 11.296 | 11.1602 | 9.8639 | 9.672 | 8.8887 | 8.7249 | 16.5306 | 16.3231 | 10.2438 | 10.1017 | 2021-05-06
TX_MA_SPLIT MNW HEATING COIL Heating Capacity [kBtu/hr] | SPLIT MNW HEATING COIL Heating Capacity [kBtu/hr] | 11.3606 | 11.2137 | 9.9335 | 9.7308 | 8.9527 | 8.7777 | 16.6467 | 16.4257 | 10.3093 | 10.1593 | 2021-05-06
TX_MA_SPLIT MSE HEATING COIL Heating Capacity [kBtu/hr] | SPLIT MSE HEATING COIL Heating Capacity [kBtu/hr] | 11.2566 | 11.1282 | 9.8639 | 9.672 | 8.8887 | 8.7249 | 16.5306 | 16.3231 | 10.2815 | 10.1341 | 2021-05-06
TX_MA_SPLIT MNE HEATING COIL Heating Capacity [kBtu/hr] | SPLIT MNE HEATING COIL Heating Capacity [kBtu/hr] | 11.3213 | 11.1819 | 9.9335 | 9.7308 | 8.9527 | 8.7777 | 16.6467 | 16.4257 | 10.347 | 10.1917 | 2021-05-06
TX_MA_SPLIT MN1 HEATING COIL Heating Capacity [kBtu/hr] | SPLIT MN1 HEATING COIL Heating Capacity [kBtu/hr] | 8.0531 | 8.0531 | 8.8856 | 8.8856 | 8.2192 | 8.2192 | 11.074 | 10.9754 | 8.4009 | 8.4009 | 2021-05-06
TX_MA_SPLIT MN2 HEATING COIL Heating Capacity [kBtu/hr] | SPLIT MN2 HEATING COIL Heating Capacity [kBtu/hr] | 8.0531 | 8.0531 | 8.8856 | 8.8856 | 8.2192 | 8.2192 | 11.074 | 10.9754 | 8.4009 | 8.4009 | 2021-05-06
TX_MA_SPLIT MS1 HEATING COIL Heating Capacity [kBtu/hr] | SPLIT MS1 HEATING COIL Heating Capacity [kBtu/hr] | 8.0531 | 8.0531 | 8.8856 | 8.8856 | 8.2192 | 8.2192 | 10.965 | 10.88 | 8.4009 | 8.4009 | 2021-05-06
TX_MA_SPLIT MS2 HEATING COIL Heating Capacity [kBtu/hr] | SPLIT MS2 HEATING COIL Heating Capacity [kBtu/hr] | 8.0531 | 8.0531 | 8.8856 | 8.8856 | 8.2192 | 8.2192 | 10.965 | 10.88 | 8.4009 | 8.4009 | 2021-05-06
TX_MA_SPLIT TSW HEATING COIL Heating Capacity [kBtu/hr] | SPLIT TSW HEATING COIL Heating Capacity [kBtu/hr] | 8.0636 | 7.9971 | 7.6336 | 7.5407 | 6.9954 | 6.9167 | 12.0123 | 11.9101 | 8.0748 | 8.005 | 2021-05-06
TX_MA_SPLIT TNW HEATING COIL Heating Capacity [kBtu/hr] | SPLIT TNW HEATING COIL Heating Capacity [kBtu/hr] | 8.0998 | 8.0279 | 7.6745 | 7.5763 | 7.0325 | 6.9486 | 12.0785 | 11.9696 | 8.1146 | 8.041 | 2021-05-06
TX_MA_SPLIT TSE HEATING COIL Heating Capacity [kBtu/hr] | SPLIT TSE HEATING COIL Heating Capacity [kBtu/hr] | 8.0435 | 7.9809 | 7.6336 | 7.5407 | 6.9954 | 6.9167 | 12.0123 | 11.9101 | 8.0948 | 8.0221 | 2021-05-06
TX_MA_SPLIT TNE HEATING COIL Heating Capacity [kBtu/hr] | SPLIT TNE HEATING COIL Heating Capacity [kBtu/hr] | 8.0797 | 8.0117 | 7.6745 | 7.5763 | 7.0325 | 6.9486 | 12.0785 | 11.9696 | 8.1345 | 8.0581 | 2021-05-06
TX_MA_SPLIT TN1 HEATING COIL Heating Capacity [kBtu/hr] | SPLIT TN1 HEATING COIL Heating Capacity [kBtu/hr] | 5.792 | 5.7659 | 5.8088 | 5.7665 | 5.1843 | 5.1508 | 9.0393 | 8.9905 | 6.2366 | 6.2085 | 2021-05-06
TX_MA_SPLIT TN2 HEATING COIL Heating Capacity [kBtu/hr] | SPLIT TN2 HEATING COIL Heating Capacity [kBtu/hr] | 5.7914 | 5.7654 | 5.8088 | 5.7665 | 5.1843 | 5.1508 | 9.0393 | 8.9905 | 6.2372 | 6.209 | 2021-05-06
TX_MA_SPLIT TS1 HEATING COIL Heating Capacity [kBtu/hr] | SPLIT TS1 HEATING COIL Heating Capacity [kBtu/hr] | 5.7475 | 5.7267 | 5.7609 | 5.7235 | 5.1399 | 5.1114 | 8.9662 | 8.924 | 6.1898 | 6.1654 | 2021-05-06
TX_MA_SPLIT TS2 HEATING COIL Heating Capacity [kBtu/hr] | SPLIT TS2 HEATING COIL Heating Capacity [kBtu/hr] | 5.7469 | 5.7263 | 5.7609 | 5.7235 | 5.1399 | 5.1114 | 8.9662 | 8.924 | 6.1904 | 6.1659 | 2021-05-06
TX_MA_Split_GSW ERV Flag | Split_GSW ERV Flag | No | Yes | No | Yes | No | Yes | No | Yes | No | Yes | 2021-05-06
TX_MA_Split_GNW ERV Flag | Split_GNW ERV Flag | No | Yes | No | Yes | No | Yes | No | Yes | No | Yes | 2021-05-06
TX_MA_Split_GNE ERV Flag | Split_GNE ERV Flag | No | Yes | No | Yes | No | Yes | No | Yes | No | Yes | 2021-05-06
TX_MA_Split_GN1 ERV Flag | Split_GN1 ERV Flag | No | Yes | No | Yes | No | Yes | No | Yes | No | Yes | 2021-05-06
TX_MA_Split_GN2 ERV Flag | Split_GN2 ERV Flag | No | Yes | No | Yes | No | Yes | No | Yes | No | Yes | 2021-05-06
TX_MA_Split_GS1 ERV Flag | Split_GS1 ERV Flag | No | Yes | No | Yes | No | Yes | No | Yes | No | Yes | 2021-05-06
TX_MA_Split_GS2 ERV Flag | Split_GS2 ERV Flag | No | Yes | No | Yes | No | Yes | No | Yes | No | Yes | 2021-05-06
TX_MA_Split_MSW ERV Flag | Split_MSW ERV Flag | No | Yes | No | Yes | No | Yes | No | Yes | No | Yes | 2021-05-06
TX_MA_Split_MNW ERV Flag | Split_MNW ERV Flag | No | Yes | No | Yes | No | Yes | No | Yes | No | Yes | 2021-05-06
TX_MA_Split_MSE ERV Flag | Split_MSE ERV Flag | No | Yes | No | Yes | No | Yes | No | Yes | No | Yes | 2021-05-06
TX_MA_Split_MNE ERV Flag | Split_MNE ERV Flag | No | Yes | No | Yes | No | Yes | No | Yes | No | Yes | 2021-05-06
TX_MA_Split_MN1 ERV Flag | Split_MN1 ERV Flag | No | Yes | No | Yes | No | Yes | No | Yes | No | Yes | 2021-05-06
TX_MA_Split_MN2 ERV Flag | Split_MN2 ERV Flag | No | Yes | No | Yes | No | Yes | No | Yes | No | Yes | 2021-05-06
TX_MA_Split_MS1 ERV Flag | Split_MS1 ERV Flag | No | Yes | No | Yes | No | Yes | No | Yes | No | Yes | 2021-05-06
TX_MA_Split_MS2 ERV Flag | Split_MS2 ERV Flag | No | Yes | No | Yes | No | Yes | No | Yes | No | Yes | 2021-05-06
TX_MA_Split_TSW ERV Flag | Split_TSW ERV Flag | No | Yes | No | Yes | No | No | No | Yes | No | No | 2021-05-06
TX_MA_Split_TNW ERV Flag | Split_TNW ERV Flag | No | Yes | No | Yes | No | Yes | No | Yes | No | Yes | 2021-05-06
TX_MA_Split_TSE ERV Flag | Split_TSE ERV Flag | No | Yes | No | Yes | No | Yes | No | Yes | No | Yes | 2021-05-06
TX_MA_Split_TNE ERV Flag | Split_TNE ERV Flag | No | Yes | No | Yes | No | Yes | No | Yes | No | Yes | 2021-05-06
TX_MA_Split_TN1 ERV Flag | Split_TN1 ERV Flag | No | Yes | No | Yes | No | Yes | No | Yes | No | Yes | 2021-05-06
TX_MA_Split_TN2 ERV Flag | Split_TN2 ERV Flag | No | Yes | No | Yes | No | Yes | No | Yes | No | Yes | 2021-05-06
TX_MA_Split_TS1 ERV Flag | Split_TS1 ERV Flag | No | Yes | No | Yes | No | Yes | No | Yes | No | Yes | 2021-05-06
TX_MA_Split_TS2 ERV Flag | Split_TS2 ERV Flag | No | Yes | No | Yes | No | Yes | No | Yes | No | Yes | 2021-05-06
id | item | Zone3B(UT-SaintGeorge-UT) ASHRAE901-state_STD2016 | Zone3B(UT-SaintGeorge-UT) ASHRAE901-state_STD2019 | Zone5B(UT-SaltLakeCity-UT) ASHRAE901-state_STD2016 | Zone5B(UT-SaltLakeCity-UT) ASHRAE901-state_STD2019 | Zone6B(UT-Vernal-UT) ASHRAE901-state_STD2016 | Zone6B(UT-Vernal-UT) ASHRAE901-state_STD2019 |  |  |  |  | 2021-05-06
UT_SO_PSZ-AC:1 Cooling Capacity [ton] | PSZ-AC:1 Cooling Capacity [ton] | 1.9042 | 1.7993 | 1.6842 | 1.5704 | 1.7208 | 1.5965 |  |  |  |  | 2021-05-06
UT_SO_PSZ-AC:2 Cooling Capacity [ton] | PSZ-AC:2 Cooling Capacity [ton] | 1.9232 | 1.8359 | 1.5392 | 1.4613 | 1.488 | 1.389 |  |  |  |  | 2021-05-06
UT_SO_PSZ-AC:3 Cooling Capacity [ton] | PSZ-AC:3 Cooling Capacity [ton] | 1.2611 | 1.2105 | 1.2082 | 1.1582 | 1.2181 | 1.1328 |  |  |  |  | 2021-05-06
UT_SO_PSZ-AC:4 Cooling Capacity [ton] | PSZ-AC:4 Cooling Capacity [ton] | 1.875 | 1.781 | 1.4623 | 1.3682 | 1.4188 | 1.3063 |  |  |  |  | 2021-05-06
UT_SO_PSZ-AC:5 Cooling Capacity [ton] | PSZ-AC:5 Cooling Capacity [ton] | 1.4871 | 1.4334 | 1.4475 | 1.3962 | 1.5142 | 1.423 |  |  |  |  | 2021-05-06
UT_SO_PSZ-AC:1 Supply Flow Rate [cfm] | PSZ-AC:1 Supply Flow Rate [cfm] | 783.9856 | 720.4192 | 762.7968 | 699.2304 | 783.9856 | 720.4192 |  |  |  |  | 2021-05-06
UT_SO_PSZ-AC:2 Supply Flow Rate [cfm] | PSZ-AC:2 Supply Flow Rate [cfm] | 805.1744 | 762.7968 | 699.2304 | 656.8528 | 678.0416 | 635.664 |  |  |  |  | 2021-05-06
UT_SO_PSZ-AC:3 Supply Flow Rate [cfm] | PSZ-AC:3 Supply Flow Rate [cfm] | 572.0976 | 550.9088 | 550.9088 | 529.72 | 550.9088 | 508.5312 |  |  |  |  | 2021-05-06
UT_SO_PSZ-AC:4 Supply Flow Rate [cfm] | PSZ-AC:4 Supply Flow Rate [cfm] | 783.9856 | 741.608 | 656.8528 | 614.4752 | 635.664 | 593.2864 |  |  |  |  | 2021-05-06
UT_SO_PSZ-AC:5 Supply Flow Rate [cfm] | PSZ-AC:5 Supply Flow Rate [cfm] | 678.0416 | 635.664 | 656.8528 | 635.664 | 678.0416 | 635.664 |  |  |  |  | 2021-05-06
UT_SO_PSZ-AC:1 OA Rate [cfm] | PSZ-AC:1 OA Rate [cfm] | 136.9178 | 136.9178 | 136.9178 | 136.9178 | 136.9178 | 136.9178 |  |  |  |  | 2021-05-06
UT_SO_PSZ-AC:2 OA Rate [cfm] | PSZ-AC:2 OA Rate [cfm] | 103.7925 | 103.7925 | 103.7925 | 103.7925 | 103.7925 | 103.7925 |  |  |  |  | 2021-05-06
UT_SO_PSZ-AC:3 OA Rate [cfm] | PSZ-AC:3 OA Rate [cfm] | 61.5711 | 61.5711 | 61.5711 | 61.5711 | 61.5711 | 61.5711 |  |  |  |  | 2021-05-06
UT_SO_PSZ-AC:4 OA Rate [cfm] | PSZ-AC:4 OA Rate [cfm] | 103.7925 | 103.7925 | 103.7925 | 103.7925 | 103.7925 | 103.7925 |  |  |  |  | 2021-05-06
UT_SO_PSZ-AC:5 OA Rate [cfm] | PSZ-AC:5 OA Rate [cfm] | 61.5711 | 61.5711 | 61.5711 | 61.5711 | 61.5711 | 61.5711 |  |  |  |  | 2021-05-06
UT_SO_PSZ-AC:1 heating Capacity [kBtu/hr] | PSZ-AC:1 heating Capacity [kBtu/hr] | 10.2819 | 10.2819 | 12.0201 | 12.0201 | 12.5919 | 12.5685 |  |  |  |  | 2021-05-06
UT_SO_PSZ-AC:2 heating Capacity [kBtu/hr] | PSZ-AC:2 heating Capacity [kBtu/hr] | 12.7234 | 12.5298 | 16.7623 | 16.5587 | 17.2776 | 17.0549 |  |  |  |  | 2021-05-06
UT_SO_PSZ-AC:3 heating Capacity [kBtu/hr] | PSZ-AC:3 heating Capacity [kBtu/hr] | 7.7423 | 7.6321 | 10.1825 | 10.0699 | 10.4521 | 10.329 |  |  |  |  | 2021-05-06
UT_SO_PSZ-AC:4 heating Capacity [kBtu/hr] | PSZ-AC:4 heating Capacity [kBtu/hr] | 12.5444 | 12.3813 | 16.519 | 16.3588 | 17.1904 | 17.0031 |  |  |  |  | 2021-05-06
UT_SO_PSZ-AC:5 heating Capacity [kBtu/hr] | PSZ-AC:5 heating Capacity [kBtu/hr] | 7.7212 | 7.6141 | 10.1422 | 10.0339 | 10.4863 | 10.3596 |  |  |  |  | 2021-05-06
id | item | Zone3B(UT-SaintGeorge-UT) ASHRAE901-state_STD2016 | Zone3B(UT-SaintGeorge-UT) ASHRAE901-state_STD2019 | Zone5B(UT-SaltLakeCity-UT) ASHRAE901-state_STD2016 | Zone5B(UT-SaltLakeCity-UT) ASHRAE901-state_STD2019 | Zone6B(UT-Vernal-UT) ASHRAE901-state_STD2016 | Zone6B(UT-Vernal-UT) ASHRAE901-state_STD2019 |  |  |  |  | 2021-05-06
UT_LO_CAV_BAS Supply Flow Rate [cfm] | CAV_BAS Supply Flow Rate [cfm] | 13009.9232 | 12056.4272 | 13582.0208 | 12564.9584 | 14111.7408 | 13052.3008 |  |  |  |  | 2021-05-06
UT_LO_VAV_BOT WITH REHEAT Supply Flow Rate [cfm] | VAV_BOT WITH REHEAT Supply Flow Rate [cfm] | 21739.7088 | 20680.2688 | 22883.904 | 21803.2752 | 23456.0016 | 22163.4848 |  |  |  |  | 2021-05-06
UT_LO_VAV_MID WITH REHEAT Supply Flow Rate [cfm] | VAV_MID WITH REHEAT Supply Flow Rate [cfm] | 203009.8931 | 192924.0243 | 212756.7411 | 202480.1731 | 217291.1443 | 204577.8643 |  |  |  |  | 2021-05-06
UT_LO_VAV_TOP WITH REHEAT Supply Flow Rate [cfm] | VAV_TOP WITH REHEAT Supply Flow Rate [cfm] | 22311.8064 | 21358.3104 | 23222.9248 | 22290.6176 | 23604.3232 | 22354.184 |  |  |  |  | 2021-05-06
UT_LO_Supply Air Temp. Reset Flag | Supply Air Temp. Reset Flag | Yes | Yes | Yes | Yes | Yes | Yes |  |  |  |  | 2021-05-06
UT_LO_CAV_BAS OA Rate [cfm] | CAV_BAS OA Rate [cfm] | 2542.8255 | 2542.8255 | 2542.8255 | 2542.8255 | 2542.8255 | 2542.8255 |  |  |  |  | 2021-05-06
UT_LO_VAV_BOT WITH REHEAT OA Rate [cfm] | VAV_BOT WITH REHEAT OA Rate [cfm] | 5377.8022 | 4302.174 | 5377.8022 | 4302.174 | 5377.8022 | 4302.174 |  |  |  |  | 2021-05-06
UT_LO_VAV_MID WITH REHEAT OA Rate [cfm] | VAV_MID WITH REHEAT OA Rate [cfm] | 53777.9373 | 43021.7396 | 53777.9373 | 43021.7396 | 53777.9373 | 43021.7396 |  |  |  |  | 2021-05-06
UT_LO_VAV_TOP WITH REHEAT OA Rate [cfm] | VAV_TOP WITH REHEAT OA Rate [cfm] | 5377.8022 | 4302.174 | 5377.8022 | 4302.174 | 5377.8022 | 4302.174 |  |  |  |  | 2021-05-06
UT_LO_AIRLOOP DATACENTER BASEMENT OA Rate [cfm] | AIRLOOP DATACENTER BASEMENT OA Rate [cfm] | 716.9654 | 716.9654 | 716.9654 | 716.9654 | 716.9654 | 716.9654 |  |  |  |  | 2021-05-06
UT_LO_VAV_bot_WITH_REHEAT ERV Flag | VAV_bot_WITH_REHEAT ERV Flag | No | No | No | No | No | No |  |  |  |  | 2021-05-06
UT_LO_VAV_mid_WITH_REHEAT ERV Flag | VAV_mid_WITH_REHEAT ERV Flag | No | No | No | No | No | No |  |  |  |  | 2021-05-06
UT_LO_VAV_top_WITH_REHEAT ERV Flag | VAV_top_WITH_REHEAT ERV Flag | No | No | No | No | No | No |  |  |  |  | 2021-05-06
UT_LO_COOLSYS1 CHILLER1 Capacity [ton] | COOLSYS1 CHILLER1 Capacity [ton] | 352.0817 | 324.4212 | 332.7321 | 308.7385 | 316.4202 | 292.7363 |  |  |  |  | 2021-05-06
UT_LO_COOLSYS1 CHILLER2 Capacity [ton] | COOLSYS1 CHILLER2 Capacity [ton] | 352.0817 | 324.4212 | 332.7321 | 308.7385 | 316.4202 | 292.7363 |  |  |  |  | 2021-05-06
UT_LO_TOWERWATERSYS COOLTOWER 1 Capacity [ton] | TOWERWATERSYS COOLTOWER 1 Capacity [ton] | 334.5629 | 308.2794 | 316.2182 | 293.4144 | 300.7221 | 278.2074 |  |  |  |  | 2021-05-06
UT_LO_TOWERWATERSYS COOLTOWER 2 Capacity [ton] | TOWERWATERSYS COOLTOWER 2 Capacity [ton] | 334.5629 | 308.2794 | 316.2182 | 293.4144 | 300.7221 | 278.2074 |  |  |  |  | 2021-05-06
UT_LO_HEATSYS1 BOILER Capacity [MMBTU/h] | HEATSYS1 BOILER Capacity [MMBTU/h] | 3086.5159 | 2728.393 | 3842.0707 | 3411.3072 | 4068.6696 | 3586.418 |  |  |  |  | 2021-05-06
UT_LO_COOLSYS1 PUMP Flow Rate [gal/min] | COOLSYS1 PUMP Flow Rate [gal/min] | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 2021-05-06
UT_LO_COOLSYS1 CHILLER1 PUMP Flow Rate [gal/min] | COOLSYS1 CHILLER1 PUMP Flow Rate [gal/min] | 550.7607 | 507.3467 | 522.9465 | 482.1985 | 497.0138 | 459.7814 |  |  |  |  | 2021-05-06
UT_LO_COOLSYS1 CHILLER2 PUMP Flow Rate [gal/min] | COOLSYS1 CHILLER2 PUMP Flow Rate [gal/min] | 550.7607 | 507.3467 | 522.9465 | 482.1985 | 497.0138 | 459.7814 |  |  |  |  | 2021-05-06
UT_LO_COOLSYS1 PUMP SECONDARY Flow Rate [gal/min] | COOLSYS1 PUMP SECONDARY Flow Rate [gal/min] | 1101.523 | 1014.6933 | 1045.8931 | 964.3986 | 994.0292 | 919.5613 |  |  |  |  | 2021-05-06
UT_LO_HEATSYS1 PUMP Flow Rate [gal/min] | HEATSYS1 PUMP Flow Rate [gal/min] | 633.5485 | 560.0379 | 788.636 | 700.2166 | 835.1488 | 736.1603 |  |  |  |  | 2021-05-06
UT_LO_TOWERWATERSYS PUMP Flow Rate [gal/min] | TOWERWATERSYS PUMP Flow Rate [gal/min] | 1942.4571 | 1789.8185 | 1835.6259 | 1703.2757 | 1745.7546 | 1654.6152 |  |  |  |  | 2021-05-06
UT_LO_PLANT CIRC PUMP Flow Rate [gal/min] | PLANT CIRC PUMP Flow Rate [gal/min] | 221.3799 | 220.4178 | 226.2982 | 225.3773 | 230.0231 | 228.7043 |  |  |  |  | 2021-05-06
UT_LO_COOLSYS1 PUMP SECONDARY Pressure setpoint reset [yes,no] | COOLSYS1 PUMP SECONDARY Pressure setpoint reset [yes,no] | pump_ride_on_curve | pump_ride_on_curve | pump_ride_on_curve | pump_ride_on_curve | pump_ride_on_curve | pump_ride_on_curve |  |  |  |  | 2021-05-06
UT_LO_COOLSYS1 CHILLER1 PUMP Pump Power [hp] | COOLSYS1 CHILLER1 PUMP Pump Power [hp] | 2.9712 | 2.7099 | 2.8211 | 2.5755 | 2.6812 | 2.4558 |  |  |  |  | 2021-05-06
UT_LO_COOLSYS1 CHILLER2 PUMP Pump Power [hp] | COOLSYS1 CHILLER2 PUMP Pump Power [hp] | 2.9712 | 2.7099 | 2.8211 | 2.5755 | 2.6812 | 2.4558 |  |  |  |  | 2021-05-06
UT_LO_COOLSYS1 PUMP SECONDARY Pump Power [hp] | COOLSYS1 PUMP SECONDARY Pump Power [hp] | 17.827 | 16.2591 | 16.9267 | 15.4532 | 16.0873 | 14.7348 |  |  |  |  | 2021-05-06
UT_LO_HEATSYS1 PUMP Pump Power [hp] | HEATSYS1 PUMP Pump Power [hp] | 13.6945 | 11.9857 | 17.0468 | 14.9857 | 18.0522 | 15.755 |  |  |  |  | 2021-05-06
UT_LO_TOWERWATERSYS PUMP Pump Power [hp] | TOWERWATERSYS PUMP Pump Power [hp] | 34.7779 | 31.7284 | 32.8666 | 30.1946 | 31.2553 | 29.3305 |  |  |  |  | 2021-05-06
UT_LO_PLANT CIRC PUMP Pump Power [hp] | PLANT CIRC PUMP Pump Power [hp] | 4.7771 | 4.7092 | 4.8832 | 4.8152 | 4.9636 | 4.8863 |  |  |  |  | 2021-05-06
UT_LO_Datacenter PLANT CIRC PUMP Pump Power [hp] | Datacenter PLANT CIRC PUMP Pump Power [hp] | 4.7771 | 4.7092 | 4.8832 | 4.8152 | 4.9636 | 4.8863 |  |  |  |  | 2021-05-06
UT_LO_ZN_VAV_BOXes_Max_Reheat_Water_Flow_GPM | ZN_VAV_BOXes_Max_Reheat_Water_Flow_GPM | 367.5582 | 349.7382 | 424.264 | 405.1405 | 429.279 | 409.0709 |  |  |  |  | 2021-05-06
UT_LO_COOLSYS1 PUMP SECONDARY VSD | COOLSYS1 PUMP SECONDARY VSD | No | No | No | No | No | No |  |  |  |  | 2021-05-06
UT_LO_HEATSYS1 PUMP VSD | HEATSYS1 PUMP VSD | No | No | No | No | No | No |  |  |  |  | 2021-05-06
UT_LO_DATACENTER BASEMENT Cooling Capacity [ton] | DATACENTER BASEMENT Cooling Capacity [ton] | 130.2945 | 129.91 | 132.3664 | 131.9709 | 134.2447 | 133.8319 |  |  |  |  | 2021-05-06
UT_LO_DATACENTER BOT Cooling Capacity [ton] | DATACENTER BOT Cooling Capacity [ton] | 2.7754 | 2.746 | 2.8895 | 2.8635 | 2.9606 | 2.9136 |  |  |  |  | 2021-05-06
UT_LO_DATACENTER MID Cooling Capacity [ton] | DATACENTER MID Cooling Capacity [ton] | 26.407 | 26.1383 | 27.6872 | 27.4566 | 28.3961 | 27.9359 |  |  |  |  | 2021-05-06
UT_LO_DATACENTER TOP Cooling Capacity [ton] | DATACENTER TOP Cooling Capacity [ton] | 2.6886 | 2.6669 | 2.8253 | 2.803 | 2.8951 | 2.8495 |  |  |  |  | 2021-05-06
id | item | Zone3B(UT-SaintGeorge-UT) ASHRAE901-state_STD2016 | Zone3B(UT-SaintGeorge-UT) ASHRAE901-state_STD2019 | Zone5B(UT-SaltLakeCity-UT) ASHRAE901-state_STD2016 | Zone5B(UT-SaltLakeCity-UT) ASHRAE901-state_STD2019 | Zone6B(UT-Vernal-UT) ASHRAE901-state_STD2016 | Zone6B(UT-Vernal-UT) ASHRAE901-state_STD2019 |  |  |  |  | 2021-05-06
UT_RS_PSZ-AC:1 Cooling Capacity [ton] | PSZ-AC:1 Cooling Capacity [ton] | 10.8634 | 10.325 | 10.0206 | 9.357 | 10.0385 | 9.2826 |  |  |  |  | 2021-05-06
UT_RS_PSZ-AC:2 Cooling Capacity [ton] | PSZ-AC:2 Cooling Capacity [ton] | 50.919 | 48.609 | 45.6445 | 43.5772 | 42.5324 | 40.8099 |  |  |  |  | 2021-05-06
UT_RS_PSZ-AC:3 Cooling Capacity [ton] | PSZ-AC:3 Cooling Capacity [ton] | 7.1935 | 7.0119 | 6.2933 | 6.1251 | 5.7122 | 5.5223 |  |  |  |  | 2021-05-06
UT_RS_PSZ-AC:4 Cooling Capacity [ton] | PSZ-AC:4 Cooling Capacity [ton] | 5.9745 | 5.7841 | 5.0295 | 4.8704 | 4.4867 | 4.2858 |  |  |  |  | 2021-05-06
UT_RS_PSZ-AC:1 Supply Flow Rate [cfm] | PSZ-AC:1 Supply Flow Rate [cfm] | 4809.8576 | 4534.4032 | 4513.2144 | 4216.5712 | 4364.8928 | 3983.4944 |  |  |  |  | 2021-05-06
UT_RS_PSZ-AC:2 Supply Flow Rate [cfm] | PSZ-AC:2 Supply Flow Rate [cfm] | 17268.872 | 16251.8096 | 17565.5152 | 16569.6416 | 17671.4592 | 16675.5856 |  |  |  |  | 2021-05-06
UT_RS_PSZ-AC:3 Supply Flow Rate [cfm] | PSZ-AC:3 Supply Flow Rate [cfm] | 2690.9776 | 2606.2224 | 2627.4112 | 2542.656 | 2542.656 | 2436.712 |  |  |  |  | 2021-05-06
UT_RS_PSZ-AC:4 Supply Flow Rate [cfm] | PSZ-AC:4 Supply Flow Rate [cfm] | 2161.2576 | 2076.5024 | 2034.1248 | 1949.3696 | 1928.1808 | 1822.2368 |  |  |  |  | 2021-05-06
UT_RS_PSZ-AC:1 OA Rate [cfm] | PSZ-AC:1 OA Rate [cfm] | 490.669 | 490.669 | 490.669 | 490.669 | 490.669 | 490.669 |  |  |  |  | 2021-05-06
UT_RS_PSZ-AC:2 OA Rate [cfm] | PSZ-AC:2 OA Rate [cfm] | 4005.1282 | 4005.1282 | 4005.1282 | 4005.1282 | 4005.1282 | 4005.1282 |  |  |  |  | 2021-05-06
UT_RS_PSZ-AC:3 OA Rate [cfm] | PSZ-AC:3 OA Rate [cfm] | 377.3937 | 377.3937 | 377.3937 | 377.3937 | 377.3937 | 377.3937 |  |  |  |  | 2021-05-06
UT_RS_PSZ-AC:4 OA Rate [cfm] | PSZ-AC:4 OA Rate [cfm] | 377.3937 | 377.3937 | 377.3937 | 377.3937 | 377.3937 | 377.3937 |  |  |  |  | 2021-05-06
UT_RS_PSZ-AC:1 OA Damper [gravity, motorized] | PSZ-AC:1 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | motorized | motorized |  |  |  |  | 2021-05-06
UT_RS_PSZ-AC:2 OA Damper [gravity, motorized] | PSZ-AC:2 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | motorized | motorized |  |  |  |  | 2021-05-06
UT_RS_PSZ-AC:3 OA Damper [gravity, motorized] | PSZ-AC:3 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | motorized | motorized |  |  |  |  | 2021-05-06
UT_RS_PSZ-AC:4 OA Damper [gravity, motorized] | PSZ-AC:4 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | motorized | motorized |  |  |  |  | 2021-05-06
UT_RS_PSZ-AC:1 Heating Capacity [kBtu/hr] | PSZ-AC:1 Heating Capacity [kBtu/hr] | 181.4099 | 171.9186 | 170.7633 | 160.2429 | 162.464 | 149.267 |  |  |  |  | 2021-05-06
UT_RS_PSZ-AC:2 Heating Capacity [kBtu/hr] | PSZ-AC:2 Heating Capacity [kBtu/hr] | 735.8652 | 698.3778 | 773.5811 | 738.0715 | 773.669 | 740.5948 |  |  |  |  | 2021-05-06
UT_RS_PSZ-AC:3 Heating Capacity [kBtu/hr] | PSZ-AC:3 Heating Capacity [kBtu/hr] | 105.8147 | 103.1438 | 104.6458 | 102.0777 | 100.7525 | 97.8013 |  |  |  |  | 2021-05-06
UT_RS_PSZ-AC:4 Heating Capacity [kBtu/hr] | PSZ-AC:4 Heating Capacity [kBtu/hr] | 86.2932 | 83.5564 | 84.6608 | 81.946 | 81.881 | 78.7805 |  |  |  |  | 2021-05-06
id | item | Zone3B(UT-SaintGeorge-UT) ASHRAE901-state_STD2016 | Zone3B(UT-SaintGeorge-UT) ASHRAE901-state_STD2019 | Zone5B(UT-SaltLakeCity-UT) ASHRAE901-state_STD2016 | Zone5B(UT-SaltLakeCity-UT) ASHRAE901-state_STD2019 | Zone6B(UT-Vernal-UT) ASHRAE901-state_STD2016 | Zone6B(UT-Vernal-UT) ASHRAE901-state_STD2019 |  |  |  |  | 2021-05-06
UT_PS_VAV_POD_1 Cooling Capacity [ton] | VAV_POD_1 Cooling Capacity [ton] | 23.4727 | 22.0722 | 22.9019 | 21.5154 | 21.2979 | 19.7291 |  |  |  |  | 2021-05-06
UT_PS_VAV_POD_2 Cooling Capacity [ton] | VAV_POD_2 Cooling Capacity [ton] | 23.4548 | 21.8871 | 22.5977 | 21.1797 | 21.0752 | 19.4294 |  |  |  |  | 2021-05-06
UT_PS_VAV_POD_3 Cooling Capacity [ton] | VAV_POD_3 Cooling Capacity [ton] | 21.2912 | 20.0148 | 20.988 | 19.802 | 19.6031 | 18.025 |  |  |  |  | 2021-05-06
UT_PS_VAV_OTHER Cooling Capacity [ton] | VAV_OTHER Cooling Capacity [ton] | 29.7697 | 26.7504 | 25.7249 | 23.4173 | 23.4971 | 21.2559 |  |  |  |  | 2021-05-06
UT_PS_PSZ-AC_1:6 Cooling Capacity [ton] | PSZ-AC_1:6 Cooling Capacity [ton] | 8.7928 | 8.4823 | 8.2588 | 7.9716 | 7.9525 | 7.6478 |  |  |  |  | 2021-05-06
UT_PS_PSZ-AC_2:5 Cooling Capacity [ton] | PSZ-AC_2:5 Cooling Capacity [ton] | 6.2008 | 5.9975 | 5.9424 | 5.9223 | 5.4627 | 5.4049 |  |  |  |  | 2021-05-06
UT_PS_PSZ-AC_2:7 Cooling Capacity [ton] | PSZ-AC_2:7 Cooling Capacity [ton] | 10.5074 | 10.5074 | 10.5074 | 10.5074 | 9.6875 | 9.6875 |  |  |  |  | 2021-05-06
UT_PS_VAV_POD_1 Supply Flow Rate [cfm] | VAV_POD_1 Supply Flow Rate [cfm] | 7034.6816 | 6632.0944 | 6865.1712 | 6462.584 | 6738.0384 | 6250.696 |  |  |  |  | 2021-05-06
UT_PS_VAV_POD_2 Supply Flow Rate [cfm] | VAV_POD_2 Supply Flow Rate [cfm] | 7034.6816 | 6568.528 | 6780.416 | 6356.64 | 6674.472 | 6144.752 |  |  |  |  | 2021-05-06
UT_PS_VAV_POD_3 Supply Flow Rate [cfm] | VAV_POD_3 Supply Flow Rate [cfm] | 6399.0176 | 5996.4304 | 6293.0736 | 5932.864 | 6208.3184 | 5742.1648 |  |  |  |  | 2021-05-06
UT_PS_VAV_OTHER Supply Flow Rate [cfm] | VAV_OTHER Supply Flow Rate [cfm] | 9534.96 | 8984.0512 | 9640.904 | 9089.9952 | 9662.0928 | 8962.8624 |  |  |  |  | 2021-05-06
UT_PS_PSZ-AC_2:5 Supply Flow Rate [cfm] | PSZ-AC_2:5 Supply Flow Rate [cfm] | 1864.6144 | 1801.048 | 1970.5584 | 1970.5584 | 1991.7472 | 1970.5584 |  |  |  |  | 2021-05-06
UT_PS_PSZ-AC_1:6 Supply Flow Rate [cfm] | PSZ-AC_1:6 Supply Flow Rate [cfm] | 2839.2992 | 2712.1664 | 2966.432 | 2839.2992 | 3072.376 | 2924.0544 |  |  |  |  | 2021-05-06
UT_PS_PSZ-AC_2:7 Supply Flow Rate [cfm] | PSZ-AC_2:7 Supply Flow Rate [cfm] | 3157.1312 | 3157.1312 | 3157.1312 | 3157.1312 | 3157.1312 | 3157.1312 |  |  |  |  | 2021-05-06
UT_PS_Supply Air Temp. Reset Flag | Supply Air Temp. Reset Flag | Yes | Yes | Yes | Yes | Yes | Yes |  |  |  |  | 2021-05-06
UT_PS_VAV_POD_1 OA Rate [cfm] | VAV_POD_1 OA Rate [cfm] | 7041.7799 | 6282.2673 | 6870.532 | 6282.2673 | 6742.5728 | 6240.9704 |  |  |  |  | 2021-05-06
UT_PS_VAV_POD_2 OA Rate [cfm] | VAV_POD_2 OA Rate [cfm] | 7035.3597 | 6282.2673 | 6777.8734 | 6282.2673 | 6666.8229 | 6146.1928 |  |  |  |  | 2021-05-06
UT_PS_VAV_POD_3 OA Rate [cfm] | VAV_POD_3 OA Rate [cfm] | 6387.8511 | 5422.002 | 6296.5062 | 5422.002 | 6200.9023 | 5422.002 |  |  |  |  | 2021-05-06
UT_PS_VAV_OTHER OA Rate [cfm] | VAV_OTHER OA Rate [cfm] | 3736.1787 | 2988.8921 | 3736.1787 | 2988.8921 | 3736.1787 | 2988.8921 |  |  |  |  | 2021-05-06
UT_PS_PSZ-AC_2:5 OA Rate [cfm] | PSZ-AC_2:5 OA Rate [cfm] | 1152.7343 | 1152.7343 | 1152.7343 | 1152.7343 | 1152.7343 | 1152.7343 |  |  |  |  | 2021-05-06
UT_PS_PSZ-AC_1:6 OA Rate [cfm] | PSZ-AC_1:6 OA Rate [cfm] | 539.9118 | 539.9118 | 539.9118 | 539.9118 | 539.9118 | 539.9118 |  |  |  |  | 2021-05-06
UT_PS_PSZ-AC_2:7 OA Rate [cfm] | PSZ-AC_2:7 OA Rate [cfm] | 3153.0841 | 3153.0841 | 3153.0841 | 3153.0841 | 3153.0841 | 3153.0841 |  |  |  |  | 2021-05-06
UT_PS_VAV_POD_1 OA Damper [gravity, motorized] | VAV_POD_1 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | motorized | motorized |  |  |  |  | 2021-05-06
UT_PS_VAV_POD_2 OA Damper [gravity, motorized] | VAV_POD_2 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | motorized | motorized |  |  |  |  | 2021-05-06
UT_PS_VAV_POD_3 OA Damper [gravity, motorized] | VAV_POD_3 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | motorized | motorized |  |  |  |  | 2021-05-06
UT_PS_VAV_OTHER OA Damper [gravity, motorized] | VAV_OTHER OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | motorized | motorized |  |  |  |  | 2021-05-06
UT_PS_PSZ-AC_2:5 OA Damper [gravity, motorized] | PSZ-AC_2:5 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | motorized | motorized |  |  |  |  | 2021-05-06
UT_PS_PSZ-AC_1:6 OA Damper [gravity, motorized] | PSZ-AC_1:6 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | motorized | motorized |  |  |  |  | 2021-05-06
UT_PS_PSZ-AC_2:7 OA Damper [gravity, motorized] | PSZ-AC_2:7 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | motorized | motorized |  |  |  |  | 2021-05-06
UT_PS_VAV_POD_1 (economizer) | VAV_POD_1 (economizer) | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb |  |  |  |  | 2021-05-06
UT_PS_VAV_POD_2 (economizer) | VAV_POD_2 (economizer) | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb |  |  |  |  | 2021-05-06
UT_PS_VAV_POD_3 (economizer) | VAV_POD_3 (economizer) | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb |  |  |  |  | 2021-05-06
UT_PS_VAV_OTHER (economizer) | VAV_OTHER (economizer) | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb |  |  |  |  | 2021-05-06
UT_PS_PSZ-AC_2:5 (economizer) | PSZ-AC_2:5 (economizer) | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb |  |  |  |  | 2021-05-06
UT_PS_PSZ-AC_1:6 (economizer) | PSZ-AC_1:6 (economizer) | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb |  |  |  |  | 2021-05-06
UT_PS_PSZ-AC_2:7 (economizer) | PSZ-AC_2:7 (economizer) | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb |  |  |  |  | 2021-05-06
UT_PS_VAV_Pod_1_ERV Flag | VAV_Pod_1_ERV Flag | No | No | No | No | Yes | Yes |  |  |  |  | 2021-05-06
UT_PS_VAV_Pod_2_ERV Flag | VAV_Pod_2_ERV Flag | No | No | No | No | Yes | Yes |  |  |  |  | 2021-05-06
UT_PS_VAV_Pod_3_ERV Flag | VAV_Pod_3_ERV Flag | No | No | No | No | Yes | Yes |  |  |  |  | 2021-05-06
UT_PS_VAV_OTHER_ERV Flag | VAV_OTHER_ERV Flag | No | No | No | No | No | No |  |  |  |  | 2021-05-06
UT_PS_PSZ_AC_2_5_ERV Flag | PSZ_AC_2_5_ERV Flag | No | No | No | No | No | No |  |  |  |  | 2021-05-06
UT_PS_PSZ_AC_2_7_ERV Flag | PSZ_AC_2_7_ERV Flag | No | No | No | No | Yes | Yes |  |  |  |  | 2021-05-06
UT_PS_HEATSYS1 Capacity [MMBTU/h] | HEATSYS1 Capacity [MMBTU/h] | 0.83941 | 0.76826 | 1.0356 | 0.96331 | 1.0788 | 0.99869 |  |  |  |  | 2021-05-06
UT_PS_HEATSYS1 Flow Rate [gal/min] | HEATSYS1 Flow Rate [gal/min] | 86.1505 | 78.8479 | 106.2855 | 98.8662 | 110.7231 | 102.4975 |  |  |  |  | 2021-05-06
UT_PS_VAV_POD_1 Fan Power [hp] | VAV_POD_1 Fan Power [hp] | 10.313 | 9.7716 | 10.0621 | 9.5251 | 9.8719 | 9.2073 |  |  |  |  | 2021-05-06
UT_PS_VAV_POD_2 Fan Power [hp] | VAV_POD_2 Fan Power [hp] | 10.3051 | 9.6897 | 9.9285 | 9.3766 | 9.8356 | 9.0675 |  |  |  |  | 2021-05-06
UT_PS_VAV_POD_3 Fan Power [hp] | VAV_POD_3 Fan Power [hp] | 9.4259 | 8.8608 | 9.2917 | 8.7666 | 9.1485 | 8.4598 |  |  |  |  | 2021-05-06
UT_PS_VAV_OTHER Fan Power [hp] | VAV_OTHER Fan Power [hp] | 13.9509 | 13.1679 | 14.1307 | 13.3054 | 14.1521 | 13.1319 |  |  |  |  | 2021-05-06
UT_PS_HEATSYS1 Pump Power [hp] | HEATSYS1 Pump Power [hp] | 1.8622 | 1.6875 | 2.2974 | 2.1159 | 2.3933 | 2.1936 |  |  |  |  | 2021-05-06
UT_PS_PSZ-AC_1:6 Heating Capacity [kBtu/hr] | PSZ-AC_1:6 Heating Capacity [kBtu/hr] | 200.9381 | 192.2687 | 209.7529 | 201.3167 | 211.7999 | 202.6715 |  |  |  |  | 2021-05-06
UT_PS_PSZ-AC_2:5 Heating Capacity [kBtu/hr] | PSZ-AC_2:5 Heating Capacity [kBtu/hr] | 110.1137 | 108.0842 | 127.0874 | 126.809 | 131.6914 | 130.8652 |  |  |  |  | 2021-05-06
UT_PS_PSZ-AC_2:7 Heating Capacity [kBtu/hr] | PSZ-AC_2:7 Heating Capacity [kBtu/hr] | 236.7822 | 236.7822 | 276.811 | 276.811 | 289.4412 | 289.4412 |  |  |  |  | 2021-05-06
UT_PS_ZN_VAV_BOXes_Max_Reheat_Water_Flow_GPM | ZN_VAV_BOXes_Max_Reheat_Water_Flow_GPM | 60.7656 | 54.9932 | 67.6458 | 62.5252 | 67.3251 | 62.3397 |  |  |  |  | 2021-05-06
id | item | Zone3B(UT-SaintGeorge-UT) ASHRAE901-state_STD2016 | Zone3B(UT-SaintGeorge-UT) ASHRAE901-state_STD2019 | Zone5B(UT-SaltLakeCity-UT) ASHRAE901-state_STD2016 | Zone5B(UT-SaltLakeCity-UT) ASHRAE901-state_STD2019 | Zone6B(UT-Vernal-UT) ASHRAE901-state_STD2016 | Zone6B(UT-Vernal-UT) ASHRAE901-state_STD2019 |  |  |  |  | 2021-05-06
UT_SH_SAC_FRONTOFFICE Cooling Capacity [ton] | SAC_FRONTOFFICE Cooling Capacity [ton] | 2.6492 | 2.4975 | 2.2241 | 2.0924 | 2.0532 | 1.9137 |  |  |  |  | 2021-05-06
UT_SH_SAC_FRONTLOUNGE Cooling Capacity [ton] | SAC_FRONTLOUNGE Cooling Capacity [ton] | 6.6254 | 6.3485 | 5.8193 | 5.5595 | 5.4134 | 5.146 |  |  |  |  | 2021-05-06
UT_SH_SAC_MEETINGROOM Cooling Capacity [ton] | SAC_MEETINGROOM Cooling Capacity [ton] | 3.4006 | 3.3046 | 3.0171 | 2.9411 | 2.8522 | 2.7752 |  |  |  |  | 2021-05-06
UT_SH_SAC_EXC_EMPLGE_RESTRM Cooling Capacity [ton] | SAC_EXC_EMPLGE_RESTRM Cooling Capacity [ton] | 6.4184 | 6.3712 | 5.9929 | 5.932 | 5.8595 | 5.8044 |  |  |  |  | 2021-05-06
UT_SH_SAC_FO_ADDAQ SUPPLY FAN Supply Flow Rate [cfm] | SAC_FO_ADDAQ SUPPLY FAN Supply Flow Rate [cfm] | 995.8736 | 932.3072 | 911.1184 | 847.552 | 889.9296 | 826.3632 |  |  |  |  | 2021-05-06
UT_SH_SAC_FL_ADDAQ SUPPLY FAN Supply Flow Rate [cfm] | SAC_FL_ADDAQ SUPPLY FAN Supply Flow Rate [cfm] | 2203.6352 | 2097.6912 | 2140.0688 | 2034.1248 | 2140.0688 | 2012.936 |  |  |  |  | 2021-05-06
UT_SH_SAC_MR_ADDAQ SUPPLY FAN Supply Flow Rate [cfm] | SAC_MR_ADDAQ SUPPLY FAN Supply Flow Rate [cfm] | 1038.2512 | 995.8736 | 1017.0624 | 974.6848 | 1017.0624 | 995.8736 |  |  |  |  | 2021-05-06
UT_SH_SAC_EXC_ADDAQ SUPPLY FAN Supply Flow Rate [cfm] | SAC_EXC_ADDAQ SUPPLY FAN Supply Flow Rate [cfm] | 2457.9008 | 2436.712 | 2563.8448 | 2542.656 | 2627.4112 | 2606.2224 |  |  |  |  | 2021-05-06
UT_SH_SAC_Exc_EmpLge_RestRm OA Rate [cfm] | SAC_Exc_EmpLge_RestRm OA Rate [cfm] | 199.9928 | 199.9928 | 199.9928 | 199.9928 | 199.9928 | 199.9928 |  |  |  |  | 2021-05-06
UT_SH_SAC_FrontLounge OA Rate [cfm] | SAC_FrontLounge OA Rate [cfm] | 500.0133 | 500.0133 | 500.0133 | 500.0133 | 500.0133 | 500.0133 |  |  |  |  | 2021-05-06
UT_SH_SAC_FrontOffice OA Rate [cfm] | SAC_FrontOffice OA Rate [cfm] | 119.2938 | 119.2938 | 119.2938 | 119.2938 | 119.2938 | 119.2938 |  |  |  |  | 2021-05-06
UT_SH_SAC_MeetingRoom OA Rate [cfm] | SAC_MeetingRoom OA Rate [cfm] | 267.7629 | 267.7629 | 267.7629 | 267.7629 | 267.7629 | 267.7629 |  |  |  |  | 2021-05-06
UT_SH_SAC_FrontLounge OA Damper [gravity, motorized] | SAC_FrontLounge OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | motorized | motorized |  |  |  |  | 2021-05-06
UT_SH_SAC_FrontOffice (economizer) | SAC_FrontOffice (economizer) | No | No | No | No | No | No |  |  |  |  | 2021-05-06
UT_SH_SAC_FrontLounge (economizer) | SAC_FrontLounge (economizer) | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb |  |  |  |  | 2021-05-06
UT_SH_SAC_MeetingRoom (economizer) | SAC_MeetingRoom (economizer) | No | No | No | No | No | No |  |  |  |  | 2021-05-06
UT_SH_SAC_Exc_EmpLge_RestRm (economizer) | SAC_Exc_EmpLge_RestRm (economizer) | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb |  |  |  |  | 2021-05-06
UT_SH_SAC_FRONTOFFICE Heating Capacity [kBtu/hr] | SAC_FRONTOFFICE Heating Capacity [kBtu/hr] | 37.9753 | 35.8437 | 35.4978 | 33.7405 | 34.424 | 32.4659 |  |  |  |  | 2021-05-06
UT_SH_SAC_FRONTLOUNGE Heating Capacity [kBtu/hr] | SAC_FRONTLOUNGE Heating Capacity [kBtu/hr] | 93.995 | 90.5571 | 95.622 | 92.246 | 95.5528 | 92.0455 |  |  |  |  | 2021-05-06
UT_SH_SAC_MEETINGROOM Heating Capacity [kBtu/hr] | SAC_MEETINGROOM Heating Capacity [kBtu/hr] | 45.6048 | 44.3876 | 47.0587 | 46.0549 | 47.4999 | 46.4674 |  |  |  |  | 2021-05-06
UT_SH_SAC_EXC_EMPLGE_RESTRM Heating Capacity [kBtu/hr] | SAC_EXC_EMPLGE_RESTRM Heating Capacity [kBtu/hr] | 89.7683 | 89.1067 | 91.7667 | 91.1099 | 92.2513 | 91.4999 |  |  |  |  | 2021-05-06
id | item | Zone3B(UT-SaintGeorge-UT) ASHRAE901-state_STD2016 | Zone3B(UT-SaintGeorge-UT) ASHRAE901-state_STD2019 | Zone5B(UT-SaltLakeCity-UT) ASHRAE901-state_STD2016 | Zone5B(UT-SaltLakeCity-UT) ASHRAE901-state_STD2019 | Zone6B(UT-Vernal-UT) ASHRAE901-state_STD2016 | Zone6B(UT-Vernal-UT) ASHRAE901-state_STD2019 |  |  |  |  | 2021-05-06
UT_MA_SPLIT GSW COOLING COIL Cooling Capacity [ton] | SPLIT GSW COOLING COIL Cooling Capacity [ton] | 1.0034 | 0.99001 | 0.86362 | 0.84585 | 0.82309 | 0.78502 |  |  |  |  | 2021-05-06
UT_MA_SPLIT GNW COOLING COIL Cooling Capacity [ton] | SPLIT GNW COOLING COIL Cooling Capacity [ton] | 0.96367 | 0.9507 | 0.81781 | 0.8006 | 0.78176 | 0.7455 |  |  |  |  | 2021-05-06
UT_MA_SPLIT OFFICE COOLING COIL Cooling Capacity [ton] | SPLIT OFFICE COOLING COIL Cooling Capacity [ton] | 1.8737 | 1.7664 | 1.8957 | 1.6552 | 1.862 | 1.6411 |  |  |  |  | 2021-05-06
UT_MA_SPLIT GNE COOLING COIL Cooling Capacity [ton] | SPLIT GNE COOLING COIL Cooling Capacity [ton] | 0.86518 | 0.85318 | 0.68163 | 0.6667 | 0.63116 | 0.60207 |  |  |  |  | 2021-05-06
UT_MA_SPLIT GN1 COOLING COIL Cooling Capacity [ton] | SPLIT GN1 COOLING COIL Cooling Capacity [ton] | 0.68505 | 0.67527 | 0.55644 | 0.54464 | 0.51959 | 0.50089 |  |  |  |  | 2021-05-06
UT_MA_SPLIT GN2 COOLING COIL Cooling Capacity [ton] | SPLIT GN2 COOLING COIL Cooling Capacity [ton] | 0.68323 | 0.67346 | 0.55378 | 0.54206 | 0.51645 | 0.49789 |  |  |  |  | 2021-05-06
UT_MA_SPLIT GS1 COOLING COIL Cooling Capacity [ton] | SPLIT GS1 COOLING COIL Cooling Capacity [ton] | 0.73631 | 0.72573 | 0.60318 | 0.5904 | 0.56273 | 0.54116 |  |  |  |  | 2021-05-06
UT_MA_SPLIT GS2 COOLING COIL Cooling Capacity [ton] | SPLIT GS2 COOLING COIL Cooling Capacity [ton] | 0.7671 | 0.7537 | 0.64924 | 0.6308 | 0.60868 | 0.58094 |  |  |  |  | 2021-05-06
UT_MA_SPLIT MSW COOLING COIL Cooling Capacity [ton] | SPLIT MSW COOLING COIL Cooling Capacity [ton] | 2.2106 | 2.1822 | 2.1602 | 2.1201 | 2.0862 | 1.9933 |  |  |  |  | 2021-05-06
UT_MA_SPLIT MNW COOLING COIL Cooling Capacity [ton] | SPLIT MNW COOLING COIL Cooling Capacity [ton] | 2.1493 | 2.1219 | 2.0646 | 2.0257 | 2.0044 | 1.9146 |  |  |  |  | 2021-05-06
UT_MA_SPLIT MSE COOLING COIL Cooling Capacity [ton] | SPLIT MSE COOLING COIL Cooling Capacity [ton] | 2.0943 | 2.0643 | 1.7208 | 1.6875 | 1.5815 | 1.512 |  |  |  |  | 2021-05-06
UT_MA_SPLIT MNE COOLING COIL Cooling Capacity [ton] | SPLIT MNE COOLING COIL Cooling Capacity [ton] | 1.8463 | 1.8216 | 1.6179 | 1.58 | 1.52 | 1.4332 |  |  |  |  | 2021-05-06
UT_MA_SPLIT MN1 COOLING COIL Cooling Capacity [ton] | SPLIT MN1 COOLING COIL Cooling Capacity [ton] | 1.4088 | 1.3887 | 1.2569 | 1.2347 | 1.1904 | 1.1535 |  |  |  |  | 2021-05-06
UT_MA_SPLIT MN2 COOLING COIL Cooling Capacity [ton] | SPLIT MN2 COOLING COIL Cooling Capacity [ton] | 1.4042 | 1.3842 | 1.2496 | 1.2273 | 1.1812 | 1.1451 |  |  |  |  | 2021-05-06
UT_MA_SPLIT MS1 COOLING COIL Cooling Capacity [ton] | SPLIT MS1 COOLING COIL Cooling Capacity [ton] | 1.529 | 1.5073 | 1.3486 | 1.3246 | 1.2618 | 1.2209 |  |  |  |  | 2021-05-06
UT_MA_SPLIT MS2 COOLING COIL Cooling Capacity [ton] | SPLIT MS2 COOLING COIL Cooling Capacity [ton] | 1.525 | 1.5033 | 1.3418 | 1.3181 | 1.2539 | 1.2137 |  |  |  |  | 2021-05-06
UT_MA_SPLIT TSW COOLING COIL Cooling Capacity [ton] | SPLIT TSW COOLING COIL Cooling Capacity [ton] | 1.4123 | 1.391 | 1.3927 | 1.371 | 1.3477 | 1.2954 |  |  |  |  | 2021-05-06
UT_MA_SPLIT TNW COOLING COIL Cooling Capacity [ton] | SPLIT TNW COOLING COIL Cooling Capacity [ton] | 1.3629 | 1.3489 | 1.3396 | 1.3185 | 1.3029 | 1.252 |  |  |  |  | 2021-05-06
UT_MA_SPLIT TSE COOLING COIL Cooling Capacity [ton] | SPLIT TSE COOLING COIL Cooling Capacity [ton] | 1.3483 | 1.333 | 1.1728 | 1.1553 | 1.09 | 1.0525 |  |  |  |  | 2021-05-06
UT_MA_SPLIT TNE COOLING COIL Cooling Capacity [ton] | SPLIT TNE COOLING COIL Cooling Capacity [ton] | 1.2693 | 1.255 | 1.0743 | 1.0589 | 0.99789 | 0.96558 |  |  |  |  | 2021-05-06
UT_MA_SPLIT TN1 COOLING COIL Cooling Capacity [ton] | SPLIT TN1 COOLING COIL Cooling Capacity [ton] | 0.95394 | 0.94355 | 0.85831 | 0.84668 | 0.80716 | 0.78684 |  |  |  |  | 2021-05-06
UT_MA_SPLIT TN2 COOLING COIL Cooling Capacity [ton] | SPLIT TN2 COOLING COIL Cooling Capacity [ton] | 0.94898 | 0.93861 | 0.85004 | 0.83863 | 0.79752 | 0.77791 |  |  |  |  | 2021-05-06
UT_MA_SPLIT TS1 COOLING COIL Cooling Capacity [ton] | SPLIT TS1 COOLING COIL Cooling Capacity [ton] | 1.0856 | 1.0729 | 0.93787 | 0.92449 | 0.88355 | 0.85828 |  |  |  |  | 2021-05-06
UT_MA_SPLIT TS2 COOLING COIL Cooling Capacity [ton] | SPLIT TS2 COOLING COIL Cooling Capacity [ton] | 1.0876 | 1.0749 | 0.9388 | 0.92543 | 0.88363 | 0.85864 |  |  |  |  | 2021-05-06
UT_MA_Split GN1 Furnace with DX Cooling OA Rate [cfm] | Split GN1 Furnace with DX Cooling OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 |  |  |  |  | 2021-05-06
UT_MA_Split GN2 Furnace with DX Cooling OA Rate [cfm] | Split GN2 Furnace with DX Cooling OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 |  |  |  |  | 2021-05-06
UT_MA_Split GNE Furnace with DX Cooling OA Rate [cfm] | Split GNE Furnace with DX Cooling OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 |  |  |  |  | 2021-05-06
UT_MA_Split GNW Furnace with DX Cooling OA Rate [cfm] | Split GNW Furnace with DX Cooling OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 |  |  |  |  | 2021-05-06
UT_MA_Split GS1 Furnace with DX Cooling OA Rate [cfm] | Split GS1 Furnace with DX Cooling OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 |  |  |  |  | 2021-05-06
UT_MA_Split GS2 Furnace with DX Cooling OA Rate [cfm] | Split GS2 Furnace with DX Cooling OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 |  |  |  |  | 2021-05-06
UT_MA_Split GSW Furnace with DX Cooling OA Rate [cfm] | Split GSW Furnace with DX Cooling OA Rate [cfm] | 56.9945 | 56.9945 | 56.9945 | 56.9945 | 56.9945 | 56.9945 |  |  |  |  | 2021-05-06
UT_MA_Split MN1 Furnace with DX Cooling OA Rate [cfm] | Split MN1 Furnace with DX Cooling OA Rate [cfm] | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824 |  |  |  |  | 2021-05-06
UT_MA_Split MN2 Furnace with DX Cooling OA Rate [cfm] | Split MN2 Furnace with DX Cooling OA Rate [cfm] | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824 |  |  |  |  | 2021-05-06
UT_MA_Split MNE Furnace with DX Cooling OA Rate [cfm] | Split MNE Furnace with DX Cooling OA Rate [cfm] | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824 |  |  |  |  | 2021-05-06
UT_MA_Split MNW Furnace with DX Cooling OA Rate [cfm] | Split MNW Furnace with DX Cooling OA Rate [cfm] | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824 |  |  |  |  | 2021-05-06
UT_MA_Split MS1 Furnace with DX Cooling OA Rate [cfm] | Split MS1 Furnace with DX Cooling OA Rate [cfm] | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824 |  |  |  |  | 2021-05-06
UT_MA_Split MS2 Furnace with DX Cooling OA Rate [cfm] | Split MS2 Furnace with DX Cooling OA Rate [cfm] | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824 |  |  |  |  | 2021-05-06
UT_MA_Split MSE Furnace with DX Cooling OA Rate [cfm] | Split MSE Furnace with DX Cooling OA Rate [cfm] | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824 |  |  |  |  | 2021-05-06
UT_MA_Split MSW Furnace with DX Cooling OA Rate [cfm] | Split MSW Furnace with DX Cooling OA Rate [cfm] | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824 |  |  |  |  | 2021-05-06
UT_MA_Split Office Furnace with DX Cooling OA Rate [cfm] | Split Office Furnace with DX Cooling OA Rate [cfm] | 80.7372 | 80.7372 | 80.7372 | 80.7372 | 80.7372 | 80.7372 |  |  |  |  | 2021-05-06
UT_MA_Split TN1 Furnace with DX Cooling OA Rate [cfm] | Split TN1 Furnace with DX Cooling OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 |  |  |  |  | 2021-05-06
UT_MA_Split TN2 Furnace with DX Cooling OA Rate [cfm] | Split TN2 Furnace with DX Cooling OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 |  |  |  |  | 2021-05-06
UT_MA_Split TNE Furnace with DX Cooling OA Rate [cfm] | Split TNE Furnace with DX Cooling OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 |  |  |  |  | 2021-05-06
UT_MA_Split TNW Furnace with DX Cooling OA Rate [cfm] | Split TNW Furnace with DX Cooling OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 |  |  |  |  | 2021-05-06
UT_MA_Split TS1 Furnace with DX Cooling OA Rate [cfm] | Split TS1 Furnace with DX Cooling OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 |  |  |  |  | 2021-05-06
UT_MA_Split TS2 Furnace with DX Cooling OA Rate [cfm] | Split TS2 Furnace with DX Cooling OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 |  |  |  |  | 2021-05-06
UT_MA_Split TSE Furnace with DX Cooling OA Rate [cfm] | Split TSE Furnace with DX Cooling OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 |  |  |  |  | 2021-05-06
UT_MA_Split TSW Furnace with DX Cooling OA Rate [cfm] | Split TSW Furnace with DX Cooling OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 |  |  |  |  | 2021-05-06
UT_MA_SPLIT GSW HEATING COIL Heating Capacity [kBtu/hr] | SPLIT GSW HEATING COIL Heating Capacity [kBtu/hr] | 4.5489 | 4.4856 | 7.6549 | 7.715 | 7.6653 | 7.7259 |  |  |  |  | 2021-05-06
UT_MA_SPLIT GNW HEATING COIL Heating Capacity [kBtu/hr] | SPLIT GNW HEATING COIL Heating Capacity [kBtu/hr] | 4.4946 | 4.4293 | 7.5492 | 7.6095 | 7.596 | 7.6568 |  |  |  |  | 2021-05-06
UT_MA_SPLIT OFFICE HEATING COIL Heating Capacity [kBtu/hr] | SPLIT OFFICE HEATING COIL Heating Capacity [kBtu/hr] | 13.3007 | 13.1793 | 19.402 | 19.53 | 19.3257 | 19.4603 |  |  |  |  | 2021-05-06
UT_MA_SPLIT GNE HEATING COIL Heating Capacity [kBtu/hr] | SPLIT GNE HEATING COIL Heating Capacity [kBtu/hr] | 4.5043 | 4.4375 | 7.5658 | 7.6261 | 7.5817 | 7.6425 |  |  |  |  | 2021-05-06
UT_MA_SPLIT GN1 HEATING COIL Heating Capacity [kBtu/hr] | SPLIT GN1 HEATING COIL Heating Capacity [kBtu/hr] | 4.1296 | 4.1296 | 5.4341 | 5.4945 | 5.6241 | 5.6848 |  |  |  |  | 2021-05-06
UT_MA_SPLIT GN2 HEATING COIL Heating Capacity [kBtu/hr] | SPLIT GN2 HEATING COIL Heating Capacity [kBtu/hr] | 4.1296 | 4.1296 | 5.4346 | 5.495 | 5.6236 | 5.6844 |  |  |  |  | 2021-05-06
UT_MA_SPLIT GS1 HEATING COIL Heating Capacity [kBtu/hr] | SPLIT GS1 HEATING COIL Heating Capacity [kBtu/hr] | 4.1296 | 4.1296 | 5.4435 | 5.5037 | 5.5856 | 5.6462 |  |  |  |  | 2021-05-06
UT_MA_SPLIT GS2 HEATING COIL Heating Capacity [kBtu/hr] | SPLIT GS2 HEATING COIL Heating Capacity [kBtu/hr] | 4.1296 | 4.1296 | 5.9203 | 5.9825 | 6.0544 | 6.1185 |  |  |  |  | 2021-05-06
UT_MA_SPLIT MSW HEATING COIL Heating Capacity [kBtu/hr] | SPLIT MSW HEATING COIL Heating Capacity [kBtu/hr] | 8.3914 | 8.2619 | 13.1131 | 13.2429 | 13.0481 | 13.1799 |  |  |  |  | 2021-05-06
UT_MA_SPLIT MNW HEATING COIL Heating Capacity [kBtu/hr] | SPLIT MNW HEATING COIL Heating Capacity [kBtu/hr] | 8.4396 | 8.3047 | 13.0633 | 13.1927 | 13.1108 | 13.2423 |  |  |  |  | 2021-05-06
UT_MA_SPLIT MSE HEATING COIL Heating Capacity [kBtu/hr] | SPLIT MSE HEATING COIL Heating Capacity [kBtu/hr] | 8.4152 | 8.2822 | 13.1526 | 13.2825 | 13.0139 | 13.1457 |  |  |  |  | 2021-05-06
UT_MA_SPLIT MNE HEATING COIL Heating Capacity [kBtu/hr] | SPLIT MNE HEATING COIL Heating Capacity [kBtu/hr] | 8.4633 | 8.3249 | 13.1029 | 13.2323 | 13.0766 | 13.2081 |  |  |  |  | 2021-05-06
UT_MA_SPLIT MN1 HEATING COIL Heating Capacity [kBtu/hr] | SPLIT MN1 HEATING COIL Heating Capacity [kBtu/hr] | 8.2592 | 8.2592 | 9.6554 | 9.6554 | 10.0959 | 10.0959 |  |  |  |  | 2021-05-06
UT_MA_SPLIT MN2 HEATING COIL Heating Capacity [kBtu/hr] | SPLIT MN2 HEATING COIL Heating Capacity [kBtu/hr] | 8.2592 | 8.2592 | 9.6554 | 9.6554 | 10.0959 | 10.0959 |  |  |  |  | 2021-05-06
UT_MA_SPLIT MS1 HEATING COIL Heating Capacity [kBtu/hr] | SPLIT MS1 HEATING COIL Heating Capacity [kBtu/hr] | 8.2592 | 8.2592 | 9.6554 | 9.6554 | 10.0959 | 10.0959 |  |  |  |  | 2021-05-06
UT_MA_SPLIT MS2 HEATING COIL Heating Capacity [kBtu/hr] | SPLIT MS2 HEATING COIL Heating Capacity [kBtu/hr] | 8.2592 | 8.2592 | 9.6554 | 9.6554 | 10.0959 | 10.0959 |  |  |  |  | 2021-05-06
UT_MA_SPLIT TSW HEATING COIL Heating Capacity [kBtu/hr] | SPLIT TSW HEATING COIL Heating Capacity [kBtu/hr] | 6.9298 | 6.8726 | 9.6933 | 9.755 | 9.8566 | 9.9186 |  |  |  |  | 2021-05-06
UT_MA_SPLIT TNW HEATING COIL Heating Capacity [kBtu/hr] | SPLIT TNW HEATING COIL Heating Capacity [kBtu/hr] | 6.9583 | 6.8987 | 9.673 | 9.7349 | 9.897 | 9.9591 |  |  |  |  | 2021-05-06
UT_MA_SPLIT TSE HEATING COIL Heating Capacity [kBtu/hr] | SPLIT TSE HEATING COIL Heating Capacity [kBtu/hr] | 6.9424 | 6.8833 | 9.7143 | 9.776 | 9.8382 | 9.9002 |  |  |  |  | 2021-05-06
UT_MA_SPLIT TNE HEATING COIL Heating Capacity [kBtu/hr] | SPLIT TNE HEATING COIL Heating Capacity [kBtu/hr] | 6.9709 | 6.9093 | 9.6941 | 9.7559 | 9.8785 | 9.9407 |  |  |  |  | 2021-05-06
UT_MA_SPLIT TN1 HEATING COIL Heating Capacity [kBtu/hr] | SPLIT TN1 HEATING COIL Heating Capacity [kBtu/hr] | 5.405 | 5.3864 | 7.4408 | 7.5025 | 7.8358 | 7.8979 |  |  |  |  | 2021-05-06
UT_MA_SPLIT TN2 HEATING COIL Heating Capacity [kBtu/hr] | SPLIT TN2 HEATING COIL Heating Capacity [kBtu/hr] | 5.4054 | 5.3867 | 7.4414 | 7.5032 | 7.8352 | 7.8973 |  |  |  |  | 2021-05-06
UT_MA_SPLIT TS1 HEATING COIL Heating Capacity [kBtu/hr] | SPLIT TS1 HEATING COIL Heating Capacity [kBtu/hr] | 5.3692 | 5.3531 | 7.4548 | 7.5164 | 7.7886 | 7.8506 |  |  |  |  | 2021-05-06
UT_MA_SPLIT TS2 HEATING COIL Heating Capacity [kBtu/hr] | SPLIT TS2 HEATING COIL Heating Capacity [kBtu/hr] | 5.3697 | 5.3534 | 7.4554 | 7.5171 | 7.7881 | 7.8501 |  |  |  |  | 2021-05-06
UT_MA_Split_GSW ERV Flag | Split_GSW ERV Flag | No | Yes | No | Yes | Yes | Yes |  |  |  |  | 2021-05-06
UT_MA_Split_GNW ERV Flag | Split_GNW ERV Flag | No | Yes | No | Yes | Yes | Yes |  |  |  |  | 2021-05-06
UT_MA_Split_GNE ERV Flag | Split_GNE ERV Flag | No | Yes | No | Yes | Yes | Yes |  |  |  |  | 2021-05-06
UT_MA_Split_GN1 ERV Flag | Split_GN1 ERV Flag | No | Yes | No | Yes | Yes | Yes |  |  |  |  | 2021-05-06
UT_MA_Split_GN2 ERV Flag | Split_GN2 ERV Flag | No | Yes | No | Yes | Yes | Yes |  |  |  |  | 2021-05-06
UT_MA_Split_GS1 ERV Flag | Split_GS1 ERV Flag | No | Yes | No | Yes | Yes | Yes |  |  |  |  | 2021-05-06
UT_MA_Split_GS2 ERV Flag | Split_GS2 ERV Flag | No | Yes | No | Yes | Yes | Yes |  |  |  |  | 2021-05-06
UT_MA_Split_MSW ERV Flag | Split_MSW ERV Flag | No | Yes | No | Yes | Yes | Yes |  |  |  |  | 2021-05-06
UT_MA_Split_MNW ERV Flag | Split_MNW ERV Flag | No | Yes | No | Yes | Yes | Yes |  |  |  |  | 2021-05-06
UT_MA_Split_MSE ERV Flag | Split_MSE ERV Flag | No | Yes | No | Yes | Yes | Yes |  |  |  |  | 2021-05-06
UT_MA_Split_MNE ERV Flag | Split_MNE ERV Flag | No | Yes | No | Yes | Yes | Yes |  |  |  |  | 2021-05-06
UT_MA_Split_MN1 ERV Flag | Split_MN1 ERV Flag | No | Yes | No | Yes | Yes | Yes |  |  |  |  | 2021-05-06
UT_MA_Split_MN2 ERV Flag | Split_MN2 ERV Flag | No | Yes | No | Yes | Yes | Yes |  |  |  |  | 2021-05-06
UT_MA_Split_MS1 ERV Flag | Split_MS1 ERV Flag | No | Yes | No | Yes | Yes | Yes |  |  |  |  | 2021-05-06
UT_MA_Split_MS2 ERV Flag | Split_MS2 ERV Flag | No | Yes | No | Yes | Yes | Yes |  |  |  |  | 2021-05-06
UT_MA_Split_TSW ERV Flag | Split_TSW ERV Flag | No | No | No | No | No | No |  |  |  |  | 2021-05-06
UT_MA_Split_TNW ERV Flag | Split_TNW ERV Flag | No | No | No | No | No | No |  |  |  |  | 2021-05-06
UT_MA_Split_TSE ERV Flag | Split_TSE ERV Flag | No | No | No | Yes | Yes | Yes |  |  |  |  | 2021-05-06
UT_MA_Split_TNE ERV Flag | Split_TNE ERV Flag | No | Yes | No | Yes | Yes | Yes |  |  |  |  | 2021-05-06
UT_MA_Split_TN1 ERV Flag | Split_TN1 ERV Flag | No | Yes | No | Yes | Yes | Yes |  |  |  |  | 2021-05-06
UT_MA_Split_TN2 ERV Flag | Split_TN2 ERV Flag | No | Yes | No | Yes | Yes | Yes |  |  |  |  | 2021-05-06
UT_MA_Split_TS1 ERV Flag | Split_TS1 ERV Flag | No | Yes | No | Yes | Yes | Yes |  |  |  |  | 2021-05-06
UT_MA_Split_TS2 ERV Flag | Split_TS2 ERV Flag | No | Yes | No | Yes | Yes | Yes |  |  |  |  | 2021-05-06
id | item | Zone3A(VA-Norfolk-VA) ASHRAE901-state_STD2016 | Zone3A(VA-Norfolk-VA) ASHRAE901-state_STD2019 | Zone4A(VA-Richmond-VA) ASHRAE901-state_STD2016 | Zone4A(VA-Richmond-VA) ASHRAE901-state_STD2019 | Zone5A(VA-Elkins-WV) ASHRAE901-state_STD2016 | Zone5A(VA-Elkins-WV) ASHRAE901-state_STD2019 |  |  |  |  | 2021-05-06
VA_SO_PSZ-AC:1 Cooling Capacity [ton] | PSZ-AC:1 Cooling Capacity [ton] | 2.0142 | 1.919 | 1.9627 | 1.8642 | 1.7003 | 1.6084 |  |  |  |  | 2021-05-06
VA_SO_PSZ-AC:2 Cooling Capacity [ton] | PSZ-AC:2 Cooling Capacity [ton] | 1.7712 | 1.7038 | 1.7471 | 1.6832 | 1.3959 | 1.3356 |  |  |  |  | 2021-05-06
VA_SO_PSZ-AC:3 Cooling Capacity [ton] | PSZ-AC:3 Cooling Capacity [ton] | 1.163 | 1.1227 | 1.1662 | 1.1272 | 0.9916 | 0.95384 |  |  |  |  | 2021-05-06
VA_SO_PSZ-AC:4 Cooling Capacity [ton] | PSZ-AC:4 Cooling Capacity [ton] | 1.7379 | 1.6614 | 1.6923 | 1.6267 | 1.3535 | 1.275 |  |  |  |  | 2021-05-06
VA_SO_PSZ-AC:5 Cooling Capacity [ton] | PSZ-AC:5 Cooling Capacity [ton] | 1.3378 | 1.2954 | 1.3731 | 1.3332 | 1.1913 | 1.1525 |  |  |  |  | 2021-05-06
VA_SO_PSZ-AC:1 Supply Flow Rate [cfm] | PSZ-AC:1 Supply Flow Rate [cfm] | 656.8528 | 614.4752 | 656.8528 | 614.4752 | 678.0416 | 614.4752 |  |  |  |  | 2021-05-06
VA_SO_PSZ-AC:2 Supply Flow Rate [cfm] | PSZ-AC:2 Supply Flow Rate [cfm] | 614.4752 | 572.0976 | 614.4752 | 572.0976 | 550.9088 | 529.72 |  |  |  |  | 2021-05-06
VA_SO_PSZ-AC:3 Supply Flow Rate [cfm] | PSZ-AC:3 Supply Flow Rate [cfm] | 444.9648 | 423.776 | 444.9648 | 423.776 | 444.9648 | 423.776 |  |  |  |  | 2021-05-06
VA_SO_PSZ-AC:4 Supply Flow Rate [cfm] | PSZ-AC:4 Supply Flow Rate [cfm] | 593.2864 | 550.9088 | 572.0976 | 550.9088 | 529.72 | 487.3424 |  |  |  |  | 2021-05-06
VA_SO_PSZ-AC:5 Supply Flow Rate [cfm] | PSZ-AC:5 Supply Flow Rate [cfm] | 508.5312 | 487.3424 | 529.72 | 508.5312 | 529.72 | 508.5312 |  |  |  |  | 2021-05-06
VA_SO_PSZ-AC:1 OA Rate [cfm] | PSZ-AC:1 OA Rate [cfm] | 136.9178 | 136.9178 | 136.9178 | 136.9178 | 136.9178 | 136.9178 |  |  |  |  | 2021-05-06
VA_SO_PSZ-AC:2 OA Rate [cfm] | PSZ-AC:2 OA Rate [cfm] | 103.7925 | 103.7925 | 103.7925 | 103.7925 | 103.7925 | 103.7925 |  |  |  |  | 2021-05-06
VA_SO_PSZ-AC:3 OA Rate [cfm] | PSZ-AC:3 OA Rate [cfm] | 61.5711 | 61.5711 | 61.5711 | 61.5711 | 61.5711 | 61.5711 |  |  |  |  | 2021-05-06
VA_SO_PSZ-AC:4 OA Rate [cfm] | PSZ-AC:4 OA Rate [cfm] | 103.7925 | 103.7925 | 103.7925 | 103.7925 | 103.7925 | 103.7925 |  |  |  |  | 2021-05-06
VA_SO_PSZ-AC:5 OA Rate [cfm] | PSZ-AC:5 OA Rate [cfm] | 61.5711 | 61.5711 | 61.5711 | 61.5711 | 61.5711 | 61.5711 |  |  |  |  | 2021-05-06
VA_SO_PSZ-AC:1 heating Capacity [kBtu/hr] | PSZ-AC:1 heating Capacity [kBtu/hr] | 12.1837 | 12.1837 | 12.8379 | 12.8379 | 14.3668 | 14.3668 |  |  |  |  | 2021-05-06
VA_SO_PSZ-AC:2 heating Capacity [kBtu/hr] | PSZ-AC:2 heating Capacity [kBtu/hr] | 17.2106 | 16.9847 | 16.2755 | 16.1002 | 19.3723 | 19.1413 |  |  |  |  | 2021-05-06
VA_SO_PSZ-AC:3 heating Capacity [kBtu/hr] | PSZ-AC:3 heating Capacity [kBtu/hr] | 10.6318 | 10.5003 | 9.9755 | 9.8745 | 11.6946 | 11.5705 |  |  |  |  | 2021-05-06
VA_SO_PSZ-AC:4 heating Capacity [kBtu/hr] | PSZ-AC:4 heating Capacity [kBtu/hr] | 17.0479 | 16.8532 | 16.1786 | 16.0292 | 19.1738 | 18.985 |  |  |  |  | 2021-05-06
VA_SO_PSZ-AC:5 heating Capacity [kBtu/hr] | PSZ-AC:5 heating Capacity [kBtu/hr] | 10.6318 | 10.5003 | 9.9755 | 9.8745 | 11.7329 | 11.6052 |  |  |  |  | 2021-05-06
id | item | Zone3A(VA-Norfolk-VA) ASHRAE901-state_STD2016 | Zone3A(VA-Norfolk-VA) ASHRAE901-state_STD2019 | Zone4A(VA-Richmond-VA) ASHRAE901-state_STD2016 | Zone4A(VA-Richmond-VA) ASHRAE901-state_STD2019 | Zone5A(VA-Elkins-WV) ASHRAE901-state_STD2016 | Zone5A(VA-Elkins-WV) ASHRAE901-state_STD2019 |  |  |  |  | 2021-05-06
VA_LO_CAV_BAS Supply Flow Rate [cfm] | CAV_BAS Supply Flow Rate [cfm] | 11357.1968 | 10488.456 | 11759.784 | 10891.0432 | 12331.8816 | 11399.5744 |  |  |  |  | 2021-05-06
VA_LO_VAV_BOT WITH REHEAT Supply Flow Rate [cfm] | VAV_BOT WITH REHEAT Supply Flow Rate [cfm] | 19112.2976 | 18179.9904 | 19663.2064 | 18730.8992 | 20235.304 | 19260.6192 |  |  |  |  | 2021-05-06
VA_LO_VAV_MID WITH REHEAT Supply Flow Rate [cfm] | VAV_MID WITH REHEAT Supply Flow Rate [cfm] | 178346.1299 | 169383.2675 | 182859.3443 | 173896.4819 | 186842.8387 | 177392.6339 |  |  |  |  | 2021-05-06
VA_LO_VAV_TOP WITH REHEAT Supply Flow Rate [cfm] | VAV_TOP WITH REHEAT Supply Flow Rate [cfm] | 18497.8224 | 17692.648 | 19557.2624 | 18752.088 | 19896.2832 | 19069.92 |  |  |  |  | 2021-05-06
VA_LO_Supply Air Temp. Reset Flag | Supply Air Temp. Reset Flag | No | Yes | Yes | Yes | Yes | Yes |  |  |  |  | 2021-05-06
VA_LO_CAV_BAS OA Rate [cfm] | CAV_BAS OA Rate [cfm] | 2542.8255 | 2542.8255 | 2542.8255 | 2542.8255 | 2542.8255 | 2542.8255 |  |  |  |  | 2021-05-06
VA_LO_VAV_BOT WITH REHEAT OA Rate [cfm] | VAV_BOT WITH REHEAT OA Rate [cfm] | 5377.8022 | 4302.174 | 5377.8022 | 4302.174 | 5377.8022 | 4302.174 |  |  |  |  | 2021-05-06
VA_LO_VAV_MID WITH REHEAT OA Rate [cfm] | VAV_MID WITH REHEAT OA Rate [cfm] | 53777.9373 | 43021.7396 | 53777.9373 | 43021.7396 | 53777.9373 | 43021.7396 |  |  |  |  | 2021-05-06
VA_LO_VAV_TOP WITH REHEAT OA Rate [cfm] | VAV_TOP WITH REHEAT OA Rate [cfm] | 5377.8022 | 4302.174 | 5377.8022 | 4302.174 | 5377.8022 | 4302.174 |  |  |  |  | 2021-05-06
VA_LO_AIRLOOP DATACENTER BASEMENT OA Rate [cfm] | AIRLOOP DATACENTER BASEMENT OA Rate [cfm] | 716.9654 | 716.9654 | 716.9654 | 716.9654 | 716.9654 | 716.9654 |  |  |  |  | 2021-05-06
VA_LO_VAV_bot_WITH_REHEAT ERV Flag | VAV_bot_WITH_REHEAT ERV Flag | Yes | Yes | Yes | Yes | Yes | Yes |  |  |  |  | 2021-05-06
VA_LO_VAV_mid_WITH_REHEAT ERV Flag | VAV_mid_WITH_REHEAT ERV Flag | Yes | Yes | Yes | Yes | Yes | Yes |  |  |  |  | 2021-05-06
VA_LO_VAV_top_WITH_REHEAT ERV Flag | VAV_top_WITH_REHEAT ERV Flag | Yes | Yes | Yes | Yes | Yes | Yes |  |  |  |  | 2021-05-06
VA_LO_COOLSYS1 CHILLER1 Capacity [ton] | COOLSYS1 CHILLER1 Capacity [ton] | 437.349 | 391.8958 | 434.1379 | 389.7303 | 363.4577 | 331.1099 |  |  |  |  | 2021-05-06
VA_LO_COOLSYS1 CHILLER2 Capacity [ton] | COOLSYS1 CHILLER2 Capacity [ton] | 437.349 | 391.8958 | 434.1379 | 389.7303 | 363.4577 | 331.1099 |  |  |  |  | 2021-05-06
VA_LO_TOWERWATERSYS COOLTOWER 1 Capacity [ton] | TOWERWATERSYS COOLTOWER 1 Capacity [ton] | 415.1287 | 371.9802 | 412.0701 | 369.9193 | 345.0898 | 314.3769 |  |  |  |  | 2021-05-06
VA_LO_TOWERWATERSYS COOLTOWER 2 Capacity [ton] | TOWERWATERSYS COOLTOWER 2 Capacity [ton] | 415.1287 | 371.9802 | 412.0701 | 369.9193 | 345.0898 | 314.3769 |  |  |  |  | 2021-05-06
VA_LO_HEATSYS1 BOILER Capacity [MMBTU/h] | HEATSYS1 BOILER Capacity [MMBTU/h] | 3717.8784 | 3317.4877 | 3810.2757 | 3382.3836 | 4500.1534 | 3968.7556 |  |  |  |  | 2021-05-06
VA_LO_COOLSYS1 PUMP Flow Rate [gal/min] | COOLSYS1 PUMP Flow Rate [gal/min] | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 2021-05-06
VA_LO_COOLSYS1 CHILLER1 PUMP Flow Rate [gal/min] | COOLSYS1 CHILLER1 PUMP Flow Rate [gal/min] | 689.432 | 614.9529 | 684.2632 | 611.3581 | 572.2743 | 521.2712 |  |  |  |  | 2021-05-06
VA_LO_COOLSYS1 CHILLER2 PUMP Flow Rate [gal/min] | COOLSYS1 CHILLER2 PUMP Flow Rate [gal/min] | 689.432 | 614.9529 | 684.2632 | 611.3581 | 572.2743 | 521.2712 |  |  |  |  | 2021-05-06
VA_LO_COOLSYS1 PUMP SECONDARY Flow Rate [gal/min] | COOLSYS1 PUMP SECONDARY Flow Rate [gal/min] | 1378.864 | 1229.9058 | 1368.5264 | 1222.7161 | 1144.5502 | 1042.5423 |  |  |  |  | 2021-05-06
VA_LO_HEATSYS1 PUMP Flow Rate [gal/min] | HEATSYS1 PUMP Flow Rate [gal/min] | 763.1439 | 680.9584 | 782.1088 | 694.279 | 923.7156 | 814.64 |  |  |  |  | 2021-05-06
VA_LO_TOWERWATERSYS PUMP Flow Rate [gal/min] | TOWERWATERSYS PUMP Flow Rate [gal/min] | 2412.8947 | 2162.1426 | 2395.1423 | 2150.0963 | 2005.2244 | 1826.7497 |  |  |  |  | 2021-05-06
VA_LO_PLANT CIRC PUMP Flow Rate [gal/min] | PLANT CIRC PUMP Flow Rate [gal/min] | 207.2382 | 206.7072 | 208.9247 | 208.0941 | 212.0789 | 211.2277 |  |  |  |  | 2021-05-06
VA_LO_COOLSYS1 PUMP SECONDARY Pressure setpoint reset [yes,no] | COOLSYS1 PUMP SECONDARY Pressure setpoint reset [yes,no] | pump_ride_on_curve | pump_ride_on_curve | pump_ride_on_curve | pump_ride_on_curve | pump_ride_on_curve | pump_ride_on_curve |  |  |  |  | 2021-05-06
VA_LO_COOLSYS1 CHILLER1 PUMP Pump Power [hp] | COOLSYS1 CHILLER1 PUMP Pump Power [hp] | 3.7192 | 3.2846 | 3.6914 | 3.2654 | 3.0872 | 2.7842 |  |  |  |  | 2021-05-06
VA_LO_COOLSYS1 CHILLER2 PUMP Pump Power [hp] | COOLSYS1 CHILLER2 PUMP Pump Power [hp] | 3.7192 | 3.2846 | 3.6914 | 3.2654 | 3.0872 | 2.7842 |  |  |  |  | 2021-05-06
VA_LO_COOLSYS1 PUMP SECONDARY Pump Power [hp] | COOLSYS1 PUMP SECONDARY Pump Power [hp] | 22.3155 | 19.7076 | 22.1482 | 19.5925 | 18.5233 | 16.7054 |  |  |  |  | 2021-05-06
VA_LO_HEATSYS1 PUMP Pump Power [hp] | HEATSYS1 PUMP Pump Power [hp] | 16.4958 | 14.5736 | 16.9057 | 14.8587 | 19.9667 | 17.4346 |  |  |  |  | 2021-05-06
VA_LO_TOWERWATERSYS PUMP Pump Power [hp] | TOWERWATERSYS PUMP Pump Power [hp] | 43.2004 | 38.3274 | 42.8832 | 38.1156 | 35.9016 | 32.3825 |  |  |  |  | 2021-05-06
VA_LO_PLANT CIRC PUMP Pump Power [hp] | PLANT CIRC PUMP Pump Power [hp] | 4.4719 | 4.4163 | 4.5083 | 4.4459 | 4.5764 | 4.5129 |  |  |  |  | 2021-05-06
VA_LO_Datacenter PLANT CIRC PUMP Pump Power [hp] | Datacenter PLANT CIRC PUMP Pump Power [hp] | 4.4719 | 4.4163 | 4.5083 | 4.4459 | 4.5764 | 4.5129 |  |  |  |  | 2021-05-06
VA_LO_ZN_VAV_BOXes_Max_Reheat_Water_Flow_GPM | ZN_VAV_BOXes_Max_Reheat_Water_Flow_GPM | 431.9138 | 413.8416 | 414.2219 | 397.9581 | 458.5624 | 440.301 |  |  |  |  | 2021-05-06
VA_LO_COOLSYS1 PUMP SECONDARY VSD | COOLSYS1 PUMP SECONDARY VSD | No | No | No | No | No | No |  |  |  |  | 2021-05-06
VA_LO_HEATSYS1 PUMP VSD | HEATSYS1 PUMP VSD | No | No | No | No | No | No |  |  |  |  | 2021-05-06
VA_LO_DATACENTER BASEMENT Cooling Capacity [ton] | DATACENTER BASEMENT Cooling Capacity [ton] | 121.7783 | 121.4223 | 122.375 | 122.0139 | 124.1601 | 123.791 |  |  |  |  | 2021-05-06
VA_LO_DATACENTER BOT Cooling Capacity [ton] | DATACENTER BOT Cooling Capacity [ton] | 2.6143 | 2.5871 | 2.6574 | 2.6341 | 2.7015 | 2.6776 |  |  |  |  | 2021-05-06
VA_LO_DATACENTER MID Cooling Capacity [ton] | DATACENTER MID Cooling Capacity [ton] | 24.8916 | 24.9053 | 25.4168 | 25.213 | 25.8589 | 25.6489 |  |  |  |  | 2021-05-06
VA_LO_DATACENTER TOP Cooling Capacity [ton] | DATACENTER TOP Cooling Capacity [ton] | 2.5225 | 2.5031 | 2.592 | 2.5721 | 2.6321 | 2.6117 |  |  |  |  | 2021-05-06
id | item | Zone3A(VA-Norfolk-VA) ASHRAE901-state_STD2016 | Zone3A(VA-Norfolk-VA) ASHRAE901-state_STD2019 | Zone4A(VA-Richmond-VA) ASHRAE901-state_STD2016 | Zone4A(VA-Richmond-VA) ASHRAE901-state_STD2019 | Zone5A(VA-Elkins-WV) ASHRAE901-state_STD2016 | Zone5A(VA-Elkins-WV) ASHRAE901-state_STD2019 |  |  |  |  | 2021-05-06
VA_RS_PSZ-AC:1 Cooling Capacity [ton] | PSZ-AC:1 Cooling Capacity [ton] | 11.073 | 10.7249 | 10.8825 | 10.5394 | 9.3456 | 8.872 |  |  |  |  | 2021-05-06
VA_RS_PSZ-AC:2 Cooling Capacity [ton] | PSZ-AC:2 Cooling Capacity [ton] | 50.3883 | 47.5666 | 51.3159 | 48.6666 | 44.0328 | 42.0973 |  |  |  |  | 2021-05-06
VA_RS_PSZ-AC:3 Cooling Capacity [ton] | PSZ-AC:3 Cooling Capacity [ton] | 6.7839 | 6.6257 | 6.8422 | 6.6769 | 5.6682 | 5.5067 |  |  |  |  | 2021-05-06
VA_RS_PSZ-AC:4 Cooling Capacity [ton] | PSZ-AC:4 Cooling Capacity [ton] | 5.58 | 5.426 | 5.6101 | 5.4505 | 4.4422 | 4.2758 |  |  |  |  | 2021-05-06
VA_RS_PSZ-AC:1 Supply Flow Rate [cfm] | PSZ-AC:1 Supply Flow Rate [cfm] | 4047.0608 | 3813.984 | 4089.4384 | 3856.3616 | 3835.1728 | 3496.152 |  |  |  |  | 2021-05-06
VA_RS_PSZ-AC:2 Supply Flow Rate [cfm] | PSZ-AC:2 Supply Flow Rate [cfm] | 15128.8032 | 14281.2512 | 15404.2576 | 14599.0832 | 15594.9568 | 14641.4608 |  |  |  |  | 2021-05-06
VA_RS_PSZ-AC:3 Supply Flow Rate [cfm] | PSZ-AC:3 Supply Flow Rate [cfm] | 2288.3904 | 2224.824 | 2330.768 | 2267.2016 | 2224.824 | 2161.2576 |  |  |  |  | 2021-05-06
VA_RS_PSZ-AC:4 Supply Flow Rate [cfm] | PSZ-AC:4 Supply Flow Rate [cfm] | 1758.6704 | 1695.104 | 1801.048 | 1737.4816 | 1652.7264 | 1567.9712 |  |  |  |  | 2021-05-06
VA_RS_PSZ-AC:1 OA Rate [cfm] | PSZ-AC:1 OA Rate [cfm] | 490.669 | 490.669 | 490.669 | 490.669 | 490.669 | 490.669 |  |  |  |  | 2021-05-06
VA_RS_PSZ-AC:2 OA Rate [cfm] | PSZ-AC:2 OA Rate [cfm] | 4005.1282 | 4005.1282 | 4005.1282 | 4005.1282 | 4005.1282 | 4005.1282 |  |  |  |  | 2021-05-06
VA_RS_PSZ-AC:3 OA Rate [cfm] | PSZ-AC:3 OA Rate [cfm] | 377.3937 | 377.3937 | 377.3937 | 377.3937 | 377.3937 | 377.3937 |  |  |  |  | 2021-05-06
VA_RS_PSZ-AC:4 OA Rate [cfm] | PSZ-AC:4 OA Rate [cfm] | 377.3937 | 377.3937 | 377.3937 | 377.3937 | 377.3937 | 377.3937 |  |  |  |  | 2021-05-06
VA_RS_PSZ-AC:1 OA Damper [gravity, motorized] | PSZ-AC:1 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | motorized | motorized |  |  |  |  | 2021-05-06
VA_RS_PSZ-AC:2 OA Damper [gravity, motorized] | PSZ-AC:2 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | motorized | motorized |  |  |  |  | 2021-05-06
VA_RS_PSZ-AC:3 OA Damper [gravity, motorized] | PSZ-AC:3 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | motorized | motorized |  |  |  |  | 2021-05-06
VA_RS_PSZ-AC:4 OA Damper [gravity, motorized] | PSZ-AC:4 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | motorized | motorized |  |  |  |  | 2021-05-06
VA_RS_PSZ-AC:1 Heating Capacity [kBtu/hr] | PSZ-AC:1 Heating Capacity [kBtu/hr] | 175.2156 | 165.1843 | 178.3661 | 168.1324 | 164.8422 | 151.7326 |  |  |  |  | 2021-05-06
VA_RS_PSZ-AC:2 Heating Capacity [kBtu/hr] | PSZ-AC:2 Heating Capacity [kBtu/hr] | 754.962 | 720.1648 | 782.7982 | 749.219 | 807.2915 | 769.1389 |  |  |  |  | 2021-05-06
VA_RS_PSZ-AC:3 Heating Capacity [kBtu/hr] | PSZ-AC:3 Heating Capacity [kBtu/hr] | 104.7608 | 102.0822 | 107.9716 | 105.2558 | 103.7532 | 101.0419 |  |  |  |  | 2021-05-06
VA_RS_PSZ-AC:4 Heating Capacity [kBtu/hr] | PSZ-AC:4 Heating Capacity [kBtu/hr] | 85.0622 | 82.2456 | 87.9988 | 85.1746 | 82.6649 | 79.3067 |  |  |  |  | 2021-05-06
id | item | Zone3A(VA-Norfolk-VA) ASHRAE901-state_STD2016 | Zone3A(VA-Norfolk-VA) ASHRAE901-state_STD2019 | Zone4A(VA-Richmond-VA) ASHRAE901-state_STD2016 | Zone4A(VA-Richmond-VA) ASHRAE901-state_STD2019 | Zone5A(VA-Elkins-WV) ASHRAE901-state_STD2016 | Zone5A(VA-Elkins-WV) ASHRAE901-state_STD2019 |  |  |  |  | 2021-05-06
VA_PS_VAV_POD_1 Cooling Capacity [ton] | VAV_POD_1 Cooling Capacity [ton] | 18.3713 | 17.9536 | 19.3956 | 18.737 | 19.0068 | 18.4003 |  |  |  |  | 2021-05-06
VA_PS_VAV_POD_2 Cooling Capacity [ton] | VAV_POD_2 Cooling Capacity [ton] | 18.2853 | 17.9167 | 19.0897 | 18.4836 | 18.7328 | 18.3446 |  |  |  |  | 2021-05-06
VA_PS_VAV_POD_3 Cooling Capacity [ton] | VAV_POD_3 Cooling Capacity [ton] | 16.703 | 15.8455 | 17.7145 | 16.8481 | 17.2954 | 16.4449 |  |  |  |  | 2021-05-06
VA_PS_VAV_OTHER Cooling Capacity [ton] | VAV_OTHER Cooling Capacity [ton] | 25.2837 | 23.7556 | 27.0894 | 25.5686 | 26.4605 | 23.7189 |  |  |  |  | 2021-05-06
VA_PS_PSZ-AC_1:6 Cooling Capacity [ton] | PSZ-AC_1:6 Cooling Capacity [ton] | 8.2846 | 7.9109 | 8.531 | 8.1625 | 7.861 | 7.6005 |  |  |  |  | 2021-05-06
VA_PS_PSZ-AC_2:5 Cooling Capacity [ton] | PSZ-AC_2:5 Cooling Capacity [ton] | 5.0324 | 4.8718 | 5.4277 | 5.5141 | 5.6024 | 5.5826 |  |  |  |  | 2021-05-06
VA_PS_PSZ-AC_2:7 Cooling Capacity [ton] | PSZ-AC_2:7 Cooling Capacity [ton] | 10.5074 | 10.5074 | 10.5074 | 10.5074 | 10.5074 | 10.5074 |  |  |  |  | 2021-05-06
VA_PS_VAV_POD_1 Supply Flow Rate [cfm] | VAV_POD_1 Supply Flow Rate [cfm] | 5509.088 | 5381.9552 | 5826.92 | 5615.032 | 5699.7872 | 5530.2768 |  |  |  |  | 2021-05-06
VA_PS_VAV_POD_2 Supply Flow Rate [cfm] | VAV_POD_2 Supply Flow Rate [cfm] | 5487.8992 | 5381.9552 | 5720.976 | 5551.4656 | 5615.032 | 5509.088 |  |  |  |  | 2021-05-06
VA_PS_VAV_POD_3 Supply Flow Rate [cfm] | VAV_POD_3 Supply Flow Rate [cfm] | 5021.7456 | 4746.2912 | 5318.3888 | 5064.1232 | 5191.256 | 4936.9904 |  |  |  |  | 2021-05-06
VA_PS_VAV_OTHER Supply Flow Rate [cfm] | VAV_OTHER Supply Flow Rate [cfm] | 7585.5904 | 7119.4368 | 8136.4992 | 7670.3456 | 8094.1216 | 7585.5904 |  |  |  |  | 2021-05-06
VA_PS_PSZ-AC_2:5 Supply Flow Rate [cfm] | PSZ-AC_2:5 Supply Flow Rate [cfm] | 1504.4048 | 1462.0272 | 1631.5376 | 1652.7264 | 1673.9152 | 1673.9152 |  |  |  |  | 2021-05-06
VA_PS_PSZ-AC_1:6 Supply Flow Rate [cfm] | PSZ-AC_1:6 Supply Flow Rate [cfm] | 2479.0896 | 2373.1456 | 2563.8448 | 2457.9008 | 2690.9776 | 2563.8448 |  |  |  |  | 2021-05-06
VA_PS_PSZ-AC_2:7 Supply Flow Rate [cfm] | PSZ-AC_2:7 Supply Flow Rate [cfm] | 3157.1312 | 3157.1312 | 3157.1312 | 3157.1312 | 3157.1312 | 3157.1312 |  |  |  |  | 2021-05-06
VA_PS_Supply Air Temp. Reset Flag | Supply Air Temp. Reset Flag | No | No | Yes | Yes | Yes | Yes |  |  |  |  | 2021-05-06
VA_PS_VAV_POD_1 OA Rate [cfm] | VAV_POD_1 OA Rate [cfm] | 5510.5288 | 5387.5702 | 5820.2667 | 5622.66 | 5702.9867 | 5521.6318 |  |  |  |  | 2021-05-06
VA_PS_VAV_POD_2 OA Rate [cfm] | VAV_POD_2 OA Rate [cfm] | 5487.1152 | 5376.4885 | 5728.5192 | 5546.6346 | 5621.3886 | 5504.935 |  |  |  |  | 2021-05-06
VA_PS_VAV_POD_3 OA Rate [cfm] | VAV_POD_3 OA Rate [cfm] | 5012.2954 | 4754.9786 | 5313.4942 | 5055.8172 | 5189.7728 | 4934.8503 |  |  |  |  | 2021-05-06
VA_PS_VAV_OTHER OA Rate [cfm] | VAV_OTHER OA Rate [cfm] | 3736.1787 | 2988.8921 | 3736.1787 | 2988.8921 | 3736.1787 | 2988.8921 |  |  |  |  | 2021-05-06
VA_PS_PSZ-AC_2:5 OA Rate [cfm] | PSZ-AC_2:5 OA Rate [cfm] | 1152.7343 | 1152.7343 | 1152.7343 | 1152.7343 | 1152.7343 | 1152.7343 |  |  |  |  | 2021-05-06
VA_PS_PSZ-AC_1:6 OA Rate [cfm] | PSZ-AC_1:6 OA Rate [cfm] | 539.9118 | 539.9118 | 539.9118 | 539.9118 | 539.9118 | 539.9118 |  |  |  |  | 2021-05-06
VA_PS_PSZ-AC_2:7 OA Rate [cfm] | PSZ-AC_2:7 OA Rate [cfm] | 3153.0841 | 3153.0841 | 3153.0841 | 3153.0841 | 3153.0841 | 3153.0841 |  |  |  |  | 2021-05-06
VA_PS_VAV_POD_1 OA Damper [gravity, motorized] | VAV_POD_1 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | motorized | motorized |  |  |  |  | 2021-05-06
VA_PS_VAV_POD_2 OA Damper [gravity, motorized] | VAV_POD_2 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | motorized | motorized |  |  |  |  | 2021-05-06
VA_PS_VAV_POD_3 OA Damper [gravity, motorized] | VAV_POD_3 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | motorized | motorized |  |  |  |  | 2021-05-06
VA_PS_VAV_OTHER OA Damper [gravity, motorized] | VAV_OTHER OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | motorized | motorized |  |  |  |  | 2021-05-06
VA_PS_PSZ-AC_2:5 OA Damper [gravity, motorized] | PSZ-AC_2:5 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | motorized | motorized |  |  |  |  | 2021-05-06
VA_PS_PSZ-AC_1:6 OA Damper [gravity, motorized] | PSZ-AC_1:6 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | motorized | motorized |  |  |  |  | 2021-05-06
VA_PS_PSZ-AC_2:7 OA Damper [gravity, motorized] | PSZ-AC_2:7 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | motorized | motorized |  |  |  |  | 2021-05-06
VA_PS_VAV_POD_1 (economizer) | VAV_POD_1 (economizer) | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialDryBulb | DifferentialDryBulb |  |  |  |  | 2021-05-06
VA_PS_VAV_POD_2 (economizer) | VAV_POD_2 (economizer) | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialDryBulb | DifferentialDryBulb |  |  |  |  | 2021-05-06
VA_PS_VAV_POD_3 (economizer) | VAV_POD_3 (economizer) | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialDryBulb | DifferentialDryBulb |  |  |  |  | 2021-05-06
VA_PS_VAV_OTHER (economizer) | VAV_OTHER (economizer) | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialDryBulb | DifferentialDryBulb |  |  |  |  | 2021-05-06
VA_PS_PSZ-AC_2:5 (economizer) | PSZ-AC_2:5 (economizer) | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialDryBulb | DifferentialDryBulb |  |  |  |  | 2021-05-06
VA_PS_PSZ-AC_1:6 (economizer) | PSZ-AC_1:6 (economizer) | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialDryBulb | DifferentialDryBulb |  |  |  |  | 2021-05-06
VA_PS_PSZ-AC_2:7 (economizer) | PSZ-AC_2:7 (economizer) | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialDryBulb | DifferentialDryBulb |  |  |  |  | 2021-05-06
VA_PS_VAV_Pod_1_ERV Flag | VAV_Pod_1_ERV Flag | Yes | Yes | Yes | Yes | Yes | Yes |  |  |  |  | 2021-05-06
VA_PS_VAV_Pod_2_ERV Flag | VAV_Pod_2_ERV Flag | Yes | Yes | Yes | Yes | Yes | Yes |  |  |  |  | 2021-05-06
VA_PS_VAV_Pod_3_ERV Flag | VAV_Pod_3_ERV Flag | Yes | Yes | Yes | Yes | Yes | Yes |  |  |  |  | 2021-05-06
VA_PS_VAV_OTHER_ERV Flag | VAV_OTHER_ERV Flag | Yes | Yes | Yes | Yes | Yes | Yes |  |  |  |  | 2021-05-06
VA_PS_PSZ_AC_2_5_ERV Flag | PSZ_AC_2_5_ERV Flag | Yes | Yes | Yes | No | No | No |  |  |  |  | 2021-05-06
VA_PS_PSZ_AC_2_7_ERV Flag | PSZ_AC_2_7_ERV Flag | Yes | Yes | Yes | Yes | Yes | Yes |  |  |  |  | 2021-05-06
VA_PS_HEATSYS1 Capacity [MMBTU/h] | HEATSYS1 Capacity [MMBTU/h] | 0.89762 | 0.85678 | 0.93097 | 0.88365 | 1.0873 | 1.0454 |  |  |  |  | 2021-05-06
VA_PS_HEATSYS1 Flow Rate [gal/min] | HEATSYS1 Flow Rate [gal/min] | 92.1245 | 87.9324 | 95.5473 | 90.6902 | 111.5864 | 107.2919 |  |  |  |  | 2021-05-06
VA_PS_VAV_POD_1 Fan Power [hp] | VAV_POD_1 Fan Power [hp] | 8.1332 | 7.9483 | 8.5867 | 8.2951 | 8.4146 | 8.1461 |  |  |  |  | 2021-05-06
VA_PS_VAV_POD_2 Fan Power [hp] | VAV_POD_2 Fan Power [hp] | 8.0951 | 7.9319 | 8.4513 | 8.1829 | 8.2933 | 8.1214 |  |  |  |  | 2021-05-06
VA_PS_VAV_POD_3 Fan Power [hp] | VAV_POD_3 Fan Power [hp] | 7.3946 | 7.015 | 7.8425 | 7.4589 | 7.6569 | 7.2804 |  |  |  |  | 2021-05-06
VA_PS_VAV_OTHER Fan Power [hp] | VAV_OTHER Fan Power [hp] | 11.1086 | 10.4373 | 11.902 | 11.2338 | 11.8369 | 11.1054 |  |  |  |  | 2021-05-06
VA_PS_HEATSYS1 Pump Power [hp] | HEATSYS1 Pump Power [hp] | 1.9913 | 1.8819 | 2.0653 | 1.9409 | 2.412 | 2.2962 |  |  |  |  | 2021-05-06
VA_PS_PSZ-AC_1:6 Heating Capacity [kBtu/hr] | PSZ-AC_1:6 Heating Capacity [kBtu/hr] | 199.6248 | 190.8908 | 207.1613 | 198.5923 | 212.4876 | 203.9726 |  |  |  |  | 2021-05-06
VA_PS_PSZ-AC_2:5 Heating Capacity [kBtu/hr] | PSZ-AC_2:5 Heating Capacity [kBtu/hr] | 115.8004 | 114.0168 | 125.6062 | 126.5604 | 139.1847 | 138.9798 |  |  |  |  | 2021-05-06
VA_PS_PSZ-AC_2:7 Heating Capacity [kBtu/hr] | PSZ-AC_2:7 Heating Capacity [kBtu/hr] | 280.5793 | 280.5793 | 295.6441 | 295.6441 | 330.8534 | 330.8534 |  |  |  |  | 2021-05-06
VA_PS_ZN_VAV_BOXes_Max_Reheat_Water_Flow_GPM | ZN_VAV_BOXes_Max_Reheat_Water_Flow_GPM | 65.9498 | 62.8134 | 63.9423 | 60.4709 | 69.5114 | 67.0183 |  |  |  |  | 2021-05-06
id | item | Zone3A(VA-Norfolk-VA) ASHRAE901-state_STD2016 | Zone3A(VA-Norfolk-VA) ASHRAE901-state_STD2019 | Zone4A(VA-Richmond-VA) ASHRAE901-state_STD2016 | Zone4A(VA-Richmond-VA) ASHRAE901-state_STD2019 | Zone5A(VA-Elkins-WV) ASHRAE901-state_STD2016 | Zone5A(VA-Elkins-WV) ASHRAE901-state_STD2019 |  |  |  |  | 2021-05-06
VA_SH_SAC_FRONTOFFICE Cooling Capacity [ton] | SAC_FRONTOFFICE Cooling Capacity [ton] | 2.508 | 2.3661 | 2.4715 | 2.351 | 2.076 | 1.9507 |  |  |  |  | 2021-05-06
VA_SH_SAC_FRONTLOUNGE Cooling Capacity [ton] | SAC_FRONTLOUNGE Cooling Capacity [ton] | 6.119 | 5.8112 | 6.1975 | 5.889 | 5.7536 | 5.5151 |  |  |  |  | 2021-05-06
VA_SH_SAC_MEETINGROOM Cooling Capacity [ton] | SAC_MEETINGROOM Cooling Capacity [ton] | 2.9027 | 2.8169 | 2.9093 | 2.8359 | 2.9724 | 2.8791 |  |  |  |  | 2021-05-06
VA_SH_SAC_EXC_EMPLGE_RESTRM Cooling Capacity [ton] | SAC_EXC_EMPLGE_RESTRM Cooling Capacity [ton] | 6.134 | 6.0927 | 6.2039 | 6.1622 | 5.6643 | 5.6237 |  |  |  |  | 2021-05-06
VA_SH_SAC_FO_ADDAQ SUPPLY FAN Supply Flow Rate [cfm] | SAC_FO_ADDAQ SUPPLY FAN Supply Flow Rate [cfm] | 805.1744 | 741.608 | 783.9856 | 741.608 | 762.7968 | 720.4192 |  |  |  |  | 2021-05-06
VA_SH_SAC_FL_ADDAQ SUPPLY FAN Supply Flow Rate [cfm] | SAC_FL_ADDAQ SUPPLY FAN Supply Flow Rate [cfm] | 1843.4256 | 1737.4816 | 1864.6144 | 1758.6704 | 1864.6144 | 1758.6704 |  |  |  |  | 2021-05-06
VA_SH_SAC_MR_ADDAQ SUPPLY FAN Supply Flow Rate [cfm] | SAC_MR_ADDAQ SUPPLY FAN Supply Flow Rate [cfm] | 868.7408 | 847.552 | 868.7408 | 847.552 | 889.9296 | 868.7408 |  |  |  |  | 2021-05-06
VA_SH_SAC_EXC_ADDAQ SUPPLY FAN Supply Flow Rate [cfm] | SAC_EXC_ADDAQ SUPPLY FAN Supply Flow Rate [cfm] | 2140.0688 | 2118.88 | 2203.6352 | 2182.4464 | 2309.5792 | 2288.3904 |  |  |  |  | 2021-05-06
VA_SH_SAC_Exc_EmpLge_RestRm OA Rate [cfm] | SAC_Exc_EmpLge_RestRm OA Rate [cfm] | 199.9928 | 199.9928 | 199.9928 | 199.9928 | 199.9928 | 199.9928 |  |  |  |  | 2021-05-06
VA_SH_SAC_FrontLounge OA Rate [cfm] | SAC_FrontLounge OA Rate [cfm] | 500.0133 | 500.0133 | 500.0133 | 500.0133 | 500.0133 | 500.0133 |  |  |  |  | 2021-05-06
VA_SH_SAC_FrontOffice OA Rate [cfm] | SAC_FrontOffice OA Rate [cfm] | 119.2938 | 119.2938 | 119.2938 | 119.2938 | 119.2938 | 119.2938 |  |  |  |  | 2021-05-06
VA_SH_SAC_MeetingRoom OA Rate [cfm] | SAC_MeetingRoom OA Rate [cfm] | 267.7629 | 267.7629 | 267.7629 | 267.7629 | 267.7629 | 267.7629 |  |  |  |  | 2021-05-06
VA_SH_SAC_FrontLounge OA Damper [gravity, motorized] | SAC_FrontLounge OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | motorized | motorized |  |  |  |  | 2021-05-06
VA_SH_SAC_FrontOffice (economizer) | SAC_FrontOffice (economizer) | No | No | No | No | No | No |  |  |  |  | 2021-05-06
VA_SH_SAC_FrontLounge (economizer) | SAC_FrontLounge (economizer) | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialDryBulb | DifferentialDryBulb |  |  |  |  | 2021-05-06
VA_SH_SAC_MeetingRoom (economizer) | SAC_MeetingRoom (economizer) | No | No | No | No | No | No |  |  |  |  | 2021-05-06
VA_SH_SAC_Exc_EmpLge_RestRm (economizer) | SAC_Exc_EmpLge_RestRm (economizer) | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialDryBulb | DifferentialDryBulb |  |  |  |  | 2021-05-06
VA_SH_SAC_FRONTOFFICE Heating Capacity [kBtu/hr] | SAC_FRONTOFFICE Heating Capacity [kBtu/hr] | 35.618 | 33.4336 | 35.7624 | 33.9715 | 34.8152 | 33.0316 |  |  |  |  | 2021-05-06
VA_SH_SAC_FRONTLOUNGE Heating Capacity [kBtu/hr] | SAC_FRONTLOUNGE Heating Capacity [kBtu/hr] | 93.64 | 90.2421 | 96.6405 | 93.2531 | 99.1768 | 95.8175 |  |  |  |  | 2021-05-06
VA_SH_SAC_MEETINGROOM Heating Capacity [kBtu/hr] | SAC_MEETINGROOM Heating Capacity [kBtu/hr] | 46.0156 | 45.0688 | 47.2542 | 46.4487 | 49.5008 | 48.5407 |  |  |  |  | 2021-05-06
VA_SH_SAC_EXC_EMPLGE_RESTRM Heating Capacity [kBtu/hr] | SAC_EXC_EMPLGE_RESTRM Heating Capacity [kBtu/hr] | 89.4031 | 88.7527 | 91.8048 | 91.1499 | 93.2931 | 92.6291 |  |  |  |  | 2021-05-06
id | item | Zone3A(VA-Norfolk-VA) ASHRAE901-state_STD2016 | Zone3A(VA-Norfolk-VA) ASHRAE901-state_STD2019 | Zone4A(VA-Richmond-VA) ASHRAE901-state_STD2016 | Zone4A(VA-Richmond-VA) ASHRAE901-state_STD2019 | Zone5A(VA-Elkins-WV) ASHRAE901-state_STD2016 | Zone5A(VA-Elkins-WV) ASHRAE901-state_STD2019 |  |  |  |  | 2021-05-06
VA_MA_SPLIT GSW COOLING COIL Cooling Capacity [ton] | SPLIT GSW COOLING COIL Cooling Capacity [ton] | 0.90959 | 0.89918 | 0.93443 | 0.92066 | 0.71127 | 0.69747 |  |  |  |  | 2021-05-06
VA_MA_SPLIT GNW COOLING COIL Cooling Capacity [ton] | SPLIT GNW COOLING COIL Cooling Capacity [ton] | 0.88372 | 0.87333 | 0.9033 | 0.88983 | 0.6776 | 0.66405 |  |  |  |  | 2021-05-06
VA_MA_SPLIT OFFICE COOLING COIL Cooling Capacity [ton] | SPLIT OFFICE COOLING COIL Cooling Capacity [ton] | 1.7618 | 1.6798 | 1.754 | 1.6692 | 1.5419 | 1.3715 |  |  |  |  | 2021-05-06
VA_MA_SPLIT GNE COOLING COIL Cooling Capacity [ton] | SPLIT GNE COOLING COIL Cooling Capacity [ton] | 0.79886 | 0.78775 | 0.80564 | 0.79367 | 0.57612 | 0.56424 |  |  |  |  | 2021-05-06
VA_MA_SPLIT GN1 COOLING COIL Cooling Capacity [ton] | SPLIT GN1 COOLING COIL Cooling Capacity [ton] | 0.69352 | 0.68474 | 0.67826 | 0.66857 | 0.4927 | 0.48328 |  |  |  |  | 2021-05-06
VA_MA_SPLIT GN2 COOLING COIL Cooling Capacity [ton] | SPLIT GN2 COOLING COIL Cooling Capacity [ton] | 0.69207 | 0.6833 | 0.67638 | 0.66674 | 0.49059 | 0.48123 |  |  |  |  | 2021-05-06
VA_MA_SPLIT GS1 COOLING COIL Cooling Capacity [ton] | SPLIT GS1 COOLING COIL Cooling Capacity [ton] | 0.71852 | 0.70948 | 0.71717 | 0.7069 | 0.53668 | 0.52657 |  |  |  |  | 2021-05-06
VA_MA_SPLIT GS2 COOLING COIL Cooling Capacity [ton] | SPLIT GS2 COOLING COIL Cooling Capacity [ton] | 0.75225 | 0.73954 | 0.74847 | 0.7346 | 0.5711 | 0.55614 |  |  |  |  | 2021-05-06
VA_MA_SPLIT MSW COOLING COIL Cooling Capacity [ton] | SPLIT MSW COOLING COIL Cooling Capacity [ton] | 2.0762 | 2.0551 | 2.159 | 2.1285 | 1.7797 | 1.749 |  |  |  |  | 2021-05-06
VA_MA_SPLIT MNW COOLING COIL Cooling Capacity [ton] | SPLIT MNW COOLING COIL Cooling Capacity [ton] | 2.0268 | 2.0062 | 2.0998 | 2.0701 | 1.7199 | 1.6898 |  |  |  |  | 2021-05-06
VA_MA_SPLIT MSE COOLING COIL Cooling Capacity [ton] | SPLIT MSE COOLING COIL Cooling Capacity [ton] | 1.907 | 1.8856 | 1.9231 | 1.8965 | 1.4902 | 1.4157 |  |  |  |  | 2021-05-06
VA_MA_SPLIT MNE COOLING COIL Cooling Capacity [ton] | SPLIT MNE COOLING COIL Cooling Capacity [ton] | 1.7909 | 1.7719 | 1.794 | 1.7709 | 1.3646 | 1.3356 |  |  |  |  | 2021-05-06
VA_MA_SPLIT MN1 COOLING COIL Cooling Capacity [ton] | SPLIT MN1 COOLING COIL Cooling Capacity [ton] | 1.4928 | 1.4768 | 1.4659 | 1.4426 | 1.1387 | 1.1207 |  |  |  |  | 2021-05-06
VA_MA_SPLIT MN2 COOLING COIL Cooling Capacity [ton] | SPLIT MN2 COOLING COIL Cooling Capacity [ton] | 1.489 | 1.4686 | 1.4606 | 1.4376 | 1.1328 | 1.115 |  |  |  |  | 2021-05-06
VA_MA_SPLIT MS1 COOLING COIL Cooling Capacity [ton] | SPLIT MS1 COOLING COIL Cooling Capacity [ton] | 1.5372 | 1.5198 | 1.5316 | 1.5121 | 1.218 | 1.1992 |  |  |  |  | 2021-05-06
VA_MA_SPLIT MS2 COOLING COIL Cooling Capacity [ton] | SPLIT MS2 COOLING COIL Cooling Capacity [ton] | 1.5334 | 1.516 | 1.5265 | 1.5071 | 1.2127 | 1.194 |  |  |  |  | 2021-05-06
VA_MA_SPLIT TSW COOLING COIL Cooling Capacity [ton] | SPLIT TSW COOLING COIL Cooling Capacity [ton] | 1.2701 | 1.2593 | 1.3543 | 1.3375 | 1.1192 | 1.1025 |  |  |  |  | 2021-05-06
VA_MA_SPLIT TNW COOLING COIL Cooling Capacity [ton] | SPLIT TNW COOLING COIL Cooling Capacity [ton] | 1.23 | 1.2199 | 1.3126 | 1.2964 | 1.0782 | 1.0619 |  |  |  |  | 2021-05-06
VA_MA_SPLIT TSE COOLING COIL Cooling Capacity [ton] | SPLIT TSE COOLING COIL Cooling Capacity [ton] | 1.1872 | 1.1766 | 1.2341 | 1.2204 | 0.97559 | 0.96212 |  |  |  |  | 2021-05-06
VA_MA_SPLIT TNE COOLING COIL Cooling Capacity [ton] | SPLIT TNE COOLING COIL Cooling Capacity [ton] | 1.119 | 1.1091 | 1.1695 | 1.1567 | 0.90959 | 0.89703 |  |  |  |  | 2021-05-06
VA_MA_SPLIT TN1 COOLING COIL Cooling Capacity [ton] | SPLIT TN1 COOLING COIL Cooling Capacity [ton] | 0.90766 | 0.89929 | 0.92995 | 0.91844 | 0.73428 | 0.72498 |  |  |  |  | 2021-05-06
VA_MA_SPLIT TN2 COOLING COIL Cooling Capacity [ton] | SPLIT TN2 COOLING COIL Cooling Capacity [ton] | 0.90317 | 0.8948 | 0.95585 | 0.94583 | 0.7278 | 0.71867 |  |  |  |  | 2021-05-06
VA_MA_SPLIT TS1 COOLING COIL Cooling Capacity [ton] | SPLIT TS1 COOLING COIL Cooling Capacity [ton] | 0.98566 | 0.97631 | 1.0202 | 1.0109 | 0.81639 | 0.80566 |  |  |  |  | 2021-05-06
VA_MA_SPLIT TS2 COOLING COIL Cooling Capacity [ton] | SPLIT TS2 COOLING COIL Cooling Capacity [ton] | 0.98763 | 0.97825 | 1.0243 | 1.0133 | 0.81655 | 0.80587 |  |  |  |  | 2021-05-06
VA_MA_Split GN1 Furnace with DX Cooling OA Rate [cfm] | Split GN1 Furnace with DX Cooling OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 |  |  |  |  | 2021-05-06
VA_MA_Split GN2 Furnace with DX Cooling OA Rate [cfm] | Split GN2 Furnace with DX Cooling OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 |  |  |  |  | 2021-05-06
VA_MA_Split GNE Furnace with DX Cooling OA Rate [cfm] | Split GNE Furnace with DX Cooling OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 |  |  |  |  | 2021-05-06
VA_MA_Split GNW Furnace with DX Cooling OA Rate [cfm] | Split GNW Furnace with DX Cooling OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 |  |  |  |  | 2021-05-06
VA_MA_Split GS1 Furnace with DX Cooling OA Rate [cfm] | Split GS1 Furnace with DX Cooling OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 |  |  |  |  | 2021-05-06
VA_MA_Split GS2 Furnace with DX Cooling OA Rate [cfm] | Split GS2 Furnace with DX Cooling OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 |  |  |  |  | 2021-05-06
VA_MA_Split GSW Furnace with DX Cooling OA Rate [cfm] | Split GSW Furnace with DX Cooling OA Rate [cfm] | 56.9945 | 56.9945 | 56.9945 | 56.9945 | 56.9945 | 56.9945 |  |  |  |  | 2021-05-06
VA_MA_Split MN1 Furnace with DX Cooling OA Rate [cfm] | Split MN1 Furnace with DX Cooling OA Rate [cfm] | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824 |  |  |  |  | 2021-05-06
VA_MA_Split MN2 Furnace with DX Cooling OA Rate [cfm] | Split MN2 Furnace with DX Cooling OA Rate [cfm] | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824 |  |  |  |  | 2021-05-06
VA_MA_Split MNE Furnace with DX Cooling OA Rate [cfm] | Split MNE Furnace with DX Cooling OA Rate [cfm] | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824 |  |  |  |  | 2021-05-06
VA_MA_Split MNW Furnace with DX Cooling OA Rate [cfm] | Split MNW Furnace with DX Cooling OA Rate [cfm] | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824 |  |  |  |  | 2021-05-06
VA_MA_Split MS1 Furnace with DX Cooling OA Rate [cfm] | Split MS1 Furnace with DX Cooling OA Rate [cfm] | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824 |  |  |  |  | 2021-05-06
VA_MA_Split MS2 Furnace with DX Cooling OA Rate [cfm] | Split MS2 Furnace with DX Cooling OA Rate [cfm] | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824 |  |  |  |  | 2021-05-06
VA_MA_Split MSE Furnace with DX Cooling OA Rate [cfm] | Split MSE Furnace with DX Cooling OA Rate [cfm] | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824 |  |  |  |  | 2021-05-06
VA_MA_Split MSW Furnace with DX Cooling OA Rate [cfm] | Split MSW Furnace with DX Cooling OA Rate [cfm] | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824 |  |  |  |  | 2021-05-06
VA_MA_Split Office Furnace with DX Cooling OA Rate [cfm] | Split Office Furnace with DX Cooling OA Rate [cfm] | 80.7372 | 80.7372 | 80.7372 | 80.7372 | 80.7372 | 80.7372 |  |  |  |  | 2021-05-06
VA_MA_Split TN1 Furnace with DX Cooling OA Rate [cfm] | Split TN1 Furnace with DX Cooling OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 |  |  |  |  | 2021-05-06
VA_MA_Split TN2 Furnace with DX Cooling OA Rate [cfm] | Split TN2 Furnace with DX Cooling OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 |  |  |  |  | 2021-05-06
VA_MA_Split TNE Furnace with DX Cooling OA Rate [cfm] | Split TNE Furnace with DX Cooling OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 |  |  |  |  | 2021-05-06
VA_MA_Split TNW Furnace with DX Cooling OA Rate [cfm] | Split TNW Furnace with DX Cooling OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 |  |  |  |  | 2021-05-06
VA_MA_Split TS1 Furnace with DX Cooling OA Rate [cfm] | Split TS1 Furnace with DX Cooling OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 |  |  |  |  | 2021-05-06
VA_MA_Split TS2 Furnace with DX Cooling OA Rate [cfm] | Split TS2 Furnace with DX Cooling OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 |  |  |  |  | 2021-05-06
VA_MA_Split TSE Furnace with DX Cooling OA Rate [cfm] | Split TSE Furnace with DX Cooling OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 |  |  |  |  | 2021-05-06
VA_MA_Split TSW Furnace with DX Cooling OA Rate [cfm] | Split TSW Furnace with DX Cooling OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 |  |  |  |  | 2021-05-06
VA_MA_SPLIT GSW HEATING COIL Heating Capacity [kBtu/hr] | SPLIT GSW HEATING COIL Heating Capacity [kBtu/hr] | 7.3451 | 7.2592 | 7.4076 | 7.4666 | 9.3371 | 9.3963 |  |  |  |  | 2021-05-06
VA_MA_SPLIT GNW HEATING COIL Heating Capacity [kBtu/hr] | SPLIT GNW HEATING COIL Heating Capacity [kBtu/hr] | 7.2958 | 7.2054 | 7.344 | 7.4032 | 9.2312 | 9.2905 |  |  |  |  | 2021-05-06
VA_MA_SPLIT OFFICE HEATING COIL Heating Capacity [kBtu/hr] | SPLIT OFFICE HEATING COIL Heating Capacity [kBtu/hr] | 18.6721 | 18.5204 | 18.8464 | 18.9781 | 22.1512 | 22.2428 |  |  |  |  | 2021-05-06
VA_MA_SPLIT GNE HEATING COIL Heating Capacity [kBtu/hr] | SPLIT GNE HEATING COIL Heating Capacity [kBtu/hr] | 7.2958 | 7.2054 | 7.344 | 7.4032 | 9.215 | 9.2743 |  |  |  |  | 2021-05-06
VA_MA_SPLIT GN1 HEATING COIL Heating Capacity [kBtu/hr] | SPLIT GN1 HEATING COIL Heating Capacity [kBtu/hr] | 5.1542 | 5.1135 | 5.2991 | 5.3583 | 6.9126 | 6.972 |  |  |  |  | 2021-05-06
VA_MA_SPLIT GN2 HEATING COIL Heating Capacity [kBtu/hr] | SPLIT GN2 HEATING COIL Heating Capacity [kBtu/hr] | 5.1542 | 5.1135 | 5.2991 | 5.3583 | 6.9121 | 6.9715 |  |  |  |  | 2021-05-06
VA_MA_SPLIT GS1 HEATING COIL Heating Capacity [kBtu/hr] | SPLIT GS1 HEATING COIL Heating Capacity [kBtu/hr] | 5.1125 | 5.076 | 5.2625 | 5.3216 | 6.8936 | 6.9528 |  |  |  |  | 2021-05-06
VA_MA_SPLIT GS2 HEATING COIL Heating Capacity [kBtu/hr] | SPLIT GS2 HEATING COIL Heating Capacity [kBtu/hr] | 5.6008 | 5.5608 | 5.7456 | 5.8069 | 7.3976 | 7.4583 |  |  |  |  | 2021-05-06
VA_MA_SPLIT MSW HEATING COIL Heating Capacity [kBtu/hr] | SPLIT MSW HEATING COIL Heating Capacity [kBtu/hr] | 13.6408 | 13.4722 | 13.1559 | 13.2852 | 15.1642 | 15.2946 |  |  |  |  | 2021-05-06
VA_MA_SPLIT MNW HEATING COIL Heating Capacity [kBtu/hr] | SPLIT MNW HEATING COIL Heating Capacity [kBtu/hr] | 13.73 | 13.5504 | 13.2151 | 13.3441 | 15.1758 | 15.3057 |  |  |  |  | 2021-05-06
VA_MA_SPLIT MSE HEATING COIL Heating Capacity [kBtu/hr] | SPLIT MSE HEATING COIL Heating Capacity [kBtu/hr] | 13.6408 | 13.4722 | 13.1559 | 13.2852 | 15.1253 | 15.2557 |  |  |  |  | 2021-05-06
VA_MA_SPLIT MNE HEATING COIL Heating Capacity [kBtu/hr] | SPLIT MNE HEATING COIL Heating Capacity [kBtu/hr] | 13.73 | 13.5504 | 13.2151 | 13.3441 | 15.1368 | 15.2667 |  |  |  |  | 2021-05-06
VA_MA_SPLIT MN1 HEATING COIL Heating Capacity [kBtu/hr] | SPLIT MN1 HEATING COIL Heating Capacity [kBtu/hr] | 9.7868 | 9.7868 | 10.3123 | 10.3123 | 11.5404 | 11.5404 |  |  |  |  | 2021-05-06
VA_MA_SPLIT MN2 HEATING COIL Heating Capacity [kBtu/hr] | SPLIT MN2 HEATING COIL Heating Capacity [kBtu/hr] | 9.7868 | 9.7868 | 10.3123 | 10.3123 | 11.5404 | 11.5404 |  |  |  |  | 2021-05-06
VA_MA_SPLIT MS1 HEATING COIL Heating Capacity [kBtu/hr] | SPLIT MS1 HEATING COIL Heating Capacity [kBtu/hr] | 9.7868 | 9.7868 | 10.3123 | 10.3123 | 11.5404 | 11.5404 |  |  |  |  | 2021-05-06
VA_MA_SPLIT MS2 HEATING COIL Heating Capacity [kBtu/hr] | SPLIT MS2 HEATING COIL Heating Capacity [kBtu/hr] | 9.7868 | 9.7868 | 10.3123 | 10.3123 | 11.5404 | 11.5404 |  |  |  |  | 2021-05-06
VA_MA_SPLIT TSW HEATING COIL Heating Capacity [kBtu/hr] | SPLIT TSW HEATING COIL Heating Capacity [kBtu/hr] | 10.1084 | 10.0256 | 9.4923 | 9.5538 | 10.9654 | 11.0273 |  |  |  |  | 2021-05-06
VA_MA_SPLIT TNW HEATING COIL Heating Capacity [kBtu/hr] | SPLIT TNW HEATING COIL Heating Capacity [kBtu/hr] | 10.1606 | 10.0723 | 9.5292 | 9.5907 | 10.9778 | 11.04 |  |  |  |  | 2021-05-06
VA_MA_SPLIT TSE HEATING COIL Heating Capacity [kBtu/hr] | SPLIT TSE HEATING COIL Heating Capacity [kBtu/hr] | 10.1084 | 10.0256 | 9.4923 | 9.5538 | 10.9444 | 11.0063 |  |  |  |  | 2021-05-06
VA_MA_SPLIT TNE HEATING COIL Heating Capacity [kBtu/hr] | SPLIT TNE HEATING COIL Heating Capacity [kBtu/hr] | 10.1606 | 10.0723 | 9.5292 | 9.5907 | 10.9568 | 11.0189 |  |  |  |  | 2021-05-06
VA_MA_SPLIT TN1 HEATING COIL Heating Capacity [kBtu/hr] | SPLIT TN1 HEATING COIL Heating Capacity [kBtu/hr] | 7.632 | 7.5963 | 7.2459 | 7.3073 | 8.7254 | 8.7874 |  |  |  |  | 2021-05-06
VA_MA_SPLIT TN2 HEATING COIL Heating Capacity [kBtu/hr] | SPLIT TN2 HEATING COIL Heating Capacity [kBtu/hr] | 7.632 | 7.5963 | 7.2459 | 7.3073 | 8.7247 | 8.7868 |  |  |  |  | 2021-05-06
VA_MA_SPLIT TS1 HEATING COIL Heating Capacity [kBtu/hr] | SPLIT TS1 HEATING COIL Heating Capacity [kBtu/hr] | 7.5727 | 7.5424 | 7.2016 | 7.2629 | 8.7066 | 8.7685 |  |  |  |  | 2021-05-06
VA_MA_SPLIT TS2 HEATING COIL Heating Capacity [kBtu/hr] | SPLIT TS2 HEATING COIL Heating Capacity [kBtu/hr] | 7.5727 | 7.5424 | 7.2016 | 7.2629 | 8.706 | 8.7679 |  |  |  |  | 2021-05-06
VA_MA_Split_GSW ERV Flag | Split_GSW ERV Flag | No | Yes | Yes | Yes | Yes | Yes |  |  |  |  | 2021-05-06
VA_MA_Split_GNW ERV Flag | Split_GNW ERV Flag | No | Yes | Yes | Yes | Yes | Yes |  |  |  |  | 2021-05-06
VA_MA_Split_GNE ERV Flag | Split_GNE ERV Flag | No | Yes | Yes | Yes | Yes | Yes |  |  |  |  | 2021-05-06
VA_MA_Split_GN1 ERV Flag | Split_GN1 ERV Flag | No | Yes | Yes | Yes | Yes | Yes |  |  |  |  | 2021-05-06
VA_MA_Split_GN2 ERV Flag | Split_GN2 ERV Flag | No | Yes | Yes | Yes | Yes | Yes |  |  |  |  | 2021-05-06
VA_MA_Split_GS1 ERV Flag | Split_GS1 ERV Flag | No | Yes | Yes | Yes | Yes | Yes |  |  |  |  | 2021-05-06
VA_MA_Split_GS2 ERV Flag | Split_GS2 ERV Flag | No | Yes | Yes | Yes | Yes | Yes |  |  |  |  | 2021-05-06
VA_MA_Split_MSW ERV Flag | Split_MSW ERV Flag | No | Yes | Yes | Yes | Yes | Yes |  |  |  |  | 2021-05-06
VA_MA_Split_MNW ERV Flag | Split_MNW ERV Flag | No | Yes | Yes | Yes | Yes | Yes |  |  |  |  | 2021-05-06
VA_MA_Split_MSE ERV Flag | Split_MSE ERV Flag | No | Yes | Yes | Yes | Yes | Yes |  |  |  |  | 2021-05-06
VA_MA_Split_MNE ERV Flag | Split_MNE ERV Flag | No | Yes | Yes | Yes | Yes | Yes |  |  |  |  | 2021-05-06
VA_MA_Split_MN1 ERV Flag | Split_MN1 ERV Flag | No | Yes | Yes | Yes | Yes | Yes |  |  |  |  | 2021-05-06
VA_MA_Split_MN2 ERV Flag | Split_MN2 ERV Flag | No | Yes | Yes | Yes | Yes | Yes |  |  |  |  | 2021-05-06
VA_MA_Split_MS1 ERV Flag | Split_MS1 ERV Flag | No | Yes | Yes | Yes | Yes | Yes |  |  |  |  | 2021-05-06
VA_MA_Split_MS2 ERV Flag | Split_MS2 ERV Flag | No | Yes | Yes | Yes | Yes | Yes |  |  |  |  | 2021-05-06
VA_MA_Split_TSW ERV Flag | Split_TSW ERV Flag | No | Yes | Yes | Yes | Yes | Yes |  |  |  |  | 2021-05-06
VA_MA_Split_TNW ERV Flag | Split_TNW ERV Flag | No | Yes | Yes | Yes | Yes | Yes |  |  |  |  | 2021-05-06
VA_MA_Split_TSE ERV Flag | Split_TSE ERV Flag | No | Yes | Yes | Yes | Yes | Yes |  |  |  |  | 2021-05-06
VA_MA_Split_TNE ERV Flag | Split_TNE ERV Flag | No | Yes | Yes | Yes | Yes | Yes |  |  |  |  | 2021-05-06
VA_MA_Split_TN1 ERV Flag | Split_TN1 ERV Flag | No | Yes | Yes | Yes | Yes | Yes |  |  |  |  | 2021-05-06
VA_MA_Split_TN2 ERV Flag | Split_TN2 ERV Flag | No | Yes | Yes | Yes | Yes | Yes |  |  |  |  | 2021-05-06
VA_MA_Split_TS1 ERV Flag | Split_TS1 ERV Flag | No | Yes | Yes | Yes | Yes | Yes |  |  |  |  | 2021-05-06
VA_MA_Split_TS2 ERV Flag | Split_TS2 ERV Flag | No | Yes | Yes | Yes | Yes | Yes |  |  |  |  | 2021-05-06
id | item | Zone6A(VT-Burlington-VT) ASHRAE901-state_STD2016 | Zone6A(VT-Burlington-VT) ASHRAE901-state_STD2019 | [8 empty] | 2021-05-06
VT_SO_PSZ-AC:1 Cooling Capacity [ton] | PSZ-AC:1 Cooling Capacity [ton] | 1.6925 | 1.5934 | [8 empty] | 2021-05-06
VT_SO_PSZ-AC:2 Cooling Capacity [ton] | PSZ-AC:2 Cooling Capacity [ton] | 1.4596 | 1.3826 | [8 empty] | 2021-05-06
VT_SO_PSZ-AC:3 Cooling Capacity [ton] | PSZ-AC:3 Cooling Capacity [ton] | 1.0228 | 0.96216 | [8 empty] | 2021-05-06
VT_SO_PSZ-AC:4 Cooling Capacity [ton] | PSZ-AC:4 Cooling Capacity [ton] | 1.3586 | 1.2678 | [8 empty] | 2021-05-06
VT_SO_PSZ-AC:5 Cooling Capacity [ton] | PSZ-AC:5 Cooling Capacity [ton] | 1.2436 | 1.1786 | [8 empty] | 2021-05-06
VT_SO_PSZ-AC:1 Supply Flow Rate [cfm] | PSZ-AC:1 Supply Flow Rate [cfm] | 635.664 | 593.2864 | [8 empty] | 2021-05-06
VT_SO_PSZ-AC:2 Supply Flow Rate [cfm] | PSZ-AC:2 Supply Flow Rate [cfm] | 550.9088 | 529.72 | [8 empty] | 2021-05-06
VT_SO_PSZ-AC:3 Supply Flow Rate [cfm] | PSZ-AC:3 Supply Flow Rate [cfm] | 444.9648 | 423.776 | [8 empty] | 2021-05-06
VT_SO_PSZ-AC:4 Supply Flow Rate [cfm] | PSZ-AC:4 Supply Flow Rate [cfm] | 508.5312 | 466.1536 | [8 empty] | 2021-05-06
VT_SO_PSZ-AC:5 Supply Flow Rate [cfm] | PSZ-AC:5 Supply Flow Rate [cfm] | 529.72 | 508.5312 | [8 empty] | 2021-05-06
VT_SO_PSZ-AC:1 OA Rate [cfm] | PSZ-AC:1 OA Rate [cfm] | 136.9178 | 136.9178 | [8 empty] | 2021-05-06
VT_SO_PSZ-AC:2 OA Rate [cfm] | PSZ-AC:2 OA Rate [cfm] | 103.7925 | 103.7925 | [8 empty] | 2021-05-06
VT_SO_PSZ-AC:3 OA Rate [cfm] | PSZ-AC:3 OA Rate [cfm] | 61.5711 | 61.5711 | [8 empty] | 2021-05-06
VT_SO_PSZ-AC:4 OA Rate [cfm] | PSZ-AC:4 OA Rate [cfm] | 103.7925 | 103.7925 | [8 empty] | 2021-05-06
VT_SO_PSZ-AC:5 OA Rate [cfm] | PSZ-AC:5 OA Rate [cfm] | 61.5711 | 61.5711 | [8 empty] | 2021-05-06
VT_SO_PSZ-AC:1 heating Capacity [kBtu/hr] | PSZ-AC:1 heating Capacity [kBtu/hr] | 16.4514 | 16.4514 | [8 empty] | 2021-05-06
VT_SO_PSZ-AC:2 heating Capacity [kBtu/hr] | PSZ-AC:2 heating Capacity [kBtu/hr] | 22.7613 | 22.5002 | [8 empty] | 2021-05-06
VT_SO_PSZ-AC:3 heating Capacity [kBtu/hr] | PSZ-AC:3 heating Capacity [kBtu/hr] | 13.9099 | 13.7598 | [8 empty] | 2021-05-06
VT_SO_PSZ-AC:4 heating Capacity [kBtu/hr] | PSZ-AC:4 heating Capacity [kBtu/hr] | 22.6882 | 22.4662 | [8 empty] | 2021-05-06
VT_SO_PSZ-AC:5 heating Capacity [kBtu/hr] | PSZ-AC:5 heating Capacity [kBtu/hr] | 13.8505 | 13.7063 | [8 empty] | 2021-05-06
id | item | Zone6A(VT-Burlington-VT) ASHRAE901-state_STD2016 | Zone6A(VT-Burlington-VT) ASHRAE901-state_STD2019 | [8 empty] | 2021-05-06
VT_LO_CAV_BAS Supply Flow Rate [cfm] | CAV_BAS Supply Flow Rate [cfm] | 11717.4064 | 10848.6656 | [8 empty] | 2021-05-06
VT_LO_VAV_BOT WITH REHEAT Supply Flow Rate [cfm] | VAV_BOT WITH REHEAT Supply Flow Rate [cfm] | 19875.0944 | 18773.2768 | [8 empty] | 2021-05-06
VT_LO_VAV_MID WITH REHEAT Supply Flow Rate [cfm] | VAV_MID WITH REHEAT Supply Flow Rate [cfm] | 185084.1683 | 174510.9571 | [8 empty] | 2021-05-06
VT_LO_VAV_TOP WITH REHEAT Supply Flow Rate [cfm] | VAV_TOP WITH REHEAT Supply Flow Rate [cfm] | 19345.3744 | 18328.312 | [8 empty] | 2021-05-06
VT_LO_Supply Air Temp. Reset Flag | Supply Air Temp. Reset Flag | Yes | Yes | [8 empty] | 2021-05-06
VT_LO_CAV_BAS OA Rate [cfm] | CAV_BAS OA Rate [cfm] | 2542.8255 | 2542.8255 | [8 empty] | 2021-05-06
VT_LO_VAV_BOT WITH REHEAT OA Rate [cfm] | VAV_BOT WITH REHEAT OA Rate [cfm] | 5377.8022 | 4302.174 | [8 empty] | 2021-05-06
VT_LO_VAV_MID WITH REHEAT OA Rate [cfm] | VAV_MID WITH REHEAT OA Rate [cfm] | 53777.9373 | 43021.7396 | [8 empty] | 2021-05-06
VT_LO_VAV_TOP WITH REHEAT OA Rate [cfm] | VAV_TOP WITH REHEAT OA Rate [cfm] | 5377.8022 | 4302.174 | [8 empty] | 2021-05-06
VT_LO_AIRLOOP DATACENTER BASEMENT OA Rate [cfm] | AIRLOOP DATACENTER BASEMENT OA Rate [cfm] | 716.9654 | 716.9654 | [8 empty] | 2021-05-06
VT_LO_VAV_bot_WITH_REHEAT ERV Flag | VAV_bot_WITH_REHEAT ERV Flag | Yes | Yes | [8 empty] | 2021-05-06
VT_LO_VAV_mid_WITH_REHEAT ERV Flag | VAV_mid_WITH_REHEAT ERV Flag | Yes | Yes | [8 empty] | 2021-05-06
VT_LO_VAV_top_WITH_REHEAT ERV Flag | VAV_top_WITH_REHEAT ERV Flag | Yes | Yes | [8 empty] | 2021-05-06
VT_LO_COOLSYS1 CHILLER1 Capacity [ton] | COOLSYS1 CHILLER1 Capacity [ton] | 373.3111 | 339.2901 | [8 empty] | 2021-05-06
VT_LO_COOLSYS1 CHILLER2 Capacity [ton] | COOLSYS1 CHILLER2 Capacity [ton] | 373.3111 | 339.2901 | [8 empty] | 2021-05-06
VT_LO_TOWERWATERSYS COOLTOWER 1 Capacity [ton] | TOWERWATERSYS COOLTOWER 1 Capacity [ton] | 354.3933 | 322.0957 | [8 empty] | 2021-05-06
VT_LO_TOWERWATERSYS COOLTOWER 2 Capacity [ton] | TOWERWATERSYS COOLTOWER 2 Capacity [ton] | 354.3933 | 322.0957 | [8 empty] | 2021-05-06
VT_LO_HEATSYS1 BOILER Capacity [MMBTU/h] | HEATSYS1 BOILER Capacity [MMBTU/h] | 5118.4467 | 4503.7054 | [8 empty] | 2021-05-06
VT_LO_COOLSYS1 PUMP Flow Rate [gal/min] | COOLSYS1 PUMP Flow Rate [gal/min] | 0 | 0 | [8 empty] | 2021-05-06
VT_LO_COOLSYS1 CHILLER1 PUMP Flow Rate [gal/min] | COOLSYS1 CHILLER1 PUMP Flow Rate [gal/min] | 587.9662 | 534.2985 | [8 empty] | 2021-05-06
VT_LO_COOLSYS1 CHILLER2 PUMP Flow Rate [gal/min] | COOLSYS1 CHILLER2 PUMP Flow Rate [gal/min] | 587.9662 | 534.2985 | [8 empty] | 2021-05-06
VT_LO_COOLSYS1 PUMP SECONDARY Flow Rate [gal/min] | COOLSYS1 PUMP SECONDARY Flow Rate [gal/min] | 1175.9323 | 1068.5955 | [8 empty] | 2021-05-06
VT_LO_HEATSYS1 PUMP Flow Rate [gal/min] | HEATSYS1 PUMP Flow Rate [gal/min] | 1050.6292 | 924.4447 | [8 empty] | 2021-05-06
VT_LO_TOWERWATERSYS PUMP Flow Rate [gal/min] | TOWERWATERSYS PUMP Flow Rate [gal/min] | 2059.591 | 1871.9232 | [8 empty] | 2021-05-06
VT_LO_PLANT CIRC PUMP Flow Rate [gal/min] | PLANT CIRC PUMP Flow Rate [gal/min] | 208.3604 | 207.216 | [8 empty] | 2021-05-06
VT_LO_COOLSYS1 PUMP SECONDARY Pressure setpoint reset [yes,no] | COOLSYS1 PUMP SECONDARY Pressure setpoint reset [yes,no] | pump_ride_on_curve | pump_ride_on_curve | [8 empty] | 2021-05-06
VT_LO_COOLSYS1 CHILLER1 PUMP Pump Power [hp] | COOLSYS1 CHILLER1 PUMP Pump Power [hp] | 3.1719 | 2.8538 | [8 empty] | 2021-05-06
VT_LO_COOLSYS1 CHILLER2 PUMP Pump Power [hp] | COOLSYS1 CHILLER2 PUMP Pump Power [hp] | 3.1719 | 2.8538 | [8 empty] | 2021-05-06
VT_LO_COOLSYS1 PUMP SECONDARY Pump Power [hp] | COOLSYS1 PUMP SECONDARY Pump Power [hp] | 19.0312 | 17.1229 | [8 empty] | 2021-05-06
VT_LO_HEATSYS1 PUMP Pump Power [hp] | HEATSYS1 PUMP Pump Power [hp] | 22.71 | 19.7846 | [8 empty] | 2021-05-06
VT_LO_TOWERWATERSYS PUMP Pump Power [hp] | TOWERWATERSYS PUMP Pump Power [hp] | 36.8749 | 33.1826 | [8 empty] | 2021-05-06
VT_LO_PLANT CIRC PUMP Pump Power [hp] | PLANT CIRC PUMP Pump Power [hp] | 4.4961 | 4.4272 | [8 empty] | 2021-05-06
VT_LO_Datacenter PLANT CIRC PUMP Pump Power [hp] | Datacenter PLANT CIRC PUMP Pump Power [hp] | 4.4961 | 4.4272 | [8 empty] | 2021-05-06
VT_LO_ZN_VAV_BOXes_Max_Reheat_Water_Flow_GPM | ZN_VAV_BOXes_Max_Reheat_Water_Flow_GPM | 500.269 | 480.618 | [8 empty] | 2021-05-06
VT_LO_COOLSYS1 PUMP SECONDARY VSD | COOLSYS1 PUMP SECONDARY VSD | No | No | [8 empty] | 2021-05-06
VT_LO_HEATSYS1 PUMP VSD | HEATSYS1 PUMP VSD | No | No | [8 empty] | 2021-05-06
VT_LO_DATACENTER BASEMENT Cooling Capacity [ton] | DATACENTER BASEMENT Cooling Capacity [ton] | 121.5393 | 121.1682 | [8 empty] | 2021-05-06
VT_LO_DATACENTER BOT Cooling Capacity [ton] | DATACENTER BOT Cooling Capacity [ton] | 2.6883 | 2.6482 | [8 empty] | 2021-05-06
VT_LO_DATACENTER MID Cooling Capacity [ton] | DATACENTER MID Cooling Capacity [ton] | 25.7777 | 25.3888 | [8 empty] | 2021-05-06
VT_LO_DATACENTER TOP Cooling Capacity [ton] | DATACENTER TOP Cooling Capacity [ton] | 2.6232 | 2.5847 | [8 empty] | 2021-05-06
id | item | Zone6A(VT-Burlington-VT) ASHRAE901-state_STD2016 | Zone6A(VT-Burlington-VT) ASHRAE901-state_STD2019 | [8 empty] | 2021-05-06
VT_RS_PSZ-AC:1 Cooling Capacity [ton] | PSZ-AC:1 Cooling Capacity [ton] | 9.498 | 9.0529 | [8 empty] | 2021-05-06
VT_RS_PSZ-AC:2 Cooling Capacity [ton] | PSZ-AC:2 Cooling Capacity [ton] | 44.661 | 42.9674 | [8 empty] | 2021-05-06
VT_RS_PSZ-AC:3 Cooling Capacity [ton] | PSZ-AC:3 Cooling Capacity [ton] | 5.8058 | 5.6474 | [8 empty] | 2021-05-06
VT_RS_PSZ-AC:4 Cooling Capacity [ton] | PSZ-AC:4 Cooling Capacity [ton] | 4.6311 | 4.4499 | [8 empty] | 2021-05-06
VT_RS_PSZ-AC:1 Supply Flow Rate [cfm] | PSZ-AC:1 Supply Flow Rate [cfm] | 3771.6064 | 3474.9632 | [8 empty] | 2021-05-06
VT_RS_PSZ-AC:2 Supply Flow Rate [cfm] | PSZ-AC:2 Supply Flow Rate [cfm] | 15171.1808 | 14366.0064 | [8 empty] | 2021-05-06
VT_RS_PSZ-AC:3 Supply Flow Rate [cfm] | PSZ-AC:3 Supply Flow Rate [cfm] | 2246.0128 | 2161.2576 | [8 empty] | 2021-05-06
VT_RS_PSZ-AC:4 Supply Flow Rate [cfm] | PSZ-AC:4 Supply Flow Rate [cfm] | 1695.104 | 1589.16 | [8 empty] | 2021-05-06
VT_RS_PSZ-AC:1 OA Rate [cfm] | PSZ-AC:1 OA Rate [cfm] | 490.669 | 490.669 | [8 empty] | 2021-05-06
VT_RS_PSZ-AC:2 OA Rate [cfm] | PSZ-AC:2 OA Rate [cfm] | 4005.1282 | 4005.1282 | [8 empty] | 2021-05-06
VT_RS_PSZ-AC:3 OA Rate [cfm] | PSZ-AC:3 OA Rate [cfm] | 377.3937 | 377.3937 | [8 empty] | 2021-05-06
VT_RS_PSZ-AC:4 OA Rate [cfm] | PSZ-AC:4 OA Rate [cfm] | 377.3937 | 377.3937 | [8 empty] | 2021-05-06
VT_RS_PSZ-AC:1 OA Damper [gravity, motorized] | PSZ-AC:1 OA Damper [gravity, motorized] | motorized | motorized | [8 empty] | 2021-05-06
VT_RS_PSZ-AC:2 OA Damper [gravity, motorized] | PSZ-AC:2 OA Damper [gravity, motorized] | motorized | motorized | [8 empty] | 2021-05-06
VT_RS_PSZ-AC:3 OA Damper [gravity, motorized] | PSZ-AC:3 OA Damper [gravity, motorized] | motorized | motorized | [8 empty] | 2021-05-06
VT_RS_PSZ-AC:4 OA Damper [gravity, motorized] | PSZ-AC:4 OA Damper [gravity, motorized] | motorized | motorized | [8 empty] | 2021-05-06
VT_RS_PSZ-AC:1 Heating Capacity [kBtu/hr] | PSZ-AC:1 Heating Capacity [kBtu/hr] | 177.4889 | 165.0882 | [8 empty] | 2021-05-06
VT_RS_PSZ-AC:2 Heating Capacity [kBtu/hr] | PSZ-AC:2 Heating Capacity [kBtu/hr] | 874.7221 | 842.2828 | [8 empty] | 2021-05-06
VT_RS_PSZ-AC:3 Heating Capacity [kBtu/hr] | PSZ-AC:3 Heating Capacity [kBtu/hr] | 113.564 | 110.5404 | [8 empty] | 2021-05-06
VT_RS_PSZ-AC:4 Heating Capacity [kBtu/hr] | PSZ-AC:4 Heating Capacity [kBtu/hr] | 92.7632 | 89.11 | [8 empty] | 2021-05-06
id | item | Zone6A(VT-Burlington-VT) ASHRAE901-state_STD2016 | Zone6A(VT-Burlington-VT) ASHRAE901-state_STD2019 | [8 empty] | 2021-05-06
VT_PS_VAV_POD_1 Cooling Capacity [ton] | VAV_POD_1 Cooling Capacity [ton] | 18.9723 | 18.2529 | [8 empty] | 2021-05-06
VT_PS_VAV_POD_2 Cooling Capacity [ton] | VAV_POD_2 Cooling Capacity [ton] | 18.6952 | 18.2037 | [8 empty] | 2021-05-06
VT_PS_VAV_POD_3 Cooling Capacity [ton] | VAV_POD_3 Cooling Capacity [ton] | 17.2431 | 16.2141 | [8 empty] | 2021-05-06
VT_PS_VAV_OTHER Cooling Capacity [ton] | VAV_OTHER Cooling Capacity [ton] | 26.1143 | 23.3858 | [8 empty] | 2021-05-06
VT_PS_PSZ-AC_1:6 Cooling Capacity [ton] | PSZ-AC_1:6 Cooling Capacity [ton] | 7.7457 | 7.467 | [8 empty] | 2021-05-06
VT_PS_PSZ-AC_2:5 Cooling Capacity [ton] | PSZ-AC_2:5 Cooling Capacity [ton] | 5.3284 | 5.2463 | [8 empty] | 2021-05-06
VT_PS_PSZ-AC_2:7 Cooling Capacity [ton] | PSZ-AC_2:7 Cooling Capacity [ton] | 10.5074 | 10.5074 | [8 empty] | 2021-05-06
VT_PS_VAV_POD_1 Supply Flow Rate [cfm] | VAV_POD_1 Supply Flow Rate [cfm] | 5699.7872 | 5487.8992 | [8 empty] | 2021-05-06
VT_PS_VAV_POD_2 Supply Flow Rate [cfm] | VAV_POD_2 Supply Flow Rate [cfm] | 5615.032 | 5466.7104 | [8 empty] | 2021-05-06
VT_PS_VAV_POD_3 Supply Flow Rate [cfm] | VAV_POD_3 Supply Flow Rate [cfm] | 5170.0672 | 4873.424 | [8 empty] | 2021-05-06
VT_PS_VAV_OTHER Supply Flow Rate [cfm] | VAV_OTHER Supply Flow Rate [cfm] | 7839.856 | 7267.7584 | [8 empty] | 2021-05-06
VT_PS_PSZ-AC_2:5 Supply Flow Rate [cfm] | PSZ-AC_2:5 Supply Flow Rate [cfm] | 1589.16 | 1567.9712 | [8 empty] | 2021-05-06
VT_PS_PSZ-AC_1:6 Supply Flow Rate [cfm] | PSZ-AC_1:6 Supply Flow Rate [cfm] | 2542.656 | 2436.712 | [8 empty] | 2021-05-06
VT_PS_PSZ-AC_2:7 Supply Flow Rate [cfm] | PSZ-AC_2:7 Supply Flow Rate [cfm] | 3157.1312 | 3157.1312 | [8 empty] | 2021-05-06
VT_PS_Supply Air Temp. Reset Flag | Supply Air Temp. Reset Flag | Yes | Yes | [8 empty] | 2021-05-06
VT_PS_VAV_POD_1 OA Rate [cfm] | VAV_POD_1 OA Rate [cfm] | 5693.2822 | 5477.3896 | [8 empty] | 2021-05-06
VT_PS_VAV_POD_2 OA Rate [cfm] | VAV_POD_2 OA Rate [cfm] | 5610.1374 | 5462.6422 | [8 empty] | 2021-05-06
VT_PS_VAV_POD_3 OA Rate [cfm] | VAV_POD_3 OA Rate [cfm] | 5174.3685 | 4865.5842 | [8 empty] | 2021-05-06
VT_PS_VAV_OTHER OA Rate [cfm] | VAV_OTHER OA Rate [cfm] | 3736.1787 | 2988.8921 | [8 empty] | 2021-05-06
VT_PS_PSZ-AC_2:5 OA Rate [cfm] | PSZ-AC_2:5 OA Rate [cfm] | 1152.7343 | 1152.7343 | [8 empty] | 2021-05-06
VT_PS_PSZ-AC_1:6 OA Rate [cfm] | PSZ-AC_1:6 OA Rate [cfm] | 539.9118 | 539.9118 | [8 empty] | 2021-05-06
VT_PS_PSZ-AC_2:7 OA Rate [cfm] | PSZ-AC_2:7 OA Rate [cfm] | 3153.0841 | 3153.0841 | [8 empty] | 2021-05-06
VT_PS_VAV_POD_1 OA Damper [gravity, motorized] | VAV_POD_1 OA Damper [gravity, motorized] | motorized | motorized | [8 empty] | 2021-05-06
VT_PS_VAV_POD_2 OA Damper [gravity, motorized] | VAV_POD_2 OA Damper [gravity, motorized] | motorized | motorized | [8 empty] | 2021-05-06
VT_PS_VAV_POD_3 OA Damper [gravity, motorized] | VAV_POD_3 OA Damper [gravity, motorized] | motorized | motorized | [8 empty] | 2021-05-06
VT_PS_VAV_OTHER OA Damper [gravity, motorized] | VAV_OTHER OA Damper [gravity, motorized] | motorized | motorized | [8 empty] | 2021-05-06
VT_PS_PSZ-AC_2:5 OA Damper [gravity, motorized] | PSZ-AC_2:5 OA Damper [gravity, motorized] | motorized | motorized | [8 empty] | 2021-05-06
VT_PS_PSZ-AC_1:6 OA Damper [gravity, motorized] | PSZ-AC_1:6 OA Damper [gravity, motorized] | motorized | motorized | [8 empty] | 2021-05-06
VT_PS_PSZ-AC_2:7 OA Damper [gravity, motorized] | PSZ-AC_2:7 OA Damper [gravity, motorized] | motorized | motorized | [8 empty] | 2021-05-06
VT_PS_VAV_POD_1 (economizer) | VAV_POD_1 (economizer) | DifferentialDryBulb | DifferentialDryBulb | [8 empty] | 2021-05-06
VT_PS_VAV_POD_2 (economizer) | VAV_POD_2 (economizer) | DifferentialDryBulb | DifferentialDryBulb | [8 empty] | 2021-05-06
VT_PS_VAV_POD_3 (economizer) | VAV_POD_3 (economizer) | DifferentialDryBulb | DifferentialDryBulb | [8 empty] | 2021-05-06
VT_PS_VAV_OTHER (economizer) | VAV_OTHER (economizer) | DifferentialDryBulb | DifferentialDryBulb | [8 empty] | 2021-05-06
VT_PS_PSZ-AC_2:5 (economizer) | PSZ-AC_2:5 (economizer) | DifferentialDryBulb | DifferentialDryBulb | [8 empty] | 2021-05-06
VT_PS_PSZ-AC_1:6 (economizer) | PSZ-AC_1:6 (economizer) | DifferentialDryBulb | DifferentialDryBulb | [8 empty] | 2021-05-06
VT_PS_PSZ-AC_2:7 (economizer) | PSZ-AC_2:7 (economizer) | DifferentialDryBulb | DifferentialDryBulb | [8 empty] | 2021-05-06
VT_PS_VAV_Pod_1_ERV Flag | VAV_Pod_1_ERV Flag | Yes | Yes | [8 empty] | 2021-05-06
VT_PS_VAV_Pod_2_ERV Flag | VAV_Pod_2_ERV Flag | Yes | Yes | [8 empty] | 2021-05-06
VT_PS_VAV_Pod_3_ERV Flag | VAV_Pod_3_ERV Flag | Yes | Yes | [8 empty] | 2021-05-06
VT_PS_VAV_OTHER_ERV Flag | VAV_OTHER_ERV Flag | Yes | Yes | [8 empty] | 2021-05-06
VT_PS_PSZ_AC_2_5_ERV Flag | PSZ_AC_2_5_ERV Flag | Yes | Yes | [8 empty] | 2021-05-06
VT_PS_PSZ_AC_2_7_ERV Flag | PSZ_AC_2_7_ERV Flag | Yes | Yes | [8 empty] | 2021-05-06
VT_PS_HEATSYS1 Capacity [MMBTU/h] | HEATSYS1 Capacity [MMBTU/h] | 1.2471 | 1.1964 | [8 empty] | 2021-05-06
VT_PS_HEATSYS1 Flow Rate [gal/min] | HEATSYS1 Flow Rate [gal/min] | 127.9925 | 122.7853 | [8 empty] | 2021-05-06
VT_PS_VAV_POD_1 Fan Power [hp] | VAV_POD_1 Fan Power [hp] | 8.3993 | 8.0808 | [8 empty] | 2021-05-06
VT_PS_VAV_POD_2 Fan Power [hp] | VAV_POD_2 Fan Power [hp] | 8.2766 | 8.059 | [8 empty] | 2021-05-06
VT_PS_VAV_POD_3 Fan Power [hp] | VAV_POD_3 Fan Power [hp] | 7.6337 | 7.1782 | [8 empty] | 2021-05-06
VT_PS_VAV_OTHER Fan Power [hp] | VAV_OTHER Fan Power [hp] | 11.4736 | 10.6325 | [8 empty] | 2021-05-06
VT_PS_HEATSYS1 Pump Power [hp] | HEATSYS1 Pump Power [hp] | 2.7666 | 2.6278 | [8 empty] | 2021-05-06
VT_PS_PSZ-AC_1:6 Heating Capacity [kBtu/hr] | PSZ-AC_1:6 Heating Capacity [kBtu/hr] | 219.5226 | 210.2708 | [8 empty] | 2021-05-06
VT_PS_PSZ-AC_2:5 Heating Capacity [kBtu/hr] | PSZ-AC_2:5 Heating Capacity [kBtu/hr] | 154.8337 | 153.9314 | [8 empty] | 2021-05-06
VT_PS_PSZ-AC_2:7 Heating Capacity [kBtu/hr] | PSZ-AC_2:7 Heating Capacity [kBtu/hr] | 378.8593 | 378.8593 | [8 empty] | 2021-05-06
VT_PS_ZN_VAV_BOXes_Max_Reheat_Water_Flow_GPM | ZN_VAV_BOXes_Max_Reheat_Water_Flow_GPM | 77.2511 | 74.6455 | [8 empty] | 2021-05-06
id | item | Zone6A(VT-Burlington-VT) ASHRAE901-state_STD2016 | Zone6A(VT-Burlington-VT) ASHRAE901-state_STD2019 | [8 empty] | 2021-05-06
VT_SH_SAC_FRONTOFFICE Cooling Capacity [ton] | SAC_FRONTOFFICE Cooling Capacity [ton] | 2.0891 | 1.9792 | [8 empty] | 2021-05-06
VT_SH_SAC_FRONTLOUNGE Cooling Capacity [ton] | SAC_FRONTLOUNGE Cooling Capacity [ton] | 5.7061 | 5.4636 | [8 empty] | 2021-05-06
VT_SH_SAC_MEETINGROOM Cooling Capacity [ton] | SAC_MEETINGROOM Cooling Capacity [ton] | 2.8345 | 2.744 | [8 empty] | 2021-05-06
VT_SH_SAC_EXC_EMPLGE_RESTRM Cooling Capacity [ton] | SAC_EXC_EMPLGE_RESTRM Cooling Capacity [ton] | 5.6239 | 5.5782 | [8 empty] | 2021-05-06
VT_SH_SAC_FO_ADDAQ SUPPLY FAN Supply Flow Rate [cfm] | SAC_FO_ADDAQ SUPPLY FAN Supply Flow Rate [cfm] | 741.608 | 699.2304 | [8 empty] | 2021-05-06
VT_SH_SAC_FL_ADDAQ SUPPLY FAN Supply Flow Rate [cfm] | SAC_FL_ADDAQ SUPPLY FAN Supply Flow Rate [cfm] | 1779.8592 | 1673.9152 | [8 empty] | 2021-05-06
VT_SH_SAC_MR_ADDAQ SUPPLY FAN Supply Flow Rate [cfm] | SAC_MR_ADDAQ SUPPLY FAN Supply Flow Rate [cfm] | 847.552 | 826.3632 | [8 empty] | 2021-05-06
VT_SH_SAC_EXC_ADDAQ SUPPLY FAN Supply Flow Rate [cfm] | SAC_EXC_ADDAQ SUPPLY FAN Supply Flow Rate [cfm] | 2182.4464 | 2161.2576 | [8 empty] | 2021-05-06
VT_SH_SAC_Exc_EmpLge_RestRm OA Rate [cfm] | SAC_Exc_EmpLge_RestRm OA Rate [cfm] | 199.9928 | 199.9928 | [8 empty] | 2021-05-06
VT_SH_SAC_FrontLounge OA Rate [cfm] | SAC_FrontLounge OA Rate [cfm] | 500.0133 | 500.0133 | [8 empty] | 2021-05-06
VT_SH_SAC_FrontOffice OA Rate [cfm] | SAC_FrontOffice OA Rate [cfm] | 119.2938 | 119.2938 | [8 empty] | 2021-05-06
VT_SH_SAC_MeetingRoom OA Rate [cfm] | SAC_MeetingRoom OA Rate [cfm] | 267.7629 | 267.7629 | [8 empty] | 2021-05-06
VT_SH_SAC_FrontLounge OA Damper [gravity, motorized] | SAC_FrontLounge OA Damper [gravity, motorized] | motorized | motorized | [8 empty] | 2021-05-06
VT_SH_SAC_FrontOffice (economizer) | SAC_FrontOffice (economizer) | No | No | [8 empty] | 2021-05-06
VT_SH_SAC_FrontLounge (economizer) | SAC_FrontLounge (economizer) | DifferentialDryBulb | DifferentialDryBulb | [8 empty] | 2021-05-06
VT_SH_SAC_MeetingRoom (economizer) | SAC_MeetingRoom (economizer) | No | No | [8 empty] | 2021-05-06
VT_SH_SAC_Exc_EmpLge_RestRm (economizer) | SAC_Exc_EmpLge_RestRm (economizer) | DifferentialDryBulb | DifferentialDryBulb | [8 empty] | 2021-05-06
VT_SH_SAC_FRONTOFFICE Heating Capacity [kBtu/hr] | SAC_FRONTOFFICE Heating Capacity [kBtu/hr] | 37.09 | 35.2995 | [8 empty] | 2021-05-06
VT_SH_SAC_FRONTLOUNGE Heating Capacity [kBtu/hr] | SAC_FRONTLOUNGE Heating Capacity [kBtu/hr] | 106.5255 | 103.0614 | [8 empty] | 2021-05-06
VT_SH_SAC_MEETINGROOM Heating Capacity [kBtu/hr] | SAC_MEETINGROOM Heating Capacity [kBtu/hr] | 53.3708 | 52.383 | [8 empty] | 2021-05-06
VT_SH_SAC_EXC_EMPLGE_RESTRM Heating Capacity [kBtu/hr] | SAC_EXC_EMPLGE_RESTRM Heating Capacity [kBtu/hr] | 96.159 | 95.4075 | [8 empty] | 2021-05-06
id | item | Zone6A(VT-Burlington-VT) ASHRAE901-state_STD2016 | Zone6A(VT-Burlington-VT) ASHRAE901-state_STD2019 | [8 empty] | 2021-05-06
VT_MA_SPLIT GSW COOLING COIL Cooling Capacity [ton] | SPLIT GSW COOLING COIL Cooling Capacity [ton] | 0.767 | 0.7375 | [8 empty] | 2021-05-06
VT_MA_SPLIT GNW COOLING COIL Cooling Capacity [ton] | SPLIT GNW COOLING COIL Cooling Capacity [ton] | 0.71747 | 0.69098 | [8 empty] | 2021-05-06
VT_MA_SPLIT OFFICE COOLING COIL Cooling Capacity [ton] | SPLIT OFFICE COOLING COIL Cooling Capacity [ton] | 1.6487 | 1.4364 | [8 empty] | 2021-05-06
VT_MA_SPLIT GNE COOLING COIL Cooling Capacity [ton] | SPLIT GNE COOLING COIL Cooling Capacity [ton] | 0.60929 | 0.5879 | [8 empty] | 2021-05-06
VT_MA_SPLIT GN1 COOLING COIL Cooling Capacity [ton] | SPLIT GN1 COOLING COIL Cooling Capacity [ton] | 0.51614 | 0.50222 | [8 empty] | 2021-05-06
VT_MA_SPLIT GN2 COOLING COIL Cooling Capacity [ton] | SPLIT GN2 COOLING COIL Cooling Capacity [ton] | 0.51384 | 0.50007 | [8 empty] | 2021-05-06
VT_MA_SPLIT GS1 COOLING COIL Cooling Capacity [ton] | SPLIT GS1 COOLING COIL Cooling Capacity [ton] | 0.57253 | 0.55487 | [8 empty] | 2021-05-06
VT_MA_SPLIT GS2 COOLING COIL Cooling Capacity [ton] | SPLIT GS2 COOLING COIL Cooling Capacity [ton] | 0.6077 | 0.58528 | [8 empty] | 2021-05-06
VT_MA_SPLIT MSW COOLING COIL Cooling Capacity [ton] | SPLIT MSW COOLING COIL Cooling Capacity [ton] | 1.8841 | 1.8137 | [8 empty] | 2021-05-06
VT_MA_SPLIT MNW COOLING COIL Cooling Capacity [ton] | SPLIT MNW COOLING COIL Cooling Capacity [ton] | 1.7888 | 1.724 | [8 empty] | 2021-05-06
VT_MA_SPLIT MSE COOLING COIL Cooling Capacity [ton] | SPLIT MSE COOLING COIL Cooling Capacity [ton] | 1.6365 | 1.5725 | [8 empty] | 2021-05-06
VT_MA_SPLIT MNE COOLING COIL Cooling Capacity [ton] | SPLIT MNE COOLING COIL Cooling Capacity [ton] | 1.4305 | 1.3664 | [8 empty] | 2021-05-06
VT_MA_SPLIT MN1 COOLING COIL Cooling Capacity [ton] | SPLIT MN1 COOLING COIL Cooling Capacity [ton] | 1.1696 | 1.142 | [8 empty] | 2021-05-06
VT_MA_SPLIT MN2 COOLING COIL Cooling Capacity [ton] | SPLIT MN2 COOLING COIL Cooling Capacity [ton] | 1.1632 | 1.136 | [8 empty] | 2021-05-06
VT_MA_SPLIT MS1 COOLING COIL Cooling Capacity [ton] | SPLIT MS1 COOLING COIL Cooling Capacity [ton] | 1.2686 | 1.235 | [8 empty] | 2021-05-06
VT_MA_SPLIT MS2 COOLING COIL Cooling Capacity [ton] | SPLIT MS2 COOLING COIL Cooling Capacity [ton] | 1.2623 | 1.2291 | [8 empty] | 2021-05-06
VT_MA_SPLIT TSW COOLING COIL Cooling Capacity [ton] | SPLIT TSW COOLING COIL Cooling Capacity [ton] | 1.1751 | 1.1353 | [8 empty] | 2021-05-06
VT_MA_SPLIT TNW COOLING COIL Cooling Capacity [ton] | SPLIT TNW COOLING COIL Cooling Capacity [ton] | 1.1141 | 1.0773 | [8 empty] | 2021-05-06
VT_MA_SPLIT TSE COOLING COIL Cooling Capacity [ton] | SPLIT TSE COOLING COIL Cooling Capacity [ton] | 1.0477 | 1.0124 | [8 empty] | 2021-05-06
VT_MA_SPLIT TNE COOLING COIL Cooling Capacity [ton] | SPLIT TNE COOLING COIL Cooling Capacity [ton] | 0.93227 | 0.90872 | [8 empty] | 2021-05-06
VT_MA_SPLIT TN1 COOLING COIL Cooling Capacity [ton] | SPLIT TN1 COOLING COIL Cooling Capacity [ton] | 0.73698 | 0.72199 | [8 empty] | 2021-05-06
VT_MA_SPLIT TN2 COOLING COIL Cooling Capacity [ton] | SPLIT TN2 COOLING COIL Cooling Capacity [ton] | 0.76581 | 0.74956 | [8 empty] | 2021-05-06
VT_MA_SPLIT TS1 COOLING COIL Cooling Capacity [ton] | SPLIT TS1 COOLING COIL Cooling Capacity [ton] | 0.87099 | 0.84672 | [8 empty] | 2021-05-06
VT_MA_SPLIT TS2 COOLING COIL Cooling Capacity [ton] | SPLIT TS2 COOLING COIL Cooling Capacity [ton] | 0.87429 | 0.84876 | [8 empty] | 2021-05-06
VT_MA_Split GN1 Furnace with DX Cooling OA Rate [cfm] | Split GN1 Furnace with DX Cooling OA Rate [cfm] | 54.9913 | 54.9913 | [8 empty] | 2021-05-06
VT_MA_Split GN2 Furnace with DX Cooling OA Rate [cfm] | Split GN2 Furnace with DX Cooling OA Rate [cfm] | 54.9913 | 54.9913 | [8 empty] | 2021-05-06
VT_MA_Split GNE Furnace with DX Cooling OA Rate [cfm] | Split GNE Furnace with DX Cooling OA Rate [cfm] | 54.9913 | 54.9913 | [8 empty] | 2021-05-06
VT_MA_Split GNW Furnace with DX Cooling OA Rate [cfm] | Split GNW Furnace with DX Cooling OA Rate [cfm] | 54.9913 | 54.9913 | [8 empty] | 2021-05-06
VT_MA_Split GS1 Furnace with DX Cooling OA Rate [cfm] | Split GS1 Furnace with DX Cooling OA Rate [cfm] | 54.9913 | 54.9913 | [8 empty] | 2021-05-06
VT_MA_Split GS2 Furnace with DX Cooling OA Rate [cfm] | Split GS2 Furnace with DX Cooling OA Rate [cfm] | 54.9913 | 54.9913 | [8 empty] | 2021-05-06
VT_MA_Split GSW Furnace with DX Cooling OA Rate [cfm] | Split GSW Furnace with DX Cooling OA Rate [cfm] | 56.9945 | 56.9945 | [8 empty] | 2021-05-06
VT_MA_Split MN1 Furnace with DX Cooling OA Rate [cfm] | Split MN1 Furnace with DX Cooling OA Rate [cfm] | 109.9824 | 109.9824 | [8 empty] | 2021-05-06
VT_MA_Split MN2 Furnace with DX Cooling OA Rate [cfm] | Split MN2 Furnace with DX Cooling OA Rate [cfm] | 109.9824 | 109.9824 | [8 empty] | 2021-05-06
VT_MA_Split MNE Furnace with DX Cooling OA Rate [cfm] | Split MNE Furnace with DX Cooling OA Rate [cfm] | 109.9824 | 109.9824 | [8 empty] | 2021-05-06
VT_MA_Split MNW Furnace with DX Cooling OA Rate [cfm] | Split MNW Furnace with DX Cooling OA Rate [cfm] | 109.9824 | 109.9824 | [8 empty] | 2021-05-06
VT_MA_Split MS1 Furnace with DX Cooling OA Rate [cfm] | Split MS1 Furnace with DX Cooling OA Rate [cfm] | 109.9824 | 109.9824 | [8 empty] | 2021-05-06
VT_MA_Split MS2 Furnace with DX Cooling OA Rate [cfm] | Split MS2 Furnace with DX Cooling OA Rate [cfm] | 109.9824 | 109.9824 | [8 empty] | 2021-05-06
VT_MA_Split MSE Furnace with DX Cooling OA Rate [cfm] | Split MSE Furnace with DX Cooling OA Rate [cfm] | 109.9824 | 109.9824 | [8 empty] | 2021-05-06
VT_MA_Split MSW Furnace with DX Cooling OA Rate [cfm] | Split MSW Furnace with DX Cooling OA Rate [cfm] | 109.9824 | 109.9824 | [8 empty] | 2021-05-06
VT_MA_Split Office Furnace with DX Cooling OA Rate [cfm] | Split Office Furnace with DX Cooling OA Rate [cfm] | 80.7372 | 80.7372 | [8 empty] | 2021-05-06
VT_MA_Split TN1 Furnace with DX Cooling OA Rate [cfm] | Split TN1 Furnace with DX Cooling OA Rate [cfm] | 54.9913 | 54.9913 | [8 empty] | 2021-05-06
VT_MA_Split TN2 Furnace with DX Cooling OA Rate [cfm] | Split TN2 Furnace with DX Cooling OA Rate [cfm] | 54.9913 | 54.9913 | [8 empty] | 2021-05-06
VT_MA_Split TNE Furnace with DX Cooling OA Rate [cfm] | Split TNE Furnace with DX Cooling OA Rate [cfm] | 54.9913 | 54.9913 | [8 empty] | 2021-05-06
VT_MA_Split TNW Furnace with DX Cooling OA Rate [cfm] | Split TNW Furnace with DX Cooling OA Rate [cfm] | 54.9913 | 54.9913 | [8 empty] | 2021-05-06
VT_MA_Split TS1 Furnace with DX Cooling OA Rate [cfm] | Split TS1 Furnace with DX Cooling OA Rate [cfm] | 54.9913 | 54.9913 | [8 empty] | 2021-05-06
VT_MA_Split TS2 Furnace with DX Cooling OA Rate [cfm] | Split TS2 Furnace with DX Cooling OA Rate [cfm] | 54.9913 | 54.9913 | [8 empty] | 2021-05-06
VT_MA_Split TSE Furnace with DX Cooling OA Rate [cfm] | Split TSE Furnace with DX Cooling OA Rate [cfm] | 54.9913 | 54.9913 | [8 empty] | 2021-05-06
VT_MA_Split TSW Furnace with DX Cooling OA Rate [cfm] | Split TSW Furnace with DX Cooling OA Rate [cfm] | 54.9913 | 54.9913 | [8 empty] | 2021-05-06
VT_MA_SPLIT GSW HEATING COIL Heating Capacity [kBtu/hr] | SPLIT GSW HEATING COIL Heating Capacity [kBtu/hr] | 11.2738 | 11.3333 | [8 empty] | 2021-05-06
VT_MA_SPLIT GNW HEATING COIL Heating Capacity [kBtu/hr] | SPLIT GNW HEATING COIL Heating Capacity [kBtu/hr] | 11.1814 | 11.241 | [8 empty] | 2021-05-06
VT_MA_SPLIT OFFICE HEATING COIL Heating Capacity [kBtu/hr] | SPLIT OFFICE HEATING COIL Heating Capacity [kBtu/hr] | 24.7485 | 24.8298 | [8 empty] | 2021-05-06
VT_MA_SPLIT GNE HEATING COIL Heating Capacity [kBtu/hr] | SPLIT GNE HEATING COIL Heating Capacity [kBtu/hr] | 11.2064 | 11.2659 | [8 empty] | 2021-05-06
VT_MA_SPLIT GN1 HEATING COIL Heating Capacity [kBtu/hr] | SPLIT GN1 HEATING COIL Heating Capacity [kBtu/hr] | 8.4949 | 8.5544 | [8 empty] | 2021-05-06
VT_MA_SPLIT GN2 HEATING COIL Heating Capacity [kBtu/hr] | SPLIT GN2 HEATING COIL Heating Capacity [kBtu/hr] | 8.4956 | 8.5552 | [8 empty] | 2021-05-06
VT_MA_SPLIT GS1 HEATING COIL Heating Capacity [kBtu/hr] | SPLIT GS1 HEATING COIL Heating Capacity [kBtu/hr] | 8.4362 | 8.4957 | [8 empty] | 2021-05-06
VT_MA_SPLIT GS2 HEATING COIL Heating Capacity [kBtu/hr] | SPLIT GS2 HEATING COIL Heating Capacity [kBtu/hr] | 8.957 | 9.0172 | [8 empty] | 2021-05-06
VT_MA_SPLIT MSW HEATING COIL Heating Capacity [kBtu/hr] | SPLIT MSW HEATING COIL Heating Capacity [kBtu/hr] | 19.4758 | 19.605 | [8 empty] | 2021-05-06
VT_MA_SPLIT MNW HEATING COIL Heating Capacity [kBtu/hr] | SPLIT MNW HEATING COIL Heating Capacity [kBtu/hr] | 19.5766 | 19.7059 | [8 empty] | 2021-05-06
VT_MA_SPLIT MSE HEATING COIL Heating Capacity [kBtu/hr] | SPLIT MSE HEATING COIL Heating Capacity [kBtu/hr] | 19.5346 | 19.6639 | [8 empty] | 2021-05-06
VT_MA_SPLIT MNE HEATING COIL Heating Capacity [kBtu/hr] | SPLIT MNE HEATING COIL Heating Capacity [kBtu/hr] | 19.6355 | 19.7648 | [8 empty] | 2021-05-06
VT_MA_SPLIT MN1 HEATING COIL Heating Capacity [kBtu/hr] | SPLIT MN1 HEATING COIL Heating Capacity [kBtu/hr] | 14.0443 | 14.1706 | [8 empty] | 2021-05-06
VT_MA_SPLIT MN2 HEATING COIL Heating Capacity [kBtu/hr] | SPLIT MN2 HEATING COIL Heating Capacity [kBtu/hr] | 14.0459 | 14.1722 | [8 empty] | 2021-05-06
VT_MA_SPLIT MS1 HEATING COIL Heating Capacity [kBtu/hr] | SPLIT MS1 HEATING COIL Heating Capacity [kBtu/hr] | 13.9538 | 14.0801 | [8 empty] | 2021-05-06
VT_MA_SPLIT MS2 HEATING COIL Heating Capacity [kBtu/hr] | SPLIT MS2 HEATING COIL Heating Capacity [kBtu/hr] | 13.9554 | 14.0816 | [8 empty] | 2021-05-06
VT_MA_SPLIT TSW HEATING COIL Heating Capacity [kBtu/hr] | SPLIT TSW HEATING COIL Heating Capacity [kBtu/hr] | 13.7818 | 13.8439 | [8 empty] | 2021-05-06
VT_MA_SPLIT TNW HEATING COIL Heating Capacity [kBtu/hr] | SPLIT TNW HEATING COIL Heating Capacity [kBtu/hr] | 13.8427 | 13.9049 | [8 empty] | 2021-05-06
VT_MA_SPLIT TSE HEATING COIL Heating Capacity [kBtu/hr] | SPLIT TSE HEATING COIL Heating Capacity [kBtu/hr] | 13.8132 | 13.8753 | [8 empty] | 2021-05-06
VT_MA_SPLIT TNE HEATING COIL Heating Capacity [kBtu/hr] | SPLIT TNE HEATING COIL Heating Capacity [kBtu/hr] | 13.8741 | 13.9363 | [8 empty] | 2021-05-06
VT_MA_SPLIT TN1 HEATING COIL Heating Capacity [kBtu/hr] | SPLIT TN1 HEATING COIL Heating Capacity [kBtu/hr] | 10.8769 | 10.939 | [8 empty] | 2021-05-06
VT_MA_SPLIT TN2 HEATING COIL Heating Capacity [kBtu/hr] | SPLIT TN2 HEATING COIL Heating Capacity [kBtu/hr] | 10.8777 | 10.9398 | [8 empty] | 2021-05-06
VT_MA_SPLIT TS1 HEATING COIL Heating Capacity [kBtu/hr] | SPLIT TS1 HEATING COIL Heating Capacity [kBtu/hr] | 10.8094 | 10.8715 | [8 empty] | 2021-05-06
VT_MA_SPLIT TS2 HEATING COIL Heating Capacity [kBtu/hr] | SPLIT TS2 HEATING COIL Heating Capacity [kBtu/hr] | 10.8103 | 10.8723 | [8 empty] | 2021-05-06
VT_MA_Split_GSW ERV Flag | Split_GSW ERV Flag | Yes | Yes | [8 empty] | 2021-05-06
VT_MA_Split_GNW ERV Flag | Split_GNW ERV Flag | Yes | Yes | [8 empty] | 2021-05-06
VT_MA_Split_GNE ERV Flag | Split_GNE ERV Flag | Yes | Yes | [8 empty] | 2021-05-06
VT_MA_Split_GN1 ERV Flag | Split_GN1 ERV Flag | Yes | Yes | [8 empty] | 2021-05-06
VT_MA_Split_GN2 ERV Flag | Split_GN2 ERV Flag | Yes | Yes | [8 empty] | 2021-05-06
VT_MA_Split_GS1 ERV Flag | Split_GS1 ERV Flag | Yes | Yes | [8 empty] | 2021-05-06
VT_MA_Split_GS2 ERV Flag | Split_GS2 ERV Flag | Yes | Yes | [8 empty] | 2021-05-06
VT_MA_Split_MSW ERV Flag | Split_MSW ERV Flag | Yes | Yes | [8 empty] | 2021-05-06
VT_MA_Split_MNW ERV Flag | Split_MNW ERV Flag | Yes | Yes | [8 empty] | 2021-05-06
VT_MA_Split_MSE ERV Flag | Split_MSE ERV Flag | Yes | Yes | [8 empty] | 2021-05-06
VT_MA_Split_MNE ERV Flag | Split_MNE ERV Flag | Yes | Yes | [8 empty] | 2021-05-06
VT_MA_Split_MN1 ERV Flag | Split_MN1 ERV Flag | Yes | Yes | [8 empty] | 2021-05-06
VT_MA_Split_MN2 ERV Flag | Split_MN2 ERV Flag | Yes | Yes | [8 empty] | 2021-05-06
VT_MA_Split_MS1 ERV Flag | Split_MS1 ERV Flag | Yes | Yes | [8 empty] | 2021-05-06
VT_MA_Split_MS2 ERV Flag | Split_MS2 ERV Flag | Yes | Yes | [8 empty] | 2021-05-06
VT_MA_Split_TSW ERV Flag | Split_TSW ERV Flag | Yes | Yes | [8 empty] | 2021-05-06
VT_MA_Split_TNW ERV Flag | Split_TNW ERV Flag | Yes | Yes | [8 empty] | 2021-05-06
VT_MA_Split_TSE ERV Flag | Split_TSE ERV Flag | Yes | Yes | [8 empty] | 2021-05-06
VT_MA_Split_TNE ERV Flag | Split_TNE ERV Flag | Yes | Yes | [8 empty] | 2021-05-06
VT_MA_Split_TN1 ERV Flag | Split_TN1 ERV Flag | Yes | Yes | [8 empty] | 2021-05-06
VT_MA_Split_TN2 ERV Flag | Split_TN2 ERV Flag | Yes | Yes | [8 empty] | 2021-05-06
VT_MA_Split_TS1 ERV Flag | Split_TS1 ERV Flag | Yes | Yes | [8 empty] | 2021-05-06
VT_MA_Split_TS2 ERV Flag | Split_TS2 ERV Flag | Yes | Yes | [8 empty] | 2021-05-06
id | item | Zone4C(WA-Seattle-WA) ASHRAE901-state_STD2016 | Zone4C(WA-Seattle-WA) ASHRAE901-state_STD2019 | Zone5B(WA-Spokane-WA) ASHRAE901-state_STD2016 | Zone5B(WA-Spokane-WA) ASHRAE901-state_STD2019 | Zone5C(WA-Quillayute-WA) ASHRAE901-state_STD2016 | Zone5C(WA-Quillayute-WA) ASHRAE901-state_STD2019 | Zone6B(WA-Kalispell-MT) ASHRAE901-state_STD2016 | Zone6B(WA-Kalispell-MT) ASHRAE901-state_STD2019 |  |  | 2021-05-06
WA_SO_PSZ-AC:1 Cooling Capacity [ton] | PSZ-AC:1 Cooling Capacity [ton] | 1.4477 | 1.3577 | 1.5544 | 1.4472 | 1.3672 | 1.2685 | 1.5561 | 1.4422 |  |  | 2021-05-06
WA_SO_PSZ-AC:2 Cooling Capacity [ton] | PSZ-AC:2 Cooling Capacity [ton] | 1.5557 | 1.4884 | 1.4183 | 1.344 | 1.4903 | 1.4203 | 1.4109 | 1.306 |  |  | 2021-05-06
WA_SO_PSZ-AC:3 Cooling Capacity [ton] | PSZ-AC:3 Cooling Capacity [ton] | 1.0026 | 0.95999 | 1.1377 | 1.0915 | 0.9656 | 0.92323 | 1.1195 | 1.0413 |  |  | 2021-05-06
WA_SO_PSZ-AC:4 Cooling Capacity [ton] | PSZ-AC:4 Cooling Capacity [ton] | 1.1326 | 1.0569 | 1.2732 | 1.1899 | 1.0102 | 0.92761 | 1.217 | 1.1258 |  |  | 2021-05-06
WA_SO_PSZ-AC:5 Cooling Capacity [ton] | PSZ-AC:5 Cooling Capacity [ton] | 1.2335 | 1.1891 | 1.3989 | 1.3498 | 1.1739 | 1.1303 | 1.4004 | 1.3138 |  |  | 2021-05-06
WA_SO_PSZ-AC:1 Supply Flow Rate [cfm] | PSZ-AC:1 Supply Flow Rate [cfm] | 635.664 | 593.2864 | 699.2304 | 656.8528 | 614.4752 | 572.0976 | 699.2304 | 656.8528 |  |  | 2021-05-06
WA_SO_PSZ-AC:2 Supply Flow Rate [cfm] | PSZ-AC:2 Supply Flow Rate [cfm] | 699.2304 | 678.0416 | 635.664 | 614.4752 | 678.0416 | 635.664 | 635.664 | 593.2864 |  |  | 2021-05-06
WA_SO_PSZ-AC:3 Supply Flow Rate [cfm] | PSZ-AC:3 Supply Flow Rate [cfm] | 444.9648 | 423.776 | 508.5312 | 487.3424 | 444.9648 | 423.776 | 508.5312 | 466.1536 |  |  | 2021-05-06
WA_SO_PSZ-AC:4 Supply Flow Rate [cfm] | PSZ-AC:4 Supply Flow Rate [cfm] | 487.3424 | 466.1536 | 572.0976 | 529.72 | 444.9648 | 423.776 | 550.9088 | 508.5312 |  |  | 2021-05-06
WA_SO_PSZ-AC:5 Supply Flow Rate [cfm] | PSZ-AC:5 Supply Flow Rate [cfm] | 550.9088 | 529.72 | 635.664 | 614.4752 | 529.72 | 508.5312 | 635.664 | 593.2864 |  |  | 2021-05-06
WA_SO_PSZ-AC:1 OA Rate [cfm] | PSZ-AC:1 OA Rate [cfm] | 136.9178 | 136.9178 | 136.9178 | 136.9178 | 136.9178 | 136.9178 | 136.9178 | 136.9178 |  |  | 2021-05-06
WA_SO_PSZ-AC:2 OA Rate [cfm] | PSZ-AC:2 OA Rate [cfm] | 103.7925 | 103.7925 | 103.7925 | 103.7925 | 103.7925 | 103.7925 | 103.7925 | 103.7925 |  |  | 2021-05-06
WA_SO_PSZ-AC:3 OA Rate [cfm] | PSZ-AC:3 OA Rate [cfm] | 61.5711 | 61.5711 | 61.5711 | 61.5711 | 61.5711 | 61.5711 | 61.5711 | 61.5711 |  |  | 2021-05-06
WA_SO_PSZ-AC:4 OA Rate [cfm] | PSZ-AC:4 OA Rate [cfm] | 103.7925 | 103.7925 | 103.7925 | 103.7925 | 103.7925 | 103.7925 | 103.7925 | 103.7925 |  |  | 2021-05-06
WA_SO_PSZ-AC:5 OA Rate [cfm] | PSZ-AC:5 OA Rate [cfm] | 61.5711 | 61.5711 | 61.5711 | 61.5711 | 61.5711 | 61.5711 | 61.5711 | 61.5711 |  |  | 2021-05-06
WA_SO_PSZ-AC:1 heating Capacity [kBtu/hr] | PSZ-AC:1 heating Capacity [kBtu/hr] | 11.624 | 11.624 | 13.6646 | 13.6646 | 11.8229 | 11.8229 | 15.1454 | 15.1133 |  |  | 2021-05-06
WA_SO_PSZ-AC:2 heating Capacity [kBtu/hr] | PSZ-AC:2 heating Capacity [kBtu/hr] | 14.2934 | 14.142 | 18.5076 | 18.2891 | 13.5503 | 13.3983 | 20.9082 | 20.6508 |  |  | 2021-05-06
WA_SO_PSZ-AC:3 heating Capacity [kBtu/hr] | PSZ-AC:3 heating Capacity [kBtu/hr] | 8.7753 | 8.6878 | 11.2704 | 11.1446 | 8.2439 | 8.1568 | 12.724 | 12.5769 |  |  | 2021-05-06
WA_SO_PSZ-AC:4 heating Capacity [kBtu/hr] | PSZ-AC:4 heating Capacity [kBtu/hr] | 14.2053 | 14.0758 | 18.4028 | 18.2167 | 13.4559 | 13.3272 | 20.8238 | 20.6061 |  |  | 2021-05-06
WA_SO_PSZ-AC:5 heating Capacity [kBtu/hr] | PSZ-AC:5 heating Capacity [kBtu/hr] | 8.7482 | 8.6644 | 11.2205 | 11.0996 | 8.2215 | 8.1374 | 12.6736 | 12.5314 |  |  | 2021-05-06
id | item | Zone4C(WA-Seattle-WA) ASHRAE901-state_STD2016 | Zone4C(WA-Seattle-WA) ASHRAE901-state_STD2019 | Zone5B(WA-Spokane-WA) ASHRAE901-state_STD2016 | Zone5B(WA-Spokane-WA) ASHRAE901-state_STD2019 | Zone5C(WA-Quillayute-WA) ASHRAE901-state_STD2016 | Zone5C(WA-Quillayute-WA) ASHRAE901-state_STD2019 | Zone6B(WA-Kalispell-MT) ASHRAE901-state_STD2016 | Zone6B(WA-Kalispell-MT) ASHRAE901-state_STD2019 |  |  | 2021-05-06
WA_LO_CAV_BAS Supply Flow Rate [cfm] | CAV_BAS Supply Flow Rate [cfm] | 11780.9728 | 10912.232 | 12734.4688 | 11780.9728 | 11611.4624 | 10763.9104 | 12903.9792 | 11929.2944 |  |  | 2021-05-06
WA_LO_VAV_BOT WITH REHEAT Supply Flow Rate [cfm] | VAV_BOT WITH REHEAT Supply Flow Rate [cfm] | 19345.3744 | 18413.0672 | 21676.1424 | 20680.2688 | 18942.7872 | 18031.6688 | 21443.0656 | 20235.304 |  |  | 2021-05-06
WA_LO_VAV_MID WITH REHEAT Supply Flow Rate [cfm] | VAV_MID WITH REHEAT Supply Flow Rate [cfm] | 178367.3187 | 169468.0227 | 202692.0611 | 193199.4787 | 174171.9363 | 165272.6402 | 198305.9795 | 186652.1395 |  |  | 2021-05-06
WA_LO_VAV_TOP WITH REHEAT Supply Flow Rate [cfm] | VAV_TOP WITH REHEAT Supply Flow Rate [cfm] | 18561.3888 | 17777.4032 | 21337.1216 | 20468.3808 | 18095.2352 | 17311.2496 | 21209.9888 | 20065.7936 |  |  | 2021-05-06
WA_LO_Supply Air Temp. Reset Flag | Supply Air Temp. Reset Flag | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  |  | 2021-05-06
WA_LO_CAV_BAS OA Rate [cfm] | CAV_BAS OA Rate [cfm] | 2542.8255 | 2542.8255 | 2542.8255 | 2542.8255 | 2542.8255 | 2542.8255 | 2542.8255 | 2542.8255 |  |  | 2021-05-06
WA_LO_VAV_BOT WITH REHEAT OA Rate [cfm] | VAV_BOT WITH REHEAT OA Rate [cfm] | 5377.8022 | 4302.174 | 5377.8022 | 4302.174 | 5377.8022 | 4302.174 | 5377.8022 | 4302.174 |  |  | 2021-05-06
WA_LO_VAV_MID WITH REHEAT OA Rate [cfm] | VAV_MID WITH REHEAT OA Rate [cfm] | 53777.9373 | 43021.7396 | 53777.9373 | 43021.7396 | 53777.9373 | 43021.7396 | 53777.9373 | 43021.7396 |  |  | 2021-05-06
WA_LO_VAV_TOP WITH REHEAT OA Rate [cfm] | VAV_TOP WITH REHEAT OA Rate [cfm] | 5377.8022 | 4302.174 | 5377.8022 | 4302.174 | 5377.8022 | 4302.174 | 5377.8022 | 4302.174 |  |  | 2021-05-06
WA_LO_AIRLOOP DATACENTER BASEMENT OA Rate [cfm] | AIRLOOP DATACENTER BASEMENT OA Rate [cfm] | 716.9654 | 716.9654 | 716.9654 | 716.9654 | 716.9654 | 716.9654 | 716.9654 | 716.9654 |  |  | 2021-05-06
WA_LO_VAV_bot_WITH_REHEAT ERV Flag | VAV_bot_WITH_REHEAT ERV Flag | No | No | No | No | No | No | No | No |  |  | 2021-05-06
WA_LO_VAV_mid_WITH_REHEAT ERV Flag | VAV_mid_WITH_REHEAT ERV Flag | No | No | No | No | No | No | No | No |  |  | 2021-05-06
WA_LO_VAV_top_WITH_REHEAT ERV Flag | VAV_top_WITH_REHEAT ERV Flag | No | No | No | No | No | No | No | No |  |  | 2021-05-06
WA_LO_COOLSYS1 CHILLER1 Capacity [ton] | COOLSYS1 CHILLER1 Capacity [ton] | 294.8668 | 276.5502 | 324.1495 | 300.6995 | 269.3886 | 253.9338 | 312.8666 | 289.8074 |  |  | 2021-05-06
WA_LO_COOLSYS1 CHILLER2 Capacity [ton] | COOLSYS1 CHILLER2 Capacity [ton] | 294.8668 | 276.5502 | 324.1495 | 300.6995 | 269.3886 | 253.9338 | 312.8666 | 289.8074 |  |  | 2021-05-06
WA_LO_TOWERWATERSYS COOLTOWER 1 Capacity [ton] | TOWERWATERSYS COOLTOWER 1 Capacity [ton] | 280.2315 | 262.8295 | 308.0562 | 285.778 | 256.0212 | 241.3269 | 297.3442 | 275.421 |  |  | 2021-05-06
WA_LO_TOWERWATERSYS COOLTOWER 2 Capacity [ton] | TOWERWATERSYS COOLTOWER 2 Capacity [ton] | 280.2315 | 262.8295 | 308.0562 | 285.778 | 256.0212 | 241.3269 | 297.3442 | 275.421 |  |  | 2021-05-06
WA_LO_HEATSYS1 BOILER Capacity [MMBTU/h] | HEATSYS1 BOILER Capacity [MMBTU/h] | 3364.0554 | 3002.2325 | 4340.1498 | 3843.271 | 3294.287 | 2935.0039 | 4808.6209 | 4232.5198 |  |  | 2021-05-06
WA_LO_COOLSYS1 PUMP Flow Rate [gal/min] | COOLSYS1 PUMP Flow Rate [gal/min] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 2021-05-06
WA_LO_COOLSYS1 CHILLER1 PUMP Flow Rate [gal/min] | COOLSYS1 CHILLER1 PUMP Flow Rate [gal/min] | 463.3747 | 432.3398 | 509.5625 | 472.3967 | 423.3542 | 396.6654 | 491.9972 | 455.7285 |  |  | 2021-05-06
WA_LO_COOLSYS1 CHILLER2 PUMP Flow Rate [gal/min] | COOLSYS1 CHILLER2 PUMP Flow Rate [gal/min] | 463.3747 | 432.3398 | 509.5625 | 472.3967 | 423.3542 | 396.6654 | 491.9972 | 455.7285 |  |  | 2021-05-06
WA_LO_COOLSYS1 PUMP SECONDARY Flow Rate [gal/min] | COOLSYS1 PUMP SECONDARY Flow Rate [gal/min] | 926.7478 | 864.6811 | 1019.1235 | 944.7934 | 846.7084 | 793.3309 | 983.996 | 911.4554 |  |  | 2021-05-06
WA_LO_HEATSYS1 PUMP Flow Rate [gal/min] | HEATSYS1 PUMP Flow Rate [gal/min] | 690.5162 | 616.2479 | 890.8722 | 788.8817 | 676.1954 | 602.4486 | 987.0329 | 868.78 |  |  | 2021-05-06
WA_LO_TOWERWATERSYS PUMP Flow Rate [gal/min] | TOWERWATERSYS PUMP Flow Rate [gal/min] | 1666.6615 | 1563.0971 | 1788.392 | 1659.0533 | 1522.6185 | 1435.2658 | 1726.1002 | 1637.9724 |  |  | 2021-05-06
WA_LO_PLANT CIRC PUMP Flow Rate [gal/min] | PLANT CIRC PUMP Flow Rate [gal/min] | 207.1352 | 206.2856 | 221.9109 | 221.0026 | 206.1144 | 205.2664 | 223.1504 | 221.7999 |  |  | 2021-05-06
WA_LO_COOLSYS1 PUMP SECONDARY Pressure setpoint reset [yes,no] | COOLSYS1 PUMP SECONDARY Pressure setpoint reset [yes,no] | pump_ride_on_curve | pump_ride_on_curve | pump_ride_on_curve | pump_ride_on_curve | pump_ride_on_curve | pump_ride_on_curve | pump_ride_on_curve | pump_ride_on_curve |  |  | 2021-05-06
WA_LO_COOLSYS1 CHILLER1 PUMP Pump Power [hp] | COOLSYS1 CHILLER1 PUMP Pump Power [hp] | 2.4997 | 2.3092 | 2.7489 | 2.5232 | 2.2838 | 2.1187 | 2.6542 | 2.4342 |  |  | 2021-05-06
WA_LO_COOLSYS1 CHILLER2 PUMP Pump Power [hp] | COOLSYS1 CHILLER2 PUMP Pump Power [hp] | 2.4997 | 2.3092 | 2.7489 | 2.5232 | 2.2838 | 2.1187 | 2.6542 | 2.4342 |  |  | 2021-05-06
WA_LO_COOLSYS1 PUMP SECONDARY Pump Power [hp] | COOLSYS1 PUMP SECONDARY Pump Power [hp] | 14.9984 | 13.8554 | 16.4934 | 15.1391 | 13.7031 | 12.7121 | 15.9249 | 14.6049 |  |  | 2021-05-06
WA_LO_HEATSYS1 PUMP Pump Power [hp] | HEATSYS1 PUMP Pump Power [hp] | 14.9259 | 13.1887 | 19.2567 | 16.8833 | 14.6164 | 12.8933 | 21.3353 | 18.5933 |  |  | 2021-05-06
WA_LO_TOWERWATERSYS PUMP Pump Power [hp] | TOWERWATERSYS PUMP Pump Power [hp] | 29.8394 | 27.7088 | 32.0188 | 29.4084 | 27.2611 | 25.4427 | 30.9043 | 29.0371 |  |  | 2021-05-06
WA_LO_PLANT CIRC PUMP Pump Power [hp] | PLANT CIRC PUMP Pump Power [hp] | 4.4697 | 4.4073 | 4.7885 | 4.7217 | 4.4477 | 4.3855 | 4.8153 | 4.7387 |  |  | 2021-05-06
WA_LO_Datacenter PLANT CIRC PUMP Pump Power [hp] | Datacenter PLANT CIRC PUMP Pump Power [hp] | 4.4697 | 4.4073 | 4.7885 | 4.7217 | 4.4477 | 4.3855 | 4.8153 | 4.7387 |  |  | 2021-05-06
WA_LO_ZN_VAV_BOXes_Max_Reheat_Water_Flow_GPM | ZN_VAV_BOXes_Max_Reheat_Water_Flow_GPM | 379.9429 | 365.0485 | 460.5899 | 441.1082 | 363.4518 | 346.5003 | 481.3045 | 460.5819 |  |  | 2021-05-06
WA_LO_COOLSYS1 PUMP SECONDARY VSD | COOLSYS1 PUMP SECONDARY VSD | No | No | No | No | No | No | No | No |  |  | 2021-05-06
WA_LO_HEATSYS1 PUMP VSD | HEATSYS1 PUMP VSD | No | No | No | No | No | No | No | No |  |  | 2021-05-06
WA_LO_DATACENTER BASEMENT Cooling Capacity [ton] | DATACENTER BASEMENT Cooling Capacity [ton] | 120.5001 | 120.1385 | 129.0174 | 128.6315 | 119.7737 | 119.4135 | 129.7067 | 129.3061 |  |  | 2021-05-06
WA_LO_DATACENTER BOT Cooling Capacity [ton] | DATACENTER BOT Cooling Capacity [ton] | 2.7028 | 2.6786 | 2.8958 | 2.8699 | 2.6996 | 2.6755 | 2.9134 | 2.8637 |  |  | 2021-05-06
WA_LO_DATACENTER MID Cooling Capacity [ton] | DATACENTER MID Cooling Capacity [ton] | 25.8998 | 25.6838 | 27.8101 | 27.5794 | 25.8865 | 25.671 | 27.9972 | 27.5067 |  |  | 2021-05-06
WA_LO_DATACENTER TOP Cooling Capacity [ton] | DATACENTER TOP Cooling Capacity [ton] | 2.6284 | 2.6076 | 2.8307 | 2.8085 | 2.6232 | 2.6024 | 2.8446 | 2.7962 |  |  | 2021-05-06
id | item | Zone4C(WA-Seattle-WA) ASHRAE901-state_STD2016 | Zone4C(WA-Seattle-WA) ASHRAE901-state_STD2019 | Zone5B(WA-Spokane-WA) ASHRAE901-state_STD2016 | Zone5B(WA-Spokane-WA) ASHRAE901-state_STD2019 | Zone5C(WA-Quillayute-WA) ASHRAE901-state_STD2016 | Zone5C(WA-Quillayute-WA) ASHRAE901-state_STD2019 | Zone6B(WA-Kalispell-MT) ASHRAE901-state_STD2016 | Zone6B(WA-Kalispell-MT) ASHRAE901-state_STD2019 |  |  | 2021-05-06
WA_RS_PSZ-AC:1 Cooling Capacity [ton] | PSZ-AC:1 Cooling Capacity [ton] | 8.205 | 7.736 | 9.2328 | 8.5769 | 7.6902 | 7.1423 | 9.1769 | 8.4769 |  |  | 2021-05-06
WA_RS_PSZ-AC:2 Cooling Capacity [ton] | PSZ-AC:2 Cooling Capacity [ton] | 36.1917 | 34.2609 | 42.0628 | 40.0596 | 32.9347 | 30.9347 | 39.9804 | 38.176 |  |  | 2021-05-06
WA_RS_PSZ-AC:3 Cooling Capacity [ton] | PSZ-AC:3 Cooling Capacity [ton] | 5.4997 | 5.3641 | 5.7552 | 5.6171 | 5.259 | 5.1145 | 5.6083 | 5.3866 |  |  | 2021-05-06
WA_RS_PSZ-AC:4 Cooling Capacity [ton] | PSZ-AC:4 Cooling Capacity [ton] | 4.5185 | 4.3756 | 4.6934 | 4.5257 | 4.1734 | 4.0125 | 4.4875 | 4.2477 |  |  | 2021-05-06
WA_RS_PSZ-AC:1 Supply Flow Rate [cfm] | PSZ-AC:1 Supply Flow Rate [cfm] | 3538.5296 | 3241.8864 | 4153.0048 | 3835.1728 | 3326.6416 | 2987.6208 | 3835.1728 | 3496.152 |  |  | 2021-05-06
WA_RS_PSZ-AC:2 Supply Flow Rate [cfm] | PSZ-AC:2 Supply Flow Rate [cfm] | 14705.0272 | 13815.0976 | 16760.3408 | 15700.9008 | 14323.6288 | 13370.1328 | 16018.7328 | 15149.992 |  |  | 2021-05-06
WA_RS_PSZ-AC:3 Supply Flow Rate [cfm] | PSZ-AC:3 Supply Flow Rate [cfm] | 2436.712 | 2373.1456 | 2457.9008 | 2373.1456 | 2373.1456 | 2309.5792 | 2436.712 | 2330.768 |  |  | 2021-05-06
WA_RS_PSZ-AC:4 Supply Flow Rate [cfm] | PSZ-AC:4 Supply Flow Rate [cfm] | 1949.3696 | 1885.8032 | 1928.1808 | 1864.6144 | 1885.8032 | 1801.048 | 1885.8032 | 1758.6704 |  |  | 2021-05-06
WA_RS_PSZ-AC:1 OA Rate [cfm] | PSZ-AC:1 OA Rate [cfm] | 490.669 | 490.669 | 490.669 | 490.669 | 490.669 | 490.669 | 490.669 | 490.669 |  |  | 2021-05-06
WA_RS_PSZ-AC:2 OA Rate [cfm] | PSZ-AC:2 OA Rate [cfm] | 4005.1282 | 4005.1282 | 4005.1282 | 4005.1282 | 4005.1282 | 4005.1282 | 4005.1282 | 4005.1282 |  |  | 2021-05-06
WA_RS_PSZ-AC:3 OA Rate [cfm] | PSZ-AC:3 OA Rate [cfm] | 377.3937 | 377.3937 | 377.3937 | 377.3937 | 377.3937 | 377.3937 | 377.3937 | 377.3937 |  |  | 2021-05-06
WA_RS_PSZ-AC:4 OA Rate [cfm] | PSZ-AC:4 OA Rate [cfm] | 377.3937 | 377.3937 | 377.3937 | 377.3937 | 377.3937 | 377.3937 | 377.3937 | 377.3937 |  |  | 2021-05-06
WA_RS_PSZ-AC:1 OA Damper [gravity, motorized] | PSZ-AC:1 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | motorized | motorized | motorized | motorized |  |  | 2021-05-06
WA_RS_PSZ-AC:2 OA Damper [gravity, motorized] | PSZ-AC:2 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | motorized | motorized | motorized | motorized |  |  | 2021-05-06
WA_RS_PSZ-AC:3 OA Damper [gravity, motorized] | PSZ-AC:3 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | motorized | motorized | motorized | motorized |  |  | 2021-05-06
WA_RS_PSZ-AC:4 OA Damper [gravity, motorized] | PSZ-AC:4 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | motorized | motorized | motorized | motorized |  |  | 2021-05-06
WA_RS_PSZ-AC:1 Heating Capacity [kBtu/hr] | PSZ-AC:1 Heating Capacity [kBtu/hr] | 149.8185 | 136.7868 | 171.8345 | 159.4791 | 142.6242 | 135.1087 | 162.8172 | 149.5723 |  |  | 2021-05-06
WA_RS_PSZ-AC:2 Heating Capacity [kBtu/hr] | PSZ-AC:2 Heating Capacity [kBtu/hr] | 717.9935 | 681.3348 | 818.6195 | 779.324 | 707.2206 | 670.7515 | 822.5503 | 790.5929 |  |  | 2021-05-06
WA_RS_PSZ-AC:3 Heating Capacity [kBtu/hr] | PSZ-AC:3 Heating Capacity [kBtu/hr] | 107.5591 | 105.109 | 107.4597 | 104.73 | 106.0764 | 103.6723 | 109.858 | 106.212 |  |  | 2021-05-06
WA_RS_PSZ-AC:4 Heating Capacity [kBtu/hr] | PSZ-AC:4 Heating Capacity [kBtu/hr] | 89.8894 | 87.1977 | 90.4281 | 87.7168 | 88.029 | 85.3544 | 91.4847 | 87.5797 |  |  | 2021-05-06
id | item | Zone4C(WA-Seattle-WA) ASHRAE901-state_STD2016 | Zone4C(WA-Seattle-WA) ASHRAE901-state_STD2019 | Zone5B(WA-Spokane-WA) ASHRAE901-state_STD2016 | Zone5B(WA-Spokane-WA) ASHRAE901-state_STD2019 | Zone5C(WA-Quillayute-WA) ASHRAE901-state_STD2016 | Zone5C(WA-Quillayute-WA) ASHRAE901-state_STD2019 | Zone6B(WA-Kalispell-MT) ASHRAE901-state_STD2016 | Zone6B(WA-Kalispell-MT) ASHRAE901-state_STD2019 |  |  | 2021-05-06
WA_PS_VAV_POD_1 Cooling Capacity [ton] | VAV_POD_1 Cooling Capacity [ton] | 17.3328 | 16.7188 | 20.8224 | 19.8481 | 14.622 | 14.1069 | 19.4811 | 18.4823 |  |  | 2021-05-06
WA_PS_VAV_POD_2 Cooling Capacity [ton] | VAV_POD_2 Cooling Capacity [ton] | 17.1832 | 16.5556 | 20.765 | 19.663 | 14.488 | 13.9522 | 19.376 | 18.2857 |  |  | 2021-05-06
WA_PS_VAV_POD_3 Cooling Capacity [ton] | VAV_POD_3 Cooling Capacity [ton] | 15.8227 | 15.0998 | 19.0815 | 18.113 | 13.3128 | 12.6991 | 17.9656 | 16.8116 |  |  | 2021-05-06
WA_PS_VAV_OTHER Cooling Capacity [ton] | VAV_OTHER Cooling Capacity [ton] | 20.0299 | 18.3724 | 23.1615 | 21.2085 | 17.5205 | 16.2054 | 22.1242 | 20.0586 |  |  | 2021-05-06
WA_PS_PSZ-AC_1:6 Cooling Capacity [ton] | PSZ-AC_1:6 Cooling Capacity [ton] | 6.7943 | 6.5408 | 7.6534 | 7.3787 | 6.4178 | 6.1686 | 7.4921 | 7.1988 |  |  | 2021-05-06
WA_PS_PSZ-AC_2:5 Cooling Capacity [ton] | PSZ-AC_2:5 Cooling Capacity [ton] | 4.0237 | 4.1159 | 5.1599 | 5.135 | 3.3198 | 3.4123 | 4.9477 | 4.8845 |  |  | 2021-05-06
WA_PS_PSZ-AC_2:7 Cooling Capacity [ton] | PSZ-AC_2:7 Cooling Capacity [ton] | 8.926 | 8.926 | 10.3568 | 10.3568 | 7.5183 | 7.5183 | 9.6506 | 9.6506 |  |  | 2021-05-06
WA_PS_VAV_POD_1 Supply Flow Rate [cfm] | VAV_POD_1 Supply Flow Rate [cfm] | 5826.92 | 5615.032 | 6250.696 | 5954.0528 | 5699.7872 | 5509.088 | 6081.1856 | 5784.5424 |  |  | 2021-05-06
WA_PS_VAV_POD_2 Supply Flow Rate [cfm] | VAV_POD_2 Supply Flow Rate [cfm] | 5763.3536 | 5551.4656 | 6229.5072 | 5890.4864 | 5657.4096 | 5445.5216 | 6059.9968 | 5720.976 |  |  | 2021-05-06
WA_PS_VAV_POD_3 Supply Flow Rate [cfm] | VAV_POD_3 Supply Flow Rate [cfm] | 5318.3888 | 5064.1232 | 5720.976 | 5445.5216 | 5191.256 | 4958.1792 | 5615.032 | 5254.8224 |  |  | 2021-05-06
WA_PS_VAV_OTHER Supply Flow Rate [cfm] | VAV_OTHER Supply Flow Rate [cfm] | 7670.3456 | 7161.8144 | 8750.9744 | 8263.632 | 7331.3248 | 6843.9824 | 8602.6528 | 7988.1776 |  |  | 2021-05-06
WA_PS_PSZ-AC_2:5 Supply Flow Rate [cfm] | PSZ-AC_2:5 Supply Flow Rate [cfm] | 1462.0272 | 1504.4048 | 1779.8592 | 1758.6704 | 1419.6496 | 1462.0272 | 1758.6704 | 1737.4816 |  |  | 2021-05-06
WA_PS_PSZ-AC_1:6 Supply Flow Rate [cfm] | PSZ-AC_1:6 Supply Flow Rate [cfm] | 2521.4672 | 2415.5232 | 2775.7328 | 2648.6 | 2479.0896 | 2373.1456 | 2796.9216 | 2669.7888 |  |  | 2021-05-06
WA_PS_PSZ-AC_2:7 Supply Flow Rate [cfm] | PSZ-AC_2:7 Supply Flow Rate [cfm] | 3157.1312 | 3157.1312 | 3157.1312 | 3157.1312 | 3157.1312 | 3157.1312 | 3157.1312 | 3157.1312 |  |  | 2021-05-06
WA_PS_Supply Air Temp. Reset Flag | Supply Air Temp. Reset Flag | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  |  | 2021-05-06
WA_PS_VAV_POD_1 OA Rate [cfm] | VAV_POD_1 OA Rate [cfm] | 5818.9318 | 5613.4217 | 6248.4712 | 5956.0869 | 5708.5382 | 5507.4353 | 6086.6523 | 5774.5837 |  |  | 2021-05-06
WA_PS_VAV_POD_2 OA Rate [cfm] | VAV_POD_2 OA Rate [cfm] | 5769.35 | 5558.6486 | 6231.2447 | 5900.5299 | 5654.422 | 5447.026 | 6053.8309 | 5713.1785 |  |  | 2021-05-06
WA_PS_VAV_POD_3 OA Rate [cfm] | VAV_POD_3 OA Rate [cfm] | 5312.5619 | 5069.8442 | 5726.0613 | 5422.002 | 5197.4219 | 4957.7978 | 5613.1462 | 5252.5976 |  |  | 2021-05-06
WA_PS_VAV_OTHER OA Rate [cfm] | VAV_OTHER OA Rate [cfm] | 3736.1787 | 2988.8921 | 3736.1787 | 2988.8921 | 3736.1787 | 2988.8921 | 3736.1787 | 2988.8921 |  |  | 2021-05-06
WA_PS_PSZ-AC_2:5 OA Rate [cfm] | PSZ-AC_2:5 OA Rate [cfm] | 1152.7343 | 1152.7343 | 1152.7343 | 1152.7343 | 1152.7343 | 1152.7343 | 1152.7343 | 1152.7343 |  |  | 2021-05-06
WA_PS_PSZ-AC_1:6 OA Rate [cfm] | PSZ-AC_1:6 OA Rate [cfm] | 539.9118 | 539.9118 | 539.9118 | 539.9118 | 539.9118 | 539.9118 | 539.9118 | 539.9118 |  |  | 2021-05-06
WA_PS_PSZ-AC_2:7 OA Rate [cfm] | PSZ-AC_2:7 OA Rate [cfm] | 3153.0841 | 3153.0841 | 3153.0841 | 3153.0841 | 3153.0841 | 3153.0841 | 3153.0841 | 3153.0841 |  |  | 2021-05-06
WA_PS_VAV_POD_1 OA Damper [gravity, motorized] | VAV_POD_1 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | motorized | motorized | motorized | motorized |  |  | 2021-05-06
WA_PS_VAV_POD_2 OA Damper [gravity, motorized] | VAV_POD_2 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | motorized | motorized | motorized | motorized |  |  | 2021-05-06
WA_PS_VAV_POD_3 OA Damper [gravity, motorized] | VAV_POD_3 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | motorized | motorized | motorized | motorized |  |  | 2021-05-06
WA_PS_VAV_OTHER OA Damper [gravity, motorized] | VAV_OTHER OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | motorized | motorized | motorized | motorized |  |  | 2021-05-06
WA_PS_PSZ-AC_2:5 OA Damper [gravity, motorized] | PSZ-AC_2:5 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | motorized | motorized | motorized | motorized |  |  | 2021-05-06
WA_PS_PSZ-AC_1:6 OA Damper [gravity, motorized] | PSZ-AC_1:6 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | motorized | motorized | motorized | motorized |  |  | 2021-05-06
WA_PS_PSZ-AC_2:7 OA Damper [gravity, motorized] | PSZ-AC_2:7 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | motorized | motorized | motorized | motorized |  |  | 2021-05-06
WA_PS_VAV_POD_1 (economizer) | VAV_POD_1 (economizer) | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb |  |  | 2021-05-06
WA_PS_VAV_POD_2 (economizer) | VAV_POD_2 (economizer) | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb |  |  | 2021-05-06
WA_PS_VAV_POD_3 (economizer) | VAV_POD_3 (economizer) | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb |  |  | 2021-05-06
WA_PS_VAV_OTHER (economizer) | VAV_OTHER (economizer) | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb |  |  | 2021-05-06
WA_PS_PSZ-AC_2:5 (economizer) | PSZ-AC_2:5 (economizer) | No | No | DifferentialDryBulb | DifferentialDryBulb | No | No | DifferentialDryBulb | DifferentialDryBulb |  |  | 2021-05-06
WA_PS_PSZ-AC_1:6 (economizer) | PSZ-AC_1:6 (economizer) | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb |  |  | 2021-05-06
WA_PS_PSZ-AC_2:7 (economizer) | PSZ-AC_2:7 (economizer) | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb |  |  | 2021-05-06
WA_PS_VAV_Pod_1_ERV Flag | VAV_Pod_1_ERV Flag | No | No | No | No | Yes | Yes | Yes | Yes |  |  | 2021-05-06
WA_PS_VAV_Pod_2_ERV Flag | VAV_Pod_2_ERV Flag | No | No | No | No | Yes | Yes | Yes | Yes |  |  | 2021-05-06
WA_PS_VAV_Pod_3_ERV Flag | VAV_Pod_3_ERV Flag | No | No | No | No | Yes | Yes | Yes | Yes |  |  | 2021-05-06
WA_PS_VAV_OTHER_ERV Flag | VAV_OTHER_ERV Flag | No | No | No | No | No | No | Yes | No |  |  | 2021-05-06
WA_PS_PSZ_AC_2_5_ERV Flag | PSZ_AC_2_5_ERV Flag | No | No | No | No | No | No | No | No |  |  | 2021-05-06
WA_PS_PSZ_AC_2_7_ERV Flag | PSZ_AC_2_7_ERV Flag | No | No | No | No | No | No | Yes | Yes |  |  | 2021-05-06
WA_PS_HEATSYS1 Capacity [MMBTU/h] | HEATSYS1 Capacity [MMBTU/h] | 0.81874 | 0.78196 | 1.0993 | 1.0438 | 0.80207 | 0.76397 | 1.2075 | 1.152 |  |  | 2021-05-06
WA_PS_HEATSYS1 Flow Rate [gal/min] | HEATSYS1 Flow Rate [gal/min] | 84.0281 | 80.2535 | 112.8201 | 107.1246 | 82.3179 | 78.4076 | 123.9288 | 118.232 |  |  | 2021-05-06
WA_PS_VAV_POD_1 Fan Power [hp] | VAV_POD_1 Fan Power [hp] | 8.5856 | 8.2815 | 9.2184 | 8.787 | 8.4218 | 8.1251 | 8.9796 | 8.5192 |  |  | 2021-05-06
WA_PS_VAV_POD_2 Fan Power [hp] | VAV_POD_2 Fan Power [hp] | 8.5115 | 8.2007 | 9.1929 | 8.7051 | 8.3446 | 8.036 | 8.9312 | 8.4286 |  |  | 2021-05-06
WA_PS_VAV_POD_3 Fan Power [hp] | VAV_POD_3 Fan Power [hp] | 7.8376 | 7.4795 | 8.4476 | 8.0188 | 7.6678 | 7.3143 | 8.2811 | 7.7492 |  |  | 2021-05-06
WA_PS_VAV_OTHER Fan Power [hp] | VAV_OTHER Fan Power [hp] | 11.2173 | 10.4806 | 12.8102 | 12.1014 | 10.7488 | 10.0167 | 12.5888 | 11.7074 |  |  | 2021-05-06
WA_PS_HEATSYS1 Pump Power [hp] | HEATSYS1 Pump Power [hp] | 1.8163 | 1.7176 | 2.4387 | 2.2926 | 1.7793 | 1.678 | 2.6788 | 2.5303 |  |  | 2021-05-06
WA_PS_PSZ-AC_1:6 Heating Capacity [kBtu/hr] | PSZ-AC_1:6 Heating Capacity [kBtu/hr] | 197.7692 | 189.2222 | 212.4184 | 203.9321 | 196.9509 | 188.4111 | 216.6827 | 207.4787 |  |  | 2021-05-06
WA_PS_PSZ-AC_2:5 Heating Capacity [kBtu/hr] | PSZ-AC_2:5 Heating Capacity [kBtu/hr] | 109.4943 | 110.9488 | 136.1179 | 135.7394 | 109.1093 | 110.5978 | 146.2379 | 145.3037 |  |  | 2021-05-06
WA_PS_PSZ-AC_2:7 Heating Capacity [kBtu/hr] | PSZ-AC_2:7 Heating Capacity [kBtu/hr] | 267.6897 | 267.6897 | 314.6831 | 314.6831 | 272.2707 | 272.2707 | 345.0965 | 345.0965 |  |  | 2021-05-06
WA_PS_ZN_VAV_BOXes_Max_Reheat_Water_Flow_GPM | ZN_VAV_BOXes_Max_Reheat_Water_Flow_GPM | 59.3334 | 56.7277 | 70.0792 | 66.6002 | 57.524 | 54.8064 | 73.7124 | 71.0936 |  |  | 2021-05-06
id | item | Zone4C(WA-Seattle-WA) ASHRAE901-state_STD2016 | Zone4C(WA-Seattle-WA) ASHRAE901-state_STD2019 | Zone5B(WA-Spokane-WA) ASHRAE901-state_STD2016 | Zone5B(WA-Spokane-WA) ASHRAE901-state_STD2019 | Zone5C(WA-Quillayute-WA) ASHRAE901-state_STD2016 | Zone5C(WA-Quillayute-WA) ASHRAE901-state_STD2019 | Zone6B(WA-Kalispell-MT) ASHRAE901-state_STD2016 | Zone6B(WA-Kalispell-MT) ASHRAE901-state_STD2019 |  |  | 2021-05-06
WA_SH_SAC_FRONTOFFICE Cooling Capacity [ton] | SAC_FRONTOFFICE Cooling Capacity [ton] | 1.9596 | 1.8541 | 2.0155 | 1.909 | 1.7651 | 1.6712 | 1.9368 | 1.8042 |  |  | 2021-05-06
WA_SH_SAC_FRONTLOUNGE Cooling Capacity [ton] | SAC_FRONTLOUNGE Cooling Capacity [ton] | 4.8007 | 4.5742 | 5.1847 | 4.9618 | 4.3378 | 4.1197 | 4.9813 | 4.7507 |  |  | 2021-05-06
WA_SH_SAC_MEETINGROOM Cooling Capacity [ton] | SAC_MEETINGROOM Cooling Capacity [ton] | 2.5464 | 2.471 | 2.7348 | 2.6483 | 2.3155 | 2.2444 | 2.6531 | 2.5716 |  |  | 2021-05-06
WA_SH_SAC_EXC_EMPLGE_RESTRM Cooling Capacity [ton] | SAC_EXC_EMPLGE_RESTRM Cooling Capacity [ton] | 5.263 | 5.2232 | 5.5778 | 5.5354 | 4.9733 | 4.9352 | 5.5242 | 5.4745 |  |  | 2021-05-06
WA_SH_SAC_FO_ADDAQ SUPPLY FAN Supply Flow Rate [cfm] | SAC_FO_ADDAQ SUPPLY FAN Supply Flow Rate [cfm] | 805.1744 | 762.7968 | 847.552 | 783.9856 | 762.7968 | 720.4192 | 826.3632 | 762.7968 |  |  | 2021-05-06
WA_SH_SAC_FL_ADDAQ SUPPLY FAN Supply Flow Rate [cfm] | SAC_FL_ADDAQ SUPPLY FAN Supply Flow Rate [cfm] | 1758.6704 | 1652.7264 | 1949.3696 | 1843.4256 | 1695.104 | 1589.16 | 1928.1808 | 1822.2368 |  |  | 2021-05-06
WA_SH_SAC_MR_ADDAQ SUPPLY FAN Supply Flow Rate [cfm] | SAC_MR_ADDAQ SUPPLY FAN Supply Flow Rate [cfm] | 868.7408 | 826.3632 | 932.3072 | 911.1184 | 826.3632 | 805.1744 | 932.3072 | 911.1184 |  |  | 2021-05-06
WA_SH_SAC_EXC_ADDAQ SUPPLY FAN Supply Flow Rate [cfm] | SAC_EXC_ADDAQ SUPPLY FAN Supply Flow Rate [cfm] | 2203.6352 | 2203.6352 | 2394.3344 | 2373.1456 | 2182.4464 | 2161.2576 | 2415.5232 | 2394.3344 |  |  | 2021-05-06
WA_SH_SAC_Exc_EmpLge_RestRm OA Rate [cfm] | SAC_Exc_EmpLge_RestRm OA Rate [cfm] | 199.9928 | 199.9928 | 199.9928 | 199.9928 | 199.9928 | 199.9928 | 199.9928 | 199.9928 |  |  | 2021-05-06
WA_SH_SAC_FrontLounge OA Rate [cfm] | SAC_FrontLounge OA Rate [cfm] | 500.0133 | 500.0133 | 500.0133 | 500.0133 | 500.0133 | 500.0133 | 500.0133 | 500.0133 |  |  | 2021-05-06
WA_SH_SAC_FrontOffice OA Rate [cfm] | SAC_FrontOffice OA Rate [cfm] | 119.2938 | 119.2938 | 119.2938 | 119.2938 | 119.2938 | 119.2938 | 119.2938 | 119.2938 |  |  | 2021-05-06
WA_SH_SAC_MeetingRoom OA Rate [cfm] | SAC_MeetingRoom OA Rate [cfm] | 267.7629 | 267.7629 | 267.7629 | 267.7629 | 267.7629 | 267.7629 | 267.7629 | 267.7629 |  |  | 2021-05-06
WA_SH_SAC_FrontLounge OA Damper [gravity, motorized] | SAC_FrontLounge OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | motorized | motorized | motorized | motorized |  |  | 2021-05-06
WA_SH_SAC_FrontOffice (economizer) | SAC_FrontOffice (economizer) | No | No | No | No | No | No | No | No |  |  | 2021-05-06
WA_SH_SAC_FrontLounge (economizer) | SAC_FrontLounge (economizer) | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | No | No | DifferentialDryBulb | DifferentialDryBulb |  |  | 2021-05-06
WA_SH_SAC_MeetingRoom (economizer) | SAC_MeetingRoom (economizer) | No | No | No | No | No | No | No | No |  |  | 2021-05-06
WA_SH_SAC_Exc_EmpLge_RestRm (economizer) | SAC_Exc_EmpLge_RestRm (economizer) | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb |  |  | 2021-05-06
WA_SH_SAC_FRONTOFFICE Heating Capacity [kBtu/hr] | SAC_FRONTOFFICE Heating Capacity [kBtu/hr] | 34.9312 | 33.1564 | 36.3392 | 34.3126 | 33.7362 | 32.1031 | 36.3786 | 34.3038 |  |  | 2021-05-06
WA_SH_SAC_FRONTLOUNGE Heating Capacity [kBtu/hr] | SAC_FRONTLOUNGE Heating Capacity [kBtu/hr] | 87.8472 | 84.4522 | 98.3303 | 95.0459 | 86.7866 | 83.3951 | 101.8991 | 98.4494 |  |  | 2021-05-06
WA_SH_SAC_MEETINGROOM Heating Capacity [kBtu/hr] | SAC_MEETINGROOM Heating Capacity [kBtu/hr] | 44.224 | 43.0979 | 49.2862 | 48.0801 | 43.8501 | 42.7545 | 51.4244 | 50.273 |  |  | 2021-05-06
WA_SH_SAC_EXC_EMPLGE_RESTRM Heating Capacity [kBtu/hr] | SAC_EXC_EMPLGE_RESTRM Heating Capacity [kBtu/hr] | 89.991 | 89.3342 | 93.2862 | 92.6246 | 89.6397 | 88.9873 | 95.0753 | 94.2873 |  |  | 2021-05-06
id | item | Zone4C(WA-Seattle-WA) ASHRAE901-state_STD2016 | Zone4C(WA-Seattle-WA) ASHRAE901-state_STD2019 | Zone5B(WA-Spokane-WA) ASHRAE901-state_STD2016 | Zone5B(WA-Spokane-WA) ASHRAE901-state_STD2019 | Zone5C(WA-Quillayute-WA) ASHRAE901-state_STD2016 | Zone5C(WA-Quillayute-WA) ASHRAE901-state_STD2019 | Zone6B(WA-Kalispell-MT) ASHRAE901-state_STD2016 | Zone6B(WA-Kalispell-MT) ASHRAE901-state_STD2019 |  |  | 2021-05-06
WA_MA_SPLIT GSW COOLING COIL Cooling Capacity [ton] | SPLIT GSW COOLING COIL Cooling Capacity [ton] | 0.72312 | 0.70517 | 0.78284 | 0.7648 | 0.66262 | 0.64467 | 0.76873 | 0.72966 |  |  | 2021-05-06
WA_MA_SPLIT GNW COOLING COIL Cooling Capacity [ton] | SPLIT GNW COOLING COIL Cooling Capacity [ton] | 0.58638 | 0.57191 | 0.71289 | 0.6964 | 0.52447 | 0.51007 | 0.68897 | 0.65519 |  |  | 2021-05-06
WA_MA_SPLIT OFFICE COOLING COIL Cooling Capacity [ton] | SPLIT OFFICE COOLING COIL Cooling Capacity [ton] | 1.586 | 1.4266 | 1.7572 | 1.588 | 1.489 | 1.3278 | 1.6848 | 1.4759 |  |  | 2021-05-06
WA_MA_SPLIT GNE COOLING COIL Cooling Capacity [ton] | SPLIT GNE COOLING COIL Cooling Capacity [ton] | 0.45451 | 0.44252 | 0.56403 | 0.55026 | 0.39898 | 0.38703 | 0.54191 | 0.51466 |  |  | 2021-05-06
WA_MA_SPLIT GN1 COOLING COIL Cooling Capacity [ton] | SPLIT GN1 COOLING COIL Cooling Capacity [ton] | 0.38743 | 0.37796 | 0.47111 | 0.46013 | 0.34558 | 0.3361 | 0.44744 | 0.42967 |  |  | 2021-05-06
WA_MA_SPLIT GN2 COOLING COIL Cooling Capacity [ton] | SPLIT GN2 COOLING COIL Cooling Capacity [ton] | 0.38487 | 0.37543 | 0.46809 | 0.45719 | 0.34307 | 0.33365 | 0.44483 | 0.42714 |  |  | 2021-05-06
WA_MA_SPLIT GS1 COOLING COIL Cooling Capacity [ton] | SPLIT GS1 COOLING COIL Cooling Capacity [ton] | 0.54154 | 0.52633 | 0.53593 | 0.5232 | 0.4942 | 0.47741 | 0.53094 | 0.5071 |  |  | 2021-05-06
WA_MA_SPLIT GS2 COOLING COIL Cooling Capacity [ton] | SPLIT GS2 COOLING COIL Cooling Capacity [ton] | 0.58258 | 0.56228 | 0.57701 | 0.55891 | 0.5384 | 0.51587 | 0.57295 | 0.54312 |  |  | 2021-05-06
WA_MA_SPLIT MSW COOLING COIL Cooling Capacity [ton] | SPLIT MSW COOLING COIL Cooling Capacity [ton] | 1.7963 | 1.7559 | 1.998 | 1.9574 | 1.7029 | 1.6627 | 1.9941 | 1.8995 |  |  | 2021-05-06
WA_MA_SPLIT MNW COOLING COIL Cooling Capacity [ton] | SPLIT MNW COOLING COIL Cooling Capacity [ton] | 1.506 | 1.473 | 1.8613 | 1.8237 | 1.4166 | 1.3837 | 1.8269 | 1.7427 |  |  | 2021-05-06
WA_MA_SPLIT MSE COOLING COIL Cooling Capacity [ton] | SPLIT MSE COOLING COIL Cooling Capacity [ton] | 1.6119 | 1.5672 | 1.6417 | 1.6028 | 1.5402 | 1.4957 | 1.6201 | 1.5281 |  |  | 2021-05-06
WA_MA_SPLIT MNE COOLING COIL Cooling Capacity [ton] | SPLIT MNE COOLING COIL Cooling Capacity [ton] | 1.1458 | 1.1144 | 1.431 | 1.3946 | 1.089 | 1.0582 | 1.3859 | 1.305 |  |  | 2021-05-06
WA_MA_SPLIT MN1 COOLING COIL Cooling Capacity [ton] | SPLIT MN1 COOLING COIL Cooling Capacity [ton] | 0.88943 | 0.87153 | 1.1068 | 1.0855 | 0.82966 | 0.81185 | 1.0501 | 1.0168 |  |  | 2021-05-06
WA_MA_SPLIT MN2 COOLING COIL Cooling Capacity [ton] | SPLIT MN2 COOLING COIL Cooling Capacity [ton] | 0.88214 | 0.8645 | 1.0982 | 1.0771 | 0.8223 | 0.80471 | 1.0413 | 1.0087 |  |  | 2021-05-06
WA_MA_SPLIT MS1 COOLING COIL Cooling Capacity [ton] | SPLIT MS1 COOLING COIL Cooling Capacity [ton] | 1.3028 | 1.2651 | 1.2306 | 1.2036 | 1.2552 | 1.2176 | 1.227 | 1.1705 |  |  | 2021-05-06
WA_MA_SPLIT MS2 COOLING COIL Cooling Capacity [ton] | SPLIT MS2 COOLING COIL Cooling Capacity [ton] | 1.308 | 1.2702 | 1.2367 | 1.2088 | 1.2607 | 1.223 | 1.2332 | 1.1674 |  |  | 2021-05-06
WA_MA_SPLIT TSW COOLING COIL Cooling Capacity [ton] | SPLIT TSW COOLING COIL Cooling Capacity [ton] | 1.0972 | 1.0758 | 1.2601 | 1.2385 | 1.0274 | 1.006 | 1.2633 | 1.2115 |  |  | 2021-05-06
WA_MA_SPLIT TNW COOLING COIL Cooling Capacity [ton] | SPLIT TNW COOLING COIL Cooling Capacity [ton] | 0.94069 | 0.92269 | 1.1841 | 1.1638 | 0.87929 | 0.86138 | 1.1728 | 1.1259 |  |  | 2021-05-06
WA_MA_SPLIT TSE COOLING COIL Cooling Capacity [ton] | SPLIT TSE COOLING COIL Cooling Capacity [ton] | 1.0346 | 1.0098 | 1.0893 | 1.0685 | 0.98062 | 0.95573 | 1.0755 | 1.0243 |  |  | 2021-05-06
WA_MA_SPLIT TNE COOLING COIL Cooling Capacity [ton] | SPLIT TNE COOLING COIL Cooling Capacity [ton] | 0.69804 | 0.68521 | 0.90473 | 0.8904 | 0.63355 | 0.62071 | 0.86419 | 0.83462 |  |  | 2021-05-06
WA_MA_SPLIT TN1 COOLING COIL Cooling Capacity [ton] | SPLIT TN1 COOLING COIL Cooling Capacity [ton] | 0.56331 | 0.55407 | 0.71812 | 0.70762 | 0.51734 | 0.50809 | 0.70939 | 0.69128 |  |  | 2021-05-06
WA_MA_SPLIT TN2 COOLING COIL Cooling Capacity [ton] | SPLIT TN2 COOLING COIL Cooling Capacity [ton] | 0.56598 | 0.55707 | 0.71482 | 0.70379 | 0.50957 | 0.50053 | 0.70123 | 0.68374 |  |  | 2021-05-06
WA_MA_SPLIT TS1 COOLING COIL Cooling Capacity [ton] | SPLIT TS1 COOLING COIL Cooling Capacity [ton] | 0.87747 | 0.85597 | 0.87986 | 0.86304 | 0.83629 | 0.81489 | 0.87572 | 0.83711 |  |  | 2021-05-06
WA_MA_SPLIT TS2 COOLING COIL Cooling Capacity [ton] | SPLIT TS2 COOLING COIL Cooling Capacity [ton] | 0.88181 | 0.86024 | 0.88465 | 0.86761 | 0.84085 | 0.81938 | 0.88065 | 0.8418 |  |  | 2021-05-06
WA_MA_Split GN1 Furnace with DX Cooling OA Rate [cfm] | Split GN1 Furnace with DX Cooling OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 |  |  | 2021-05-06
WA_MA_Split GN2 Furnace with DX Cooling OA Rate [cfm] | Split GN2 Furnace with DX Cooling OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 |  |  | 2021-05-06
WA_MA_Split GNE Furnace with DX Cooling OA Rate [cfm] | Split GNE Furnace with DX Cooling OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 |  |  | 2021-05-06
WA_MA_Split GNW Furnace with DX Cooling OA Rate [cfm] | Split GNW Furnace with DX Cooling OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 |  |  | 2021-05-06
WA_MA_Split GS1 Furnace with DX Cooling OA Rate [cfm] | Split GS1 Furnace with DX Cooling OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 |  |  | 2021-05-06
WA_MA_Split GS2 Furnace with DX Cooling OA Rate [cfm] | Split GS2 Furnace with DX Cooling OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 |  |  | 2021-05-06
WA_MA_Split GSW Furnace with DX Cooling OA Rate [cfm] | Split GSW Furnace with DX Cooling OA Rate [cfm] | 56.9945 | 56.9945 | 56.9945 | 56.9945 | 56.9945 | 56.9945 | 56.9945 | 56.9945 |  |  | 2021-05-06
WA_MA_Split MN1 Furnace with DX Cooling OA Rate [cfm] | Split MN1 Furnace with DX Cooling OA Rate [cfm] | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824 |  |  | 2021-05-06
WA_MA_Split MN2 Furnace with DX Cooling OA Rate [cfm] | Split MN2 Furnace with DX Cooling OA Rate [cfm] | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824 |  |  | 2021-05-06
WA_MA_Split MNE Furnace with DX Cooling OA Rate [cfm] | Split MNE Furnace with DX Cooling OA Rate [cfm] | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824 |  |  | 2021-05-06
WA_MA_Split MNW Furnace with DX Cooling OA Rate [cfm] | Split MNW Furnace with DX Cooling OA Rate [cfm] | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824 |  |  | 2021-05-06
WA_MA_Split MS1 Furnace with DX Cooling OA Rate [cfm] | Split MS1 Furnace with DX Cooling OA Rate [cfm] | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824 |  |  | 2021-05-06
WA_MA_Split MS2 Furnace with DX Cooling OA Rate [cfm] | Split MS2 Furnace with DX Cooling OA Rate [cfm] | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824 |  |  | 2021-05-06
WA_MA_Split MSE Furnace with DX Cooling OA Rate [cfm] | Split MSE Furnace with DX Cooling OA Rate [cfm] | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824 |  |  | 2021-05-06
WA_MA_Split MSW Furnace with DX Cooling OA Rate [cfm] | Split MSW Furnace with DX Cooling OA Rate [cfm] | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824 |  |  | 2021-05-06
WA_MA_Split Office Furnace with DX Cooling OA Rate [cfm] | Split Office Furnace with DX Cooling OA Rate [cfm] | 80.7372 | 80.7372 | 80.7372 | 80.7372 | 80.7372 | 80.7372 | 80.7372 | 80.7372 |  |  | 2021-05-06
WA_MA_Split TN1 Furnace with DX Cooling OA Rate [cfm] | Split TN1 Furnace with DX Cooling OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 |  |  | 2021-05-06
WA_MA_Split TN2 Furnace with DX Cooling OA Rate [cfm] | Split TN2 Furnace with DX Cooling OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 |  |  | 2021-05-06
WA_MA_Split TNE Furnace with DX Cooling OA Rate [cfm] | Split TNE Furnace with DX Cooling OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 |  |  | 2021-05-06
WA_MA_Split TNW Furnace with DX Cooling OA Rate [cfm] | Split TNW Furnace with DX Cooling OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 |  |  | 2021-05-06
WA_MA_Split TS1 Furnace with DX Cooling OA Rate [cfm] | Split TS1 Furnace with DX Cooling OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 |  |  | 2021-05-06
WA_MA_Split TS2 Furnace with DX Cooling OA Rate [cfm] | Split TS2 Furnace with DX Cooling OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 |  |  | 2021-05-06
WA_MA_Split TSE Furnace with DX Cooling OA Rate [cfm] | Split TSE Furnace with DX Cooling OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 |  |  | 2021-05-06
WA_MA_Split TSW Furnace with DX Cooling OA Rate [cfm] | Split TSW Furnace with DX Cooling OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 |  |  | 2021-05-06
WA_MA_SPLIT GSW HEATING COIL Heating Capacity [kBtu/hr] | SPLIT GSW HEATING COIL Heating Capacity [kBtu/hr] | 6.1984 | 6.2561 | 8.7934 | 8.8536 | 5.7035 | 5.7616 | 10.0022 | 10.0619 |  |  | 2021-05-06
WA_MA_SPLIT GNW HEATING COIL Heating Capacity [kBtu/hr] | SPLIT GNW HEATING COIL Heating Capacity [kBtu/hr] | 6.1371 | 6.1951 | 8.7252 | 8.7856 | 5.6369 | 5.6952 | 9.9175 | 9.9772 |  |  | 2021-05-06
WA_MA_SPLIT OFFICE HEATING COIL Heating Capacity [kBtu/hr] | SPLIT OFFICE HEATING COIL Heating Capacity [kBtu/hr] | 16.6649 | 16.7896 | 21.2529 | 21.3484 | 15.5586 | 15.9048 | 23.2278 | 23.3129 |  |  | 2021-05-06
WA_MA_SPLIT GNE HEATING COIL Heating Capacity [kBtu/hr] | SPLIT GNE HEATING COIL Heating Capacity [kBtu/hr] | 6.1472 | 6.2052 | 8.7461 | 8.8065 | 5.6455 | 5.7038 | 9.9387 | 9.9984 |  |  | 2021-05-06
WA_MA_SPLIT GN1 HEATING COIL Heating Capacity [kBtu/hr] | SPLIT GN1 HEATING COIL Heating Capacity [kBtu/hr] | 4.6686 | 4.6686 | 6.4553 | 6.5158 | 4.7485 | 4.7485 | 7.5165 | 7.5763 |  |  | 2021-05-06
WA_MA_SPLIT GN2 HEATING COIL Heating Capacity [kBtu/hr] | SPLIT GN2 HEATING COIL Heating Capacity [kBtu/hr] | 4.6686 | 4.6686 | 6.456 | 6.5164 | 4.7485 | 4.7485 | 7.5172 | 7.5769 |  |  | 2021-05-06
WA_MA_SPLIT GS1 HEATING COIL Heating Capacity [kBtu/hr] | SPLIT GS1 HEATING COIL Heating Capacity [kBtu/hr] | 4.6686 | 4.6686 | 6.4067 | 6.467 | 4.7485 | 4.7485 | 7.4649 | 7.5246 |  |  | 2021-05-06
WA_MA_SPLIT GS2 HEATING COIL Heating Capacity [kBtu/hr] | SPLIT GS2 HEATING COIL Heating Capacity [kBtu/hr] | 4.7348 | 4.7964 | 6.9015 | 6.9634 | 4.7485 | 4.7485 | 7.9795 | 8.0402 |  |  | 2021-05-06
WA_MA_SPLIT MSW HEATING COIL Heating Capacity [kBtu/hr] | SPLIT MSW HEATING COIL Heating Capacity [kBtu/hr] | 11.1236 | 11.256 | 15.8122 | 15.9406 | 9.497 | 9.5659 | 17.1252 | 17.2538 |  |  | 2021-05-06
WA_MA_SPLIT MNW HEATING COIL Heating Capacity [kBtu/hr] | SPLIT MNW HEATING COIL Heating Capacity [kBtu/hr] | 11.1698 | 11.3017 | 15.898 | 16.0264 | 9.497 | 9.608 | 17.2133 | 17.3417 |  |  | 2021-05-06
WA_MA_SPLIT MSE HEATING COIL Heating Capacity [kBtu/hr] | SPLIT MSE HEATING COIL Heating Capacity [kBtu/hr] | 11.1483 | 11.2807 | 15.8619 | 15.9903 | 9.497 | 9.5869 | 17.1756 | 17.3042 |  |  | 2021-05-06
WA_MA_SPLIT MNE HEATING COIL Heating Capacity [kBtu/hr] | SPLIT MNE HEATING COIL Heating Capacity [kBtu/hr] | 11.1944 | 11.3264 | 15.9477 | 16.076 | 9.497 | 9.629 | 17.2638 | 17.3922 |  |  | 2021-05-06
WA_MA_SPLIT MN1 HEATING COIL Heating Capacity [kBtu/hr] | SPLIT MN1 HEATING COIL Heating Capacity [kBtu/hr] | 9.3373 | 9.3373 | 11.0293 | 11.1555 | 9.497 | 9.497 | 12.2822 | 12.4091 |  |  | 2021-05-06
WA_MA_SPLIT MN2 HEATING COIL Heating Capacity [kBtu/hr] | SPLIT MN2 HEATING COIL Heating Capacity [kBtu/hr] | 9.3373 | 9.3373 | 11.0307 | 11.1568 | 9.497 | 9.497 | 12.2835 | 12.4105 |  |  | 2021-05-06
WA_MA_SPLIT MS1 HEATING COIL Heating Capacity [kBtu/hr] | SPLIT MS1 HEATING COIL Heating Capacity [kBtu/hr] | 9.3373 | 9.3373 | 10.9764 | 11.0786 | 9.497 | 9.497 | 12.2043 | 12.3312 |  |  | 2021-05-06
WA_MA_SPLIT MS2 HEATING COIL Heating Capacity [kBtu/hr] | SPLIT MS2 HEATING COIL Heating Capacity [kBtu/hr] | 9.3373 | 9.3373 | 10.9764 | 11.08 | 9.497 | 9.497 | 12.2057 | 12.3326 |  |  | 2021-05-06
WA_MA_SPLIT TSW HEATING COIL Heating Capacity [kBtu/hr] | SPLIT TSW HEATING COIL Heating Capacity [kBtu/hr] | 8.2104 | 8.2717 | 11.3808 | 11.4427 | 7.255 | 7.3165 | 12.4001 | 12.4623 |  |  | 2021-05-06
WA_MA_SPLIT TNW HEATING COIL Heating Capacity [kBtu/hr] | SPLIT TNW HEATING COIL Heating Capacity [kBtu/hr] | 8.2398 | 8.3012 | 11.4327 | 11.4947 | 7.2821 | 7.3437 | 12.4545 | 12.5168 |  |  | 2021-05-06
WA_MA_SPLIT TSE HEATING COIL Heating Capacity [kBtu/hr] | SPLIT TSE HEATING COIL Heating Capacity [kBtu/hr] | 8.2233 | 8.2845 | 11.4072 | 11.469 | 7.2662 | 7.3276 | 12.4272 | 12.4894 |  |  | 2021-05-06
WA_MA_SPLIT TNE HEATING COIL Heating Capacity [kBtu/hr] | SPLIT TNE HEATING COIL Heating Capacity [kBtu/hr] | 8.2526 | 8.314 | 11.4591 | 11.521 | 7.2932 | 7.3548 | 12.4816 | 12.5439 |  |  | 2021-05-06
WA_MA_SPLIT TN1 HEATING COIL Heating Capacity [kBtu/hr] | SPLIT TN1 HEATING COIL Heating Capacity [kBtu/hr] | 6.1425 | 6.2036 | 8.8542 | 8.9161 | 5.5993 | 5.6607 | 9.8879 | 9.9501 |  |  | 2021-05-06
WA_MA_SPLIT TN2 HEATING COIL Heating Capacity [kBtu/hr] | SPLIT TN2 HEATING COIL Heating Capacity [kBtu/hr] | 6.1429 | 6.204 | 8.855 | 8.9168 | 5.5997 | 5.6611 | 9.8887 | 9.9509 |  |  | 2021-05-06
WA_MA_SPLIT TS1 HEATING COIL Heating Capacity [kBtu/hr] | SPLIT TS1 HEATING COIL Heating Capacity [kBtu/hr] | 6.1053 | 6.1664 | 8.7956 | 8.8573 | 5.5646 | 5.6259 | 9.8272 | 9.8893 |  |  | 2021-05-06
WA_MA_SPLIT TS2 HEATING COIL Heating Capacity [kBtu/hr] | SPLIT TS2 HEATING COIL Heating Capacity [kBtu/hr] | 6.1057 | 6.1668 | 8.7963 | 8.8581 | 5.5649 | 5.6262 | 9.828 | 9.8901 |  |  | 2021-05-06
WA_MA_Split_GSW ERV Flag | Split_GSW ERV Flag | No | Yes | No | Yes | No | Yes | Yes | Yes |  |  | 2021-05-06
WA_MA_Split_GNW ERV Flag | Split_GNW ERV Flag | No | Yes | No | Yes | No | Yes | Yes | Yes |  |  | 2021-05-06
WA_MA_Split_GNE ERV Flag | Split_GNE ERV Flag | No | Yes | No | Yes | No | Yes | Yes | Yes |  |  | 2021-05-06
WA_MA_Split_GN1 ERV Flag | Split_GN1 ERV Flag | No | Yes | No | Yes | No | Yes | Yes | Yes |  |  | 2021-05-06
WA_MA_Split_GN2 ERV Flag | Split_GN2 ERV Flag | No | Yes | No | Yes | No | Yes | Yes | Yes |  |  | 2021-05-06
WA_MA_Split_GS1 ERV Flag | Split_GS1 ERV Flag | No | Yes | No | Yes | No | Yes | Yes | Yes |  |  | 2021-05-06
WA_MA_Split_GS2 ERV Flag | Split_GS2 ERV Flag | No | Yes | No | Yes | No | Yes | Yes | Yes |  |  | 2021-05-06
WA_MA_Split_MSW ERV Flag | Split_MSW ERV Flag | No | Yes | No | Yes | No | Yes | Yes | Yes |  |  | 2021-05-06
WA_MA_Split_MNW ERV Flag | Split_MNW ERV Flag | No | Yes | No | Yes | No | Yes | Yes | Yes |  |  | 2021-05-06
WA_MA_Split_MSE ERV Flag | Split_MSE ERV Flag | No | Yes | No | Yes | No | Yes | Yes | Yes |  |  | 2021-05-06
WA_MA_Split_MNE ERV Flag | Split_MNE ERV Flag | No | Yes | No | Yes | No | Yes | Yes | Yes |  |  | 2021-05-06
WA_MA_Split_MN1 ERV Flag | Split_MN1 ERV Flag | No | Yes | No | Yes | No | Yes | Yes | Yes |  |  | 2021-05-06
WA_MA_Split_MN2 ERV Flag | Split_MN2 ERV Flag | No | Yes | No | Yes | No | Yes | Yes | Yes |  |  | 2021-05-06
WA_MA_Split_MS1 ERV Flag | Split_MS1 ERV Flag | No | Yes | No | Yes | No | Yes | Yes | Yes |  |  | 2021-05-06
WA_MA_Split_MS2 ERV Flag | Split_MS2 ERV Flag | No | Yes | No | Yes | No | Yes | Yes | Yes |  |  | 2021-05-06
WA_MA_Split_TSW ERV Flag | Split_TSW ERV Flag | No | Yes | No | No | No | Yes | No | No |  |  | 2021-05-06
WA_MA_Split_TNW ERV Flag | Split_TNW ERV Flag | No | Yes | No | Yes | No | Yes | Yes | Yes |  |  | 2021-05-06
WA_MA_Split_TSE ERV Flag | Split_TSE ERV Flag | No | Yes | No | Yes | No | Yes | Yes | Yes |  |  | 2021-05-06
WA_MA_Split_TNE ERV Flag | Split_TNE ERV Flag | No | Yes | No | Yes | No | Yes | Yes | Yes |  |  | 2021-05-06
WA_MA_Split_TN1 ERV Flag | Split_TN1 ERV Flag | No | Yes | No | Yes | No | Yes | Yes | Yes |  |  | 2021-05-06
WA_MA_Split_TN2 ERV Flag | Split_TN2 ERV Flag | No | Yes | No | Yes | No | Yes | Yes | Yes |  |  | 2021-05-06
WA_MA_Split_TS1 ERV Flag | Split_TS1 ERV Flag | No | Yes | No | Yes | No | Yes | Yes | Yes |  |  | 2021-05-06
WA_MA_Split_TS2 ERV Flag | Split_TS2 ERV Flag | No | Yes | No | Yes | No | Yes | Yes | Yes |  |  | 2021-05-06
id | item | Zone5A(WI-Milwaukee-WI) ASHRAE901-state_STD2016 | Zone5A(WI-Milwaukee-WI) ASHRAE901-state_STD2019 | Zone6A(WI-GreenBay-WI) ASHRAE901-state_STD2016 | Zone6A(WI-GreenBay-WI) ASHRAE901-state_STD2019 | [6 empty] | 2021-05-06
WI_SO_PSZ-AC:1 Cooling Capacity [ton] | PSZ-AC:1 Cooling Capacity [ton] | 1.8699 | 1.7763 | 1.8031 | 1.7067 | [6 empty] | 2021-05-06
WI_SO_PSZ-AC:2 Cooling Capacity [ton] | PSZ-AC:2 Cooling Capacity [ton] | 1.6039 | 1.5411 | 1.5418 | 1.4637 | [6 empty] | 2021-05-06
WI_SO_PSZ-AC:3 Cooling Capacity [ton] | PSZ-AC:3 Cooling Capacity [ton] | 1.1377 | 1.0993 | 1.0893 | 1.0242 | [6 empty] | 2021-05-06
WI_SO_PSZ-AC:4 Cooling Capacity [ton] | PSZ-AC:4 Cooling Capacity [ton] | 1.5279 | 1.4425 | 1.4413 | 1.3534 | [6 empty] | 2021-05-06
WI_SO_PSZ-AC:5 Cooling Capacity [ton] | PSZ-AC:5 Cooling Capacity [ton] | 1.3391 | 1.299 | 1.313 | 1.2464 | [6 empty] | 2021-05-06
WI_SO_PSZ-AC:1 Supply Flow Rate [cfm] | PSZ-AC:1 Supply Flow Rate [cfm] | 656.8528 | 614.4752 | 635.664 | 593.2864 | [6 empty] | 2021-05-06
WI_SO_PSZ-AC:2 Supply Flow Rate [cfm] | PSZ-AC:2 Supply Flow Rate [cfm] | 572.0976 | 529.72 | 572.0976 | 529.72 | [6 empty] | 2021-05-06
WI_SO_PSZ-AC:3 Supply Flow Rate [cfm] | PSZ-AC:3 Supply Flow Rate [cfm] | 466.1536 | 444.9648 | 466.1536 | 423.776 | [6 empty] | 2021-05-06
WI_SO_PSZ-AC:4 Supply Flow Rate [cfm] | PSZ-AC:4 Supply Flow Rate [cfm] | 529.72 | 487.3424 | 508.5312 | 466.1536 | [6 empty] | 2021-05-06
WI_SO_PSZ-AC:5 Supply Flow Rate [cfm] | PSZ-AC:5 Supply Flow Rate [cfm] | 550.9088 | 529.72 | 550.9088 | 508.5312 | [6 empty] | 2021-05-06
WI_SO_PSZ-AC:1 OA Rate [cfm] | PSZ-AC:1 OA Rate [cfm] | 136.9178 | 136.9178 | 136.9178 | 136.9178 | [6 empty] | 2021-05-06
WI_SO_PSZ-AC:2 OA Rate [cfm] | PSZ-AC:2 OA Rate [cfm] | 103.7925 | 103.7925 | 103.7925 | 103.7925 | [6 empty] | 2021-05-06
WI_SO_PSZ-AC:3 OA Rate [cfm] | PSZ-AC:3 OA Rate [cfm] | 61.5711 | 61.5711 | 61.5711 | 61.5711 | [6 empty] | 2021-05-06
WI_SO_PSZ-AC:4 OA Rate [cfm] | PSZ-AC:4 OA Rate [cfm] | 103.7925 | 103.7925 | 103.7925 | 103.7925 | [6 empty] | 2021-05-06
WI_SO_PSZ-AC:5 OA Rate [cfm] | PSZ-AC:5 OA Rate [cfm] | 61.5711 | 61.5711 | 61.5711 | 61.5711 | [6 empty] | 2021-05-06
WI_SO_PSZ-AC:1 heating Capacity [kBtu/hr] | PSZ-AC:1 heating Capacity [kBtu/hr] | 15.6241 | 15.6241 | 16.4756 | 16.4756 | [6 empty] | 2021-05-06
WI_SO_PSZ-AC:2 heating Capacity [kBtu/hr] | PSZ-AC:2 heating Capacity [kBtu/hr] | 23.21 | 22.9636 | 23.9158 | 23.6356 | [6 empty] | 2021-05-06
WI_SO_PSZ-AC:3 heating Capacity [kBtu/hr] | PSZ-AC:3 heating Capacity [kBtu/hr] | 14.1989 | 14.0627 | 14.52 | 14.3717 | [6 empty] | 2021-05-06
WI_SO_PSZ-AC:4 heating Capacity [kBtu/hr] | PSZ-AC:4 heating Capacity [kBtu/hr] | 23.1256 | 22.9135 | 23.7288 | 23.4997 | [6 empty] | 2021-05-06
WI_SO_PSZ-AC:5 heating Capacity [kBtu/hr] | PSZ-AC:5 heating Capacity [kBtu/hr] | 14.274 | 14.1306 | 14.5889 | 14.4338 | [6 empty] | 2021-05-06
id | item | Zone5A(WI-Milwaukee-WI) ASHRAE901-state_STD2016 | Zone5A(WI-Milwaukee-WI) ASHRAE901-state_STD2019 | Zone6A(WI-GreenBay-WI) ASHRAE901-state_STD2016 | Zone6A(WI-GreenBay-WI) ASHRAE901-state_STD2019 | [6 empty] | 2021-05-06
WI_LO_CAV_BAS Supply Flow Rate [cfm] | CAV_BAS Supply Flow Rate [cfm] | 11802.1616 | 10912.232 | 11865.728 | 10954.6096 | [6 empty] | 2021-05-06
WI_LO_VAV_BOT WITH REHEAT Supply Flow Rate [cfm] | VAV_BOT WITH REHEAT Supply Flow Rate [cfm] | 20341.248 | 19408.9408 | 20129.36 | 19048.7312 | [6 empty] | 2021-05-06
WI_LO_VAV_MID WITH REHEAT Supply Flow Rate [cfm] | VAV_MID WITH REHEAT Supply Flow Rate [cfm] | 190529.6899 | 181524.4499 | 187732.7683 | 176968.8579 | [6 empty] | 2021-05-06
WI_LO_VAV_TOP WITH REHEAT Supply Flow Rate [cfm] | VAV_TOP WITH REHEAT Supply Flow Rate [cfm] | 19726.7728 | 18942.7872 | 19599.64 | 18561.3888 | [6 empty] | 2021-05-06
WI_LO_Supply Air Temp. Reset Flag | Supply Air Temp. Reset Flag | Yes | Yes | Yes | Yes | [6 empty] | 2021-05-06
WI_LO_CAV_BAS OA Rate [cfm] | CAV_BAS OA Rate [cfm] | 2542.8255 | 2542.8255 | 2542.8255 | 2542.8255 | [6 empty] | 2021-05-06
WI_LO_VAV_BOT WITH REHEAT OA Rate [cfm] | VAV_BOT WITH REHEAT OA Rate [cfm] | 5377.8022 | 4302.174 | 5377.8022 | 4302.174 | [6 empty] | 2021-05-06
WI_LO_VAV_MID WITH REHEAT OA Rate [cfm] | VAV_MID WITH REHEAT OA Rate [cfm] | 53777.9373 | 43021.7396 | 53777.9373 | 43021.7396 | [6 empty] | 2021-05-06
WI_LO_VAV_TOP WITH REHEAT OA Rate [cfm] | VAV_TOP WITH REHEAT OA Rate [cfm] | 5377.8022 | 4302.174 | 5377.8022 | 4302.174 | [6 empty] | 2021-05-06
WI_LO_AIRLOOP DATACENTER BASEMENT OA Rate [cfm] | AIRLOOP DATACENTER BASEMENT OA Rate [cfm] | 716.9654 | 716.9654 | 716.9654 | 716.9654 | [6 empty] | 2021-05-06
WI_LO_VAV_bot_WITH_REHEAT ERV Flag | VAV_bot_WITH_REHEAT ERV Flag | Yes | Yes | Yes | Yes | [6 empty] | 2021-05-06
WI_LO_VAV_mid_WITH_REHEAT ERV Flag | VAV_mid_WITH_REHEAT ERV Flag | Yes | Yes | Yes | Yes | [6 empty] | 2021-05-06
WI_LO_VAV_top_WITH_REHEAT ERV Flag | VAV_top_WITH_REHEAT ERV Flag | Yes | Yes | Yes | Yes | [6 empty] | 2021-05-06
WI_LO_COOLSYS1 CHILLER1 Capacity [ton] | COOLSYS1 CHILLER1 Capacity [ton] | 425.4285 | 385.281 | 411.1269 | 369.1894 | [6 empty] | 2021-05-06
WI_LO_COOLSYS1 CHILLER2 Capacity [ton] | COOLSYS1 CHILLER2 Capacity [ton] | 425.4285 | 385.281 | 411.1269 | 369.1894 | [6 empty] | 2021-05-06
WI_LO_TOWERWATERSYS COOLTOWER 1 Capacity [ton] | TOWERWATERSYS COOLTOWER 1 Capacity [ton] | 403.8132 | 365.7055 | 390.2399 | 350.4256 | [6 empty] | 2021-05-06
WI_LO_TOWERWATERSYS COOLTOWER 2 Capacity [ton] | TOWERWATERSYS COOLTOWER 2 Capacity [ton] | 403.8132 | 365.7055 | 390.2399 | 350.4256 | [6 empty] | 2021-05-06
WI_LO_HEATSYS1 BOILER Capacity [MMBTU/h] | HEATSYS1 BOILER Capacity [MMBTU/h] | 5052.2372 | 4484.359 | 5246.7179 | 4605.862 | [6 empty] | 2021-05-06
WI_LO_COOLSYS1 PUMP Flow Rate [gal/min] | COOLSYS1 PUMP Flow Rate [gal/min] | 0 | 0 | 0 | 0 | [6 empty] | 2021-05-06
WI_LO_COOLSYS1 CHILLER1 PUMP Flow Rate [gal/min] | COOLSYS1 CHILLER1 PUMP Flow Rate [gal/min] | 670.3688 | 607.0119 | 647.7837 | 581.588 | [6 empty] | 2021-05-06
WI_LO_COOLSYS1 CHILLER2 PUMP Flow Rate [gal/min] | COOLSYS1 CHILLER2 PUMP Flow Rate [gal/min] | 670.3688 | 607.0119 | 647.7837 | 581.588 | [6 empty] | 2021-05-06
WI_LO_COOLSYS1 PUMP SECONDARY Flow Rate [gal/min] | COOLSYS1 PUMP SECONDARY Flow Rate [gal/min] | 1340.7376 | 1214.0238 | 1295.5674 | 1163.176 | [6 empty] | 2021-05-06
WI_LO_HEATSYS1 PUMP Flow Rate [gal/min] | HEATSYS1 PUMP Flow Rate [gal/min] | 1037.0375 | 920.4742 | 1076.9581 | 945.4131 | [6 empty] | 2021-05-06
WI_LO_TOWERWATERSYS PUMP Flow Rate [gal/min] | TOWERWATERSYS PUMP Flow Rate [gal/min] | 2347.1159 | 2125.6868 | 2268.1812 | 2036.7665 | [6 empty] | 2021-05-06
WI_LO_PLANT CIRC PUMP Flow Rate [gal/min] | PLANT CIRC PUMP Flow Rate [gal/min] | 210.7491 | 209.9724 | 210.8695 | 209.695 | [6 empty] | 2021-05-06
WI_LO_COOLSYS1 PUMP SECONDARY Pressure setpoint reset [yes,no] | COOLSYS1 PUMP SECONDARY Pressure setpoint reset [yes,no] | pump_ride_on_curve | pump_ride_on_curve | pump_ride_on_curve | pump_ride_on_curve | [6 empty] | 2021-05-06
WI_LO_COOLSYS1 CHILLER1 PUMP Pump Power [hp] | COOLSYS1 CHILLER1 PUMP Pump Power [hp] | 3.6164 | 3.2422 | 3.4946 | 3.1064 | [6 empty] | 2021-05-06
WI_LO_COOLSYS1 CHILLER2 PUMP Pump Power [hp] | COOLSYS1 CHILLER2 PUMP Pump Power [hp] | 3.6164 | 3.2422 | 3.4946 | 3.1064 | [6 empty] | 2021-05-06
WI_LO_COOLSYS1 PUMP SECONDARY Pump Power [hp] | COOLSYS1 PUMP SECONDARY Pump Power [hp] | 21.6984 | 19.4532 | 20.9674 | 18.6384 | [6 empty] | 2021-05-06
WI_LO_HEATSYS1 PUMP Pump Power [hp] | HEATSYS1 PUMP Pump Power [hp] | 22.4162 | 19.6996 | 23.2791 | 20.2333 | [6 empty] | 2021-05-06
WI_LO_TOWERWATERSYS PUMP Pump Power [hp] | TOWERWATERSYS PUMP Pump Power [hp] | 42.023 | 37.6805 | 40.6103 | 36.1067 | [6 empty] | 2021-05-06
WI_LO_PLANT CIRC PUMP Pump Power [hp] | PLANT CIRC PUMP Pump Power [hp] | 4.5477 | 4.486 | 4.5503 | 4.4801 | [6 empty] | 2021-05-06
WI_LO_Datacenter PLANT CIRC PUMP Pump Power [hp] | Datacenter PLANT CIRC PUMP Pump Power [hp] | 4.5477 | 4.486 | 4.5503 | 4.4801 | [6 empty] | 2021-05-06
WI_LO_ZN_VAV_BOXes_Max_Reheat_Water_Flow_GPM | ZN_VAV_BOXes_Max_Reheat_Water_Flow_GPM | 527.8809 | 508.5028 | 521.8442 | 501.6671 | [6 empty] | 2021-05-06
WI_LO_COOLSYS1 PUMP SECONDARY VSD | COOLSYS1 PUMP SECONDARY VSD | No | No | No | No | [6 empty] | 2021-05-06
WI_LO_HEATSYS1 PUMP VSD | HEATSYS1 PUMP VSD | No | No | No | No | [6 empty] | 2021-05-06
WI_LO_DATACENTER BASEMENT Cooling Capacity [ton] | DATACENTER BASEMENT Cooling Capacity [ton] | 122.7593 | 122.4457 | 122.6631 | 122.2903 | [6 empty] | 2021-05-06
WI_LO_DATACENTER BOT Cooling Capacity [ton] | DATACENTER BOT Cooling Capacity [ton] | 2.734 | 2.7102 | 2.7475 | 2.7059 | [6 empty] | 2021-05-06
WI_LO_DATACENTER MID Cooling Capacity [ton] | DATACENTER MID Cooling Capacity [ton] | 26.2161 | 26.0053 | 26.3734 | 25.967 | [6 empty] | 2021-05-06
WI_LO_DATACENTER TOP Cooling Capacity [ton] | DATACENTER TOP Cooling Capacity [ton] | 2.6681 | 2.6477 | 2.6825 | 2.6423 | [6 empty] | 2021-05-06
id | item | Zone5A(WI-Milwaukee-WI) ASHRAE901-state_STD2016 | Zone5A(WI-Milwaukee-WI) ASHRAE901-state_STD2019 | Zone6A(WI-GreenBay-WI) ASHRAE901-state_STD2016 | Zone6A(WI-GreenBay-WI) ASHRAE901-state_STD2019 | [6 empty] | 2021-05-06
WI_RS_PSZ-AC:1 Cooling Capacity [ton] | PSZ-AC:1 Cooling Capacity [ton] | 10.5411 | 10.1458 | 9.915 | 9.4511 | [6 empty] | 2021-05-06
WI_RS_PSZ-AC:2 Cooling Capacity [ton] | PSZ-AC:2 Cooling Capacity [ton] | 49.7409 | 48.272 | 48.4319 | 46.5981 | [6 empty] | 2021-05-06
WI_RS_PSZ-AC:3 Cooling Capacity [ton] | PSZ-AC:3 Cooling Capacity [ton] | 6.5156 | 6.3525 | 6.1209 | 5.953 | [6 empty] | 2021-05-06
WI_RS_PSZ-AC:4 Cooling Capacity [ton] | PSZ-AC:4 Cooling Capacity [ton] | 5.3236 | 5.1647 | 4.9213 | 4.7271 | [6 empty] | 2021-05-06
WI_RS_PSZ-AC:1 Supply Flow Rate [cfm] | PSZ-AC:1 Supply Flow Rate [cfm] | 4004.6832 | 3729.2288 | 3792.7952 | 3496.152 | [6 empty] | 2021-05-06
WI_RS_PSZ-AC:2 Supply Flow Rate [cfm] | PSZ-AC:2 Supply Flow Rate [cfm] | 15679.712 | 14832.16 | 15361.88 | 14535.5168 | [6 empty] | 2021-05-06
WI_RS_PSZ-AC:3 Supply Flow Rate [cfm] | PSZ-AC:3 Supply Flow Rate [cfm] | 2330.768 | 2267.2016 | 2246.0128 | 2161.2576 | [6 empty] | 2021-05-06
WI_RS_PSZ-AC:4 Supply Flow Rate [cfm] | PSZ-AC:4 Supply Flow Rate [cfm] | 1779.8592 | 1716.2928 | 1695.104 | 1589.16 | [6 empty] | 2021-05-06
WI_RS_PSZ-AC:1 OA Rate [cfm] | PSZ-AC:1 OA Rate [cfm] | 490.669 | 490.669 | 490.669 | 490.669 | [6 empty] | 2021-05-06
WI_RS_PSZ-AC:2 OA Rate [cfm] | PSZ-AC:2 OA Rate [cfm] | 4005.1282 | 4005.1282 | 4005.1282 | 4005.1282 | [6 empty] | 2021-05-06
WI_RS_PSZ-AC:3 OA Rate [cfm] | PSZ-AC:3 OA Rate [cfm] | 377.3937 | 377.3937 | 377.3937 | 377.3937 | [6 empty] | 2021-05-06
WI_RS_PSZ-AC:4 OA Rate [cfm] | PSZ-AC:4 OA Rate [cfm] | 377.3937 | 377.3937 | 377.3937 | 377.3937 | [6 empty] | 2021-05-06
WI_RS_PSZ-AC:1 OA Damper [gravity, motorized] | PSZ-AC:1 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2021-05-06
WI_RS_PSZ-AC:2 OA Damper [gravity, motorized] | PSZ-AC:2 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2021-05-06
WI_RS_PSZ-AC:3 OA Damper [gravity, motorized] | PSZ-AC:3 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2021-05-06
WI_RS_PSZ-AC:4 OA Damper [gravity, motorized] | PSZ-AC:4 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2021-05-06
WI_RS_PSZ-AC:1 Heating Capacity [kBtu/hr] | PSZ-AC:1 Heating Capacity [kBtu/hr] | 182.3256 | 170.9379 | 176.6149 | 164.0076 | [6 empty] | 2021-05-06
WI_RS_PSZ-AC:2 Heating Capacity [kBtu/hr] | PSZ-AC:2 Heating Capacity [kBtu/hr] | 868.2732 | 831.8957 | 877.3236 | 844.9733 | [6 empty] | 2021-05-06
WI_RS_PSZ-AC:3 Heating Capacity [kBtu/hr] | PSZ-AC:3 Heating Capacity [kBtu/hr] | 113.9735 | 111.2177 | 112.9718 | 109.9652 | [6 empty] | 2021-05-06
WI_RS_PSZ-AC:4 Heating Capacity [kBtu/hr] | PSZ-AC:4 Heating Capacity [kBtu/hr] | 93.9137 | 90.849 | 92.0987 | 88.4078 | [6 empty] | 2021-05-06
id | item | Zone5A(WI-Milwaukee-WI) ASHRAE901-state_STD2016 | Zone5A(WI-Milwaukee-WI) ASHRAE901-state_STD2019 | Zone6A(WI-GreenBay-WI) ASHRAE901-state_STD2016 | Zone6A(WI-GreenBay-WI) ASHRAE901-state_STD2019 | [6 empty] | 2021-05-06
WI_PS_VAV_POD_1 Cooling Capacity [ton] | VAV_POD_1 Cooling Capacity [ton] | 19.0876 | 18.4596 | 19.0333 | 18.3072 | [6 empty] | 2021-05-06
WI_PS_VAV_POD_2 Cooling Capacity [ton] | VAV_POD_2 Cooling Capacity [ton] | 18.8786 | 18.4111 | 18.806 | 18.2603 | [6 empty] | 2021-05-06
WI_PS_VAV_POD_3 Cooling Capacity [ton] | VAV_POD_3 Cooling Capacity [ton] | 17.3904 | 16.5738 | 17.3397 | 16.2854 | [6 empty] | 2021-05-06
WI_PS_VAV_OTHER Cooling Capacity [ton] | VAV_OTHER Cooling Capacity [ton] | 26.5409 | 24.936 | 26.4101 | 24.493 | [6 empty] | 2021-05-06
WI_PS_PSZ-AC_1:6 Cooling Capacity [ton] | PSZ-AC_1:6 Cooling Capacity [ton] | 8.4182 | 8.1533 | 8.1925 | 7.911 | [6 empty] | 2021-05-06
WI_PS_PSZ-AC_2:5 Cooling Capacity [ton] | PSZ-AC_2:5 Cooling Capacity [ton] | 5.4941 | 5.4638 | 5.4118 | 5.3272 | [6 empty] | 2021-05-06
WI_PS_PSZ-AC_2:7 Cooling Capacity [ton] | PSZ-AC_2:7 Cooling Capacity [ton] | 10.5074 | 10.5074 | 10.5074 | 10.5074 | [6 empty] | 2021-05-06
WI_PS_VAV_POD_1 Supply Flow Rate [cfm] | VAV_POD_1 Supply Flow Rate [cfm] | 5720.976 | 5530.2768 | 5720.976 | 5487.8992 | [6 empty] | 2021-05-06
WI_PS_VAV_POD_2 Supply Flow Rate [cfm] | VAV_POD_2 Supply Flow Rate [cfm] | 5657.4096 | 5530.2768 | 5636.2208 | 5487.8992 | [6 empty] | 2021-05-06
WI_PS_VAV_POD_3 Supply Flow Rate [cfm] | VAV_POD_3 Supply Flow Rate [cfm] | 5212.4448 | 4979.368 | 5212.4448 | 4894.6128 | [6 empty] | 2021-05-06
WI_PS_VAV_OTHER Supply Flow Rate [cfm] | VAV_OTHER Supply Flow Rate [cfm] | 7966.9888 | 7479.6464 | 7924.6112 | 7352.5136 | [6 empty] | 2021-05-06
WI_PS_PSZ-AC_2:5 Supply Flow Rate [cfm] | PSZ-AC_2:5 Supply Flow Rate [cfm] | 1652.7264 | 1631.5376 | 1631.5376 | 1589.16 | [6 empty] | 2021-05-06
WI_PS_PSZ-AC_1:6 Supply Flow Rate [cfm] | PSZ-AC_1:6 Supply Flow Rate [cfm] | 2585.0336 | 2479.0896 | 2585.0336 | 2457.9008 | [6 empty] | 2021-05-06
WI_PS_PSZ-AC_2:7 Supply Flow Rate [cfm] | PSZ-AC_2:7 Supply Flow Rate [cfm] | 3157.1312 | 3157.1312 | 3157.1312 | 3157.1312 | [6 empty] | 2021-05-06
WI_PS_Supply Air Temp. Reset Flag | Supply Air Temp. Reset Flag | Yes | Yes | Yes | Yes | [6 empty] | 2021-05-06
WI_PS_VAV_POD_1 OA Rate [cfm] | VAV_POD_1 OA Rate [cfm] | 5727.8836 | 5539.4304 | 5711.5894 | 5493.7049 | [6 empty] | 2021-05-06
WI_PS_VAV_POD_2 OA Rate [cfm] | VAV_POD_2 OA Rate [cfm] | 5664.0629 | 5524.8525 | 5641.0519 | 5479.6356 | [6 empty] | 2021-05-06
WI_PS_VAV_POD_3 OA Rate [cfm] | VAV_POD_3 OA Rate [cfm] | 5217.0852 | 4973.5411 | 5203.3548 | 4886.9848 | [6 empty] | 2021-05-06
WI_PS_VAV_OTHER OA Rate [cfm] | VAV_OTHER OA Rate [cfm] | 3736.1787 | 2988.8921 | 3736.1787 | 2988.8921 | [6 empty] | 2021-05-06
WI_PS_PSZ-AC_2:5 OA Rate [cfm] | PSZ-AC_2:5 OA Rate [cfm] | 1152.7343 | 1152.7343 | 1152.7343 | 1152.7343 | [6 empty] | 2021-05-06
WI_PS_PSZ-AC_1:6 OA Rate [cfm] | PSZ-AC_1:6 OA Rate [cfm] | 539.9118 | 539.9118 | 539.9118 | 539.9118 | [6 empty] | 2021-05-06
WI_PS_PSZ-AC_2:7 OA Rate [cfm] | PSZ-AC_2:7 OA Rate [cfm] | 3153.0841 | 3153.0841 | 3153.0841 | 3153.0841 | [6 empty] | 2021-05-06
WI_PS_VAV_POD_1 OA Damper [gravity, motorized] | VAV_POD_1 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2021-05-06
WI_PS_VAV_POD_2 OA Damper [gravity, motorized] | VAV_POD_2 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2021-05-06
WI_PS_VAV_POD_3 OA Damper [gravity, motorized] | VAV_POD_3 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2021-05-06
WI_PS_VAV_OTHER OA Damper [gravity, motorized] | VAV_OTHER OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2021-05-06
WI_PS_PSZ-AC_2:5 OA Damper [gravity, motorized] | PSZ-AC_2:5 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2021-05-06
WI_PS_PSZ-AC_1:6 OA Damper [gravity, motorized] | PSZ-AC_1:6 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2021-05-06
WI_PS_PSZ-AC_2:7 OA Damper [gravity, motorized] | PSZ-AC_2:7 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2021-05-06
WI_PS_VAV_POD_1 (economizer) | VAV_POD_1 (economizer) | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | [6 empty] | 2021-05-06
WI_PS_VAV_POD_2 (economizer) | VAV_POD_2 (economizer) | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | [6 empty] | 2021-05-06
WI_PS_VAV_POD_3 (economizer) | VAV_POD_3 (economizer) | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | [6 empty] | 2021-05-06
WI_PS_VAV_OTHER (economizer) | VAV_OTHER (economizer) | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | [6 empty] | 2021-05-06
WI_PS_PSZ-AC_2:5 (economizer) | PSZ-AC_2:5 (economizer) | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | [6 empty] | 2021-05-06
WI_PS_PSZ-AC_1:6 (economizer) | PSZ-AC_1:6 (economizer) | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | [6 empty] | 2021-05-06
WI_PS_PSZ-AC_2:7 (economizer) | PSZ-AC_2:7 (economizer) | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | [6 empty] | 2021-05-06
WI_PS_VAV_Pod_1_ERV Flag | VAV_Pod_1_ERV Flag | Yes | Yes | Yes | Yes | [6 empty] | 2021-05-06
WI_PS_VAV_Pod_2_ERV Flag | VAV_Pod_2_ERV Flag | Yes | Yes | Yes | Yes | [6 empty] | 2021-05-06
WI_PS_VAV_Pod_3_ERV Flag | VAV_Pod_3_ERV Flag | Yes | Yes | Yes | Yes | [6 empty] | 2021-05-06
WI_PS_VAV_OTHER_ERV Flag | VAV_OTHER_ERV Flag | Yes | Yes | Yes | Yes | [6 empty] | 2021-05-06
WI_PS_PSZ_AC_2_5_ERV Flag | PSZ_AC_2_5_ERV Flag | No | Yes | Yes | Yes | [6 empty] | 2021-05-06
WI_PS_PSZ_AC_2_7_ERV Flag | PSZ_AC_2_7_ERV Flag | Yes | Yes | Yes | Yes | [6 empty] | 2021-05-06
WI_PS_HEATSYS1 Capacity [MMBTU/h] | HEATSYS1 Capacity [MMBTU/h] | 1.2395 | 1.1946 | 1.2854 | 1.2336 | [6 empty] | 2021-05-06
WI_PS_HEATSYS1 Flow Rate [gal/min] | HEATSYS1 Flow Rate [gal/min] | 127.2164 | 122.6054 | 131.9227 | 126.6026 | [6 empty] | 2021-05-06
WI_PS_VAV_POD_1 Fan Power [hp] | VAV_POD_1 Fan Power [hp] | 8.4503 | 8.1723 | 8.4263 | 8.1049 | [6 empty] | 2021-05-06
WI_PS_VAV_POD_2 Fan Power [hp] | VAV_POD_2 Fan Power [hp] | 8.3578 | 8.1508 | 8.3257 | 8.0841 | [6 empty] | 2021-05-06
WI_PS_VAV_POD_3 Fan Power [hp] | VAV_POD_3 Fan Power [hp] | 7.699 | 7.3375 | 7.6765 | 7.2098 | [6 empty] | 2021-05-06
WI_PS_VAV_OTHER Fan Power [hp] | VAV_OTHER Fan Power [hp] | 11.661 | 10.9559 | 11.6036 | 10.7612 | [6 empty] | 2021-05-06
WI_PS_HEATSYS1 Pump Power [hp] | HEATSYS1 Pump Power [hp] | 2.7499 | 2.624 | 2.8516 | 2.7095 | [6 empty] | 2021-05-06
WI_PS_PSZ-AC_1:6 Heating Capacity [kBtu/hr] | PSZ-AC_1:6 Heating Capacity [kBtu/hr] | 217.468 | 208.8836 | 220.1424 | 210.8898 | [6 empty] | 2021-05-06
WI_PS_PSZ-AC_2:5 Heating Capacity [kBtu/hr] | PSZ-AC_2:5 Heating Capacity [kBtu/hr] | 149.465 | 149.1357 | 155.7322 | 154.8152 | [6 empty] | 2021-05-06
WI_PS_PSZ-AC_2:7 Heating Capacity [kBtu/hr] | PSZ-AC_2:7 Heating Capacity [kBtu/hr] | 359.8082 | 359.8082 | 379.4168 | 379.4168 | [6 empty] | 2021-05-06
WI_PS_ZN_VAV_BOXes_Max_Reheat_Water_Flow_GPM | ZN_VAV_BOXes_Max_Reheat_Water_Flow_GPM | 80.0131 | 77.4293 | 80.1905 | 77.5609 | [6 empty] | 2021-05-06
id | item | Zone5A(WI-Milwaukee-WI) ASHRAE901-state_STD2016 | Zone5A(WI-Milwaukee-WI) ASHRAE901-state_STD2019 | Zone6A(WI-GreenBay-WI) ASHRAE901-state_STD2016 | Zone6A(WI-GreenBay-WI) ASHRAE901-state_STD2019 | [6 empty] | 2021-05-06
WI_SH_SAC_FRONTOFFICE Cooling Capacity [ton] | SAC_FRONTOFFICE Cooling Capacity [ton] | 2.3539 | 2.2303 | 2.2203 | 2.0964 | [6 empty] | 2021-05-06
WI_SH_SAC_FRONTLOUNGE Cooling Capacity [ton] | SAC_FRONTLOUNGE Cooling Capacity [ton] | 6.1323 | 5.8235 | 5.9977 | 5.6774 | [6 empty] | 2021-05-06
WI_SH_SAC_MEETINGROOM Cooling Capacity [ton] | SAC_MEETINGROOM Cooling Capacity [ton] | 2.9221 | 2.8294 | 2.8733 | 2.7779 | [6 empty] | 2021-05-06
WI_SH_SAC_EXC_EMPLGE_RESTRM Cooling Capacity [ton] | SAC_EXC_EMPLGE_RESTRM Cooling Capacity [ton] | 5.9624 | 5.9208 | 5.8142 | 5.7682 | [6 empty] | 2021-05-06
WI_SH_SAC_FO_ADDAQ SUPPLY FAN Supply Flow Rate [cfm] | SAC_FO_ADDAQ SUPPLY FAN Supply Flow Rate [cfm] | 783.9856 | 741.608 | 762.7968 | 699.2304 | [6 empty] | 2021-05-06
WI_SH_SAC_FL_ADDAQ SUPPLY FAN Supply Flow Rate [cfm] | SAC_FL_ADDAQ SUPPLY FAN Supply Flow Rate [cfm] | 1843.4256 | 1737.4816 | 1801.048 | 1695.104 | [6 empty] | 2021-05-06
WI_SH_SAC_MR_ADDAQ SUPPLY FAN Supply Flow Rate [cfm] | SAC_MR_ADDAQ SUPPLY FAN Supply Flow Rate [cfm] | 868.7408 | 847.552 | 868.7408 | 826.3632 | [6 empty] | 2021-05-06
WI_SH_SAC_EXC_ADDAQ SUPPLY FAN Supply Flow Rate [cfm] | SAC_EXC_ADDAQ SUPPLY FAN Supply Flow Rate [cfm] | 2203.6352 | 2182.4464 | 2203.6352 | 2182.4464 | [6 empty] | 2021-05-06
WI_SH_SAC_Exc_EmpLge_RestRm OA Rate [cfm] | SAC_Exc_EmpLge_RestRm OA Rate [cfm] | 199.9928 | 199.9928 | 199.9928 | 199.9928 | [6 empty] | 2021-05-06
WI_SH_SAC_FrontLounge OA Rate [cfm] | SAC_FrontLounge OA Rate [cfm] | 500.0133 | 500.0133 | 500.0133 | 500.0133 | [6 empty] | 2021-05-06
WI_SH_SAC_FrontOffice OA Rate [cfm] | SAC_FrontOffice OA Rate [cfm] | 119.2938 | 119.2938 | 119.2938 | 119.2938 | [6 empty] | 2021-05-06
WI_SH_SAC_MeetingRoom OA Rate [cfm] | SAC_MeetingRoom OA Rate [cfm] | 267.7629 | 267.7629 | 267.7629 | 267.7629 | [6 empty] | 2021-05-06
WI_SH_SAC_FrontLounge OA Damper [gravity, motorized] | SAC_FrontLounge OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2021-05-06
WI_SH_SAC_FrontOffice (economizer) | SAC_FrontOffice (economizer) | No | No | No | No | [6 empty] | 2021-05-06
WI_SH_SAC_FrontLounge (economizer) | SAC_FrontLounge (economizer) | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | [6 empty] | 2021-05-06
WI_SH_SAC_MeetingRoom (economizer) | SAC_MeetingRoom (economizer) | No | No | No | No | [6 empty] | 2021-05-06
WI_SH_SAC_Exc_EmpLge_RestRm (economizer) | SAC_Exc_EmpLge_RestRm (economizer) | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | [6 empty] | 2021-05-06
WI_SH_SAC_FRONTOFFICE Heating Capacity [kBtu/hr] | SAC_FRONTOFFICE Heating Capacity [kBtu/hr] | 37.3976 | 35.6022 | 37.1889 | 35.377 | [6 empty] | 2021-05-06
WI_SH_SAC_FRONTLOUNGE Heating Capacity [kBtu/hr] | SAC_FRONTLOUNGE Heating Capacity [kBtu/hr] | 105.2041 | 101.8747 | 106.8405 | 103.389 | [6 empty] | 2021-05-06
WI_SH_SAC_MEETINGROOM Heating Capacity [kBtu/hr] | SAC_MEETINGROOM Heating Capacity [kBtu/hr] | 52.4371 | 51.4369 | 53.5652 | 52.5379 | [6 empty] | 2021-05-06
WI_SH_SAC_EXC_EMPLGE_RESTRM Heating Capacity [kBtu/hr] | SAC_EXC_EMPLGE_RESTRM Heating Capacity [kBtu/hr] | 94.7503 | 94.0936 | 96.0223 | 95.2724 | [6 empty] | 2021-05-06
id | item | Zone5A(WI-Milwaukee-WI) ASHRAE901-state_STD2016 | Zone5A(WI-Milwaukee-WI) ASHRAE901-state_STD2019 | Zone6A(WI-GreenBay-WI) ASHRAE901-state_STD2016 | Zone6A(WI-GreenBay-WI) ASHRAE901-state_STD2019 | [6 empty] | 2021-05-06
WI_MA_SPLIT GSW COOLING COIL Cooling Capacity [ton] | SPLIT GSW COOLING COIL Cooling Capacity [ton] | 0.8796 | 0.86507 | 0.83008 | 0.79983 | [6 empty] | 2021-05-06
WI_MA_SPLIT GNW COOLING COIL Cooling Capacity [ton] | SPLIT GNW COOLING COIL Cooling Capacity [ton] | 0.83431 | 0.82047 | 0.77881 | 0.75162 | [6 empty] | 2021-05-06
WI_MA_SPLIT OFFICE COOLING COIL Cooling Capacity [ton] | SPLIT OFFICE COOLING COIL Cooling Capacity [ton] | 1.6951 | 1.5599 | 1.7447 | 1.5993 | [6 empty] | 2021-05-06
WI_MA_SPLIT GNE COOLING COIL Cooling Capacity [ton] | SPLIT GNE COOLING COIL Cooling Capacity [ton] | 0.72213 | 0.71012 | 0.66472 | 0.64275 | [6 empty] | 2021-05-06
WI_MA_SPLIT GN1 COOLING COIL Cooling Capacity [ton] | SPLIT GN1 COOLING COIL Cooling Capacity [ton] | 0.61575 | 0.60647 | 0.56297 | 0.5487 | [6 empty] | 2021-05-06
WI_MA_SPLIT GN2 COOLING COIL Cooling Capacity [ton] | SPLIT GN2 COOLING COIL Cooling Capacity [ton] | 0.61345 | 0.60423 | 0.56058 | 0.54646 | [6 empty] | 2021-05-06
WI_MA_SPLIT GS1 COOLING COIL Cooling Capacity [ton] | SPLIT GS1 COOLING COIL Cooling Capacity [ton] | 0.66269 | 0.65213 | 0.6206 | 0.60264 | [6 empty] | 2021-05-06
WI_MA_SPLIT GS2 COOLING COIL Cooling Capacity [ton] | SPLIT GS2 COOLING COIL Cooling Capacity [ton] | 0.69606 | 0.68047 | 0.65617 | 0.63334 | [6 empty] | 2021-05-06
WI_MA_SPLIT MSW COOLING COIL Cooling Capacity [ton] | SPLIT MSW COOLING COIL Cooling Capacity [ton] | 2.1776 | 2.1451 | 2.0441 | 1.9717 | [6 empty] | 2021-05-06
WI_MA_SPLIT MNW COOLING COIL Cooling Capacity [ton] | SPLIT MNW COOLING COIL Cooling Capacity [ton] | 2.0956 | 2.0646 | 1.9461 | 1.8801 | [6 empty] | 2021-05-06
WI_MA_SPLIT MSE COOLING COIL Cooling Capacity [ton] | SPLIT MSE COOLING COIL Cooling Capacity [ton] | 1.906 | 1.8782 | 1.7861 | 1.7207 | [6 empty] | 2021-05-06
WI_MA_SPLIT MNE COOLING COIL Cooling Capacity [ton] | SPLIT MNE COOLING COIL Cooling Capacity [ton] | 1.7438 | 1.7134 | 1.5756 | 1.5108 | [6 empty] | 2021-05-06
WI_MA_SPLIT MN1 COOLING COIL Cooling Capacity [ton] | SPLIT MN1 COOLING COIL Cooling Capacity [ton] | 1.4088 | 1.391 | 1.2827 | 1.2545 | [6 empty] | 2021-05-06
WI_MA_SPLIT MN2 COOLING COIL Cooling Capacity [ton] | SPLIT MN2 COOLING COIL Cooling Capacity [ton] | 1.4024 | 1.3847 | 1.276 | 1.2482 | [6 empty] | 2021-05-06
WI_MA_SPLIT MS1 COOLING COIL Cooling Capacity [ton] | SPLIT MS1 COOLING COIL Cooling Capacity [ton] | 1.4909 | 1.4713 | 1.3825 | 1.3486 | [6 empty] | 2021-05-06
WI_MA_SPLIT MS2 COOLING COIL Cooling Capacity [ton] | SPLIT MS2 COOLING COIL Cooling Capacity [ton] | 1.4845 | 1.4651 | 1.3759 | 1.3425 | [6 empty] | 2021-05-06
WI_MA_SPLIT TSW COOLING COIL Cooling Capacity [ton] | SPLIT TSW COOLING COIL Cooling Capacity [ton] | 1.3457 | 1.3281 | 1.2648 | 1.2242 | [6 empty] | 2021-05-06
WI_MA_SPLIT TNW COOLING COIL Cooling Capacity [ton] | SPLIT TNW COOLING COIL Cooling Capacity [ton] | 1.2913 | 1.2745 | 1.2037 | 1.1658 | [6 empty] | 2021-05-06
WI_MA_SPLIT TSE COOLING COIL Cooling Capacity [ton] | SPLIT TSE COOLING COIL Cooling Capacity [ton] | 1.2105 | 1.1951 | 1.1331 | 1.0973 | [6 empty] | 2021-05-06
WI_MA_SPLIT TNE COOLING COIL Cooling Capacity [ton] | SPLIT TNE COOLING COIL Cooling Capacity [ton] | 1.1111 | 1.0984 | 1.0156 | 0.99159 | [6 empty] | 2021-05-06
WI_MA_SPLIT TN1 COOLING COIL Cooling Capacity [ton] | SPLIT TN1 COOLING COIL Cooling Capacity [ton] | 0.89875 | 0.86494 | 0.80082 | 0.78567 | [6 empty] | 2021-05-06
WI_MA_SPLIT TN2 COOLING COIL Cooling Capacity [ton] | SPLIT TN2 COOLING COIL Cooling Capacity [ton] | 0.90029 | 0.89046 | 0.83002 | 0.81368 | [6 empty] | 2021-05-06
WI_MA_SPLIT TS1 COOLING COIL Cooling Capacity [ton] | SPLIT TS1 COOLING COIL Cooling Capacity [ton] | 0.99081 | 0.97874 | 0.93621 | 0.9118 | [6 empty] | 2021-05-06
WI_MA_SPLIT TS2 COOLING COIL Cooling Capacity [ton] | SPLIT TS2 COOLING COIL Cooling Capacity [ton] | 0.99315 | 0.98184 | 0.93983 | 0.91406 | [6 empty] | 2021-05-06
WI_MA_Split GN1 Furnace with DX Cooling OA Rate [cfm] | Split GN1 Furnace with DX Cooling OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | [6 empty] | 2021-05-06
WI_MA_Split GN2 Furnace with DX Cooling OA Rate [cfm] | Split GN2 Furnace with DX Cooling OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | [6 empty] | 2021-05-06
WI_MA_Split GNE Furnace with DX Cooling OA Rate [cfm] | Split GNE Furnace with DX Cooling OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | [6 empty] | 2021-05-06
WI_MA_Split GNW Furnace with DX Cooling OA Rate [cfm] | Split GNW Furnace with DX Cooling OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | [6 empty] | 2021-05-06
WI_MA_Split GS1 Furnace with DX Cooling OA Rate [cfm] | Split GS1 Furnace with DX Cooling OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | [6 empty] | 2021-05-06
WI_MA_Split GS2 Furnace with DX Cooling OA Rate [cfm] | Split GS2 Furnace with DX Cooling OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | [6 empty] | 2021-05-06
WI_MA_Split GSW Furnace with DX Cooling OA Rate [cfm] | Split GSW Furnace with DX Cooling OA Rate [cfm] | 56.9945 | 56.9945 | 56.9945 | 56.9945 | [6 empty] | 2021-05-06
WI_MA_Split MN1 Furnace with DX Cooling OA Rate [cfm] | Split MN1 Furnace with DX Cooling OA Rate [cfm] | 109.9824 | 109.9824 | 109.9824 | 109.9824 | [6 empty] | 2021-05-06
WI_MA_Split MN2 Furnace with DX Cooling OA Rate [cfm] | Split MN2 Furnace with DX Cooling OA Rate [cfm] | 109.9824 | 109.9824 | 109.9824 | 109.9824 | [6 empty] | 2021-05-06
WI_MA_Split MNE Furnace with DX Cooling OA Rate [cfm] | Split MNE Furnace with DX Cooling OA Rate [cfm] | 109.9824 | 109.9824 | 109.9824 | 109.9824 | [6 empty] | 2021-05-06
WI_MA_Split MNW Furnace with DX Cooling OA Rate [cfm] | Split MNW Furnace with DX Cooling OA Rate [cfm] | 109.9824 | 109.9824 | 109.9824 | 109.9824 | [6 empty] | 2021-05-06
WI_MA_Split MS1 Furnace with DX Cooling OA Rate [cfm] | Split MS1 Furnace with DX Cooling OA Rate [cfm] | 109.9824 | 109.9824 | 109.9824 | 109.9824 | [6 empty] | 2021-05-06
WI_MA_Split MS2 Furnace with DX Cooling OA Rate [cfm] | Split MS2 Furnace with DX Cooling OA Rate [cfm] | 109.9824 | 109.9824 | 109.9824 | 109.9824 | [6 empty] | 2021-05-06
WI_MA_Split MSE Furnace with DX Cooling OA Rate [cfm] | Split MSE Furnace with DX Cooling OA Rate [cfm] | 109.9824 | 109.9824 | 109.9824 | 109.9824 | [6 empty] | 2021-05-06
WI_MA_Split MSW Furnace with DX Cooling OA Rate [cfm] | Split MSW Furnace with DX Cooling OA Rate [cfm] | 109.9824 | 109.9824 | 109.9824 | 109.9824 | [6 empty] | 2021-05-06
WI_MA_Split Office Furnace with DX Cooling OA Rate [cfm] | Split Office Furnace with DX Cooling OA Rate [cfm] | 80.7372 | 80.7372 | 80.7372 | 80.7372 | [6 empty] | 2021-05-06
WI_MA_Split TN1 Furnace with DX Cooling OA Rate [cfm] | Split TN1 Furnace with DX Cooling OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | [6 empty] | 2021-05-06
WI_MA_Split TN2 Furnace with DX Cooling OA Rate [cfm] | Split TN2 Furnace with DX Cooling OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | [6 empty] | 2021-05-06
WI_MA_Split TNE Furnace with DX Cooling OA Rate [cfm] | Split TNE Furnace with DX Cooling OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | [6 empty] | 2021-05-06
WI_MA_Split TNW Furnace with DX Cooling OA Rate [cfm] | Split TNW Furnace with DX Cooling OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | [6 empty] | 2021-05-06
WI_MA_Split TS1 Furnace with DX Cooling OA Rate [cfm] | Split TS1 Furnace with DX Cooling OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | [6 empty] | 2021-05-06
WI_MA_Split TS2 Furnace with DX Cooling OA Rate [cfm] | Split TS2 Furnace with DX Cooling OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | [6 empty] | 2021-05-06
WI_MA_Split TSE Furnace with DX Cooling OA Rate [cfm] | Split TSE Furnace with DX Cooling OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | [6 empty] | 2021-05-06
WI_MA_Split TSW Furnace with DX Cooling OA Rate [cfm] | Split TSW Furnace with DX Cooling OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | [6 empty] | 2021-05-06
WI_MA_SPLIT GSW HEATING COIL Heating Capacity [kBtu/hr] | SPLIT GSW HEATING COIL Heating Capacity [kBtu/hr] | 12.0113 | 12.0702 | 12.0411 | 12.1005 | [6 empty] | 2021-05-06
WI_MA_SPLIT GNW HEATING COIL Heating Capacity [kBtu/hr] | SPLIT GNW HEATING COIL Heating Capacity [kBtu/hr] | 11.9392 | 11.9981 | 11.9101 | 11.9696 | [6 empty] | 2021-05-06
WI_MA_SPLIT OFFICE HEATING COIL Heating Capacity [kBtu/hr] | SPLIT OFFICE HEATING COIL Heating Capacity [kBtu/hr] | 25.4257 | 25.5056 | 25.6932 | 25.7744 | [6 empty] | 2021-05-06
WI_MA_SPLIT GNE HEATING COIL Heating Capacity [kBtu/hr] | SPLIT GNE HEATING COIL Heating Capacity [kBtu/hr] | 11.9074 | 11.9664 | 11.881 | 11.9406 | [6 empty] | 2021-05-06
WI_MA_SPLIT GN1 HEATING COIL Heating Capacity [kBtu/hr] | SPLIT GN1 HEATING COIL Heating Capacity [kBtu/hr] | 8.7761 | 8.8351 | 8.9406 | 9.0002 | [6 empty] | 2021-05-06
WI_MA_SPLIT GN2 HEATING COIL Heating Capacity [kBtu/hr] | SPLIT GN2 HEATING COIL Heating Capacity [kBtu/hr] | 8.7751 | 8.8342 | 8.9398 | 8.9993 | [6 empty] | 2021-05-06
WI_MA_SPLIT GS1 HEATING COIL Heating Capacity [kBtu/hr] | SPLIT GS1 HEATING COIL Heating Capacity [kBtu/hr] | 8.7079 | 8.7668 | 8.9199 | 8.9793 | [6 empty] | 2021-05-06
WI_MA_SPLIT GS2 HEATING COIL Heating Capacity [kBtu/hr] | SPLIT GS2 HEATING COIL Heating Capacity [kBtu/hr] | 9.2223 | 9.282 | 9.4393 | 9.4996 | [6 empty] | 2021-05-06
WI_MA_SPLIT MSW HEATING COIL Heating Capacity [kBtu/hr] | SPLIT MSW HEATING COIL Heating Capacity [kBtu/hr] | 22.1487 | 22.278 | 21.4555 | 21.5851 | [6 empty] | 2021-05-06
WI_MA_SPLIT MNW HEATING COIL Heating Capacity [kBtu/hr] | SPLIT MNW HEATING COIL Heating Capacity [kBtu/hr] | 22.2727 | 22.4019 | 21.4681 | 21.5976 | [6 empty] | 2021-05-06
WI_MA_SPLIT MSE HEATING COIL Heating Capacity [kBtu/hr] | SPLIT MSE HEATING COIL Heating Capacity [kBtu/hr] | 22.0748 | 22.2041 | 21.3878 | 21.5174 | [6 empty] | 2021-05-06
WI_MA_SPLIT MNE HEATING COIL Heating Capacity [kBtu/hr] | SPLIT MNE HEATING COIL Heating Capacity [kBtu/hr] | 22.1987 | 22.328 | 21.4003 | 21.5298 | [6 empty] | 2021-05-06
WI_MA_SPLIT MN1 HEATING COIL Heating Capacity [kBtu/hr] | SPLIT MN1 HEATING COIL Heating Capacity [kBtu/hr] | 15.4285 | 15.5542 | 15.1981 | 15.3242 | [6 empty] | 2021-05-06
WI_MA_SPLIT MN2 HEATING COIL Heating Capacity [kBtu/hr] | SPLIT MN2 HEATING COIL Heating Capacity [kBtu/hr] | 15.4266 | 15.5523 | 15.1963 | 15.3225 | [6 empty] | 2021-05-06
WI_MA_SPLIT MS1 HEATING COIL Heating Capacity [kBtu/hr] | SPLIT MS1 HEATING COIL Heating Capacity [kBtu/hr] | 15.3144 | 15.4401 | 15.1955 | 15.3217 | [6 empty] | 2021-05-06
WI_MA_SPLIT MS2 HEATING COIL Heating Capacity [kBtu/hr] | SPLIT MS2 HEATING COIL Heating Capacity [kBtu/hr] | 15.3125 | 15.4382 | 15.1937 | 15.32 | [6 empty] | 2021-05-06
WI_MA_SPLIT TSW HEATING COIL Heating Capacity [kBtu/hr] | SPLIT TSW HEATING COIL Heating Capacity [kBtu/hr] | 15.3762 | 15.4381 | 15.0545 | 15.1166 | [6 empty] | 2021-05-06
WI_MA_SPLIT TNW HEATING COIL Heating Capacity [kBtu/hr] | SPLIT TNW HEATING COIL Heating Capacity [kBtu/hr] | 15.4478 | 15.5098 | 15.0682 | 15.1303 | [6 empty] | 2021-05-06
WI_MA_SPLIT TSE HEATING COIL Heating Capacity [kBtu/hr] | SPLIT TSE HEATING COIL Heating Capacity [kBtu/hr] | 15.3374 | 15.3992 | 15.0186 | 15.0807 | [6 empty] | 2021-05-06
WI_MA_SPLIT TNE HEATING COIL Heating Capacity [kBtu/hr] | SPLIT TNE HEATING COIL Heating Capacity [kBtu/hr] | 15.4089 | 15.4709 | 15.0322 | 15.0944 | [6 empty] | 2021-05-06
WI_MA_SPLIT TN1 HEATING COIL Heating Capacity [kBtu/hr] | SPLIT TN1 HEATING COIL Heating Capacity [kBtu/hr] | 11.6438 | 11.7056 | 11.6397 | 11.7017 | [6 empty] | 2021-05-06
WI_MA_SPLIT TN2 HEATING COIL Heating Capacity [kBtu/hr] | SPLIT TN2 HEATING COIL Heating Capacity [kBtu/hr] | 11.6427 | 11.7045 | 11.6387 | 11.7007 | [6 empty] | 2021-05-06
WI_MA_SPLIT TS1 HEATING COIL Heating Capacity [kBtu/hr] | SPLIT TS1 HEATING COIL Heating Capacity [kBtu/hr] | 11.5657 | 11.6274 | 11.6201 | 11.6821 | [6 empty] | 2021-05-06
WI_MA_SPLIT TS2 HEATING COIL Heating Capacity [kBtu/hr] | SPLIT TS2 HEATING COIL Heating Capacity [kBtu/hr] | 11.5646 | 11.6263 | 11.6191 | 11.6811 | [6 empty] | 2021-05-06
WI_MA_Split_GSW ERV Flag | Split_GSW ERV Flag | Yes | Yes | Yes | Yes | [6 empty] | 2021-05-06
WI_MA_Split_GNW ERV Flag | Split_GNW ERV Flag | Yes | Yes | Yes | Yes | [6 empty] | 2021-05-06
WI_MA_Split_GNE ERV Flag | Split_GNE ERV Flag | Yes | Yes | Yes | Yes | [6 empty] | 2021-05-06
WI_MA_Split_GN1 ERV Flag | Split_GN1 ERV Flag | Yes | Yes | Yes | Yes | [6 empty] | 2021-05-06
WI_MA_Split_GN2 ERV Flag | Split_GN2 ERV Flag | Yes | Yes | Yes | Yes | [6 empty] | 2021-05-06
WI_MA_Split_GS1 ERV Flag | Split_GS1 ERV Flag | Yes | Yes | Yes | Yes | [6 empty] | 2021-05-06
WI_MA_Split_GS2 ERV Flag | Split_GS2 ERV Flag | Yes | Yes | Yes | Yes | [6 empty] | 2021-05-06
WI_MA_Split_MSW ERV Flag | Split_MSW ERV Flag | Yes | Yes | Yes | Yes | [6 empty] | 2021-05-06
WI_MA_Split_MNW ERV Flag | Split_MNW ERV Flag | Yes | Yes | Yes | Yes | [6 empty] | 2021-05-06
WI_MA_Split_MSE ERV Flag | Split_MSE ERV Flag | Yes | Yes | Yes | Yes | [6 empty] | 2021-05-06
WI_MA_Split_MNE ERV Flag | Split_MNE ERV Flag | Yes | Yes | Yes | Yes | [6 empty] | 2021-05-06
WI_MA_Split_MN1 ERV Flag | Split_MN1 ERV Flag | Yes | Yes | Yes | Yes | [6 empty] | 2021-05-06
WI_MA_Split_MN2 ERV Flag | Split_MN2 ERV Flag | Yes | Yes | Yes | Yes | [6 empty] | 2021-05-06
WI_MA_Split_MS1 ERV Flag | Split_MS1 ERV Flag | Yes | Yes | Yes | Yes | [6 empty] | 2021-05-06
WI_MA_Split_MS2 ERV Flag | Split_MS2 ERV Flag | Yes | Yes | Yes | Yes | [6 empty] | 2021-05-06
WI_MA_Split_TSW ERV Flag | Split_TSW ERV Flag | Yes | Yes | Yes | Yes | [6 empty] | 2021-05-06
WI_MA_Split_TNW ERV Flag | Split_TNW ERV Flag | Yes | Yes | Yes | Yes | [6 empty] | 2021-05-06
WI_MA_Split_TSE ERV Flag | Split_TSE ERV Flag | Yes | Yes | Yes | Yes | [6 empty] | 2021-05-06
WI_MA_Split_TNE ERV Flag | Split_TNE ERV Flag | Yes | Yes | Yes | Yes | [6 empty] | 2021-05-06
WI_MA_Split_TN1 ERV Flag | Split_TN1 ERV Flag | Yes | Yes | Yes | Yes | [6 empty] | 2021-05-06
WI_MA_Split_TN2 ERV Flag | Split_TN2 ERV Flag | Yes | Yes | Yes | Yes | [6 empty] | 2021-05-06
WI_MA_Split_TS1 ERV Flag | Split_TS1 ERV Flag | Yes | Yes | Yes | Yes | [6 empty] | 2021-05-06
WI_MA_Split_TS2 ERV Flag | Split_TS2 ERV Flag | Yes | Yes | Yes | Yes | [6 empty] | 2021-05-06
id | item | Zone4A(WV-Charleston-WV) ASHRAE901-state_STD2016 | Zone4A(WV-Charleston-WV) ASHRAE901-state_STD2019 | Zone5A(WV-Elkins-WV) ASHRAE901-state_STD2016 | Zone5A(WV-Elkins-WV) ASHRAE901-state_STD2019 | [6 empty] | 2021-05-06
WV_SO_PSZ-AC:1 Cooling Capacity [ton] | PSZ-AC:1 Cooling Capacity [ton] | 1.8366 | 1.7437 | 1.7003 | 1.6084 | [6 empty] | 2021-05-06
WV_SO_PSZ-AC:2 Cooling Capacity [ton] | PSZ-AC:2 Cooling Capacity [ton] | 1.5866 | 1.5244 | 1.3959 | 1.3356 | [6 empty] | 2021-05-06
WV_SO_PSZ-AC:3 Cooling Capacity [ton] | PSZ-AC:3 Cooling Capacity [ton] | 1.1048 | 1.0661 | 0.9916 | 0.95384 | [6 empty] | 2021-05-06
WV_SO_PSZ-AC:4 Cooling Capacity [ton] | PSZ-AC:4 Cooling Capacity [ton] | 1.5349 | 1.4618 | 1.3535 | 1.275 | [6 empty] | 2021-05-06
WV_SO_PSZ-AC:5 Cooling Capacity [ton] | PSZ-AC:5 Cooling Capacity [ton] | 1.2988 | 1.2593 | 1.1913 | 1.1525 | [6 empty] | 2021-05-06
WV_SO_PSZ-AC:1 Supply Flow Rate [cfm] | PSZ-AC:1 Supply Flow Rate [cfm] | 656.8528 | 614.4752 | 678.0416 | 614.4752 | [6 empty] | 2021-05-06
WV_SO_PSZ-AC:2 Supply Flow Rate [cfm] | PSZ-AC:2 Supply Flow Rate [cfm] | 593.2864 | 550.9088 | 550.9088 | 529.72 | [6 empty] | 2021-05-06
WV_SO_PSZ-AC:3 Supply Flow Rate [cfm] | PSZ-AC:3 Supply Flow Rate [cfm] | 466.1536 | 444.9648 | 444.9648 | 423.776 | [6 empty] | 2021-05-06
WV_SO_PSZ-AC:4 Supply Flow Rate [cfm] | PSZ-AC:4 Supply Flow Rate [cfm] | 572.0976 | 529.72 | 529.72 | 487.3424 | [6 empty] | 2021-05-06
WV_SO_PSZ-AC:5 Supply Flow Rate [cfm] | PSZ-AC:5 Supply Flow Rate [cfm] | 550.9088 | 529.72 | 529.72 | 508.5312 | [6 empty] | 2021-05-06
WV_SO_PSZ-AC:1 OA Rate [cfm] | PSZ-AC:1 OA Rate [cfm] | 136.9178 | 136.9178 | 136.9178 | 136.9178 | [6 empty] | 2021-05-06
WV_SO_PSZ-AC:2 OA Rate [cfm] | PSZ-AC:2 OA Rate [cfm] | 103.7925 | 103.7925 | 103.7925 | 103.7925 | [6 empty] | 2021-05-06
WV_SO_PSZ-AC:3 OA Rate [cfm] | PSZ-AC:3 OA Rate [cfm] | 61.5711 | 61.5711 | 61.5711 | 61.5711 | [6 empty] | 2021-05-06
WV_SO_PSZ-AC:4 OA Rate [cfm] | PSZ-AC:4 OA Rate [cfm] | 103.7925 | 103.7925 | 103.7925 | 103.7925 | [6 empty] | 2021-05-06
WV_SO_PSZ-AC:5 OA Rate [cfm] | PSZ-AC:5 OA Rate [cfm] | 61.5711 | 61.5711 | 61.5711 | 61.5711 | [6 empty] | 2021-05-06
WV_SO_PSZ-AC:1 heating Capacity [kBtu/hr] | PSZ-AC:1 heating Capacity [kBtu/hr] | 13.6295 | 13.6295 | 14.3668 | 14.3668 | [6 empty] | 2021-05-06
WV_SO_PSZ-AC:2 heating Capacity [kBtu/hr] | PSZ-AC:2 heating Capacity [kBtu/hr] | 17.9325 | 17.7269 | 19.3723 | 19.1413 | [6 empty] | 2021-05-06
WV_SO_PSZ-AC:3 heating Capacity [kBtu/hr] | PSZ-AC:3 heating Capacity [kBtu/hr] | 10.8793 | 10.7694 | 11.6946 | 11.5705 | [6 empty] | 2021-05-06
WV_SO_PSZ-AC:4 heating Capacity [kBtu/hr] | PSZ-AC:4 heating Capacity [kBtu/hr] | 17.6857 | 17.5232 | 19.1738 | 18.985 | [6 empty] | 2021-05-06
WV_SO_PSZ-AC:5 heating Capacity [kBtu/hr] | PSZ-AC:5 heating Capacity [kBtu/hr] | 10.916 | 10.8023 | 11.7329 | 11.6052 | [6 empty] | 2021-05-06
id | item | Zone4A(WV-Charleston-WV) ASHRAE901-state_STD2016 | Zone4A(WV-Charleston-WV) ASHRAE901-state_STD2019 | Zone5A(WV-Elkins-WV) ASHRAE901-state_STD2016 | Zone5A(WV-Elkins-WV) ASHRAE901-state_STD2019 | [6 empty] | 2021-05-06
WV_LO_CAV_BAS Supply Flow Rate [cfm] | CAV_BAS Supply Flow Rate [cfm] | 12056.4272 | 11166.4976 | 12331.8816 | 11399.5744 | [6 empty] | 2021-05-06
WV_LO_VAV_BOT WITH REHEAT Supply Flow Rate [cfm] | VAV_BOT WITH REHEAT Supply Flow Rate [cfm] | 19853.9056 | 18900.4096 | 20235.304 | 19260.6192 | [6 empty] | 2021-05-06
WV_LO_VAV_MID WITH REHEAT Supply Flow Rate [cfm] | VAV_MID WITH REHEAT Supply Flow Rate [cfm] | 183897.5955 | 174701.6563 | 186842.8387 | 177392.6339 | [6 empty] | 2021-05-06
WV_LO_VAV_TOP WITH REHEAT Supply Flow Rate [cfm] | VAV_TOP WITH REHEAT Supply Flow Rate [cfm] | 19684.3952 | 18879.2208 | 19896.2832 | 19069.92 | [6 empty] | 2021-05-06
WV_LO_Supply Air Temp. Reset Flag | Supply Air Temp. Reset Flag | Yes | Yes | Yes | Yes | [6 empty] | 2021-05-06
WV_LO_CAV_BAS OA Rate [cfm] | CAV_BAS OA Rate [cfm] | 2542.8255 | 2542.8255 | 2542.8255 | 2542.8255 | [6 empty] | 2021-05-06
WV_LO_VAV_BOT WITH REHEAT OA Rate [cfm] | VAV_BOT WITH REHEAT OA Rate [cfm] | 5377.8022 | 4302.174 | 5377.8022 | 4302.174 | [6 empty] | 2021-05-06
WV_LO_VAV_MID WITH REHEAT OA Rate [cfm] | VAV_MID WITH REHEAT OA Rate [cfm] | 53777.9373 | 43021.7396 | 53777.9373 | 43021.7396 | [6 empty] | 2021-05-06
WV_LO_VAV_TOP WITH REHEAT OA Rate [cfm] | VAV_TOP WITH REHEAT OA Rate [cfm] | 5377.8022 | 4302.174 | 5377.8022 | 4302.174 | [6 empty] | 2021-05-06
WV_LO_AIRLOOP DATACENTER BASEMENT OA Rate [cfm] | AIRLOOP DATACENTER BASEMENT OA Rate [cfm] | 716.9654 | 716.9654 | 716.9654 | 716.9654 | [6 empty] | 2021-05-06
WV_LO_VAV_bot_WITH_REHEAT ERV Flag | VAV_bot_WITH_REHEAT ERV Flag | Yes | Yes | Yes | Yes | [6 empty] | 2021-05-06
WV_LO_VAV_mid_WITH_REHEAT ERV Flag | VAV_mid_WITH_REHEAT ERV Flag | Yes | Yes | Yes | Yes | [6 empty] | 2021-05-06
WV_LO_VAV_top_WITH_REHEAT ERV Flag | VAV_top_WITH_REHEAT ERV Flag | Yes | Yes | Yes | Yes | [6 empty] | 2021-05-06
WV_LO_COOLSYS1 CHILLER1 Capacity [ton] | COOLSYS1 CHILLER1 Capacity [ton] | 396.7611 | 358.4962 | 363.4577 | 331.1099 | [6 empty] | 2021-05-06
WV_LO_COOLSYS1 CHILLER2 Capacity [ton] | COOLSYS1 CHILLER2 Capacity [ton] | 396.7611 | 358.4962 | 363.4577 | 331.1099 | [6 empty] | 2021-05-06
WV_LO_TOWERWATERSYS COOLTOWER 1 Capacity [ton] | TOWERWATERSYS COOLTOWER 1 Capacity [ton] | 376.6009 | 340.2785 | 345.0898 | 314.3769 | [6 empty] | 2021-05-06
WV_LO_TOWERWATERSYS COOLTOWER 2 Capacity [ton] | TOWERWATERSYS COOLTOWER 2 Capacity [ton] | 376.6009 | 340.2785 | 345.0898 | 314.3769 | [6 empty] | 2021-05-06
WV_LO_HEATSYS1 BOILER Capacity [MMBTU/h] | HEATSYS1 BOILER Capacity [MMBTU/h] | 4169.7653 | 3691.4642 | 4500.1534 | 3968.7556 | [6 empty] | 2021-05-06
WV_LO_COOLSYS1 PUMP Flow Rate [gal/min] | COOLSYS1 PUMP Flow Rate [gal/min] | 0 | 0 | 0 | 0 | [6 empty] | 2021-05-06
WV_LO_COOLSYS1 CHILLER1 PUMP Flow Rate [gal/min] | COOLSYS1 CHILLER1 PUMP Flow Rate [gal/min] | 625.0686 | 561.8765 | 572.2743 | 521.2712 | [6 empty] | 2021-05-06
WV_LO_COOLSYS1 CHILLER2 PUMP Flow Rate [gal/min] | COOLSYS1 CHILLER2 PUMP Flow Rate [gal/min] | 625.0686 | 561.8765 | 572.2743 | 521.2712 | [6 empty] | 2021-05-06
WV_LO_COOLSYS1 PUMP SECONDARY Flow Rate [gal/min] | COOLSYS1 PUMP SECONDARY Flow Rate [gal/min] | 1250.1356 | 1123.753 | 1144.5502 | 1042.5423 | [6 empty] | 2021-05-06
WV_LO_HEATSYS1 PUMP Flow Rate [gal/min] | HEATSYS1 PUMP Flow Rate [gal/min] | 855.9 | 757.7215 | 923.7156 | 814.64 | [6 empty] | 2021-05-06
WV_LO_TOWERWATERSYS PUMP Flow Rate [gal/min] | TOWERWATERSYS PUMP Flow Rate [gal/min] | 2188.9296 | 1977.8033 | 2005.2244 | 1826.7497 | [6 empty] | 2021-05-06
WV_LO_PLANT CIRC PUMP Flow Rate [gal/min] | PLANT CIRC PUMP Flow Rate [gal/min] | 210.3068 | 209.4652 | 212.0789 | 211.2277 | [6 empty] | 2021-05-06
WV_LO_COOLSYS1 PUMP SECONDARY Pressure setpoint reset [yes,no] | COOLSYS1 PUMP SECONDARY Pressure setpoint reset [yes,no] | pump_ride_on_curve | pump_ride_on_curve | pump_ride_on_curve | pump_ride_on_curve | [6 empty] | 2021-05-06
WV_LO_COOLSYS1 CHILLER1 PUMP Pump Power [hp] | COOLSYS1 CHILLER1 PUMP Pump Power [hp] | 3.372 | 3.0011 | 3.0872 | 2.7842 | [6 empty] | 2021-05-06
WV_LO_COOLSYS1 CHILLER2 PUMP Pump Power [hp] | COOLSYS1 CHILLER2 PUMP Pump Power [hp] | 3.372 | 3.0011 | 3.0872 | 2.7842 | [6 empty] | 2021-05-06
WV_LO_COOLSYS1 PUMP SECONDARY Pump Power [hp] | COOLSYS1 PUMP SECONDARY Pump Power [hp] | 20.2321 | 18.0067 | 18.5233 | 16.7054 | [6 empty] | 2021-05-06
WV_LO_HEATSYS1 PUMP Pump Power [hp] | HEATSYS1 PUMP Pump Power [hp] | 18.5008 | 16.2164 | 19.9667 | 17.4346 | [6 empty] | 2021-05-06
WV_LO_TOWERWATERSYS PUMP Pump Power [hp] | TOWERWATERSYS PUMP Pump Power [hp] | 39.1912 | 35.0609 | 35.9016 | 32.3825 | [6 empty] | 2021-05-06
WV_LO_PLANT CIRC PUMP Pump Power [hp] | PLANT CIRC PUMP Pump Power [hp] | 4.5381 | 4.4752 | 4.5764 | 4.5129 | [6 empty] | 2021-05-06
WV_LO_Datacenter PLANT CIRC PUMP Pump Power [hp] | Datacenter PLANT CIRC PUMP Pump Power [hp] | 4.5381 | 4.4752 | 4.5764 | 4.5129 | [6 empty] | 2021-05-06
WV_LO_ZN_VAV_BOXes_Max_Reheat_Water_Flow_GPM | ZN_VAV_BOXes_Max_Reheat_Water_Flow_GPM | 438.4086 | 421.0237 | 458.5624 | 440.301 | [6 empty] | 2021-05-06
WV_LO_COOLSYS1 PUMP SECONDARY VSD | COOLSYS1 PUMP SECONDARY VSD | No | No | No | No | [6 empty] | 2021-05-06
WV_LO_HEATSYS1 PUMP VSD | HEATSYS1 PUMP VSD | No | No | No | No | [6 empty] | 2021-05-06
WV_LO_DATACENTER BASEMENT Cooling Capacity [ton] | DATACENTER BASEMENT Cooling Capacity [ton] | 123.1743 | 122.8094 | 124.1601 | 123.791 | [6 empty] | 2021-05-06
WV_LO_DATACENTER BOT Cooling Capacity [ton] | DATACENTER BOT Cooling Capacity [ton] | 2.6756 | 2.652 | 2.7015 | 2.6776 | [6 empty] | 2021-05-06
WV_LO_DATACENTER MID Cooling Capacity [ton] | DATACENTER MID Cooling Capacity [ton] | 25.5949 | 25.3877 | 25.8589 | 25.6489 | [6 empty] | 2021-05-06
WV_LO_DATACENTER TOP Cooling Capacity [ton] | DATACENTER TOP Cooling Capacity [ton] | 2.6089 | 2.5888 | 2.6321 | 2.6117 | [6 empty] | 2021-05-06
id | item | Zone4A(WV-Charleston-WV) ASHRAE901-state_STD2016 | Zone4A(WV-Charleston-WV) ASHRAE901-state_STD2019 | Zone5A(WV-Elkins-WV) ASHRAE901-state_STD2016 | Zone5A(WV-Elkins-WV) ASHRAE901-state_STD2019 | [6 empty] | 2021-05-06
WV_RS_PSZ-AC:1 Cooling Capacity [ton] | PSZ-AC:1 Cooling Capacity [ton] | 10.1832 | 9.8636 | 9.3456 | 8.872 | [6 empty] | 2021-05-06
WV_RS_PSZ-AC:2 Cooling Capacity [ton] | PSZ-AC:2 Cooling Capacity [ton] | 48.0799 | 46.24 | 44.0328 | 42.0973 | [6 empty] | 2021-05-06
WV_RS_PSZ-AC:3 Cooling Capacity [ton] | PSZ-AC:3 Cooling Capacity [ton] | 6.2689 | 6.1095 | 5.6682 | 5.5067 | [6 empty] | 2021-05-06
WV_RS_PSZ-AC:4 Cooling Capacity [ton] | PSZ-AC:4 Cooling Capacity [ton] | 5.0576 | 4.8992 | 4.4422 | 4.2758 | [6 empty] | 2021-05-06
WV_RS_PSZ-AC:1 Supply Flow Rate [cfm] | PSZ-AC:1 Supply Flow Rate [cfm] | 4025.872 | 3771.6064 | 3835.1728 | 3496.152 | [6 empty] | 2021-05-06
WV_RS_PSZ-AC:2 Supply Flow Rate [cfm] | PSZ-AC:2 Supply Flow Rate [cfm] | 15552.5792 | 14683.8384 | 15594.9568 | 14641.4608 | [6 empty] | 2021-05-06
WV_RS_PSZ-AC:3 Supply Flow Rate [cfm] | PSZ-AC:3 Supply Flow Rate [cfm] | 2288.3904 | 2224.824 | 2224.824 | 2161.2576 | [6 empty] | 2021-05-06
WV_RS_PSZ-AC:4 Supply Flow Rate [cfm] | PSZ-AC:4 Supply Flow Rate [cfm] | 1737.4816 | 1673.9152 | 1652.7264 | 1567.9712 | [6 empty] | 2021-05-06
WV_RS_PSZ-AC:1 OA Rate [cfm] | PSZ-AC:1 OA Rate [cfm] | 490.669 | 490.669 | 490.669 | 490.669 | [6 empty] | 2021-05-06
WV_RS_PSZ-AC:2 OA Rate [cfm] | PSZ-AC:2 OA Rate [cfm] | 4005.1282 | 4005.1282 | 4005.1282 | 4005.1282 | [6 empty] | 2021-05-06
WV_RS_PSZ-AC:3 OA Rate [cfm] | PSZ-AC:3 OA Rate [cfm] | 377.3937 | 377.3937 | 377.3937 | 377.3937 | [6 empty] | 2021-05-06
WV_RS_PSZ-AC:4 OA Rate [cfm] | PSZ-AC:4 OA Rate [cfm] | 377.3937 | 377.3937 | 377.3937 | 377.3937 | [6 empty] | 2021-05-06
WV_RS_PSZ-AC:1 OA Damper [gravity, motorized] | PSZ-AC:1 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2021-05-06
WV_RS_PSZ-AC:2 OA Damper [gravity, motorized] | PSZ-AC:2 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2021-05-06
WV_RS_PSZ-AC:3 OA Damper [gravity, motorized] | PSZ-AC:3 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2021-05-06
WV_RS_PSZ-AC:4 OA Damper [gravity, motorized] | PSZ-AC:4 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2021-05-06
WV_RS_PSZ-AC:1 Heating Capacity [kBtu/hr] | PSZ-AC:1 Heating Capacity [kBtu/hr] | 174.2969 | 163.7702 | 164.8422 | 151.7326 | [6 empty] | 2021-05-06
WV_RS_PSZ-AC:2 Heating Capacity [kBtu/hr] | PSZ-AC:2 Heating Capacity [kBtu/hr] | 798.4503 | 762.6267 | 807.2915 | 769.1389 | [6 empty] | 2021-05-06
WV_RS_PSZ-AC:3 Heating Capacity [kBtu/hr] | PSZ-AC:3 Heating Capacity [kBtu/hr] | 106.2356 | 103.5769 | 103.7532 | 101.0419 | [6 empty] | 2021-05-06
WV_RS_PSZ-AC:4 Heating Capacity [kBtu/hr] | PSZ-AC:4 Heating Capacity [kBtu/hr] | 86.1238 | 83.2655 | 82.6649 | 79.3067 | [6 empty] | 2021-05-06
id | item | Zone4A(WV-Charleston-WV) ASHRAE901-state_STD2016 | Zone4A(WV-Charleston-WV) ASHRAE901-state_STD2019 | Zone5A(WV-Elkins-WV) ASHRAE901-state_STD2016 | Zone5A(WV-Elkins-WV) ASHRAE901-state_STD2019 | [6 empty] | 2021-05-06
WV_PS_VAV_POD_1 Cooling Capacity [ton] | VAV_POD_1 Cooling Capacity [ton] | 19.3808 | 18.6761 | 19.0068 | 18.4003 | [6 empty] | 2021-05-06
WV_PS_VAV_POD_2 Cooling Capacity [ton] | VAV_POD_2 Cooling Capacity [ton] | 19.1334 | 18.504 | 18.7328 | 18.3446 | [6 empty] | 2021-05-06
WV_PS_VAV_POD_3 Cooling Capacity [ton] | VAV_POD_3 Cooling Capacity [ton] | 17.6921 | 16.8291 | 17.2954 | 16.4449 | [6 empty] | 2021-05-06
WV_PS_VAV_OTHER Cooling Capacity [ton] | VAV_OTHER Cooling Capacity [ton] | 27.3669 | 25.7473 | 26.4605 | 23.7189 | [6 empty] | 2021-05-06
WV_PS_PSZ-AC_1:6 Cooling Capacity [ton] | PSZ-AC_1:6 Cooling Capacity [ton] | 8.295 | 8.0303 | 7.861 | 7.6005 | [6 empty] | 2021-05-06
WV_PS_PSZ-AC_2:5 Cooling Capacity [ton] | PSZ-AC_2:5 Cooling Capacity [ton] | 5.6155 | 5.5944 | 5.6024 | 5.5826 | [6 empty] | 2021-05-06
WV_PS_PSZ-AC_2:7 Cooling Capacity [ton] | PSZ-AC_2:7 Cooling Capacity [ton] | 10.5074 | 10.5074 | 10.5074 | 10.5074 | [6 empty] | 2021-05-06
WV_PS_VAV_POD_1 Supply Flow Rate [cfm] | VAV_POD_1 Supply Flow Rate [cfm] | 5805.7312 | 5593.8432 | 5699.7872 | 5530.2768 | [6 empty] | 2021-05-06
WV_PS_VAV_POD_2 Supply Flow Rate [cfm] | VAV_POD_2 Supply Flow Rate [cfm] | 5742.1648 | 5551.4656 | 5615.032 | 5509.088 | [6 empty] | 2021-05-06
WV_PS_VAV_POD_3 Supply Flow Rate [cfm] | VAV_POD_3 Supply Flow Rate [cfm] | 5318.3888 | 5042.9344 | 5191.256 | 4936.9904 | [6 empty] | 2021-05-06
WV_PS_VAV_OTHER Supply Flow Rate [cfm] | VAV_OTHER Supply Flow Rate [cfm] | 8221.2544 | 7733.912 | 8094.1216 | 7585.5904 | [6 empty] | 2021-05-06
WV_PS_PSZ-AC_2:5 Supply Flow Rate [cfm] | PSZ-AC_2:5 Supply Flow Rate [cfm] | 1695.104 | 1673.9152 | 1673.9152 | 1673.9152 | [6 empty] | 2021-05-06
WV_PS_PSZ-AC_1:6 Supply Flow Rate [cfm] | PSZ-AC_1:6 Supply Flow Rate [cfm] | 2627.4112 | 2521.4672 | 2690.9776 | 2563.8448 | [6 empty] | 2021-05-06
WV_PS_PSZ-AC_2:7 Supply Flow Rate [cfm] | PSZ-AC_2:7 Supply Flow Rate [cfm] | 3157.1312 | 3157.1312 | 3157.1312 | 3157.1312 | [6 empty] | 2021-05-06
WV_PS_Supply Air Temp. Reset Flag | Supply Air Temp. Reset Flag | Yes | Yes | Yes | Yes | [6 empty] | 2021-05-06
WV_PS_VAV_POD_1 OA Rate [cfm] | VAV_POD_1 OA Rate [cfm] | 5815.8595 | 5604.374 | 5702.9867 | 5521.6318 | [6 empty] | 2021-05-06
WV_PS_VAV_POD_2 OA Rate [cfm] | VAV_POD_2 OA Rate [cfm] | 5740.3849 | 5552.7369 | 5621.3886 | 5504.935 | [6 empty] | 2021-05-06
WV_PS_VAV_POD_3 OA Rate [cfm] | VAV_POD_3 OA Rate [cfm] | 5307.7732 | 5050.1386 | 5189.7728 | 4934.8503 | [6 empty] | 2021-05-06
WV_PS_VAV_OTHER OA Rate [cfm] | VAV_OTHER OA Rate [cfm] | 3736.1787 | 2988.8921 | 3736.1787 | 2988.8921 | [6 empty] | 2021-05-06
WV_PS_PSZ-AC_2:5 OA Rate [cfm] | PSZ-AC_2:5 OA Rate [cfm] | 1152.7343 | 1152.7343 | 1152.7343 | 1152.7343 | [6 empty] | 2021-05-06
WV_PS_PSZ-AC_1:6 OA Rate [cfm] | PSZ-AC_1:6 OA Rate [cfm] | 539.9118 | 539.9118 | 539.9118 | 539.9118 | [6 empty] | 2021-05-06
WV_PS_PSZ-AC_2:7 OA Rate [cfm] | PSZ-AC_2:7 OA Rate [cfm] | 3153.0841 | 3153.0841 | 3153.0841 | 3153.0841 | [6 empty] | 2021-05-06
WV_PS_VAV_POD_1 OA Damper [gravity, motorized] | VAV_POD_1 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2021-05-06
WV_PS_VAV_POD_2 OA Damper [gravity, motorized] | VAV_POD_2 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2021-05-06
WV_PS_VAV_POD_3 OA Damper [gravity, motorized] | VAV_POD_3 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2021-05-06
WV_PS_VAV_OTHER OA Damper [gravity, motorized] | VAV_OTHER OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2021-05-06
WV_PS_PSZ-AC_2:5 OA Damper [gravity, motorized] | PSZ-AC_2:5 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2021-05-06
WV_PS_PSZ-AC_1:6 OA Damper [gravity, motorized] | PSZ-AC_1:6 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2021-05-06
WV_PS_PSZ-AC_2:7 OA Damper [gravity, motorized] | PSZ-AC_2:7 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2021-05-06
WV_PS_VAV_POD_1 (economizer) | VAV_POD_1 (economizer) | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialDryBulb | DifferentialDryBulb | [6 empty] | 2021-05-06
WV_PS_VAV_POD_2 (economizer) | VAV_POD_2 (economizer) | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialDryBulb | DifferentialDryBulb | [6 empty] | 2021-05-06
WV_PS_VAV_POD_3 (economizer) | VAV_POD_3 (economizer) | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialDryBulb | DifferentialDryBulb | [6 empty] | 2021-05-06
WV_PS_VAV_OTHER (economizer) | VAV_OTHER (economizer) | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialDryBulb | DifferentialDryBulb | [6 empty] | 2021-05-06
WV_PS_PSZ-AC_2:5 (economizer) | PSZ-AC_2:5 (economizer) | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialDryBulb | DifferentialDryBulb | [6 empty] | 2021-05-06
WV_PS_PSZ-AC_1:6 (economizer) | PSZ-AC_1:6 (economizer) | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialDryBulb | DifferentialDryBulb | [6 empty] | 2021-05-06
WV_PS_PSZ-AC_2:7 (economizer) | PSZ-AC_2:7 (economizer) | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialDryBulb | DifferentialDryBulb | [6 empty] | 2021-05-06
WV_PS_VAV_Pod_1_ERV Flag | VAV_Pod_1_ERV Flag | Yes | Yes | Yes | Yes | [6 empty] | 2021-05-06
WV_PS_VAV_Pod_2_ERV Flag | VAV_Pod_2_ERV Flag | Yes | Yes | Yes | Yes | [6 empty] | 2021-05-06
WV_PS_VAV_Pod_3_ERV Flag | VAV_Pod_3_ERV Flag | Yes | Yes | Yes | Yes | [6 empty] | 2021-05-06
WV_PS_VAV_OTHER_ERV Flag | VAV_OTHER_ERV Flag | Yes | Yes | Yes | Yes | [6 empty] | 2021-05-06
WV_PS_PSZ_AC_2_5_ERV Flag | PSZ_AC_2_5_ERV Flag | No | No | No | No | [6 empty] | 2021-05-06
WV_PS_PSZ_AC_2_7_ERV Flag | PSZ_AC_2_7_ERV Flag | Yes | Yes | Yes | Yes | [6 empty] | 2021-05-06
WV_PS_HEATSYS1 Capacity [MMBTU/h] | HEATSYS1 Capacity [MMBTU/h] | 1.0155 | 0.96823 | 1.0873 | 1.0454 | [6 empty] | 2021-05-06
WV_PS_HEATSYS1 Flow Rate [gal/min] | HEATSYS1 Flow Rate [gal/min] | 104.2274 | 99.3706 | 111.5864 | 107.2919 | [6 empty] | 2021-05-06
WV_PS_VAV_POD_1 Fan Power [hp] | VAV_POD_1 Fan Power [hp] | 8.5801 | 8.2681 | 8.4146 | 8.1461 | [6 empty] | 2021-05-06
WV_PS_VAV_POD_2 Fan Power [hp] | VAV_POD_2 Fan Power [hp] | 8.4706 | 8.192 | 8.2933 | 8.1214 | [6 empty] | 2021-05-06
WV_PS_VAV_POD_3 Fan Power [hp] | VAV_POD_3 Fan Power [hp] | 7.8325 | 7.4505 | 7.6569 | 7.2804 | [6 empty] | 2021-05-06
WV_PS_VAV_OTHER Fan Power [hp] | VAV_OTHER Fan Power [hp] | 12.0239 | 11.3123 | 11.8369 | 11.1054 | [6 empty] | 2021-05-06
WV_PS_HEATSYS1 Pump Power [hp] | HEATSYS1 Pump Power [hp] | 2.2529 | 2.1267 | 2.412 | 2.2962 | [6 empty] | 2021-05-06
WV_PS_PSZ-AC_1:6 Heating Capacity [kBtu/hr] | PSZ-AC_1:6 Heating Capacity [kBtu/hr] | 210.3978 | 201.8487 | 212.4876 | 203.9726 | [6 empty] | 2021-05-06
WV_PS_PSZ-AC_2:5 Heating Capacity [kBtu/hr] | PSZ-AC_2:5 Heating Capacity [kBtu/hr] | 133.7489 | 133.5232 | 139.1847 | 138.9798 | [6 empty] | 2021-05-06
WV_PS_PSZ-AC_2:7 Heating Capacity [kBtu/hr] | PSZ-AC_2:7 Heating Capacity [kBtu/hr] | 313.8756 | 313.8756 | 330.8534 | 330.8534 | [6 empty] | 2021-05-06
WV_PS_ZN_VAV_BOXes_Max_Reheat_Water_Flow_GPM | ZN_VAV_BOXes_Max_Reheat_Water_Flow_GPM | 66.8099 | 63.6618 | 69.5114 | 67.0183 | [6 empty] | 2021-05-06
id | item | Zone4A(WV-Charleston-WV) ASHRAE901-state_STD2016 | Zone4A(WV-Charleston-WV) ASHRAE901-state_STD2019 | Zone5A(WV-Elkins-WV) ASHRAE901-state_STD2016 | Zone5A(WV-Elkins-WV) ASHRAE901-state_STD2019 | [6 empty] | 2021-05-06
WV_SH_SAC_FRONTOFFICE Cooling Capacity [ton] | SAC_FRONTOFFICE Cooling Capacity [ton] | 2.2673 | 2.1387 | 2.076 | 1.9507 | [6 empty] | 2021-05-06
WV_SH_SAC_FRONTLOUNGE Cooling Capacity [ton] | SAC_FRONTLOUNGE Cooling Capacity [ton] | 6.1813 | 5.8644 | 5.7536 | 5.5151 | [6 empty] | 2021-05-06
WV_SH_SAC_MEETINGROOM Cooling Capacity [ton] | SAC_MEETINGROOM Cooling Capacity [ton] | 2.9367 | 2.8531 | 2.9724 | 2.8791 | [6 empty] | 2021-05-06
WV_SH_SAC_EXC_EMPLGE_RESTRM Cooling Capacity [ton] | SAC_EXC_EMPLGE_RESTRM Cooling Capacity [ton] | 5.9419 | 5.9 | 5.6643 | 5.6237 | [6 empty] | 2021-05-06
WV_SH_SAC_FO_ADDAQ SUPPLY FAN Supply Flow Rate [cfm] | SAC_FO_ADDAQ SUPPLY FAN Supply Flow Rate [cfm] | 783.9856 | 720.4192 | 762.7968 | 720.4192 | [6 empty] | 2021-05-06
WV_SH_SAC_FL_ADDAQ SUPPLY FAN Supply Flow Rate [cfm] | SAC_FL_ADDAQ SUPPLY FAN Supply Flow Rate [cfm] | 1864.6144 | 1758.6704 | 1864.6144 | 1758.6704 | [6 empty] | 2021-05-06
WV_SH_SAC_MR_ADDAQ SUPPLY FAN Supply Flow Rate [cfm] | SAC_MR_ADDAQ SUPPLY FAN Supply Flow Rate [cfm] | 889.9296 | 847.552 | 889.9296 | 868.7408 | [6 empty] | 2021-05-06
WV_SH_SAC_EXC_ADDAQ SUPPLY FAN Supply Flow Rate [cfm] | SAC_EXC_ADDAQ SUPPLY FAN Supply Flow Rate [cfm] | 2246.0128 | 2246.0128 | 2309.5792 | 2288.3904 | [6 empty] | 2021-05-06
WV_SH_SAC_Exc_EmpLge_RestRm OA Rate [cfm] | SAC_Exc_EmpLge_RestRm OA Rate [cfm] | 199.9928 | 199.9928 | 199.9928 | 199.9928 | [6 empty] | 2021-05-06
WV_SH_SAC_FrontLounge OA Rate [cfm] | SAC_FrontLounge OA Rate [cfm] | 500.0133 | 500.0133 | 500.0133 | 500.0133 | [6 empty] | 2021-05-06
WV_SH_SAC_FrontOffice OA Rate [cfm] | SAC_FrontOffice OA Rate [cfm] | 119.2938 | 119.2938 | 119.2938 | 119.2938 | [6 empty] | 2021-05-06
WV_SH_SAC_MeetingRoom OA Rate [cfm] | SAC_MeetingRoom OA Rate [cfm] | 267.7629 | 267.7629 | 267.7629 | 267.7629 | [6 empty] | 2021-05-06
WV_SH_SAC_FrontLounge OA Damper [gravity, motorized] | SAC_FrontLounge OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2021-05-06
WV_SH_SAC_FrontOffice (economizer) | SAC_FrontOffice (economizer) | No | No | No | No | [6 empty] | 2021-05-06
WV_SH_SAC_FrontLounge (economizer) | SAC_FrontLounge (economizer) | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialDryBulb | DifferentialDryBulb | [6 empty] | 2021-05-06
WV_SH_SAC_MeetingRoom (economizer) | SAC_MeetingRoom (economizer) | No | No | No | No | [6 empty] | 2021-05-06
WV_SH_SAC_Exc_EmpLge_RestRm (economizer) | SAC_Exc_EmpLge_RestRm (economizer) | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialDryBulb | DifferentialDryBulb | [6 empty] | 2021-05-06
WV_SH_SAC_FRONTOFFICE Heating Capacity [kBtu/hr] | SAC_FRONTOFFICE Heating Capacity [kBtu/hr] | 35.3419 | 33.5397 | 34.8152 | 33.0316 | [6 empty] | 2021-05-06
WV_SH_SAC_FRONTLOUNGE Heating Capacity [kBtu/hr] | SAC_FRONTLOUNGE Heating Capacity [kBtu/hr] | 97.843 | 94.4684 | 99.1768 | 95.8175 | [6 empty] | 2021-05-06
WV_SH_SAC_MEETINGROOM Heating Capacity [kBtu/hr] | SAC_MEETINGROOM Heating Capacity [kBtu/hr] | 48.4197 | 47.5296 | 49.5008 | 48.5407 | [6 empty] | 2021-05-06
WV_SH_SAC_EXC_EMPLGE_RESTRM Heating Capacity [kBtu/hr] | SAC_EXC_EMPLGE_RESTRM Heating Capacity [kBtu/hr] | 92.8172 | 92.1569 | 93.2931 | 92.6291 | [6 empty] | 2021-05-06
id | item | Zone4A(WV-Charleston-WV) ASHRAE901-state_STD2016 | Zone4A(WV-Charleston-WV) ASHRAE901-state_STD2019 | Zone5A(WV-Elkins-WV) ASHRAE901-state_STD2016 | Zone5A(WV-Elkins-WV) ASHRAE901-state_STD2019 | [6 empty] | 2021-05-06
WV_MA_SPLIT GSW COOLING COIL Cooling Capacity [ton] | SPLIT GSW COOLING COIL Cooling Capacity [ton] | 0.82949 | 0.81562 | 0.71127 | 0.69747 | [6 empty] | 2021-05-06
WV_MA_SPLIT GNW COOLING COIL Cooling Capacity [ton] | SPLIT GNW COOLING COIL Cooling Capacity [ton] | 0.79564 | 0.78206 | 0.6776 | 0.66405 | [6 empty] | 2021-05-06
WV_MA_SPLIT OFFICE COOLING COIL Cooling Capacity [ton] | SPLIT OFFICE COOLING COIL Cooling Capacity [ton] | 1.7014 | 1.571 | 1.5419 | 1.3715 | [6 empty] | 2021-05-06
WV_MA_SPLIT GNE COOLING COIL Cooling Capacity [ton] | SPLIT GNE COOLING COIL Cooling Capacity [ton] | 0.69258 | 0.68049 | 0.57612 | 0.56424 | [6 empty] | 2021-05-06
WV_MA_SPLIT GN1 COOLING COIL Cooling Capacity [ton] | SPLIT GN1 COOLING COIL Cooling Capacity [ton] | 0.58881 | 0.57916 | 0.4927 | 0.48328 | [6 empty] | 2021-05-06
WV_MA_SPLIT GN2 COOLING COIL Cooling Capacity [ton] | SPLIT GN2 COOLING COIL Cooling Capacity [ton] | 0.58674 | 0.57714 | 0.49059 | 0.48123 | [6 empty] | 2021-05-06
WV_MA_SPLIT GS1 COOLING COIL Cooling Capacity [ton] | SPLIT GS1 COOLING COIL Cooling Capacity [ton] | 0.63019 | 0.61988 | 0.53668 | 0.52657 | [6 empty] | 2021-05-06
WV_MA_SPLIT GS2 COOLING COIL Cooling Capacity [ton] | SPLIT GS2 COOLING COIL Cooling Capacity [ton] | 0.66053 | 0.64626 | 0.5711 | 0.55614 | [6 empty] | 2021-05-06
WV_MA_SPLIT MSW COOLING COIL Cooling Capacity [ton] | SPLIT MSW COOLING COIL Cooling Capacity [ton] | 1.9578 | 1.9268 | 1.7797 | 1.749 | [6 empty] | 2021-05-06
WV_MA_SPLIT MNW COOLING COIL Cooling Capacity [ton] | SPLIT MNW COOLING COIL Cooling Capacity [ton] | 1.9002 | 1.87 | 1.7199 | 1.6898 | [6 empty] | 2021-05-06
WV_MA_SPLIT MSE COOLING COIL Cooling Capacity [ton] | SPLIT MSE COOLING COIL Cooling Capacity [ton] | 1.6256 | 1.6018 | 1.4902 | 1.4157 | [6 empty] | 2021-05-06
WV_MA_SPLIT MNE COOLING COIL Cooling Capacity [ton] | SPLIT MNE COOLING COIL Cooling Capacity [ton] | 1.5479 | 1.5186 | 1.3646 | 1.3356 | [6 empty] | 2021-05-06
WV_MA_SPLIT MN1 COOLING COIL Cooling Capacity [ton] | SPLIT MN1 COOLING COIL Cooling Capacity [ton] | 1.2914 | 1.2729 | 1.1387 | 1.1207 | [6 empty] | 2021-05-06
WV_MA_SPLIT MN2 COOLING COIL Cooling Capacity [ton] | SPLIT MN2 COOLING COIL Cooling Capacity [ton] | 1.2858 | 1.2674 | 1.1328 | 1.115 | [6 empty] | 2021-05-06
WV_MA_SPLIT MS1 COOLING COIL Cooling Capacity [ton] | SPLIT MS1 COOLING COIL Cooling Capacity [ton] | 1.3677 | 1.3483 | 1.218 | 1.1992 | [6 empty] | 2021-05-06
WV_MA_SPLIT MS2 COOLING COIL Cooling Capacity [ton] | SPLIT MS2 COOLING COIL Cooling Capacity [ton] | 1.3627 | 1.3435 | 1.2127 | 1.194 | [6 empty] | 2021-05-06
WV_MA_SPLIT TSW COOLING COIL Cooling Capacity [ton] | SPLIT TSW COOLING COIL Cooling Capacity [ton] | 1.2246 | 1.2077 | 1.1192 | 1.1025 | [6 empty] | 2021-05-06
WV_MA_SPLIT TNW COOLING COIL Cooling Capacity [ton] | SPLIT TNW COOLING COIL Cooling Capacity [ton] | 1.1863 | 1.1698 | 1.0782 | 1.0619 | [6 empty] | 2021-05-06
WV_MA_SPLIT TSE COOLING COIL Cooling Capacity [ton] | SPLIT TSE COOLING COIL Cooling Capacity [ton] | 1.0896 | 1.0761 | 0.97559 | 0.96212 | [6 empty] | 2021-05-06
WV_MA_SPLIT TNE COOLING COIL Cooling Capacity [ton] | SPLIT TNE COOLING COIL Cooling Capacity [ton] | 1.0252 | 1.0126 | 0.90959 | 0.89703 | [6 empty] | 2021-05-06
WV_MA_SPLIT TN1 COOLING COIL Cooling Capacity [ton] | SPLIT TN1 COOLING COIL Cooling Capacity [ton] | 0.83376 | 0.82413 | 0.73428 | 0.72498 | [6 empty] | 2021-05-06
WV_MA_SPLIT TN2 COOLING COIL Cooling Capacity [ton] | SPLIT TN2 COOLING COIL Cooling Capacity [ton] | 0.82772 | 0.81825 | 0.7278 | 0.71867 | [6 empty] | 2021-05-06
WV_MA_SPLIT TS1 COOLING COIL Cooling Capacity [ton] | SPLIT TS1 COOLING COIL Cooling Capacity [ton] | 0.91152 | 0.90074 | 0.81639 | 0.80566 | [6 empty] | 2021-05-06
WV_MA_SPLIT TS2 COOLING COIL Cooling Capacity [ton] | SPLIT TS2 COOLING COIL Cooling Capacity [ton] | 0.91198 | 0.90124 | 0.81655 | 0.80587 | [6 empty] | 2021-05-06
WV_MA_Split GN1 Furnace with DX Cooling OA Rate [cfm] | Split GN1 Furnace with DX Cooling OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | [6 empty] | 2021-05-06
WV_MA_Split GN2 Furnace with DX Cooling OA Rate [cfm] | Split GN2 Furnace with DX Cooling OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | [6 empty] | 2021-05-06
WV_MA_Split GNE Furnace with DX Cooling OA Rate [cfm] | Split GNE Furnace with DX Cooling OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | [6 empty] | 2021-05-06
WV_MA_Split GNW Furnace with DX Cooling OA Rate [cfm] | Split GNW Furnace with DX Cooling OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | [6 empty] | 2021-05-06
WV_MA_Split GS1 Furnace with DX Cooling OA Rate [cfm] | Split GS1 Furnace with DX Cooling OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | [6 empty] | 2021-05-06
WV_MA_Split GS2 Furnace with DX Cooling OA Rate [cfm] | Split GS2 Furnace with DX Cooling OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | [6 empty] | 2021-05-06
WV_MA_Split GSW Furnace with DX Cooling OA Rate [cfm] | Split GSW Furnace with DX Cooling OA Rate [cfm] | 56.9945 | 56.9945 | 56.9945 | 56.9945 | [6 empty] | 2021-05-06
WV_MA_Split MN1 Furnace with DX Cooling OA Rate [cfm] | Split MN1 Furnace with DX Cooling OA Rate [cfm] | 109.9824 | 109.9824 | 109.9824 | 109.9824 | [6 empty] | 2021-05-06
WV_MA_Split MN2 Furnace with DX Cooling OA Rate [cfm] | Split MN2 Furnace with DX Cooling OA Rate [cfm] | 109.9824 | 109.9824 | 109.9824 | 109.9824 | [6 empty] | 2021-05-06
WV_MA_Split MNE Furnace with DX Cooling OA Rate [cfm] | Split MNE Furnace with DX Cooling OA Rate [cfm] | 109.9824 | 109.9824 | 109.9824 | 109.9824 | [6 empty] | 2021-05-06
WV_MA_Split MNW Furnace with DX Cooling OA Rate [cfm] | Split MNW Furnace with DX Cooling OA Rate [cfm] | 109.9824 | 109.9824 | 109.9824 | 109.9824 | [6 empty] | 2021-05-06
WV_MA_Split MS1 Furnace with DX Cooling OA Rate [cfm] | Split MS1 Furnace with DX Cooling OA Rate [cfm] | 109.9824 | 109.9824 | 109.9824 | 109.9824 | [6 empty] | 2021-05-06
WV_MA_Split MS2 Furnace with DX Cooling OA Rate [cfm] | Split MS2 Furnace with DX Cooling OA Rate [cfm] | 109.9824 | 109.9824 | 109.9824 | 109.9824 | [6 empty] | 2021-05-06
WV_MA_Split MSE Furnace with DX Cooling OA Rate [cfm] | Split MSE Furnace with DX Cooling OA Rate [cfm] | 109.9824 | 109.9824 | 109.9824 | 109.9824 | [6 empty] | 2021-05-06
WV_MA_Split MSW Furnace with DX Cooling OA Rate [cfm] | Split MSW Furnace with DX Cooling OA Rate [cfm] | 109.9824 | 109.9824 | 109.9824 | 109.9824 | [6 empty] | 2021-05-06
WV_MA_Split Office Furnace with DX Cooling OA Rate [cfm] | Split Office Furnace with DX Cooling OA Rate [cfm] | 80.7372 | 80.7372 | 80.7372 | 80.7372 | [6 empty] | 2021-05-06
WV_MA_Split TN1 Furnace with DX Cooling OA Rate [cfm] | Split TN1 Furnace with DX Cooling OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | [6 empty] | 2021-05-06
WV_MA_Split TN2 Furnace with DX Cooling OA Rate [cfm] | Split TN2 Furnace with DX Cooling OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | [6 empty] | 2021-05-06
WV_MA_Split TNE Furnace with DX Cooling OA Rate [cfm] | Split TNE Furnace with DX Cooling OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | [6 empty] | 2021-05-06
WV_MA_Split TNW Furnace with DX Cooling OA Rate [cfm] | Split TNW Furnace with DX Cooling OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | [6 empty] | 2021-05-06
WV_MA_Split TS1 Furnace with DX Cooling OA Rate [cfm] | Split TS1 Furnace with DX Cooling OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | [6 empty] | 2021-05-06
WV_MA_Split TS2 Furnace with DX Cooling OA Rate [cfm] | Split TS2 Furnace with DX Cooling OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | [6 empty] | 2021-05-06
WV_MA_Split TSE Furnace with DX Cooling OA Rate [cfm] | Split TSE Furnace with DX Cooling OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | [6 empty] | 2021-05-06
WV_MA_Split TSW Furnace with DX Cooling OA Rate [cfm] | Split TSW Furnace with DX Cooling OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | [6 empty] | 2021-05-06
WV_MA_SPLIT GSW HEATING COIL Heating Capacity [kBtu/hr] | SPLIT GSW HEATING COIL Heating Capacity [kBtu/hr] | 8.37 | 8.4292 | 9.3371 | 9.3963 | [6 empty] | 2021-05-06
WV_MA_SPLIT GNW HEATING COIL Heating Capacity [kBtu/hr] | SPLIT GNW HEATING COIL Heating Capacity [kBtu/hr] | 8.2522 | 8.3116 | 9.2312 | 9.2905 | [6 empty] | 2021-05-06
WV_MA_SPLIT OFFICE HEATING COIL Heating Capacity [kBtu/hr] | SPLIT OFFICE HEATING COIL Heating Capacity [kBtu/hr] | 20.6048 | 20.7199 | 22.1512 | 22.2428 | [6 empty] | 2021-05-06
WV_MA_SPLIT GNE HEATING COIL Heating Capacity [kBtu/hr] | SPLIT GNE HEATING COIL Heating Capacity [kBtu/hr] | 8.2374 | 8.2968 | 9.215 | 9.2743 | [6 empty] | 2021-05-06
WV_MA_SPLIT GN1 HEATING COIL Heating Capacity [kBtu/hr] | SPLIT GN1 HEATING COIL Heating Capacity [kBtu/hr] | 6.0776 | 6.1372 | 6.9126 | 6.972 | [6 empty] | 2021-05-06
WV_MA_SPLIT GN2 HEATING COIL Heating Capacity [kBtu/hr] | SPLIT GN2 HEATING COIL Heating Capacity [kBtu/hr] | 6.0772 | 6.1367 | 6.9121 | 6.9715 | [6 empty] | 2021-05-06
WV_MA_SPLIT GS1 HEATING COIL Heating Capacity [kBtu/hr] | SPLIT GS1 HEATING COIL Heating Capacity [kBtu/hr] | 6.0833 | 6.1426 | 6.8936 | 6.9528 | [6 empty] | 2021-05-06
WV_MA_SPLIT GS2 HEATING COIL Heating Capacity [kBtu/hr] | SPLIT GS2 HEATING COIL Heating Capacity [kBtu/hr] | 6.5651 | 6.627 | 7.3976 | 7.4583 | [6 empty] | 2021-05-06
WV_MA_SPLIT MSW HEATING COIL Heating Capacity [kBtu/hr] | SPLIT MSW HEATING COIL Heating Capacity [kBtu/hr] | 14.2258 | 14.3555 | 15.1642 | 15.2946 | [6 empty] | 2021-05-06
WV_MA_SPLIT MNW HEATING COIL Heating Capacity [kBtu/hr] | SPLIT MNW HEATING COIL Heating Capacity [kBtu/hr] | 14.1826 | 14.3117 | 15.1758 | 15.3057 | [6 empty] | 2021-05-06
WV_MA_SPLIT MSE HEATING COIL Heating Capacity [kBtu/hr] | SPLIT MSE HEATING COIL Heating Capacity [kBtu/hr] | 14.1901 | 14.3197 | 15.1253 | 15.2557 | [6 empty] | 2021-05-06
WV_MA_SPLIT MNE HEATING COIL Heating Capacity [kBtu/hr] | SPLIT MNE HEATING COIL Heating Capacity [kBtu/hr] | 14.1468 | 14.2759 | 15.1368 | 15.2667 | [6 empty] | 2021-05-06
WV_MA_SPLIT MN1 HEATING COIL Heating Capacity [kBtu/hr] | SPLIT MN1 HEATING COIL Heating Capacity [kBtu/hr] | 10.9482 | 10.9482 | 11.5404 | 11.5404 | [6 empty] | 2021-05-06
WV_MA_SPLIT MN2 HEATING COIL Heating Capacity [kBtu/hr] | SPLIT MN2 HEATING COIL Heating Capacity [kBtu/hr] | 10.9482 | 10.9482 | 11.5404 | 11.5404 | [6 empty] | 2021-05-06
WV_MA_SPLIT MS1 HEATING COIL Heating Capacity [kBtu/hr] | SPLIT MS1 HEATING COIL Heating Capacity [kBtu/hr] | 10.9482 | 10.9482 | 11.5404 | 11.5404 | [6 empty] | 2021-05-06
WV_MA_SPLIT MS2 HEATING COIL Heating Capacity [kBtu/hr] | SPLIT MS2 HEATING COIL Heating Capacity [kBtu/hr] | 10.9482 | 10.9482 | 11.5404 | 11.5404 | [6 empty] | 2021-05-06
WV_MA_SPLIT TSW HEATING COIL Heating Capacity [kBtu/hr] | SPLIT TSW HEATING COIL Heating Capacity [kBtu/hr] | 10.2084 | 10.2701 | 10.9654 | 11.0273 | [6 empty] | 2021-05-06
WV_MA_SPLIT TNW HEATING COIL Heating Capacity [kBtu/hr] | SPLIT TNW HEATING COIL Heating Capacity [kBtu/hr] | 10.1912 | 10.253 | 10.9778 | 11.04 | [6 empty] | 2021-05-06
WV_MA_SPLIT TSE HEATING COIL Heating Capacity [kBtu/hr] | SPLIT TSE HEATING COIL Heating Capacity [kBtu/hr] | 10.1893 | 10.251 | 10.9444 | 11.0063 | [6 empty] | 2021-05-06
WV_MA_SPLIT TNE HEATING COIL Heating Capacity [kBtu/hr] | SPLIT TNE HEATING COIL Heating Capacity [kBtu/hr] | 10.1721 | 10.2339 | 10.9568 | 11.0189 | [6 empty] | 2021-05-06
WV_MA_SPLIT TN1 HEATING COIL Heating Capacity [kBtu/hr] | SPLIT TN1 HEATING COIL Heating Capacity [kBtu/hr] | 7.9473 | 8.0091 | 8.7254 | 8.7874 | [6 empty] | 2021-05-06
WV_MA_SPLIT TN2 HEATING COIL Heating Capacity [kBtu/hr] | SPLIT TN2 HEATING COIL Heating Capacity [kBtu/hr] | 7.9467 | 8.0085 | 8.7247 | 8.7868 | [6 empty] | 2021-05-06
WV_MA_SPLIT TS1 HEATING COIL Heating Capacity [kBtu/hr] | SPLIT TS1 HEATING COIL Heating Capacity [kBtu/hr] | 7.9582 | 8.0199 | 8.7066 | 8.7685 | [6 empty] | 2021-05-06
WV_MA_SPLIT TS2 HEATING COIL Heating Capacity [kBtu/hr] | SPLIT TS2 HEATING COIL Heating Capacity [kBtu/hr] | 7.9577 | 8.0193 | 8.706 | 8.7679 | [6 empty] | 2021-05-06
WV_MA_Split_GSW ERV Flag | Split_GSW ERV Flag | Yes | Yes | Yes | Yes | [6 empty] | 2021-05-06
WV_MA_Split_GNW ERV Flag | Split_GNW ERV Flag | Yes | Yes | Yes | Yes | [6 empty] | 2021-05-06
WV_MA_Split_GNE ERV Flag | Split_GNE ERV Flag | Yes | Yes | Yes | Yes | [6 empty] | 2021-05-06
WV_MA_Split_GN1 ERV Flag | Split_GN1 ERV Flag | Yes | Yes | Yes | Yes | [6 empty] | 2021-05-06
WV_MA_Split_GN2 ERV Flag | Split_GN2 ERV Flag | Yes | Yes | Yes | Yes | [6 empty] | 2021-05-06
WV_MA_Split_GS1 ERV Flag | Split_GS1 ERV Flag | Yes | Yes | Yes | Yes | [6 empty] | 2021-05-06
WV_MA_Split_GS2 ERV Flag | Split_GS2 ERV Flag | Yes | Yes | Yes | Yes | [6 empty] | 2021-05-06
WV_MA_Split_MSW ERV Flag | Split_MSW ERV Flag | Yes | Yes | Yes | Yes | [6 empty] | 2021-05-06
WV_MA_Split_MNW ERV Flag | Split_MNW ERV Flag | Yes | Yes | Yes | Yes | [6 empty] | 2021-05-06
WV_MA_Split_MSE ERV Flag | Split_MSE ERV Flag | Yes | Yes | Yes | Yes | [6 empty] | 2021-05-06
WV_MA_Split_MNE ERV Flag | Split_MNE ERV Flag | Yes | Yes | Yes | Yes | [6 empty] | 2021-05-06
WV_MA_Split_MN1 ERV Flag | Split_MN1 ERV Flag | Yes | Yes | Yes | Yes | [6 empty] | 2021-05-06
WV_MA_Split_MN2 ERV Flag | Split_MN2 ERV Flag | Yes | Yes | Yes | Yes | [6 empty] | 2021-05-06
WV_MA_Split_MS1 ERV Flag | Split_MS1 ERV Flag | Yes | Yes | Yes | Yes | [6 empty] | 2021-05-06
WV_MA_Split_MS2 ERV Flag | Split_MS2 ERV Flag | Yes | Yes | Yes | Yes | [6 empty] | 2021-05-06
WV_MA_Split_TSW ERV Flag | Split_TSW ERV Flag | Yes | Yes | Yes | Yes | [6 empty] | 2021-05-06
WV_MA_Split_TNW ERV Flag | Split_TNW ERV Flag | Yes | Yes | Yes | Yes | [6 empty] | 2021-05-06
WV_MA_Split_TSE ERV Flag | Split_TSE ERV Flag | Yes | Yes | Yes | Yes | [6 empty] | 2021-05-06
WV_MA_Split_TNE ERV Flag | Split_TNE ERV Flag | Yes | Yes | Yes | Yes | [6 empty] | 2021-05-06
WV_MA_Split_TN1 ERV Flag | Split_TN1 ERV Flag | Yes | Yes | Yes | Yes | [6 empty] | 2021-05-06
WV_MA_Split_TN2 ERV Flag | Split_TN2 ERV Flag | Yes | Yes | Yes | Yes | [6 empty] | 2021-05-06
WV_MA_Split_TS1 ERV Flag | Split_TS1 ERV Flag | Yes | Yes | Yes | Yes | [6 empty] | 2021-05-06
WV_MA_Split_TS2 ERV Flag | Split_TS2 ERV Flag | Yes | Yes | Yes | Yes | [6 empty] | 2021-05-06
id | item | Zone5B(WY-Cheyenne-WY) ASHRAE901-state_STD2016 | Zone5B(WY-Cheyenne-WY) ASHRAE901-state_STD2019 | Zone6B(WY-Casper-WY) ASHRAE901-state_STD2016 | Zone6B(WY-Casper-WY) ASHRAE901-state_STD2019 | Zone7(WY-JacksonHole-WY) ASHRAE901-state_STD2016 | Zone7(WY-JacksonHole-WY) ASHRAE901-state_STD2019 |  |  |  |  | 2021-05-06
WY_SO_PSZ-AC:1 Cooling Capacity [ton] | PSZ-AC:1 Cooling Capacity [ton] | 1.7367 | 1.6138 | 1.7131 | 1.5884 | 1.7077 | 1.5667 |  |  |  |  | 2021-05-06
WY_SO_PSZ-AC:2 Cooling Capacity [ton] | PSZ-AC:2 Cooling Capacity [ton] | 1.4366 | 1.3546 | 1.511 | 1.4094 | 1.3948 | 1.2438 |  |  |  |  | 2021-05-06
WY_SO_PSZ-AC:3 Cooling Capacity [ton] | PSZ-AC:3 Cooling Capacity [ton] | 1.1584 | 1.1064 | 1.188 | 1.1027 | 1.2469 | 1.1032 |  |  |  |  | 2021-05-06
WY_SO_PSZ-AC:4 Cooling Capacity [ton] | PSZ-AC:4 Cooling Capacity [ton] | 1.3577 | 1.2584 | 1.4 | 1.2882 | 1.2609 | 1.1229 |  |  |  |  | 2021-05-06
WY_SO_PSZ-AC:5 Cooling Capacity [ton] | PSZ-AC:5 Cooling Capacity [ton] | 1.4521 | 1.3978 | 1.4868 | 1.3957 | 1.5665 | 1.4016 |  |  |  |  | 2021-05-06
WY_SO_PSZ-AC:1 Supply Flow Rate [cfm] | PSZ-AC:1 Supply Flow Rate [cfm] | 783.9856 | 720.4192 | 762.7968 | 720.4192 | 762.7968 | 699.2304 |  |  |  |  | 2021-05-06
WY_SO_PSZ-AC:2 Supply Flow Rate [cfm] | PSZ-AC:2 Supply Flow Rate [cfm] | 656.8528 | 614.4752 | 678.0416 | 635.664 | 635.664 | 550.9088 |  |  |  |  | 2021-05-06
WY_SO_PSZ-AC:3 Supply Flow Rate [cfm] | PSZ-AC:3 Supply Flow Rate [cfm] | 529.72 | 508.5312 | 529.72 | 487.3424 | 550.9088 | 487.3424 |  |  |  |  | 2021-05-06
WY_SO_PSZ-AC:4 Supply Flow Rate [cfm] | PSZ-AC:4 Supply Flow Rate [cfm] | 614.4752 | 572.0976 | 635.664 | 572.0976 | 572.0976 | 508.5312 |  |  |  |  | 2021-05-06
WY_SO_PSZ-AC:5 Supply Flow Rate [cfm] | PSZ-AC:5 Supply Flow Rate [cfm] | 656.8528 | 635.664 | 678.0416 | 635.664 | 699.2304 | 635.664 |  |  |  |  | 2021-05-06
WY_SO_PSZ-AC:1 OA Rate [cfm] | PSZ-AC:1 OA Rate [cfm] | 136.9178 | 136.9178 | 136.9178 | 136.9178 | 136.9178 | 136.9178 |  |  |  |  | 2021-05-06
WY_SO_PSZ-AC:2 OA Rate [cfm] | PSZ-AC:2 OA Rate [cfm] | 103.7925 | 103.7925 | 103.7925 | 103.7925 | 103.7925 | 103.7925 |  |  |  |  | 2021-05-06
WY_SO_PSZ-AC:3 OA Rate [cfm] | PSZ-AC:3 OA Rate [cfm] | 61.5711 | 61.5711 | 61.5711 | 61.5711 | 61.5711 | 61.5711 |  |  |  |  | 2021-05-06
WY_SO_PSZ-AC:4 OA Rate [cfm] | PSZ-AC:4 OA Rate [cfm] | 103.7925 | 103.7925 | 103.7925 | 103.7925 | 103.7925 | 103.7925 |  |  |  |  | 2021-05-06
WY_SO_PSZ-AC:5 OA Rate [cfm] | PSZ-AC:5 OA Rate [cfm] | 61.5711 | 61.5711 | 61.5711 | 61.5711 | 61.5711 | 61.5711 |  |  |  |  | 2021-05-06
WY_SO_PSZ-AC:1 heating Capacity [kBtu/hr] | PSZ-AC:1 heating Capacity [kBtu/hr] | 13.5613 | 13.5294 | 14.475 | 14.4413 | 14.2513 | 14.1776 |  |  |  |  | 2021-05-06
WY_SO_PSZ-AC:2 heating Capacity [kBtu/hr] | PSZ-AC:2 heating Capacity [kBtu/hr] | 20.478 | 20.2316 | 21.2163 | 20.9524 | 20.8601 | 20.2862 |  |  |  |  | 2021-05-06
WY_SO_PSZ-AC:3 heating Capacity [kBtu/hr] | PSZ-AC:3 heating Capacity [kBtu/hr] | 12.5301 | 12.3875 | 12.9717 | 12.8194 | 12.7629 | 12.4345 |  |  |  |  | 2021-05-06
WY_SO_PSZ-AC:4 heating Capacity [kBtu/hr] | PSZ-AC:4 heating Capacity [kBtu/hr] | 20.3894 | 20.1784 | 21.1583 | 20.9331 | 20.8528 | 20.367 |  |  |  |  | 2021-05-06
WY_SO_PSZ-AC:5 heating Capacity [kBtu/hr] | PSZ-AC:5 heating Capacity [kBtu/hr] | 12.5301 | 12.3875 | 12.9056 | 12.7597 | 12.708 | 12.3909 |  |  |  |  | 2021-05-06
id | item | Zone5B(WY-Cheyenne-WY) ASHRAE901-state_STD2016 | Zone5B(WY-Cheyenne-WY) ASHRAE901-state_STD2019 | Zone6B(WY-Casper-WY) ASHRAE901-state_STD2016 | Zone6B(WY-Casper-WY) ASHRAE901-state_STD2019 | Zone7(WY-JacksonHole-WY) ASHRAE901-state_STD2016 | Zone7(WY-JacksonHole-WY) ASHRAE901-state_STD2019 |  |  |  |  | 2021-05-06
WY_LO_CAV_BAS Supply Flow Rate [cfm] | CAV_BAS Supply Flow Rate [cfm] | 14366.0064 | 13264.1888 | 14090.552 | 13031.112 | 14768.5936 | 13624.3984 |  |  |  |  | 2021-05-06
WY_LO_VAV_BOT WITH REHEAT Supply Flow Rate [cfm] | VAV_BOT WITH REHEAT Supply Flow Rate [cfm] | 24006.9104 | 22862.7152 | 23540.7568 | 22248.24 | 24345.9312 | 22735.5824 |  |  |  |  | 2021-05-06
WY_LO_VAV_MID WITH REHEAT Supply Flow Rate [cfm] | VAV_MID WITH REHEAT Supply Flow Rate [cfm] | 222418.8339 | 211506.6019 | 218202.2627 | 205488.9827 | 223902.0499 | 207374.7859 |  |  |  |  | 2021-05-06
WY_LO_VAV_TOP WITH REHEAT Supply Flow Rate [cfm] | VAV_TOP WITH REHEAT Supply Flow Rate [cfm] | 23689.0784 | 22714.3936 | 23752.6448 | 22502.5056 | 23604.3232 | 21782.0864 |  |  |  |  | 2021-05-06
WY_LO_Supply Air Temp. Reset Flag | Supply Air Temp. Reset Flag | Yes | Yes | Yes | Yes | Yes | Yes |  |  |  |  | 2021-05-06
WY_LO_CAV_BAS OA Rate [cfm] | CAV_BAS OA Rate [cfm] | 2542.8255 | 2542.8255 | 2542.8255 | 2542.8255 | 2542.8255 | 2542.8255 |  |  |  |  | 2021-05-06
WY_LO_VAV_BOT WITH REHEAT OA Rate [cfm] | VAV_BOT WITH REHEAT OA Rate [cfm] | 5377.8022 | 4302.174 | 5377.8022 | 4302.174 | 5377.8022 | 4302.174 |  |  |  |  | 2021-05-06
WY_LO_VAV_MID WITH REHEAT OA Rate [cfm] | VAV_MID WITH REHEAT OA Rate [cfm] | 53777.9373 | 43021.7396 | 53777.9373 | 43021.7396 | 53777.9373 | 43021.7396 |  |  |  |  | 2021-05-06
WY_LO_VAV_TOP WITH REHEAT OA Rate [cfm] | VAV_TOP WITH REHEAT OA Rate [cfm] | 5377.8022 | 4302.174 | 5377.8022 | 4302.174 | 5377.8022 | 4302.174 |  |  |  |  | 2021-05-06
WY_LO_AIRLOOP DATACENTER BASEMENT OA Rate [cfm] | AIRLOOP DATACENTER BASEMENT OA Rate [cfm] | 716.9654 | 716.9654 | 716.9654 | 716.9654 | 716.9654 | 716.9654 |  |  |  |  | 2021-05-06
WY_LO_VAV_bot_WITH_REHEAT ERV Flag | VAV_bot_WITH_REHEAT ERV Flag | No | No | No | No | Yes | Yes |  |  |  |  | 2021-05-06
WY_LO_VAV_mid_WITH_REHEAT ERV Flag | VAV_mid_WITH_REHEAT ERV Flag | No | No | No | No | Yes | Yes |  |  |  |  | 2021-05-06
WY_LO_VAV_top_WITH_REHEAT ERV Flag | VAV_top_WITH_REHEAT ERV Flag | No | No | No | No | Yes | Yes |  |  |  |  | 2021-05-06
WY_LO_COOLSYS1 CHILLER1 Capacity [ton] | COOLSYS1 CHILLER1 Capacity [ton] | 296.734 | 278.9872 | 307.0631 | 282.6607 | 273.9608 | 250.3107 |  |  |  |  | 2021-05-06
WY_LO_COOLSYS1 CHILLER2 Capacity [ton] | COOLSYS1 CHILLER2 Capacity [ton] | 296.734 | 278.9872 | 307.0631 | 282.6607 | 273.9608 | 250.3107 |  |  |  |  | 2021-05-06
WY_LO_TOWERWATERSYS COOLTOWER 1 Capacity [ton] | TOWERWATERSYS COOLTOWER 1 Capacity [ton] | 282.0058 | 265.1428 | 291.824 | 268.6258 | 260.3586 | 237.8833 |  |  |  |  | 2021-05-06
WY_LO_TOWERWATERSYS COOLTOWER 2 Capacity [ton] | TOWERWATERSYS COOLTOWER 2 Capacity [ton] | 282.0058 | 265.1428 | 291.824 | 268.6258 | 260.3586 | 237.8833 |  |  |  |  | 2021-05-06
WY_LO_HEATSYS1 BOILER Capacity [MMBTU/h] | HEATSYS1 BOILER Capacity [MMBTU/h] | 4575.2386 | 4069.5043 | 4719.3429 | 4205.3179 | 4662.5379 | 4086.8674 |  |  |  |  | 2021-05-06
WY_LO_COOLSYS1 PUMP Flow Rate [gal/min] | COOLSYS1 PUMP Flow Rate [gal/min] | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 2021-05-06
WY_LO_COOLSYS1 CHILLER1 PUMP Flow Rate [gal/min] | COOLSYS1 CHILLER1 PUMP Flow Rate [gal/min] | 465.776 | 434.8187 | 482.1938 | 443.8233 | 429.6817 | 392.557 |  |  |  |  | 2021-05-06
WY_LO_COOLSYS1 CHILLER2 PUMP Flow Rate [gal/min] | COOLSYS1 CHILLER2 PUMP Flow Rate [gal/min] | 465.776 | 434.8187 | 482.1938 | 443.8233 | 429.6817 | 392.557 |  |  |  |  | 2021-05-06
WY_LO_COOLSYS1 PUMP SECONDARY Flow Rate [gal/min] | COOLSYS1 PUMP SECONDARY Flow Rate [gal/min] | 931.552 | 869.6375 | 964.386 | 887.6466 | 859.3633 | 785.1156 |  |  |  |  | 2021-05-06
WY_LO_HEATSYS1 PUMP Flow Rate [gal/min] | HEATSYS1 PUMP Flow Rate [gal/min] | 939.1285 | 835.32 | 968.7068 | 863.1975 | 957.0473 | 838.8831 |  |  |  |  | 2021-05-06
WY_LO_TOWERWATERSYS PUMP Flow Rate [gal/min] | TOWERWATERSYS PUMP Flow Rate [gal/min] | 1677.1227 | 1576.871 | 1694.0825 | 1597.7126 | 1548.4609 | 1414.7887 |  |  |  |  | 2021-05-06
WY_LO_PLANT CIRC PUMP Flow Rate [gal/min] | PLANT CIRC PUMP Flow Rate [gal/min] | 231.8522 | 230.9059 | 230.1641 | 228.8612 | 226.8879 | 224.8923 |  |  |  |  | 2021-05-06
WY_LO_COOLSYS1 PUMP SECONDARY Pressure setpoint reset [yes,no] | COOLSYS1 PUMP SECONDARY Pressure setpoint reset [yes,no] | pump_ride_on_curve | pump_ride_on_curve | pump_ride_on_curve | pump_ride_on_curve | pump_ride_on_curve | pump_ride_on_curve |  |  |  |  | 2021-05-06
WY_LO_COOLSYS1 CHILLER1 PUMP Pump Power [hp] | COOLSYS1 CHILLER1 PUMP Pump Power [hp] | 2.5127 | 2.3225 | 2.6013 | 2.3706 | 2.318 | 2.0967 |  |  |  |  | 2021-05-06
WY_LO_COOLSYS1 CHILLER2 PUMP Pump Power [hp] | COOLSYS1 CHILLER2 PUMP Pump Power [hp] | 2.5127 | 2.3225 | 2.6013 | 2.3706 | 2.318 | 2.0967 |  |  |  |  | 2021-05-06
WY_LO_COOLSYS1 PUMP SECONDARY Pump Power [hp] | COOLSYS1 PUMP SECONDARY Pump Power [hp] | 15.0762 | 13.9348 | 15.6076 | 14.2234 | 13.9079 | 12.5805 |  |  |  |  | 2021-05-06
WY_LO_HEATSYS1 PUMP Pump Power [hp] | HEATSYS1 PUMP Pump Power [hp] | 20.2998 | 17.8771 | 20.9392 | 18.4738 | 20.6871 | 17.9534 |  |  |  |  | 2021-05-06
WY_LO_TOWERWATERSYS PUMP Pump Power [hp] | TOWERWATERSYS PUMP Pump Power [hp] | 30.0284 | 27.9529 | 30.3311 | 28.321 | 27.7238 | 25.0797 |  |  |  |  | 2021-05-06
WY_LO_PLANT CIRC PUMP Pump Power [hp] | PLANT CIRC PUMP Pump Power [hp] | 5.003 | 4.9333 | 4.9666 | 4.8896 | 4.8959 | 4.8048 |  |  |  |  | 2021-05-06
WY_LO_Datacenter PLANT CIRC PUMP Pump Power [hp] | Datacenter PLANT CIRC PUMP Pump Power [hp] | 5.003 | 4.9333 | 4.9666 | 4.8896 | 4.8959 | 4.8048 |  |  |  |  | 2021-05-06
WY_LO_ZN_VAV_BOXes_Max_Reheat_Water_Flow_GPM | ZN_VAV_BOXes_Max_Reheat_Water_Flow_GPM | 502.0438 | 481.5704 | 498.9438 | 479.3924 | 478.4009 | 447.1881 |  |  |  |  | 2021-05-06
WY_LO_COOLSYS1 PUMP SECONDARY VSD | COOLSYS1 PUMP SECONDARY VSD | No | No | No | No | No | No |  |  |  |  | 2021-05-06
WY_LO_HEATSYS1 PUMP VSD | HEATSYS1 PUMP VSD | No | No | No | No | No | No |  |  |  |  | 2021-05-06
WY_LO_DATACENTER BASEMENT Cooling Capacity [ton] | DATACENTER BASEMENT Cooling Capacity [ton] | 135.5652 | 135.1586 | 134.3993 | 133.9861 | 131.669 | 131.2465 |  |  |  |  | 2021-05-06
WY_LO_DATACENTER BOT Cooling Capacity [ton] | DATACENTER BOT Cooling Capacity [ton] | 2.9651 | 2.9384 | 2.9564 | 2.9102 | 2.9776 | 2.8948 |  |  |  |  | 2021-05-06
WY_LO_DATACENTER MID Cooling Capacity [ton] | DATACENTER MID Cooling Capacity [ton] | 28.413 | 28.1765 | 28.3557 | 27.9036 | 28.6506 | 27.7803 |  |  |  |  | 2021-05-06
WY_LO_DATACENTER TOP Cooling Capacity [ton] | DATACENTER TOP Cooling Capacity [ton] | 2.8927 | 2.87 | 2.8891 | 2.8462 | 2.9029 | 2.8162 |  |  |  |  | 2021-05-06
id | item | Zone5B(WY-Cheyenne-WY) ASHRAE901-state_STD2016 | Zone5B(WY-Cheyenne-WY) ASHRAE901-state_STD2019 | Zone6B(WY-Casper-WY) ASHRAE901-state_STD2016 | Zone6B(WY-Casper-WY) ASHRAE901-state_STD2019 | Zone7(WY-JacksonHole-WY) ASHRAE901-state_STD2016 | Zone7(WY-JacksonHole-WY) ASHRAE901-state_STD2019 |  |  |  |  | 2021-05-06
WY_RS_PSZ-AC:1 Cooling Capacity [ton] | PSZ-AC:1 Cooling Capacity [ton] | 9.6978 | 8.8276 | 9.6692 | 8.9114 | 8.5229 | 7.672 |  |  |  |  | 2021-05-06
WY_RS_PSZ-AC:2 Cooling Capacity [ton] | PSZ-AC:2 Cooling Capacity [ton] | 40.3787 | 37.9592 | 41.4902 | 39.4287 | 38.8528 | 36.5165 |  |  |  |  | 2021-05-06
WY_RS_PSZ-AC:3 Cooling Capacity [ton] | PSZ-AC:3 Cooling Capacity [ton] | 5.7536 | 5.548 | 5.6991 | 5.4721 | 5.5887 | 5.157 |  |  |  |  | 2021-05-06
WY_RS_PSZ-AC:4 Cooling Capacity [ton] | PSZ-AC:4 Cooling Capacity [ton] | 4.2567 | 4.062 | 4.4498 | 4.2299 | 4.1248 | 3.6738 |  |  |  |  | 2021-05-06
WY_RS_PSZ-AC:1 Supply Flow Rate [cfm] | PSZ-AC:1 Supply Flow Rate [cfm] | 4364.8928 | 3983.4944 | 4280.1376 | 3898.7392 | 3835.1728 | 3453.7744 |  |  |  |  | 2021-05-06
WY_RS_PSZ-AC:2 Supply Flow Rate [cfm] | PSZ-AC:2 Supply Flow Rate [cfm] | 18179.9904 | 17078.1728 | 17713.8368 | 16717.9632 | 17480.76 | 16442.5088 |  |  |  |  | 2021-05-06
WY_RS_PSZ-AC:3 Supply Flow Rate [cfm] | PSZ-AC:3 Supply Flow Rate [cfm] | 2585.0336 | 2500.2784 | 2563.8448 | 2457.9008 | 2521.4672 | 2330.768 |  |  |  |  | 2021-05-06
WY_RS_PSZ-AC:4 Supply Flow Rate [cfm] | PSZ-AC:4 Supply Flow Rate [cfm] | 1906.992 | 1822.2368 | 1970.5584 | 1864.6144 | 1864.6144 | 1652.7264 |  |  |  |  | 2021-05-06
WY_RS_PSZ-AC:1 OA Rate [cfm] | PSZ-AC:1 OA Rate [cfm] | 490.669 | 490.669 | 490.669 | 490.669 | 490.669 | 490.669 |  |  |  |  | 2021-05-06
WY_RS_PSZ-AC:2 OA Rate [cfm] | PSZ-AC:2 OA Rate [cfm] | 4005.1282 | 4005.1282 | 4005.1282 | 4005.1282 | 4005.1282 | 4005.1282 |  |  |  |  | 2021-05-06
WY_RS_PSZ-AC:3 OA Rate [cfm] | PSZ-AC:3 OA Rate [cfm] | 377.3937 | 377.3937 | 377.3937 | 377.3937 | 377.3937 | 377.3937 |  |  |  |  | 2021-05-06
WY_RS_PSZ-AC:4 OA Rate [cfm] | PSZ-AC:4 OA Rate [cfm] | 377.3937 | 377.3937 | 377.3937 | 377.3937 | 377.3937 | 377.3937 |  |  |  |  | 2021-05-06
WY_RS_PSZ-AC:1 OA Damper [gravity, motorized] | PSZ-AC:1 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | motorized | motorized |  |  |  |  | 2021-05-06
WY_RS_PSZ-AC:2 OA Damper [gravity, motorized] | PSZ-AC:2 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | motorized | motorized |  |  |  |  | 2021-05-06
WY_RS_PSZ-AC:3 OA Damper [gravity, motorized] | PSZ-AC:3 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | motorized | motorized |  |  |  |  | 2021-05-06
WY_RS_PSZ-AC:4 OA Damper [gravity, motorized] | PSZ-AC:4 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | motorized | motorized |  |  |  |  | 2021-05-06
WY_RS_PSZ-AC:1 Heating Capacity [kBtu/hr] | PSZ-AC:1 Heating Capacity [kBtu/hr] | 159.9454 | 146.3057 | 163.5692 | 150.2255 | 142.3284 | 135.624 |  |  |  |  | 2021-05-06
WY_RS_PSZ-AC:2 Heating Capacity [kBtu/hr] | PSZ-AC:2 Heating Capacity [kBtu/hr] | 791.7328 | 754.0121 | 813.6354 | 780.1747 | 783.623 | 750.184 |  |  |  |  | 2021-05-06
WY_RS_PSZ-AC:3 Heating Capacity [kBtu/hr] | PSZ-AC:3 Heating Capacity [kBtu/hr] | 101.5174 | 98.7743 | 104.7264 | 101.7248 | 100.2476 | 94.4646 |  |  |  |  | 2021-05-06
WY_RS_PSZ-AC:4 Heating Capacity [kBtu/hr] | PSZ-AC:4 Heating Capacity [kBtu/hr] | 81.5518 | 78.9543 | 86.9609 | 83.5747 | 81.1033 | 75.2038 |  |  |  |  | 2021-05-06
id | item | Zone5B(WY-Cheyenne-WY) ASHRAE901-state_STD2016 | Zone5B(WY-Cheyenne-WY) ASHRAE901-state_STD2019 | Zone6B(WY-Casper-WY) ASHRAE901-state_STD2016 | Zone6B(WY-Casper-WY) ASHRAE901-state_STD2019 | Zone7(WY-JacksonHole-WY) ASHRAE901-state_STD2016 | Zone7(WY-JacksonHole-WY) ASHRAE901-state_STD2019 |  |  |  |  | 2021-05-06
WY_PS_VAV_POD_1 Cooling Capacity [ton] | VAV_POD_1 Cooling Capacity [ton] | 18.2909 | 17.1096 | 21.593 | 19.9435 | 14.8308 | 13.6135 |  |  |  |  | 2021-05-06
WY_PS_VAV_POD_2 Cooling Capacity [ton] | VAV_POD_2 Cooling Capacity [ton] | 18.0631 | 16.7764 | 21.2724 | 19.5765 | 14.62 | 13.3904 |  |  |  |  | 2021-05-06
WY_PS_VAV_POD_3 Cooling Capacity [ton] | VAV_POD_3 Cooling Capacity [ton] | 16.8573 | 15.6803 | 19.8856 | 18.1959 | 13.7629 | 12.3957 |  |  |  |  | 2021-05-06
WY_PS_VAV_OTHER Cooling Capacity [ton] | VAV_OTHER Cooling Capacity [ton] | 21.2016 | 19.8463 | 23.1023 | 20.7647 | 20.505 | 18.4036 |  |  |  |  | 2021-05-06
WY_PS_PSZ-AC_1:6 Cooling Capacity [ton] | PSZ-AC_1:6 Cooling Capacity [ton] | 7.6085 | 7.3294 | 7.7724 | 7.4666 | 7.0423 | 6.6663 |  |  |  |  | 2021-05-06
WY_PS_PSZ-AC_2:5 Cooling Capacity [ton] | PSZ-AC_2:5 Cooling Capacity [ton] | 4.7478 | 4.7322 | 5.294 | 5.2374 | 4.5851 | 4.5373 |  |  |  |  | 2021-05-06
WY_PS_PSZ-AC_2:7 Cooling Capacity [ton] | PSZ-AC_2:7 Cooling Capacity [ton] | 8.7516 | 8.7516 | 10.0701 | 10.0701 | 7.6239 | 7.6239 |  |  |  |  | 2021-05-06
WY_PS_VAV_POD_1 Supply Flow Rate [cfm] | VAV_POD_1 Supply Flow Rate [cfm] | 6589.7168 | 6165.9408 | 6738.0384 | 6229.5072 | 6314.2624 | 5805.7312 |  |  |  |  | 2021-05-06
WY_PS_VAV_POD_2 Supply Flow Rate [cfm] | VAV_POD_2 Supply Flow Rate [cfm] | 6504.9616 | 6038.808 | 6632.0944 | 6102.3744 | 6229.5072 | 5699.7872 |  |  |  |  | 2021-05-06
WY_PS_VAV_POD_3 Supply Flow Rate [cfm] | VAV_POD_3 Supply Flow Rate [cfm] | 6081.1856 | 5699.7872 | 6208.3184 | 5742.1648 | 5869.2976 | 5276.0112 |  |  |  |  | 2021-05-06
WY_PS_VAV_OTHER Supply Flow Rate [cfm] | VAV_OTHER Supply Flow Rate [cfm] | 9534.96 | 8941.6736 | 9619.7152 | 8899.296 | 9238.3168 | 8284.8208 |  |  |  |  | 2021-05-06
WY_PS_PSZ-AC_2:5 Supply Flow Rate [cfm] | PSZ-AC_2:5 Supply Flow Rate [cfm] | 1991.7472 | 1970.5584 | 1970.5584 | 1949.3696 | 2055.3136 | 2034.1248 |  |  |  |  | 2021-05-06
WY_PS_PSZ-AC_1:6 Supply Flow Rate [cfm] | PSZ-AC_1:6 Supply Flow Rate [cfm] | 3135.9424 | 2987.6208 | 3072.376 | 2924.0544 | 3178.32 | 3008.8096 |  |  |  |  | 2021-05-06
WY_PS_PSZ-AC_2:7 Supply Flow Rate [cfm] | PSZ-AC_2:7 Supply Flow Rate [cfm] | 3157.1312 | 3157.1312 | 3157.1312 | 3157.1312 | 3157.1312 | 3157.1312 |  |  |  |  | 2021-05-06
WY_PS_Supply Air Temp. Reset Flag | Supply Air Temp. Reset Flag | Yes | Yes | Yes | Yes | Yes | Yes |  |  |  |  | 2021-05-06
WY_PS_VAV_POD_1 OA Rate [cfm] | VAV_POD_1 OA Rate [cfm] | 6592.0476 | 6166.3222 | 6747.1496 | 6226.901 | 6316.8474 | 5800.3916 |  |  |  |  | 2021-05-06
WY_PS_VAV_POD_2 OA Rate [cfm] | VAV_POD_2 OA Rate [cfm] | 6509.941 | 6046.2029 | 6641.8201 | 6112.312 | 6227.0069 | 5705.3599 |  |  |  |  | 2021-05-06
WY_PS_VAV_POD_3 OA Rate [cfm] | VAV_POD_3 OA Rate [cfm] | 6072.3287 | 5422.002 | 6208.382 | 5422.002 | 5863.1529 | 5281.5203 |  |  |  |  | 2021-05-06
WY_PS_VAV_OTHER OA Rate [cfm] | VAV_OTHER OA Rate [cfm] | 3736.1787 | 2988.8921 | 3736.1787 | 2988.8921 | 3736.1787 | 2988.8921 |  |  |  |  | 2021-05-06
WY_PS_PSZ-AC_2:5 OA Rate [cfm] | PSZ-AC_2:5 OA Rate [cfm] | 1152.7343 | 1152.7343 | 1152.7343 | 1152.7343 | 1152.7343 | 1152.7343 |  |  |  |  | 2021-05-06
WY_PS_PSZ-AC_1:6 OA Rate [cfm] | PSZ-AC_1:6 OA Rate [cfm] | 539.9118 | 539.9118 | 539.9118 | 539.9118 | 539.9118 | 539.9118 |  |  |  |  | 2021-05-06
WY_PS_PSZ-AC_2:7 OA Rate [cfm] | PSZ-AC_2:7 OA Rate [cfm] | 3153.0841 | 3153.0841 | 3153.0841 | 3153.0841 | 3153.0841 | 3153.0841 |  |  |  |  | 2021-05-06
WY_PS_VAV_POD_1 OA Damper [gravity, motorized] | VAV_POD_1 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | motorized | motorized |  |  |  |  | 2021-05-06
WY_PS_VAV_POD_2 OA Damper [gravity, motorized] | VAV_POD_2 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | motorized | motorized |  |  |  |  | 2021-05-06
WY_PS_VAV_POD_3 OA Damper [gravity, motorized] | VAV_POD_3 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | motorized | motorized |  |  |  |  | 2021-05-06
WY_PS_VAV_OTHER OA Damper [gravity, motorized] | VAV_OTHER OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | motorized | motorized |  |  |  |  | 2021-05-06
WY_PS_PSZ-AC_2:5 OA Damper [gravity, motorized] | PSZ-AC_2:5 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | motorized | motorized |  |  |  |  | 2021-05-06
WY_PS_PSZ-AC_1:6 OA Damper [gravity, motorized] | PSZ-AC_1:6 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | motorized | motorized |  |  |  |  | 2021-05-06
WY_PS_PSZ-AC_2:7 OA Damper [gravity, motorized] | PSZ-AC_2:7 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | motorized | motorized |  |  |  |  | 2021-05-06
WY_PS_VAV_POD_1 (economizer) | VAV_POD_1 (economizer) | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb |  |  |  |  | 2021-05-06
WY_PS_VAV_POD_2 (economizer) | VAV_POD_2 (economizer) | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb |  |  |  |  | 2021-05-06
WY_PS_VAV_POD_3 (economizer) | VAV_POD_3 (economizer) | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb |  |  |  |  | 2021-05-06
WY_PS_VAV_OTHER (economizer) | VAV_OTHER (economizer) | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb |  |  |  |  | 2021-05-06
WY_PS_PSZ-AC_2:5 (economizer) | PSZ-AC_2:5 (economizer) | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb |  |  |  |  | 2021-05-06
WY_PS_PSZ-AC_1:6 (economizer) | PSZ-AC_1:6 (economizer) | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb |  |  |  |  | 2021-05-06
WY_PS_PSZ-AC_2:7 (economizer) | PSZ-AC_2:7 (economizer) | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb |  |  |  |  | 2021-05-06
WY_PS_VAV_Pod_1_ERV Flag | VAV_Pod_1_ERV Flag | No | No | Yes | Yes | Yes | Yes |  |  |  |  | 2021-05-06
WY_PS_VAV_Pod_2_ERV Flag | VAV_Pod_2_ERV Flag | No | No | Yes | Yes | Yes | Yes |  |  |  |  | 2021-05-06
WY_PS_VAV_Pod_3_ERV Flag | VAV_Pod_3_ERV Flag | No | No | Yes | Yes | Yes | Yes |  |  |  |  | 2021-05-06
WY_PS_VAV_OTHER_ERV Flag | VAV_OTHER_ERV Flag | No | No | No | No | Yes | Yes |  |  |  |  | 2021-05-06
WY_PS_PSZ_AC_2_5_ERV Flag | PSZ_AC_2_5_ERV Flag | No | No | No | No | Yes | Yes |  |  |  |  | 2021-05-06
WY_PS_PSZ_AC_2_7_ERV Flag | PSZ_AC_2_7_ERV Flag | No | No | Yes | Yes | Yes | Yes |  |  |  |  | 2021-05-06
WY_PS_HEATSYS1 Capacity [MMBTU/h] | HEATSYS1 Capacity [MMBTU/h] | 1.193 | 1.1215 | 1.2627 | 1.177 | 1.1956 | 1.0969 |  |  |  |  | 2021-05-06
WY_PS_HEATSYS1 Flow Rate [gal/min] | HEATSYS1 Flow Rate [gal/min] | 122.4417 | 115.1024 | 129.5889 | 120.7959 | 122.7099 | 112.5777 |  |  |  |  | 2021-05-06
WY_PS_VAV_POD_1 Fan Power [hp] | VAV_POD_1 Fan Power [hp] | 9.7252 | 9.0972 | 9.8787 | 9.1865 | 9.3225 | 8.5573 |  |  |  |  | 2021-05-06
WY_PS_VAV_POD_2 Fan Power [hp] | VAV_POD_2 Fan Power [hp] | 9.6041 | 8.92 | 9.7987 | 9.0175 | 9.19 | 8.4171 |  |  |  |  | 2021-05-06
WY_PS_VAV_POD_3 Fan Power [hp] | VAV_POD_3 Fan Power [hp] | 8.963 | 8.3976 | 9.1599 | 8.4722 | 8.6513 | 7.7918 |  |  |  |  | 2021-05-06
WY_PS_VAV_OTHER Fan Power [hp] | VAV_OTHER Fan Power [hp] | 13.9739 | 13.0806 | 14.0691 | 13.0294 | 13.5147 | 12.1297 |  |  |  |  | 2021-05-06
WY_PS_HEATSYS1 Pump Power [hp] | HEATSYS1 Pump Power [hp] | 2.6466 | 2.4634 | 2.8011 | 2.5852 | 2.6524 | 2.4093 |  |  |  |  | 2021-05-06
WY_PS_PSZ-AC_1:6 Heating Capacity [kBtu/hr] | PSZ-AC_1:6 Heating Capacity [kBtu/hr] | 212.4048 | 204.0132 | 216.4172 | 207.287 | 215.0798 | 204.7499 |  |  |  |  | 2021-05-06
WY_PS_PSZ-AC_2:5 Heating Capacity [kBtu/hr] | PSZ-AC_2:5 Heating Capacity [kBtu/hr] | 134.4949 | 134.2343 | 142.1593 | 141.2753 | 142.8646 | 142.2398 |  |  |  |  | 2021-05-06
WY_PS_PSZ-AC_2:7 Heating Capacity [kBtu/hr] | PSZ-AC_2:7 Heating Capacity [kBtu/hr] | 300.431 | 300.431 | 320.5699 | 320.5699 | 318.5068 | 318.5068 |  |  |  |  | 2021-05-06
WY_PS_ZN_VAV_BOXes_Max_Reheat_Water_Flow_GPM | ZN_VAV_BOXes_Max_Reheat_Water_Flow_GPM | 75.5697 | 71.303 | 77.3241 | 72.5147 | 72.0603 | 66.639 |  |  |  |  | 2021-05-06
id | item | Zone5B(WY-Cheyenne-WY) ASHRAE901-state_STD2016 | Zone5B(WY-Cheyenne-WY) ASHRAE901-state_STD2019 | Zone6B(WY-Casper-WY) ASHRAE901-state_STD2016 | Zone6B(WY-Casper-WY) ASHRAE901-state_STD2019 | Zone7(WY-JacksonHole-WY) ASHRAE901-state_STD2016 | Zone7(WY-JacksonHole-WY) ASHRAE901-state_STD2019 |  |  |  |  | 2021-05-06
WY_SH_SAC_FRONTOFFICE Cooling Capacity [ton] | SAC_FRONTOFFICE Cooling Capacity [ton] | 2.0133 | 1.8777 | 2.0165 | 1.8969 | 1.9649 | 1.8031 |  |  |  |  | 2021-05-06
WY_SH_SAC_FRONTLOUNGE Cooling Capacity [ton] | SAC_FRONTLOUNGE Cooling Capacity [ton] | 5.0566 | 4.8101 | 5.3025 | 5.0352 | 4.8 | 4.516 |  |  |  |  | 2021-05-06
WY_SH_SAC_MEETINGROOM Cooling Capacity [ton] | SAC_MEETINGROOM Cooling Capacity [ton] | 2.6702 | 2.5967 | 2.7793 | 2.7032 | 2.3999 | 2.325 |  |  |  |  | 2021-05-06
WY_SH_SAC_EXC_EMPLGE_RESTRM Cooling Capacity [ton] | SAC_EXC_EMPLGE_RESTRM Cooling Capacity [ton] | 5.9583 | 5.9082 | 5.8466 | 5.7912 | 6.0424 | 5.9732 |  |  |  |  | 2021-05-06
WY_SH_SAC_FO_ADDAQ SUPPLY FAN Supply Flow Rate [cfm] | SAC_FO_ADDAQ SUPPLY FAN Supply Flow Rate [cfm] | 911.1184 | 847.552 | 911.1184 | 847.552 | 889.9296 | 805.1744 |  |  |  |  | 2021-05-06
WY_SH_SAC_FL_ADDAQ SUPPLY FAN Supply Flow Rate [cfm] | SAC_FL_ADDAQ SUPPLY FAN Supply Flow Rate [cfm] | 2182.4464 | 2076.5024 | 2161.2576 | 2055.3136 | 2161.2576 | 2034.1248 |  |  |  |  | 2021-05-06
WY_SH_SAC_MR_ADDAQ SUPPLY FAN Supply Flow Rate [cfm] | SAC_MR_ADDAQ SUPPLY FAN Supply Flow Rate [cfm] | 1038.2512 | 1017.0624 | 1038.2512 | 995.8736 | 1038.2512 | 995.8736 |  |  |  |  | 2021-05-06
WY_SH_SAC_EXC_ADDAQ SUPPLY FAN Supply Flow Rate [cfm] | SAC_EXC_ADDAQ SUPPLY FAN Supply Flow Rate [cfm] | 2690.9776 | 2669.7888 | 2627.4112 | 2606.2224 | 2712.1664 | 2690.9776 |  |  |  |  | 2021-05-06
WY_SH_SAC_Exc_EmpLge_RestRm OA Rate [cfm] | SAC_Exc_EmpLge_RestRm OA Rate [cfm] | 199.9928 | 199.9928 | 199.9928 | 199.9928 | 199.9928 | 199.9928 |  |  |  |  | 2021-05-06
WY_SH_SAC_FrontLounge OA Rate [cfm] | SAC_FrontLounge OA Rate [cfm] | 500.0133 | 500.0133 | 500.0133 | 500.0133 | 500.0133 | 500.0133 |  |  |  |  | 2021-05-06
WY_SH_SAC_FrontOffice OA Rate [cfm] | SAC_FrontOffice OA Rate [cfm] | 119.2938 | 119.2938 | 119.2938 | 119.2938 | 119.2938 | 119.2938 |  |  |  |  | 2021-05-06
WY_SH_SAC_MeetingRoom OA Rate [cfm] | SAC_MeetingRoom OA Rate [cfm] | 267.7629 | 267.7629 | 267.7629 | 267.7629 | 267.7629 | 267.7629 |  |  |  |  | 2021-05-06
WY_SH_SAC_FrontLounge OA Damper [gravity, motorized] | SAC_FrontLounge OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | motorized | motorized |  |  |  |  | 2021-05-06
WY_SH_SAC_FrontOffice (economizer) | SAC_FrontOffice (economizer) | No | No | No | No | No | No |  |  |  |  | 2021-05-06
WY_SH_SAC_FrontLounge (economizer) | SAC_FrontLounge (economizer) | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb |  |  |  |  | 2021-05-06
WY_SH_SAC_MeetingRoom (economizer) | SAC_MeetingRoom (economizer) | No | No | No | No | No | No |  |  |  |  | 2021-05-06
WY_SH_SAC_Exc_EmpLge_RestRm (economizer) | SAC_Exc_EmpLge_RestRm (economizer) | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb |  |  |  |  | 2021-05-06
WY_SH_SAC_FRONTOFFICE Heating Capacity [kBtu/hr] | SAC_FRONTOFFICE Heating Capacity [kBtu/hr] | 34.4738 | 32.6817 | 35.8868 | 34.1029 | 34.1064 | 32.0069 |  |  |  |  | 2021-05-06
WY_SH_SAC_FRONTLOUNGE Heating Capacity [kBtu/hr] | SAC_FRONTLOUNGE Heating Capacity [kBtu/hr] | 96.9686 | 93.6451 | 101.1958 | 97.7103 | 98.3758 | 94.6913 |  |  |  |  | 2021-05-06
WY_SH_SAC_MEETINGROOM Heating Capacity [kBtu/hr] | SAC_MEETINGROOM Heating Capacity [kBtu/hr] | 48.3919 | 47.3839 | 50.3418 | 49.3201 | 49.3476 | 48.2872 |  |  |  |  | 2021-05-06
WY_SH_SAC_EXC_EMPLGE_RESTRM Heating Capacity [kBtu/hr] | SAC_EXC_EMPLGE_RESTRM Heating Capacity [kBtu/hr] | 91.9278 | 91.2654 | 93.8759 | 93.1228 | 92.8318 | 91.9339 |  |  |  |  | 2021-05-06
id | item | Zone5B(WY-Cheyenne-WY) ASHRAE901-state_STD2016 | Zone5B(WY-Cheyenne-WY) ASHRAE901-state_STD2019 | Zone6B(WY-Casper-WY) ASHRAE901-state_STD2016 | Zone6B(WY-Casper-WY) ASHRAE901-state_STD2019 | Zone7(WY-JacksonHole-WY) ASHRAE901-state_STD2016 | Zone7(WY-JacksonHole-WY) ASHRAE901-state_STD2019 |  |  |  |  | 2021-05-06
WY_MA_SPLIT GSW COOLING COIL Cooling Capacity [ton] | SPLIT GSW COOLING COIL Cooling Capacity [ton] | 0.76586 | 0.74635 | 0.83273 | 0.79306 | 0.77458 | 0.69628 |  |  |  |  | 2021-05-06
WY_MA_SPLIT GNW COOLING COIL Cooling Capacity [ton] | SPLIT GNW COOLING COIL Cooling Capacity [ton] | 0.72026 | 0.70141 | 0.77807 | 0.74156 | 0.70779 | 0.64231 |  |  |  |  | 2021-05-06
WY_MA_SPLIT OFFICE COOLING COIL Cooling Capacity [ton] | SPLIT OFFICE COOLING COIL Cooling Capacity [ton] | 1.7519 | 1.5517 | 1.838 | 1.6131 | 1.7076 | 1.4412 |  |  |  |  | 2021-05-06
WY_MA_SPLIT GNE COOLING COIL Cooling Capacity [ton] | SPLIT GNE COOLING COIL Cooling Capacity [ton] | 0.57056 | 0.55464 | 0.63137 | 0.60225 | 0.54644 | 0.49634 |  |  |  |  | 2021-05-06
WY_MA_SPLIT GN1 COOLING COIL Cooling Capacity [ton] | SPLIT GN1 COOLING COIL Cooling Capacity [ton] | 0.48821 | 0.4756 | 0.52017 | 0.50049 | 0.45403 | 0.42524 |  |  |  |  | 2021-05-06
WY_MA_SPLIT GN2 COOLING COIL Cooling Capacity [ton] | SPLIT GN2 COOLING COIL Cooling Capacity [ton] | 0.48506 | 0.47254 | 0.51731 | 0.49785 | 0.45108 | 0.42271 |  |  |  |  | 2021-05-06
WY_MA_SPLIT GS1 COOLING COIL Cooling Capacity [ton] | SPLIT GS1 COOLING COIL Cooling Capacity [ton] | 0.53302 | 0.5192 | 0.57654 | 0.55355 | 0.52092 | 0.4797 |  |  |  |  | 2021-05-06
WY_MA_SPLIT GS2 COOLING COIL Cooling Capacity [ton] | SPLIT GS2 COOLING COIL Cooling Capacity [ton] | 0.57715 | 0.55692 | 0.62149 | 0.59213 | 0.5654 | 0.51763 |  |  |  |  | 2021-05-06
WY_MA_SPLIT MSW COOLING COIL Cooling Capacity [ton] | SPLIT MSW COOLING COIL Cooling Capacity [ton] | 2.0786 | 2.0348 | 2.1465 | 2.051 | 2.1596 | 1.9582 |  |  |  |  | 2021-05-06
WY_MA_SPLIT MNW COOLING COIL Cooling Capacity [ton] | SPLIT MNW COOLING COIL Cooling Capacity [ton] | 1.9876 | 1.9456 | 2.0373 | 1.948 | 2.0236 | 1.8477 |  |  |  |  | 2021-05-06
WY_MA_SPLIT MSE COOLING COIL Cooling Capacity [ton] | SPLIT MSE COOLING COIL Cooling Capacity [ton] | 1.6126 | 1.5761 | 1.7135 | 1.6345 | 1.6734 | 1.4809 |  |  |  |  | 2021-05-06
WY_MA_SPLIT MNE COOLING COIL Cooling Capacity [ton] | SPLIT MNE COOLING COIL Cooling Capacity [ton] | 1.4863 | 1.4472 | 1.5308 | 1.4751 | 1.5053 | 1.3415 |  |  |  |  | 2021-05-06
WY_MA_SPLIT MN1 COOLING COIL Cooling Capacity [ton] | SPLIT MN1 COOLING COIL Cooling Capacity [ton] | 1.2056 | 1.1816 | 1.216 | 1.1786 | 1.1466 | 1.0779 |  |  |  |  | 2021-05-06
WY_MA_SPLIT MN2 COOLING COIL Cooling Capacity [ton] | SPLIT MN2 COOLING COIL Cooling Capacity [ton] | 1.1967 | 1.173 | 1.2072 | 1.1705 | 1.1354 | 1.0683 |  |  |  |  | 2021-05-06
WY_MA_SPLIT MS1 COOLING COIL Cooling Capacity [ton] | SPLIT MS1 COOLING COIL Cooling Capacity [ton] | 1.2792 | 1.2539 | 1.3183 | 1.2749 | 1.261 | 1.1769 |  |  |  |  | 2021-05-06
WY_MA_SPLIT MS2 COOLING COIL Cooling Capacity [ton] | SPLIT MS2 COOLING COIL Cooling Capacity [ton] | 1.2707 | 1.2456 | 1.3102 | 1.2674 | 1.2519 | 1.1692 |  |  |  |  | 2021-05-06
WY_MA_SPLIT TSW COOLING COIL Cooling Capacity [ton] | SPLIT TSW COOLING COIL Cooling Capacity [ton] | 1.3271 | 1.3034 | 1.3767 | 1.3229 | 1.3315 | 1.218 |  |  |  |  | 2021-05-06
WY_MA_SPLIT TNW COOLING COIL Cooling Capacity [ton] | SPLIT TNW COOLING COIL Cooling Capacity [ton] | 1.274 | 1.2509 | 1.3131 | 1.2622 | 1.2639 | 1.1626 |  |  |  |  | 2021-05-06
WY_MA_SPLIT TSE COOLING COIL Cooling Capacity [ton] | SPLIT TSE COOLING COIL Cooling Capacity [ton] | 1.0891 | 1.0701 | 1.1545 | 1.112 | 1.0742 | 0.96372 |  |  |  |  | 2021-05-06
WY_MA_SPLIT TNE COOLING COIL Cooling Capacity [ton] | SPLIT TNE COOLING COIL Cooling Capacity [ton] | 0.98209 | 0.96548 | 1.028 | 0.99554 | 0.90259 | 0.83906 |  |  |  |  | 2021-05-06
WY_MA_SPLIT TN1 COOLING COIL Cooling Capacity [ton] | SPLIT TN1 COOLING COIL Cooling Capacity [ton] | 0.7864 | 0.77394 | 0.81159 | 0.79104 | 0.72236 | 0.6893 |  |  |  |  | 2021-05-06
WY_MA_SPLIT TN2 COOLING COIL Cooling Capacity [ton] | SPLIT TN2 COOLING COIL Cooling Capacity [ton] | 0.78472 | 0.77186 | 0.81029 | 0.78895 | 0.71123 | 0.67972 |  |  |  |  | 2021-05-06
WY_MA_SPLIT TS1 COOLING COIL Cooling Capacity [ton] | SPLIT TS1 COOLING COIL Cooling Capacity [ton] | 0.88396 | 0.86924 | 0.9231 | 0.89402 | 0.85367 | 0.77412 |  |  |  |  | 2021-05-06
WY_MA_SPLIT TS2 COOLING COIL Cooling Capacity [ton] | SPLIT TS2 COOLING COIL Cooling Capacity [ton] | 0.88663 | 0.8718 | 0.92693 | 0.89725 | 0.85944 | 0.77906 |  |  |  |  | 2021-05-06
WY_MA_Split GN1 Furnace with DX Cooling OA Rate [cfm] | Split GN1 Furnace with DX Cooling OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 |  |  |  |  | 2021-05-06
WY_MA_Split GN2 Furnace with DX Cooling OA Rate [cfm] | Split GN2 Furnace with DX Cooling OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 |  |  |  |  | 2021-05-06
WY_MA_Split GNE Furnace with DX Cooling OA Rate [cfm] | Split GNE Furnace with DX Cooling OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 |  |  |  |  | 2021-05-06
WY_MA_Split GNW Furnace with DX Cooling OA Rate [cfm] | Split GNW Furnace with DX Cooling OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 |  |  |  |  | 2021-05-06
WY_MA_Split GS1 Furnace with DX Cooling OA Rate [cfm] | Split GS1 Furnace with DX Cooling OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 |  |  |  |  | 2021-05-06
WY_MA_Split GS2 Furnace with DX Cooling OA Rate [cfm] | Split GS2 Furnace with DX Cooling OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 |  |  |  |  | 2021-05-06
WY_MA_Split GSW Furnace with DX Cooling OA Rate [cfm] | Split GSW Furnace with DX Cooling OA Rate [cfm] | 56.9945 | 56.9945 | 56.9945 | 56.9945 | 56.9945 | 56.9945 |  |  |  |  | 2021-05-06
WY_MA_Split MN1 Furnace with DX Cooling OA Rate [cfm] | Split MN1 Furnace with DX Cooling OA Rate [cfm] | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824 |  |  |  |  | 2021-05-06
WY_MA_Split MN2 Furnace with DX Cooling OA Rate [cfm] | Split MN2 Furnace with DX Cooling OA Rate [cfm] | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824 |  |  |  |  | 2021-05-06
WY_MA_Split MNE Furnace with DX Cooling OA Rate [cfm] | Split MNE Furnace with DX Cooling OA Rate [cfm] | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824 |  |  |  |  | 2021-05-06
WY_MA_Split MNW Furnace with DX Cooling OA Rate [cfm] | Split MNW Furnace with DX Cooling OA Rate [cfm] | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824 |  |  |  |  | 2021-05-06
WY_MA_Split MS1 Furnace with DX Cooling OA Rate [cfm] | Split MS1 Furnace with DX Cooling OA Rate [cfm] | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824 |  |  |  |  | 2021-05-06
WY_MA_Split MS2 Furnace with DX Cooling OA Rate [cfm] | Split MS2 Furnace with DX Cooling OA Rate [cfm] | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824 |  |  |  |  | 2021-05-06
WY_MA_Split MSE Furnace with DX Cooling OA Rate [cfm] | Split MSE Furnace with DX Cooling OA Rate [cfm] | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824 |  |  |  |  | 2021-05-06
WY_MA_Split MSW Furnace with DX Cooling OA Rate [cfm] | Split MSW Furnace with DX Cooling OA Rate [cfm] | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824 |  |  |  |  | 2021-05-06
WY_MA_Split Office Furnace with DX Cooling OA Rate [cfm] | Split Office Furnace with DX Cooling OA Rate [cfm] | 80.7372 | 80.7372 | 80.7372 | 80.7372 | 80.7372 | 80.7372 |  |  |  |  | 2021-05-06
WY_MA_Split TN1 Furnace with DX Cooling OA Rate [cfm] | Split TN1 Furnace with DX Cooling OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 |  |  |  |  | 2021-05-06
WY_MA_Split TN2 Furnace with DX Cooling OA Rate [cfm] | Split TN2 Furnace with DX Cooling OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 |  |  |  |  | 2021-05-06
WY_MA_Split TNE Furnace with DX Cooling OA Rate [cfm] | Split TNE Furnace with DX Cooling OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 |  |  |  |  | 2021-05-06
WY_MA_Split TNW Furnace with DX Cooling OA Rate [cfm] | Split TNW Furnace with DX Cooling OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 |  |  |  |  | 2021-05-06
WY_MA_Split TS1 Furnace with DX Cooling OA Rate [cfm] | Split TS1 Furnace with DX Cooling OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 |  |  |  |  | 2021-05-06
WY_MA_Split TS2 Furnace with DX Cooling OA Rate [cfm] | Split TS2 Furnace with DX Cooling OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 |  |  |  |  | 2021-05-06
WY_MA_Split TSE Furnace with DX Cooling OA Rate [cfm] | Split TSE Furnace with DX Cooling OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 |  |  |  |  | 2021-05-06
WY_MA_Split TSW Furnace with DX Cooling OA Rate [cfm] | Split TSW Furnace with DX Cooling OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 |  |  |  |  | 2021-05-06
WY_MA_SPLIT GSW HEATING COIL Heating Capacity [kBtu/hr] | SPLIT GSW HEATING COIL Heating Capacity [kBtu/hr] | 10.105 | 10.1646 | 10.2424 | 10.3026 | 9.9036 | 9.7869 |  |  |  |  | 2021-05-06
WY_MA_SPLIT GNW HEATING COIL Heating Capacity [kBtu/hr] | SPLIT GNW HEATING COIL Heating Capacity [kBtu/hr] | 10.0516 | 10.1114 | 10.1768 | 10.237 | 9.8302 | 9.7098 |  |  |  |  | 2021-05-06
WY_MA_SPLIT OFFICE HEATING COIL Heating Capacity [kBtu/hr] | SPLIT OFFICE HEATING COIL Heating Capacity [kBtu/hr] | 22.8243 | 22.9051 | 23.2808 | 23.3618 | 22.9301 | 22.7894 |  |  |  |  | 2021-05-06
WY_MA_SPLIT GNE HEATING COIL Heating Capacity [kBtu/hr] | SPLIT GNE HEATING COIL Heating Capacity [kBtu/hr] | 10.0516 | 10.1114 | 10.2046 | 10.2648 | 9.8529 | 9.7299 |  |  |  |  | 2021-05-06
WY_MA_SPLIT GN1 HEATING COIL Heating Capacity [kBtu/hr] | SPLIT GN1 HEATING COIL Heating Capacity [kBtu/hr] | 7.3128 | 7.3726 | 7.5478 | 7.6081 | 7.3679 | 7.3078 |  |  |  |  | 2021-05-06
WY_MA_SPLIT GN2 HEATING COIL Heating Capacity [kBtu/hr] | SPLIT GN2 HEATING COIL Heating Capacity [kBtu/hr] | 7.3128 | 7.3726 | 7.5487 | 7.6089 | 7.3686 | 7.3085 |  |  |  |  | 2021-05-06
WY_MA_SPLIT GS1 HEATING COIL Heating Capacity [kBtu/hr] | SPLIT GS1 HEATING COIL Heating Capacity [kBtu/hr] | 7.2505 | 7.3102 | 7.4873 | 7.5473 | 7.3137 | 7.2572 |  |  |  |  | 2021-05-06
WY_MA_SPLIT GS2 HEATING COIL Heating Capacity [kBtu/hr] | SPLIT GS2 HEATING COIL Heating Capacity [kBtu/hr] | 7.7639 | 7.8243 | 8.0044 | 8.0652 | 7.8321 | 7.775 |  |  |  |  | 2021-05-06
WY_MA_SPLIT MSW HEATING COIL Heating Capacity [kBtu/hr] | SPLIT MSW HEATING COIL Heating Capacity [kBtu/hr] | 18.4769 | 18.6057 | 18.681 | 18.8102 | 17.0204 | 16.7892 |  |  |  |  | 2021-05-06
WY_MA_SPLIT MNW HEATING COIL Heating Capacity [kBtu/hr] | SPLIT MNW HEATING COIL Heating Capacity [kBtu/hr] | 18.593 | 18.7218 | 18.7918 | 18.921 | 17.1136 | 16.8729 |  |  |  |  | 2021-05-06
WY_MA_SPLIT MSE HEATING COIL Heating Capacity [kBtu/hr] | SPLIT MSE HEATING COIL Heating Capacity [kBtu/hr] | 18.4769 | 18.6057 | 18.7461 | 18.8753 | 17.0738 | 16.8364 |  |  |  |  | 2021-05-06
WY_MA_SPLIT MNE HEATING COIL Heating Capacity [kBtu/hr] | SPLIT MNE HEATING COIL Heating Capacity [kBtu/hr] | 18.593 | 18.7218 | 18.857 | 18.9861 | 17.1671 | 16.9202 |  |  |  |  | 2021-05-06
WY_MA_SPLIT MN1 HEATING COIL Heating Capacity [kBtu/hr] | SPLIT MN1 HEATING COIL Heating Capacity [kBtu/hr] | 12.6735 | 12.7997 | 13.0539 | 13.1802 | 12.033 | 11.921 |  |  |  |  | 2021-05-06
WY_MA_SPLIT MN2 HEATING COIL Heating Capacity [kBtu/hr] | SPLIT MN2 HEATING COIL Heating Capacity [kBtu/hr] | 12.6735 | 12.7997 | 13.0556 | 13.182 | 12.0345 | 11.9223 |  |  |  |  | 2021-05-06
WY_MA_SPLIT MS1 HEATING COIL Heating Capacity [kBtu/hr] | SPLIT MS1 HEATING COIL Heating Capacity [kBtu/hr] | 12.5673 | 12.6934 | 12.9535 | 13.0798 | 11.9507 | 11.848 |  |  |  |  | 2021-05-06
WY_MA_SPLIT MS2 HEATING COIL Heating Capacity [kBtu/hr] | SPLIT MS2 HEATING COIL Heating Capacity [kBtu/hr] | 12.5673 | 12.6934 | 12.9552 | 13.0815 | 11.9522 | 11.8493 |  |  |  |  | 2021-05-06
WY_MA_SPLIT TSW HEATING COIL Heating Capacity [kBtu/hr] | SPLIT TSW HEATING COIL Heating Capacity [kBtu/hr] | 13.2294 | 13.2913 | 13.4889 | 13.551 | 12.2475 | 12.1345 |  |  |  |  | 2021-05-06
WY_MA_SPLIT TNW HEATING COIL Heating Capacity [kBtu/hr] | SPLIT TNW HEATING COIL Heating Capacity [kBtu/hr] | 13.297 | 13.359 | 13.5546 | 13.6168 | 12.3044 | 12.1867 |  |  |  |  | 2021-05-06
WY_MA_SPLIT TSE HEATING COIL Heating Capacity [kBtu/hr] | SPLIT TSE HEATING COIL Heating Capacity [kBtu/hr] | 13.2294 | 13.2913 | 13.5234 | 13.5855 | 12.276 | 12.1597 |  |  |  |  | 2021-05-06
WY_MA_SPLIT TNE HEATING COIL Heating Capacity [kBtu/hr] | SPLIT TNE HEATING COIL Heating Capacity [kBtu/hr] | 13.297 | 13.359 | 13.5891 | 13.6513 | 12.3329 | 12.212 |  |  |  |  | 2021-05-06
WY_MA_SPLIT TN1 HEATING COIL Heating Capacity [kBtu/hr] | SPLIT TN1 HEATING COIL Heating Capacity [kBtu/hr] | 10.1216 | 10.1835 | 10.4692 | 10.5313 | 9.6135 | 9.5577 |  |  |  |  | 2021-05-06
WY_MA_SPLIT TN2 HEATING COIL Heating Capacity [kBtu/hr] | SPLIT TN2 HEATING COIL Heating Capacity [kBtu/hr] | 10.1216 | 10.1835 | 10.4703 | 10.5323 | 9.6143 | 9.5584 |  |  |  |  | 2021-05-06
WY_MA_SPLIT TS1 HEATING COIL Heating Capacity [kBtu/hr] | SPLIT TS1 HEATING COIL Heating Capacity [kBtu/hr] | 10.0476 | 10.1095 | 10.3972 | 10.4592 | 9.5503 | 9.499 |  |  |  |  | 2021-05-06
WY_MA_SPLIT TS2 HEATING COIL Heating Capacity [kBtu/hr] | SPLIT TS2 HEATING COIL Heating Capacity [kBtu/hr] | 10.0476 | 10.1095 | 10.3982 | 10.4602 | 9.5511 | 9.4997 |  |  |  |  | 2021-05-06
WY_MA_Split_GSW ERV Flag | Split_GSW ERV Flag | No | Yes | Yes | Yes | Yes | Yes |  |  |  |  | 2021-05-06
WY_MA_Split_GNW ERV Flag | Split_GNW ERV Flag | No | Yes | Yes | Yes | Yes | Yes |  |  |  |  | 2021-05-06
WY_MA_Split_GNE ERV Flag | Split_GNE ERV Flag | No | Yes | Yes | Yes | Yes | Yes |  |  |  |  | 2021-05-06
WY_MA_Split_GN1 ERV Flag | Split_GN1 ERV Flag | No | Yes | Yes | Yes | Yes | Yes |  |  |  |  | 2021-05-06
WY_MA_Split_GN2 ERV Flag | Split_GN2 ERV Flag | No | Yes | Yes | Yes | Yes | Yes |  |  |  |  | 2021-05-06
WY_MA_Split_GS1 ERV Flag | Split_GS1 ERV Flag | No | Yes | Yes | Yes | Yes | Yes |  |  |  |  | 2021-05-06
WY_MA_Split_GS2 ERV Flag | Split_GS2 ERV Flag | No | Yes | Yes | Yes | Yes | Yes |  |  |  |  | 2021-05-06
WY_MA_Split_MSW ERV Flag | Split_MSW ERV Flag | No | Yes | Yes | Yes | Yes | Yes |  |  |  |  | 2021-05-06
WY_MA_Split_MNW ERV Flag | Split_MNW ERV Flag | No | Yes | Yes | Yes | Yes | Yes |  |  |  |  | 2021-05-06
WY_MA_Split_MSE ERV Flag | Split_MSE ERV Flag | No | Yes | Yes | Yes | Yes | Yes |  |  |  |  | 2021-05-06
WY_MA_Split_MNE ERV Flag | Split_MNE ERV Flag | No | Yes | Yes | Yes | Yes | Yes |  |  |  |  | 2021-05-06
WY_MA_Split_MN1 ERV Flag | Split_MN1 ERV Flag | No | Yes | Yes | Yes | Yes | Yes |  |  |  |  | 2021-05-06
WY_MA_Split_MN2 ERV Flag | Split_MN2 ERV Flag | No | Yes | Yes | Yes | Yes | Yes |  |  |  |  | 2021-05-06
WY_MA_Split_MS1 ERV Flag | Split_MS1 ERV Flag | No | Yes | Yes | Yes | Yes | Yes |  |  |  |  | 2021-05-06
WY_MA_Split_MS2 ERV Flag | Split_MS2 ERV Flag | No | Yes | Yes | Yes | Yes | Yes |  |  |  |  | 2021-05-06
WY_MA_Split_TSW ERV Flag | Split_TSW ERV Flag | No | No | No | No | No | No |  |  |  |  | 2021-05-06
WY_MA_Split_TNW ERV Flag | Split_TNW ERV Flag | No | No | No | No | No | Yes |  |  |  |  | 2021-05-06
WY_MA_Split_TSE ERV Flag | Split_TSE ERV Flag | No | Yes | Yes | Yes | Yes | Yes |  |  |  |  | 2021-05-06
WY_MA_Split_TNE ERV Flag | Split_TNE ERV Flag | No | Yes | Yes | Yes | Yes | Yes |  |  |  |  | 2021-05-06
WY_MA_Split_TN1 ERV Flag | Split_TN1 ERV Flag | No | Yes | Yes | Yes | Yes | Yes |  |  |  |  | 2021-05-06
WY_MA_Split_TN2 ERV Flag | Split_TN2 ERV Flag | No | Yes | Yes | Yes | Yes | Yes |  |  |  |  | 2021-05-06
WY_MA_Split_TS1 ERV Flag | Split_TS1 ERV Flag | No | Yes | Yes | Yes | Yes | Yes |  |  |  |  | 2021-05-06
WY_MA_Split_TS2 ERV Flag | Split_TS2 ERV Flag | No | Yes | Yes | Yes | Yes | Yes |  |  |  |  | 2021-05-06
Note on A433: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Cells B433 to B437 are new outputs from 2023 analysis. Per Matt's comment: "! The gas furnace efficiency improved last code cycle, thus we needed gas coils extraction last time. The electric coils might be backup heat and electric efficiency did not change."
Note on B428: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: In 2023 analysis these names are "PSZ-AC:1_SUPPHEATCOIL heating Capacity [kBtu/hr]. I kept the prior names per Matt's instruction.
Note on B433: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Cells B433 to B437 are new outputs from 2023 analysis. Per Matt's comment: "! The gas furnace efficiency improved last code cycle, thus we needed gas coils extraction last time. The electric coils might be backup heat and electric efficiency did not change."
Note on B452: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: This output does not exist in the 2023 analysis.
Note on B456: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: B456 to B459 do not exist in 2023 analysis.
Note on B483: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: B483 to B486 do not exist in 2023 analysis.
Note on B539: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: In the 2023 analysis cells B539 to B542 are named PSZ-AC:1 HEATING COIL Heating Capacity [kBtu/hr]
Note on B543: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: In the 2023 analysis this is a new output
Note on B579: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: This output does not exist in the 2023 analysis.
Note on B581: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: This output does not exist in the 2023 analysis.
Note on B596: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Cells B596 to B601 do not exist in the 2023 analysis.
Note on B612: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: This output does not exist in the 2023 analysis.
Note on B688: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: In the 2023 analysis these names (cells B688 to B711) are Split GN1_Unitary_Package_DX OA Rare [cfm]
Note on B736: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: In the 2023 analysis cells B736 to B758 do not exist.

## HVAC_Summary
Small Office | Climate Zone 1 | 2A | [5 empty] | Small Office | Climate Zone 2 | 3A | [5 empty] | Small Office | Climate Zone 3 | 3B | [5 empty] | Small Office | Climate Zone 4 | 4A | [5 empty] | Small Office | Climate Zone 5 | 5A
90.1-2019 |  |  | 90.1-2022 |  |  | Incremental Cost |  | 90.1-2019 |  |  | 90.1-2022 |  |  | Incremental Cost |  | 90.1-2019 |  |  | 90.1-2022 |  |  | Incremental Cost |  | 90.1-2019 |  |  | 90.1-2022 |  |  | Incremental Cost |  | 90.1-2019 |  |  | 90.1-2022 |  |  | Incremental Cost
Category | All Costs with First Replacement Only | With Repeated Replacements | Category | All Costs with First Replacement Only | With Repeated Replacements | 30 Year | 40 Year | Category | All Costs with First Replacement Only | With Repeated Replacements | Category | All Costs with First Replacement Only | With Repeated Replacements | 30 Year | 40 Year | Category | All Costs with First Replacement Only | With Repeated Replacements | Category | All Costs with First Replacement Only | With Repeated Replacements | 30 Year | 40 Year | Category | All Costs with First Replacement Only | With Repeated Replacements | Category | All Costs with First Replacement Only | With Repeated Replacements | 30 Year | 40 Year | Category | All Costs with First Replacement Only | With Repeated Replacements | Category | All Costs with First Replacement Only | With Repeated Replacements | 30 Year | 40 Year
New Construction | 77118.2774 | 77118.2774 | New Construction | 75962.4365 | 75962.4365 | -1155.8408 | -1155.8408 | New Construction | 75503.0638 | 75503.0638 | New Construction | 74229.4654 | 74229.4654 | -1273.5984 | -1273.5984 | New Construction | 77793.4773 | 77793.4773 | New Construction | 76595.5044 | 76595.5044 | -1197.9729 | -1197.9729 | New Construction | 74006.6306 | 74006.6306 | New Construction | 72414.9743 | 72414.9743 | -1591.6563 | -1591.6563 | New Construction | 72815.3592 | 72815.3592 | New Construction | 71735.937 | 71735.937 | -1079.4222 | -1079.4222
Maintenance | 0 | 0 | Maintenance | 0 | 0 | 0 | 0 | Maintenance | 0 | 0 | Maintenance | 0 | 0 | 0 | 0 | Maintenance | 0 | 0 | Maintenance | 0 | 0 | 0 | 0 | Maintenance | 0 | 0 | Maintenance | 0 | 0 | 0 | 0 | Maintenance | 0 | 0 | Maintenance | 0 | 0 | 0 | 0
Replacement - Year |  |  | Replacement - Year |  |  | 0 | 0 | Replacement - Year |  |  | Replacement - Year |  |  | 0 | 0 | Replacement - Year |  |  | Replacement - Year |  |  | 0 | 0 | Replacement - Year |  |  | Replacement - Year |  |  | 0 | 0 | Replacement - Year |  |  | Replacement - Year |  |  | 0 | 0
1 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 0
2 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 0 | 0
3 | 0 | 0 | 3 | 0 | 0 | 0 | 0 | 3 | 0 | 0 | 3 | 0 | 0 | 0 | 0 | 3 | 0 | 0 | 3 | 0 | 0 | 0 | 0 | 3 | 0 | 0 | 3 | 0 | 0 | 0 | 0 | 3 | 0 | 0 | 3 | 0 | 0 | 0 | 0
4 | 0 | 0 | 4 | 0 | 0 | 0 | 0 | 4 | 0 | 0 | 4 | 0 | 0 | 0 | 0 | 4 | 0 | 0 | 4 | 0 | 0 | 0 | 0 | 4 | 0 | 0 | 4 | 0 | 0 | 0 | 0 | 4 | 0 | 0 | 4 | 0 | 0 | 0 | 0
5 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 5 | 0 | 0 | 0 | 0
6 | 0 | 0 | 6 | 0 | 0 | 0 | 0 | 6 | 0 | 0 | 6 | 0 | 0 | 0 | 0 | 6 | 0 | 0 | 6 | 0 | 0 | 0 | 0 | 6 | 0 | 0 | 6 | 0 | 0 | 0 | 0 | 6 | 0 | 0 | 6 | 0 | 0 | 0 | 0
7 | 0 | 0 | 7 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 7 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 7 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 7 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 7 | 0 | 0 | 0 | 0
8 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 8 | 0 | 0 | 0 | 0
9 | 0 | 0 | 9 | 0 | 0 | 0 | 0 | 9 | 0 | 0 | 9 | 0 | 0 | 0 | 0 | 9 | 0 | 0 | 9 | 0 | 0 | 0 | 0 | 9 | 0 | 0 | 9 | 0 | 0 | 0 | 0 | 9 | 0 | 0 | 9 | 0 | 0 | 0 | 0
10 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 10 | 0 | 0 | 0 | 0
11 | 0 | 0 | 11 | 0 | 0 | 0 | 0 | 11 | 0 | 0 | 11 | 0 | 0 | 0 | 0 | 11 | 0 | 0 | 11 | 0 | 0 | 0 | 0 | 11 | 0 | 0 | 11 | 0 | 0 | 0 | 0 | 11 | 0 | 0 | 11 | 0 | 0 | 0 | 0
12 | 0 | 0 | 12 | 0 | 0 | 0 | 0 | 12 | 0 | 0 | 12 | 0 | 0 | 0 | 0 | 12 | 0 | 0 | 12 | 0 | 0 | 0 | 0 | 12 | 0 | 0 | 12 | 0 | 0 | 0 | 0 | 12 | 0 | 0 | 12 | 0 | 0 | 0 | 0
13 | 0 | 0 | 13 | 0 | 0 | 0 | 0 | 13 | 0 | 0 | 13 | 0 | 0 | 0 | 0 | 13 | 0 | 0 | 13 | 0 | 0 | 0 | 0 | 13 | 0 | 0 | 13 | 0 | 0 | 0 | 0 | 13 | 0 | 0 | 13 | 0 | 0 | 0 | 0
14 | 0 | 0 | 14 | 0 | 0 | 0 | 0 | 14 | 0 | 0 | 14 | 0 | 0 | 0 | 0 | 14 | 0 | 0 | 14 | 0 | 0 | 0 | 0 | 14 | 0 | 0 | 14 | 0 | 0 | 0 | 0 | 14 | 0 | 0 | 14 | 0 | 0 | 0 | 0
15 | 30888.199 | 30888.199 | 15 | 30119.4732 | 30119.4732 | -768.7257 | -768.7257 | 15 | 29449.0928 | 29449.0928 | 15 | 28784.8774 | 28784.8774 | -664.2154 | -664.2154 | 15 | 29126.6838 | 29126.6838 | 15 | 28430.4904 | 28430.4904 | -696.1934 | -696.1934 | 15 | 28518.9733 | 28518.9733 | 15 | 27719.667 | 27719.667 | -799.3063 | -799.3063 | 15 | 27464.1151 | 27464.1151 | 15 | 27031.6062 | 27031.6062 | -432.5089 | -432.5089
16 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 16 | 0 | 0 | 0 | 0
17 | 0 | 0 | 17 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 17 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 17 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 17 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 17 | 0 | 0 | 0 | 0
18 | 0 | 0 | 18 | 0 | 0 | 0 | 0 | 18 | 0 | 0 | 18 | 0 | 0 | 0 | 0 | 18 | 0 | 0 | 18 | 0 | 0 | 0 | 0 | 18 | 0 | 0 | 18 | 0 | 0 | 0 | 0 | 18 | 0 | 0 | 18 | 0 | 0 | 0 | 0
19 | 0 | 0 | 19 | 0 | 0 | 0 | 0 | 19 | 0 | 0 | 19 | 0 | 0 | 0 | 0 | 19 | 0 | 0 | 19 | 0 | 0 | 0 | 0 | 19 | 0 | 0 | 19 | 0 | 0 | 0 | 0 | 19 | 0 | 0 | 19 | 0 | 0 | 0 | 0
20 | 0 | 0 | 20 | 0 | 0 | 0 | 0 | 20 | 0 | 0 | 20 | 0 | 0 | 0 | 0 | 20 | 0 | 0 | 20 | 0 | 0 | 0 | 0 | 20 | 0 | 0 | 20 | 0 | 0 | 0 | 0 | 20 | 0 | 0 | 20 | 0 | 0 | 0 | 0
21 | 0 | 0 | 21 | 0 | 0 | 0 | 0 | 21 | 0 | 0 | 21 | 0 | 0 | 0 | 0 | 21 | 0 | 0 | 21 | 0 | 0 | 0 | 0 | 21 | 0 | 0 | 21 | 0 | 0 | 0 | 0 | 21 | 0 | 0 | 21 | 0 | 0 | 0 | 0
22 | 0 | 0 | 22 | 0 | 0 | 0 | 0 | 22 | 0 | 0 | 22 | 0 | 0 | 0 | 0 | 22 | 0 | 0 | 22 | 0 | 0 | 0 | 0 | 22 | 0 | 0 | 22 | 0 | 0 | 0 | 0 | 22 | 0 | 0 | 22 | 0 | 0 | 0 | 0
23 | 0 | 0 | 23 | 0 | 0 | 0 | 0 | 23 | 0 | 0 | 23 | 0 | 0 | 0 | 0 | 23 | 0 | 0 | 23 | 0 | 0 | 0 | 0 | 23 | 0 | 0 | 23 | 0 | 0 | 0 | 0 | 23 | 0 | 0 | 23 | 0 | 0 | 0 | 0
24 | 0 | 0 | 24 | 0 | 0 | 0 | 0 | 24 | 0 | 0 | 24 | 0 | 0 | 0 | 0 | 24 | 0 | 0 | 24 | 0 | 0 | 0 | 0 | 24 | 0 | 0 | 24 | 0 | 0 | 0 | 0 | 24 | 0 | 0 | 24 | 0 | 0 | 0 | 0
25 | 0 | 0 | 25 | 0 | 0 | 0 | 0 | 25 | 0 | 0 | 25 | 0 | 0 | 0 | 0 | 25 | 0 | 0 | 25 | 0 | 0 | 0 | 0 | 25 | 0 | 0 | 25 | 0 | 0 | 0 | 0 | 25 | 0 | 0 | 25 | 0 | 0 | 0 | 0
26 | 0 | 0 | 26 | 0 | 0 | 0 | 0 | 26 | 0 | 0 | 26 | 0 | 0 | 0 | 0 | 26 | 0 | 0 | 26 | 0 | 0 | 0 | 0 | 26 | 0 | 0 | 26 | 0 | 0 | 0 | 0 | 26 | 0 | 0 | 26 | 0 | 0 | 0 | 0
27 | 0 | 0 | 27 | 0 | 0 | 0 | 0 | 27 | 0 | 0 | 27 | 0 | 0 | 0 | 0 | 27 | 0 | 0 | 27 | 0 | 0 | 0 | 0 | 27 | 0 | 0 | 27 | 0 | 0 | 0 | 0 | 27 | 0 | 0 | 27 | 0 | 0 | 0 | 0
28 | 0 | 0 | 28 | 0 | 0 | 0 | 0 | 28 | 0 | 0 | 28 | 0 | 0 | 0 | 0 | 28 | 0 | 0 | 28 | 0 | 0 | 0 | 0 | 28 | 0 | 0 | 28 | 0 | 0 | 0 | 0 | 28 | 0 | 0 | 28 | 0 | 0 | 0 | 0
29 | 0 | 0 | 29 | 0 | 0 | 0 | 0 | 29 | 0 | 0 | 29 | 0 | 0 | 0 | 0 | 29 | 0 | 0 | 29 | 0 | 0 | 0 | 0 | 29 | 0 | 0 | 29 | 0 | 0 | 0 | 0 | 29 | 0 | 0 | 29 | 0 | 0 | 0 | 0
30 | 82845.7908 | 113733.9897 | 30 | 81993.54 | 112113.0132 | 0 | -1620.9765 | 30 | 82163.9901 | 111613.0829 | 30 | 80970.839 | 109755.7164 | 0 | -1857.3665 | 30 | 86425.2441 | 115551.928 | 30 | 85402.5432 | 113833.0336 | 0 | -1718.8944 | 30 | 80970.839 | 109489.8123 | 30 | 79436.7876 | 107156.4545 | 0 | -2333.3577 | 30 | 80459.4885 | 107923.6036 | 30 | 79266.3374 | 106297.9436 | 0 | -1625.6601
31 | 0 | 0 | 31 | 0 | 0 |  | 0 | 31 | 0 | 0 | 31 | 0 | 0 |  | 0 | 31 | 0 | 0 | 31 | 0 | 0 |  | 0 | 31 | 0 | 0 | 31 | 0 | 0 |  | 0 | 31 | 0 | 0 | 31 | 0 | 0 |  | 0
32 | 0 | 0 | 32 | 0 | 0 |  | 0 | 32 | 0 | 0 | 32 | 0 | 0 |  | 0 | 32 | 0 | 0 | 32 | 0 | 0 |  | 0 | 32 | 0 | 0 | 32 | 0 | 0 |  | 0 | 32 | 0 | 0 | 32 | 0 | 0 |  | 0
33 | 0 | 0 | 33 | 0 | 0 |  | 0 | 33 | 0 | 0 | 33 | 0 | 0 |  | 0 | 33 | 0 | 0 | 33 | 0 | 0 |  | 0 | 33 | 0 | 0 | 33 | 0 | 0 |  | 0 | 33 | 0 | 0 | 33 | 0 | 0 |  | 0
34 | 0 | 0 | 34 | 0 | 0 |  | 0 | 34 | 0 | 0 | 34 | 0 | 0 |  | 0 | 34 | 0 | 0 | 34 | 0 | 0 |  | 0 | 34 | 0 | 0 | 34 | 0 | 0 |  | 0 | 34 | 0 | 0 | 34 | 0 | 0 |  | 0
35 | 0 | 0 | 35 | 0 | 0 |  | 0 | 35 | 0 | 0 | 35 | 0 | 0 |  | 0 | 35 | 0 | 0 | 35 | 0 | 0 |  | 0 | 35 | 0 | 0 | 35 | 0 | 0 |  | 0 | 35 | 0 | 0 | 35 | 0 | 0 |  | 0
36 | 0 | 0 | 36 | 0 | 0 |  | 0 | 36 | 0 | 0 | 36 | 0 | 0 |  | 0 | 36 | 0 | 0 | 36 | 0 | 0 |  | 0 | 36 | 0 | 0 | 36 | 0 | 0 |  | 0 | 36 | 0 | 0 | 36 | 0 | 0 |  | 0
37 | 0 | 0 | 37 | 0 | 0 |  | 0 | 37 | 0 | 0 | 37 | 0 | 0 |  | 0 | 37 | 0 | 0 | 37 | 0 | 0 |  | 0 | 37 | 0 | 0 | 37 | 0 | 0 |  | 0 | 37 | 0 | 0 | 37 | 0 | 0 |  | 0
38 | 0 | 0 | 38 | 0 | 0 |  | 0 | 38 | 0 | 0 | 38 | 0 | 0 |  | 0 | 38 | 0 | 0 | 38 | 0 | 0 |  | 0 | 38 | 0 | 0 | 38 | 0 | 0 |  | 0 | 38 | 0 | 0 | 38 | 0 | 0 |  | 0
39 | 0 | 0 | 39 | 0 | 0 |  | 0 | 39 | 0 | 0 | 39 | 0 | 0 |  | 0 | 39 | 0 | 0 | 39 | 0 | 0 |  | 0 | 39 | 0 | 0 | 39 | 0 | 0 |  | 0 | 39 | 0 | 0 | 39 | 0 | 0 |  | 0
40 | 0 | 0 | 40 | 0 | 0 |  | 824.4091 | 40 | 0 | 0 | 40 | 0 | 0 |  | 1016.8392 | 40 | 0 | 0 | 40 | 0 | 0 |  | 913.8651 | 40 | 0 | 0 | 40 | 0 | 0 |  | 1289.1364 | 40 | 0 | 0 | 40 | 0 | 0 |  | 939.6037
Residual Year 30 |  | 0 | Residual Year 30 |  | 0 |  |  | Residual Year 30 |  | 0 | Residual Year 30 |  | 0 |  |  | Residual Year 30 |  | 0 | Residual Year 30 |  | 0 |  |  | Residual Year 30 |  | 0 | Residual Year 30 |  | 0 |  |  | Residual Year 30 |  | 0 | Residual Year 30 |  | 0
Residual Year 40 |  | -65526.5935 | Residual Year 40 |  | -64702.1844 |  |  | Residual Year 40 |  | -64592.3577 | Residual Year 40 |  | -63575.5185 |  |  | Residual Year 40 |  | -67325.724 | Residual Year 40 |  | -66411.8589 |  |  | Residual Year 40 |  | -63486.8838 | Residual Year 40 |  | -62197.7474 |  |  | Residual Year 40 |  | -62794.3641 | Residual Year 40 |  | -61854.7603
Large Office | Climate Zone 1 | 2A | [5 empty] | Large Office | Climate Zone 2 | 3A | [5 empty] | Large Office | Climate Zone 3 | 3B | [5 empty] | Large Office | Climate Zone 4 | 4A | [5 empty] | Large Office | Climate Zone 5 | 5A
90.1-2019 |  |  | 90.1-2022 |  |  | Incremental Cost |  | 90.1-2019 |  |  | 90.1-2022 |  |  | Incremental Cost |  | 90.1-2019 |  |  | 90.1-2022 |  |  | Incremental Cost |  | 90.1-2019 |  |  | 90.1-2022 |  |  | Incremental Cost |  | 90.1-2019 |  |  | 90.1-2022 |  |  | Incremental Cost
Category | All Costs with First Replacement Only | With Repeated Replacements | Category | All Costs with First Replacement Only | With Repeated Replacements | 30 Year | 40 Year | Category | All Costs with First Replacement Only | With Repeated Replacements | Category | All Costs with First Replacement Only | With Repeated Replacements | 30 Year | 40 Year | Category | All Costs with First Replacement Only | With Repeated Replacements | Category | All Costs with First Replacement Only | With Repeated Replacements | 30 Year | 40 Year | Category | All Costs with First Replacement Only | With Repeated Replacements | Category | All Costs with First Replacement Only | With Repeated Replacements | 30 Year | 40 Year | Category | All Costs with First Replacement Only | With Repeated Replacements | Category | All Costs with First Replacement Only | With Repeated Replacements | 30 Year | 40 Year
New Construction | 9305380.4274 | 9305380.4274 | New Construction | 9546065.4436 | 9546065.4436 | 240685.0162 | 240685.0162 | New Construction | 9815301.2057 | 9815301.2057 | New Construction | 9781098.999 | 9781098.999 | -34202.2068 | -34202.2068 | New Construction | 9502360.5661 | 9502360.5661 | New Construction | 9454382.0994 | 9454382.0994 | -47978.4667 | -47978.4667 | New Construction | 9962968.0842 | 9962968.0842 | New Construction | 9923520.8572 | 9923520.8572 | -39447.227 | -39447.227 | New Construction | 9951319.3717 | 9951319.3717 | New Construction | 9907369.0576 | 9907369.0576 | -43950.3141 | -43950.3141
Maintenance | 3060.99 | 3060.99 | Maintenance | 3460.99 | 3460.99 | 400 | 400 | Maintenance | 3060.99 | 3060.99 | Maintenance | 3460.99 | 3460.99 | 400 | 400 | Maintenance | 0 | 0 | Maintenance | 400 | 400 | 400 | 400 | Maintenance | 3060.99 | 3060.99 | Maintenance | 3460.99 | 3460.99 | 400 | 400 | Maintenance | 3060.99 | 3060.99 | Maintenance | 3460.99 | 3460.99 | 400 | 400
Replacement - Year |  |  | Replacement - Year |  |  | 0 |  | Replacement - Year |  |  | Replacement - Year |  |  | 0 | 0 | Replacement - Year |  |  | Replacement - Year |  |  | 0 | 0 | Replacement - Year |  |  | Replacement - Year |  |  | 0 | 0 | Replacement - Year |  |  | Replacement - Year |  |  | 0 | 0
1 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 0
2 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 0 | 0
3 | 0 | 0 | 3 | 0 | 0 | 0 | 0 | 3 | 0 | 0 | 3 | 0 | 0 | 0 | 0 | 3 | 0 | 0 | 3 | 0 | 0 | 0 | 0 | 3 | 0 | 0 | 3 | 0 | 0 | 0 | 0 | 3 | 0 | 0 | 3 | 0 | 0 | 0 | 0
4 | 0 | 0 | 4 | 0 | 0 | 0 | 0 | 4 | 0 | 0 | 4 | 0 | 0 | 0 | 0 | 4 | 0 | 0 | 4 | 0 | 0 | 0 | 0 | 4 | 0 | 0 | 4 | 0 | 0 | 0 | 0 | 4 | 0 | 0 | 4 | 0 | 0 | 0 | 0
5 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 5 | 0 | 0 | 0 | 0
6 | 0 | 0 | 6 | 0 | 0 | 0 | 0 | 6 | 0 | 0 | 6 | 0 | 0 | 0 | 0 | 6 | 0 | 0 | 6 | 0 | 0 | 0 | 0 | 6 | 0 | 0 | 6 | 0 | 0 | 0 | 0 | 6 | 0 | 0 | 6 | 0 | 0 | 0 | 0
7 | 0 | 0 | 7 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 7 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 7 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 7 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 7 | 0 | 0 | 0 | 0
8 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 8 | 0 | 0 | 0 | 0
9 | 0 | 0 | 9 | 0 | 0 | 0 | 0 | 9 | 0 | 0 | 9 | 0 | 0 | 0 | 0 | 9 | 0 | 0 | 9 | 0 | 0 | 0 | 0 | 9 | 0 | 0 | 9 | 0 | 0 | 0 | 0 | 9 | 0 | 0 | 9 | 0 | 0 | 0 | 0
10 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 10 | 0 | 0 | 0 | 0
11 | 0 | 0 | 11 | 0 | 0 | 0 | 0 | 11 | 0 | 0 | 11 | 0 | 0 | 0 | 0 | 11 | 0 | 0 | 11 | 0 | 0 | 0 | 0 | 11 | 0 | 0 | 11 | 0 | 0 | 0 | 0 | 11 | 0 | 0 | 11 | 0 | 0 | 0 | 0
12 | 0 | 0 | 12 | 0 | 0 | 0 | 0 | 12 | 0 | 0 | 12 | 0 | 0 | 0 | 0 | 12 | 0 | 0 | 12 | 0 | 0 | 0 | 0 | 12 | 0 | 0 | 12 | 0 | 0 | 0 | 0 | 12 | 0 | 0 | 12 | 0 | 0 | 0 | 0
13 | 0 | 0 | 13 | 0 | 0 | 0 | 0 | 13 | 0 | 0 | 13 | 0 | 0 | 0 | 0 | 13 | 0 | 0 | 13 | 0 | 0 | 0 | 0 | 13 | 0 | 0 | 13 | 0 | 0 | 0 | 0 | 13 | 0 | 0 | 13 | 0 | 0 | 0 | 0
14 | 0 | 0 | 14 | 0 | 0 | 0 | 0 | 14 | 0 | 0 | 14 | 0 | 0 | 0 | 0 | 14 | 0 | 0 | 14 | 0 | 0 | 0 | 0 | 14 | 0 | 0 | 14 | 0 | 0 | 0 | 0 | 14 | 0 | 0 | 14 | 0 | 0 | 0 | 0
15 | 1228029.0721 | 1228029.0721 | 15 | 1216216.7785 | 1216216.7785 | -11812.2936 | -11812.2936 | 15 | 1240061.9545 | 1240061.9545 | 15 | 1227710.7012 | 1227710.7012 | -12351.2534 | -12351.2534 | 15 | 860944.6465 | 860944.6465 | 15 | 842571.1863 | 842571.1863 | -18373.4602 | -18373.4602 | 15 | 1252083.3809 | 1252083.3809 | 15 | 1245170.9594 | 1245170.9594 | -6912.4215 | -6912.4215 | 15 | 1251268.2211 | 1251268.2211 | 15 | 1247516.5581 | 1247516.5581 | -3751.663 | -3751.663
16 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 16 | 0 | 0 | 0 | 0
17 | 0 | 0 | 17 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 17 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 17 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 17 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 17 | 0 | 0 | 0 | 0
18 | 0 | 0 | 18 | 0 | 0 | 0 | 0 | 18 | 0 | 0 | 18 | 0 | 0 | 0 | 0 | 18 | 0 | 0 | 18 | 0 | 0 | 0 | 0 | 18 | 0 | 0 | 18 | 0 | 0 | 0 | 0 | 18 | 0 | 0 | 18 | 0 | 0 | 0 | 0
19 | 0 | 0 | 19 | 0 | 0 | 0 | 0 | 19 | 0 | 0 | 19 | 0 | 0 | 0 | 0 | 19 | 0 | 0 | 19 | 0 | 0 | 0 | 0 | 19 | 0 | 0 | 19 | 0 | 0 | 0 | 0 | 19 | 0 | 0 | 19 | 0 | 0 | 0 | 0
20 | 497292.2713 | 497292.2713 | 20 | 814734.8554 | 814734.8554 | 317442.5841 | 317442.5841 | 20 | 801131.6849 | 801131.6849 | 20 | 788924.4855 | 788924.4855 | -12207.1994 | -12207.1994 | 20 | 719159.9261 | 719159.9261 | 20 | 707362.1174 | 707362.1174 | -11797.8086 | -11797.8086 | 20 | 808315.5668 | 808315.5668 | 20 | 795264.0386 | 795264.0386 | -13051.5282 | -13051.5282 | 20 | 770497.0656 | 770497.0656 | 20 | 757279.2824 | 757279.2824 | -13217.7833 | -13217.7833
21 | 0 | 0 | 21 | 0 | 0 | 0 | 0 | 21 | 0 | 0 | 21 | 0 | 0 | 0 | 0 | 21 | 0 | 0 | 21 | 0 | 0 | 0 | 0 | 21 | 0 | 0 | 21 | 0 | 0 | 0 | 0 | 21 | 0 | 0 | 21 | 0 | 0 | 0 | 0
22 | 0 | 0 | 22 | 0 | 0 | 0 | 0 | 22 | 0 | 0 | 22 | 0 | 0 | 0 | 0 | 22 | 0 | 0 | 22 | 0 | 0 | 0 | 0 | 22 | 0 | 0 | 22 | 0 | 0 | 0 | 0 | 22 | 0 | 0 | 22 | 0 | 0 | 0 | 0
23 | 621477.4115 | 621477.4115 | 23 | 620181.2263 | 620181.2263 | -1296.1852 | -1296.1852 | 23 | 617291.5533 | 617291.5533 | 23 | 615991.8302 | 615991.8302 | -1299.723 | -1299.723 | 23 | 608183.0767 | 608183.0767 | 23 | 606887.1665 | 606887.1665 | -1295.9102 | -1295.9102 | 23 | 617834.5771 | 617834.5771 | 23 | 616463.2445 | 616463.2445 | -1371.3326 | -1371.3326 | 23 | 613274.2097 | 613274.2097 | 23 | 611918.7978 | 611918.7978 | -1355.4119 | -1355.4119
24 | 0 | 0 | 24 | 0 | 0 | 0 | 0 | 24 | 0 | 0 | 24 | 0 | 0 | 0 | 0 | 24 | 0 | 0 | 24 | 0 | 0 | 0 | 0 | 24 | 0 | 0 | 24 | 0 | 0 | 0 | 0 | 24 | 0 | 0 | 24 | 0 | 0 | 0 | 0
25 | 0 | 0 | 25 | 0 | 0 | 0 | 0 | 25 | 0 | 0 | 25 | 0 | 0 | 0 | 0 | 25 | 0 | 0 | 25 | 0 | 0 | 0 | 0 | 25 | 0 | 0 | 25 | 0 | 0 | 0 | 0 | 25 | 0 | 0 | 25 | 0 | 0 | 0 | 0
26 | 0 | 0 | 26 | 0 | 0 | 0 | 0 | 26 | 0 | 0 | 26 | 0 | 0 | 0 | 0 | 26 | 0 | 0 | 26 | 0 | 0 | 0 | 0 | 26 | 0 | 0 | 26 | 0 | 0 | 0 | 0 | 26 | 0 | 0 | 26 | 0 | 0 | 0 | 0
27 | 0 | 0 | 27 | 0 | 0 | 0 | 0 | 27 | 0 | 0 | 27 | 0 | 0 | 0 | 0 | 27 | 0 | 0 | 27 | 0 | 0 | 0 | 0 | 27 | 0 | 0 | 27 | 0 | 0 | 0 | 0 | 27 | 0 | 0 | 27 | 0 | 0 | 0 | 0
28 | 0 | 0 | 28 | 0 | 0 | 0 | 0 | 28 | 0 | 0 | 28 | 0 | 0 | 0 | 0 | 28 | 0 | 0 | 28 | 0 | 0 | 0 | 0 | 28 | 0 | 0 | 28 | 0 | 0 | 0 | 0 | 28 | 0 | 0 | 28 | 0 | 0 | 0 | 0
29 | 0 | 0 | 29 | 0 | 0 | 0 | 0 | 29 | 0 | 0 | 29 | 0 | 0 | 0 | 0 | 29 | 0 | 0 | 29 | 0 | 0 | 0 | 0 | 29 | 0 | 0 | 29 | 0 | 0 | 0 | 0 | 29 | 0 | 0 | 29 | 0 | 0 | 0 | 0
30 | 11760049.207 | 12988078.279 | 30 | 11690839.9375 | 12907056.7159 | -162731.0499 | -81021.5631 | 30 | 11997464.5612 | 13237526.5158 | 30 | 11925297.5056 | 13153008.2068 | -560.0737 | -84518.309 | 30 | 12241801.3421 | 13102745.9886 | 30 | 12101871.5431 | 12944442.7294 | 347.9293 | -158303.2592 | 30 | 12088305.4861 | 13340388.867 | 30 | 12001583.0937 | 13246754.0532 | -705.6181 | -93634.8139 | 30 | 12087649.3613 | 13338917.5824 | 30 | 11993051.1635 | 13240567.7216 | -747.2902 | -98349.8608
31 | 0 | 0 | 31 | 0 | 0 |  | 0 | 31 | 0 | 0 | 31 | 0 | 0 |  | 0 | 31 | 0 | 0 | 31 | 0 | 0 |  | 0 | 31 | 0 | 0 | 31 | 0 | 0 |  | 0 | 31 | 0 | 0 | 31 | 0 | 0 |  | 0
32 | 0 | 0 | 32 | 0 | 0 |  | 0 | 32 | 0 | 0 | 32 | 0 | 0 |  | 0 | 32 | 0 | 0 | 32 | 0 | 0 |  | 0 | 32 | 0 | 0 | 32 | 0 | 0 |  | 0 | 32 | 0 | 0 | 32 | 0 | 0 |  | 0
33 | 0 | 0 | 33 | 0 | 0 |  | 0 | 33 | 0 | 0 | 33 | 0 | 0 |  | 0 | 33 | 0 | 0 | 33 | 0 | 0 |  | 0 | 33 | 0 | 0 | 33 | 0 | 0 |  | 0 | 33 | 0 | 0 | 33 | 0 | 0 |  | 0
34 | 0 | 0 | 34 | 0 | 0 |  | 0 | 34 | 0 | 0 | 34 | 0 | 0 |  | 0 | 34 | 0 | 0 | 34 | 0 | 0 |  | 0 | 34 | 0 | 0 | 34 | 0 | 0 |  | 0 | 34 | 0 | 0 | 34 | 0 | 0 |  | 0
35 | 140778.7406 | 140778.7406 | 35 | 140505.4858 | 140505.4858 |  | -273.2549 | 35 | 211793.7439 | 211793.7439 | 35 | 211400.7533 | 211400.7533 |  | -392.9906 | 35 | 182251.8486 | 182251.8486 | 35 | 181851.5636 | 181851.5636 |  | -400.285 | 35 | 253053.5109 | 253053.5109 | 35 | 249231.307 | 249231.307 |  | -3822.2039 | 35 | 275956.0683 | 275956.0683 | 35 | 268944.7144 | 268944.7144 |  | -7011.3539
36 | 0 | 0 | 36 | 0 | 0 |  | 0 | 36 | 0 | 0 | 36 | 0 | 0 |  | 0 | 36 | 0 | 0 | 36 | 0 | 0 |  | 0 | 36 | 0 | 0 | 36 | 0 | 0 |  | 0 | 36 | 0 | 0 | 36 | 0 | 0 |  | 0
37 | 0 | 0 | 37 | 0 | 0 |  | 0 | 37 | 0 | 0 | 37 | 0 | 0 |  | 0 | 37 | 0 | 0 | 37 | 0 | 0 |  | 0 | 37 | 0 | 0 | 37 | 0 | 0 |  | 0 | 37 | 0 | 0 | 37 | 0 | 0 |  | 0
38 | 0 | 0 | 38 | 0 | 0 |  | 0 | 38 | 0 | 0 | 38 | 0 | 0 |  | 0 | 38 | 0 | 0 | 38 | 0 | 0 |  | 0 | 38 | 0 | 0 | 38 | 0 | 0 |  | 0 | 38 | 0 | 0 | 38 | 0 | 0 |  | 0
39 | 0 | 0 | 39 | 0 | 0 |  | 0 | 39 | 0 | 0 | 39 | 0 | 0 |  | 0 | 39 | 0 | 0 | 39 | 0 | 0 |  | 0 | 39 | 0 | 0 | 39 | 0 | 0 |  | 0 | 39 | 0 | 0 | 39 | 0 | 0 |  | 0
40 | 0 | 0 | 40 | 19801.9533 | 0 |  | 50649.2979 | 40 | 0 | 0 | 40 | 30495.8804 | 0 |  | 52904.3621 | 40 | 0 | 0 | 40 | 26038.6452 | 0 |  | 100092.1844 | 40 | 0 | 0 | 40 | 34925.5272 | 0 |  | 63752.9825 | 40 | 0 | 0 | 40 | 37202.7962 | 0 |  | 70679.3371
Residual Year 30 |  | -701089.4966 | Residual Year 30 |  | -863820.5465 |  |  | Residual Year 30 |  | -860242.3026 | Residual Year 30 |  | -860802.3763 |  |  | Residual Year 30 |  | -808699.8209 | Residual Year 30 |  | -808351.8915 |  |  | Residual Year 30 |  | -870106.2516 | Residual Year 30 |  | -870811.8697 |  |  | Residual Year 30 |  | -851296.3655 | Residual Year 30 |  | -852043.6557
Residual Year 40 |  | -8532167.8628 | Residual Year 40 |  | -8481518.5648 |  |  | Residual Year 40 |  | -8754233.7662 | Residual Year 40 |  | -8701329.4041 |  |  | Residual Year 40 |  | -8763054.7686 | Residual Year 40 |  | -8662962.5842 |  |  | Residual Year 40 |  | -8854308.6979 | Residual Year 40 |  | -8790555.7154 |  |  | Residual Year 40 |  | -8872040.6639 | Residual Year 40 |  | -8801361.3267
Standalone Retail | Climate Zone 1 | 2A | [5 empty] | Standalone Retail | Climate Zone 2 | 3A | [5 empty] | Standalone Retail | Climate Zone 3 | 3B | [5 empty] | Standalone Retail | Climate Zone 4 | 4A | [5 empty] | Standalone Retail | Climate Zone 5 | 5A
90.1-2019 |  |  | 90.1-2022 |  |  | Incremental Cost |  | 90.1-2019 |  |  | 90.1-2022 |  |  | Incremental Cost |  | 90.1-2019 |  |  | 90.1-2022 |  |  | Incremental Cost |  | 90.1-2019 |  |  | 90.1-2022 |  |  | Incremental Cost |  | 90.1-2019 |  |  | 90.1-2022 |  |  | Incremental Cost
Category | All Costs with First Replacement Only | With Repeated Replacements | Category | All Costs with First Replacement Only | With Repeated Replacements | 30 Year | 40 Year | Category | All Costs with First Replacement Only | With Repeated Replacements | Category | All Costs with First Replacement Only | With Repeated Replacements | 30 Year | 40 Year | Category | All Costs with First Replacement Only | With Repeated Replacements | Category | All Costs with First Replacement Only | With Repeated Replacements | 30 Year | 40 Year | Category | All Costs with First Replacement Only | With Repeated Replacements | Category | All Costs with First Replacement Only | With Repeated Replacements | 30 Year | 40 Year | Category | All Costs with First Replacement Only | With Repeated Replacements | Category | All Costs with First Replacement Only | With Repeated Replacements | 30 Year | 40 Year
New Construction | 338535.3781 | 338535.3781 | New Construction | 332203.5098 | 332203.5098 | -6331.8683 | -6331.8683 | New Construction | 335875.0677 | 335875.0677 | New Construction | 331290.4259 | 331290.4259 | -4584.6419 | -4584.6419 | New Construction | 351249.032 | 351249.032 | New Construction | 345788.6988 | 345788.6988 | -5460.3332 | -5460.3332 | New Construction | 336688.4194 | 336688.4194 | New Construction | 329740.7596 | 329740.7596 | -6947.6598 | -6947.6598 | New Construction | 334857.3566 | 334857.3566 | New Construction | 324452.9707 | 324452.9707 | -10404.3859 | -10404.3859
Maintenance | 0 | 0 | Maintenance | 0 | 0 | 0 | 0 | Maintenance | 0 | 0 | Maintenance | 134.8431 | 134.8431 | 134.8431 | 134.8431 | Maintenance | 0 | 0 | Maintenance | 134.8431 | 134.8431 | 134.8431 | 134.8431 | Maintenance | 0 | 0 | Maintenance | 134.8431 | 134.8431 | 134.8431 | 134.8431 | Maintenance | 0 | 0 | Maintenance | 134.8431 | 134.8431 | 134.8431 | 134.8431
Replacement - Year |  |  | Replacement - Year |  |  | 0 | 0 | Replacement - Year |  |  | Replacement - Year |  |  | 0 | 0 | Replacement - Year |  |  | Replacement - Year |  |  | 0 | 0 | Replacement - Year |  |  | Replacement - Year |  |  | 0 | 0 | Replacement - Year |  |  | Replacement - Year |  |  | 0 | 0
1 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 0
2 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 0 | 0
3 | 0 | 0 | 3 | 0 | 0 | 0 | 0 | 3 | 0 | 0 | 3 | 0 | 0 | 0 | 0 | 3 | 0 | 0 | 3 | 0 | 0 | 0 | 0 | 3 | 0 | 0 | 3 | 0 | 0 | 0 | 0 | 3 | 0 | 0 | 3 | 0 | 0 | 0 | 0
4 | 0 | 0 | 4 | 0 | 0 | 0 | 0 | 4 | 0 | 0 | 4 | 0 | 0 | 0 | 0 | 4 | 0 | 0 | 4 | 0 | 0 | 0 | 0 | 4 | 0 | 0 | 4 | 0 | 0 | 0 | 0 | 4 | 0 | 0 | 4 | 0 | 0 | 0 | 0
5 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 5 | 0 | 0 | 0 | 0
6 | 0 | 0 | 6 | 0 | 0 | 0 | 0 | 6 | 0 | 0 | 6 | 0 | 0 | 0 | 0 | 6 | 0 | 0 | 6 | 0 | 0 | 0 | 0 | 6 | 0 | 0 | 6 | 0 | 0 | 0 | 0 | 6 | 0 | 0 | 6 | 0 | 0 | 0 | 0
7 | 0 | 0 | 7 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 7 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 7 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 7 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 7 | 0 | 0 | 0 | 0
8 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 8 | 0 | 0 | 0 | 0
9 | 0 | 0 | 9 | 0 | 0 | 0 | 0 | 9 | 0 | 0 | 9 | 0 | 0 | 0 | 0 | 9 | 0 | 0 | 9 | 0 | 0 | 0 | 0 | 9 | 0 | 0 | 9 | 0 | 0 | 0 | 0 | 9 | 0 | 0 | 9 | 0 | 0 | 0 | 0
10 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 10 | 0 | 0 | 0 | 0
11 | 0 | 0 | 11 | 0 | 0 | 0 | 0 | 11 | 0 | 0 | 11 | 0 | 0 | 0 | 0 | 11 | 0 | 0 | 11 | 0 | 0 | 0 | 0 | 11 | 0 | 0 | 11 | 0 | 0 | 0 | 0 | 11 | 0 | 0 | 11 | 0 | 0 | 0 | 0
12 | 0 | 0 | 12 | 0 | 0 | 0 | 0 | 12 | 0 | 0 | 12 | 0 | 0 | 0 | 0 | 12 | 0 | 0 | 12 | 0 | 0 | 0 | 0 | 12 | 0 | 0 | 12 | 0 | 0 | 0 | 0 | 12 | 0 | 0 | 12 | 0 | 0 | 0 | 0
13 | 0 | 0 | 13 | 0 | 0 | 0 | 0 | 13 | 0 | 0 | 13 | 0 | 0 | 0 | 0 | 13 | 0 | 0 | 13 | 0 | 0 | 0 | 0 | 13 | 0 | 0 | 13 | 0 | 0 | 0 | 0 | 13 | 0 | 0 | 13 | 0 | 0 | 0 | 0
14 | 0 | 0 | 14 | 0 | 0 | 0 | 0 | 14 | 0 | 0 | 14 | 0 | 0 | 0 | 0 | 14 | 0 | 0 | 14 | 0 | 0 | 0 | 0 | 14 | 0 | 0 | 14 | 0 | 0 | 0 | 0 | 14 | 0 | 0 | 14 | 0 | 0 | 0 | 0
15 | 77373.491 | 77373.491 | 15 | 76313.8896 | 76313.8896 | -1059.6015 | -1059.6015 | 15 | 74536.8399 | 74536.8399 | 15 | 75806.3775 | 75806.3775 | 1269.5377 | 1269.5377 | 15 | 75169.1808 | 75169.1808 | 15 | 76159.7569 | 76159.7569 | 990.576 | 990.576 | 15 | 74381.5858 | 74381.5858 | 15 | 74730.9285 | 74730.9285 | 349.3426 | 349.3426 | 15 | 72620.7305 | 72620.7305 | 15 | 72162.3969 | 72162.3969 | -458.3335 | -458.3335
16 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 16 | 0 | 0 | 0 | 0
17 | 0 | 0 | 17 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 17 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 17 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 17 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 17 | 0 | 0 | 0 | 0
18 | 0 | 0 | 18 | 0 | 0 | 0 | 0 | 18 | 0 | 0 | 18 | 0 | 0 | 0 | 0 | 18 | 0 | 0 | 18 | 0 | 0 | 0 | 0 | 18 | 0 | 0 | 18 | 0 | 0 | 0 | 0 | 18 | 0 | 0 | 18 | 0 | 0 | 0 | 0
19 | 0 | 0 | 19 | 0 | 0 | 0 | 0 | 19 | 0 | 0 | 19 | 0 | 0 | 0 | 0 | 19 | 0 | 0 | 19 | 0 | 0 | 0 | 0 | 19 | 0 | 0 | 19 | 0 | 0 | 0 | 0 | 19 | 0 | 0 | 19 | 0 | 0 | 0 | 0
20 | 0 | 0 | 20 | 0 | 0 | 0 | 0 | 20 | 0 | 0 | 20 | 0 | 0 | 0 | 0 | 20 | 0 | 0 | 20 | 0 | 0 | 0 | 0 | 20 | 0 | 0 | 20 | 0 | 0 | 0 | 0 | 20 | 0 | 0 | 20 | 0 | 0 | 0 | 0
21 | 0 | 0 | 21 | 0 | 0 | 0 | 0 | 21 | 0 | 0 | 21 | 0 | 0 | 0 | 0 | 21 | 0 | 0 | 21 | 0 | 0 | 0 | 0 | 21 | 0 | 0 | 21 | 0 | 0 | 0 | 0 | 21 | 0 | 0 | 21 | 0 | 0 | 0 | 0
22 | 0 | 0 | 22 | 0 | 0 | 0 | 0 | 22 | 0 | 0 | 22 | 0 | 0 | 0 | 0 | 22 | 0 | 0 | 22 | 0 | 0 | 0 | 0 | 22 | 0 | 0 | 22 | 0 | 0 | 0 | 0 | 22 | 0 | 0 | 22 | 0 | 0 | 0 | 0
23 | 0 | 0 | 23 | 0 | 0 | 0 | 0 | 23 | 0 | 0 | 23 | 0 | 0 | 0 | 0 | 23 | 0 | 0 | 23 | 0 | 0 | 0 | 0 | 23 | 0 | 0 | 23 | 0 | 0 | 0 | 0 | 23 | 0 | 0 | 23 | 0 | 0 | 0 | 0
24 | 0 | 0 | 24 | 0 | 0 | 0 | 0 | 24 | 0 | 0 | 24 | 0 | 0 | 0 | 0 | 24 | 0 | 0 | 24 | 0 | 0 | 0 | 0 | 24 | 0 | 0 | 24 | 0 | 0 | 0 | 0 | 24 | 0 | 0 | 24 | 0 | 0 | 0 | 0
25 | 0 | 0 | 25 | 0 | 0 | 0 | 0 | 25 | 0 | 0 | 25 | 0 | 0 | 0 | 0 | 25 | 0 | 0 | 25 | 0 | 0 | 0 | 0 | 25 | 0 | 0 | 25 | 0 | 0 | 0 | 0 | 25 | 0 | 0 | 25 | 0 | 0 | 0 | 0
26 | 0 | 0 | 26 | 0 | 0 | 0 | 0 | 26 | 0 | 0 | 26 | 0 | 0 | 0 | 0 | 26 | 0 | 0 | 26 | 0 | 0 | 0 | 0 | 26 | 0 | 0 | 26 | 0 | 0 | 0 | 0 | 26 | 0 | 0 | 26 | 0 | 0 | 0 | 0
27 | 0 | 0 | 27 | 0 | 0 | 0 | 0 | 27 | 0 | 0 | 27 | 0 | 0 | 0 | 0 | 27 | 0 | 0 | 27 | 0 | 0 | 0 | 0 | 27 | 0 | 0 | 27 | 0 | 0 | 0 | 0 | 27 | 0 | 0 | 27 | 0 | 0 | 0 | 0
28 | 0 | 0 | 28 | 0 | 0 | 0 | 0 | 28 | 0 | 0 | 28 | 0 | 0 | 0 | 0 | 28 | 0 | 0 | 28 | 0 | 0 | 0 | 0 | 28 | 0 | 0 | 28 | 0 | 0 | 0 | 0 | 28 | 0 | 0 | 28 | 0 | 0 | 0 | 0
29 | 0 | 0 | 29 | 0 | 0 | 0 | 0 | 29 | 0 | 0 | 29 | 0 | 0 | 0 | 0 | 29 | 0 | 0 | 29 | 0 | 0 | 0 | 0 | 29 | 0 | 0 | 29 | 0 | 0 | 0 | 0 | 29 | 0 | 0 | 29 | 0 | 0 | 0 | 0
30 | 350558.4634 | 427931.9544 | 30 | 343739.1348 | 420053.0243 | 0 | -7878.9301 | 30 | 350103.8415 | 424640.6814 | 30 | 342943.5464 | 418749.924 | 0 | -5890.7574 | 30 | 367947.7515 | 443116.9324 | 30 | 359991.8681 | 436151.6249 | 0 | -6965.3074 | 30 | 351240.3963 | 425621.9821 | 30 | 342147.9581 | 416878.8865 | 0 | -8743.0956 | 30 | 350785.7744 | 423406.5048 | 30 | 338283.6718 | 410446.0688 | 0 | -12960.4361
31 | 0 | 0 | 31 | 0 | 0 |  | 0 | 31 | 0 | 0 | 31 | 0 | 0 |  | 0 | 31 | 0 | 0 | 31 | 0 | 0 |  | 0 | 31 | 0 | 0 | 31 | 0 | 0 |  | 0 | 31 | 0 | 0 | 31 | 0 | 0 |  | 0
32 | 0 | 0 | 32 | 0 | 0 |  | 0 | 32 | 0 | 0 | 32 | 0 | 0 |  | 0 | 32 | 0 | 0 | 32 | 0 | 0 |  | 0 | 32 | 0 | 0 | 32 | 0 | 0 |  | 0 | 32 | 0 | 0 | 32 | 0 | 0 |  | 0
33 | 0 | 0 | 33 | 0 | 0 |  | 0 | 33 | 0 | 0 | 33 | 0 | 0 |  | 0 | 33 | 0 | 0 | 33 | 0 | 0 |  | 0 | 33 | 0 | 0 | 33 | 0 | 0 |  | 0 | 33 | 0 | 0 | 33 | 0 | 0 |  | 0
34 | 0 | 0 | 34 | 0 | 0 |  | 0 | 34 | 0 | 0 | 34 | 0 | 0 |  | 0 | 34 | 0 | 0 | 34 | 0 | 0 |  | 0 | 34 | 0 | 0 | 34 | 0 | 0 |  | 0 | 34 | 0 | 0 | 34 | 0 | 0 |  | 0
35 | 0 | 0 | 35 | 0 | 0 |  | 0 | 35 | 0 | 0 | 35 | 0 | 0 |  | 0 | 35 | 0 | 0 | 35 | 0 | 0 |  | 0 | 35 | 0 | 0 | 35 | 0 | 0 |  | 0 | 35 | 0 | 0 | 35 | 0 | 0 |  | 0
36 | 0 | 0 | 36 | 0 | 0 |  | 0 | 36 | 0 | 0 | 36 | 0 | 0 |  | 0 | 36 | 0 | 0 | 36 | 0 | 0 |  | 0 | 36 | 0 | 0 | 36 | 0 | 0 |  | 0 | 36 | 0 | 0 | 36 | 0 | 0 |  | 0
37 | 0 | 0 | 37 | 0 | 0 |  | 0 | 37 | 0 | 0 | 37 | 0 | 0 |  | 0 | 37 | 0 | 0 | 37 | 0 | 0 |  | 0 | 37 | 0 | 0 | 37 | 0 | 0 |  | 0 | 37 | 0 | 0 | 37 | 0 | 0 |  | 0
38 | 0 | 0 | 38 | 0 | 0 |  | 0 | 38 | 0 | 0 | 38 | 0 | 0 |  | 0 | 38 | 0 | 0 | 38 | 0 | 0 |  | 0 | 38 | 0 | 0 | 38 | 0 | 0 |  | 0 | 38 | 0 | 0 | 38 | 0 | 0 |  | 0
39 | 0 | 0 | 39 | 0 | 0 |  | 0 | 39 | 0 | 0 | 39 | 0 | 0 |  | 0 | 39 | 0 | 0 | 39 | 0 | 0 |  | 0 | 39 | 0 | 0 | 39 | 0 | 0 |  | 0 | 39 | 0 | 0 | 39 | 0 | 0 |  | 0
40 | 0 | 0 | 40 | 0 | 0 |  | 259496.806 | 40 | 0 | 0 | 40 | 0 | 0 |  | 0 | 40 | 0 | 0 | 40 | 0 | 0 |  | -265381.1643 | 40 | 0 | 0 | 40 | 0 | 0 |  | 5945.1779 | 40 | 0 | 0 | 40 | 0 | 0 |  | 8487.5129
Residual Year 30 |  | 0 | Residual Year 30 |  | 0 |  |  | Residual Year 30 |  | 0 | Residual Year 30 |  | 0 |  |  | Residual Year 30 |  | 0 | Residual Year 30 |  | 0 |  |  | Residual Year 30 |  | 0 | Residual Year 30 |  | 0 |  |  | Residual Year 30 |  | 0 | Residual Year 30 |  | 0
Residual Year 40 |  | -259496.806 | Residual Year 40 |  | 0 |  |  | Residual Year 40 |  | 0 | Residual Year 40 |  | 0 |  |  | Residual Year 40 |  | 0 | Residual Year 40 |  | -265381.1643 |  |  | Residual Year 40 |  | -258954.1261 | Residual Year 40 |  | -253008.9482 |  |  | Residual Year 40 |  | -258064.0931 | Residual Year 40 |  | -249576.5802
Primary School | Climate Zone 1 | 2A | [5 empty] | Primary School | Climate Zone 2 | 3A | [5 empty] | Primary School | Climate Zone 3 | 3B | [5 empty] | Primary School | Climate Zone 4 | 4A | [5 empty] | Primary School | Climate Zone 5 | 5A
90.1-2019 |  |  | 90.1-2022 |  |  | Incremental Cost |  | 90.1-2019 |  |  | 90.1-2022 |  |  | Incremental Cost |  | 90.1-2019 |  |  | 90.1-2022 |  |  | Incremental Cost |  | 90.1-2019 |  |  | 90.1-2022 |  |  | Incremental Cost |  | 90.1-2019 |  |  | 90.1-2022 |  |  | Incremental Cost
Category | All Costs with First Replacement Only | With Repeated Replacements | Category | All Costs with First Replacement Only | With Repeated Replacements | 30 Year | 40 Year | Category | All Costs with First Replacement Only | With Repeated Replacements | Category | All Costs with First Replacement Only | With Repeated Replacements | 30 Year | 40 Year | Category | All Costs with First Replacement Only | With Repeated Replacements | Category | All Costs with First Replacement Only | With Repeated Replacements | 30 Year | 40 Year | Category | All Costs with First Replacement Only | With Repeated Replacements | Category | All Costs with First Replacement Only | With Repeated Replacements | 30 Year | 40 Year | Category | All Costs with First Replacement Only | With Repeated Replacements | Category | All Costs with First Replacement Only | With Repeated Replacements | 30 Year | 40 Year
New Construction | 1562653.1007 | 1562653.1007 | New Construction | 1566546.6884 | 1566546.6884 | 3893.5877 | 3893.5877 | New Construction | 1576634.3073 | 1576634.3073 | New Construction | 1581936.4334 | 1581936.4334 | 5302.1261 | 5302.1261 | New Construction | 1486237.6771 | 1486237.6771 | New Construction | 1486433.5149 | 1486433.5149 | 195.8378 | 195.8378 | New Construction | 1611151.5279 | 1611151.5279 | New Construction | 1595024.9359 | 1595024.9359 | -16126.592 | -16126.592 | New Construction | 1622516.0813 | 1622516.0813 | New Construction | 1607553.3745 | 1607553.3745 | -14962.7068 | -14962.7068
Maintenance | 2647.6953 | 2647.6953 | Maintenance | 3045.7245 | 3045.7245 | 398.0292 | 398.0292 | Maintenance | 2654.7337 | 2654.7337 | Maintenance | 3052.4814 | 3052.4814 | 397.7477 | 397.7477 | Maintenance | 1402.3702 | 1402.3702 | Maintenance | 1801.8071 | 1801.8071 | 399.4369 | 399.4369 | Maintenance | 2652.1998 | 2652.1998 | Maintenance | 3042.3461 | 3042.3461 | 390.1462 | 390.1462 | Maintenance | 2658.3936 | 2658.3936 | Maintenance | 3048.5399 | 3048.5399 | 390.1462 | 390.1462
Replacement - Year |  |  | Replacement - Year |  |  | 0 | 0 | Replacement - Year |  |  | Replacement - Year |  |  | 0 | 0 | Replacement - Year |  |  | Replacement - Year |  |  | 0 | 0 | Replacement - Year |  |  | Replacement - Year |  |  | 0 | 0 | Replacement - Year |  |  | Replacement - Year |  |  | 0 | 0
1 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 0
2 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 0 | 0
3 | 0 | 0 | 3 | 0 | 0 | 0 | 0 | 3 | 0 | 0 | 3 | 0 | 0 | 0 | 0 | 3 | 0 | 0 | 3 | 0 | 0 | 0 | 0 | 3 | 0 | 0 | 3 | 0 | 0 | 0 | 0 | 3 | 0 | 0 | 3 | 0 | 0 | 0 | 0
4 | 0 | 0 | 4 | 0 | 0 | 0 | 0 | 4 | 0 | 0 | 4 | 0 | 0 | 0 | 0 | 4 | 0 | 0 | 4 | 0 | 0 | 0 | 0 | 4 | 0 | 0 | 4 | 0 | 0 | 0 | 0 | 4 | 0 | 0 | 4 | 0 | 0 | 0 | 0
5 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 5 | 0 | 0 | 0 | 0
6 | 0 | 0 | 6 | 0 | 0 | 0 | 0 | 6 | 0 | 0 | 6 | 0 | 0 | 0 | 0 | 6 | 0 | 0 | 6 | 0 | 0 | 0 | 0 | 6 | 0 | 0 | 6 | 0 | 0 | 0 | 0 | 6 | 0 | 0 | 6 | 0 | 0 | 0 | 0
7 | 0 | 0 | 7 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 7 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 7 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 7 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 7 | 0 | 0 | 0 | 0
8 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 8 | 0 | 0 | 0 | 0
9 | 0 | 0 | 9 | 0 | 0 | 0 | 0 | 9 | 0 | 0 | 9 | 0 | 0 | 0 | 0 | 9 | 0 | 0 | 9 | 0 | 0 | 0 | 0 | 9 | 0 | 0 | 9 | 0 | 0 | 0 | 0 | 9 | 0 | 0 | 9 | 0 | 0 | 0 | 0
10 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 10 | 0 | 0 | 0 | 0
11 | 0 | 0 | 11 | 0 | 0 | 0 | 0 | 11 | 0 | 0 | 11 | 0 | 0 | 0 | 0 | 11 | 0 | 0 | 11 | 0 | 0 | 0 | 0 | 11 | 0 | 0 | 11 | 0 | 0 | 0 | 0 | 11 | 0 | 0 | 11 | 0 | 0 | 0 | 0
12 | 0 | 0 | 12 | 0 | 0 | 0 | 0 | 12 | 0 | 0 | 12 | 0 | 0 | 0 | 0 | 12 | 0 | 0 | 12 | 0 | 0 | 0 | 0 | 12 | 0 | 0 | 12 | 0 | 0 | 0 | 0 | 12 | 0 | 0 | 12 | 0 | 0 | 0 | 0
13 | 0 | 0 | 13 | 0 | 0 | 0 | 0 | 13 | 0 | 0 | 13 | 0 | 0 | 0 | 0 | 13 | 0 | 0 | 13 | 0 | 0 | 0 | 0 | 13 | 0 | 0 | 13 | 0 | 0 | 0 | 0 | 13 | 0 | 0 | 13 | 0 | 0 | 0 | 0
14 | 0 | 0 | 14 | 0 | 0 | 0 | 0 | 14 | 0 | 0 | 14 | 0 | 0 | 0 | 0 | 14 | 0 | 0 | 14 | 0 | 0 | 0 | 0 | 14 | 0 | 0 | 14 | 0 | 0 | 0 | 0 | 14 | 0 | 0 | 14 | 0 | 0 | 0 | 0
15 | 703834.4307 | 703834.4307 | 15 | 706399.7137 | 706399.7137 | 2565.283 | 2565.283 | 15 | 708390.1304 | 708390.1304 | 15 | 710882.3519 | 710882.3519 | 2492.2215 | 2492.2215 | 15 | 534610.741 | 534610.741 | 15 | 532722.8341 | 532722.8341 | -1887.9069 | -1887.9069 | 15 | 710522.7476 | 710522.7476 | 15 | 701334.2578 | 701334.2578 | -9188.4898 | -9188.4898 | 15 | 711295.7268 | 711295.7268 | 15 | 702840.7285 | 702840.7285 | -8454.9983 | -8454.9983
16 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 16 | 0 | 0 | 0 | 0
17 | 0 | 0 | 17 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 17 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 17 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 17 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 17 | 0 | 0 | 0 | 0
18 | 0 | 0 | 18 | 0 | 0 | 0 | 0 | 18 | 0 | 0 | 18 | 0 | 0 | 0 | 0 | 18 | 0 | 0 | 18 | 0 | 0 | 0 | 0 | 18 | 0 | 0 | 18 | 0 | 0 | 0 | 0 | 18 | 0 | 0 | 18 | 0 | 0 | 0 | 0
19 | 0 | 0 | 19 | 0 | 0 | 0 | 0 | 19 | 0 | 0 | 19 | 0 | 0 | 0 | 0 | 19 | 0 | 0 | 19 | 0 | 0 | 0 | 0 | 19 | 0 | 0 | 19 | 0 | 0 | 0 | 0 | 19 | 0 | 0 | 19 | 0 | 0 | 0 | 0
20 | 0 | 0 | 20 | 0 | 0 | 0 | 0 | 20 | 0 | 0 | 20 | 0 | 0 | 0 | 0 | 20 | 0 | 0 | 20 | 0 | 0 | 0 | 0 | 20 | 32847.9703 | 32847.9703 | 20 | 32620.5784 | 32620.5784 | -227.3919 | -227.3919 | 20 | 33552.5196 | 33552.5196 | 20 | 33283.6809 | 33283.6809 | -268.8387 | -268.8387
21 | 0 | 0 | 21 | 0 | 0 | 0 | 0 | 21 | 0 | 0 | 21 | 0 | 0 | 0 | 0 | 21 | 0 | 0 | 21 | 0 | 0 | 0 | 0 | 21 | 0 | 0 | 21 | 0 | 0 | 0 | 0 | 21 | 0 | 0 | 21 | 0 | 0 | 0 | 0
22 | 0 | 0 | 22 | 0 | 0 | 0 | 0 | 22 | 0 | 0 | 22 | 0 | 0 | 0 | 0 | 22 | 0 | 0 | 22 | 0 | 0 | 0 | 0 | 22 | 0 | 0 | 22 | 0 | 0 | 0 | 0 | 22 | 0 | 0 | 22 | 0 | 0 | 0 | 0
23 | 0 | 0 | 23 | 0 | 0 | 0 | 0 | 23 | 0 | 0 | 23 | 0 | 0 | 0 | 0 | 23 | 0 | 0 | 23 | 0 | 0 | 0 | 0 | 23 | 0 | 0 | 23 | 0 | 0 | 0 | 0 | 23 | 0 | 0 | 23 | 0 | 0 | 0 | 0
24 | 0 | 0 | 24 | 0 | 0 | 0 | 0 | 24 | 0 | 0 | 24 | 0 | 0 | 0 | 0 | 24 | 0 | 0 | 24 | 0 | 0 | 0 | 0 | 24 | 0 | 0 | 24 | 0 | 0 | 0 | 0 | 24 | 0 | 0 | 24 | 0 | 0 | 0 | 0
25 | 0 | 0 | 25 | 0 | 0 | 0 | 0 | 25 | 0 | 0 | 25 | 0 | 0 | 0 | 0 | 25 | 0 | 0 | 25 | 0 | 0 | 0 | 0 | 25 | 0 | 0 | 25 | 0 | 0 | 0 | 0 | 25 | 0 | 0 | 25 | 0 | 0 | 0 | 0
26 | 0 | 0 | 26 | 0 | 0 | 0 | 0 | 26 | 0 | 0 | 26 | 0 | 0 | 0 | 0 | 26 | 0 | 0 | 26 | 0 | 0 | 0 | 0 | 26 | 0 | 0 | 26 | 0 | 0 | 0 | 0 | 26 | 0 | 0 | 26 | 0 | 0 | 0 | 0
27 | 0 | 0 | 27 | 0 | 0 | 0 | 0 | 27 | 0 | 0 | 27 | 0 | 0 | 0 | 0 | 27 | 0 | 0 | 27 | 0 | 0 | 0 | 0 | 27 | 0 | 0 | 27 | 0 | 0 | 0 | 0 | 27 | 0 | 0 | 27 | 0 | 0 | 0 | 0
28 | 0 | 0 | 28 | 0 | 0 | 0 | 0 | 28 | 0 | 0 | 28 | 0 | 0 | 0 | 0 | 28 | 0 | 0 | 28 | 0 | 0 | 0 | 0 | 28 | 0 | 0 | 28 | 0 | 0 | 0 | 0 | 28 | 0 | 0 | 28 | 0 | 0 | 0 | 0
29 | 0 | 0 | 29 | 0 | 0 | 0 | 0 | 29 | 0 | 0 | 29 | 0 | 0 | 0 | 0 | 29 | 0 | 0 | 29 | 0 | 0 | 0 | 0 | 29 | 0 | 0 | 29 | 0 | 0 | 0 | 0 | 29 | 0 | 0 | 29 | 0 | 0 | 0 | 0
30 | 1618623.1182 | 2322457.5489 | 30 | 1505585.4579 | 2211985.1716 | -834.5083 | -110472.3773 | 30 | 1514431.6905 | 2222821.8208 | 30 | 1510445.8306 | 2221328.1825 | -1237.7995 | -1493.6383 | 30 | 1620279.0174 | 2154889.7584 | 30 | 1616025.5016 | 2148748.3356 | -1104.0878 | -6141.4228 | 30 | 1520112.4368 | 2230635.1844 | 30 | 1498023.4725 | 2199357.7303 | -1056.0828 | -31277.4541 | 30 | 1531204.7363 | 2242500.4631 | 30 | 1509388.6628 | 2212229.3913 | -1168.1572 | -30271.0718
31 | 0 | 0 | 31 | 0 | 0 |  | 0 | 31 | 0 | 0 | 31 | 0 | 0 |  | 0 | 31 | 0 | 0 | 31 | 0 | 0 |  | 0 | 31 | 0 | 0 | 31 | 0 | 0 |  | 0 | 31 | 0 | 0 | 31 | 0 | 0 |  | 0
32 | 0 | 0 | 32 | 0 | 0 |  | 0 | 32 | 0 | 0 | 32 | 0 | 0 |  | 0 | 32 | 0 | 0 | 32 | 0 | 0 |  | 0 | 32 | 0 | 0 | 32 | 0 | 0 |  | 0 | 32 | 0 | 0 | 32 | 0 | 0 |  | 0
33 | 0 | 0 | 33 | 0 | 0 |  | 0 | 33 | 0 | 0 | 33 | 0 | 0 |  | 0 | 33 | 0 | 0 | 33 | 0 | 0 |  | 0 | 33 | 0 | 0 | 33 | 0 | 0 |  | 0 | 33 | 0 | 0 | 33 | 0 | 0 |  | 0
34 | 0 | 0 | 34 | 0 | 0 |  | 0 | 34 | 0 | 0 | 34 | 0 | 0 |  | 0 | 34 | 0 | 0 | 34 | 0 | 0 |  | 0 | 34 | 0 | 0 | 34 | 0 | 0 |  | 0 | 34 | 0 | 0 | 34 | 0 | 0 |  | 0
35 | 33963.8765 | 33963.8765 | 35 | 33944.6507 | 33944.6507 |  | -19.2259 | 35 | 44241.1149 | 44241.1149 | 35 | 44184.6889 | 44184.6889 |  | -56.426 | 35 | 40890.6355 | 40890.6355 | 35 | 40834.1088 | 40834.1088 |  | -56.5268 | 35 | 49012.3451 | 49012.3451 | 35 | 47542.0102 | 47542.0102 |  | -1470.335 | 35 | 53568.1843 | 53568.1843 | 35 | 51829.7784 | 51829.7784 |  | -1738.4059
36 | 0 | 0 | 36 | 0 | 0 |  | 0 | 36 | 0 | 0 | 36 | 0 | 0 |  | 0 | 36 | 0 | 0 | 36 | 0 | 0 |  | 0 | 36 | 0 | 0 | 36 | 0 | 0 |  | 0 | 36 | 0 | 0 | 36 | 0 | 0 |  | 0
37 | 0 | 0 | 37 | 0 | 0 |  | 0 | 37 | 0 | 0 | 37 | 0 | 0 |  | 0 | 37 | 0 | 0 | 37 | 0 | 0 |  | 0 | 37 | 0 | 0 | 37 | 0 | 0 |  | 0 | 37 | 0 | 0 | 37 | 0 | 0 |  | 0
38 | 0 | 0 | 38 | 0 | 0 |  | 0 | 38 | 0 | 0 | 38 | 0 | 0 |  | 0 | 38 | 0 | 0 | 38 | 0 | 0 |  | 0 | 38 | 0 | 0 | 38 | 0 | 0 |  | 0 | 38 | 0 | 0 | 38 | 0 | 0 |  | 0
39 | 0 | 0 | 39 | 0 | 0 |  | 0 | 39 | 0 | 0 | 39 | 0 | 0 |  | 0 | 39 | 0 | 0 | 39 | 0 | 0 |  | 0 | 39 | 0 | 0 | 39 | 0 | 0 |  | 0 | 39 | 0 | 0 | 39 | 0 | 0 |  | 0
40 | 0 | 0 | 40 | 3349.0193 | 0 |  | 74519.8252 | 40 | 0 | 0 | 40 | 4983.4412 | 0 |  | 1874.8645 | 40 | 0 | 0 | 40 | 4448.6521 | 0 |  | 3513.4311 | 40 | 0 | 0 | 40 | 5519.3063 | 0 |  | 19049.0932 | 40 | 0 | 0 | 40 | 6203.681 | 0 |  | 18852.444
Residual Year 30 |  | -4851.9824 | Residual Year 30 |  | -5686.4906 |  |  | Residual Year 30 |  | -6320.1593 | Residual Year 30 |  | -7557.9587 |  |  | Residual Year 30 |  | -5841.5194 | Residual Year 30 |  | -6945.6071 |  |  | Residual Year 30 |  | -23425.7487 | Residual Year 30 |  | -24481.8315 |  |  | Residual Year 30 |  | -24428.8576 | Residual Year 30 |  | -25597.0147
Residual Year 40 |  | -1342805.4499 | Residual Year 40 |  | -1268285.6247 |  |  | Residual Year 40 |  | -1283672.126 | Residual Year 40 |  | -1281797.2615 |  |  | Residual Year 40 |  | -1293438.7081 | Residual Year 40 |  | -1289925.2771 |  |  | Residual Year 40 |  | -1292259.7886 | Residual Year 40 |  | -1273210.6954 |  |  | Residual Year 40 |  | -1303817.3197 | Residual Year 40 |  | -1284964.8757
Small Hotel | Climate Zone 1 | 2A | [5 empty] | Small Hotel | Climate Zone 2 | 3A | [5 empty] | Small Hotel | Climate Zone 3 | 3B | [5 empty] | Small Hotel | Climate Zone 4 | 4A | [5 empty] | Small Hotel | Climate Zone 5 | 5A
90.1-2019 |  |  | 90.1-2022 |  |  | Incremental Cost |  | 90.1-2019 |  |  | 90.1-2022 |  |  | Incremental Cost |  | 90.1-2019 |  |  | 90.1-2022 |  |  | Incremental Cost |  | 90.1-2019 |  |  | 90.1-2022 |  |  | Incremental Cost |  | 90.1-2019 |  |  | 90.1-2022 |  |  | Incremental Cost
Category | All Costs with First Replacement Only | With Repeated Replacements | Category | All Costs with First Replacement Only | With Repeated Replacements | 30 Year | 40 Year | Category | All Costs with First Replacement Only | With Repeated Replacements | Category | All Costs with First Replacement Only | With Repeated Replacements | 30 Year | 40 Year | Category | All Costs with First Replacement Only | With Repeated Replacements | Category | All Costs with First Replacement Only | With Repeated Replacements | 30 Year | 40 Year | Category | All Costs with First Replacement Only | With Repeated Replacements | Category | All Costs with First Replacement Only | With Repeated Replacements | 30 Year | 40 Year | Category | All Costs with First Replacement Only | With Repeated Replacements | Category | All Costs with First Replacement Only | With Repeated Replacements | 30 Year | 40 Year
New Construction | 149519.8358 | 149519.8358 | New Construction | 151937.3859 | 151937.3859 | 2417.55 | 2417.55 | New Construction | 149589.7986 | 149589.7986 | New Construction | 152431.6564 | 152431.6564 | 2841.8577 | 2841.8577 | New Construction | 157794.0211 | 157794.0211 | New Construction | 159684.0012 | 159684.0012 | 1889.9802 | 1889.9802 | New Construction | 147531.2833 | 147531.2833 | New Construction | 145430.3647 | 145430.3647 | -2100.9186 | -2100.9186 | New Construction | 147037.9887 | 147037.9887 | New Construction | 144983.809 | 144983.809 | -2054.1797 | -2054.1797
Maintenance | 296.0409 | 296.0409 | Maintenance | 563.7563 | 563.7563 | 267.7154 | 267.7154 | Maintenance | 296.604 | 296.604 | Maintenance | 564.6009 | 564.6009 | 267.9969 | 267.9969 | Maintenance | 304.2054 | 304.2054 | Maintenance | 571.3577 | 571.3577 | 267.1523 | 267.1523 | Maintenance | 295.1963 | 295.1963 | Maintenance | 293.2255 | 293.2255 | -1.9708 | -1.9708 | Maintenance | 295.7594 | 295.7594 | Maintenance | 293.2255 | 293.2255 | -2.5338 | -2.5338
Replacement - Year |  |  | Replacement - Year |  |  | 0 | 0 | Replacement - Year |  |  | Replacement - Year |  |  | 0 | 0 | Replacement - Year |  |  | Replacement - Year |  |  | 0 | 0 | Replacement - Year |  |  | Replacement - Year |  |  | 0 | 0 | Replacement - Year |  |  | Replacement - Year |  |  | 0 | 0
1 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 0
2 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 0 | 0
3 | 0 | 0 | 3 | 0 | 0 | 0 | 0 | 3 | 0 | 0 | 3 | 0 | 0 | 0 | 0 | 3 | 0 | 0 | 3 | 0 | 0 | 0 | 0 | 3 | 0 | 0 | 3 | 0 | 0 | 0 | 0 | 3 | 0 | 0 | 3 | 0 | 0 | 0 | 0
4 | 0 | 0 | 4 | 0 | 0 | 0 | 0 | 4 | 0 | 0 | 4 | 0 | 0 | 0 | 0 | 4 | 0 | 0 | 4 | 0 | 0 | 0 | 0 | 4 | 0 | 0 | 4 | 0 | 0 | 0 | 0 | 4 | 0 | 0 | 4 | 0 | 0 | 0 | 0
5 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 5 | 0 | 0 | 0 | 0
6 | 0 | 0 | 6 | 0 | 0 | 0 | 0 | 6 | 0 | 0 | 6 | 0 | 0 | 0 | 0 | 6 | 0 | 0 | 6 | 0 | 0 | 0 | 0 | 6 | 0 | 0 | 6 | 0 | 0 | 0 | 0 | 6 | 0 | 0 | 6 | 0 | 0 | 0 | 0
7 | 0 | 0 | 7 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 7 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 7 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 7 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 7 | 0 | 0 | 0 | 0
8 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 8 | 0 | 0 | 0 | 0
9 | 0 | 0 | 9 | 0 | 0 | 0 | 0 | 9 | 0 | 0 | 9 | 0 | 0 | 0 | 0 | 9 | 0 | 0 | 9 | 0 | 0 | 0 | 0 | 9 | 0 | 0 | 9 | 0 | 0 | 0 | 0 | 9 | 0 | 0 | 9 | 0 | 0 | 0 | 0
10 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 10 | 0 | 0 | 0 | 0
11 | 0 | 0 | 11 | 0 | 0 | 0 | 0 | 11 | 0 | 0 | 11 | 0 | 0 | 0 | 0 | 11 | 0 | 0 | 11 | 0 | 0 | 0 | 0 | 11 | 0 | 0 | 11 | 0 | 0 | 0 | 0 | 11 | 0 | 0 | 11 | 0 | 0 | 0 | 0
12 | 0 | 0 | 12 | 0 | 0 | 0 | 0 | 12 | 0 | 0 | 12 | 0 | 0 | 0 | 0 | 12 | 0 | 0 | 12 | 0 | 0 | 0 | 0 | 12 | 0 | 0 | 12 | 0 | 0 | 0 | 0 | 12 | 0 | 0 | 12 | 0 | 0 | 0 | 0
13 | 0 | 0 | 13 | 0 | 0 | 0 | 0 | 13 | 0 | 0 | 13 | 0 | 0 | 0 | 0 | 13 | 0 | 0 | 13 | 0 | 0 | 0 | 0 | 13 | 0 | 0 | 13 | 0 | 0 | 0 | 0 | 13 | 0 | 0 | 13 | 0 | 0 | 0 | 0
14 | 0 | 0 | 14 | 0 | 0 | 0 | 0 | 14 | 0 | 0 | 14 | 0 | 0 | 0 | 0 | 14 | 0 | 0 | 14 | 0 | 0 | 0 | 0 | 14 | 0 | 0 | 14 | 0 | 0 | 0 | 0 | 14 | 0 | 0 | 14 | 0 | 0 | 0 | 0
15 | 51719.7114 | 51719.7114 | 15 | 56638.6787 | 56638.6787 | 4918.9673 | 4918.9673 | 15 | 51539.7829 | 51539.7829 | 15 | 56482.3633 | 56482.3633 | 4942.5804 | 4942.5804 | 15 | 52039.6238 | 52039.6238 | 15 | 57010.7189 | 57010.7189 | 4971.0952 | 4971.0952 | 15 | 50473.6329 | 50473.6329 | 15 | 50700.9845 | 50700.9845 | 227.3517 | 227.3517 | 15 | 49573.0628 | 49573.0628 | 15 | 50115.4544 | 50115.4544 | 542.3916 | 542.3916
16 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 16 | 0 | 0 | 0 | 0
17 | 0 | 0 | 17 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 17 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 17 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 17 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 17 | 0 | 0 | 0 | 0
18 | 0 | 0 | 18 | 0 | 0 | 0 | 0 | 18 | 0 | 0 | 18 | 0 | 0 | 0 | 0 | 18 | 0 | 0 | 18 | 0 | 0 | 0 | 0 | 18 | 0 | 0 | 18 | 0 | 0 | 0 | 0 | 18 | 0 | 0 | 18 | 0 | 0 | 0 | 0
19 | 0 | 0 | 19 | 0 | 0 | 0 | 0 | 19 | 0 | 0 | 19 | 0 | 0 | 0 | 0 | 19 | 0 | 0 | 19 | 0 | 0 | 0 | 0 | 19 | 0 | 0 | 19 | 0 | 0 | 0 | 0 | 19 | 0 | 0 | 19 | 0 | 0 | 0 | 0
20 | 0 | 0 | 20 | 0 | 0 | 0 | 0 | 20 | 0 | 0 | 20 | 0 | 0 | 0 | 0 | 20 | 0 | 0 | 20 | 0 | 0 | 0 | 0 | 20 | 0 | 0 | 20 | 0 | 0 | 0 | 0 | 20 | 0 | 0 | 20 | 0 | 0 | 0 | 0
21 | 0 | 0 | 21 | 0 | 0 | 0 | 0 | 21 | 0 | 0 | 21 | 0 | 0 | 0 | 0 | 21 | 0 | 0 | 21 | 0 | 0 | 0 | 0 | 21 | 0 | 0 | 21 | 0 | 0 | 0 | 0 | 21 | 0 | 0 | 21 | 0 | 0 | 0 | 0
22 | 0 | 0 | 22 | 0 | 0 | 0 | 0 | 22 | 0 | 0 | 22 | 0 | 0 | 0 | 0 | 22 | 0 | 0 | 22 | 0 | 0 | 0 | 0 | 22 | 0 | 0 | 22 | 0 | 0 | 0 | 0 | 22 | 0 | 0 | 22 | 0 | 0 | 0 | 0
23 | 0 | 0 | 23 | 0 | 0 | 0 | 0 | 23 | 0 | 0 | 23 | 0 | 0 | 0 | 0 | 23 | 0 | 0 | 23 | 0 | 0 | 0 | 0 | 23 | 0 | 0 | 23 | 0 | 0 | 0 | 0 | 23 | 0 | 0 | 23 | 0 | 0 | 0 | 0
24 | 0 | 0 | 24 | 0 | 0 | 0 | 0 | 24 | 0 | 0 | 24 | 0 | 0 | 0 | 0 | 24 | 0 | 0 | 24 | 0 | 0 | 0 | 0 | 24 | 0 | 0 | 24 | 0 | 0 | 0 | 0 | 24 | 0 | 0 | 24 | 0 | 0 | 0 | 0
25 | 0 | 0 | 25 | 0 | 0 | 0 | 0 | 25 | 0 | 0 | 25 | 0 | 0 | 0 | 0 | 25 | 0 | 0 | 25 | 0 | 0 | 0 | 0 | 25 | 0 | 0 | 25 | 0 | 0 | 0 | 0 | 25 | 0 | 0 | 25 | 0 | 0 | 0 | 0
26 | 0 | 0 | 26 | 0 | 0 | 0 | 0 | 26 | 0 | 0 | 26 | 0 | 0 | 0 | 0 | 26 | 0 | 0 | 26 | 0 | 0 | 0 | 0 | 26 | 0 | 0 | 26 | 0 | 0 | 0 | 0 | 26 | 0 | 0 | 26 | 0 | 0 | 0 | 0
27 | 0 | 0 | 27 | 0 | 0 | 0 | 0 | 27 | 0 | 0 | 27 | 0 | 0 | 0 | 0 | 27 | 0 | 0 | 27 | 0 | 0 | 0 | 0 | 27 | 0 | 0 | 27 | 0 | 0 | 0 | 0 | 27 | 0 | 0 | 27 | 0 | 0 | 0 | 0
28 | 0 | 0 | 28 | 0 | 0 | 0 | 0 | 28 | 0 | 0 | 28 | 0 | 0 | 0 | 0 | 28 | 0 | 0 | 28 | 0 | 0 | 0 | 0 | 28 | 0 | 0 | 28 | 0 | 0 | 0 | 0 | 28 | 0 | 0 | 28 | 0 | 0 | 0 | 0
29 | 0 | 0 | 29 | 0 | 0 | 0 | 0 | 29 | 0 | 0 | 29 | 0 | 0 | 0 | 0 | 29 | 0 | 0 | 29 | 0 | 0 | 0 | 0 | 29 | 0 | 0 | 29 | 0 | 0 | 0 | 0 | 29 | 0 | 0 | 29 | 0 | 0 | 0 | 0
30 | 178916.5995 | 230636.311 | 30 | 175302.9042 | 231941.5829 | 0 | 1305.2719 | 30 | 179245.1173 | 230784.9002 | 30 | 176288.4575 | 232770.8208 | 0 | 1985.9206 | 30 | 192057.31 | 244096.9338 | 30 | 187458.0613 | 244468.7803 | 0 | 371.8465 | 30 | 177274.0107 | 227747.6436 | 30 | 173003.2798 | 223704.2644 | 0 | -4043.3792 | 30 | 177602.5285 | 227175.5913 | 30 | 173003.2798 | 223118.7342 | 0 | -4056.8571
31 | 0 | 0 | 31 | 0 | 0 |  | 0 | 31 | 0 | 0 | 31 | 0 | 0 |  | 0 | 31 | 0 | 0 | 31 | 0 | 0 |  | 0 | 31 | 0 | 0 | 31 | 0 | 0 |  | 0 | 31 | 0 | 0 | 31 | 0 | 0 |  | 0
32 | 0 | 0 | 32 | 0 | 0 |  | 0 | 32 | 0 | 0 | 32 | 0 | 0 |  | 0 | 32 | 0 | 0 | 32 | 0 | 0 |  | 0 | 32 | 0 | 0 | 32 | 0 | 0 |  | 0 | 32 | 0 | 0 | 32 | 0 | 0 |  | 0
33 | 0 | 0 | 33 | 0 | 0 |  | 0 | 33 | 0 | 0 | 33 | 0 | 0 |  | 0 | 33 | 0 | 0 | 33 | 0 | 0 |  | 0 | 33 | 0 | 0 | 33 | 0 | 0 |  | 0 | 33 | 0 | 0 | 33 | 0 | 0 |  | 0
34 | 0 | 0 | 34 | 0 | 0 |  | 0 | 34 | 0 | 0 | 34 | 0 | 0 |  | 0 | 34 | 0 | 0 | 34 | 0 | 0 |  | 0 | 34 | 0 | 0 | 34 | 0 | 0 |  | 0 | 34 | 0 | 0 | 34 | 0 | 0 |  | 0
35 | 0 | 0 | 35 | 0 | 0 |  | 0 | 35 | 0 | 0 | 35 | 0 | 0 |  | 0 | 35 | 0 | 0 | 35 | 0 | 0 |  | 0 | 35 | 0 | 0 | 35 | 0 | 0 |  | 0 | 35 | 0 | 0 | 35 | 0 | 0 |  | 0
36 | 0 | 0 | 36 | 0 | 0 |  | 0 | 36 | 0 | 0 | 36 | 0 | 0 |  | 0 | 36 | 0 | 0 | 36 | 0 | 0 |  | 0 | 36 | 0 | 0 | 36 | 0 | 0 |  | 0 | 36 | 0 | 0 | 36 | 0 | 0 |  | 0
37 | 0 | 0 | 37 | 0 | 0 |  | 0 | 37 | 0 | 0 | 37 | 0 | 0 |  | 0 | 37 | 0 | 0 | 37 | 0 | 0 |  | 0 | 37 | 0 | 0 | 37 | 0 | 0 |  | 0 | 37 | 0 | 0 | 37 | 0 | 0 |  | 0
38 | 0 | 0 | 38 | 0 | 0 |  | 0 | 38 | 0 | 0 | 38 | 0 | 0 |  | 0 | 38 | 0 | 0 | 38 | 0 | 0 |  | 0 | 38 | 0 | 0 | 38 | 0 | 0 |  | 0 | 38 | 0 | 0 | 38 | 0 | 0 |  | 0
39 | 0 | 0 | 39 | 0 | 0 |  | 0 | 39 | 0 | 0 | 39 | 0 | 0 |  | 0 | 39 | 0 | 0 | 39 | 0 | 0 |  | 0 | 39 | 0 | 0 | 39 | 0 | 0 |  | 0 | 39 | 0 | 0 | 39 | 0 | 0 |  | 0
40 | 0 | 0 | 40 | 0 | 0 |  | 769.4745 | 40 | 0 | 0 | 40 | 0 | 0 |  | 323.5798 | 40 | 0 | 0 | 40 | 0 | 0 |  | 1409.1341 | 40 | 0 | 0 | 40 | 0 | 0 |  | 2771.37 | 40 | 0 | 0 | 40 | 0 | 0 |  | 2885.3686
Residual Year 30 |  | 0 | Residual Year 30 |  | 0 |  |  | Residual Year 30 |  | 0 | Residual Year 30 |  | 0 |  |  | Residual Year 30 |  | 0 | Residual Year 30 |  | 0 |  |  | Residual Year 30 |  | 0 | Residual Year 30 |  | 0 |  |  | Residual Year 30 |  | 0 | Residual Year 30 |  | 0
Residual Year 40 |  | -136517.6368 | Residual Year 40 |  | -135748.1624 |  |  | Residual Year 40 |  | -136676.6725 | Residual Year 40 |  | -136353.0927 |  |  | Residual Year 40 |  | -145384.7479 | Residual Year 40 |  | -143975.6139 |  |  | Residual Year 40 |  | -135007.2181 | Residual Year 40 |  | -132235.8481 |  |  | Residual Year 40 |  | -134926.0399 | Residual Year 40 |  | -132040.6714
Mid-rise Apartment | Climate Zone 1 | 2A | [5 empty] | Mid-rise Apartment | Climate Zone 2 | 3A | [5 empty] | Mid-rise Apartment | Climate Zone 3 | 3B | [5 empty] | Mid-rise Apartment | Climate Zone 4 | 4A | [5 empty] | Mid-rise Apartment | Climate Zone 5 | 5A
90.1-2019 |  |  | 90.1-2022 |  |  | Incremental Cost |  | 90.1-2019 |  |  | 90.1-2022 |  |  | Incremental Cost |  | 90.1-2019 |  |  | 90.1-2022 |  |  | Incremental Cost |  | 90.1-2019 |  |  | 90.1-2022 |  |  | Incremental Cost |  | 90.1-2019 |  |  | 90.1-2022 |  |  | Incremental Cost
Category | All Costs with First Replacement Only | With Repeated Replacements | Category | All Costs with First Replacement Only | With Repeated Replacements | 30 Year | 40 Year | Category | All Costs with First Replacement Only | With Repeated Replacements | Category | All Costs with First Replacement Only | With Repeated Replacements | 30 Year | 40 Year | Category | All Costs with First Replacement Only | With Repeated Replacements | Category | All Costs with First Replacement Only | With Repeated Replacements | 30 Year | 40 Year | Category | All Costs with First Replacement Only | With Repeated Replacements | Category | All Costs with First Replacement Only | With Repeated Replacements | 30 Year | 40 Year | Category | All Costs with First Replacement Only | With Repeated Replacements | Category | All Costs with First Replacement Only | With Repeated Replacements | 30 Year | 40 Year
New Construction | 353490.914 | 353490.914 | New Construction | 330825.2557 | 330825.2557 | -22665.6583 | -22665.6583 | New Construction | 340186.4032 | 340186.4032 | New Construction | 317206.1919 | 317206.1919 | -22980.2112 | -22980.2112 | New Construction | 343343.1591 | 343343.1591 | New Construction | 316263.3746 | 316263.3746 | -27079.7846 | -27079.7846 | New Construction | 347930.7123 | 347930.7123 | New Construction | 314565.7116 | 314565.7116 | -33365.0007 | -33365.0007 | New Construction | 323780.4655 | 323780.4655 | New Construction | 291801.9448 | 291801.9448 | -31978.5206 | -31978.5206
Maintenance | 0 | 0 | Maintenance | 0 | 0 | 0 | 0 | Maintenance | 0 | 0 | Maintenance | 0 | 0 | 0 | 0 | Maintenance | 0 | 0 | Maintenance | 0 | 0 | 0 | 0 | Maintenance | 0 | 0 | Maintenance | 0 | 0 | 0 | 0 | Maintenance | 0 | 0 | Maintenance | 0 | 0 | 0 | 0
Replacement - Year |  |  | Replacement - Year |  |  | 0 | 0 | Replacement - Year |  |  | Replacement - Year |  |  | 0 | 0 | Replacement - Year |  |  | Replacement - Year |  |  | 0 | 0 | Replacement - Year |  |  | Replacement - Year |  |  | 0 | 0 | Replacement - Year |  |  | Replacement - Year |  |  | 0 | 0
1 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 0
2 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 0 | 0
3 | 0 | 0 | 3 | 0 | 0 | 0 | 0 | 3 | 0 | 0 | 3 | 0 | 0 | 0 | 0 | 3 | 0 | 0 | 3 | 0 | 0 | 0 | 0 | 3 | 0 | 0 | 3 | 0 | 0 | 0 | 0 | 3 | 0 | 0 | 3 | 0 | 0 | 0 | 0
4 | 0 | 0 | 4 | 0 | 0 | 0 | 0 | 4 | 0 | 0 | 4 | 0 | 0 | 0 | 0 | 4 | 0 | 0 | 4 | 0 | 0 | 0 | 0 | 4 | 0 | 0 | 4 | 0 | 0 | 0 | 0 | 4 | 0 | 0 | 4 | 0 | 0 | 0 | 0
5 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 5 | 0 | 0 | 0 | 0
6 | 0 | 0 | 6 | 0 | 0 | 0 | 0 | 6 | 0 | 0 | 6 | 0 | 0 | 0 | 0 | 6 | 0 | 0 | 6 | 0 | 0 | 0 | 0 | 6 | 0 | 0 | 6 | 0 | 0 | 0 | 0 | 6 | 0 | 0 | 6 | 0 | 0 | 0 | 0
7 | 0 | 0 | 7 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 7 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 7 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 7 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 7 | 0 | 0 | 0 | 0
8 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 8 | 0 | 0 | 0 | 0
9 | 0 | 0 | 9 | 0 | 0 | 0 | 0 | 9 | 0 | 0 | 9 | 0 | 0 | 0 | 0 | 9 | 0 | 0 | 9 | 0 | 0 | 0 | 0 | 9 | 0 | 0 | 9 | 0 | 0 | 0 | 0 | 9 | 0 | 0 | 9 | 0 | 0 | 0 | 0
10 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 10 | 0 | 0 | 0 | 0
11 | 0 | 0 | 11 | 0 | 0 | 0 | 0 | 11 | 0 | 0 | 11 | 0 | 0 | 0 | 0 | 11 | 0 | 0 | 11 | 0 | 0 | 0 | 0 | 11 | 0 | 0 | 11 | 0 | 0 | 0 | 0 | 11 | 0 | 0 | 11 | 0 | 0 | 0 | 0
12 | 0 | 0 | 12 | 0 | 0 | 0 | 0 | 12 | 0 | 0 | 12 | 0 | 0 | 0 | 0 | 12 | 0 | 0 | 12 | 0 | 0 | 0 | 0 | 12 | 0 | 0 | 12 | 0 | 0 | 0 | 0 | 12 | 0 | 0 | 12 | 0 | 0 | 0 | 0
13 | 0 | 0 | 13 | 0 | 0 | 0 | 0 | 13 | 0 | 0 | 13 | 0 | 0 | 0 | 0 | 13 | 0 | 0 | 13 | 0 | 0 | 0 | 0 | 13 | 0 | 0 | 13 | 0 | 0 | 0 | 0 | 13 | 0 | 0 | 13 | 0 | 0 | 0 | 0
14 | 0 | 0 | 14 | 0 | 0 | 0 | 0 | 14 | 0 | 0 | 14 | 0 | 0 | 0 | 0 | 14 | 0 | 0 | 14 | 0 | 0 | 0 | 0 | 14 | 0 | 0 | 14 | 0 | 0 | 0 | 0 | 14 | 0 | 0 | 14 | 0 | 0 | 0 | 0
15 | 525045.9196 | 525045.9196 | 15 | 491122.4164 | 491122.4164 | -33923.5031 | -33923.5031 | 15 | 505190.924 | 505190.924 | 15 | 470811.1711 | 470811.1711 | -34379.7528 | -34379.7528 | 15 | 509920.8422 | 509920.8422 | 15 | 469423.871 | 469423.871 | -40496.9712 | -40496.9712 | 15 | 516768.801 | 516768.801 | 15 | 466881.0975 | 466881.0975 | -49887.7036 | -49887.7036 | 15 | 480735.2608 | 480735.2608 | 15 | 432948.4393 | 432948.4393 | -47786.8215 | -47786.8215
16 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 16 | 0 | 0 | 0 | 0
17 | 0 | 0 | 17 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 17 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 17 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 17 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 17 | 0 | 0 | 0 | 0
18 | 0 | 0 | 18 | 0 | 0 | 0 | 0 | 18 | 0 | 0 | 18 | 0 | 0 | 0 | 0 | 18 | 0 | 0 | 18 | 0 | 0 | 0 | 0 | 18 | 0 | 0 | 18 | 0 | 0 | 0 | 0 | 18 | 0 | 0 | 18 | 0 | 0 | 0 | 0
19 | 0 | 0 | 19 | 0 | 0 | 0 | 0 | 19 | 0 | 0 | 19 | 0 | 0 | 0 | 0 | 19 | 0 | 0 | 19 | 0 | 0 | 0 | 0 | 19 | 0 | 0 | 19 | 0 | 0 | 0 | 0 | 19 | 0 | 0 | 19 | 0 | 0 | 0 | 0
20 | 0 | 0 | 20 | 0 | 0 | 0 | 0 | 20 | 0 | 0 | 20 | 0 | 0 | 0 | 0 | 20 | 0 | 0 | 20 | 0 | 0 | 0 | 0 | 20 | 0 | 0 | 20 | 0 | 0 | 0 | 0 | 20 | 0 | 0 | 20 | 0 | 0 | 0 | 0
21 | 0 | 0 | 21 | 0 | 0 | 0 | 0 | 21 | 0 | 0 | 21 | 0 | 0 | 0 | 0 | 21 | 0 | 0 | 21 | 0 | 0 | 0 | 0 | 21 | 0 | 0 | 21 | 0 | 0 | 0 | 0 | 21 | 0 | 0 | 21 | 0 | 0 | 0 | 0
22 | 0 | 0 | 22 | 0 | 0 | 0 | 0 | 22 | 0 | 0 | 22 | 0 | 0 | 0 | 0 | 22 | 0 | 0 | 22 | 0 | 0 | 0 | 0 | 22 | 0 | 0 | 22 | 0 | 0 | 0 | 0 | 22 | 0 | 0 | 22 | 0 | 0 | 0 | 0
23 | 0 | 0 | 23 | 0 | 0 | 0 | 0 | 23 | 0 | 0 | 23 | 0 | 0 | 0 | 0 | 23 | 0 | 0 | 23 | 0 | 0 | 0 | 0 | 23 | 0 | 0 | 23 | 0 | 0 | 0 | 0 | 23 | 0 | 0 | 23 | 0 | 0 | 0 | 0
24 | 0 | 0 | 24 | 0 | 0 | 0 | 0 | 24 | 0 | 0 | 24 | 0 | 0 | 0 | 0 | 24 | 0 | 0 | 24 | 0 | 0 | 0 | 0 | 24 | 0 | 0 | 24 | 0 | 0 | 0 | 0 | 24 | 0 | 0 | 24 | 0 | 0 | 0 | 0
25 | 0 | 0 | 25 | 0 | 0 | 0 | 0 | 25 | 0 | 0 | 25 | 0 | 0 | 0 | 0 | 25 | 0 | 0 | 25 | 0 | 0 | 0 | 0 | 25 | 0 | 0 | 25 | 0 | 0 | 0 | 0 | 25 | 0 | 0 | 25 | 0 | 0 | 0 | 0
26 | 0 | 0 | 26 | 0 | 0 | 0 | 0 | 26 | 0 | 0 | 26 | 0 | 0 | 0 | 0 | 26 | 0 | 0 | 26 | 0 | 0 | 0 | 0 | 26 | 0 | 0 | 26 | 0 | 0 | 0 | 0 | 26 | 0 | 0 | 26 | 0 | 0 | 0 | 0
27 | 0 | 0 | 27 | 0 | 0 | 0 | 0 | 27 | 0 | 0 | 27 | 0 | 0 | 0 | 0 | 27 | 0 | 0 | 27 | 0 | 0 | 0 | 0 | 27 | 0 | 0 | 27 | 0 | 0 | 0 | 0 | 27 | 0 | 0 | 27 | 0 | 0 | 0 | 0
28 | 0 | 0 | 28 | 0 | 0 | 0 | 0 | 28 | 0 | 0 | 28 | 0 | 0 | 0 | 0 | 28 | 0 | 0 | 28 | 0 | 0 | 0 | 0 | 28 | 0 | 0 | 28 | 0 | 0 | 0 | 0 | 28 | 0 | 0 | 28 | 0 | 0 | 0 | 0
29 | 0 | 0 | 29 | 0 | 0 | 0 | 0 | 29 | 0 | 0 | 29 | 0 | 0 | 0 | 0 | 29 | 0 | 0 | 29 | 0 | 0 | 0 | 0 | 29 | 0 | 0 | 29 | 0 | 0 | 0 | 0 | 29 | 0 | 0 | 29 | 0 | 0 | 0 | 0
30 | 0 | 525045.9196 | 30 | 0 | 491122.4164 | 0 | -33923.5031 | 30 | 0 | 505190.924 | 30 | 0 | 470811.1711 | 0 | -34379.7528 | 30 | 0 | 509920.8422 | 30 | 0 | 469423.871 | 0 | -40496.9712 | 30 | 0 | 516768.801 | 30 | 0 | 466881.0975 | 0 | -49887.7036 | 30 | 0 | 480735.2608 | 30 | 0 | 432948.4393 | 0 | -47786.8215
31 | 0 | 0 | 31 | 0 | 0 |  | 0 | 31 | 0 | 0 | 31 | 0 | 0 |  | 0 | 31 | 0 | 0 | 31 | 0 | 0 |  | 0 | 31 | 0 | 0 | 31 | 0 | 0 |  | 0 | 31 | 0 | 0 | 31 | 0 | 0 |  | 0
32 | 0 | 0 | 32 | 0 | 0 |  | 0 | 32 | 0 | 0 | 32 | 0 | 0 |  | 0 | 32 | 0 | 0 | 32 | 0 | 0 |  | 0 | 32 | 0 | 0 | 32 | 0 | 0 |  | 0 | 32 | 0 | 0 | 32 | 0 | 0 |  | 0
33 | 0 | 0 | 33 | 0 | 0 |  | 0 | 33 | 0 | 0 | 33 | 0 | 0 |  | 0 | 33 | 0 | 0 | 33 | 0 | 0 |  | 0 | 33 | 0 | 0 | 33 | 0 | 0 |  | 0 | 33 | 0 | 0 | 33 | 0 | 0 |  | 0
34 | 0 | 0 | 34 | 0 | 0 |  | 0 | 34 | 0 | 0 | 34 | 0 | 0 |  | 0 | 34 | 0 | 0 | 34 | 0 | 0 |  | 0 | 34 | 0 | 0 | 34 | 0 | 0 |  | 0 | 34 | 0 | 0 | 34 | 0 | 0 |  | 0
35 | 0 | 0 | 35 | 0 | 0 |  | 0 | 35 | 0 | 0 | 35 | 0 | 0 |  | 0 | 35 | 0 | 0 | 35 | 0 | 0 |  | 0 | 35 | 0 | 0 | 35 | 0 | 0 |  | 0 | 35 | 0 | 0 | 35 | 0 | 0 |  | 0
36 | 0 | 0 | 36 | 0 | 0 |  | 0 | 36 | 0 | 0 | 36 | 0 | 0 |  | 0 | 36 | 0 | 0 | 36 | 0 | 0 |  | 0 | 36 | 0 | 0 | 36 | 0 | 0 |  | 0 | 36 | 0 | 0 | 36 | 0 | 0 |  | 0
37 | 0 | 0 | 37 | 0 | 0 |  | 0 | 37 | 0 | 0 | 37 | 0 | 0 |  | 0 | 37 | 0 | 0 | 37 | 0 | 0 |  | 0 | 37 | 0 | 0 | 37 | 0 | 0 |  | 0 | 37 | 0 | 0 | 37 | 0 | 0 |  | 0
38 | 0 | 0 | 38 | 0 | 0 |  | 0 | 38 | 0 | 0 | 38 | 0 | 0 |  | 0 | 38 | 0 | 0 | 38 | 0 | 0 |  | 0 | 38 | 0 | 0 | 38 | 0 | 0 |  | 0 | 38 | 0 | 0 | 38 | 0 | 0 |  | 0
39 | 0 | 0 | 39 | 0 | 0 |  | 0 | 39 | 0 | 0 | 39 | 0 | 0 |  | 0 | 39 | 0 | 0 | 39 | 0 | 0 |  | 0 | 39 | 0 | 0 | 39 | 0 | 0 |  | 0 | 39 | 0 | 0 | 39 | 0 | 0 |  | 0
40 | 0 | 0 | 40 | 0 | 0 |  | 11307.8344 | 40 | 0 | 0 | 40 | 0 | 0 |  | 11459.9176 | 40 | 0 | 0 | 40 | 0 | 0 |  | 13498.9904 | 40 | 0 | 0 | 40 | 0 | 0 |  | 16629.2345 | 40 | 0 | 0 | 40 | 0 | 0 |  | 15928.9405
Residual Year 30 |  | 0 | Residual Year 30 |  | 0 |  |  | Residual Year 30 |  | 0 | Residual Year 30 |  | 0 |  |  | Residual Year 30 |  | 0 | Residual Year 30 |  | 0 |  |  | Residual Year 30 |  | 0 | Residual Year 30 |  | 0 |  |  | Residual Year 30 |  | 0 | Residual Year 30 |  | 0
Residual Year 40 |  | -175015.3065 | Residual Year 40 |  | -163707.4721 |  |  | Residual Year 40 |  | -168396.9747 | Residual Year 40 |  | -156937.057 |  |  | Residual Year 40 |  | -169973.6141 | Residual Year 40 |  | -156474.6237 |  |  | Residual Year 40 |  | -172256.267 | Residual Year 40 |  | -155627.0325 |  |  | Residual Year 40 |  | -160245.0869 | Residual Year 40 |  | -144316.1464
| 525045.9196 |  |  | 491122.4164 |  |  |  |  | 505190.924 |  |  | 470811.1711 |  |  |  |  | 509920.8422 |  |  | 469423.871 |  |  |  |  | 516768.801 |  |  | 466881.0975 |  |  |  |  | 480735.2608 |  |  | 432948.4393

## HVAC Small Office Proto
90.1 Cost Effectiveness - Cost Estimate - HVAC - Small Office | [7 empty] | Small Office
[8 empty] | 3 | 4 | [8 empty] | 5 | 6 | [8 empty] | 7 | 8 | [8 empty] | 9 | 10 | [8 empty] | 11 | 12
[7 empty] | City-year parameter column |  |  | I | I | I | I | J | J | J | J |  |  | S | S | S | S | T | T | T | T |  |  | AC | AC | AC | AC | AD | AD | AD | AD |  |  | AM | AM | AM | AM | AN | AN | AN | AN |  |  | AW | AW | AW | AW | AX | AX | AX | AX
[7 empty] | Parameter range lookup extension |  |  | _2007Par | _2007Par | _2007Par | _2007Par | _2010Par | _2010Par | _2010Par | _2010Par |  |  | _2007Par | _2007Par | _2007Par | _2007Par | _2010Par | _2010Par | _2010Par | _2010Par |  |  | _2007Par | _2007Par | _2007Par | _2007Par | _2010Par | _2010Par | _2010Par | _2010Par |  |  | _2007Par | _2007Par | _2007Par | _2007Par | _2010Par | _2010Par | _2010Par | _2010Par |  |  | _2007Par | _2007Par | _2007Par | _2007Par | _2010Par | _2010Par | _2010Par | _2010Par
[7 empty] | Cost range lookup extension |  |  | _2007Costs | _2007Costs | _2007Costs | _2007Costs | _2010Costs | _2010Costs | _2010Costs | _2010Costs |  |  | _2007Costs | _2007Costs | _2007Costs | _2007Costs | _2010Costs | _2010Costs | _2010Costs | _2010Costs |  |  | _2007Costs | _2007Costs | _2007Costs | _2007Costs | _2010Costs | _2010Costs | _2010Costs | _2010Costs |  |  | _2007Costs | _2007Costs | _2007Costs | _2007Costs | _2010Costs | _2010Costs | _2010Costs | _2010Costs |  |  | _2007Costs | _2007Costs | _2007Costs | _2007Costs | _2010Costs | _2010Costs | _2010Costs | _2010Costs
[7 empty] | Cost range column index values |  |  | 9 | 10 | 11 | 20 | 10 | 11 | 12 | 22 |  |  | 9 | 10 | 11 | 20 | 10 | 11 | 12 | 22 |  |  | 9 | 10 | 11 | 20 | 10 | 11 | 12 | 22 |  |  | 9 | 10 | 11 | 20 | 10 | 11 | 12 | 22 |  |  | 9 | 10 | 11 | 20 | 10 | 11 | 12 | 22
[8 empty] | Climate Zone 1 | 2A | Base Code | 2019 |  |  | Target Code | 2022 |  |  | Climate Zone 2 | 3A | Base Code | 2019 |  |  | Target Code | 2022 |  |  | Climate Zone 3 | 3B | Base Code | 2019 |  |  | Target Code | 2022 |  |  | Climate Zone 4 | 4A | Base Code | 2019 |  |  | Target Code | 2022 |  |  | Climate Zone 5 | 5A | Base Code | 2019 |  |  | Target Code | 2022 |  |  | First cost difference |  | 2019 | vs | 2022
Costs row marked x, other rows not marked | [7 empty] | Base | Target | [8 empty] | Base | Target | [8 empty] | Base | Target | [8 empty] | Base | Target | [8 empty] | Base | Target | [8 empty] | Total new construction (added cost)
| Addendum or general | Key Word | Description |  |  | Parameter | Lookup Value in HVAC Data, Current_HVAC_Data | Prototype | Prototype | Total New | Maintenance | Replacement Life | Total | Total New | Maintenance | Replacement Life | Total | Prototype | Prototype | Total New | Maintenance | Replacement Life | Total | Total New | Maintenance | Replacement Life | Total | Prototype | Prototype | Total New | Maintenance | Replacement Life | Total | Total New | Maintenance | Replacement Life | Total | Prototype | Prototype | Total New | Maintenance | Replacement Life | Total | Total New | Maintenance | Replacement Life | Total | Prototype | Prototype | Total New | Maintenance | Replacement Life | Total | Total New | Maintenance | Replacement Life | Total | 2A | 3A | 3B | 4A | 5A
| load change | [6 empty] | Data | Data | Construction |  |  | Replacement Cost | Construction |  |  | Replacement Cost | Data | Data | Construction |  |  | Replacement Cost | Construction |  |  | Replacement Cost | Data | Data | Construction |  |  | Replacement Cost | Construction |  |  | Replacement Cost | Data | Data | Construction |  |  | Replacement Cost | Construction |  |  | Replacement Cost | Data | Data | Construction |  |  | Replacement Cost | Construction |  |  | Replacement Cost
| HVAC System - general load change |  | Prototype Data is set to a minimum of 1.5 tons as no incremental cost benefit below minimum size.
x |  | Heat_Pump |  | PSZ-AC:1 | CAVDX | PSZ-AC:1 Cooling Capacity [ton] | US_SO_PSZ-AC:1 Cooling Capacity [ton] | 1.9478 | 1.9013 | 5423.6982 | 0 | 15 | 6626.8146 | 5312.2059 | 0 | 15 | 6493.7731 | 1.848 | 1.8009 | 5184.3567 | 0 | 15 | 6341.2133 | 5071.5627 | 0 | 15 | 6206.6184 | 1.7121 | 1.6619 | 4858.6783 | 0 | 15 | 5952.588 | 4738.4692 | 0 | 15 | 5809.1448 | 1.7143 | 1.6663 | 4863.8921 | 0 | 15 | 5958.8094 | 4748.9716 | 0 | 15 | 5821.6772 | 1.599 | 1.5518 | 4587.7204 | 0 | 15 | 5629.2594 | 4474.5924 | 0 | 15 | 5494.2661 | -111.4923 | -112.7941 | -120.2092 | -114.9205 | -113.128
x |  | Heat_Pump |  | PSZ-AC:2 | CAVDX | PSZ-AC:2 Cooling Capacity [ton] | US_SO_PSZ-AC:2 Cooling Capacity [ton] | 2.0037 | 1.9189 | 5555.6678 | 0 | 15 | 6784.8782 | 5354.3384 | 0 | 15 | 6544.0489 | 1.8169 | 1.7245 | 5109.9126 | 0 | 15 | 6252.3807 | 4888.4069 | 0 | 15 | 5988.0625 | 1.8117 | 1.7264 | 5097.4474 | 0 | 15 | 6237.5061 | 4892.9391 | 0 | 15 | 5993.4706 | 1.7795 | 1.662 | 5020.2771 | 0 | 15 | 6145.4205 | 4738.5305 | 0 | 15 | 5809.218 | 1.6576 | 1.5536 | 4728.1507 | 0 | 15 | 5796.8321 | 4478.8247 | 0 | 15 | 5499.3165 | -201.3294 | -221.5057 | -204.5083 | -281.7466 | -249.326
x |  | Heat_Pump |  | PSZ-AC:3 | CAVDX | PSZ-AC:3 Cooling Capacity [ton] | US_SO_PSZ-AC:3 Cooling Capacity [ton] | 1.5 | 1.5 | 4350.348 | 0 | 15 | 5346.0079 | 4350.348 | 0 | 15 | 5346.0079 | 1.5 | 1.5 | 4350.348 | 0 | 15 | 5346.0079 | 4350.348 | 0 | 15 | 5346.0079 | 1.5 | 1.5 | 4350.348 | 0 | 15 | 5346.0079 | 4350.348 | 0 | 15 | 5346.0079 | 1.5 | 1.5 | 4350.348 | 0 | 15 | 5346.0079 | 4350.348 | 0 | 15 | 5346.0079 | 1.5 | 1.5 | 4350.348 | 0 | 15 | 5346.0079 | 4350.348 | 0 | 15 | 5346.0079 | 0 | 0 | 0 | 0 | 0
x |  | Heat_Pump |  | PSZ-AC:4 | CAVDX | PSZ-AC:4 Cooling Capacity [ton] | US_SO_PSZ-AC:4 Cooling Capacity [ton] | 1.9331 | 1.8491 | 5388.422 | 0 | 15 | 6584.7202 | 5187.0965 | 0 | 15 | 6344.4826 | 1.7858 | 1.6931 | 5035.414 | 0 | 15 | 6163.483 | 4813.0836 | 0 | 15 | 5898.1807 | 1.789 | 1.7062 | 5043.0677 | 0 | 15 | 6172.616 | 4844.6592 | 0 | 15 | 5935.8592 | 1.6317 | 1.5177 | 4666.0492 | 0 | 15 | 5722.7276 | 4392.8763 | 0 | 15 | 5396.756 | 1.5 | 1.5 | 4350.348 | 0 | 15 | 5346.0079 | 4350.348 | 0 | 15 | 5346.0079 | -201.3255 | -222.3304 | -198.4085 | -273.1729 | 0
x |  | Heat_Pump |  | PSZ-AC:5 | CAVDX | PSZ-AC:5 Cooling Capacity [ton] | US_SO_PSZ-AC:5 Cooling Capacity [ton] | 1.5698 | 1.5158 | 4517.7608 | 0 | 15 | 5545.7781 | 4388.1874 | 0 | 15 | 5391.1608 | 1.5 | 1.5 | 4350.348 | 0 | 15 | 5346.0079 | 4350.348 | 0 | 15 | 5346.0079 | 1.5252 | 1.5 | 4410.6508 | 0 | 15 | 5417.9659 | 4350.348 | 0 | 15 | 5346.0079 | 1.5 | 1.5 | 4350.348 | 0 | 15 | 5346.0079 | 4350.348 | 0 | 15 | 5346.0079 | 1.5 | 1.5 | 4350.348 | 0 | 15 | 5346.0079 | 4350.348 | 0 | 15 | 5346.0079 | -129.5735 | 0 | -60.3027 | 0 | 0
90.1-16bo furnace efficiency
|  | Furnace_eff | 5 units |  |  | Furnace heating capacity [Btuh] | US_SO_Furnace heating capacity [Btuh] | 5 | 5 | 22906.7107 | 0 | 75 | 27228.8465 | 23657.3571 | 0 | 75 | 28054.5575 | 5 | 5 | 22906.7107 | 0 | 75 | 27228.8465 | 23657.3571 | 0 | 75 | 28054.5575 | 5 | 5 | 22906.7107 | 0 | 75 | 27228.8465 | 23657.3571 | 0 | 75 | 28054.5575 | 5 | 5 | 22906.7107 | 0 | 75 | 27228.8465 | 23657.3571 | 0 | 75 | 28054.5575 | 5 | 5 | 22906.7107 | 0 | 75 | 27228.8465 | 23657.3571 | 0 | 75 | 28054.5575
| 90.1-16g occ standby controls | occ_standby | 5 conditioned zones |  |  |  |  | 0 | 5 | 0 | 0 | 0 | 0 | 166.698 | 0 | 75 | 292.5352 | 0 | 5 | 0 | 0 | 0 | 0 | 166.698 | 0 | 75 | 292.5352 | 0 | 5 | 0 | 0 | 0 | 0 | 166.698 | 0 | 75 | 292.5352 | 0 | 5 | 0 | 0 | 0 | 0 | 166.698 | 0 | 75 | 292.5352 | 0 | 5 | 0 | 0 | 0 | 0 | 166.698 | 0 | 75 | 292.5352
X | HVAC System - general load change | Air Distribution | curve fit from Solarc cost calculations - described in HVAC Costs Comp. Material, labor, and project cost adjustments applied in this worksheet. |  |  | Sum of PSZ-AC:1 Supply Flow Rate [cfm] to PSZ-AC:5 Supply Flow Rate [cfm] |  | 3157.1312 | 3051.1872 | 51882.3805 | 0 | 30 | 82845.7908 | 51370.2603 | 0 | 30 | 81993.54 | 3072.376 | 2924.0544 | 51472.6844 | 0 | 30 | 82163.9901 | 50755.7161 | 0 | 30 | 80970.839 | 3602.096 | 3474.9632 | 54033.2852 | 0 | 30 | 86425.2441 | 53418.741 | 0 | 30 | 85402.5432 | 2924.0544 | 2733.3552 | 50755.7161 | 0 | 30 | 80970.839 | 49833.8999 | 0 | 30 | 79436.7876 | 2860.488 | 2712.1664 | 50448.4441 | 0 | 30 | 80459.4885 | 49731.4758 | 0 | 30 | 79266.3374 | -512.1202 | -716.9682 | -614.5442 | -921.8163 | -716.9682
|  |  | Material y = 0.2902x + 4511.3 R² = 0.8963 |  |  | PSZ-AC:1 Supply Flow Rate [cfm] | US_SO_PSZ-AC:1 Supply Flow Rate [cfm] | 635.664 | 614.4752 | [8 empty] | 656.8528 | 635.664 | [8 empty] | 741.608 | 720.4192 | [8 empty] | 593.2864 | 572.0976 | [8 empty] | 593.2864 | 572.0976
|  |  | Labor y = 1.5764x + 9922.5 R² = 0.9473 |  |  | PSZ-AC:2 Supply Flow Rate [cfm] | US_SO_PSZ-AC:2 Supply Flow Rate [cfm] | 699.2304 | 678.0416 | [8 empty] | 678.0416 | 635.664 | [8 empty] | 805.1744 | 783.9856 | [8 empty] | 656.8528 | 614.4752 | [8 empty] | 656.8528 | 614.4752
[6 empty] | PSZ-AC:3 Supply Flow Rate [cfm] | US_SO_PSZ-AC:3 Supply Flow Rate [cfm] | 529.72 | 529.72 | [8 empty] | 508.5312 | 487.3424 | [8 empty] | 572.0976 | 550.9088 | [8 empty] | 508.5312 | 466.1536 | [8 empty] | 487.3424 | 466.1536
[6 empty] | PSZ-AC:4 Supply Flow Rate [cfm] | US_SO_PSZ-AC:4 Supply Flow Rate [cfm] | 678.0416 | 635.664 | [8 empty] | 656.8528 | 614.4752 | [8 empty] | 805.1744 | 762.7968 | [8 empty] | 593.2864 | 550.9088 | [8 empty] | 550.9088 | 508.5312
[6 empty] | PSZ-AC:5 Supply Flow Rate [cfm] | US_SO_PSZ-AC:5 Supply Flow Rate [cfm] | 614.4752 | 593.2864 | [8 empty] | 572.0976 | 550.9088 | [8 empty] | 678.0416 | 656.8528 | [8 empty] | 572.0976 | 529.72 | [8 empty] | 572.0976 | 550.9088
[8 empty] | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8
[8 empty] | 593.2864 3: 77118.2774; 593.2864 6: 113733.9897; 593.2864 7: 75962.4365 |  | 112113.0132 |  |  | 75503.0638 |  |  | 111613.0829 | 74229.4654 |  |  | 109755.7164 |  |  | 77793.4773 |  |  | 115551.928 | 76595.5044 |  |  | 113833.0336 |  |  | 74006.6306 |  |  | 109489.8123 | 72414.9743 |  |  | 107156.4545 |  |  | 72815.3592 |  |  | 107923.6036 | 71735.937 |  |  | 106297.9436
[8 empty] | 593.2864 2: 113733.9897; 593.2864 6: 112113.0132 |  |  |  | 111613.0829 |  |  |  | 109755.7164 | [5 empty] | 115551.928 |  |  |  | 113833.0336 | [5 empty] | 109489.8123 |  |  |  | 107156.4545 | [5 empty] | 107923.6036 |  |  |  | 106297.9436

## HVAC Large Office Proto
90.1 Cost Effectiveness - Cost Estimate - HVAC - Large Office | [5 empty] | US National |  | Large Office
[6 empty] | CAV_BAS Preheat Coil |  |  |  | $AP | $AQ | $AR | $BA | $BK | $BL | $BM | $BW |  |  | $AP | $AQ | $AR | $BA | $BK | $BL | $BM | $BW |  |  | $AP | $AQ | $AR | $BA | $BK | $BL | $BM | $BW |  |  | $AP | $AQ | $AR | $BA | $BK | $BL | $BM | $BW |  |  | $AP | $AQ | $AR | $BA | $BK | $BL | $BM | $BW | Find Row
|  |  | YES |  |  | VAV_BOT WITH REHEAT Preheat Coil |  | 3 | 4 | [8 empty] | 5 | 6 | [8 empty] | 7 | 8 | [8 empty] | 9 | 10 | [8 empty] | 11 | 12
[6 empty] | VAV_MID WITH REHEAT Preheat Coil | City-year parameter column |  |  | I | I | I | I | J | J | J | J |  |  | S | S | S | S | T | T | T | T |  |  | AC | AC | AC | AC | AD | AD | AD | AD |  |  | AM | AM | AM | AM | AN | AN | AN | AN |  |  | AW | AW | AW | AW | AX | AX | AX | AX
[6 empty] | VAV_MID WITH REHEAT Preheat Coil | Parameter range lookup extension |  |  | _2007Par | _2007Par | _2007Par | _2007Par | _2010Par | _2010Par | _2010Par | _2010Par |  |  | _2007Par | _2007Par | _2007Par | _2007Par | _2010Par | _2010Par | _2010Par | _2010Par |  |  | _2007Par | _2007Par | _2007Par | _2007Par | _2010Par | _2010Par | _2010Par | _2010Par |  |  | _2007Par | _2007Par | _2007Par | _2007Par | _2010Par | _2010Par | _2010Par | _2010Par |  |  | _2007Par | _2007Par | _2007Par | _2007Par | _2010Par | _2010Par | _2010Par | _2010Par
[7 empty] | Cost range lookup extension |  |  | _2007Costs | _2007Costs | _2007Costs | _2007Costs | _2010Costs | _2010Costs | _2010Costs | _2010Costs |  |  | _2007Costs | _2007Costs | _2007Costs | _2007Costs | _2010Costs | _2010Costs | _2010Costs | _2010Costs |  |  | _2007Costs | _2007Costs | _2007Costs | _2007Costs | _2010Costs | _2010Costs | _2010Costs | _2010Costs |  |  | _2007Costs | _2007Costs | _2007Costs | _2007Costs | _2010Costs | _2010Costs | _2010Costs | _2010Costs |  |  | _2007Costs | _2007Costs | _2007Costs | _2007Costs | _2010Costs | _2010Costs | _2010Costs | _2010Costs
[7 empty] | Cost range column index values |  |  | 9 | 10 | 11 | 20 | 10 | 11 | 12 | 22 |  |  | 9 | 10 | 11 | 20 | 10 | 11 | 12 | 22 |  |  | 9 | 10 | 11 | 20 | 10 | 11 | 12 | 22 |  |  | 9 | 10 | 11 | 20 | 10 | 11 | 12 | 22 |  |  | 9 | 10 | 11 | 20 | 10 | 11 | 12 | 22
[8 empty] | Climate Zone 1 | 2A | Base Code | 2019 |  |  | Target Code | 2022 |  |  | Climate Zone 2 | 3A | Base Code | 2019 |  |  | Target Code | 2022 |  |  | Climate Zone 3 | 3B | Base Code | 2019 |  |  | Target Code | 2022 |  |  | Climate Zone 4 | 4A | Base Code | 2019 |  |  | Target Code | 2022 |  |  | Climate Zone 5 | 5A | Base Code | 2019 |  |  | Target Code | 2022 |  |  |  | Z1 v Z2 |  |  |  |  | First cost difference |  | 2019 | vs | 2022
Costs row marked x, other rows not marked | [7 empty] | Base Code | Target Code | [8 empty] | 2019 | 2022 | [8 empty] | 2019 | 2022 | [8 empty] | 2019 | 2022 | [8 empty] | 2019 | 2022 | [9 empty] | First Only |  |  |  |  | Total new construction (added cost)
| Addendum or general | Key Word | Description | Model | Type | Parameter | Lookup Value in HVAC Data, Current_HVAC_Data | Prototype | Prototype | Total New | Maintenance | Replacement Life | Total | Total New | Maintenance | Replacement Life | Total | Prototype | Prototype | Total New | Maintenance | Replacement Life | Total | Total New | Maintenance | Replacement Life | Total | Prototype | Prototype | Total New | Maintenance | Replacement Life | Total | Total New | Maintenance | Replacement Life | Total | Prototype | Prototype | Total New | Maintenance | Replacement Life | Total | Total New | Maintenance | Replacement Life | Total | Prototype | Prototype | Total New | Maintenance | Replacement Life | Total | Total New | Maintenance | Replacement Life | Total |  | 2013 | 2016 |  | 3dT | 5dT | 2A | 3A | 3B | 4A | 5A
| load change |  |  | Object |  |  |  | Data | Data | Construction |  |  | Replacement Cost | Construction |  |  | Replacement Cost | Data | Data | Construction |  |  | Replacement Cost | Construction |  |  | Replacement Cost | Data | Data | Construction |  |  | Replacement Cost | Construction |  |  | Replacement Cost | Data | Data | Construction |  |  | Replacement Cost | Construction |  |  | Replacement Cost | Data | Data | Construction |  |  | Replacement Cost | Construction |  |  | Replacement Cost
| HVAC System - General load change |  | lookup cost based on supply airflow, cfm
x |  | VAV_AHU |  | VAV_BOT | VAVCHW | VAV_BOT WITH REHEAT Supply Flow Rate [cfm] | US_LO_VAV_BOT WITH REHEAT Supply Flow Rate [cfm] | 18455.4448 | 17925.7248 | 51566.692 | 0 | 15 | 63324.3615 | 50893.8823 | 0 | 15 | 62374.0963 | 18963.976 | 18413.0672 | 52212.5893 | 0 | 15 | 64236.616 | 51512.8672 | 0 | 15 | 63248.3402 | 21633.7648 | 21040.4784 | 57811.1186 | 0 | 15 | 71336.405 | 56255.914 | 0 | 15 | 69433.0888 | 19430.1296 | 18858.032 | 52804.6619 | 0 | 15 | 65072.8494 | 52078.0274 | 0 | 15 | 64046.563 | 19514.8848 | 18942.7872 | 52912.3115 | 0 | 15 | 65224.8918 | 52185.677 | 0 | 15 | 64198.6054 | [6 empty] | -672.8097 | -699.7221 | -1555.2046 | -726.6345 | -726.6345
x |  | Multiplier for MID systems: | 10 | VAV_MID (Asjusted for floor multiplier from below) | VAVCHW | VAV_MID WITH REHEAT Supply Flow Rate [cfm] |  |  |  | 498093.1303 | 0 | 15 | 608422.6884 | 491634.157 | 0 | 15 | 599300.1428 |  |  | 505467.1248 | 0 | 15 | 618837.5946 | 498712.1152 | 0 | 15 | 609296.9323 |  |  | 541063.99 | 0 | 15 | 668024.3391 | 530603.2959 | 0 | 15 | 654339.5012 |  |  | 512841.1193 | 0 | 15 | 629252.5008 | 505870.8107 | 0 | 15 | 619407.7537 |  |  | 511630.0618 | 0 | 15 | 627542.0235 | 504605.9284 | 0 | 15 | 617621.2552 |  | -7373.9945 | -13832.9678 |  |  |  | -6458.9733 | -6755.0096 | -10460.6941 | -6970.3087 | -7024.1335
|  | VAV_AHU |  | VAV_MID | VAVCHW | VAV_MID WITH REHEAT Supply Flow Rate [cfm] | US_LO_VAV_MID WITH REHEAT Supply Flow Rate [cfm] | 17071.8162 | 16563.285 | 49809.313 | 0 | 15 | 60842.2688 | 49163.4157 | 0 | 15 | 59930.0143 | 17652.3893 | 17120.5504 | 50546.7125 | 0 | 15 | 61883.7595 | 49871.2115 | 0 | 15 | 60929.6932 | 20220.4719 | 19631.4232 | 54106.399 | 0 | 15 | 66802.4339 | 53060.3296 | 0 | 15 | 65433.9501 | 18232.9624 | 17684.1725 | 51284.1119 | 0 | 15 | 62925.2501 | 50587.0811 | 0 | 15 | 61940.7754 | 18137.6128 | 17584.5851 | 51163.0062 | 0 | 15 | 62754.2024 | 50460.5928 | 0 | 15 | 61762.1255 |  | -737.3995 | -1383.2968
x |  | VAV_AHU |  | VAV_TOP | VAVCHW | VAV_TOP WITH REHEAT Supply Flow Rate [cfm] | US_LO_VAV_TOP WITH REHEAT Supply Flow Rate [cfm] | 18858.032 | 18413.0672 | 52078.0274 | 0 | 15 | 64046.563 | 51512.8672 | 0 | 15 | 63248.3402 | 19451.3184 | 18985.1648 | 52831.5743 | 0 | 15 | 65110.86 | 52239.5017 | 0 | 15 | 64274.6266 | 22756.7712 | 22248.24 | 60754.8988 | 0 | 15 | 74939.1106 | 59421.8663 | 0 | 15 | 73307.6967 | 20086.9824 | 19578.4512 | 53756.478 | 0 | 15 | 66374.1878 | 52993.0486 | 0 | 15 | 65338.9236 | 20192.9264 | 19684.3952 | 54034.1931 | 0 | 15 | 66714.0657 | 53127.6106 | 0 | 15 | 65528.9766 |  | -753.5469 | -1318.707 |  |  |  | -565.1602 | -592.0726 | -1333.0325 | -763.4293 | -906.5825
0 | 90.1-10au | VAV_AHU | If PH coil = NO | VAV_BOT | VAVCHW | VAV_BOT WITH REHEAT Preheat Coil | US_LO_VAV_BOT WITH REHEAT Preheat Coil | N/A | #N/A | 0 | 0 | 15 | 0 | #N/A | 0 | 15 | #N/A | N/A | #N/A | 0 | 0 | 15 | 0 | #N/A | 0 | 15 | #N/A | N/A | #N/A | 0 | 0 | 15 | 0 | #N/A | 0 | 15 | #N/A | N/A | #N/A | 0 | 0 | 15 | 0 | #N/A | 0 | 15 | #N/A | N/A | #N/A | 0 | 0 | 15 | 0 | #N/A | 0 | 15 | #N/A |  | 0 | #N/A
0 |  | VAV_AHU | increase | VAV_MID | VAVCHW | VAV_MID WITH REHEAT Preheat Coil | US_LO_VAV_MID WITH REHEAT Preheat Coil | N/A | -999 | 0 | 0 | 15 | 0 | 0 | 0 | 15 | 0 | N/A | -999 | 0 | 0 | 15 | 0 | 0 | 0 | 15 | 0 | N/A | -999 | 0 | 0 | 15 | 0 | 0 | 0 | 15 | 0 | N/A | YES | 0 | 0 | 15 | 0 | 0 | 0 | 15 | 0 | N/A | -999 | 0 | 0 | 15 | 0 | 0 | 0 | 15 | 0 |  | 0 | 0
|  | VAV_AHU | duct cost by | VAV_MID | VAVCHW | CAV_BAS Preheat Coil | US_LO_CAV_BAS Preheat Coil | N/A | -999 | 0 | 0 | 15 | 0 | 0 | 0 | 15 | 0 | N/A | -999 | 0 | 0 | 15 | 0 | 0 | 0 | 15 | 0 | N/A | -999 | 0 | 0 | 15 | 0 | 0 | 0 | 15 | 0 | N/A | NO | 0 | 0 | 15 | 0 | 1391.1447 | 0 | 15 | 1703.3713 | N/A | -999 | 0 | 0 | 15 | 0 | 0 | 0 | 15 | 0 |  | 0 | 0
0 |  | VAV_AHU | 2.75% | VAV_TOP | VAVCHW | VAV_MID WITH REHEAT Preheat Coil | US_LO_VAV_MID WITH REHEAT Preheat Coil | N/A | -999 | 0 | 0 | 15 | 0 | 0 | 0 | 15 | 0 | N/A | -999 | 0 | 0 | 15 | 0 | 0 | 0 | 15 | 0 | N/A | -999 | 0 | 0 | 15 | 0 | 0 | 0 | 15 | 0 | N/A | NO | 0 | 0 | 15 | 0 | 1457.3088 | 0 | 15 | 1796.8204 | N/A | -999 | 0 | 0 | 15 | 0 | 0 | 0 | 15 | 0 |  | 0 | 0
2019 |  | CAV_AHU | lookup cost based on cooling tons | [55 empty] | 0 | 0
x |  | CAV_AHU |  | CAV_BAS | CAVCHW | CAV_BAS Supply Flow Rate [cfm] | US_LO_CAV_BAS Supply Flow Rate [cfm] | 11060.5536 | 10615.5888 | 36129.653 | 0 | 15 | 43966.9548 | 35373.2156 | 0 | 15 | 43025.6947 | 10891.0432 | 10424.8896 | 35841.4863 | 0 | 15 | 43608.3795 | 35049.0282 | 0 | 15 | 42622.2975 | 12289.504 | 11780.9728 | 38287.267 | 0 | 15 | 46644.7918 | 37354.3611 | 0 | 15 | 45490.8997 | 10657.9664 | 10213.0016 | 35445.2573 | 0 | 15 | 43115.3385 | 34688.8199 | 0 | 15 | 42174.0784 | 10848.6656 | 10382.512 | 35769.4447 | 0 | 15 | 43518.7357 | 34976.9865 | 0 | 15 | 42532.6537 |  | 288.1666 | -468.2708 |  |  |  | -756.4374 | -792.4582 | -932.9059 | -756.4374 | -792.4582
[59 empty] | 0 | 0
x | HVAC System - General load change | Air Distribution material y = 0.7091x + 503192 labor y = 3.2521x + 1.604E+06 | curve fit from Solarc cost calculations - described in HVAC Costs Comp. Material, labor, and project cost adjustments applied in this worksheet. | All systems |  | Sum of Supply Airflow (cfm) values for all 4 systems from above values |  | 133733.1114 | 129770.8058 | 6765565.892 | 0 | 30 | 10969079.8025 | 6725054.7554 | 0 | 30 | 10902233.3195 | 137568.2842 | 133425.8738 | 6804777.206 | 0 | 30 | 11033781.4786 | 6762424.6541 | 0 | 30 | 10963896.5191 | 157782.3994 | 153226.8074 | 7011448.9935 | 0 | 30 | 11374805.7823 | 6964872.0184 | 0 | 30 | 11297950.2002 | 141339.8906 | 137070.3474 | 6843338.6087 | 0 | 30 | 11097410.7512 | 6799686.2343 | 0 | 30 | 11025380.9847 | 141244.541 | 136932.6202 | 6842363.7418 | 0 | 30 | 11095802.146 | 6798278.0932 | 0 | 30 | 11023057.4439 |  | -39211.314 | -79722.4505 |  |  |  | -40511.1366 | -42352.5518 | -46576.9752 | -43652.3744 | -44085.6486
check differential of above | [8 empty] | -2.963% | -0.5988% | -40511.1366 | [7 empty] | -3.011% | -0.6224% | -42352.5518 | [7 empty] | -2.887% | -0.6643% | -46576.9752 | [7 empty] | -3.021% | -0.6379% | -43652.3744 | [7 empty] | -3.053% | -0.6443% | -44085.6486 | [7 empty] | 0.0002361 | 0.0062239
| 90.1-2016ap SAT reset only 0A, 1A, 2A, 3A MZ systems only <3000 cfm design OA is exempt; <10,000 for 2A | Material cost = 4E-07x2 + 0.0307x + 1618 Labor hours = 0.0054x + 3.6055 | lookup cost based on supply airflow, cfm new for 2019, thus base code = 0 costs
|  | SAT_reset_16ap |  | VAV_BOT | VAVCHW | VAV_BOT WITH REHEAT Supply Flow Rate [cfm] | US_LO_VAV_BOT WITH REHEAT Supply Flow Rate [cfm] | 18455.4448 | 17925.7248 | 0 | 0 |  | 0 | 5565.187 | 0 | 20 | 6295.4 | 18963.976 | 18413.0672 | 0 | 0 |  | 0 | 5623.0078 | 0 | 20 | 6363.5555 | 21633.7648 | 21040.4784 | 0 | 0 |  | 0 | 0 | 0 | 20 | 0 | 19430.1296 | 18858.032 | 0 | 0 |  | 0 | 0 | 0 | 20 | 0 | 19514.8848 | 18942.7872 | 0 | 0 |  | 0 | 0 | 0 | 20 | 0
|  | Multiplier for MID systems: | 10 | VAV_MID (Asjusted for floor multiplier from below) | VAVCHW | VAV_MID WITH REHEAT Supply Flow Rate [cfm] |  |  |  | 0 | 0 |  | 0 | 54058.6636 | 0 | 20 | 61074.1977 |  |  | 0 | 0 |  | 0 | 54706.1759 | 0 | 20 | 61838.5193 |  |  | 0 | 0 |  | 0 | 0 | 0 | 20 | 0 |  |  | 0 | 0 |  | 0 | 0 | 0 | 20 | 0 |  |  | 0 | 0 |  | 0 | 0 | 0 | 20 | 0
|  | SAT_reset_16ap |  | VAV_MID | VAVCHW | VAV_MID WITH REHEAT Supply Flow Rate [cfm] | US_LO_VAV_MID WITH REHEAT Supply Flow Rate [cfm] | 17071.8162 | 16563.285 | 0 | 0 |  | 0 | 5405.8664 | 0 | 20 | 6107.4198 | 17652.3893 | 17120.5504 | 0 | 0 |  | 0 | 5470.6176 | 0 | 20 | 6183.8519 | 20220.4719 | 19631.4232 | 0 | 0 |  | 0 | 0 | 0 | 20 | 0 | 18232.9624 | 17684.1725 | 0 | 0 |  | 0 | 0 | 0 | 20 | 0 | 18137.6128 | 17584.5851 | 0 | 0 |  | 0 | 0 | 0 | 20 | 0
|  | SAT_reset_16ap |  | VAV_TOP | VAVCHW | VAV_TOP WITH REHEAT Supply Flow Rate [cfm] | US_LO_VAV_TOP WITH REHEAT Supply Flow Rate [cfm] | 18858.032 | 18413.0672 | 0 | 0 |  | 0 | 5623.0078 | 0 | 20 | 6363.5555 | 19451.3184 | 18985.1648 | 0 | 0 |  | 0 | 5691.4438 | 0 | 20 | 6444.1795 | 22756.7712 | 22248.24 | 0 | 0 |  | 0 | 0 | 0 | 20 | 0 | 20086.9824 | 19578.4512 | 0 | 0 |  | 0 | 0 | 0 | 20 | 0 | 20192.9264 | 19684.3952 | 0 | 0 |  | 0 | 0 | 0 | 20 | 0
| 90.1-07bh | Supply_Air_Temp_Reset | apply cost if "Yes" Add test *IF(Base_Code = 2009,0,1) | single line lookup | 2010 ONLY | Only one parameter - same value for all VAV systems. Note that HVAC Data parameter values are [Yes, No] | [52 empty] | 0 | 0
Not in 2016 |  | Supply_Air_Temp_Reset |  | VAV_BOT | VAVCHW | Supply Air Temp. Reset Flag | US_LO_Supply Air Temp. Reset Flag | No | No |  |  |  |  | 0 | 0 | 0 | 0 | Yes | Yes |  |  |  |  | 18734 | 0 | 20 | 18734 | Yes | Yes |  |  |  | 1 | 18734 | 0 | 20 | 18734 | Yes | Yes |  |  |  |  | 18734 | 0 | 20 | 18734 | Yes | Yes |  |  |  |  | 18734 | 0 | 20 | 18734 |  | 0 | 0
Not in 2016 |  | VAV_AHU |  | VAV_MID (estimate based on 5 systems, not 1 as modeled, costs multiplied by 5. Modeled system is too large for real application. Row included to screen out Out of Range * 5 which gives a Value error) | VAVCHW | VAV_MID WITH REHEAT Supply Flow Rate [cfm] | [7 empty] | 0 | 0 | 0 | 0 | [6 empty] | 93670 | 0 | 20 | 93670 | [6 empty] | 468350 | 0 | 20 | 93670 | [6 empty] | 468350 | 0 | 20 | 93670 | [6 empty] | 468350 | 0 | 20 | 93670 |  | 0 | 0
|  | Supply_Air_Temp_Reset |  | VAV_MID | VAVCHW | Supply Air Temp. Reset Flag | US_LO_Supply Air Temp. Reset Flag | No | No |  |  |  |  | 0 | 0 | 0 | 0 | Yes | Yes |  |  |  |  | 18734 | 0 | 20 | 18734 | Yes | Yes |  |  |  |  | 93670 | 0 | 20 | 18734 | Yes | Yes |  |  |  |  | 93670 | 0 | 20 | 18734 | Yes | Yes |  |  |  |  | 93670 | 0 | 20 | 18734 |  | 0 | 0
Not in 2016 |  | Supply_Air_Temp_Reset |  | VAV_TOP | VAVCHW | Supply Air Temp. Reset Flag | US_LO_Supply Air Temp. Reset Flag | No | No |  |  |  |  | 0 | 0 | 0 | 0 | Yes | Yes |  |  |  |  | 18734 | 0 | 20 | 18734 | Yes | Yes |  |  |  |  | 18734 | 0 | 20 | 18734 | Yes | Yes |  |  |  |  | 18734 | 0 | 20 | 18734 | Yes | Yes |  |  |  |  | 18734 | 0 | 20 | 18734 |  | 0 | 0
Not in 2016 |  | Supply_Air_Temp_Reset | interior zone added HVAC duct etc. for large office only | VAV_MID and VAV_TOP (cost is for all five systems, and VAV_Top interior areas - see description) | VAVCHW | Supply Air Temp. Reset Flag | US_LO_Supply Air Temp. Reset Flag | No | No |  |  |  |  | 0 |  | 20 | 0 | Yes | Yes |  |  |  |  | 18734 |  | 20 | 18734 | Yes | Yes |  |  |  |  | 18734 |  | 20 | 18734 | Yes | Yes |  |  |  |  | 18734 |  | 20 | 18734 | Yes | Yes |  |  |  |  | 18734 |  | 20 | 18734 |  | 0 | 0
| 90.1-13 i requires ventilation optimization without exception for DCV | Vent_Optimize | apply cost if "Yes", cost value times number of perimeter zones | NOTE: EXTRACTING THE COSTS IN THE SECOND LINE, AND APPLYING THE YES/NO CONDITION IN THE FIRST LINE. Single line lookup range. |  | Note that HVAC Data parameter values are [Yes, No] | [52 empty] | 0 | 0
|  |  |  | VAV_BOT | VAVCHW | Ventilation Reset Flag add_ck_vav_bot | US_LO_Ventilation Reset Flag add_ck_vav_bot | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A
|  | Vent_Optimize |  |  |  | Number of perimeter zones (hard coded - doesn't change) |  | 12 | 12 | 1474.116 | 0 | 0 | 0 | 1474.116 | 0 | 0 | 0 | 12 | 12 | 1474.116 | 0 | 0 | 0 | 1474.116 | 0 | 0 | 0 | 12 | 12 | 1474.116 | 0 | 0 | 0 | 1474.116 | 0 | 0 | 0 | 12 | 12 | 1474.116 | 0 | 0 | 0 | 1474.116 | 0 | 0 | 0 | 12 | 12 | 1474.116 | 0 | 0 | 0 | 1474.116 | 0 | 0 | 0 |  | 0 | 0
|  |  |  | VAV_MID (cost is for top floor and all 10 Mid floors, no multiplier of 5 needed) | VAVCHW | Ventilation Reset Flag add_ck_vav_mid | US_LO_Ventilation Reset Flag add_ck_vav_mid | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A
|  | Vent_Optimize |  |  |  | Number of perimeter zones (hard coded - doesn't change) |  | 120 | 120 | 14741.16 | 0 | 0 | 0 | 14741.16 | 0 | 0 | 0 | 120 | 120 | 14741.16 | 0 | 0 | 0 | 14741.16 | 0 | 0 | 0 | 120 | 120 | 14741.16 | 0 | 0 | 0 | 14741.16 | 0 | 0 | 0 | 120 | 120 | 14741.16 | 0 | 0 | 0 | 14741.16 | 0 | 0 | 0 | 120 | 120 | 14741.16 | 0 | 0 | 0 | 14741.16 | 0 | 0 | 0 |  | 0 | 0
|  |  |  | VAV_TOP | VAVCHW | Ventilation Reset Flag add_ck_vav_top | US_LO_Ventilation Reset Flag add_ck_vav_top | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A
|  | Vent_Optimize |  |  |  | Number of perimeter zones (hard coded - doesn't change) |  | 12 | 12 | 1474.116 | 0 | 0 | 0 | 1474.116 | 0 | 0 | 0 | 12 | 12 | 1474.116 | 0 | 0 | 0 | 1474.116 | 0 | 0 | 0 | 12 | 12 | 1474.116 | 0 | 0 | 0 | 1474.116 | 0 | 0 | 0 | 12 | 12 | 1474.116 | 0 | 0 | 0 | 1474.116 | 0 | 0 | 0 | 12 | 12 | 1474.116 | 0 | 0 | 0 | 1474.116 | 0 | 0 | 0 |  | 0 | 0
| 90.1-07cb | Outdoor_Air_Dampers | Use the upper rows for gravity dampers if value is "gravity", cost is 0. If "motorized, cost is difference between motorized and gravity. If system has an economizer, then there is no added cost for a motorized damper vs. a gravity damper and value is set to $0, | [55 empty] | 0 | 0
Not in 2016 |  | Outdoor_Air_Dampers | system cost | VAV_BOT | VAVCHW | VAV_bot WITH REHEAT OA Damper [gravity, motorized] | US_LO_VAV_bot WITH REHEAT OA Damper [gravity, motorized] | #N/A | #N/A | OUT OF RANGE | OUT OF RANGE | #N/A | OUT OF RANGE | OUT OF RANGE | OUT OF RANGE | #N/A | OUT OF RANGE | #N/A | #N/A | OUT OF RANGE | OUT OF RANGE | #N/A | OUT OF RANGE | OUT OF RANGE | OUT OF RANGE | #N/A | OUT OF RANGE | #N/A | #N/A | OUT OF RANGE | OUT OF RANGE | #N/A | OUT OF RANGE | OUT OF RANGE | OUT OF RANGE | #N/A | OUT OF RANGE | #N/A | #N/A | OUT OF RANGE | OUT OF RANGE | #N/A | OUT OF RANGE | OUT OF RANGE | OUT OF RANGE | #N/A | OUT OF RANGE | #N/A | #N/A | OUT OF RANGE | OUT OF RANGE | #N/A | OUT OF RANGE | OUT OF RANGE | OUT OF RANGE | #N/A | OUT OF RANGE |  | #VALUE! | #VALUE!
|  | Outdoor_Air_Dampers_Gravity | item cost |  |  | VAV_BOT WITH REHEAT OA Rate [cfm] | US_LO_VAV_BOT WITH REHEAT OA Rate [cfm] | 4302.3858 | 4302.3858 | 728.2558 | 146.3984 | 20 | 769.5841 | 786.8923 | 146.3984 | 20 | 958.5033 | 4302.3858 | 4302.3858 | 728.2558 | 146.3984 | 20 | 769.5841 | 786.8923 | 146.3984 | 20 | 958.5033 | 4302.3858 | 4302.3858 | 728.2558 | 146.3984 | 20 | 769.5841 | 786.8923 | 146.3984 | 20 | 958.5033 | 4302.3858 | 4302.3858 | 728.2558 | 146.3984 | 20 | 769.5841 | 786.8923 | 146.3984 | 20 | 958.5033 | 4302.3858 | 4302.3858 | 728.2558 | 146.3984 | 20 | 769.5841 | 786.8923 | 146.3984 | 20 | 958.5033 |  | 0 | 58.6365
|  | Outdoor_Air_Dampers_Motorized | item cost |  |  | VAV_BOT WITH REHEAT OA Rate [cfm] | US_LO_VAV_BOT WITH REHEAT OA Rate [cfm] | 4302.3858 | 4302.3858 | 1258.3584 | 146.3984 | 20 | 1283.0258 | 1418.4226 | 146.3984 | 20 | 1685.5202 | 4302.3858 | 4302.3858 | 1258.3584 | 146.3984 | 20 | 1283.0258 | 1418.4226 | 146.3984 | 20 | 1685.5202 | 4302.3858 | 4302.3858 | 1258.3584 | 146.3984 | 20 | 1283.0258 | 1418.4226 | 146.3984 | 20 | 1685.5202 | 4302.3858 | 4302.3858 | 1258.3584 | 146.3984 | 20 | 1283.0258 | 1418.4226 | 146.3984 | 20 | 1685.5202 | 4302.3858 | 4302.3858 | 1258.3584 | 146.3984 | 20 | 1283.0258 | 1418.4226 | 146.3984 | 20 | 1685.5202 |  | 0 | 160.0642
Not in 2016 |  |  |  | VAV_MID (estimate based on 5 systems, not 1 as modeled, costs multiplied by 5. Modeled system is too large for real application. Row included to screen out Out of Range * 5 which gives a Value error) | VAVCHW | VAV_MID WITH REHEAT Supply Flow Rate [cfm] |  |  |  | OUT OF RANGE | OUT OF RANGE | #N/A | OUT OF RANGE | OUT OF RANGE | OUT OF RANGE | #N/A | OUT OF RANGE |  |  | OUT OF RANGE | OUT OF RANGE | #N/A | OUT OF RANGE | OUT OF RANGE | OUT OF RANGE | #N/A | OUT OF RANGE |  |  | OUT OF RANGE | OUT OF RANGE | #N/A | OUT OF RANGE | OUT OF RANGE | OUT OF RANGE | #N/A | OUT OF RANGE |  |  | OUT OF RANGE | OUT OF RANGE | #N/A | OUT OF RANGE | OUT OF RANGE | OUT OF RANGE | #N/A | OUT OF RANGE |  |  | OUT OF RANGE | OUT OF RANGE | #N/A | OUT OF RANGE | OUT OF RANGE | OUT OF RANGE | #N/A | OUT OF RANGE |  | #VALUE! | #VALUE!
|  | Outdoor_Air_Dampers | system cost | VAV_MID | VAVCHW | VAV_mid WITH REHEAT OA Damper [gravity, motorized] | US_LO_VAV_mid WITH REHEAT OA Damper [gravity, motorized] | #N/A | #N/A | OUT OF RANGE | OUT OF RANGE | #N/A | OUT OF RANGE | OUT OF RANGE | OUT OF RANGE | #N/A | OUT OF RANGE | #N/A | #N/A | OUT OF RANGE | OUT OF RANGE | #N/A | OUT OF RANGE | OUT OF RANGE | OUT OF RANGE | #N/A | OUT OF RANGE | #N/A | #N/A | OUT OF RANGE | OUT OF RANGE | #N/A | OUT OF RANGE | OUT OF RANGE | OUT OF RANGE | #N/A | OUT OF RANGE | #N/A | #N/A | OUT OF RANGE | OUT OF RANGE | #N/A | OUT OF RANGE | OUT OF RANGE | OUT OF RANGE | #N/A | OUT OF RANGE | #N/A | #N/A | OUT OF RANGE | OUT OF RANGE | #N/A | OUT OF RANGE | OUT OF RANGE | OUT OF RANGE | #N/A | OUT OF RANGE |  | #VALUE! | #VALUE!
|  | Outdoor_Air_Dampers_Gravity | item cost |  |  | VAV_MID WITH REHEAT OA Rate [cfm] | US_LO_VAV_MID WITH REHEAT OA Rate [cfm] | 8605.1955 | 8605.1955 | 1335.3443 | 182.0286 | 20 | 1460.3153 | 1437.1881 | 182.0286 | 20 | 1788.4431 | 8605.1955 | 8605.1955 | 1335.3443 | 182.0286 | 20 | 1460.3153 | 1437.1881 | 182.0286 | 20 | 1788.4431 | 8605.1955 | 8605.1955 | 1335.3443 | 182.0286 | 20 | 1460.3153 | 1437.1881 | 182.0286 | 20 | 1788.4431 | 8605.1955 | 8605.1955 | 1335.3443 | 182.0286 | 20 | 1460.3153 | 1437.1881 | 182.0286 | 20 | 1788.4431 | 8605.1955 | 8605.1955 | 1335.3443 | 182.0286 | 20 | 1460.3153 | 1437.1881 | 182.0286 | 20 | 1788.4431 |  | 0 | 101.8438
|  | Outdoor_Air_Dampers_Motorized | item cost |  |  | VAV_MID WITH REHEAT OA Rate [cfm] | US_LO_VAV_MID WITH REHEAT OA Rate [cfm] | 8605.1955 | 8605.1955 | 1745.5188 | 182.0286 | 20 | 1793.7935 | 1965.1182 | 182.0286 | 20 | 2345.9942 | 8605.1955 | 8605.1955 | 1745.5188 | 182.0286 | 20 | 1793.7935 | 1965.1182 | 182.0286 | 20 | 2345.9942 | 8605.1955 | 8605.1955 | 1745.5188 | 182.0286 | 20 | 1793.7935 | 1965.1182 | 182.0286 | 20 | 2345.9942 | 8605.1955 | 8605.1955 | 1745.5188 | 182.0286 | 20 | 1793.7935 | 1965.1182 | 182.0286 | 20 | 2345.9942 | 8605.1955 | 8605.1955 | 1745.5188 | 182.0286 | 20 | 1793.7935 | 1965.1182 | 182.0286 | 20 | 2345.9942 |  | 0 | 219.5994
Not in 2016 |  | Outdoor_Air_Dampers | system cost | VAV_TOP | VAVCHW | VAV_top WITH REHEAT OA Damper [gravity, motorized] | US_LO_VAV_top WITH REHEAT OA Damper [gravity, motorized] | #N/A | #N/A | OUT OF RANGE | OUT OF RANGE | #N/A | OUT OF RANGE | OUT OF RANGE | OUT OF RANGE | #N/A | OUT OF RANGE | #N/A | #N/A | OUT OF RANGE | OUT OF RANGE | #N/A | OUT OF RANGE | OUT OF RANGE | OUT OF RANGE | #N/A | OUT OF RANGE | #N/A | #N/A | OUT OF RANGE | OUT OF RANGE | #N/A | OUT OF RANGE | OUT OF RANGE | OUT OF RANGE | #N/A | OUT OF RANGE | #N/A | #N/A | OUT OF RANGE | OUT OF RANGE | #N/A | OUT OF RANGE | OUT OF RANGE | OUT OF RANGE | #N/A | OUT OF RANGE | #N/A | #N/A | OUT OF RANGE | OUT OF RANGE | #N/A | OUT OF RANGE | OUT OF RANGE | OUT OF RANGE | #N/A | OUT OF RANGE |  | #VALUE! | #VALUE!
|  | Outdoor_Air_Dampers_Gravity | item cost |  |  | VAV_TOP WITH REHEAT OA Rate [cfm] | US_LO_VAV_TOP WITH REHEAT OA Rate [cfm] | 4302.3858 | 4302.3858 | 728.2558 | 146.3984 | 20 | 769.5841 | 786.8923 | 146.3984 | 20 | 958.5033 | 4302.3858 | 4302.3858 | 728.2558 | 146.3984 | 20 | 769.5841 | 786.8923 | 146.3984 | 20 | 958.5033 | 4302.3858 | 4302.3858 | 728.2558 | 146.3984 | 20 | 769.5841 | 786.8923 | 146.3984 | 20 | 958.5033 | 4302.3858 | 4302.3858 | 728.2558 | 146.3984 | 20 | 769.5841 | 786.8923 | 146.3984 | 20 | 958.5033 | 4302.3858 | 4302.3858 | 728.2558 | 146.3984 | 20 | 769.5841 | 786.8923 | 146.3984 | 20 | 958.5033 |  | 0 | 58.6365
|  | Outdoor_Air_Dampers_Motorized | item cost |  |  | VAV_TOP WITH REHEAT OA Rate [cfm] | US_LO_VAV_TOP WITH REHEAT OA Rate [cfm] | 4302.3858 | 4302.3858 | 1258.3584 | 146.3984 | 20 | 1283.0258 | 1418.4226 | 146.3984 | 20 | 1685.5202 | 4302.3858 | 4302.3858 | 1258.3584 | 146.3984 | 20 | 1283.0258 | 1418.4226 | 146.3984 | 20 | 1685.5202 | 4302.3858 | 4302.3858 | 1258.3584 | 146.3984 | 20 | 1283.0258 | 1418.4226 | 146.3984 | 20 | 1685.5202 | 4302.3858 | 4302.3858 | 1258.3584 | 146.3984 | 20 | 1283.0258 | 1418.4226 | 146.3984 | 20 | 1685.5202 | 4302.3858 | 4302.3858 | 1258.3584 | 146.3984 | 20 | 1283.0258 | 1418.4226 | 146.3984 | 20 | 1685.5202 |  | 0 | 160.0642
Not in 2016 |  | Outdoor_Air_Dampers | system cost | CAV_BAS | CAVCHW | CAV_bas OA Damper [gravity, motorized] | US_LO_CAV_bas OA Damper [gravity, motorized] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A
|  | Outdoor_Air_Dampers_Gravity | item cost |  |  | CAV_BAS OA Rate [cfm] | US_LO_CAV_BAS OA Rate [cfm] | 2542.8255 | 2542.8255 | 489.141 | 124.2331 | 20 | 496.3984 | 530.8893 | 124.2331 | 20 | 630.906 | 2542.8255 | 2542.8255 | 489.141 | 124.2331 | 20 | 496.3984 | 530.8893 | 124.2331 | 20 | 630.906 | 2542.8255 | 2542.8255 | 489.141 | 124.2331 | 20 | 496.3984 | 530.8893 | 124.2331 | 20 | 630.906 | 2542.8255 | 2542.8255 | 489.141 | 124.2331 | 20 | 496.3984 | 530.8893 | 124.2331 | 20 | 630.906 | 2542.8255 | 2542.8255 | 489.141 | 124.2331 | 20 | 496.3984 | 530.8893 | 124.2331 | 20 | 630.906 |  | 0 | 41.7483
|  | Outdoor_Air_Dampers_Motorized | item cost |  |  | CAV_BAS OA Rate [cfm] | US_LO_CAV_BAS OA Rate [cfm] | 2542.8255 | 2542.8255 | 1018.3507 | 124.2331 | 20 | 1025.6797 | 1150.0712 | 124.2331 | 20 | 1356.9018 | 2542.8255 | 2542.8255 | 1018.3507 | 124.2331 | 20 | 1025.6797 | 1150.0712 | 124.2331 | 20 | 1356.9018 | 2542.8255 | 2542.8255 | 1018.3507 | 124.2331 | 20 | 1025.6797 | 1150.0712 | 124.2331 | 20 | 1356.9018 | 2542.8255 | 2542.8255 | 1018.3507 | 124.2331 | 20 | 1025.6797 | 1150.0712 | 124.2331 | 20 | 1356.9018 | 2542.8255 | 2542.8255 | 1018.3507 | 124.2331 | 20 | 1025.6797 | 1150.0712 | 124.2331 | 20 | 1356.9018 |  | 0 | 131.7206
Not in 2016 |  | Outdoor_Air_Dampers | system cost - Added this, copied and pasted, verify | AirLoop DataCenter Basement | WSHP | AirLoop DataCenter Basement OA Damper [gravity, motorized] | US_LO_AirLoop DataCenter Basement OA Damper [gravity, motorized] | #N/A | #N/A | OUT OF RANGE | OUT OF RANGE | #N/A | OUT OF RANGE | OUT OF RANGE | OUT OF RANGE | #N/A | OUT OF RANGE | #N/A | #N/A | OUT OF RANGE | OUT OF RANGE | #N/A | OUT OF RANGE | OUT OF RANGE | OUT OF RANGE | #N/A | OUT OF RANGE | #N/A | #N/A | OUT OF RANGE | OUT OF RANGE | #N/A | OUT OF RANGE | OUT OF RANGE | OUT OF RANGE | #N/A | OUT OF RANGE | #N/A | #N/A | OUT OF RANGE | OUT OF RANGE | #N/A | OUT OF RANGE | OUT OF RANGE | OUT OF RANGE | #N/A | OUT OF RANGE | #N/A | #N/A | OUT OF RANGE | OUT OF RANGE | #N/A | OUT OF RANGE | OUT OF RANGE | OUT OF RANGE | #N/A | OUT OF RANGE |  | #VALUE! | #VALUE!
|  | Outdoor_Air_Dampers_Gravity | item cost |  |  | DATACENTER BASEMENT OA Rate [cfm] | US_LO_DATACENTER BASEMENT OA Rate [cfm] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A
|  | Outdoor_Air_Dampers_Motorized | item cost |  |  | DATACENTER BASEMENT OA Rate [cfm] | US_LO_DATACENTER BASEMENT OA Rate [cfm] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A
| 90.1-07cy | AHU_Economizer | If any value other than "no" lookup cost based on supply air cfm | NOTE: I'M EXTRACTING THE COSTS IN THE SECOND LINE, AND APPLYING THE YES/NO CONDITION IN THE FIRST LINE. |  | Note that HVAC Data parameter range is [No, DifferentialEnthalpy] | [52 empty] | 0 | 0
Not in 2016 | 90.1-07cy | AHU_Economizer |  | VAV_BOT | VAVCHW | VAV_bot WITH REHEAT (economizer) | US_LO_VAV_bot WITH REHEAT (economizer) | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A
|  | AHU_Economizer |  |  |  | VAV_BOT WITH REHEAT Supply Flow Rate [cfm] | US_LO_VAV_BOT WITH REHEAT Supply Flow Rate [cfm] | 18455.4448 | 17925.7248 | 22467.4676 | 359.615 | 15 | 25017.1464 | 21822.592 | 354.4092 | 15 | 24299.0882 | 18963.976 | 18413.0672 | 23086.5482 | 364.6125 | 15 | 25706.4822 | 22415.8776 | 359.1985 | 15 | 24959.7017 | 21633.7648 | 21040.4784 | 26336.7215 | 390.8497 | 15 | 29325.4953 | 25614.4608 | 385.0192 | 15 | 28521.2702 | 19430.1296 | 18858.032 | 23654.0388 | 369.1936 | 15 | 26338.3734 | 22957.5731 | 363.5714 | 15 | 25562.8706 | 19514.8848 | 18942.7872 | 23757.2189 | 370.0266 | 15 | 26453.2627 | 23060.7532 | 364.4043 | 15 | 25677.7599 |  | -619.0806 | -1263.9563
Not in 2016 |  |  |  | VAV_MID (estimate based on 5 systems, not 1 as modeled, costs multiplied by 5. Modeled system is too large for real application. Row included to screen out Out of Range * 5 which gives a Value error) | VAVCHW |  |  |  |  | OUT OF RANGE | OUT OF RANGE | #N/A | OUT OF RANGE | OUT OF RANGE | OUT OF RANGE | #N/A | OUT OF RANGE |  |  | OUT OF RANGE | OUT OF RANGE | #N/A | OUT OF RANGE | OUT OF RANGE | OUT OF RANGE | #N/A | OUT OF RANGE |  |  | OUT OF RANGE | OUT OF RANGE | #N/A | OUT OF RANGE | OUT OF RANGE | OUT OF RANGE | #N/A | OUT OF RANGE |  |  | OUT OF RANGE | OUT OF RANGE | #N/A | OUT OF RANGE | OUT OF RANGE | OUT OF RANGE | #N/A | OUT OF RANGE |  |  | OUT OF RANGE | OUT OF RANGE | #N/A | OUT OF RANGE | OUT OF RANGE | OUT OF RANGE | #N/A | OUT OF RANGE |  | #VALUE! | #VALUE!
Not in 2016 |  | AHU_Economizer |  | VAV_MID | VAVCHW | VAV_mid WITH REHEAT (economizer) | US_LO_VAV_mid WITH REHEAT (economizer) | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A
|  | AHU_Economizer |  |  |  | VAV_MID WITH REHEAT Supply Flow Rate [cfm] | US_LO_VAV_MID WITH REHEAT Supply Flow Rate [cfm] | 34143.6324 | 33126.57 | 41566.1048 | 513.7897 | 15 | 46283.1569 | 40327.9436 | 503.7946 | 15 | 44904.4852 | 35304.7786 | 34241.1009 | 42979.6722 | 525.2008 | 15 | 47857.1404 | 41684.7619 | 514.7476 | 15 | 46415.2796 | 40440.9437 | 39262.8465 | 49232.3865 | 575.6761 | 15 | 54819.4323 | 47798.1831 | 564.0985 | 15 | 53222.471 | 36465.9249 | 35368.345 | 44393.2397 | 536.6119 | 15 | 49431.1239 | 43057.0573 | 525.8255 | 15 | 47943.3074 | 36275.2257 | 35169.1703 | 44161.0844 | 534.7378 | 15 | 49172.6229 | 42814.5841 | 523.8681 | 15 | 47673.3175 |  | -1413.5674 | -2651.7287
Not in 2016 |  | AHU_Economizer |  | VAV_TOP | VAVCHW | VAV_top WITH REHEAT (economizer) | US_LO_VAV_top WITH REHEAT (economizer) | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A
|  | AHU_Economizer |  |  |  | VAV_TOP WITH REHEAT Supply Flow Rate [cfm] | US_LO_VAV_TOP WITH REHEAT Supply Flow Rate [cfm] | 18858.032 | 18413.0672 | 22957.5731 | 363.5714 | 15 | 25562.8706 | 22415.8776 | 359.1985 | 15 | 24959.7017 | 19451.3184 | 18985.1648 | 23679.8338 | 369.4019 | 15 | 26367.0957 | 23112.3433 | 364.8208 | 15 | 25735.2045 | 22756.7712 | 22248.24 | 27703.8579 | 401.886 | 15 | 30847.7786 | 27084.7772 | 396.8884 | 15 | 30158.4428 | 20086.9824 | 19578.4512 | 24453.6846 | 375.6488 | 15 | 27228.7655 | 23834.604 | 370.6512 | 15 | 26539.4297 | 20192.9264 | 19684.3952 | 24582.6597 | 376.69 | 15 | 27372.3771 | 23963.5791 | 371.6924 | 15 | 26683.0413 |  | -722.2607 | -1263.9563
Not in 2016 |  | AHU_Economizer |  | CAV_BAS | CAVCHW | CAV_bas (economizer) | US_LO_CAV_bas (economizer) | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A
|  | AHU_Economizer |  |  |  | CAV_BAS Supply Flow Rate [cfm] | US_LO_CAV_BAS Supply Flow Rate [cfm] | 11060.5536 | 10615.5888 | 13465.0035 | 286.9421 | 15 | 14993.0544 | 12923.308 | 282.5693 | 15 | 14389.8856 | 10891.0432 | 10424.8896 | 13258.6433 | 285.2763 | 15 | 14763.2758 | 12691.1528 | 280.6952 | 15 | 14131.3846 | 12289.504 | 11780.9728 | 14961.1151 | 299.0196 | 15 | 16658.9494 | 14342.0344 | 294.022 | 15 | 15969.6135 | 10657.9664 | 10213.0016 | 12974.8981 | 282.9857 | 15 | 14447.3302 | 12433.2025 | 278.6129 | 15 | 13844.1614 | 10848.6656 | 10382.512 | 13207.0533 | 284.8598 | 15 | 14705.8312 | 12639.5627 | 280.2787 | 15 | 14073.94 |  | 206.3602 | -335.3353
Not in 2019 | 90.1-13 i | AHU_Economizer |  | AirLoop DataCenter Basement | DX | AirLoop DataCenter Basement (economizer) | US_LO_AirLoop DataCenter Basement (economizer) | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A
| Lowers computer room economizer threshold | AHU_Economizer | Includes both load adjustments and requirement changes |  |  | DATACENTER BASEMENT Fan SA [cfm] | US_LO_DATACENTER BASEMENT Fan SA [cfm] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A
| ERV load change from OA reduction from 90.1-16 au, cm, & co | Energy_Recovery_AHU | if "yes" lookup up based on outside airflow, cfm. |  | 2010 ONLY | Note that HVAC Data ERV Flag parameter values are [Yes, No] | [52 empty] | 0 | 0
x |  | Energy_Recovery_AHU |  | VAV_BOT | VAVCHW | VAV_bot_WITH_REHEAT ERV Flag | US_LO_VAV_bot_WITH_REHEAT ERV Flag | Yes | Yes | 32449.1193 | 255.0825 | 15 | 37354.3033 | 32449.1193 | 255.0825 | 15 | 37354.3033 | Yes | Yes | 32449.1193 | 255.0825 | 15 | 37354.3033 | 32449.1193 | 255.0825 | 15 | 37354.3033 | No | No | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Yes | Yes | 32449.1193 | 255.0825 | 15 | 37354.3033 | 32449.1193 | 255.0825 | 15 | 37354.3033 | Yes | Yes | 32449.1193 | 255.0825 | 15 | 37354.3033 | 32449.1193 | 255.0825 | 15 | 37354.3033 |  | 0 | 0 |  |  |  | 0 | 0 | 0 | 0 | 0
|  | Energy_Recovery_AHU |  |  |  | VAV_BOT WITH REHEAT OA Rate [cfm] | US_LO_VAV_BOT WITH REHEAT OA Rate [cfm] | 4302.3858 | 4302.3858 | 32449.1193 | 255.0825 | 15 | 37354.3033 | 32449.1193 | 255.0825 | 15 | 37354.3033 | 4302.3858 | 4302.3858 | 32449.1193 | 255.0825 | 15 | 37354.3033 | 32449.1193 | 255.0825 | 15 | 37354.3033 | 4302.3858 | 4302.3858 | 32449.1193 | 255.0825 | 15 | 37354.3033 | 32449.1193 | 255.0825 | 15 | 37354.3033 | 4302.3858 | 4302.3858 | 32449.1193 | 255.0825 | 15 | 37354.3033 | 32449.1193 | 255.0825 | 15 | 37354.3033 | 4302.3858 | 4302.3858 | 32449.1193 | 255.0825 | 15 | 37354.3033 | 32449.1193 | 255.0825 | 15 | 37354.3033 |  | 0 | 0
x |  | MID SYS multiplier: | 10 | VAV_MID (estimate based on 10 systems, not 1 as modeled, costs multiplied by 10. Modeled system is too large for real application. Parameter adjusted by multiplier) | VAVCHW | VAV_MID WITH REHEAT Supply Flow Rate [cfm] |  |  |  | 324506.3011 | 2550.825 | 15 | 373559.8978 | 324506.3011 | 2550.825 | 15 | 373559.8978 |  |  | 324506.3011 | 2550.825 | 15 | 373559.8978 | 324506.3011 | 2550.825 | 15 | 373559.8978 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 324506.3011 | 2550.825 | 15 | 373559.8978 | 324506.3011 | 2550.825 | 15 | 373559.8978 |  |  | 324506.3011 | 2550.825 | 15 | 373559.8978 | 324506.3011 | 2550.825 | 15 | 373559.8978 |  | 0 | 0 |  |  |  | 0 | 0 | 0 | 0 | 0
|  | Energy_Recovery_AHU |  | VAV_MID | VAVCHW | VAV_mid_WITH_REHEAT ERV Flag | US_LO_VAV_mid_WITH_REHEAT ERV Flag | Yes | Yes | 32450.6301 | 255.0825 | 15 | 37355.9898 | 32450.6301 | 255.0825 | 15 | 37355.9898 | Yes | Yes | 32450.6301 | 255.0825 | 15 | 37355.9898 | 32450.6301 | 255.0825 | 15 | 37355.9898 | No | No | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Yes | Yes | 32450.6301 | 255.0825 | 15 | 37355.9898 | 32450.6301 | 255.0825 | 15 | 37355.9898 | Yes | Yes | 32450.6301 | 255.0825 | 15 | 37355.9898 | 32450.6301 | 255.0825 | 15 | 37355.9898 |  | 0 | 0
|  | Energy_Recovery_AHU |  |  |  | VAV_MID WITH REHEAT OA Rate [cfm] | US_LO_VAV_MID WITH REHEAT OA Rate [cfm] | 4302.5977 | 4302.5977 | 32450.6301 | 255.0825 | 15 | 37355.9898 | 32450.6301 | 255.0825 | 15 | 37355.9898 | 4302.5977 | 4302.5977 | 32450.6301 | 255.0825 | 15 | 37355.9898 | 32450.6301 | 255.0825 | 15 | 37355.9898 | 4302.5977 | 4302.5977 | 32450.6301 | 255.0825 | 15 | 37355.9898 | 32450.6301 | 255.0825 | 15 | 37355.9898 | 4302.5977 | 4302.5977 | 32450.6301 | 255.0825 | 15 | 37355.9898 | 32450.6301 | 255.0825 | 15 | 37355.9898 | 4302.5977 | 4302.5977 | 32450.6301 | 255.0825 | 15 | 37355.9898 | 32450.6301 | 255.0825 | 15 | 37355.9898 |  | 0 | 0
x |  | Energy_Recovery_AHU |  | VAV_TOP | VAVCHW | VAV_top_WITH_REHEAT ERV Flag | US_LO_VAV_top_WITH_REHEAT ERV Flag | Yes | Yes | 32449.1193 | 255.0825 | 15 | 37354.3033 | 32449.1193 | 255.0825 | 15 | 37354.3033 | Yes | Yes | 32449.1193 | 255.0825 | 15 | 37354.3033 | 32449.1193 | 255.0825 | 15 | 37354.3033 | No | No | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Yes | Yes | 32449.1193 | 255.0825 | 15 | 37354.3033 | 32449.1193 | 255.0825 | 15 | 37354.3033 | Yes | Yes | 32449.1193 | 255.0825 | 15 | 37354.3033 | 32449.1193 | 255.0825 | 15 | 37354.3033 |  | 0 | 0 |  |  |  | 0 | 0 | 0 | 0 | 0
|  | Energy_Recovery_AHU |  |  |  | VAV_TOP WITH REHEAT OA Rate [cfm] | US_LO_VAV_TOP WITH REHEAT OA Rate [cfm] | 4302.3858 | 4302.3858 | 32449.1193 | 255.0825 | 15 | 37354.3033 | 32449.1193 | 255.0825 | 15 | 37354.3033 | 4302.3858 | 4302.3858 | 32449.1193 | 255.0825 | 15 | 37354.3033 | 32449.1193 | 255.0825 | 15 | 37354.3033 | 4302.3858 | 4302.3858 | 32449.1193 | 255.0825 | 15 | 37354.3033 | 32449.1193 | 255.0825 | 15 | 37354.3033 | 4302.3858 | 4302.3858 | 32449.1193 | 255.0825 | 15 | 37354.3033 | 32449.1193 | 255.0825 | 15 | 37354.3033 | 4302.3858 | 4302.3858 | 32449.1193 | 255.0825 | 15 | 37354.3033 | 32449.1193 | 255.0825 | 15 | 37354.3033 |  | 0 | 0
| HVAC Plant - General load change |  | lookup cost based on cooling tons | [55 empty] | 0 | 0
x |  | Cent_WC_Chiller_Capacity |  | Chiller 1 | centrifugal, water-cooled | COOLSYS1 CHILLER1 Capacity [ton] | US_LO_COOLSYS1 CHILLER1 Capacity [ton] | 396.6465 | 389.1686 | 259694.1435 | 0 | 23 | 310738.7057 | 259262.062 | 0 | 23 | 310090.6131 | 372.4976 | 364.9993 | 258298.7935 | 0 | 23 | 308645.7766 | 257865.5327 | 0 | 23 | 307995.9151 | 319.9492 | 312.4729 | 255262.4956 | 0 | 23 | 304091.5384 | 254830.5058 | 0 | 23 | 303443.5833 | 375.6304 | 367.7189 | 258479.8098 | 0 | 23 | 308917.2885 | 258022.678 | 0 | 23 | 308231.6223 | 349.3208 | 341.5012 | 256959.6177 | 0 | 23 | 306637.1049 | 256507.793 | 0 | 23 | 305959.3989 |  | 1395.35 | 963.2684 |  |  |  | -432.0815 | -433.2609 | -431.9898 | -457.1318 | -451.8247
x |  | Cent_WC_Chiller_Capacity |  | Chiller 2 | centrifugal, water-cooled | COOLSYS1 CHILLER2 Capacity [ton] | US_LO_COOLSYS1 CHILLER2 Capacity [ton] | 396.6465 | 389.1686 | 259694.1435 | 0 | 23 | 310738.7057 | 259262.062 | 0 | 23 | 310090.6131 | 372.4976 | 364.9993 | 258298.7935 | 0 | 23 | 308645.7766 | 257865.5327 | 0 | 23 | 307995.9151 | 319.9492 | 312.4729 | 255262.4956 | 0 | 23 | 304091.5384 | 254830.5058 | 0 | 23 | 303443.5833 | 375.6304 | 367.7189 | 258479.8098 | 0 | 23 | 308917.2885 | 258022.678 | 0 | 23 | 308231.6223 | 349.3208 | 341.5012 | 256959.6177 | 0 | 23 | 306637.1049 | 256507.793 | 0 | 23 | 305959.3989 |  | 1395.35 | 963.2684 |  |  |  | -432.0815 | -433.2609 | -431.9898 | -457.1318 | -451.8247
| General load change | Cooling_Tower_Capacity | lookup based on cooling tons | [55 empty] | 0 | 0
x |  | Cooling_Tower_Capacity |  | Cooling Tower |  | TOWERWATERSYS COOLTOWER 1 Capacity [ton] | US_LO_TOWERWATERSYS COOLTOWER 1 Capacity [ton] | 470.6199 | 461.7427 | OUT OF RANGE | OUT OF RANGE | OUT OF RANGE | OUT OF RANGE | 138562.1706 | 0 | 20 | 161137.7814 | 441.9538 | 433.0602 | 131611.7616 | 0 | 20 | 152858.2082 | 128488.1122 | 0 | 20 | 149137.2065 | 379.9332 | 371.0487 | 109828.5215 | 0 | 20 | 126909.2417 | 106708.037 | 0 | 20 | 123192.0101 | 445.6785 | 436.2927 | 132920.0061 | 0 | 20 | 154416.6354 | 129623.4607 | 0 | 20 | 150489.6738 | 414.4809 | 405.1933 | 121962.582 | 0 | 20 | 141363.7641 | 118700.5225 | 0 | 20 | 137477.8833 |  | #VALUE! | 6950.409 |  |  |  | #VALUE! | -3123.6494 | -3120.4845 | -3296.5454 | -3262.0595
x |  | Cooling_Tower_Capacity |  | Cooling Tower |  | TOWERWATERSYS COOLTOWER 2 Capacity [ton] | US_LO_TOWERWATERSYS COOLTOWER 2 Capacity [ton] | 470.6199 | 461.7427 | OUT OF RANGE | OUT OF RANGE | OUT OF RANGE | OUT OF RANGE | 138562.1706 | 0 | 20 | 161137.7814 | 441.9538 | 433.0602 | 131611.7616 | 0 | 20 | 152858.2082 | 128488.1122 | 0 | 20 | 149137.2065 | 379.9332 | 371.0487 | 109828.5215 | 0 | 20 | 126909.2417 | 106708.037 | 0 | 20 | 123192.0101 | 445.6785 | 436.2927 | 132920.0061 | 0 | 20 | 154416.6354 | 129623.4607 | 0 | 20 | 150489.6738 | 414.4809 | 405.1933 | 121962.582 | 0 | 20 | 141363.7641 | 118700.5225 | 0 | 20 | 137477.8833 |  | #VALUE! | 6950.409 |  |  |  | #VALUE! | -3123.6494 | -3120.4845 | -3296.5454 | -3262.0595
| General Load impact | Boiler_Capacity | lookup cost based on boiler millions of Btu/h | [55 empty] | 0 | 0
x |  | Boiler_Capacity |  | Boiler |  | HEATSYS1 BOILER Capacity [MMBTU/h] | US_LO_HEATSYS1 BOILER Capacity [MMBTU/h] | 4.8398 | 4.8297 | 106845.281 | 0 | 35 | 140778.7406 | 106634.8586 | 0 | 35 | 140505.4858 | 7.4525 | 7.438 | 161531.0475 | 0 | 35 | 211793.7439 | 161228.4214 | 0 | 35 | 211400.7533 | 6.3656 | 6.3509 | 138782.0351 | 0 | 35 | 182251.8486 | 138473.7919 | 0 | 35 | 181851.5636 | 8.6261 | 8.5184 | 194723.397 | 0 | 35 | 253053.5109 | 191644.288 | 0 | 35 | 249231.307 | 9.2714 | 9.0739 | 213173.3471 | 0 | 35 | 275956.0683 | 207525.1076 | 0 | 35 | 268944.7144 |  | -54685.7665 | -54896.1889 |  |  |  | -210.4225 | -302.6261 | -308.2432 | -3079.109 | -5648.2395
x | 90.1-19bc - Condensing boilers modeled for large systems | Boiler_Capacity | cost based on boiler 1000 Btu/h, thus 1000 conversion in $ equation, manual calc hard pasted in here | Boiler |  | HEATSYS1 BOILER Capacity [MMBTU/h] | US_LO_HEATSYS1 BOILER Capacity [MMBTU/h] | 4.8398 | 4.8297 | 0 | 0 | 40 | 0 | 19801.9533 | 400 | 40 | 19801.9533 | 7.4525 | 7.438 | 0 | 0 | 40 | 0 | 30495.8804 | 400 | 40 | 30495.8804 | 6.3656 | 6.3509 | 0 | 0 | 40 | 0 | 26038.6452 | 400 | 40 | 26038.6452 | 8.6261 | 8.5184 | 0 | 0 | 40 | 0 | 34925.5272 | 400 | 40 | 34925.5272 | 9.2714 | 9.0739 | 0 | 0 | 40 | 0 | 37202.7962 | 400 | 40 | 37202.7962 |  | 0 | 19801.9533 |  |  |  | 19801.9533 | 30495.8804 | 26038.6452 | 34925.5272 | 37202.7962
| General Load impact | Pump_Flow | lookup based on flow, GPM | [55 empty] | 0 | 0
x |  | Pump_FlPri | Test for N/A | Pump | Primary CHW | COOLSYS1 PUMP Flow Rate [gal/min] | US_LO_COOLSYS1 PUMP Flow Rate [gal/min] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  |  |  | 0 | 0 | 0 | 0 | 0
x |  | Pump_FlPri | Test for N/A | Pump | Primary CHW | COOLSYS1 CHILLER1 PUMP Flow Rate [gal/min] | US_LO_COOLSYS1 CHILLER1 PUMP Flow Rate [gal/min] | 622.3931 | 610.724 | 48701.7863 | 0 | 20 | 61585.8299 | 48397.1925 | 0 | 20 | 61223.2941 | 584.0226 | 572.3282 | 47700.2098 | 0 | 20 | 60393.7265 | 47394.9541 | 0 | 20 | 60030.4028 | 499.9667 | 488.3532 | 45506.1169 | 0 | 20 | 57782.2577 | 45202.9712 | 0 | 20 | 57421.4455 | 588.8411 | 576.4984 | 47825.9861 | 0 | 20 | 60543.4288 | 47503.8085 | 0 | 20 | 60159.9643 | 550.0696 | 537.8126 | 46813.9421 | 0 | 20 | 59338.8666 | 46493.9986 | 0 | 20 | 58958.0613 |  | 1001.5765 | 696.9827 |  |  |  | -304.5938 | -305.2557 | -303.1457 | -322.1776 | -319.9434
x |  | Pump_FlPri | Test for N/A | Pump | Primary CHW | COOLSYS1 CHILLER2 PUMP Flow Rate [gal/min] | US_LO_COOLSYS1 CHILLER2 PUMP Flow Rate [gal/min] | 622.3931 | 610.724 | 48701.7863 | 0 | 20 | 61585.8299 | 48397.1925 | 0 | 20 | 61223.2941 | 584.0226 | 572.3282 | 47700.2098 | 0 | 20 | 60393.7265 | 47394.9541 | 0 | 20 | 60030.4028 | 499.9667 | 488.3532 | 45506.1169 | 0 | 20 | 57782.2577 | 45202.9712 | 0 | 20 | 57421.4455 | 588.8411 | 576.4984 | 47825.9861 | 0 | 20 | 60543.4288 | 47503.8085 | 0 | 20 | 60159.9643 | 550.0696 | 537.8126 | 46813.9421 | 0 | 20 | 59338.8666 | 46493.9986 | 0 | 20 | 58958.0613 |  | 1001.5765 | 696.9827 |  |  |  | -304.5938 | -305.2557 | -303.1457 | -322.1776 | -319.9434
x |  | Pump_Flow |  | Pump | Secondary CHW | COOLSYS1 PUMP SECONDARY Flow Rate [gal/min] | US_LO_COOLSYS1 PUMP SECONDARY Flow Rate [gal/min] | 1244.7861 | 1221.4497 | 100540.0407 | 0 | 20 | 123112.5095 | 99490.3309 | 0 | 20 | 121868.5309 | 1168.0452 | 1144.658 | 97088.1119 | 0 | 20 | 119021.7352 | 96036.1206 | 0 | 20 | 117775.0528 | 999.9319 | 976.7064 | 89526.1092 | 0 | 20 | 110060.239 | 88481.3903 | 0 | 20 | 108822.1748 | 1177.6822 | 1152.9969 | 97521.5993 | 0 | 20 | 119535.4477 | 96411.2156 | 0 | 20 | 118219.5662 | 1100.1392 | 1075.6251 | 94033.5941 | 0 | 20 | 115401.9204 | 92930.9105 | 0 | 20 | 114095.164 |  | 3451.9288 | 2402.219 |  |  |  | -1049.7097 | -1051.9913 | -1044.7189 | -1110.3837 | -1102.6836
x |  | Pump_Flow |  | Pump | Circulate | PLANT CIRC PUMP Flow Rate [gal/min] | US_LO_PLANT CIRC PUMP Flow Rate [gal/min] | 210.7649 | 210.1737 | 50786.1641 | 0 | 20 | 63401.9075 | 50738.0909 | 0 | 20 | 63339.9763 | 211.1406 | 210.5494 | 50816.7092 | 0 | 20 | 63441.2579 | 50768.6361 | 0 | 20 | 63379.3267 | 225.1237 | 224.4865 | 51953.7095 | 0 | 20 | 64906.0216 | 51901.8988 | 0 | 20 | 64839.2754 | 209.7695 | 209.1466 | 50705.2259 | 0 | 20 | 63297.6373 | 50654.5752 | 0 | 20 | 63232.3854 | 211.307 | 210.6777 | 50830.2418 | 0 | 20 | 63458.6916 | 50779.0755 | 0 | 20 | 63392.7756 |  | -30.5451 | -78.6182 |  |  |  | -48.0731 | -48.0731 | -51.8107 | -50.6508 | -51.1663
x |  | Pump_FlPri |  | Pump | Condenser Water | TOWERWATERSYS PUMP Flow Rate [gal/min] | US_LO_TOWERWATERSYS PUMP Flow Rate [gal/min] | 2188.2956 | 2132.978 | 101508.7111 | 0 | 20 | 125852.4779 | 99206.1662 | 0 | 20 | 123114.6656 | 2055.1529 | 2000.6278 | 95966.7692 | 0 | 20 | 119262.9011 | 93697.2121 | 0 | 20 | 116564.3125 | 1765.2505 | 1712.6274 | 85428.3927 | 0 | 20 | 106388.3486 | 83580.6547 | 0 | 20 | 104114.1993 | 2072.4298 | 2015.5271 | 96685.9022 | 0 | 20 | 120117.9771 | 94317.3818 | 0 | 20 | 117301.7175 | 1927.2408 | 1860.5109 | 91116.309 | 0 | 20 | 113388.8927 | 88773.2437 | 0 | 20 | 110505.1069 |  | 5541.9418 | 3239.397 |  |  |  | -2302.5449 | -2269.5571 | -1847.738 | -2368.5204 | -2343.0653
x |  | Pump_Flow |  | Pump | Hot Water | HEATSYS1 PUMP Flow Rate [gal/min] | US_LO_HEATSYS1 PUMP Flow Rate [gal/min] | 196.6835 | 196.2746 | 49493.4965 | 0 | 20 | 61753.7166 | 49442.0357 | 0 | 20 | 61689.5316 | 302.86 | 302.272 | 58170.7094 | 0 | 20 | 72901.9214 | 58144.2581 | 0 | 20 | 72870.5748 | 258.6915 | 258.0924 | 54683.1804 | 0 | 20 | 68422.318 | 54634.4628 | 0 | 20 | 68359.5567 | 350.5553 | 346.179 | 60316.1156 | 0 | 20 | 75444.3762 | 60119.2638 | 0 | 20 | 75211.0932 | 376.7796 | 368.7514 | 61495.729 | 0 | 20 | 76842.2996 | 61134.6083 | 0 | 20 | 76414.3466 |  | -8677.2129 | -8728.6736 | First cost pipe & pump diff |  |  | -51.4607 | -26.4513 | -48.7175 | -196.8518 | -361.1207
x | General Load impact | Chilled and Condenser Water Piping | curve fit from Solarc cost calculations | All systems | COOLSYS1 PUMP SECONDARY | COOLSYS1 PUMP SECONDARY Flow Rate [gal/min] | US_LO_COOLSYS1 PUMP SECONDARY Flow Rate [gal/min] | 1244.7861 | 1221.4497 | 146054.2089 | 0 | 30 | 202819.5173 | 143919.7149 | 0 | 30 | 200464.4476 | 1168.0452 | 1144.658 | 139060.6547 | 0 | 30 | 195119.967 | 136943.9895 | 0 | 30 | 192799.2075 | 999.9319 | 976.7064 | 123997.7263 | 0 | 30 | 178704.8776 | 121944.5336 | 0 | 30 | 115737.5535 | 1177.6822 | 1152.9969 | 139934.847 | 0 | 30 | 152690.3181 | 137697.9163 | 0 | 30 | 148151.5128 | 1100.1392 | 1075.6251 | 132933.7109 | 0 | 30 | 138432.7457 | 130736.0553 | 0 | 30 | 133925.4154 |  | 6993.5542 | 4859.0602 | 2143.1164 | 3571.8607 | 1428.7443 | -2134.494 | -2116.6652 | -2053.1927 | -2236.9307 | -2197.6556
x | General Load impact | Hot Water Piping | curve fit from Solarc cost calculations | All reheat coils | ZN_VAV_Box | ZN_VAV_BOXes_Max_Reheat_Water_Flow_GPM | US_LO_ZN_VAV_BOXes_Max_Reheat_Water_Flow_GPM | 134.6933 | 134.6907 | 340522.7311 | 0 | 30 | 588149.8871 | 340516.0255 | 0 | 30 | 588142.1704 | 198.3482 | 198.3626 | 496911.1534 | 0 | 30 | 768563.1156 | 496944.5765 | 0 | 30 | 768601.7791 | 169.1855 | 169.1476 | 427428.877 | 0 | 30 | 688290.6822 | 427336.2386 | 0 | 30 | 688183.7894 | 224.9228 | 220.9673 | 557038.7282 | 0 | 30 | 838204.4169 | 548281.7067 | 0 | 30 | 828050.5962 | 230.9027 | 224.0883 | 570149.8635 | 0 | 30 | 853414.4696 | 555196.7553 | 0 | 30 | 836068.3043 |  | -156388.4223 | -156395.1279 |  |  |  | -6.7056 | 33.4231 | -92.6383 | -8757.0215 | -14953.1082
| 90.1-13by SHW runout insulation | SHW_runout | Additional insulation required on SHW runouts | SHW piping heat loss |  | SHW_runout_Insul | US_LO_SHW_runout_Insul | #N/A | #N/A | #N/A | #N/A | 0 | #N/A | #N/A | #N/A | 35 | #N/A | #N/A | #N/A | #N/A | #N/A | 0 | #N/A | #N/A | #N/A | 35 | #N/A | #N/A | #N/A | #N/A | #N/A | 0 | #N/A | #N/A | #N/A | 35 | #N/A | #N/A | #N/A | #N/A | #N/A | 0 | #N/A | #N/A | #N/A | 35 | #N/A | #N/A | #N/A | #N/A | #N/A | 0 | #N/A | #N/A | #N/A | 35 | #N/A | 416 | #N/A | #N/A
[59 empty] | 0 | 0
x | General Load impact Pump speed & control CHW |  | If value is "VFD" lookup cost based on the next motor size hp greater than 1.1 times the hp shown under Power (HP) | Pump | Secondary CHW | COOLSYS1 PUMP SECONDARY VSD | US_LO_COOLSYS1 PUMP SECONDARY VSD | No | No | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | No | No | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | No | No | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | No | No | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | No | No | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  |  |  | 0 | 0 | 0 | 0 | 0
|  | VFD_Size | cost input item for VFD | Pump | Secondary CHW | COOLSYS1 PUMP SECONDARY Pump Power [hp] | US_LO_COOLSYS1 PUMP SECONDARY Pump Power [hp] | 17.0246 | 16.7054 | 7107.0414 | 0 | 15 | 9366.5628 | 7107.0414 | 0 | 15 | 9366.5628 | 15.975 | 15.6551 | 7107.0414 | 0 | 15 | 9366.5628 | 7107.0414 | 0 | 15 | 9366.5628 | 13.6758 | 13.3581 | 7107.0414 | 0 | 15 | 9366.5628 | 7107.0414 | 0 | 15 | 9366.5628 | 16.1068 | 15.7692 | 7107.0414 | 0 | 15 | 9366.5628 | 7107.0414 | 0 | 15 | 9366.5628 | 15.0463 | 14.711 | 7107.0414 | 0 | 15 | 9366.5628 | 7107.0414 | 0 | 15 | 9366.5628 |  | 0 | 0
x | General Load impact Pump speed & control HW |  | If value is "VFD" lookup cost based on the next motor size hp greater than 1.1 times the hp shown under Power (HP) | Pump | HW Pump | HEATSYS1 PUMP VSD | US_LO_HEATSYS1 PUMP VSD | No | No | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | No | No | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | No | No | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | No | VFD | 0 | 0 | 0 | 0 | 4447.6076 | 0 | 15 | 5935.1363 | No | VFD | 0 | 0 | 0 | 0 | 7107.0414 | 0 | 15 | 9366.5628 |  | 0 | 0 |  |  |  | 0 | 0 | 0 | 4447.6076 | 7107.0414
|  | VFD_Size | cost input item for VFD | Pump | HW Pump | HEATSYS1 PUMP Pump Power [hp] | US_LO_HEATSYS1 PUMP Pump Power [hp] | 4.9618 | 4.9515 | 4447.6076 | 0 | 15 | 5935.1363 | 4447.6076 | 0 | 15 | 5935.1363 | 7.6403 | 7.6255 | 4447.6076 | 0 | 15 | 5935.1363 | 4447.6076 | 0 | 15 | 5935.1363 | 6.526 | 6.5109 | 4447.6076 | 0 | 15 | 5935.1363 | 4447.6076 | 0 | 15 | 5935.1363 | 8.8435 | 8.7331 | 4447.6076 | 0 | 15 | 5935.1363 | 4447.6076 | 0 | 15 | 5935.1363 | 9.5051 | 9.3025 | 7107.0414 | 0 | 15 | 9366.5628 | 7107.0414 | 0 | 15 | 9366.5628 |  | 0 | 0
| 90.1-16g occ standby controls | occ_standby | 74 conditioned zones |  |  |  |  | 0 | 74 | 0 | 0 | 0 | 0 | 2467.1297 | 0 | 15 | 4329.5216 | 0 | 74 | 0 | 0 | 0 | 0 | 2467.1297 | 0 | 15 | 4329.5216 | 0 | 74 | 0 | 0 | 0 | 0 | 2467.1297 | 0 | 15 | 4329.5216 | 0 | 74 | 0 | 0 | 0 | 0 | 2467.1297 | 0 | 15 | 4329.5216 | 0 | 74 | 0 | 0 | 0 | 0 | 2467.1297 | 0 | 15 | 4329.5216 |  | 0 | 2467.1297
| 90.1-16 bq dry cooler efficiency | Dry_Cooler | Manually lookup cost based on capacity, which is hardcoded as 582,060 W, or 48.5 tons. |  |  | each 50 ton cooler |  | 1 | 1 | 54202.5339 | 0 | 20 | 60668.7872 | 56394.4214 | 0 | 20 | 63079.8635 | 1 | 1 | 54202.5339 | 0 | 20 | 60668.7872 | 56394.4214 | 0 | 20 | 63079.8635 | 1 | 1 | 54202.5339 | 0 | 20 | 60668.7872 | 56394.4214 | 0 | 20 | 63079.8635 | 1 | 1 | 54202.5339 | 0 | 20 | 60668.7872 | 56394.4214 | 0 | 20 | 63079.8635 | 1 | 1 | 54202.5339 | 0 | 20 | 60668.7872 | 56394.4214 | 0 | 20 | 63079.8635 |  | 0 | 2191.8875
| 90.1-16 be CRAC efficiency | CRAC_Efficiency | Cost based on capacity, which is hardcoded as 20 tons basement. 6 units total |  |  | units are 20 tons |  | 6 | 6 | 450291.4471 | 0 | 20 | 523702.5316 | 583462.1236 | 0 | 20 | 670190.2757 | 6 | 6 | 450291.4471 | 0 | 20 | 523702.5316 | 583462.1236 | 0 | 20 | 670190.2757 | 6 | 6 | 450291.4471 | 0 | 20 | 523702.5316 | 583462.1236 | 0 | 20 | 670190.2757 | 6 | 6 | 450291.4471 | 0 | 20 | 523702.5316 | 583462.1236 | 0 | 20 | 670190.2757 | 6 | 6 | 450291.4471 | 0 | 20 | 523702.5316 | 583462.1236 | 0 | 20 | 670190.2757 |  | 0 | 133170.6765
| 90.1-16 be CRAC efficiency | CRAC_Efficiency_Small | Cost based on capacity, which is hardcoded as 2.5 tons each of bot, mid, top. 12 units total |  |  | units are 2.5 tons |  | 12 | 12 | 427713.8014 | 0 | 20 | 491337.219 | 363704.6816 | 0 | 20 | 420927.1871 | 12 | 12 | 427713.8014 | 0 | 20 | 491337.219 | 363704.6816 | 0 | 20 | 420927.1871 | 12 | 12 | 427713.8014 | 0 | 20 | 491337.219 | 363704.6816 | 0 | 20 | 420927.1871 | 12 | 12 | 427713.8014 | 0 | 20 | 491337.219 | 363704.6816 | 0 | 20 | 420927.1871 | 12 | 12 | 427713.8014 | 0 | 20 | 491337.219 | 363704.6816 | 0 | 20 | 420927.1871 |  | 0 | -64009.1198
| 90.1-07aj | Motor Efficiency | lookup cost based on the next motor size hp greater than 1.1 times the hp shown in this row. If bhp is between .7 and 1, value = 1. If < 0.7 = 0 - not subject to eff. req)
Not in 2016 |  | Motor_Efficiency |  | VAV_BOT | VAVCHW | VAV_BOT WITH REHEAT Fan Power [hp] | US_LO_VAV_BOT WITH REHEAT Fan Power [hp] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
Not in 2016 |  |  |  | VAV_MID (estimate based on 5 systems, not 1 as modeled, costs multiplied by 5. Modeled system is too large for real application. Row included to screen out Out of Range * 5 which gives a Value error) | VAVCHW |  |  |  |  | OUT OF RANGE | OUT OF RANGE | #N/A | OUT OF RANGE | OUT OF RANGE | OUT OF RANGE | #N/A | OUT OF RANGE |  |  | OUT OF RANGE | OUT OF RANGE | #N/A | OUT OF RANGE | OUT OF RANGE | OUT OF RANGE | #N/A | OUT OF RANGE |  |  | OUT OF RANGE | OUT OF RANGE | #N/A | OUT OF RANGE | OUT OF RANGE | OUT OF RANGE | #N/A | OUT OF RANGE |  |  | OUT OF RANGE | OUT OF RANGE | #N/A | OUT OF RANGE | OUT OF RANGE | OUT OF RANGE | #N/A | OUT OF RANGE |  |  | OUT OF RANGE | OUT OF RANGE | #N/A | OUT OF RANGE | OUT OF RANGE | OUT OF RANGE | #N/A | OUT OF RANGE
|  | Motor_Efficiency |  | VAV_MID | VAVCHW | VAV_MID WITH REHEAT Fan Power [hp] | US_LO_VAV_MID WITH REHEAT Fan Power [hp] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
Not in 2016 |  | Motor_Efficiency |  | VAV_TOP | VAVCHW | VAV_TOP WITH REHEAT Fan Power [hp] | US_LO_VAV_TOP WITH REHEAT Fan Power [hp] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
Not in 2016 |  | Motor_Efficiency |  | CAV_BAS | CAVCHW | CAV_BAS Fan Power [hp] | US_LO_CAV_BAS Fan Power [hp] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
Not in 2016 |  | Motor_Efficiency |  | DATACENTER BASEMENT |  | DATACENTER BASEMENT Fan Power [hp] | US_LO_DATACENTER BASEMENT Fan Power [hp] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
Not in 2016 |  | Motor_Efficiency |  | DATACENTER MID |  | DATACENTER MID Fan Power [hp] | US_LO_DATACENTER MID Fan Power [hp] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
Not in 2016 |  | Motor_Efficiency |  | Pump | Primary CHW | COOLSYS1 PUMP Pump Power [hp] | US_LO_COOLSYS1 PUMP Pump Power [hp] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
Not in 2016 |  | Motor_Efficiency |  | Pump | Secondary CHW | COOLSYS1 PUMP SECONDARY Pump Power [hp] | US_LO_COOLSYS1 PUMP SECONDARY Pump Power [hp] | 17.0246 | 16.7054 | 5929.6923 | 0 | 18 | 7324.6076 | 6177.3306 | 0 | 18 | 7597.0097 | 15.975 | 15.6551 | 5929.6923 | 0 | 18 | 7324.6076 | 6177.3306 | 0 | 18 | 7597.0097 | 13.6758 | 13.3581 | 5929.6923 | 0 | 18 | 7324.6076 | 4849.3416 | 0 | 18 | 6081.5933 | 16.1068 | 15.7692 | 5929.6923 | 0 | 18 | 7324.6076 | 6177.3306 | 0 | 18 | 7597.0097 | 15.0463 | 14.711 | 5929.6923 | 0 | 18 | 7324.6076 | 6177.3306 | 0 | 18 | 7597.0097
Not in 2016 |  | Motor_Efficiency |  | Pump | Condenser Water | TOWERWATERSYS PUMP Pump Power [hp] | US_LO_TOWERWATERSYS PUMP Pump Power [hp] | 45.3836 | 44.2368 | 13429.1457 | 0 | 18 | 16042.1724 | 14033.8665 | 0 | 18 | 16707.3652 | 42.6205 | 41.4894 | 13429.1457 | 0 | 18 | 16042.1724 | 14033.8665 | 0 | 18 | 16707.3652 | 36.6081 | 35.5188 | 13429.1457 | 0 | 18 | 16042.1724 | 10120.1326 | 0 | 18 | 12265.6868 | 42.979 | 41.7986 | 13429.1457 | 0 | 18 | 16042.1724 | 14033.8665 | 0 | 18 | 16707.3652 | 39.9687 | 38.5861 | 13429.1457 | 0 | 18 | 16042.1724 | 14033.8665 | 0 | 18 | 16707.3652
Not in 2016 |  | Motor_Efficiency |  | Pump | Hot Water | HEATSYS1 PUMP Pump Power [hp] | US_LO_HEATSYS1 PUMP Pump Power [hp] | 4.9618 | 4.9515 | 2934.1197 | 0 | 18 | 3760.1593 | 3045.7408 | 0 | 18 | 3882.9426 | 7.6403 | 7.6255 | 3962.9578 | 0 | 18 | 5051.9427 | 4115.8645 | 0 | 18 | 5220.14 | 6.526 | 6.5109 | 2934.1197 | 0 | 18 | 3760.1593 | 3045.7408 | 0 | 18 | 3882.9426 | 8.8435 | 8.7331 | 3962.9578 | 0 | 18 | 5051.9427 | 4115.8645 | 0 | 18 | 5220.14 | 9.5051 | 9.3025 | 4663.9319 | 0 | 18 | 5877.6426 | 4849.3416 | 0 | 18 | 6081.5933
NOTES:
[10 empty] | 9305380.4274 |  |  | 14247626.7024 | 9546065.4436 |  |  | 14502280.2366 |  |  | 9815301.2057 |  |  | 14867743.4978 | 9781098.999 |  |  | 14799821.1563 |  |  | 9502360.5661 |  |  | 14612340.84 | 9454382.0994 |  |  | 14466582.2221 |  |  | 9962968.0842 |  |  | 15019592.5218 | 9923520.8572 |  |  | 14942638.1705 |  |  | 9951319.3717 |  |  | 14998644.9261 | 9907369.0576 |  |  | 14915913.3125
[9 empty] | 14247626.7024 |  |  |  | 14502280.2366 | [5 empty] | 14867743.4978 |  |  |  | 14799821.1563 | [5 empty] | 14612340.84 |  |  |  | 14466582.2221 | [5 empty] | 15019592.5218 |  |  |  | 14942638.1705 | [5 empty] | 14998644.9261 |  |  |  | 14915913.3125

## HVAC Standalone Retail Proto
90.1 Cost Effectiveness - Cost Estimate - HVAC - Standalone Retail | [7 empty] | Standalone Retail
[10 empty] | $AP | $AQ | $AR | $BA | $BK | $BL | $BM | $BW |  |  | $AP | $AQ | $AR | $BA | $BK | $BL | $BM | $BW |  |  | $AP | $AQ | $AR | $BA | $BK | $BL | $BM | $BW |  |  | $AP | $AQ | $AR | $BA | $BK | $BL | $BM | $BW |  |  | $AP | $AQ | $AR | $BA | $BK | $BL | $BM | $BW | Find Row
|  |  | YES |  |  |  |  | 3 | 4 | [8 empty] | 5 | 6 | [8 empty] | 7 | 8 | [8 empty] | 9 | 10 | [8 empty] | 11 | 12
[7 empty] | City-year parameter column |  |  | I | I | I | I | J | J | J | J |  |  | S | S | S | S | T | T | T | T |  |  | AC | AC | AC | AC | AD | AD | AD | AD |  |  | AM | AM | AM | AM | AN | AN | AN | AN |  |  | AW | AW | AW | AW | AX | AX | AX | AX
[7 empty] | Parameter range lookup extension |  |  | _2007Par | _2007Par | _2007Par | _2007Par | _2010Par | _2010Par | _2010Par | _2010Par |  |  | _2007Par | _2007Par | _2007Par | _2007Par | _2010Par | _2010Par | _2010Par | _2010Par |  |  | _2007Par | _2007Par | _2007Par | _2007Par | _2010Par | _2010Par | _2010Par | _2010Par |  |  | _2007Par | _2007Par | _2007Par | _2007Par | _2010Par | _2010Par | _2010Par | _2010Par |  |  | _2007Par | _2007Par | _2007Par | _2007Par | _2010Par | _2010Par | _2010Par | _2010Par
[7 empty] | Cost range lookup extension |  |  | _2007Costs | _2007Costs | _2007Costs | _2007Costs | _2010Costs | _2010Costs | _2010Costs | _2010Costs |  |  | _2007Costs | _2007Costs | _2007Costs | _2007Costs | _2010Costs | _2010Costs | _2010Costs | _2010Costs |  |  | _2007Costs | _2007Costs | _2007Costs | _2007Costs | _2010Costs | _2010Costs | _2010Costs | _2010Costs |  |  | _2007Costs | _2007Costs | _2007Costs | _2007Costs | _2010Costs | _2010Costs | _2010Costs | _2010Costs |  |  | _2007Costs | _2007Costs | _2007Costs | _2007Costs | _2010Costs | _2010Costs | _2010Costs | _2010Costs
[7 empty] | Cost range column index values |  |  | 9 | 10 | 11 | 20 | 10 | 11 | 12 | 22 |  |  | 9 | 10 | 11 | 20 | 10 | 11 | 12 | 22 |  |  | 9 | 10 | 11 | 20 | 10 | 11 | 12 | 22 |  |  | 9 | 10 | 11 | 20 | 10 | 11 | 12 | 22 |  |  | 9 | 10 | 11 | 20 | 10 | 11 | 12 | 22
[8 empty] | Climate Zone 1 | 2A | Base Code | 2019 |  |  | Target Code | 2022 |  |  | Climate Zone 2 | 3A | Base Code | 2019 |  |  | Target Code | 2022 |  |  | Climate Zone 3 | 3B | Base Code | 2019 |  |  | Target Code | 2022 |  |  | Climate Zone 4 | 4A | Base Code | 2019 |  |  | Target Code | 2022 |  |  | Climate Zone 5 | 5A | Base Code | 2019 |  |  | Target Code | 2022 |  |  |  | First cost difference |  | 2019 | vs | 2022
Costs row marked x, other rows not marked | [7 empty] | Base | Target | [8 empty] | Base | Target | [8 empty] | Base | Target | [8 empty] | Base | Target | [8 empty] | Base | Target | [9 empty] | Total new construction (added cost)
| Addendum or general | Key Word | Description | Model | Type | Parameters | Lookup Value in HVAC Data, Current_HVAC_Data | Prototype | Prototype | Total New | Maintenance | Replacement Life | Total | Total New | Maintenance | Replacement Life | Total | Prototype | Prototype | Total New | Maintenance | Replacement Life | Total | Total New | Maintenance | Replacement Life | Total | Prototype | Prototype | Total New | Maintenance | Replacement Life | Total | Total New | Maintenance | Replacement Life | Total | Prototype | Prototype | Total New | Maintenance | Replacement Life | Total | Total New | Maintenance | Replacement Life | Total | Prototype | Prototype | Total New | Maintenance | Replacement Life | Total | Total New | Maintenance | Replacement Life | Total |  | 2A | 3A | 3B | 4A | 5A
| load change |  |  | Object |  |  |  | Data | Data | Construction |  |  | Replacement Cost | Construction |  |  | Replacement Cost | Data | Data | Construction |  |  | Replacement Cost | Construction |  |  | Replacement Cost | Data | Data | Construction |  |  | Replacement Cost | Construction |  |  | Replacement Cost | Data | Data | Construction |  |  | Replacement Cost | Construction |  |  | Replacement Cost | Data | Data | Construction |  |  | Replacement Cost | Construction |  |  | Replacement Cost
| HVAC System - general load change | CAV_DX | lookup based on cooling tons
x |  | CAV_DX |  | PSZ-AC:1 | CAVDX | PSZ-AC:1 Cooling Capacity [ton] | US_RS_PSZ-AC:1 Cooling Capacity [ton] | 8.986 | 8.7948 | 12946.9747 | 0 | 15 | 17175.386 | 12779.0756 | 0 | 15 | 16952.4681 | 8.0656 | 7.8931 | 12073.3752 | 0 | 15 | 16062.8629 | 11896.0276 | 0 | 15 | 15846.1918 | 8.9189 | 8.6917 | 12888.0672 | 0 | 15 | 17097.1751 | 12688.5048 | 0 | 15 | 16832.2181 | 7.9086 | 7.7983 | 11911.9928 | 0 | 15 | 15865.6969 | 11798.4735 | 0 | 15 | 15727.0068 | 8.5417 | 8.2697 | 12556.8155 | 0 | 15 | 16657.3757 | 12283.3578 | 0 | 15 | 16319.4053 |  | -167.8991 | -177.3476 | -199.5625 | -113.5193 | -273.4577
x |  | CAV_DX | cost estimate based on two smaller units, costs per unit multiplied by two | PSZ-AC:2 | CAVDX | PSZ-AC:2 Cooling Capacity [ton] | US_RS_PSZ-AC:2 Cooling Capacity [ton] | 24.7816 | 23.2774 | 25308.131 | 0 | 15 | 32457.7592 | 24287.0947 | 0 | 15 | 31223.0149 | 24.2593 | 23.1907 | 24953.5924 | 0 | 15 | 32029.0139 | 24228.2549 | 0 | 15 | 31151.8596 | 23.385 | 22.2142 | 24360.1132 | 0 | 15 | 31311.3165 | 23565.4033 | 0 | 15 | 30350.2697 | 23.6271 | 22.5418 | 24524.4796 | 0 | 15 | 31510.0856 | 23787.7882 | 0 | 15 | 30619.201 | 21.7631 | 19.9797 | 23259.167 | 0 | 15 | 29979.9367 | 22047.6462 | 0 | 15 | 28514.3073 |  | -1021.0362 | -725.3375 | -794.7099 | -736.6914 | -1211.5208
x |  | CAV_DX |  | PSZ-AC:3 | CAVDX | PSZ-AC:3 Cooling Capacity [ton] | US_RS_PSZ-AC:3 Cooling Capacity [ton] | 6.9714 | 6.7039 | 10826.4627 | 0 | 15 | 14576.3435 | 10489.9105 | 0 | 15 | 14183.8218 | 6.4897 | 6.2459 | 10220.3639 | 0 | 15 | 13869.4489 | 9913.5752 | 0 | 15 | 13511.6405 | 6.6598 | 6.3564 | 10434.4089 | 0 | 15 | 14119.0901 | 10052.6281 | 0 | 15 | 13673.8182 | 6.7001 | 6.0487 | 10485.0871 | 0 | 15 | 14178.1962 | 9665.3583 | 0 | 15 | 13222.1445 | 6.3109 | 5.5947 | 9995.2873 | 0 | 15 | 13606.9415 | 9257.9181 | 0 | 15 | 12693.3101 |  | -336.5522 | -306.7886 | -381.7808 | -819.7287 | -737.3692
x |  | CAV_DX |  | PSZ-AC:4 | CAVDX | PSZ-AC:4 Cooling Capacity [ton] | US_RS_PSZ-AC:4 Cooling Capacity [ton] | 6.0091 | 5.668 | 9615.5067 | 0 | 15 | 13164.0024 | 9320.5555 | 0 | 15 | 12776.0694 | 5.4903 | 5.1573 | 9168.7629 | 0 | 15 | 12575.5142 | 8884.3862 | 0 | 15 | 12199.7828 | 5.5488 | 5.1647 | 9218.7801 | 0 | 15 | 12641.5991 | 8890.7145 | 0 | 15 | 12208.1441 | 5.7137 | 5.0315 | 9359.5624 | 0 | 15 | 12827.6071 | 8776.9672 | 0 | 15 | 12057.856 | 5.3139 | 4.5501 | 9018.119 | 0 | 15 | 12376.4766 | 8373.3244 | 0 | 15 | 11527.8002 |  | -294.9512 | -284.3767 | -328.0655 | -582.5952 | -644.7946
x |  | Air Distribution | curve fit from Solarc cost calculations - described in HVAC Costs Comp. Material, labor, and project cost adjustments applied in this worksheet. |  |  | sum of PSZ-AC:1 Supply Flow Rate [cfm] to PSZ-AC:4 Supply Flow Rate [cfm] (not the sum of the cooling capacity) |  | 22460.128 | 21188.8 | 279838.303 | 0 | 30 | 350558.4634 | 274148.3581 | 0 | 30 | 343739.1348 | 22375.3728 | 21040.4784 | 279458.9733 | 0 | 30 | 350103.8415 | 273484.5312 | 0 | 30 | 342943.5464 | 25702.0144 | 24218.7984 | 294347.6626 | 0 | 30 | 367947.7515 | 287709.3935 | 0 | 30 | 359991.8681 | 22587.2608 | 20892.1568 | 280407.2975 | 0 | 30 | 351240.3963 | 272820.7043 | 0 | 30 | 342147.9581 | 22502.5056 | 20171.7376 | 280027.9678 | 0 | 30 | 350785.7744 | 269596.4021 | 0 | 30 | 338283.6718 |  | -5689.9449 | -5974.4422 | -6638.2691 | -7586.5932 | -10431.5657
|  |  | Material |  |  | PSZ-AC:1 Supply Flow Rate [cfm] | US_RS_PSZ-AC:1 Supply Flow Rate [cfm] | 3284.264 | 3199.5088 | [8 empty] | 3157.1312 | 3051.1872 | [8 empty] | 3729.2288 | 3623.2848 | [8 empty] | 3008.8096 | 2924.0544 | [8 empty] | 3199.5088 | 3072.376
|  |  | y = 1.6479x + 55981 |  |  | PSZ-AC:2 Supply Flow Rate [cfm] | US_RS_PSZ-AC:2 Supply Flow Rate [cfm] | 14874.5376 | 13963.4192 | [8 empty] | 15065.2368 | 14111.7408 | [8 empty] | 17120.5504 | 16061.1104 | [8 empty] | 15107.6144 | 14111.7408 | [8 empty] | 14874.5376 | 13370.1328
|  |  | Labor |  |  | PSZ-AC:3 Supply Flow Rate [cfm] | US_RS_PSZ-AC:3 Supply Flow Rate [cfm] | 2373.1456 | 2246.0128 | [8 empty] | 2309.5792 | 2182.4464 | [8 empty] | 2690.9776 | 2542.656 | [8 empty] | 2457.9008 | 2161.2576 | [8 empty] | 2457.9008 | 2118.88
|  |  | y = 0.2548x + 18981 |  |  | PSZ-AC:4 Supply Flow Rate [cfm] | US_RS_PSZ-AC:4 Supply Flow Rate [cfm] | 1928.1808 | 1779.8592 | [8 empty] | 1843.4256 | 1695.104 | [8 empty] | 2161.2576 | 1991.7472 | [8 empty] | 2012.936 | 1695.104 | [8 empty] | 1970.5584 | 1610.3488
0 | 90.1-10ca | Vestibule_Control | Lock out vestibule or air curtain heat on outside air temperature |  |  | Vestibule count | US_SR_Vestibule count | 1 | 1 | 370.5626 | 0 | 15 | 494.9529 | 613.9657 | 0 | 15 | 616.0021 | 1 | 1 | 370.5626 | 0 | 15 | 494.9529 | 613.9657 | 0 | 15 | 616.0021 | 1 | 1 | 370.5626 | 0 | 15 | 494.9529 | 613.9657 | 0 | 15 | 616.0021 | 1 | 1 | 370.5626 | 0 | 15 | 494.9529 | 613.9657 | 0 | 15 | 616.0021 | 1 | 1 | 370.5626 | 0 | 15 | 494.9529 | 613.9657 | 0 | 15 | 616.0021 | 505
0 | 90.1-10aa 90.1-10cb | Optimum_Start_Control | Increase in controls cost to accommodate optimum start through addenda 90.1-10aa and 90.1-10cb | PSZ-AC_2:7 | CAVDX | Unit count | US_SR_Unit count | 5 | 5 | 2535.9013 | 0 | 15 | 3226.1615 | 5691.3242 | 0 | 15 | 6619.8338 | 5 | 5 | 2535.9013 | 0 | 15 | 3226.1615 | 5691.3242 | 0 | 15 | 6619.8338 | 5 | 5 | 2535.9013 | 0 | 15 | 3226.1615 | 5691.3242 | 0 | 15 | 6619.8338 | 5 | 5 | 2535.9013 | 0 | 15 | 3226.1615 | 5691.3242 | 0 | 15 | 6619.8338 | 5 | 5 | 2535.9013 | 0 | 15 | 3226.1615 | 5691.3242 | 0 | 15 | 6619.8338 | 508
| 90.1-10aq |  |  |  |  | For 2013, Cost for 2 stage fan and added cooling stage applies if single zone DX system Cooling Capacity [ton] above 5.4167 tons, prototype value shown as "yes" if so, or "no" if not. | If applicable, add the fan and staging cost together for the target code; For units greater than 110 MBH (9.167 tons) include fan control only in the base case per 2010 requirements.
0 |  |  | Capacity check & Select | PSZ-AC:1 | CAVDX |  |  | No | Yes | 0 | 0 | 0 | 0 | 1002.1536 | 0 | 15 | 1102.369 | No | Yes | 0 | 0 | 0 | 0 | 924.2712 | 0 | 15 | 1016.6983 | No | Yes | 0 | 0 | 0 | 0 | 993.2442 | 0 | 15 | 1092.5687 | No | Yes | 0 | 0 | 0 | 0 | 916.0787 | 0 | 15 | 1007.6866 | No | Yes | 0 | 0 | 0 | 0 | 956.7987 | 0 | 15 | 1052.4785
| Upgrade to 2-speed fan |  | curve fit from AHRI cost survey | PSZ-AC:1 | CAVDX | PSZ-AC:1 Cooling Capacity [ton] | US_RS_PSZ-AC:1 Cooling Capacity [ton] | 8.986 | 8.7948 | 396.5692 | 0 | 15 | 436.2261 | 394.7153 | 0 | 15 | 434.1868 | 8.0656 | 7.8931 | 387.6448 | 0 | 15 | 351.056 | 385.9731 | 0 | 15 | 424.5704 | 8.9189 | 8.6917 | 395.9187 | 0 | 15 | 435.5106 | 393.7152 | 0 | 15 | 433.0867 | 7.9086 | 7.7983 | 386.1236 | 0 | 15 | 424.7359 | 385.0535 | 0 | 15 | 423.5588 | 8.5417 | 8.2697 | 392.2611 | 0 | 15 | 431.4872 | 389.6242 | 0 | 15 | 428.5867
| Add one stage of cooling |  | curve fit from AHRI cost survey | PSZ-AC:1 | CAVDX | PSZ-AC:1 Cooling Capacity [ton] | US_RS_PSZ-AC:1 Cooling Capacity [ton] | 8.986 | 8.7948 | 622.1005 | 0 | 15 | 684.3106 | 607.4383 | 0 | 15 | 668.1822 | 8.0656 | 7.8931 | 551.5198 | 0 | 15 | 606.6717 | 538.2981 | 0 | 15 | 592.1279 | 8.9189 | 8.6917 | 616.9563 | 0 | 15 | 678.6519 | 599.529 | 0 | 15 | 659.4819 | 7.9086 | 7.7983 | 539.4883 | 0 | 15 | 593.4372 | 531.0252 | 0 | 15 | 584.1277 | 8.5417 | 8.2697 | 588.0289 | 0 | 15 | 646.8318 | 567.1744 | 0 | 15 | 623.8919
0 |  |  | Capacity check & Select | PSZ-AC:2 | CAVDX |  |  | Yes | Yes | 789.9792 | 0 | 15 | 868.9772 | 4263.6344 | 0 | 15 | 4689.9978 | Yes | Yes | 779.8514 | 0 | 15 | 351.056 | 4248.6602 | 0 | 15 | 4673.5262 | Yes | Yes | 762.8979 | 0 | 15 | 839.1877 | 4079.9701 | 0 | 15 | 4487.9671 | Yes | Yes | 767.5932 | 0 | 15 | 844.3525 | 4136.5652 | 0 | 15 | 4550.2217 | Yes | Yes | 731.4479 | 0 | 15 | 804.5927 | 3693.9617 | 0 | 15 | 4063.3578
| Upgrade to 2-speed fan |  | curve fit from AHRI cost survey | PSZ-AC:2 | CAVDX | PSZ-AC:2 Cooling Capacity [ton] | US_RS_PSZ-AC:2 Cooling Capacity [ton] | 49.5632 | 46.5549 | 789.9792 | 0 | 15 | 868.9772 | 760.812 | 0 | 15 | 836.8932 | 48.5186 | 46.3815 | 779.8514 | 0 | 15 | 351.056 | 759.1312 | 0 | 15 | 835.0443 | 46.77 | 44.4285 | 762.8979 | 0 | 15 | 839.1877 | 740.1959 | 0 | 15 | 814.2155 | 47.2543 | 45.0837 | 767.5932 | 0 | 15 | 844.3525 | 746.5486 | 0 | 15 | 821.2035 | 43.5262 | 39.9594 | 731.4479 | 0 | 15 | 804.5927 | 696.867 | 0 | 15 | 766.5537
| Add one stage of cooling |  | curve fit from AHRI cost survey | PSZ-AC:2 | CAVDX | PSZ-AC:2 Cooling Capacity [ton] | US_RS_PSZ-AC:2 Cooling Capacity [ton] | 49.5632 | 46.5549 | 3733.5001 | 0 | 15 | 4106.8501 | 3502.8224 | 0 | 15 | 3853.1046 | 48.5186 | 46.3815 | 3653.4009 | 0 | 15 | 4018.741 | 3489.529 | 0 | 15 | 3838.4819 | 46.77 | 44.4285 | 3519.3191 | 0 | 15 | 3871.251 | 3339.7742 | 0 | 15 | 3673.7516 | 47.2543 | 45.0837 | 3556.4536 | 0 | 15 | 3912.099 | 3390.0165 | 0 | 15 | 3729.0182 | 43.5262 | 39.9594 | 3270.5877 | 0 | 15 | 3597.6465 | 2997.0947 | 0 | 15 | 3296.8041
0 |  |  | Capacity check & Select | PSZ-AC:3 | CAVDX |  |  | No | Yes | 0 | 0 | 0 | 0 | 821.5556 | 0 | 15 | 903.7112 | No | Yes | 0 | 0 | 0 | 0 | 781.9974 | 0 | 15 | 860.1971 | No | Yes | 0 | 0 | 0 | 0 | 791.5416 | 0 | 15 | 870.6958 | No | Yes | 0 | 0 | 0 | 0 | 764.9603 | 0 | 15 | 841.4564 | No | Yes | 0 | 0 | 0 | 0 | 725.7442 | 0 | 15 | 798.3186
| Upgrade to 2-speed fan |  | curve fit from AHRI cost survey | PSZ-AC:3 | CAVDX | PSZ-AC:3 Cooling Capacity [ton] | US_RS_PSZ-AC:3 Cooling Capacity [ton] | 6.9714 | 6.7039 | 377.0364 | 0 | 15 | 414.74 | 374.4434 | 0 | 15 | 411.8877 | 6.4897 | 6.2459 | 372.3667 | 0 | 15 | 351.056 | 370.003 | 0 | 15 | 407.0033 | 6.6598 | 6.3564 | 374.0158 | 0 | 15 | 411.4174 | 371.0744 | 0 | 15 | 408.1818 | 6.7001 | 6.0487 | 374.4062 | 0 | 15 | 411.8469 | 368.0907 | 0 | 15 | 404.8997 | 6.3109 | 5.5947 | 370.6326 | 0 | 15 | 407.6958 | 363.6887 | 0 | 15 | 400.0576
| Add one stage of cooling |  | curve fit from AHRI cost survey | PSZ-AC:3 | CAVDX | PSZ-AC:3 Cooling Capacity [ton] | US_RS_PSZ-AC:3 Cooling Capacity [ton] | 6.9714 | 6.7039 | 467.6194 | 0 | 15 | 514.3814 | 447.1122 | 0 | 15 | 491.8235 | 6.4897 | 6.2459 | 430.6879 | 0 | 15 | 473.7567 | 411.9943 | 0 | 15 | 453.1937 | 6.6598 | 6.3564 | 443.7304 | 0 | 15 | 488.1034 | 420.4672 | 0 | 15 | 462.514 | 6.7001 | 6.0487 | 446.8183 | 0 | 15 | 491.5002 | 396.8697 | 0 | 15 | 436.5566 | 6.3109 | 5.5947 | 416.9733 | 0 | 15 | 458.6706 | 362.0555 | 0 | 15 | 398.261
0 |  |  | Capacity check & Select | PSZ-AC:4 | CAVDX |  |  | No | Yes | 0 | 0 | 0 | 0 | 732.0792 | 0 | 15 | 805.2871 | No | No | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | No | No | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | No | No | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | No | No | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Upgrade to 2-speed fan |  | curve fit from AHRI cost survey | PSZ-AC:4 | CAVDX | PSZ-AC:4 Cooling Capacity [ton] | US_RS_PSZ-AC:4 Cooling Capacity [ton] | 6.0091 | 5.668 | 367.7066 | 0 | 15 | 404.4772 | 364.3998 | 0 | 15 | 400.8398 | 5.4903 | 5.1573 | 362.6766 | 0 | 15 | 351.056 | 359.4481 | 0 | 15 | 395.393 | 5.5488 | 5.1647 | 363.2444 | 0 | 15 | 399.5688 | 359.52 | 0 | 15 | 395.472 | 5.7137 | 5.0315 | 364.8426 | 0 | 15 | 401.3269 | 358.2287 | 0 | 15 | 394.0515 | 5.3139 | 4.5501 | 360.9664 | 0 | 15 | 397.063 | 353.5611 | 0 | 15 | 388.9172
| Add one stage of cooling |  | curve fit from AHRI cost survey | PSZ-AC:4 | CAVDX | PSZ-AC:4 Cooling Capacity [ton] | US_RS_PSZ-AC:4 Cooling Capacity [ton] | 6.0091 | 5.668 | 393.8321 | 0 | 15 | 433.2153 | 367.6794 | 0 | 15 | 404.4473 | 5.4903 | 5.1573 | 354.0507 | 0 | 15 | 389.4557 | 328.5178 | 0 | 15 | 361.3696 | 5.5488 | 5.1647 | 358.5415 | 0 | 15 | 394.3956 | 329.086 | 0 | 15 | 361.9946 | 5.7137 | 5.0315 | 371.1816 | 0 | 15 | 408.2998 | 318.8732 | 0 | 15 | 350.7605 | 5.3139 | 4.5501 | 340.5251 | 0 | 15 | 374.5776 | 281.958 | 0 | 15 | 310.1539
| 90.1-10bt and impact of any changes in OA requirements | Energy_Recovery_Packaged | if "Yes" lookup and interpolate costs based on outside airflow, cfm. |  |  | [Yes,No] are parameter values, indicating if expanded ERV requirements apply. Based on 2010 and 2013 standards.
0 |  | Energy_Recovery_Packaged |  | PSZ-AC:2 | CAVDX | PSZ_AC_2 Energy Recovery [yes/no] | US_RS_PSZ_AC_2 Energy Recovery [yes/no] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  | Energy_Recovery_Packaged |  | PSZ-AC:2 | CAVDX | PSZ-AC:2 OA Rate [cfm] | US_RS_PSZ-AC:2 OA Rate [cfm] | 4005.3824 | 4005.3824 | 30331.4516 | 255.0825 | 15 | 34990.3933 | 30331.4516 | 255.0825 | 15 | 34990.3933 | 4005.3824 | 4005.3824 | 30331.4516 | 255.0825 | 15 | 34990.3933 | 30331.4516 | 255.0825 | 15 | 34990.3933 | 4005.3824 | 4005.3824 | 30331.4516 | 255.0825 | 15 | 34990.3933 | 30331.4516 | 255.0825 | 15 | 34990.3933 | 4005.3824 | 4005.3824 | 30331.4516 | 255.0825 | 15 | 34990.3933 | 30331.4516 | 255.0825 | 15 | 34990.3933 | 4005.3824 | 4005.3824 | 30331.4516 | 255.0825 | 15 | 34990.3933 | 30331.4516 | 255.0825 | 15 | 34990.3933
| 90.1-16a | Outdoor_Air_Dampers | Motorized return air damper
|  | Outdoor_Air_Dampers | system cost |  |  |  |  | motorized | motorized | 420.6784 | 0 | 20 | 404.0412 | 491.9628 | 0 | 20 | 564.2386 | motorized | motorized | 420.6784 | 0 | 20 | 404.0412 | 491.9628 | 0 | 20 | 564.2386 | motorized | motorized | 420.6784 | 0 | 20 | 404.0412 | 491.9628 | 0 | 20 | 564.2386 | motorized | motorized | 420.6784 | 0 | 20 | 404.0412 | 491.9628 | 0 | 20 | 564.2386 | motorized | motorized | 420.6784 | 0 | 20 | 404.0412 | 491.9628 | 0 | 20 | 564.2386
|  | Outdoor_Air_Dampers_Gravity | item cost |  |  | PSZ-AC:1 OA Rate [cfm] | US_RS_PSZ-AC:1 OA Rate [cfm] | 490.6902 | 490.6902 | 316.6595 | 105.7606 | 20 | 322.129 | 343.5975 | 105.7606 | 20 | 408.9198 | 490.6902 | 490.6902 | 316.6595 | 105.7606 | 20 | 322.129 | 343.5975 | 105.7606 | 20 | 408.9198 | 490.6902 | 490.6902 | 316.6595 | 105.7606 | 20 | 322.129 | 343.5975 | 105.7606 | 20 | 408.9198 | 490.6902 | 490.6902 | 316.6595 | 105.7606 | 20 | 322.129 | 343.5975 | 105.7606 | 20 | 408.9198 | 490.6902 | 490.6902 | 316.6595 | 105.7606 | 20 | 322.129 | 343.5975 | 105.7606 | 20 | 408.9198
|  | Outdoor_Air_Dampers_Motorized | item cost | PSZ-AC:1 | CAVDX | PSZ-AC:1 OA Rate [cfm] | US_RS_PSZ-AC:1 OA Rate [cfm] | 490.6902 | 490.6902 | 737.3379 | 105.7606 | 20 | 726.1702 | 835.5603 | 105.7606 | 20 | 973.1585 | 490.6902 | 490.6902 | 737.3379 | 105.7606 | 20 | 726.1702 | 835.5603 | 105.7606 | 20 | 973.1585 | 490.6902 | 490.6902 | 737.3379 | 105.7606 | 20 | 726.1702 | 835.5603 | 105.7606 | 20 | 973.1585 | 490.6902 | 490.6902 | 737.3379 | 105.7606 | 20 | 726.1702 | 835.5603 | 105.7606 | 20 | 973.1585 | 490.6902 | 490.6902 | 737.3379 | 105.7606 | 20 | 726.1702 | 835.5603 | 105.7606 | 20 | 973.1585
|  | Outdoor_Air_Dampers | system cost |  |  |  |  | motorized | motorized | 541.4608 | 0 | 20 | 530.7738 | 641.8185 | 0 | 20 | 743.8083 | motorized | motorized | 541.4608 | 0 | 20 | 530.7738 | 641.8185 | 0 | 20 | 743.8083 | motorized | motorized | 541.4608 | 0 | 20 | 530.7738 | 641.8185 | 0 | 20 | 743.8083 | motorized | motorized | 541.4608 | 0 | 20 | 530.7738 | 641.8185 | 0 | 20 | 743.8083 | motorized | motorized | 541.4608 | 0 | 20 | 530.7738 | 641.8185 | 0 | 20 | 743.8083
|  | Outdoor_Air_Dampers_Gravity | item cost |  |  | PSZ-AC:2 OA Rate [cfm] | US_RS_PSZ-AC:2 OA Rate [cfm] | 4005.3824 | 4005.3824 | 680.3681 | 144.9899 | 20 | 711.9014 | 735.965 | 144.9899 | 20 | 891.0277 | 4005.3824 | 4005.3824 | 680.3681 | 144.9899 | 20 | 711.9014 | 735.965 | 144.9899 | 20 | 891.0277 | 4005.3824 | 4005.3824 | 680.3681 | 144.9899 | 20 | 711.9014 | 735.965 | 144.9899 | 20 | 891.0277 | 4005.3824 | 4005.3824 | 680.3681 | 144.9899 | 20 | 711.9014 | 735.965 | 144.9899 | 20 | 891.0277 | 4005.3824 | 4005.3824 | 680.3681 | 144.9899 | 20 | 711.9014 | 735.965 | 144.9899 | 20 | 891.0277
|  | Outdoor_Air_Dampers_Motorized | item cost | PSZ-AC:2 | CAVDX | PSZ-AC:2 OA Rate [cfm] | US_RS_PSZ-AC:2 OA Rate [cfm] | 4005.3824 | 4005.3824 | 1221.8288 | 144.9899 | 20 | 1242.6751 | 1377.7836 | 144.9899 | 20 | 1634.836 | 4005.3824 | 4005.3824 | 1221.8288 | 144.9899 | 20 | 1242.6751 | 1377.7836 | 144.9899 | 20 | 1634.836 | 4005.3824 | 4005.3824 | 1221.8288 | 144.9899 | 20 | 1242.6751 | 1377.7836 | 144.9899 | 20 | 1634.836 | 4005.3824 | 4005.3824 | 1221.8288 | 144.9899 | 20 | 1242.6751 | 1377.7836 | 144.9899 | 20 | 1634.836 | 4005.3824 | 4005.3824 | 1221.8288 | 144.9899 | 20 | 1242.6751 | 1377.7836 | 144.9899 | 20 | 1634.836
|  | Outdoor_Air_Dampers | system cost |  |  |  |  | motorized | motorized | 408.925 | 0 | 20 | 391.0227 | 478.8933 | 0 | 20 | 547.9108 | motorized | motorized | 408.925 | 0 | 20 | 391.0227 | 478.8933 | 0 | 20 | 547.9108 | motorized | motorized | 408.925 | 0 | 20 | 391.0227 | 478.8933 | 0 | 20 | 547.9108 | motorized | motorized | 408.925 | 0 | 20 | 391.0227 | 478.8933 | 0 | 20 | 547.9108 | motorized | motorized | 408.925 | 0 | 20 | 391.0227 | 478.8933 | 0 | 20 | 547.9108
|  | Outdoor_Air_Dampers_Gravity | item cost |  |  | PSZ-AC:3 OA Rate [cfm] | US_RS_PSZ-AC:3 OA Rate [cfm] | 377.4149 | 377.4149 | 316.7157 | 104.7936 | 20 | 322.2277 | 343.6537 | 104.7936 | 20 | 409.0185 | 377.4149 | 377.4149 | 316.7157 | 104.7936 | 20 | 322.2277 | 343.6537 | 104.7936 | 20 | 409.0185 | 377.4149 | 377.4149 | 316.7157 | 104.7936 | 20 | 322.2277 | 343.6537 | 104.7936 | 20 | 409.0185 | 377.4149 | 377.4149 | 316.7157 | 104.7936 | 20 | 322.2277 | 343.6537 | 104.7936 | 20 | 409.0185 | 377.4149 | 377.4149 | 316.7157 | 104.7936 | 20 | 322.2277 | 343.6537 | 104.7936 | 20 | 409.0185
|  | Outdoor_Air_Dampers_Motorized | item cost | PSZ-AC:3 | CAVDX | PSZ-AC:3 OA Rate [cfm] | US_RS_PSZ-AC:3 OA Rate [cfm] | 377.4149 | 377.4149 | 725.6407 | 104.7936 | 20 | 713.2504 | 822.547 | 104.7936 | 20 | 956.9293 | 377.4149 | 377.4149 | 725.6407 | 104.7936 | 20 | 713.2504 | 822.547 | 104.7936 | 20 | 956.9293 | 377.4149 | 377.4149 | 725.6407 | 104.7936 | 20 | 713.2504 | 822.547 | 104.7936 | 20 | 956.9293 | 377.4149 | 377.4149 | 725.6407 | 104.7936 | 20 | 713.2504 | 822.547 | 104.7936 | 20 | 956.9293 | 377.4149 | 377.4149 | 725.6407 | 104.7936 | 20 | 713.2504 | 822.547 | 104.7936 | 20 | 956.9293
|  | Outdoor_Air_Dampers | system cost |  |  |  |  | motorized | motorized | 408.925 | 0 | 20 | 391.0227 | 478.8933 | 0 | 20 | 547.9108 | motorized | motorized | 408.925 | 0 | 20 | 391.0227 | 478.8933 | 0 | 20 | 547.9108 | motorized | motorized | 408.925 | 0 | 20 | 391.0227 | 478.8933 | 0 | 20 | 547.9108 | motorized | motorized | 408.925 | 0 | 20 | 391.0227 | 478.8933 | 0 | 20 | 547.9108 | motorized | motorized | 408.925 | 0 | 20 | 391.0227 | 478.8933 | 0 | 20 | 547.9108
|  | Outdoor_Air_Dampers_Gravity | item cost |  |  | PSZ-AC:4 OA Rate [cfm] | US_RS_PSZ-AC:4 OA Rate [cfm] | 377.4149 | 377.4149 | 316.7157 | 104.7936 | 20 | 322.2277 | 343.6537 | 104.7936 | 20 | 409.0185 | 377.4149 | 377.4149 | 316.7157 | 104.7936 | 20 | 322.2277 | 343.6537 | 104.7936 | 20 | 409.0185 | 377.4149 | 377.4149 | 316.7157 | 104.7936 | 20 | 322.2277 | 343.6537 | 104.7936 | 20 | 409.0185 | 377.4149 | 377.4149 | 316.7157 | 104.7936 | 20 | 322.2277 | 343.6537 | 104.7936 | 20 | 409.0185 | 377.4149 | 377.4149 | 316.7157 | 104.7936 | 20 | 322.2277 | 343.6537 | 104.7936 | 20 | 409.0185
|  | Outdoor_Air_Dampers_Motorized | item cost | PSZ-AC:4 | CAVDX | PSZ-AC:4 OA Rate [cfm] | US_RS_PSZ-AC:4 OA Rate [cfm] | 377.4149 | 377.4149 | 725.6407 | 104.7936 | 20 | 713.2504 | 822.547 | 104.7936 | 20 | 956.9293 | 377.4149 | 377.4149 | 725.6407 | 104.7936 | 20 | 713.2504 | 822.547 | 104.7936 | 20 | 956.9293 | 377.4149 | 377.4149 | 725.6407 | 104.7936 | 20 | 713.2504 | 822.547 | 104.7936 | 20 | 956.9293 | 377.4149 | 377.4149 | 725.6407 | 104.7936 | 20 | 713.2504 | 822.547 | 104.7936 | 20 | 956.9293 | 377.4149 | 377.4149 | 725.6407 | 104.7936 | 20 | 713.2504 | 822.547 | 104.7936 | 20 | 956.9293
x | 90.1-19 b - DCV |  | DCV modeled in more spaces, climates; exceptions removed; manual calc pasted here |  |  | Count of zones where DCV is newly required | 365 | 0 | 3 | 0 | 0 | 15 | 0 | 1095 | 0 | 15 | 1095 | 0 | 3 | 0 | 0 | 15 | 0 | 1095 | 0 | 15 | 1095 | 0 | 3 | 0 | 0 | 15 | 0 | 1095 | 0 | 15 | 1095 | 0 | 3 | 0 | 0 | 15 | 0 | 1095 | 0 | 15 | 1095 | 0 | 3 | 0 | 0 | 15 | 0 | 1095 | 0 | 15 | 1095 |  | 1095 | 1095 | 1095 | 1095 | 1095
x | 90.1-19 ci - lowers economizer threshold | DX_Economizer | 2.75 to 5.5 tons is the new range; only the last 4 CZs qualify in that range |  |  | PSZ-AC:4 OA Rate [cfm] | US_RS_PSZ-AC:4 OA Rate [cfm] | [10 empty] | 0 | 377.4149 | 0 | 0 | 15 | 0 | 1696.8161 | 134.8431 | 15 | 1910.0681 | 0 | 377.4149 | 0 | 0 | 15 | 0 | 1696.8161 | 134.8431 | 15 | 1910.0681 | 0 | 377.4149 | 0 | 0 | 15 | 0 | 1696.8161 | 134.8431 | 15 | 1910.0681 | 0 | 377.4149 | 0 | 0 | 15 | 0 | 1696.8161 | 134.8431 | 15 | 1910.0681 |  | 0 | 1696.8161 | 1696.8161 | 1696.8161 | 1696.8161
x | 90.1-19 bx furnace efficiency |  | Cost estimate based on federal rulemaking and heating capacity of units. Use the target capacity as it's not about load change but % eff improvement |  |  | Furnace heating capacity [kBtuh] | US_RS_PSZ-AC:2 Heating Capacity [kBtu/hr] | 664.1331 | 626.9925 | 0 | 0 | 15 | 0 | 83.5154 | 0 | 15 | 83.5154 | 727.1552 | 689.4494 | 0 | 0 | 15 | 0 | 91.8347 | 0 | 15 | 91.8347 | 714.9049 | 677.4665 | 0 | 0 | 15 | 0 | 90.2385 | 0 | 15 | 90.2385 | 788.7654 | 748.1381 | 0 | 0 | 15 | 0 | 99.652 | 0 | 15 | 99.652 | 801.0698 | 769.5641 | 0 | 0 | 15 | 0 | 102.5059 | 0 | 15 | 102.5059 |  | 83.5154 | 91.8347 | 90.2385 | 99.652 | 102.5059
No diff for 2010-13 so HIDE | 90.1-07cy | DX_Economizer | if any value other than "no" 1ookup cost based on supply air cfm |  |  | economizer parameter value is [No, differntial | economizer parameter value is [No, DifferentialEnthalpy]
Not in 2013 |  | DX_Economizer |  | PSZ-AC:1 | CAVDX | PSZ-AC:1 (economizer) | US_RS_PSZ-AC:1 (economizer) | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  | DX_Economizer |  |  |  | PSZ-AC:1 Supply Flow Rate [cfm] | US_RS_PSZ-AC:1 Supply Flow Rate [cfm] | 3284.264 | 3199.5088 | 4458.1268 | 165.1942 | 15 | 4972.9756 | 4348.4963 | 164.068 | 15 | 4854.1486 | 3157.1312 | 3051.1872 | 4293.681 | 163.5049 | 15 | 4794.7351 | 4156.6429 | 162.0973 | 15 | 4646.2014 | 3729.2288 | 3623.2848 | 5033.6868 | 171.1064 | 15 | 5596.8174 | 4896.6487 | 169.6987 | 15 | 5448.2836 | 3008.8096 | 2924.0544 | 4101.8277 | 161.5342 | 15 | 4586.7879 | 4042.3023 | 160.408 | 15 | 4520.7345 | 3199.5088 | 3072.376 | 4348.4963 | 164.068 | 15 | 4854.1486 | 4184.0506 | 162.3788 | 15 | 4675.9081
Not in 2013 |  | DX_Economizer |  | PSZ-AC:2 | CAVDX | PSZ-AC:2 (economizer) | US_RS_PSZ-AC:2 (economizer) | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  | DX_Economizer |  |  |  | PSZ-AC:2 Supply Flow Rate [cfm] | US_RS_PSZ-AC:2 Supply Flow Rate [cfm] | 14874.5376 | 13963.4192 | 18731.5739 | 214.5653 | 15 | 21257.182 | 17599.5512 | 214.5653 | 15 | 19982.0463 | 15065.2368 | 14111.7408 | 18980.0667 | 214.5653 | 15 | 21544.3534 | 17783.8339 | 214.5653 | 15 | 20189.6265 | 17120.5504 | 16061.1104 | 21897.8327 | 214.5653 | 15 | 25059.833 | 20393.8296 | 214.5653 | 15 | 23247.7301 | 15107.6144 | 14111.7408 | 19040.2268 | 214.5653 | 15 | 21616.8375 | 17783.8339 | 214.5653 | 15 | 20189.6265 | 14874.5376 | 13370.1328 | 18731.5739 | 214.5653 | 15 | 21257.182 | 16862.4201 | 214.5653 | 15 | 19151.7254
Not in 2013 |  | DX_Economizer |  | PSZ-AC:3 | CAVDX | PSZ-AC:3 (economizer) | US_RS_PSZ-AC:3 (economizer) | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  | DX_Economizer |  |  |  | PSZ-AC:3 Supply Flow Rate [cfm] | US_RS_PSZ-AC:3 Supply Flow Rate [cfm] | 2373.1456 | 2246.0128 | 3693.1661 | 153.0881 | 15 | 4131.1785 | 3612.5963 | 151.3989 | 15 | 4041.281 | 2309.5792 | 2182.4464 | 3652.8812 | 152.2435 | 15 | 4086.2298 | 3572.3113 | 150.5543 | 15 | 3996.3322 | 2690.9776 | 2542.656 | 3894.5909 | 157.3111 | 15 | 4355.9224 | 3800.5927 | 155.3404 | 15 | 4251.0419 | 2457.9008 | 2161.2576 | 3746.8794 | 154.2142 | 15 | 4191.1102 | 3558.883 | 150.2727 | 15 | 3981.3493 | 2457.9008 | 2118.88 | 3746.8794 | 154.2142 | 15 | 4191.1102 | 3532.0264 | 149.7097 | 15 | 3951.3834
Not in 2013 |  | DX_Economizer |  | PSZ-AC:4 | CAVDX | PSZ-AC:4 (economizer) | US_RS_PSZ-AC:4 (economizer) | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  | DX_Economizer |  |  |  | PSZ-AC:4 Supply Flow Rate [cfm] | US_RS_PSZ-AC:4 Supply Flow Rate [cfm] | 1928.1808 | 1779.8592 | 3394.7131 | 147.1758 | 15 | 3798.3715 | 3266.7247 | 145.2051 | 15 | 3655.9753 | 1843.4256 | 1695.104 | 3321.5769 | 146.0497 | 15 | 3717.0023 | 3193.5885 | 144.0789 | 15 | 3574.6061 | 2161.2576 | 1991.7472 | 3558.883 | 150.2727 | 15 | 3981.3493 | 3449.5652 | 148.0204 | 15 | 3859.3985 | 2012.936 | 1695.104 | 3464.8848 | 148.302 | 15 | 3876.4688 | 3193.5885 | 144.0789 | 15 | 3574.6061 | 1970.5584 | 1610.3488 | 3431.2812 | 147.7389 | 15 | 3839.0562 | 3120.4523 | 142.9528 | 15 | 3493.2368
No diff for 2010-13 so HIDE | 90.1-07aj | Motor_Efficiency | lookup cost based on the next motor size hp greater than 1.1 times the supply fan motor bhp
Not in 2013 |  | Motor_Efficiency |  | PSZ-AC:1 | CAVDX | PSZ-AC:1 Fan Power [hp] | US_RS_PSZ-AC:1 Fan Power [hp] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
Not in 2013 |  | Motor_Efficiency |  | PSZ-AC:2 | CAVDX | PSZ-AC:2 Fan Power [hp] | US_RS_PSZ-AC:2 Fan Power [hp] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
Not in 2013 |  | Motor_Efficiency |  | PSZ-AC:3 | CAVDX | PSZ-AC:3 Fan Power [hp] | US_RS_PSZ-AC:3 Fan Power [hp] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
Not in 2013 |  | Motor_Efficiency |  | PSZ-AC:4 | CAVDX | PSZ-AC:4 Fan Power [hp] | US_RS_PSZ-AC:4 Fan Power [hp] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
Not in 2013 |  | Motor_Efficiency |  | Unit Heater | Unit Heater | FRONT_ENTRY UNIT HEATERFAN Fan Power [bhp] | US_RS_FRONT_ENTRY UNIT HEATERFAN Fan Power [bhp] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| No differences seen in ERV Requirements for national; AC-2 set up above | [8 empty] | 338535.3781 |  |  | 427931.9544 | 332203.5098 |  |  | 420053.0243 |  |  | 335875.0677 |  |  | 424640.6814 | 331290.4259 |  |  | 418749.924 |  |  | 351249.032 |  |  | 443116.9324 | 345788.6988 |  |  | 436151.6249 |  |  | 336688.4194 |  |  | 425621.9821 | 329740.7596 |  |  | 416878.8865 |  |  | 334857.3566 |  |  | 423406.5048 | 324452.9707 |  |  | 410446.0688

## HVAC Primary School Proto
90.1 Cost Effectiveness - Cost Estimate - HVAC - Primary School | [7 empty] | Primary School
[6 empty] | $W |  |  |  | $AP | $AQ | $AR | $BA | $BK | $BL | $BM | $BW |  |  | $AP | $AQ | $AR | $BA | $BK | $BL | $BM | $BW |  |  | $AP | $AQ | $AR | $BA | $BK | $BL | $BM | $BW |  |  | $AP | $AQ | $AR | $BA | $BK | $BL | $BM | $BW |  |  | $AP | $AQ | $AR | $BA | $BK | $BL | $BM | $BW
|  |  | YES |  |  |  |  | 3 | 4 | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | 5 | 6 | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | 7 | 8 | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | 9 | 10 | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | 11 | 12 | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE
[7 empty] | City-year parameter column |  |  | I | I | I | I | J | J | J | J |  |  | S | S | S | S | T | T | T | T |  |  | AC | AC | AC | AC | AD | AD | AD | AD |  |  | AM | AM | AM | AM | AN | AN | AN | AN |  |  | AW | AW | AW | AW | AX | AX | AX | AX
[7 empty] | Parameter range lookup extension |  |  | _2007Par | _2007Par | _2007Par | _2007Par | _2010Par | _2010Par | _2010Par | _2010Par |  |  | _2007Par | _2007Par | _2007Par | _2007Par | _2010Par | _2010Par | _2010Par | _2010Par |  |  | _2007Par | _2007Par | _2007Par | _2007Par | _2010Par | _2010Par | _2010Par | _2010Par |  |  | _2007Par | _2007Par | _2007Par | _2007Par | _2010Par | _2010Par | _2010Par | _2010Par |  |  | _2007Par | _2007Par | _2007Par | _2007Par | _2010Par | _2010Par | _2010Par | _2010Par
[7 empty] | Cost range lookup extension |  |  | _2007Costs | _2007Costs | _2007Costs | _2007Costs | _2010Costs | _2010Costs | _2010Costs | _2010Costs |  |  | _2007Costs | _2007Costs | _2007Costs | _2007Costs | _2010Costs | _2010Costs | _2010Costs | _2010Costs |  |  | _2007Costs | _2007Costs | _2007Costs | _2007Costs | _2010Costs | _2010Costs | _2010Costs | _2010Costs |  |  | _2007Costs | _2007Costs | _2007Costs | _2007Costs | _2010Costs | _2010Costs | _2010Costs | _2010Costs |  |  | _2007Costs | _2007Costs | _2007Costs | _2007Costs | _2010Costs | _2010Costs | _2010Costs | _2010Costs
[7 empty] | Cost range column index values |  |  | 9 | 10 | 11 | 20 | 10 | 11 | 12 | 22 |  |  | 9 | 10 | 11 | 20 | 10 | 11 | 12 | 22 |  |  | 9 | 10 | 11 | 20 | 10 | 11 | 12 | 22 |  |  | 9 | 10 | 11 | 20 | 10 | 11 | 12 | 22 |  |  | 9 | 10 | 11 | 20 | 10 | 11 | 12 | 22
[8 empty] | Climate Zone 1 | 2A | Base Code | 2019 |  |  | Target Code | 2022 |  |  | Climate Zone 2 | 3A | Base Code | 2019 |  |  | Target Code | 2022 |  |  | Climate Zone 3 | 3B | Base Code | 2019 |  |  | Target Code | 2022 |  |  | Climate Zone 4 | 4A | Base Code | 2019 |  |  | Target Code | 2022 |  |  | Climate Zone 5 | 5A | Base Code | 2019 |  |  | Target Code | 2022 |  |  | Using Col C keyword | First cost difference |  | 2019 | vs | 2022
Costs row marked x, other rows not marked | [7 empty] | Base | Target | [8 empty] | Base | Target | [8 empty] | Base | Target | [8 empty] | Base | Target | [8 empty] | Base | Target | [8 empty] | Find | Total new construction (added cost)
| Addendum or general | Key Word | Description | Model | Type | Parameter | Lookup Value in HVAC Data, Current_HVAC_Data | Prototype | Prototype | Total New | Maintenance | Replacement Life | Total | Total New | Maintenance | Replacement Life | Total | Prototype | Prototype | Total New | Maintenance | Replacement Life | Total | Total New | Maintenance | Replacement Life | Total | Prototype | Prototype | Total New | Maintenance | Replacement Life | Total | Total New | Maintenance | Replacement Life | Total | Prototype | Prototype | Total New | Maintenance | Replacement Life | Total | Total New | Maintenance | Replacement Life | Total | Prototype | Prototype | Total New | Maintenance | Replacement Life | Total | Total New | Maintenance | Replacement Life | Total | Row in | 2A | 3A | 3B | 4A | 5A
| load change |  |  | Object |  |  |  | Data | Data | Construction |  |  | Replacement Cost | Construction |  |  | Replacement Cost | Data | Data | Construction |  |  | Replacement Cost | Construction |  |  | Replacement Cost | Data | Data | Construction |  |  | Replacement Cost | Construction |  |  | Replacement Cost | Data | Data | Construction |  |  | Replacement Cost | Construction |  |  | Replacement Cost | Data | Data | Construction |  |  | Replacement Cost | Construction |  |  | Replacement Cost | Costs_Comp
| HVAC System - General Load Change |  | Lookup based on cooling tons
x |  | VAV_DX |  | VAV_POD_1 | VAVDX | VAV_POD_1 Cooling Capacity [ton] | US_PS_VAV_POD_1 Cooling Capacity [ton] | 36.0114 | 35.7792 | 67962.3914 | 0 | 15 | 83106.6814 | 67540.9202 | 0 | 15 | 82590.939 | 36.1392 | 35.8981 | 68194.2408 | 0 | 15 | 83390.389 | 67756.791 | 0 | 15 | 82855.094 | 39.7677 | 39.5895 | 74780.2964 | 0 | 15 | 91449.5587 | 74456.8798 | 0 | 15 | 91053.8029 | 36.5221 | 35.2485 | 68889.2575 | 0 | 15 | 84240.8612 | 66577.6739 | 0 | 15 | 81412.2418 | 37.1085 | 35.8919 | 69953.6757 | 0 | 15 | 85543.3596 | 67745.4316 | 0 | 15 | 82841.1938 |  | -421.4712 | -437.4498 | -323.4166 | -2311.5837 | -2208.2441
x |  | VAV_DX |  | VAV_POD_2 | VAVDX | VAV_POD_2 Cooling Capacity [ton] | US_PS_VAV_POD_2 Cooling Capacity [ton] | 35.7567 | 35.5264 | 67500.0241 | 0 | 15 | 82540.8956 | 67082.0469 | 0 | 15 | 82029.4288 | 35.8205 | 35.5815 | 67615.7862 | 0 | 15 | 82682.5505 | 67182.0575 | 0 | 15 | 82151.8089 | 39.5021 | 39.3251 | 74298.1468 | 0 | 15 | 90859.5659 | 73976.9288 | 0 | 15 | 90466.5005 | 36.0875 | 34.8309 | 68100.4957 | 0 | 15 | 83275.6757 | 65819.5893 | 0 | 15 | 80484.5951 | 36.6966 | 35.4943 | 69205.9854 | 0 | 15 | 84628.4322 | 67023.7529 | 0 | 15 | 81958.0961 |  | -417.9772 | -433.7287 | -321.218 | -2280.9064 | -2182.2325
x |  | VAV_DX |  | VAV_POD_3 | VAVDX | VAV_POD_3 Cooling Capacity [ton] | US_PS_VAV_POD_3 Cooling Capacity [ton] | 31.857 | 31.6546 | 60421.8942 | 0 | 15 | 73879.5886 | 60054.4694 | 0 | 15 | 73429.9813 | 31.9029 | 31.6928 | 60505.1367 | 0 | 15 | 73981.45 | 60123.777 | 0 | 15 | 73514.791 | 34.859 | 34.7043 | 65870.6577 | 0 | 15 | 80547.0862 | 65589.8352 | 0 | 15 | 80203.4516 | 32.3938 | 31.2386 | 61396.0923 | 0 | 15 | 75071.6871 | 59299.4918 | 0 | 15 | 72506.1365 | 32.9832 | 31.8743 | 62466.0328 | 0 | 15 | 76380.943 | 60453.3147 | 0 | 15 | 73918.0369 |  | -367.4248 | -381.3596 | -280.8225 | -2096.6005 | -2012.7181
x |  | VAV_DX |  | VAV_OTHER | VAVDX | VAV_OTHER Cooling Capacity [ton] | US_PS_VAV_OTHER Cooling Capacity [ton] | 37.6916 | 37.6653 | 71011.9884 | 0 | 15 | 86838.3869 | 70964.2539 | 0 | 15 | 86779.9756 | 37.2384 | 37.2189 | 70189.3753 | 0 | 15 | 85831.7785 | 70153.9809 | 0 | 15 | 85788.4674 | 34.3939 | 34.3748 | 65026.5437 | 0 | 15 | 79514.1678 | 64991.7377 | 0 | 15 | 79471.5766 | 36.8219 | 35.9801 | 69433.448 | 0 | 15 | 84906.7717 | 67905.4858 | 0 | 15 | 83037.0476 | 34.8169 | 34.0344 | 65794.3105 | 0 | 15 | 80453.6622 | 64373.9043 | 0 | 15 | 78715.5514 |  | -47.7345 | -35.3944 | -34.8061 | -1527.9622 | -1420.4061
x |  | CAV_DX | lookup based on cooling tons | PSZ-AC_1:6 | CAVDX | PSZ-AC_1:6 Cooling Capacity [ton] | US_PS_PSZ-AC_1:6 Cooling Capacity [ton] | 9.1929 | 9.2251 | 13128.6532 | 0 | 15 | 17416.5986 | 13156.9136 | 0 | 15 | 17454.1195 | 9.2129 | 9.2355 | 13146.1452 | 0 | 15 | 17439.8225 | 13166.0166 | 0 | 15 | 17466.2055 | 9.2506 | 9.2756 | 13179.2941 | 0 | 15 | 17483.8339 | 13201.1953 | 0 | 15 | 17512.9119 | 8.9017 | 8.8402 | 12872.9221 | 0 | 15 | 17077.0671 | 12818.9332 | 0 | 15 | 17005.3866 | 8.5616 | 8.5016 | 12574.2675 | 0 | 15 | 16680.5466 | 12521.6118 | 0 | 15 | 16610.6361 |  | 28.2603 | 19.8714 | 21.9012 | -53.989 | -52.6557
x |  | CAV_DX |  | PSZ-AC_2:5 | CAVDX | PSZ-AC_2:5 Cooling Capacity [ton] | US_PS_PSZ-AC_2:5 Cooling Capacity [ton] | 9.5784 | 9.4416 | 13467.123 | 0 | 15 | 17865.9813 | 13346.9985 | 0 | 15 | 17706.4933 | 9.7576 | 9.6157 | 13624.436 | 0 | 15 | 18074.8441 | 13499.8499 | 0 | 15 | 17909.4325 | 9.972 | 9.8617 | 13812.6784 | 0 | 15 | 18324.7715 | 13715.8707 | 0 | 15 | 18196.241 | 9.9045 | 9.5347 | 13753.4238 | 0 | 15 | 18246.0999 | 13428.7285 | 0 | 15 | 17815.0053 | 9.7754 | 9.5076 | 13640.0929 | 0 | 15 | 18095.6316 | 13404.8998 | 0 | 15 | 17783.3682 |  | -120.1245 | -124.5861 | -96.8076 | -324.6954 | -235.1931
x |  | CAV_DX |  | PSZ-AC_2:7 | CAVDX | PSZ-AC_2:7 Cooling Capacity [ton] | US_PS_PSZ-AC_2:7 Cooling Capacity [ton] | 15.6326 | 15.5445 | 18483.0105 | 0 | 15 | 24145.2872 | 18399.8622 | 0 | 15 | 24045.0482 | 16.0142 | 15.9228 | 18843.1034 | 0 | 15 | 24579.3953 | 18756.8823 | 0 | 15 | 24475.4518 | 18.1683 | 18.0664 | 20731.1255 | 0 | 15 | 26874.811 | 20657.1137 | 0 | 15 | 26782.6422 | 15.6959 | 15.3996 | 18542.6847 | 0 | 15 | 24217.2271 | 18263.0645 | 0 | 15 | 23880.1325 | 15.868 | 15.5919 | 18705.1464 | 0 | 15 | 24413.0819 | 18444.5293 | 0 | 15 | 24098.8963 |  | -83.1483 | -86.2211 | -74.0118 | -279.6202 | -260.6171
x |  | Air Distribution | curve fit from Solarc cost calculations |  |  | sum of PSZ-AC:1 Supply Flow Rate [cfm] to PSZ-AC:4 Supply Flow Rate [cfm] (not the sum of the cooling capacity) |  | 52717.7345 | 52463.4689 | 809793.4969 | 0 | 30 | 1430281.2698 | 807765.9839 | 0 | 30 | 1317709.8323 | 53162.6993 | 52887.2449 | 813341.6446 | 0 | 30 | 1326734.32 | 811145.1722 | 0 | 30 | 1323179.2188 | 61574.6529 | 61256.8209 | 880418.5327 | 0 | 30 | 1435301.6424 | 877884.1414 | 0 | 30 | 1431199.6026 | 53480.5313 | 51785.4273 | 815876.0358 | 0 | 30 | 1330836.3599 | 802359.2826 | 0 | 30 | 1308958.8138 | 54391.6497 | 52738.9233 | 823141.2907 | 0 | 30 | 1342595.5409 | 809962.4563 | 0 | 30 | 1321264.9335 |  | -2027.513 | -2196.4724 | -2534.3912 | -13516.7533 | -13178.8344
|  | VAV_DX | Curve Fits | VAV_POD_1 | VAVDX | VAV_POD_1 Supply Flow Rate [cfm] | US_PS_VAV_POD_1 Supply Flow Rate [cfm] | 10806.288 | 10742.7216 | [8 empty] | 10848.6656 | 10763.9104 | [8 empty] | 12649.7136 | 12564.9584 | [8 empty] | 10954.6096 | 10573.2112 | [8 empty] | 11145.3088 | 10763.9104
| Material | VAV_DX | Material | VAV_POD_2 | VAVDX | VAV_POD_2 Supply Flow Rate [cfm] | US_PS_VAV_POD_2 Supply Flow Rate [cfm] | 10721.5328 | 10657.9664 | [8 empty] | 10742.7216 | 10679.1552 | [8 empty] | 12522.5808 | 12437.8256 | [8 empty] | 10827.4768 | 10446.0784 | [8 empty] | 11018.176 | 10657.9664
| y = 0.7194x + 28317 | VAV_DX | y = 0.7194x + 28317 | VAV_POD_3 | VAVDX | VAV_POD_3 Supply Flow Rate [cfm] | US_PS_VAV_POD_3 Supply Flow Rate [cfm] | 9556.1488 | 9492.5824 | [8 empty] | 9577.3376 | 9513.7712 | [8 empty] | 11145.3088 | 11081.7424 | [8 empty] | 9725.6592 | 9365.4496 | [8 empty] | 9895.1696 | 9556.1488
| R² = 0.8831 | VAV_DX | R² = 0.8831 | VAV_OTHER | VAVDX | VAV_OTHER Supply Flow Rate [cfm] | US_PS_VAV_OTHER Supply Flow Rate [cfm] | 11314.8192 | 11293.6304 | [8 empty] | 11420.7632 | 11420.7632 | [8 empty] | 13306.5664 | 13285.3776 | [8 empty] | 11526.7072 | 11166.4976 | [8 empty] | 11717.4064 | 11378.3856
| Labor | CAV_DX | Labor | PSZ-AC_1:6 | CAVDX | PSZ-AC_1:6 Supply Flow Rate [cfm] | US_PS_PSZ-AC_1:6 Supply Flow Rate [cfm] | 2754.544 | 2775.7328 | [8 empty] | 2839.2992 | 2839.2992 | [8 empty] | 3178.32 | 3178.32 | [8 empty] | 2775.7328 | 2754.544 | [8 empty] | 2839.2992 | 2796.9216
| y = 2.3902x + 122683 | CAV_DX | y = 2.3902x + 122683 | PSZ-AC_2:5 | CAVDX | PSZ-AC_2:5 Supply Flow Rate [cfm] | US_PS_PSZ-AC_2:5 Supply Flow Rate [cfm] | 2881.6768 | 2839.2992 | [8 empty] | 2924.0544 | 2881.6768 | [8 empty] | 3326.6416 | 3284.264 | [8 empty] | 2966.432 | 2860.488 | [8 empty] | 3008.8096 | 2902.8656
| R² = 0.9806 | CAV_DX | R² = 0.9806 | PSZ-AC_2:7 | CAVDX | PSZ-AC_2:7 Supply Flow Rate [cfm] | US_PS_PSZ-AC_2:7 Supply Flow Rate [cfm] | 4682.7248 | 4661.536 | [8 empty] | 4809.8576 | 4788.6688 | [8 empty] | 5445.5216 | 5424.3328 | [8 empty] | 4703.9136 | 4619.1584 | [8 empty] | 4767.48 | 4682.7248
| 90.1-2016ap SAT reset only 0A, 1A, 3A MZ systems only <3000 cfm design OA is exempt | Material cost = 4E-07x2 + 0.0307x + 1618 Labor hours = 0.0054x + 3.6055 | lookup cost based on supply airflow, cfm new for 2019, thus base code = 0 costs
|  | SAT_reset_16ap |  | VAV_POD_1 | VAVDX | VAV_POD_1 Supply Flow Rate [cfm] | US_PS_VAV_POD_1 Supply Flow Rate [cfm] | 10806.288 | 10742.7216 | 0 | 0 |  | 0 | 0 | 0 | 20 | 0 | 10848.6656 | 10763.9104 | 0 | 0 |  | 0 | 4766.0362 | 0 | 20 | 5349.4305 | 12649.7136 | 12564.9584 | 0 | 0 |  | 0 | 0 | 0 | 20 | 0 | 10954.6096 | 10573.2112 | 0 | 0 |  | 0 | 0 | 0 | 20 | 0 | 11145.3088 | 10763.9104 | 0 | 0 |  | 0 | 0 | 0 | 20 | 0
|  | SAT_reset_16ap |  | VAV_POD_2 | VAVDX | VAV_POD_2 Supply Flow Rate [cfm] | US_PS_VAV_POD_2 Supply Flow Rate [cfm] | 10721.5328 | 10657.9664 | 0 | 0 |  | 0 | 0 | 0 | 20 | 0 | 10742.7216 | 10679.1552 | 0 | 0 |  | 0 | 4757.1457 | 0 | 20 | 5338.8592 | 12522.5808 | 12437.8256 | 0 | 0 |  | 0 | 0 | 0 | 20 | 0 | 10827.4768 | 10446.0784 | 0 | 0 |  | 0 | 0 | 0 | 20 | 0 | 11018.176 | 10657.9664 | 0 | 0 |  | 0 | 0 | 0 | 20 | 0
|  | SAT_reset_16ap |  | VAV_POD_3 | VAVDX | VAV_POD_3 Supply Flow Rate [cfm] | US_PS_VAV_POD_3 Supply Flow Rate [cfm] | 9556.1488 | 9492.5824 | 0 | 0 |  | 0 | 0 | 0 | 20 | 0 | 9577.3376 | 9513.7712 | 0 | 0 |  | 0 | 4636.2458 | 0 | 20 | 5194.9826 | 11145.3088 | 11081.7424 | 0 | 0 |  | 0 | 0 | 0 | 20 | 0 | 9725.6592 | 9365.4496 | 0 | 0 |  | 0 | 0 | 0 | 20 | 0 | 9895.1696 | 9556.1488 | 0 | 0 |  | 0 | 0 | 0 | 20 | 0
|  | SAT_reset_16ap |  | VAV_OTHER | VAVDX | VAV_OTHER Supply Flow Rate [cfm] | US_PS_VAV_OTHER Supply Flow Rate [cfm] | 11314.8192 | 11293.6304 | 0 | 0 |  | 0 | 0 | 0 | 20 | 0 | 11420.7632 | 11420.7632 | 0 | 0 |  | 0 | 4835.3873 | 0 | 20 | 5431.8529 | 13306.5664 | 13285.3776 | 0 | 0 |  | 0 | 0 | 0 | 20 | 0 | 11526.7072 | 11166.4976 | 0 | 0 |  | 0 | 0 | 0 | 20 | 0 | 11717.4064 | 11378.3856 | 0 | 0 |  | 0 | 0 | 0 | 20 | 0
0 | 90.1-10au | VAV_AHU | If PH coil = NO, then increase | VAV_POD_1 | VAVDX | VAV_POD_1 Preheat Coil | US_PS_VAV_POD_1 Preheat Coil | N/A | REF!! | 0 | 0 | 15 | 0 | 0 | 0 | 15 | 0 | N/A | REF!! | 0 | 0 | 15 | 0 | 0 | 0 | 15 | 0 | N/A | REF!! | 0 | 0 | 15 | 0 | 0 | 0 | 15 | 0 | N/A | REF!! | 0 | 0 | 15 | 0 | 0 | 0 | 15 | 0 | N/A | REF!! | 0 | 0 | 15 | 0 | 0 | 0 | 15 | 0
0 |  | VAV_AHU | duct cost by | VAV_POD_2 | VAVDX | VAV_POD_2 Preheat Coil | US_PS_VAV_POD_2 Preheat Coil | N/A | REF!! | 0 | 0 | 15 | 0 | 0 | 0 | 15 | 0 | N/A | YES | 0 | 0 | 15 | 0 | 0 | 0 | 15 | 0 | N/A | YES | 0 | 0 | 15 | 0 | 0 | 0 | 15 | 0 | N/A | YES | 0 | 0 | 15 | 0 | 0 | 0 | 15 | 0 | N/A | YES | 0 | 0 | 15 | 0 | 0 | 0 | 15 | 0
0 |  | VAV_AHU | 0.0275 | VAV_POD_3 | VAVDX | VAV_POD_3 Preheat Coil | US_PS_VAV_POD_3 Preheat Coil | N/A | REF!! | 0 | 0 | 15 | 0 | 0 | 0 | 15 | 0 | N/A | REF!! | 0 | 0 | 15 | 0 | 0 | 0 | 15 | 0 | N/A | REF!! | 0 | 0 | 15 | 0 | 0 | 0 | 15 | 0 | N/A | REF!! | 0 | 0 | 15 | 0 | 0 | 0 | 15 | 0 | N/A | REF!! | 0 | 0 | 15 | 0 | 0 | 0 | 15 | 0
0 |  | VAV_AHU |  | VAV_OTHER | VAVDX | VAV_OTHER Preheat Coil | US_PS_VAV_OTHER Preheat Coil | N/A | REF!! | 0 | 0 | 15 | 0 | 0 | 0 | 15 | 0 | N/A | REF!! | 0 | 0 | 15 | 0 | 0 | 0 | 15 | 0 | N/A | REF!! | 0 | 0 | 15 | 0 | 0 | 0 | 15 | 0 | N/A | REF!! | 0 | 0 | 15 | 0 | 0 | 0 | 15 | 0 | N/A | REF!! | 0 | 0 | 15 | 0 | 0 | 0 | 15 | 0
0 |  | CAV_DX |  | PSZ-AC_1:6 | CAVDX | PSZ-AC_1:6 Preheat Coil | US_PS_PSZ-AC_1:6 Preheat Coil | N/A | REF!! | 0 | 0 | 15 | 0 | 0 | 0 | 15 | 0 | N/A | REF!! | 0 | 0 | 15 | 0 | 0 | 0 | 15 | 0 | N/A | REF!! | 0 | 0 | 15 | 0 | 0 | 0 | 15 | 0 | N/A | REF!! | 0 | 0 | 15 | 0 | 0 | 0 | 15 | 0 | N/A | REF!! | 0 | 0 | 15 | 0 | 0 | 0 | 15 | 0
0 |  | CAV_DX |  | PSZ-AC_2:5 | CAVDX | PSZ-AC_2:5 Preheat Coil | US_PS_PSZ-AC_2:5 Preheat Coil | N/A | REF!! | 0 | 0 | 15 | 0 | 0 | 0 | 15 | 0 | N/A | REF!! | 0 | 0 | 15 | 0 | 0 | 0 | 15 | 0 | N/A | REF!! | 0 | 0 | 15 | 0 | 0 | 0 | 15 | 0 | N/A | REF!! | 0 | 0 | 15 | 0 | 0 | 0 | 15 | 0 | N/A | REF!! | 0 | 0 | 15 | 0 | 0 | 0 | 15 | 0
0 |  | CAV_DX |  | PSZ-AC_2:7 | CAVDX | PSZ-AC_2:7 Preheat Coil | US_PS_PSZ-AC_2:7 Preheat Coil | N/A | REF!! | 0 | 0 | 15 | 0 | 0 | 0 | 15 | 0 | N/A | REF!! | 0 | 0 | 15 | 0 | 0 | 0 | 15 | 0 | N/A | REF!! | 0 | 0 | 15 | 0 | 0 | 0 | 15 | 0 | N/A | REF!! | 0 | 0 | 15 | 0 | 0 | 0 | 15 | 0 | N/A | REF!! | 0 | 0 | 15 | 0 | 0 | 0 | 15 | 0
| 90.1-10aq for DX single zone |  |  |  |  | Cost for 2 stage fan and added cooling stage applies if single zone DX system Cooling Capacity [ton] above 5.4167 tons, prototype value shown as "yes" if so, or "no" if not. | If applicable, add the fan and staging cost together for the target code; For units greater than 110 MBH (9.167 tons) include fan control only in the base case.
0 |  |  | Capacity check & Select | PSZ-AC_1:6 | CAVDX |  |  | Yes | Yes | 398.5752 | 0 | 15 | 438.4328 | 1039.3212 | 0 | 15 | 1143.2534 | Yes | Yes | 398.7684 | 0 | 15 | 351.056 | 1040.2167 | 0 | 15 | 1144.2384 | Yes | Yes | 399.1344 | 0 | 15 | 439.0478 | 1043.6772 | 0 | 15 | 1148.0449 | No | Yes | 0 | 0 | 0 | 0 | 1006.0744 | 0 | 15 | 1106.6818 | No | Yes | 0 | 0 | 0 | 0 | 976.8271 | 0 | 15 | 1074.5098
| Upgrade to 2-speed fan |  | curve fit from AHRI cost survey | PSZ-AC_1:6 | CAVDX | PSZ-AC_1:6 Cooling Capacity [ton] | US_PS_PSZ-AC_1:6 Cooling Capacity [ton] | 9.1929 | 9.2251 | 398.5752 | 0 | 15 | 438.4328 | 398.8873 | 0 | 15 | 438.776 | 9.2129 | 9.2355 | 398.7684 | 0 | 15 | 351.056 | 398.9878 | 0 | 15 | 438.8866 | 9.2506 | 9.2756 | 399.1344 | 0 | 15 | 439.0478 | 399.3762 | 0 | 15 | 439.3139 | 8.9017 | 8.8402 | 395.7515 | 0 | 15 | 435.3267 | 395.1554 | 0 | 15 | 434.6709 | 8.5616 | 8.5016 | 392.4538 | 0 | 15 | 431.6992 | 391.8724 | 0 | 15 | 431.0596
| Add one stage of cooling |  | curve fit from AHRI cost survey | PSZ-AC_1:6 | CAVDX | PSZ-AC_1:6 Cooling Capacity [ton] | US_PS_PSZ-AC_1:6 Cooling Capacity [ton] | 9.1929 | 9.2251 | 637.966 | 0 | 15 | 701.7627 | 640.4339 | 0 | 15 | 704.4773 | 9.2129 | 9.2355 | 639.4936 | 0 | 15 | 703.4429 | 641.2289 | 0 | 15 | 705.3518 | 9.2506 | 9.2756 | 642.3884 | 0 | 15 | 706.6272 | 644.301 | 0 | 15 | 708.7311 | 8.9017 | 8.8402 | 615.6337 | 0 | 15 | 677.1971 | 610.919 | 0 | 15 | 672.0109 | 8.5616 | 8.5016 | 589.553 | 0 | 15 | 648.5083 | 584.9547 | 0 | 15 | 643.4502
0 |  |  | Capacity check & Select | PSZ-AC_2:5 | CAVDX |  |  | Yes | Yes | 402.3126 | 0 | 15 | 442.5438 | 1058.0197 | 0 | 15 | 1163.8217 | Yes | Yes | 404.0496 | 0 | 15 | 351.056 | 1073.0556 | 0 | 15 | 1180.3612 | Yes | Yes | 406.1281 | 0 | 15 | 446.7409 | 1094.3054 | 0 | 15 | 1203.7359 | Yes | Yes | 405.4738 | 0 | 15 | 446.0212 | 1066.0594 | 0 | 15 | 1172.6654 | Yes | Yes | 404.2225 | 0 | 15 | 444.6447 | 1063.7154 | 0 | 15 | 1170.087
| Upgrade to 2-speed fan |  | curve fit from AHRI cost survey | PSZ-AC_2:5 | CAVDX | PSZ-AC_2:5 Cooling Capacity [ton] | US_PS_PSZ-AC_2:5 Cooling Capacity [ton] | 9.5784 | 9.4416 | 402.3126 | 0 | 15 | 442.5438 | 400.9862 | 0 | 15 | 441.0848 | 9.7576 | 9.6157 | 404.0496 | 0 | 15 | 351.056 | 402.6739 | 0 | 15 | 442.9413 | 9.972 | 9.8617 | 406.1281 | 0 | 15 | 446.7409 | 405.0592 | 0 | 15 | 445.5651 | 9.9045 | 9.5347 | 405.4738 | 0 | 15 | 446.0212 | 401.8886 | 0 | 15 | 442.0775 | 9.7754 | 9.5076 | 404.2225 | 0 | 15 | 444.6447 | 401.6255 | 0 | 15 | 441.7881
| Add one stage of cooling |  | curve fit from AHRI cost survey | PSZ-AC_2:5 | CAVDX | PSZ-AC_2:5 Cooling Capacity [ton] | US_PS_PSZ-AC_2:5 Cooling Capacity [ton] | 9.5784 | 9.4416 | 667.5237 | 0 | 15 | 734.2761 | 657.0336 | 0 | 15 | 722.7369 | 9.7576 | 9.6157 | 681.2615 | 0 | 15 | 749.3876 | 670.3817 | 0 | 15 | 737.4199 | 9.972 | 9.8617 | 697.7002 | 0 | 15 | 767.4702 | 689.2462 | 0 | 15 | 758.1708 | 9.9045 | 9.5347 | 692.5256 | 0 | 15 | 761.7782 | 664.1708 | 0 | 15 | 730.5879 | 9.7754 | 9.5076 | 682.6287 | 0 | 15 | 750.8916 | 662.0899 | 0 | 15 | 728.2989
0 |  |  | Capacity check & Select | PSZ-AC_2:7 | CAVDX |  |  | Yes | Yes | 461.0104 | 0 | 15 | 507.1114 | 1585.1536 | 0 | 15 | 1743.6689 | Yes | Yes | 464.7094 | 0 | 15 | 351.056 | 1617.8267 | 0 | 15 | 1779.6094 | Yes | Yes | 485.5942 | 0 | 15 | 534.1536 | 1802.9791 | 0 | 15 | 1983.277 | Yes | Yes | 461.6234 | 0 | 15 | 507.7857 | 1572.6343 | 0 | 15 | 1729.8978 | Yes | Yes | 463.2923 | 0 | 15 | 509.6215 | 1589.2413 | 0 | 15 | 1748.1654
| Upgrade to 2-speed fan |  | curve fit from AHRI cost survey | PSZ-AC_2:7 | CAVDX | PSZ-AC_2:7 Cooling Capacity [ton] | US_PS_PSZ-AC_2:7 Cooling Capacity [ton] | 15.6326 | 15.5445 | 461.0104 | 0 | 15 | 507.1114 | 460.1562 | 0 | 15 | 506.1718 | 16.0142 | 15.9228 | 464.7094 | 0 | 15 | 351.056 | 463.8237 | 0 | 15 | 510.2061 | 18.1683 | 18.0664 | 485.5942 | 0 | 15 | 534.1536 | 484.6068 | 0 | 15 | 533.0675 | 15.6959 | 15.3996 | 461.6234 | 0 | 15 | 507.7857 | 458.7509 | 0 | 15 | 504.626 | 15.868 | 15.5919 | 463.2923 | 0 | 15 | 509.6215 | 460.6151 | 0 | 15 | 506.6766
| Add one stage of cooling |  | curve fit from AHRI cost survey | PSZ-AC_2:7 | CAVDX | PSZ-AC_2:7 Cooling Capacity [ton] | US_PS_PSZ-AC_2:7 Cooling Capacity [ton] | 15.6326 | 15.5445 | 1131.7526 | 0 | 15 | 1244.9279 | 1124.9973 | 0 | 15 | 1237.4971 | 16.0142 | 15.9228 | 1161.0079 | 0 | 15 | 1277.1087 | 1154.003 | 0 | 15 | 1269.4033 | 18.1683 | 18.0664 | 1326.1808 | 0 | 15 | 1458.7989 | 1318.3722 | 0 | 15 | 1450.2095 | 15.6959 | 15.3996 | 1136.6008 | 0 | 15 | 1250.2608 | 1113.8834 | 0 | 15 | 1225.2717 | 15.868 | 15.5919 | 1149.7998 | 0 | 15 | 1264.7797 | 1128.6263 | 0 | 15 | 1241.4889
| 90.1-10aq for multiple zone with variable airflow |  |  |  |  | Cost for added cooling stage applies if DX system with varied airflow and Cooling Capacity [ton] above 5.4167 tons, prototype value shown as "yes" if so, or "no" if not. | If applicable, add staging cost for the target code; Note - these units require variable speed fans and the difference based on fan motor HP is covered in the next item.
0 |  |  | Capacity check | VAV_POD_1 | VAVDX |  |  | NA | Yes | 0 | 0 | 0 | 0 | 2676.5626 | 0 | 0 | 2944.2189 | NA | Yes | 0 | 0 | 0 | 0 | 2685.6822 | 0 | 0 | 2954.2504 | NA | Yes | 0 | 0 | 0 | 0 | 2968.732 | 0 | 0 | 3265.6052 | NA | Yes | 0 | 0 | 0 | 0 | 2635.8696 | 0 | 0 | 2899.4566 | NA | Yes | 0 | 0 | 0 | 0 | 2685.2023 | 0 | 0 | 2953.7225
| Add one stage of cooling |  | curve fit from AHRI cost survey | VAV_POD_1 | VAVDX | VAV_POD_1 Cooling Capacity [ton] | US_PS_VAV_POD_1 Cooling Capacity [ton] | 36.0114 | 35.7792 | 2694.3679 | 0 | 15 | 2963.8047 | 2676.5626 | 0 | 15 | 2944.2189 | 36.1392 | 35.8981 | 2704.1626 | 0 | 15 | 2974.5788 | 2685.6822 | 0 | 15 | 2954.2504 | 39.7677 | 39.5895 | 2982.395 | 0 | 15 | 3280.6345 | 2968.732 | 0 | 15 | 3265.6052 | 36.5221 | 35.2485 | 2733.524 | 0 | 15 | 3006.8764 | 2635.8696 | 0 | 15 | 2899.4566 | 37.1085 | 35.8919 | 2778.4911 | 0 | 15 | 3056.3402 | 2685.2023 | 0 | 15 | 2953.7225
0 |  |  | Capacity check | VAV_POD_2 | VAVDX |  |  | NA | Yes | 0 | 0 | 0 | 0 | 2657.1772 | 0 | 0 | 2922.8949 | NA | Yes | 0 | 0 | 0 | 0 | 2661.4022 | 0 | 0 | 2927.5424 | NA | Yes | 0 | 0 | 0 | 0 | 2948.4562 | 0 | 0 | 3243.3018 | NA | Yes | 0 | 0 | 0 | 0 | 2603.8438 | 0 | 0 | 2864.2282 | NA | Yes | 0 | 0 | 0 | 0 | 2654.7145 | 0 | 0 | 2920.186
| Add one stage of cooling |  | curve fit from AHRI cost survey | VAV_POD_2 | VAVDX | VAV_POD_2 Cooling Capacity [ton] | US_PS_VAV_POD_2 Cooling Capacity [ton] | 35.7567 | 35.5264 | 2674.8349 | 0 | 15 | 2942.3184 | 2657.1772 | 0 | 15 | 2922.8949 | 35.8205 | 35.5815 | 2679.7254 | 0 | 15 | 2947.6979 | 2661.4022 | 0 | 15 | 2927.5424 | 39.5021 | 39.3251 | 2962.0262 | 0 | 15 | 3258.2288 | 2948.4562 | 0 | 15 | 3243.3018 | 36.0875 | 34.8309 | 2700.2022 | 0 | 15 | 2970.2225 | 2603.8438 | 0 | 15 | 2864.2282 | 36.6966 | 35.4943 | 2746.9044 | 0 | 15 | 3021.5948 | 2654.7145 | 0 | 15 | 2920.186
0 |  |  | Capacity check | VAV_POD_3 | VAVDX |  |  | NA | Yes | 0 | 0 | 0 | 0 | 2360.2924 | 0 | 0 | 2596.3216 | NA | Yes | 0 | 0 | 0 | 0 | 2363.2203 | 0 | 0 | 2599.5424 | NA | Yes | 0 | 0 | 0 | 0 | 2594.1377 | 0 | 0 | 2853.5515 | NA | Yes | 0 | 0 | 0 | 0 | 2328.3979 | 0 | 0 | 2561.2376 | NA | Yes | 0 | 0 | 0 | 0 | 2377.1419 | 0 | 0 | 2614.8561
| Add one stage of cooling |  | curve fit from AHRI cost survey | VAV_POD_3 | VAVDX | VAV_POD_3 Cooling Capacity [ton] | US_PS_VAV_POD_3 Cooling Capacity [ton] | 31.857 | 31.6546 | 2375.8145 | 0 | 15 | 2613.396 | 2360.2924 | 0 | 15 | 2596.3216 | 31.9029 | 31.6928 | 2379.3311 | 0 | 15 | 2617.2643 | 2363.2203 | 0 | 15 | 2599.5424 | 34.859 | 34.7043 | 2606.0012 | 0 | 15 | 2866.6013 | 2594.1377 | 0 | 15 | 2853.5515 | 32.3938 | 31.2386 | 2416.9702 | 0 | 15 | 2658.6672 | 2328.3979 | 0 | 15 | 2561.2376 | 32.9832 | 31.8743 | 2462.1705 | 0 | 15 | 2708.3876 | 2377.1419 | 0 | 15 | 2614.8561
0 |  |  | Capacity check | VAV_OTHER | VAVDX |  |  | NA | Yes | 0 | 0 | 0 | 0 | 2821.1837 | 0 | 0 | 3103.302 | NA | Yes | 0 | 0 | 0 | 0 | 2786.9531 | 0 | 0 | 3065.6484 | NA | Yes | 0 | 0 | 0 | 0 | 2568.8706 | 0 | 0 | 2825.7577 | NA | Yes | 0 | 0 | 0 | 0 | 2691.9639 | 0 | 0 | 2961.1603 | NA | Yes | 0 | 0 | 0 | 0 | 2542.7699 | 0 | 0 | 2797.0468
| Add one stage of cooling |  | curve fit from AHRI cost survey | VAV_OTHER | VAVDX | VAV_OTHER Cooling Capacity [ton] | US_PS_VAV_OTHER Cooling Capacity [ton] | 37.6916 | 37.6653 | 2823.2002 | 0 | 15 | 3105.5203 | 2821.1837 | 0 | 15 | 3103.302 | 37.2384 | 37.2189 | 2788.4484 | 0 | 15 | 3067.2932 | 2786.9531 | 0 | 15 | 3065.6484 | 34.3939 | 34.3748 | 2570.3411 | 0 | 15 | 2827.3752 | 2568.8706 | 0 | 15 | 2825.7577 | 36.8219 | 35.9801 | 2756.5137 | 0 | 15 | 3032.1651 | 2691.9639 | 0 | 15 | 2961.1603 | 34.8169 | 34.0344 | 2602.7759 | 0 | 15 | 2863.0535 | 2542.7699 | 0 | 15 | 2797.0468
| Variation in VFD size and requirements based on load changes | VFD_Size | If VFD required, VFD cost applied, interpolated on VFD_Size costs based on fan bhp *1.1. Note that values in prototype data are 1.1 times the prototype data
x |  | VFD_Size | system cost | VAV_OTHER | VAVDX | VAV_OTHER Fan Power [hp] | US_PS_VAV_OTHER Fan Power [hp] | 17.1256 | 17.1137 | 6342.6145 | 0 | 15 | 8380.2346 | 6339.4369 | 0 | 15 | 8376.1345 | 17.2927 | 17.28 | 6387.0503 | 0 | 15 | 8437.5694 | 6383.6844 | 0 | 15 | 8433.2264 | 20.1333 | 20.1193 | 7133.4179 | 0 | 15 | 9400.3655 | 7130.653 | 0 | 15 | 9396.8222 | 18.4548 | 17.875 | 6696.1117 | 0 | 15 | 8836.3466 | 6541.9105 | 0 | 15 | 8637.3832 | 18.7504 | 18.1947 | 6774.7089 | 0 | 15 | 8937.7593 | 6626.9297 | 0 | 15 | 8747.0821 |  | -3.1776 | -3.3659 | -2.7649 | -154.2012 | -147.7792
x |  | VFD_Size | system cost | VAV_POD_3 | VAVDX | VAV_POD_3 Fan Power [hp] | US_PS_VAV_POD_3 Fan Power [hp] | 15.3964 | 15.2985 | 5882.7336 | 0 | 15 | 7786.8572 | 5856.7123 | 0 | 15 | 7753.2824 | 15.4185 | 15.317 | 5888.6259 | 0 | 15 | 7794.46 | 5861.62 | 0 | 15 | 7759.6147 | 17.8459 | 17.7333 | 6534.1666 | 0 | 15 | 8627.3912 | 6504.2263 | 0 | 15 | 8588.7597 | 15.6557 | 15.0975 | 5951.7155 | 0 | 15 | 7875.8636 | 5803.2497 | 0 | 15 | 7684.3005 | 15.9407 | 15.4047 | 6027.4842 | 0 | 15 | 7973.6268 | 5884.9579 | 0 | 15 | 7789.7273 |  | -26.0212 | -27.0059 | -29.9403 | -148.4658 | -142.5263
x |  | VFD_Size | system cost | VAV_POD_2 | VAVDX | VAV_POD_2 Fan Power [hp] | US_PS_VAV_POD_2 Fan Power [hp] | 17.1695 | 17.059 | 6354.3011 | 0 | 15 | 8395.3136 | 6324.8944 | 0 | 15 | 8357.3705 | 17.2002 | 17.0854 | 6362.4453 | 0 | 15 | 8405.8219 | 6331.9322 | 0 | 15 | 8366.4513 | 20.0365 | 19.9084 | 7114.2648 | 0 | 15 | 9375.8199 | 7082.6876 | 0 | 15 | 9335.1395 | 17.3284 | 16.725 | 6396.5479 | 0 | 15 | 8449.8239 | 6236.0738 | 0 | 15 | 8242.7667 | 17.6209 | 17.0436 | 6474.3252 | 0 | 15 | 8550.1788 | 6320.7948 | 0 | 15 | 8352.081 |  | -29.4068 | -30.5131 | -31.5772 | -160.474 | -153.5303
x |  | VFD_Size | system cost | VAV_POD_1 | VAVDX | VAV_POD_1 Fan Power [hp] | US_PS_VAV_POD_1 Fan Power [hp] | 17.2919 | 17.1804 | 6386.8306 | 0 | 15 | 8437.2859 | 6357.1806 | 0 | 15 | 8399.029 | 17.3532 | 17.2375 | 6403.1464 | 0 | 15 | 8458.3378 | 6372.3665 | 0 | 15 | 8418.6231 | 20.2283 | 20.0992 | 7152.2324 | 0 | 15 | 9424.4771 | 7126.6676 | 0 | 15 | 9391.7147 | 17.5371 | 16.9255 | 6452.0426 | 0 | 15 | 8521.4279 | 6289.4109 | 0 | 15 | 8311.5867 | 17.8187 | 17.2345 | 6526.9325 | 0 | 15 | 8618.0573 | 6371.5662 | 0 | 15 | 8417.5905 |  | -29.65 | -30.7798 | -25.5647 | -162.6317 | -155.3663
No diff for 2010-13 so HIDE | 90.1-07bh | Supply_Air_Temp_Reset | apply cost if "yes" unless check *IF(Base_Code = "2009", "0","1") |  |  | [Yes, No] are parameter values
Not in 2013 |  | Supply_Air_Temp_Reset |  | VAV_POD_1 | VAVDX | Supply Air Temp. Reset Flag | US_PS_Supply Air Temp. Reset Flag | No | No |  |  |  |  | 0 | 0 | 0 | 0 | No | No |  |  |  |  | 0 | 0 | 0 | 0 | Yes | Yes |  |  |  |  | 18734 | 0 | 20 | 18734 | Yes | Yes |  |  |  |  | 18734 | 0 | 20 | 18734 | Yes | Yes |  |  |  |  | 18734 | 0 | 20 | 18734
Not in 2013 |  | Supply_Air_Temp_Reset |  | VAV_POD_2 | VAVDX | Supply Air Temp. Reset Flag | US_PS_Supply Air Temp. Reset Flag | No | No |  |  |  |  | 0 | 0 | 0 | 0 | No | No |  |  |  |  | 0 | 0 | 0 | 0 | Yes | Yes |  |  |  |  | 18734 | 0 | 20 | 18734 | Yes | Yes |  |  |  |  | 18734 | 0 | 20 | 18734 | Yes | Yes |  |  |  |  | 18734 | 0 | 20 | 18734
Not in 2013 |  | Supply_Air_Temp_Reset |  | VAV_POD_3 | VAVDX | Supply Air Temp. Reset Flag | US_PS_Supply Air Temp. Reset Flag | No | No |  |  |  |  | 0 | 0 | 0 | 0 | No | No |  |  |  |  | 0 | 0 | 0 | 0 | Yes | Yes |  |  |  |  | 18734 | 0 | 20 | 18734 | Yes | Yes |  |  |  |  | 18734 | 0 | 20 | 18734 | Yes | Yes |  |  |  |  | 18734 | 0 | 20 | 18734
Not in 2013 |  | Supply_Air_Temp_Reset |  | VAV_OTHER | VAVDX | Supply Air Temp. Reset Flag | US_PS_Supply Air Temp. Reset Flag | No | No |  |  |  |  | 0 | 0 | 0 | 0 | No | No |  |  |  |  | 0 | 0 | 0 | 0 | Yes | Yes |  |  |  |  | 18734 | 0 | 20 | 18734 | Yes | Yes |  |  |  |  | 18734 | 0 | 20 | 18734 | Yes | Yes |  |  |  |  | 18734 | 0 | 20 | 18734
| 90.1-07ck | Vent_Optimize | apply cost if "Yes", cost value times number of perimeter zones Number of perimeter zones is hard coded |  |  | [Yes, No] are parameter values
Not in 2013 |  | Vent_Optimize |  | VAV_POD_1 | VAVDX | Ventilation Reset Flag add_ck_vav_pod_1 | US_PS_Ventilation Reset Flag add_ck_vav_pod_1 | #N/A | #N/A |  |  |  |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A |  |  |  |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A |  |  |  |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A |  |  |  |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A |  |  |  |  | #N/A | #N/A | #N/A | #N/A
|  | Vent_Optimize |  | VAV_POD_1 | VAVDX | Number of perimeter zones (hard coded - doesn't change) |  | 8 | 8 |  |  |  |  | 982.744 | 0 | 0 | 0 | 8 | 8 |  |  |  |  | 982.744 | 0 | 0 | 0 | 8 | 8 |  |  |  |  | 982.744 | 0 | 0 | 0 | 8 | 8 |  |  |  |  | 982.744 | 0 | 0 | 0 | 8 | 8 |  |  |  |  | 982.744 | 0 | 0 | 0
Not in 2013 |  | Vent_Optimize |  | VAV_POD_2 | VAVDX | Ventilation Reset Flag add_ck_vav_pod_2 | US_PS_Ventilation Reset Flag add_ck_vav_pod_2 | #N/A | #N/A |  |  |  |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A |  |  |  |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A |  |  |  |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A |  |  |  |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A |  |  |  |  | #N/A | #N/A | #N/A | #N/A
|  | Vent_Optimize |  | VAV_POD_2 | VAVDX | Number of perimeter zones (hard coded - doesn't change) |  | 8 | 8 |  |  |  |  | 982.744 | 0 | 0 | 0 | 8 | 8 |  |  |  |  | 982.744 | 0 | 0 | 0 | 8 | 8 |  |  |  |  | 982.744 | 0 | 0 | 0 | 8 | 8 |  |  |  |  | 982.744 | 0 | 0 | 0 | 8 | 8 |  |  |  |  | 982.744 | 0 | 0 | 0
Not in 2013 |  | Vent_Optimize |  | VAV_POD_3 | VAVDX | Ventilation Reset Flag add_ck_vav_pod_3 | US_PS_Ventilation Reset Flag add_ck_vav_pod_3 | #N/A | #N/A |  |  |  |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A |  |  |  |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A |  |  |  |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A |  |  |  |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A |  |  |  |  | #N/A | #N/A | #N/A | #N/A
|  | Vent_Optimize |  | VAV_POD_3 | VAVDX | Number of perimeter zones (hard coded - doesn't change) |  | 8 | 8 |  |  |  |  | 982.744 | 0 | 0 | 0 | 8 | 8 |  |  |  |  | 982.744 | 0 | 0 | 0 | 8 | 8 |  |  |  |  | 982.744 | 0 | 0 | 0 | 8 | 8 |  |  |  |  | 982.744 | 0 | 0 | 0 | 8 | 8 |  |  |  |  | 982.744 | 0 | 0 | 0
Not in 2013 |  | Vent_Optimize |  | VAV_OTHER | VAVDX | Ventilation Reset Flag add_ck_vav_other | US_PS_Ventilation Reset Flag add_ck_vav_other | #N/A | #N/A |  |  |  |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A |  |  |  |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A |  |  |  |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A |  |  |  |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A |  |  |  |  | #N/A | #N/A | #N/A | #N/A
|  | Vent_Optimize |  | VAV_OTHER | VAVDX | Number of perimeter zones (hard coded - doesn't change) |  | 4 | 4 |  |  |  |  | 491.372 | 0 | 0 | 0 | 4 | 4 |  |  |  |  | 491.372 | 0 | 0 | 0 | 4 | 4 |  |  |  |  | 491.372 | 0 | 0 | 0 | 4 | 4 |  |  |  |  | 491.372 | 0 | 0 | 0 | 4 | 4 |  |  |  |  | 491.372 | 0 | 0 | 0
Not in 2013 | IECC VAV fan control | VAV_fan_control | apply cost if supply fan power is 4.5 to under 6.75 bhp - incremental cost for target code only. Include flag - *=IF(Base_Code = "2009", "0","1") Could just apply cost of 7.5 hp VFD if it applies, no need for interpolation.
|  |  |  | VAV_POD_1 | VAVDX | VAV_POD_1 Fan Power [hp] | US_PS_VAV_POD_1 Fan Power [hp] | 15.7199 | 15.6185 | [8 empty] | 15.7756 | 15.6704 | [8 empty] | 18.3894 | 18.272 | [8 empty] | 15.9428 | 15.3869 | [8 empty] | 16.1988 | 15.6677
|  |  |  | VAV_POD_2 | VAVDX | VAV_POD_2 Fan Power [hp] | US_PS_VAV_POD_2 Fan Power [hp] | 15.6087 | 15.5082 | [8 empty] | 15.6365 | 15.5322 | [8 empty] | 18.215 | 18.0986 | [8 empty] | 15.7531 | 15.2045 | [8 empty] | 16.019 | 15.4941
|  |  |  | VAV_POD_3 | VAVDX | VAV_POD_3 Fan Power [hp] | US_PS_VAV_POD_3 Fan Power [hp] | 13.9967 | 13.9077 | [8 empty] | 14.0168 | 13.9245 | [8 empty] | 16.2235 | 16.1212 | [8 empty] | 14.2325 | 13.725 | [8 empty] | 14.4915 | 14.0043
|  |  |  | VAV_OTHER | VAVDX | VAV_OTHER Fan Power [hp] | US_PS_VAV_OTHER Fan Power [hp] | 15.5687 | 15.5579 | [8 empty] | 15.7206 | 15.7091 | [8 empty] | 18.303 | 18.2903 | [8 empty] | 16.7771 | 16.25 | [8 empty] | 17.0458 | 16.5406
HIDE; no diff in 2010-2013 requirement; difference in size not warrant cost adjustment for OA dampers | 90.1-07cb | Outdoor_Air_Dampers | Use the upper rows for gravity dampers if value is "gravity", cost is 0. If "motorized, cost is difference between motorized and gravity. If system has an economizer, then there is no added cost for a motorized damper vs. a gravity damper and value is set to $0,
Not in 2013 |  | Outdoor_Air_Dampers | system cost | VAV_POD_1 | VAVDX | VAV_POD_1 OA Damper [gravity, motorized] | US_PS_VAV_POD_1 OA Damper [gravity, motorized] | motorized | motorized | 454.371 | 0 | 20 | 397.8782 | 562.9327 | 0 | 20 | 615.0582 | motorized | motorized | 454.371 | 0 | 20 | 397.8782 | 562.9327 | 0 | 20 | 615.0582 | motorized | motorized | 454.371 | 0 | 20 | 397.8782 | 562.9327 | 0 | 20 | 615.0582 | motorized | motorized | 454.371 | 0 | 20 | 397.8782 | 562.9327 | 0 | 20 | 615.0582 | motorized | motorized | 454.371 | 0 | 20 | 397.8782 | 562.9327 | 0 | 20 | 615.0582
|  | Outdoor_Air_Dampers_Gravity | item cost |  |  | VAV_POD_1 OA Rate [cfm] | US_PS_VAV_POD_1 OA Rate [cfm] | 6282.6911 | 6282.6911 | 1047.5529 | 155.7897 | 20 | 1154.1903 | 1126.4557 | 155.7897 | 20 | 1408.4049 | 6282.6911 | 6282.6911 | 1047.5529 | 155.7897 | 20 | 1154.1903 | 1126.4557 | 155.7897 | 20 | 1408.4049 | 6282.6911 | 6282.6911 | 1047.5529 | 155.7897 | 20 | 1154.1903 | 1126.4557 | 155.7897 | 20 | 1408.4049 | 6282.6911 | 6282.6911 | 1047.5529 | 155.7897 | 20 | 1154.1903 | 1126.4557 | 155.7897 | 20 | 1408.4049 | 6282.6911 | 6282.6911 | 1047.5529 | 155.7897 | 20 | 1154.1903 | 1126.4557 | 155.7897 | 20 | 1408.4049
|  | Outdoor_Air_Dampers_Motorized | item cost | VAV_POD_1 | VAVDX | VAV_POD_1 OA Rate [cfm] | US_PS_VAV_POD_1 OA Rate [cfm] | 6282.6911 | 6282.6911 | 1501.9239 | 155.7897 | 20 | 1552.0685 | 1689.3884 | 155.7897 | 20 | 2023.4631 | 6282.6911 | 6282.6911 | 1501.9239 | 155.7897 | 20 | 1552.0685 | 1689.3884 | 155.7897 | 20 | 2023.4631 | 6282.6911 | 6282.6911 | 1501.9239 | 155.7897 | 20 | 1552.0685 | 1689.3884 | 155.7897 | 20 | 2023.4631 | 6282.6911 | 6282.6911 | 1501.9239 | 155.7897 | 20 | 1552.0685 | 1689.3884 | 155.7897 | 20 | 2023.4631 | 6282.6911 | 6282.6911 | 1501.9239 | 155.7897 | 20 | 1552.0685 | 1689.3884 | 155.7897 | 20 | 2023.4631
Not in 2013 |  | Outdoor_Air_Dampers | system cost | VAV_POD_2 | VAVDX | VAV_POD_2 OA Damper [gravity, motorized] | US_PS_VAV_POD_2 OA Damper [gravity, motorized] | motorized | motorized | 454.371 | 0 | 20 | 397.8782 | 562.9327 | 0 | 20 | 615.0582 | motorized | motorized | 454.371 | 0 | 20 | 397.8782 | 562.9327 | 0 | 20 | 615.0582 | motorized | motorized | 454.371 | 0 | 20 | 397.8782 | 562.9327 | 0 | 20 | 615.0582 | motorized | motorized | 454.371 | 0 | 20 | 397.8782 | 562.9327 | 0 | 20 | 615.0582 | motorized | motorized | 454.371 | 0 | 20 | 397.8782 | 562.9327 | 0 | 20 | 615.0582
|  | Outdoor_Air_Dampers_Gravity | item cost |  |  | VAV_POD_2 OA Rate [cfm] | US_PS_VAV_POD_2 OA Rate [cfm] | 6282.6911 | 6282.6911 | 1047.5529 | 155.7897 | 20 | 1154.1903 | 1126.4557 | 155.7897 | 20 | 1408.4049 | 6282.6911 | 6282.6911 | 1047.5529 | 155.7897 | 20 | 1154.1903 | 1126.4557 | 155.7897 | 20 | 1408.4049 | 6282.6911 | 6282.6911 | 1047.5529 | 155.7897 | 20 | 1154.1903 | 1126.4557 | 155.7897 | 20 | 1408.4049 | 6282.6911 | 6282.6911 | 1047.5529 | 155.7897 | 20 | 1154.1903 | 1126.4557 | 155.7897 | 20 | 1408.4049 | 6282.6911 | 6282.6911 | 1047.5529 | 155.7897 | 20 | 1154.1903 | 1126.4557 | 155.7897 | 20 | 1408.4049
|  | Outdoor_Air_Dampers_Motorized | item cost | VAV_POD_2 | VAVDX | VAV_POD_2 OA Rate [cfm] | US_PS_VAV_POD_2 OA Rate [cfm] | 6282.6911 | 6282.6911 | 1501.9239 | 155.7897 | 20 | 1552.0685 | 1689.3884 | 155.7897 | 20 | 2023.4631 | 6282.6911 | 6282.6911 | 1501.9239 | 155.7897 | 20 | 1552.0685 | 1689.3884 | 155.7897 | 20 | 2023.4631 | 6282.6911 | 6282.6911 | 1501.9239 | 155.7897 | 20 | 1552.0685 | 1689.3884 | 155.7897 | 20 | 2023.4631 | 6282.6911 | 6282.6911 | 1501.9239 | 155.7897 | 20 | 1552.0685 | 1689.3884 | 155.7897 | 20 | 2023.4631 | 6282.6911 | 6282.6911 | 1501.9239 | 155.7897 | 20 | 1552.0685 | 1689.3884 | 155.7897 | 20 | 2023.4631
Not in 2013 |  | Outdoor_Air_Dampers | system cost | VAV_POD_3 | VAVDX | VAV_POD_3 OA Damper [gravity, motorized] | US_PS_VAV_POD_3 OA Damper [gravity, motorized] | motorized | motorized | 487.2696 | 0 | 20 | 448.0802 | 592.7322 | 0 | 20 | 663.6942 | motorized | motorized | 487.2696 | 0 | 20 | 448.0802 | 592.7322 | 0 | 20 | 663.6942 | motorized | motorized | 487.2696 | 0 | 20 | 448.0802 | 592.7322 | 0 | 20 | 663.6942 | motorized | motorized | 487.2696 | 0 | 20 | 448.0802 | 592.7322 | 0 | 20 | 663.6942 | motorized | motorized | 487.2696 | 0 | 20 | 448.0802 | 592.7322 | 0 | 20 | 663.6942
|  | Outdoor_Air_Dampers_Gravity | item cost |  |  | VAV_POD_3 OA Rate [cfm] | US_PS_VAV_POD_3 OA Rate [cfm] | 5422.4258 | 5422.4258 | 908.8469 | 151.71 | 20 | 987.1133 | 978.9458 | 151.71 | 20 | 1212.963 | 5422.4258 | 5422.4258 | 908.8469 | 151.71 | 20 | 987.1133 | 978.9458 | 151.71 | 20 | 1212.963 | 5422.4258 | 5422.4258 | 908.8469 | 151.71 | 20 | 987.1133 | 978.9458 | 151.71 | 20 | 1212.963 | 5422.4258 | 5422.4258 | 908.8469 | 151.71 | 20 | 987.1133 | 978.9458 | 151.71 | 20 | 1212.963 | 5422.4258 | 5422.4258 | 908.8469 | 151.71 | 20 | 987.1133 | 978.9458 | 151.71 | 20 | 1212.963
|  | Outdoor_Air_Dampers_Motorized | item cost | VAV_POD_3 | VAVDX | VAV_POD_3 OA Rate [cfm] | US_PS_VAV_POD_3 OA Rate [cfm] | 5422.4258 | 5422.4258 | 1396.1166 | 151.71 | 20 | 1435.1936 | 1571.678 | 151.71 | 20 | 1876.6572 | 5422.4258 | 5422.4258 | 1396.1166 | 151.71 | 20 | 1435.1936 | 1571.678 | 151.71 | 20 | 1876.6572 | 5422.4258 | 5422.4258 | 1396.1166 | 151.71 | 20 | 1435.1936 | 1571.678 | 151.71 | 20 | 1876.6572 | 5422.4258 | 5422.4258 | 1396.1166 | 151.71 | 20 | 1435.1936 | 1571.678 | 151.71 | 20 | 1876.6572 | 5422.4258 | 5422.4258 | 1396.1166 | 151.71 | 20 | 1435.1936 | 1571.678 | 151.71 | 20 | 1876.6572
Not in 2013 |  | Outdoor_Air_Dampers | system cost | VAV_OTHER | VAVDX | VAV_OTHER OA Damper [gravity, motorized] | US_PS_VAV_OTHER OA Damper [gravity, motorized] | motorized | motorized | 560.0432 | 0 | 20 | 571.4363 | 655.3509 | 0 | 20 | 776.9451 | motorized | motorized | 560.0432 | 0 | 20 | 571.4363 | 655.3509 | 0 | 20 | 776.9451 | motorized | motorized | 560.0432 | 0 | 20 | 571.4363 | 655.3509 | 0 | 20 | 776.9451 | motorized | motorized | 560.0432 | 0 | 20 | 571.4363 | 655.3509 | 0 | 20 | 776.9451 | motorized | motorized | 560.0432 | 0 | 20 | 571.4363 | 655.3509 | 0 | 20 | 776.9451
|  | Outdoor_Air_Dampers_Gravity | item cost |  |  | VAV_OTHER OA Rate [cfm] | US_PS_VAV_OTHER OA Rate [cfm] | 3111.7872 | 3111.7872 | 564.4796 | 132.3278 | 20 | 571.9485 | 612.7625 | 132.3278 | 20 | 727.51 | 3111.7872 | 3111.7872 | 564.4796 | 132.3278 | 20 | 571.9485 | 612.7625 | 132.3278 | 20 | 727.51 | 3111.7872 | 3111.7872 | 564.4796 | 132.3278 | 20 | 571.9485 | 612.7625 | 132.3278 | 20 | 727.51 | 3111.7872 | 3111.7872 | 564.4796 | 132.3278 | 20 | 571.9485 | 612.7625 | 132.3278 | 20 | 727.51 | 3111.7872 | 3111.7872 | 564.4796 | 132.3278 | 20 | 571.9485 | 612.7625 | 132.3278 | 20 | 727.51
|  | Outdoor_Air_Dampers_Motorized | item cost | VAV_OTHER | VAVDX | VAV_OTHER OA Rate [cfm] | US_PS_VAV_OTHER OA Rate [cfm] | 3111.7872 | 3111.7872 | 1124.5228 | 132.3278 | 20 | 1143.3848 | 1268.1134 | 132.3278 | 20 | 1504.4551 | 3111.7872 | 3111.7872 | 1124.5228 | 132.3278 | 20 | 1143.3848 | 1268.1134 | 132.3278 | 20 | 1504.4551 | 3111.7872 | 3111.7872 | 1124.5228 | 132.3278 | 20 | 1143.3848 | 1268.1134 | 132.3278 | 20 | 1504.4551 | 3111.7872 | 3111.7872 | 1124.5228 | 132.3278 | 20 | 1143.3848 | 1268.1134 | 132.3278 | 20 | 1504.4551 | 3111.7872 | 3111.7872 | 1124.5228 | 132.3278 | 20 | 1143.3848 | 1268.1134 | 132.3278 | 20 | 1504.4551
Not in 2013 |  | Outdoor_Air_Dampers | system cost | PSZ-AC_2:5 | CAVDX | PSZ-AC_2:5 OA Damper [gravity, motorized] | US_PS_PSZ-AC_2:5 OA Damper [gravity, motorized] | motorized | motorized | 442.0028 | 0 | 20 | 418.5931 | 518.478 | 0 | 20 | 590.0971 | motorized | motorized | 442.0028 | 0 | 20 | 418.5931 | 518.478 | 0 | 20 | 590.0971 | motorized | motorized | 442.0028 | 0 | 20 | 418.5931 | 518.478 | 0 | 20 | 590.0971 | motorized | motorized | 442.0028 | 0 | 20 | 418.5931 | 518.478 | 0 | 20 | 590.0971 | motorized | motorized | 442.0028 | 0 | 20 | 418.5931 | 518.478 | 0 | 20 | 590.0971
|  | Outdoor_Air_Dampers_Gravity | item cost |  |  | PSZ-AC_2:5 OA Rate [cfm] | US_PS_PSZ-AC_2:5 OA Rate [cfm] | 1152.7343 | 1152.7343 | 350.8466 | 110.4833 | 20 | 360.7172 | 380.2534 | 110.4833 | 20 | 455.4621 | 1152.7343 | 1152.7343 | 350.8466 | 110.4833 | 20 | 360.7172 | 380.2534 | 110.4833 | 20 | 455.4621 | 1152.7343 | 1152.7343 | 350.8466 | 110.4833 | 20 | 360.7172 | 380.2534 | 110.4833 | 20 | 455.4621 | 1152.7343 | 1152.7343 | 350.8466 | 110.4833 | 20 | 360.7172 | 380.2534 | 110.4833 | 20 | 455.4621 | 1152.7343 | 1152.7343 | 350.8466 | 110.4833 | 20 | 360.7172 | 380.2534 | 110.4833 | 20 | 455.4621
|  | Outdoor_Air_Dampers_Motorized | item cost | PSZ-AC_2:5 | CAVDX | PSZ-AC_2:5 OA Rate [cfm] | US_PS_PSZ-AC_2:5 OA Rate [cfm] | 1152.7343 | 1152.7343 | 792.8494 | 110.4833 | 20 | 779.3103 | 898.7314 | 110.4833 | 20 | 1045.5592 | 1152.7343 | 1152.7343 | 792.8494 | 110.4833 | 20 | 779.3103 | 898.7314 | 110.4833 | 20 | 1045.5592 | 1152.7343 | 1152.7343 | 792.8494 | 110.4833 | 20 | 779.3103 | 898.7314 | 110.4833 | 20 | 1045.5592 | 1152.7343 | 1152.7343 | 792.8494 | 110.4833 | 20 | 779.3103 | 898.7314 | 110.4833 | 20 | 1045.5592 | 1152.7343 | 1152.7343 | 792.8494 | 110.4833 | 20 | 779.3103 | 898.7314 | 110.4833 | 20 | 1045.5592
Not in 2013 |  | Outdoor_Air_Dampers | system cost | PSZ-AC_2:7 | CAVDX | PSZ-AC_2:7 OA Damper [gravity, motorized] | US_PS_PSZ-AC_2:7 OA Damper [gravity, motorized] | motorized | motorized | 559.1888 | 0 | 20 | 569.5603 | 654.7304 | 0 | 20 | 775.4186 | motorized | motorized | 1129.0162 | 132.9153 | 20 | 1147.9672 | 1273.1782 | 132.9153 | 20 | 1510.4744 | motorized | motorized | 559.1888 | 0 | 20 | 569.5603 | 654.7304 | 0 | 20 | 775.4186 | motorized | motorized | 559.1888 | 0 | 20 | 569.5603 | 654.7304 | 0 | 20 | 775.4186 | motorized | motorized | 559.1888 | 0 | 20 | 569.5603 | 654.7304 | 0 | 20 | 775.4186
|  | Outdoor_Air_Dampers_Gravity | item cost |  |  | PSZ-AC_2:7 OA Rate [cfm] | US_PS_PSZ-AC_2:7 OA Rate [cfm] | 3153.0841 | 3153.0841 | 569.8274 | 132.9153 | 20 | 578.407 | 618.4478 | 132.9153 | 20 | 735.0558 | 3153.0841 | 3153.0841 | 569.8274 | 132.9153 | 20 | 578.407 | 618.4478 | 132.9153 | 20 | 735.0558 | 3153.0841 | 3153.0841 | 569.8274 | 132.9153 | 20 | 578.407 | 618.4478 | 132.9153 | 20 | 735.0558 | 3153.0841 | 3153.0841 | 569.8274 | 132.9153 | 20 | 578.407 | 618.4478 | 132.9153 | 20 | 735.0558 | 3153.0841 | 3153.0841 | 569.8274 | 132.9153 | 20 | 578.407 | 618.4478 | 132.9153 | 20 | 735.0558
|  | Outdoor_Air_Dampers_Motorized | item cost | PSZ-AC_2:7 | CAVDX | PSZ-AC_2:7 OA Rate [cfm] | US_PS_PSZ-AC_2:7 OA Rate [cfm] | 3153.0841 | 3153.0841 | 1129.0162 | 132.9153 | 20 | 1147.9672 | 1273.1782 | 132.9153 | 20 | 1510.4744 | 3153.0841 | 3153.0841 | 1129.0162 | 132.9153 | 20 | 1147.9672 | 1273.1782 | 132.9153 | 20 | 1510.4744 | 3153.0841 | 3153.0841 | 1129.0162 | 132.9153 | 20 | 1147.9672 | 1273.1782 | 132.9153 | 20 | 1510.4744 | 3153.0841 | 3153.0841 | 1129.0162 | 132.9153 | 20 | 1147.9672 | 1273.1782 | 132.9153 | 20 | 1510.4744 | 3153.0841 | 3153.0841 | 1129.0162 | 132.9153 | 20 | 1147.9672 | 1273.1782 | 132.9153 | 20 | 1510.4744
| 90.1-13 u Transfer air | Transfer_Door_Louvers | item cost | Manual Entry | Q | Number of restrooms |  | 8 | 8 | 2311.4557 | 0 | 30 | 2487.3521 | 1850.8818 | 0 | 30 | 2025.8582 | 8 | 8 | 2311.4557 | 0 | 30 | 2487.3521 | 1850.8818 | 0 | 30 | 2025.8582 | 8 | 8 | 2311.4557 | 0 | 30 | 2487.3521 | 1850.8818 | 0 | 30 | 2025.8582 | 8 | 8 | 2311.4557 | 0 | 30 | 2487.3521 | 1850.8818 | 0 | 30 | 2025.8582 | 8 | 8 | 2311.4557 | 0 | 30 | 2487.3521 | 1850.8818 | 0 | 30 | 2025.8582
| Differences in economizer size and requirements based on load changes | DX_Economizer | If any value other than "no" lookup cost based on supply airflow cfm |  |  | [No, DifferentialEnthalpy] are parameter values
x |  | DX_Economizer |  | VAV_POD_1 | VAVDX | VAV_POD_1 (economizer) | US_PS_VAV_POD_1 (economizer) | DifferentialEnthalpy | DifferentialEnthalpy | 13676.9607 | 214.5653 | 15 | 15563.553 | 13597.9823 | 214.5653 | 15 | 15474.59 | DifferentialEnthalpy | DifferentialEnthalpy | 13729.6129 | 214.5653 | 15 | 15622.8616 | 13624.3084 | 214.5653 | 15 | 15504.2443 | DifferentialDryBulb | DifferentialDryBulb | 15967.3323 | 214.5653 | 15 | 18143.4786 | 15862.0278 | 214.5653 | 15 | 18024.8613 | DifferentialEnthalpy | DifferentialEnthalpy | 13861.2434 | 214.5653 | 15 | 15771.1332 | 13387.3734 | 214.5653 | 15 | 15237.3555 | DifferentialDryBulb | DifferentialDryBulb | 14098.1784 | 214.5653 | 15 | 16038.022 | 13624.3084 | 214.5653 | 15 | 15504.2443 |  | -78.9783 | -105.3044 | -105.3044 | -473.87 | -473.87
|  | DX_Economizer |  | VAV_POD_1 | VAVDX | VAV_POD_1 Supply Flow Rate [cfm] | US_PS_VAV_POD_1 Supply Flow Rate [cfm] | 10806.288 | 10742.7216 | 13676.9607 | 214.5653 | 15 | 15563.553 | 13597.9823 | 214.5653 | 15 | 15474.59 | 10848.6656 | 10763.9104 | 13729.6129 | 214.5653 | 15 | 15622.8616 | 13624.3084 | 214.5653 | 15 | 15504.2443 | 12649.7136 | 12564.9584 | 15967.3323 | 214.5653 | 15 | 18143.4786 | 15862.0278 | 214.5653 | 15 | 18024.8613 | 10954.6096 | 10573.2112 | 13861.2434 | 214.5653 | 15 | 15771.1332 | 13387.3734 | 214.5653 | 15 | 15237.3555 | 11145.3088 | 10763.9104 | 14098.1784 | 214.5653 | 15 | 16038.022 | 13624.3084 | 214.5653 | 15 | 15504.2443
x |  | DX_Economizer |  | VAV_POD_2 | VAVDX | VAV_POD_2 (economizer) | US_PS_VAV_POD_2 (economizer) | DifferentialEnthalpy | DifferentialEnthalpy | 13571.6562 | 214.5653 | 15 | 15444.9357 | 13492.6779 | 214.5653 | 15 | 15355.9727 | DifferentialEnthalpy | DifferentialEnthalpy | 13597.9823 | 214.5653 | 15 | 15474.59 | 13519.004 | 214.5653 | 15 | 15385.6271 | DifferentialDryBulb | DifferentialDryBulb | 15809.3756 | 214.5653 | 15 | 17965.5527 | 15704.0712 | 214.5653 | 15 | 17846.9354 | DifferentialEnthalpy | DifferentialEnthalpy | 13703.2868 | 214.5653 | 15 | 15593.2073 | 13229.4168 | 214.5653 | 15 | 15059.4296 | DifferentialDryBulb | DifferentialDryBulb | 13940.2218 | 214.5653 | 15 | 15860.0961 | 13492.6779 | 214.5653 | 15 | 15355.9727 |  | -78.9783 | -78.9783 | -105.3044 | -473.87 | -447.5439
|  | DX_Economizer |  | VAV_POD_2 | VAVDX | VAV_POD_2 Supply Flow Rate [cfm] | US_PS_VAV_POD_2 Supply Flow Rate [cfm] | 10721.5328 | 10657.9664 | 13571.6562 | 214.5653 | 15 | 15444.9357 | 13492.6779 | 214.5653 | 15 | 15355.9727 | 10742.7216 | 10679.1552 | 13597.9823 | 214.5653 | 15 | 15474.59 | 13519.004 | 214.5653 | 15 | 15385.6271 | 12522.5808 | 12437.8256 | 15809.3756 | 214.5653 | 15 | 17965.5527 | 15704.0712 | 214.5653 | 15 | 17846.9354 | 10827.4768 | 10446.0784 | 13703.2868 | 214.5653 | 15 | 15593.2073 | 13229.4168 | 214.5653 | 15 | 15059.4296 | 11018.176 | 10657.9664 | 13940.2218 | 214.5653 | 15 | 15860.0961 | 13492.6779 | 214.5653 | 15 | 15355.9727
x |  | DX_Economizer |  | VAV_POD_3 | VAVDX | VAV_POD_3 (economizer) | US_PS_VAV_POD_3 (economizer) | DifferentialEnthalpy | DifferentialEnthalpy | 12123.0246 | 208.6678 | 15 | 13767.4686 | 12043.9467 | 207.8232 | 15 | 13671.849 | DifferentialEnthalpy | DifferentialEnthalpy | 12149.3839 | 208.9494 | 15 | 13799.3418 | 12070.306 | 208.1047 | 15 | 13703.7222 | DifferentialDryBulb | DifferentialDryBulb | 14098.1784 | 214.5653 | 15 | 16038.022 | 14019.2001 | 214.5653 | 15 | 15949.0591 | DifferentialEnthalpy | DifferentialEnthalpy | 12333.8991 | 210.9201 | 15 | 14022.4541 | 11885.7908 | 206.134 | 15 | 13480.6099 | DifferentialDryBulb | DifferentialDryBulb | 12544.7736 | 213.1724 | 15 | 14277.4396 | 12123.0246 | 208.6678 | 15 | 13767.4686 |  | -79.0779 | -79.0779 | -78.9783 | -448.1083 | -421.749
|  | DX_Economizer |  | VAV_POD_3 | VAVDX | VAV_POD_3 Supply Flow Rate [cfm] | US_PS_VAV_POD_3 Supply Flow Rate [cfm] | 9556.1488 | 9492.5824 | 12123.0246 | 208.6678 | 15 | 13767.4686 | 12043.9467 | 207.8232 | 15 | 13671.849 | 9577.3376 | 9513.7712 | 12149.3839 | 208.9494 | 15 | 13799.3418 | 12070.306 | 208.1047 | 15 | 13703.7222 | 11145.3088 | 11081.7424 | 14098.1784 | 214.5653 | 15 | 16038.022 | 14019.2001 | 214.5653 | 15 | 15949.0591 | 9725.6592 | 9365.4496 | 12333.8991 | 210.9201 | 15 | 14022.4541 | 11885.7908 | 206.134 | 15 | 13480.6099 | 9895.1696 | 9556.1488 | 12544.7736 | 213.1724 | 15 | 14277.4396 | 12123.0246 | 208.6678 | 15 | 13767.4686
x |  | DX_Economizer |  | VAV_OTHER | VAVDX | VAV_OTHER (economizer) | US_PS_VAV_OTHER (economizer) | DifferentialEnthalpy | DifferentialEnthalpy | 14308.7873 | 214.5653 | 15 | 16275.2566 | 14282.4612 | 214.5653 | 15 | 16245.6023 | DifferentialEnthalpy | DifferentialEnthalpy | 14440.4179 | 214.5653 | 15 | 16423.5282 | 14440.4179 | 214.5653 | 15 | 16423.5282 | DifferentialDryBulb | DifferentialDryBulb | 16783.4417 | 214.5653 | 15 | 19062.7625 | 16757.1156 | 214.5653 | 15 | 19033.1081 | DifferentialEnthalpy | DifferentialEnthalpy | 14572.0484 | 214.5653 | 15 | 16571.7998 | 14124.5045 | 214.5653 | 15 | 16067.6764 | DifferentialDryBulb | DifferentialDryBulb | 14808.9834 | 214.5653 | 15 | 16838.6886 | 14387.7656 | 214.5653 | 15 | 16364.2195 |  | -26.3261 | 0 | -26.3261 | -447.5439 | -421.2178
|  | DX_Economizer |  | VAV_OTHER | VAVDX | VAV_OTHER Supply Flow Rate [cfm] | US_PS_VAV_OTHER Supply Flow Rate [cfm] | 11314.8192 | 11293.6304 | 14308.7873 | 214.5653 | 15 | 16275.2566 | 14282.4612 | 214.5653 | 15 | 16245.6023 | 11420.7632 | 11420.7632 | 14440.4179 | 214.5653 | 15 | 16423.5282 | 14440.4179 | 214.5653 | 15 | 16423.5282 | 13306.5664 | 13285.3776 | 16783.4417 | 214.5653 | 15 | 19062.7625 | 16757.1156 | 214.5653 | 15 | 19033.1081 | 11526.7072 | 11166.4976 | 14572.0484 | 214.5653 | 15 | 16571.7998 | 14124.5045 | 214.5653 | 15 | 16067.6764 | 11717.4064 | 11378.3856 | 14808.9834 | 214.5653 | 15 | 16838.6886 | 14387.7656 | 214.5653 | 15 | 16364.2195
x |  | DX_Economizer |  | PSZ-AC_1:6 | CAVDX | PSZ-AC_1:6 (economizer) | US_PS_PSZ-AC_1:6 (economizer) | DifferentialEnthalpy | DifferentialEnthalpy | 3934.8758 | 158.1558 | 15 | 4400.8711 | 3948.3041 | 158.4373 | 15 | 4415.8541 | DifferentialEnthalpy | DifferentialEnthalpy | 3988.5891 | 159.2819 | 15 | 4460.8028 | 3988.5891 | 159.2819 | 15 | 4460.8028 | DifferentialDryBulb | DifferentialDryBulb | 4321.0887 | 163.7865 | 15 | 4824.4419 | 4321.0887 | 163.7865 | 15 | 4824.4419 | DifferentialEnthalpy | DifferentialEnthalpy | 3948.3041 | 158.4373 | 15 | 4415.8541 | 3934.8758 | 158.1558 | 15 | 4400.8711 | DifferentialDryBulb | DifferentialDryBulb | 3988.5891 | 159.2819 | 15 | 4460.8028 | 3961.7324 | 158.7188 | 15 | 4430.837 |  | 13.4283 | 0 | 0 | -13.4283 | -26.8566
|  | DX_Economizer |  | PSZ-AC_1:6 | CAVDX | PSZ-AC_1:6 Supply Flow Rate [cfm] | US_PS_PSZ-AC_1:6 Supply Flow Rate [cfm] | 2754.544 | 2775.7328 | 3934.8758 | 158.1558 | 15 | 4400.8711 | 3948.3041 | 158.4373 | 15 | 4415.8541 | 2839.2992 | 2839.2992 | 3988.5891 | 159.2819 | 15 | 4460.8028 | 3988.5891 | 159.2819 | 15 | 4460.8028 | 3178.32 | 3178.32 | 4321.0887 | 163.7865 | 15 | 4824.4419 | 4321.0887 | 163.7865 | 15 | 4824.4419 | 2775.7328 | 2754.544 | 3948.3041 | 158.4373 | 15 | 4415.8541 | 3934.8758 | 158.1558 | 15 | 4400.8711 | 2839.2992 | 2796.9216 | 3988.5891 | 159.2819 | 15 | 4460.8028 | 3961.7324 | 158.7188 | 15 | 4430.837
x |  | DX_Economizer |  | PSZ-AC_2:5 | CAVDX | PSZ-AC_2:5 (economizer) | US_PS_PSZ-AC_2:5 (economizer) | DifferentialEnthalpy | DifferentialEnthalpy | 4015.4457 | 159.845 | 15 | 4490.7687 | 3988.5891 | 159.2819 | 15 | 4460.8028 | DifferentialEnthalpy | DifferentialEnthalpy | 4042.3023 | 160.408 | 15 | 4520.7345 | 4015.4457 | 159.845 | 15 | 4490.7687 | DifferentialDryBulb | DifferentialDryBulb | 4512.942 | 165.7572 | 15 | 5032.3891 | 4458.1268 | 165.1942 | 15 | 4972.9756 | DifferentialEnthalpy | DifferentialEnthalpy | 4069.1589 | 160.9711 | 15 | 4550.7004 | 4002.0174 | 159.5634 | 15 | 4475.7858 | DifferentialDryBulb | DifferentialDryBulb | 4101.8277 | 161.5342 | 15 | 4586.7879 | 4028.874 | 160.1265 | 15 | 4505.7516 |  | -26.8566 | -26.8566 | -54.8152 | -67.1416 | -72.9537
|  | DX_Economizer |  | PSZ-AC_2:5 | CAVDX | PSZ-AC_2:5 Supply Flow Rate [cfm] | US_PS_PSZ-AC_2:5 Supply Flow Rate [cfm] | 2881.6768 | 2839.2992 | 4015.4457 | 159.845 | 15 | 4490.7687 | 3988.5891 | 159.2819 | 15 | 4460.8028 | 2924.0544 | 2881.6768 | 4042.3023 | 160.408 | 15 | 4520.7345 | 4015.4457 | 159.845 | 15 | 4490.7687 | 3326.6416 | 3284.264 | 4512.942 | 165.7572 | 15 | 5032.3891 | 4458.1268 | 165.1942 | 15 | 4972.9756 | 2966.432 | 2860.488 | 4069.1589 | 160.9711 | 15 | 4550.7004 | 4002.0174 | 159.5634 | 15 | 4475.7858 | 3008.8096 | 2902.8656 | 4101.8277 | 161.5342 | 15 | 4586.7879 | 4028.874 | 160.1265 | 15 | 4505.7516
x |  | DX_Economizer |  | PSZ-AC_2:7 | CAVDX | PSZ-AC_2:7 (economizer) | US_PS_PSZ-AC_2:7 (economizer) | DifferentialEnthalpy | DifferentialEnthalpy | 6125.9591 | 201.9183 | 15 | 6834.1979 | 6102.9297 | 201.0737 | 15 | 6807.5768 | DifferentialEnthalpy | DifferentialEnthalpy | 6264.1355 | 206.986 | 15 | 6993.9244 | 6241.1061 | 206.1414 | 15 | 6967.3033 | DifferentialDryBulb | DifferentialDryBulb | 7065.2043 | 214.5653 | 15 | 7908.5856 | 7036.9345 | 214.5653 | 15 | 7876.4462 | DifferentialEnthalpy | DifferentialEnthalpy | 6148.9885 | 202.763 | 15 | 6860.819 | 6056.8708 | 199.3845 | 15 | 6754.3346 | DifferentialDryBulb | DifferentialDryBulb | 6218.0767 | 205.2968 | 15 | 6940.6823 | 6125.9591 | 201.9183 | 15 | 6834.1979 |  | -23.0294 | -23.0294 | -28.2698 | -92.1176 | -92.1176
|  | DX_Economizer |  | PSZ-AC_2:7 | CAVDX | PSZ-AC_2:7 Supply Flow Rate [cfm] | US_PS_PSZ-AC_2:7 Supply Flow Rate [cfm] | 4682.7248 | 4661.536 | 6125.9591 | 201.9183 | 15 | 6834.1979 | 6102.9297 | 201.0737 | 15 | 6807.5768 | 4809.8576 | 4788.6688 | 6264.1355 | 206.986 | 15 | 6993.9244 | 6241.1061 | 206.1414 | 15 | 6967.3033 | 5445.5216 | 5424.3328 | 7065.2043 | 214.5653 | 15 | 7908.5856 | 7036.9345 | 214.5653 | 15 | 7876.4462 | 4703.9136 | 4619.1584 | 6148.9885 | 202.763 | 15 | 6860.819 | 6056.8708 | 199.3845 | 15 | 6754.3346 | 4767.48 | 4682.7248 | 6218.0767 | 205.2968 | 15 | 6940.6823 | 6125.9591 | 201.9183 | 15 | 6834.1979
| Impact of any changes in OA requirements | Energy_Recovery_Packaged | if "Yes" lookup and interpolate costs based on outside airflow, cfm. |  |  | [Yes,No] are parameter values, indicating if expanded ERV requirements apply.
x |  | Energy_Recovery_Packaged |  | VAV_POD_1 | VAVDX | VAV_Pod_1_ERV Flag | US_PS_VAV_Pod_1_ERV Flag | Yes | Yes | 46538.8576 | 255.0825 | 15 | 53063.1988 | 46538.8576 | 255.0825 | 15 | 53063.1988 | Yes | Yes | 46538.8576 | 255.0825 | 15 | 53063.1988 | 46538.8576 | 255.0825 | 15 | 53063.1988 | No | No | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Yes | Yes | 46538.8576 | 255.0825 | 15 | 53063.1988 | 46538.8576 | 255.0825 | 15 | 53063.1988 | Yes | Yes | 46538.8576 | 255.0825 | 15 | 53063.1988 | 46538.8576 | 255.0825 | 15 | 53063.1988 |  | 0 | 0 | 0 | 0 | 0
|  | Energy_Recovery_Packaged |  | VAV_POD_1 | VAVDX | VAV_POD_1 OA Rate [cfm] | US_PS_VAV_POD_1 OA Rate [cfm] | 6282.6911 | 6282.6911 | 46538.8576 | 255.0825 | 15 | 53063.1988 | 46538.8576 | 255.0825 | 15 | 53063.1988 | 6282.6911 | 6282.6911 | 46538.8576 | 255.0825 | 15 | 53063.1988 | 46538.8576 | 255.0825 | 15 | 53063.1988 | 6282.6911 | 6282.6911 | 46538.8576 | 255.0825 | 15 | 53063.1988 | 46538.8576 | 255.0825 | 15 | 53063.1988 | 6282.6911 | 6282.6911 | 46538.8576 | 255.0825 | 15 | 53063.1988 | 46538.8576 | 255.0825 | 15 | 53063.1988 | 6282.6911 | 6282.6911 | 46538.8576 | 255.0825 | 15 | 53063.1988 | 46538.8576 | 255.0825 | 15 | 53063.1988
x |  | Energy_Recovery_Packaged |  | VAV_POD_2 | VAVDX | VAV_Pod_2_ERV Flag | US_PS_VAV_Pod_2_ERV Flag | Yes | Yes | 46538.8576 | 255.0825 | 15 | 53063.1988 | 46538.8576 | 255.0825 | 15 | 53063.1988 | Yes | Yes | 46538.8576 | 255.0825 | 15 | 53063.1988 | 46538.8576 | 255.0825 | 15 | 53063.1988 | No | No | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Yes | Yes | 46538.8576 | 255.0825 | 15 | 53063.1988 | 46538.8576 | 255.0825 | 15 | 53063.1988 | Yes | Yes | 46538.8576 | 255.0825 | 15 | 53063.1988 | 46538.8576 | 255.0825 | 15 | 53063.1988 |  | 0 | 0 | 0 | 0 | 0
|  | Energy_Recovery_Packaged |  | VAV_POD_2 | VAVDX | VAV_POD_2 OA Rate [cfm] | US_PS_VAV_POD_2 OA Rate [cfm] | 6282.6911 | 6282.6911 | 46538.8576 | 255.0825 | 15 | 53063.1988 | 46538.8576 | 255.0825 | 15 | 53063.1988 | 6282.6911 | 6282.6911 | 46538.8576 | 255.0825 | 15 | 53063.1988 | 46538.8576 | 255.0825 | 15 | 53063.1988 | 6282.6911 | 6282.6911 | 46538.8576 | 255.0825 | 15 | 53063.1988 | 46538.8576 | 255.0825 | 15 | 53063.1988 | 6282.6911 | 6282.6911 | 46538.8576 | 255.0825 | 15 | 53063.1988 | 46538.8576 | 255.0825 | 15 | 53063.1988 | 6282.6911 | 6282.6911 | 46538.8576 | 255.0825 | 15 | 53063.1988 | 46538.8576 | 255.0825 | 15 | 53063.1988
x |  | Energy_Recovery_Packaged |  | VAV_POD_3 | VAVDX | VAV_Pod_3_ERV Flag | US_PS_VAV_Pod_3_ERV Flag | Yes | Yes | 40435.1302 | 255.0825 | 15 | 46268.9271 | 40435.1302 | 255.0825 | 15 | 46268.9271 | Yes | Yes | 40435.1302 | 255.0825 | 15 | 46268.9271 | 40435.1302 | 255.0825 | 15 | 46268.9271 | No | No | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Yes | Yes | 40435.1302 | 255.0825 | 15 | 46268.9271 | 40435.1302 | 255.0825 | 15 | 46268.9271 | Yes | Yes | 40435.1302 | 255.0825 | 15 | 46268.9271 | 40435.1302 | 255.0825 | 15 | 46268.9271 |  | 0 | 0 | 0 | 0 | 0
|  | Energy_Recovery_Packaged |  | VAV_POD_3 | VAVDX | VAV_POD_3 OA Rate [cfm] | US_PS_VAV_POD_3 OA Rate [cfm] | 5422.4258 | 5422.4258 | 40435.1302 | 255.0825 | 15 | 46268.9271 | 40435.1302 | 255.0825 | 15 | 46268.9271 | 5422.4258 | 5422.4258 | 40435.1302 | 255.0825 | 15 | 46268.9271 | 40435.1302 | 255.0825 | 15 | 46268.9271 | 5422.4258 | 5422.4258 | 40435.1302 | 255.0825 | 15 | 46268.9271 | 40435.1302 | 255.0825 | 15 | 46268.9271 | 5422.4258 | 5422.4258 | 40435.1302 | 255.0825 | 15 | 46268.9271 | 40435.1302 | 255.0825 | 15 | 46268.9271 | 5422.4258 | 5422.4258 | 40435.1302 | 255.0825 | 15 | 46268.9271 | 40435.1302 | 255.0825 | 15 | 46268.9271
x |  | Energy_Recovery_Packaged |  | VAV_OTHER | VAVDX | VAV_OTHER_ERV Flag | US_PS_VAV_OTHER_ERV Flag | Yes | Yes | 23897.0317 | 255.0825 | 15 | 27767.5568 | 23897.0317 | 255.0825 | 15 | 27767.5568 | Yes | Yes | 23897.0317 | 255.0825 | 15 | 27767.5568 | 23897.0317 | 255.0825 | 15 | 27767.5568 | No | No | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Yes | Yes | 23897.0317 | 255.0825 | 15 | 27767.5568 | 23897.0317 | 255.0825 | 15 | 27767.5568 | Yes | Yes | 23897.0317 | 255.0825 | 15 | 27767.5568 | 23897.0317 | 255.0825 | 15 | 27767.5568 |  | 0 | 0 | 0 | 0 | 0
|  | Energy_Recovery_Packaged |  | VAV_OTHER | VAVDX | VAV_OTHER OA Rate [cfm] | US_PS_VAV_OTHER OA Rate [cfm] | 3111.7872 | 3111.7872 | 23897.0317 | 255.0825 | 15 | 27767.5568 | 23897.0317 | 255.0825 | 15 | 27767.5568 | 3111.7872 | 3111.7872 | 23897.0317 | 255.0825 | 15 | 27767.5568 | 23897.0317 | 255.0825 | 15 | 27767.5568 | 3111.7872 | 3111.7872 | 23897.0317 | 255.0825 | 15 | 27767.5568 | 23897.0317 | 255.0825 | 15 | 27767.5568 | 3111.7872 | 3111.7872 | 23897.0317 | 255.0825 | 15 | 27767.5568 | 23897.0317 | 255.0825 | 15 | 27767.5568 | 3111.7872 | 3111.7872 | 23897.0317 | 255.0825 | 15 | 27767.5568 | 23897.0317 | 255.0825 | 15 | 27767.5568
x |  | Energy_Recovery_Packaged |  | PSZ-AC_2:7 | CAVDX | PSZ_AC_2_7_ERV Flag | US_PS_PSZ_AC_2_7_ERV Flag | Yes | Yes | 24194.4122 | 255.0825 | 15 | 28101.3868 | 24194.4122 | 255.0825 | 15 | 28101.3868 | Yes | Yes | 24194.4122 | 255.0825 | 15 | 28101.3868 | 24194.4122 | 255.0825 | 15 | 28101.3868 | No | No | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Yes | Yes | 24194.4122 | 255.0825 | 15 | 28101.3868 | 24194.4122 | 255.0825 | 15 | 28101.3868 | Yes | Yes | 24194.4122 | 255.0825 | 15 | 28101.3868 | 24194.4122 | 255.0825 | 15 | 28101.3868 |  | 0 | 0 | 0 | 0 | 0
|  | Energy_Recovery_Packaged |  | PSZ-AC_2:7 | CAVDX | PSZ-AC_2:7 OA Rate [cfm] | US_PS_PSZ-AC_2:7 OA Rate [cfm] | 3153.0841 | 3153.0841 | 24194.4122 | 255.0825 | 15 | 28101.3868 | 24194.4122 | 255.0825 | 15 | 28101.3868 | 3153.0841 | 3153.0841 | 24194.4122 | 255.0825 | 15 | 28101.3868 | 24194.4122 | 255.0825 | 15 | 28101.3868 | 3153.0841 | 3153.0841 | 24194.4122 | 255.0825 | 15 | 28101.3868 | 24194.4122 | 255.0825 | 15 | 28101.3868 | 3153.0841 | 3153.0841 | 24194.4122 | 255.0825 | 15 | 28101.3868 | 24194.4122 | 255.0825 | 15 | 28101.3868 | 3153.0841 | 3153.0841 | 24194.4122 | 255.0825 | 15 | 28101.3868 | 24194.4122 | 255.0825 | 15 | 28101.3868
| 90.1-13by SHW runout insulation | SHW_runout | Additional insulation required on SHW runouts | SHW piping heat loss |  | SHW_runout_Insul | US_PS_SHW_runout_Insul | 0 | #N/A | 0 | 0 | 0 | 0 | #N/A | #N/A | 35 | #N/A | 0 | #N/A | 0 | 0 | 0 | 0 | #N/A | #N/A | 35 | #N/A | 0 | #N/A | 0 | 0 | 0 | 0 | #N/A | #N/A | 35 | #N/A | 0 | #N/A | 0 | 0 | 0 | 0 | #N/A | #N/A | 35 | #N/A | 0 | #N/A | 0 | 0 | 0 | 0 | #N/A | #N/A | 35 | #N/A | 416
| 90.1-10aj | ECM_Motor | Upgrade from shaded pole or permanent split capicator motor to ECM. No labor as is part of replaced fan equipment. |  |  | Exhaust Fan count | US_PS_Exhaust Fan count
Not in 2016 |  | ECM_Motor_1/3 |  |  |  | Bathroom Exhaust Fan count | US_PS_Bathroom Exhaust Fan count | 1 | 1 | 301.7599 | 0 | 15 | 331.9358 | 484.1669 | 0 | 15 | 532.5836 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 15 | 0 | 0 | 17 | 0 | 0 | 15 | 0 | 8230.8378 | 0 | 15 | 9053.9216 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 15 | 0 | 500
0 |  | ECM_Motor_3/4 |  |  |  | Kitchen Exhaust Fan count | US_PS_Kitchen Exhaust Fan count | 1 | 1 | 331.4104 | 0 | 15 | 364.5514 | 607.6483 | 0 | 15 | 668.4131 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 15 | 0 | 0 | 10 | 0 | 0 | 15 | 0 | 6076.4826 | 0 | 15 | 6684.1309 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 15 | 0 | 502
| 90.1-16g occ standby controls | occ_standby | 25 conditioned zones |  |  |  |  | 0 | 25 | 0 | 0 | 0 | 0 | 833.4898 | 0 | 375 | 1462.6762 | 0 | 25 | 0 | 0 | 0 | 0 | 833.4898 | 0 | 375 | 1462.6762 | 0 | 25 | 0 | 0 | 0 | 0 | 833.4898 | 0 | 375 | 1462.6762 | 0 | 25 | 0 | 0 | 0 | 0 | 833.4898 | 0 | 375 | 1462.6762 | 0 | 25 | 0 | 0 | 0 | 0 | 833.4898 | 0 | 375 | 1462.6762
x | 90.1-19 b - DCV |  | DCV modeled in more spaces, climates; exceptions removed; manual calc pasted here |  |  | Count of zones where DCV is newly required | 365 | 0 | 13 | 0 | 0 | 15 | 0 | 4745 | 0 | 15 | 4745 | 0 | 13 | 0 | 0 | 15 | 0 | 4745 | 0 | 15 | 4745 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 15 | 0 | 0 | 13 | 0 | 0 | 15 | 0 | 4745 | 0 | 15 | 4745 | 0 | 13 | 0 | 0 | 15 | 0 | 4745 | 0 | 15 | 4745 |  | 4745 | 4745 | 0 | 4745 | 4745
x | 90.1-19bc - Condensing boilers modeled for large systems | Boiler_Capacity | cost based on boiler millions of Btu/h, manual calc hard pasted in here | Boiler |  | HEATSYS1 Capacity [MMBTU/h] | US_PS_HEATSYS1 Capacity [MMBTU/h] | 0.81758 | 0.81683 | 0 | 0 | 40 | 0 | 3349.0193 | 400 | 40 | 3349.0193 | 1.2177 | 1.2155 | 0 | 0 | 40 | 0 | 4983.4412 | 400 | 40 | 4983.4412 | 1.0872 | 1.085 | 0 | 0 | 40 | 0 | 4448.6521 | 400 | 40 | 4448.6521 | 1.4034 | 1.3462 | 0 | 0 | 40 | 0 | 5519.3063 | 400 | 40 | 5519.3063 | 1.5808 | 1.5131 | 0 | 0 | 40 | 0 | 6203.681 | 400 | 40 | 6203.681 |  | 3349.0193 | 4983.4412 | 4448.6521 | 5519.3063 | 6203.681
x | 90.1-19 bx furnace efficiency |  | Large funace >= 225k increases from 80% to 81%. Cost estimate from federal rulemaking and heating capacity of units. Use the target capacity as it's not about load change but % eff improvement | AC_1:6 |  | Furnace heating capacity [kBtuh] | US_PS_PSZ-AC_1:6 Heating Capacity [kBtu/hr] | [30 empty] | 227.1288 | 225.0276 | 0 | 0 | 15 | 0 | 29.9737 | 0 | 15 | 29.9737 | 231.7554 | 229.6802 | 0 | 0 | 15 | 0 | 30.5934 | 0 | 15 | 30.5934 |  | 0 | 0 | 0 | 29.9737 | 30.5934
x | 90.1-19 bx furnace efficiency |  | Large funace >= 225k increases from 80% to 81%. Cost estimate from federal rulemaking and heating capacity of units. Use the target capacity as it's not about load change but % eff improvement | AC_2:7 |  | Furnace heating capacity [kBtuh] | US_PS_PSZ-AC_2:7 Heating Capacity [kBtu/hr] | 274.2161 | 273.2409 | 0 | 0 | 15 | 0 | 36.3957 | 0 | 15 | 36.3957 | 333.2598 | 332.2856 | 0 | 0 | 15 | 0 | 44.2604 | 0 | 15 | 44.2604 | 314.6732 | 313.692 | 0 | 0 | 15 | 0 | 41.7838 | 0 | 15 | 41.7838 | 368.9821 | 365.6973 | 0 | 0 | 15 | 0 | 48.7109 | 0 | 15 | 48.7109 | 395.2944 | 392.3096 | 0 | 0 | 15 | 0 | 52.2556 | 0 | 15 | 52.2556 |  | 36.3957 | 44.2604 | 41.7838 | 48.7109 | 52.2556
| 90.1-16 br | eff_Refr | Addendum G Commercial Refrigerators for Primary School: 2 refrigerators, 24 cubic feet each, efficiency upgraded. |  |  | ea 24 cu ft refridg | Quantity manually entered in col I,J | 2 | 2 | 12409.6863 | 0 | 15 | 13650.6549 | 21744.7249 | 0 | 15 | 23919.1974 | 2 | 2 | 12409.6863 | 0 | 15 | 13650.6549 | 21744.7249 | 0 | 15 | 23919.1974 | 2 | 2 | 12409.6863 | 0 | 15 | 13650.6549 | 21744.7249 | 0 | 15 | 23919.1974 | 2 | 2 | 12409.6863 | 0 | 15 | 13650.6549 | 21744.7249 | 0 | 15 | 23919.1974 | 2 | 2 | 12409.6863 | 0 | 15 | 13650.6549 | 21744.7249 | 0 | 15 | 23919.1974 | 351
| 90.1-16 br | eff_Frzr | Addendum G Commercial Freezer for Primary School8/27/2014 2 freezers, 48 cubic feet each, efficiency upgraded. |  |  | ea 48 cu ft freezer | Quantity manually entered in col I,J | 2 | 2 | 13460.5912 | 0 | 15 | 14806.6504 | 15616.4477 | 0 | 15 | 17178.0925 | 2 | 2 | 13460.5912 | 0 | 15 | 14806.6504 | 15616.4477 | 0 | 15 | 17178.0925 | 2 | 2 | 13460.5912 | 0 | 15 | 14806.6504 | 15616.4477 | 0 | 15 | 17178.0925 | 2 | 2 | 13460.5912 | 0 | 15 | 14806.6504 | 15616.4477 | 0 | 15 | 17178.0925 | 2 | 2 | 13460.5912 | 0 | 15 | 14806.6504 | 15616.4477 | 0 | 15 | 17178.0925 | 352
| 90.1-16 cn | eff_WI_Refr | primary school walk-in refrigerator |  |  | 1 ea | Quantity manually entered in col I,J | 1 | 1 | 7925.6903 | 0 | 15 | 8849.2603 | 8610.2798 | 0 | 15 | 9602.3088 | 1 | 1 | 7925.6903 | 0 | 15 | 8849.2603 | 8610.2798 | 0 | 15 | 9602.3088 | 1 | 1 | 7925.6903 | 0 | 15 | 8849.2603 | 8610.2798 | 0 | 15 | 9602.3088 | 1 | 1 | 7925.6903 | 0 | 15 | 8849.2603 | 8610.2798 | 0 | 15 | 9602.3088 | 1 | 1 | 7925.6903 | 0 | 15 | 8849.2603 | 8610.2798 | 0 | 15 | 9602.3088 | 353
| 90.1-16 cn | eff_WI_Frzr | primary school walk-in freezer |  |  | 1 ea | Quantity manually entered in col I,J | 1 | 1 | 9841.3399 | 0 | 15 | 10956.4749 | 10374.2988 | 0 | 15 | 11542.7297 | 1 | 1 | 9841.3399 | 0 | 15 | 10956.4749 | 10374.2988 | 0 | 15 | 11542.7297 | 1 | 1 | 9841.3399 | 0 | 15 | 10956.4749 | 10374.2988 | 0 | 15 | 11542.7297 | 1 | 1 | 9841.3399 | 0 | 15 | 10956.4749 | 10374.2988 | 0 | 15 | 11542.7297 | 1 | 1 | 9841.3399 | 0 | 15 | 10956.4749 | 10374.2988 | 0 | 15 | 11542.7297 | 354
0 |  | WI_Refr_ECM | Addendum AR 1/20 hp motor for primary school walk-in refrigerator evaporator fan: shaded pole motor to ECM |  |  | 1 ea | Quantity manually entered in col I,J | 1 | 1 | 334.3865 | 0 | 15 | 498.9135 | 390.6099 | 0 | 15 | 560.7592 | 1 | 1 | 334.3865 | 0 | 15 | 498.9135 | 390.6099 | 0 | 15 | 560.7592 | 1 | 1 | 334.3865 | 0 | 15 | 498.9135 | 390.6099 | 0 | 15 | 560.7592 | 1 | 1 | 334.3865 | 0 | 15 | 498.9135 | 390.6099 | 0 | 15 | 560.7592 | 1 | 1 | 334.3865 | 0 | 15 | 498.9135 | 390.6099 | 0 | 15 | 560.7592 | 357
0 |  | WI_Frzr_ECM | Addendum AR 1/40 hp motor for primary school walk-in freezer evaporator fan: shaded pole motor to ECM |  |  | 1 ea | Quantity manually entered in col I,J | 1 | 1 | 340.1665 | 0 | 15 | 505.2714 | 369.787 | 0 | 15 | 537.854 | 1 | 1 | 340.1665 | 0 | 15 | 505.2714 | 369.787 | 0 | 15 | 537.854 | 1 | 1 | 340.1665 | 0 | 15 | 505.2714 | 369.787 | 0 | 15 | 537.854 | 1 | 1 | 340.1665 | 0 | 15 | 505.2714 | 369.787 | 0 | 15 | 537.854 | 1 | 1 | 340.1665 | 0 | 15 | 505.2714 | 369.787 | 0 | 15 | 537.854 | 358
0 |  | WI_OccSnsr | Addendum AR: From No walk-in lighting controls required required in base to low temperature occupancy sensors in both freezer and refrigerator walk ins |  |  | 1 ea | Quantity manually entered in col I,J | 0 | 2 | 0 | 0 | 15 | 0 | 1130.5683 | 0 | 15 | 1443.2706 | 0 | 2 | 0 | 0 | 15 | 0 | 1130.5683 | 0 | 15 | 1443.2706 | 0 | 2 | 0 | 0 | 15 | 0 | 1130.5683 | 0 | 15 | 1443.2706 | 0 | 2 | 0 | 0 | 15 | 0 | 1130.5683 | 0 | 15 | 1443.2706 | 0 | 2 | 0 | 0 | 15 | 0 | 1130.5683 | 0 | 15 | 1443.2706 | 359
| 90.1-07ax | Kitchen Exhaust two items
|  | CAV_DX | lookup based on cooling tons (note - CAV_DX key word appears under the general load changes, not under 90.1-07ax, but change is primarily due to 90.1-07ax in this case) | PSZ-AC_1:6 | CAVDX | PSZ-AC_1:6 Cooling Capacity [ton] | US_PS_PSZ-AC_1:6 Cooling Capacity [ton] | 9.1929 | 9.2251 | 13128.6532 | 0 | 15 | 17416.5986 | 13156.9136 | 0 | 15 | 17454.1195 | 9.2129 | 9.2355 | 13146.1452 | 0 | 15 | 17439.8225 | 13166.0166 | 0 | 15 | 17466.2055 | 9.2506 | 9.2756 | 13179.2941 | 0 | 15 | 17483.8339 | 13201.1953 | 0 | 15 | 17512.9119 | 8.9017 | 8.8402 | 12872.9221 | 0 | 15 | 17077.0671 | 12818.9332 | 0 | 15 | 17005.3866 | 8.5616 | 8.5016 | 12574.2675 | 0 | 15 | 16680.5466 | 12521.6118 | 0 | 15 | 16610.6361
Not in 2013 |  | Kitchen_Hood | lookup cost based on code. Multiply by flag, *IF (Target_Code = 2012, 0, 1) | Kitchen_Hood |  | Exhaust airflow, cfm - values are hard coded, don't vary with location |  |  |  | 5366.7235 | 0 | 25 | 8049.3945 | 4051.8976 | 0 | 25 | 6067.4593 |  |  | 5366.7235 | 0 | 25 | 8049.3945 | 4051.8976 | 0 | 25 | 6067.4593 |  |  | 5366.7235 | 0 | 25 | 8049.3945 | 4051.8976 | 0 | 25 | 6067.4593 |  |  | 5366.7235 | 0 | 25 | 8049.3945 | 4051.8976 | 0 | 25 | 6067.4593 |  |  | 5366.7235 | 0 | 25 | 8049.3945 | 4051.8976 | 0 | 25 | 6067.4593
| HVAC Plant - General Load Change |  | lookup cost based on boiler millions of Btu/h
x |  | Boiler_Capacity |  | Boiler |  | HEATSYS1 Capacity [MMBTU/h] | US_PS_HEATSYS1 Capacity [MMBTU/h] | 0.81758 | 0.81683 | 25649.7856 | 0 | 35 | 33963.8765 | 25635.4514 | 0 | 35 | 33944.6507 | 1.2177 | 1.2155 | 33312.2025 | 0 | 35 | 44241.1149 | 33270.1329 | 0 | 35 | 44184.6889 | 1.0872 | 1.085 | 30814.1803 | 0 | 35 | 40890.6355 | 30772.0356 | 0 | 35 | 40834.1088 | 1.4034 | 1.3462 | 36869.4962 | 0 | 35 | 49012.3451 | 35773.2563 | 0 | 35 | 47542.0102 | 1.5808 | 1.5131 | 40266.2005 | 0 | 35 | 53568.1843 | 38970.0945 | 0 | 35 | 51829.7784 |  | -14.3343 | -42.0696 | -42.1448 | -1096.24 | -1296.106
|  | Pump_Flow | lookup based on GPM
x | Pumps general load change | Pump_FlPri |  | HW Pump | HEATSYS1 PUMP | HEATSYS1 Flow Rate [gal/min] | US_PS_HEATSYS1 Flow Rate [gal/min] | 33.2256 | 33.1952 | OUT OF RANGE | OUT OF RANGE | OUT OF RANGE | OUT OF RANGE | OUT OF RANGE | OUT OF RANGE | OUT OF RANGE | OUT OF RANGE | 49.4847 | 49.3955 | OUT OF RANGE | OUT OF RANGE | OUT OF RANGE | OUT OF RANGE | OUT OF RANGE | OUT OF RANGE | OUT OF RANGE | OUT OF RANGE | 44.184 | 44.0946 | OUT OF RANGE | OUT OF RANGE | OUT OF RANGE | OUT OF RANGE | OUT OF RANGE | OUT OF RANGE | OUT OF RANGE | OUT OF RANGE | 57.0331 | 54.7069 | 25397.6908 | 0 | 20 | 32847.9703 | 25229.5958 | 0 | 20 | 32620.5784 | 64.2406 | 61.4904 | 25918.515 | 0 | 20 | 33552.5196 | 25719.7813 | 0 | 20 | 33283.6809 |  | #VALUE! | #VALUE! | #VALUE! | -168.095 | -198.7337
| 90.1-13 dd expands requirement to heating pumps |  | If value is "VFD" lookup cost based on the next motor size hp greater than 1.1 times the hp shown under Power (HP) | Pump | HW Pump | HEATSYS1 PUMP VSD | US_PS_HEATSYS1 PUMP VSD | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
x | General Load Change - HW | VFD_Size | cost input item for VFD | Pump | HW Pump | HEATSYS1 Pump Power [hp] | US_PS_HEATSYS1 Pump Power [hp] | 0.83819 | 0.83741 | OUT OF RANGE | OUT OF RANGE | OUT OF RANGE | OUT OF RANGE | OUT OF RANGE | OUT OF RANGE | OUT OF RANGE | OUT OF RANGE | 1.2484 | 1.2461 | 2618.4726 | 0 | 15 | 3753.6598 | 2618.4726 | 0 | 15 | 3753.6598 | 1.1146 | 1.1124 | 2618.4726 | 0 | 15 | 3753.6598 | 2618.4726 | 0 | 15 | 3753.6598 | 1.4388 | 1.3801 | 2618.4726 | 0 | 15 | 3753.6598 | 2618.4726 | 0 | 15 | 3753.6598 | 1.6206 | 1.5512 | 2618.4726 | 0 | 15 | 3753.6598 | 2618.4726 | 0 | 15 | 3753.6598 |  | #VALUE! | 0 | 0 | 0 | 0
x | General Load Change - HW | Heating Water Piping | curve fit from Solarc cost calculations | All reheat coils | ZN_VAV_Box | ZN_VAV_BOXes_Max_Reheat_Water_Flow_GPM | US_PS_ZN_VAV_BOXes_Max_Reheat_Water_Flow_GPM | 94.3097 | 93.4261 | 140907.2551 | 0 | 30 | 188341.8485 | 140529.9693 | 0 | 30 | 187875.6257 | 93.0721 | 92.1725 | 140385.7832 | 0 | 30 | 187697.3704 | 140037.5295 | 0 | 30 | 187266.6118 | 85.0563 | 84.1331 | 138196.1041 | 0 | 30 | 184977.375 | 138076.0691 | 0 | 30 | 184825.899 | 95.9294 | 95.578 | 141663.8722 | 0 | 30 | 189276.0768 | 141492.5873 | 0 | 30 | 189064.6587 | 94.7918 | 93.9035 | 141123.7007 | 0 | 30 | 188609.1954 | 140730.7157 | 0 | 30 | 188123.7293 |  | -377.2859 | -348.2537 | -120.0349 | -171.2849 | -392.985
No diff for 2010-13 so HIDE | 90.1-07aj | Motor_Efficiency | lookup cost based on the next motor size hp greater than 1.1 times the hp shown in this row
Not in 2013 |  | Motor_Efficiency |  | VAV_POD_1 | VAVDX | VAV_POD_1 Fan Power [hp] | US_PS_VAV_POD_1 Fan Power [hp] | 15.7199 | 15.6185 | 5929.6923 | 0 | 18 | 7324.6076 | 6177.3306 | 0 | 18 | 7597.0097 | 15.7756 | 15.6704 | 5929.6923 | 0 | 18 | 7324.6076 | 6177.3306 | 0 | 18 | 7597.0097 | 18.3894 | 18.272 | 6729.4015 | 0 | 18 | 8221.7688 | 7017.7248 | 0 | 18 | 8538.9244 | 15.9428 | 15.3869 | 5929.6923 | 0 | 18 | 7324.6076 | 6177.3306 | 0 | 18 | 7597.0097 | 16.1988 | 15.6677 | 5929.6923 | 0 | 18 | 7324.6076 | 6177.3306 | 0 | 18 | 7597.0097
Not in 2013 |  | Motor_Efficiency |  | VAV_POD_2 | VAVDX | VAV_POD_2 Fan Power [hp] | US_PS_VAV_POD_2 Fan Power [hp] | 15.6087 | 15.5082 | 5929.6923 | 0 | 18 | 7324.6076 | 6177.3306 | 0 | 18 | 7597.0097 | 15.6365 | 15.5322 | 5929.6923 | 0 | 18 | 7324.6076 | 6177.3306 | 0 | 18 | 7597.0097 | 18.215 | 18.0986 | 6729.4015 | 0 | 18 | 8221.7688 | 6177.3306 | 0 | 18 | 7597.0097 | 15.7531 | 15.2045 | 5929.6923 | 0 | 18 | 7324.6076 | 6177.3306 | 0 | 18 | 7597.0097 | 16.019 | 15.4941 | 5929.6923 | 0 | 18 | 7324.6076 | 6177.3306 | 0 | 18 | 7597.0097
Not in 2013 |  | Motor_Efficiency |  | VAV_POD_3 | VAVDX | VAV_POD_3 Fan Power [hp] | US_PS_VAV_POD_3 Fan Power [hp] | 13.9967 | 13.9077 | 5929.6923 | 0 | 18 | 7324.6076 | 6177.3306 | 0 | 18 | 7597.0097 | 14.0168 | 13.9245 | 5929.6923 | 0 | 18 | 7324.6076 | 6177.3306 | 0 | 18 | 7597.0097 | 16.2235 | 16.1212 | 5929.6923 | 0 | 18 | 7324.6076 | 6177.3306 | 0 | 18 | 7597.0097 | 14.2325 | 13.725 | 5929.6923 | 0 | 18 | 7324.6076 | 6177.3306 | 0 | 18 | 7597.0097 | 14.4915 | 14.0043 | 5929.6923 | 0 | 18 | 7324.6076 | 6177.3306 | 0 | 18 | 7597.0097
Not in 2013 |  | Motor_Efficiency |  | VAV_OTHER | VAVDX | VAV_OTHER Fan Power [hp] | US_PS_VAV_OTHER Fan Power [hp] | 15.5687 | 15.5579 | 5929.6923 | 0 | 18 | 7324.6076 | 6177.3306 | 0 | 18 | 7597.0097 | 15.7206 | 15.7091 | 5929.6923 | 0 | 18 | 7324.6076 | 6177.3306 | 0 | 18 | 7597.0097 | 18.303 | 18.2903 | 6729.4015 | 0 | 18 | 8221.7688 | 7017.7248 | 0 | 18 | 8538.9244 | 16.7771 | 16.25 | 5929.6923 | 0 | 18 | 7324.6076 | 6177.3306 | 0 | 18 | 7597.0097 | 17.0458 | 16.5406 | 5929.6923 | 0 | 18 | 7324.6076 | 6177.3306 | 0 | 18 | 7597.0097
Not in 2013 |  | Motor_Efficiency |  | PSZ-AC_1:6 | CAVDX | PSZ-AC_1:6 Fan Power [hp] | US_PS_PSZ-AC_1:6 Fan Power [hp] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
Not in 2013 |  | Motor_Efficiency |  | PSZ-AC_2:5 | CAVDX | PSZ-AC_2:5 Fan Power [hp] | US_PS_PSZ-AC_2:5 Fan Power [hp] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
Not in 2013 |  | Motor_Efficiency |  | HW Pump |  | HEATSYS1 Pump Power [hp] | US_PS_HEATSYS1 Pump Power [hp] | 1 | 1 | 1978.685 | 0 | 18 | 2655.0989 | 2044.3665 | 0 | 18 | 2727.3486 | 1.2484 | 1.2461 | 1978.685 | 0 | 18 | 2655.0989 | 2044.3665 | 0 | 18 | 2727.3486 | 1.1146 | 1.1124 | 1978.685 | 0 | 18 | 2655.0989 | 2044.3665 | 0 | 18 | 2727.3486 | 1.4388 | 1.3801 | 2187.8544 | 0 | 18 | 2911.9532 | 2262.3936 | 0 | 18 | 2993.9463 | 1.6206 | 1.5512 | 2187.8544 | 0 | 18 | 2911.9532 | 2262.3936 | 0 | 18 | 2993.9463
[10 empty] | 1562653.1007 |  |  | 2356421.4254 | 1566546.6884 |  |  | 2249278.8416 |  |  | 1576634.3073 |  |  | 2267062.9357 | 1581936.4334 |  |  | 2270496.3126 |  |  | 1486237.6771 |  |  | 2195780.3939 | 1486433.5149 |  |  | 2194031.0964 |  |  | 1611151.5279 |  |  | 2312495.4998 | 1595024.9359 |  |  | 2285039.6252 |  |  | 1622516.0813 |  |  | 2329621.167 | 1607553.3745 |  |  | 2303546.5315
[9 empty] | 2356421.4254 |  |  |  | 2249278.8416 | [5 empty] | 2267062.9357 |  |  |  | 2270496.3126 | [5 empty] | 2195780.3939 |  |  |  | 2194031.0964 | [5 empty] | 2312495.4998 |  |  |  | 2285039.6252 | [5 empty] | 2329621.167 |  |  |  | 2303546.5315

## HVAC Small Hotel Proto
90.1 Cost Effectiveness - Cost Estimate - HVAC - Small Hotel | [7 empty] | Small Hotel
[10 empty] | $AP | $AQ | $AR | $BA | $BK | $BL | $BM | $BW |  |  | $AP | $AQ | $AR | $BA | $BK | $BL | $BM | $BW |  |  | $AP | $AQ | $AR | $BA | $BK | $BL | $BM | $BW |  |  | $AP | $AQ | $AR | $BA | $BK | $BL | $BM | $BW |  |  | $AP | $AQ | $AR | $BA | $BK | $BL | $BM | $BW | Find Row
|  |  | YES |  |  |  |  | 3 | 4 | [8 empty] | 5 | 6 | [8 empty] | 7 | 8 | [8 empty] | 9 | 10 | [8 empty] | 11 | 12
[7 empty] | City-year parameter column |  |  | I | I | I | I | J | J | J | J |  |  | S | S | S | S | T | T | T | T |  |  | AC | AC | AC | AC | AD | AD | AD | AD |  |  | AM | AM | AM | AM | AN | AN | AN | AN |  |  | AW | AW | AW | AW | AX | AX | AX | AX
[7 empty] | Parameter range lookup extension |  |  | _2007Par | _2007Par | _2007Par | _2007Par | _2010Par | _2010Par | _2010Par | _2010Par |  |  | _2007Par | _2007Par | _2007Par | _2007Par | _2010Par | _2010Par | _2010Par | _2010Par |  |  | _2007Par | _2007Par | _2007Par | _2007Par | _2010Par | _2010Par | _2010Par | _2010Par |  |  | _2007Par | _2007Par | _2007Par | _2007Par | _2010Par | _2010Par | _2010Par | _2010Par |  |  | _2007Par | _2007Par | _2007Par | _2007Par | _2010Par | _2010Par | _2010Par | _2010Par
[7 empty] | Cost range lookup extension |  |  | _2007Costs | _2007Costs | _2007Costs | _2007Costs | _2010Costs | _2010Costs | _2010Costs | _2010Costs |  |  | _2007Costs | _2007Costs | _2007Costs | _2007Costs | _2010Costs | _2010Costs | _2010Costs | _2010Costs |  |  | _2007Costs | _2007Costs | _2007Costs | _2007Costs | _2010Costs | _2010Costs | _2010Costs | _2010Costs |  |  | _2007Costs | _2007Costs | _2007Costs | _2007Costs | _2010Costs | _2010Costs | _2010Costs | _2010Costs |  |  | _2007Costs | _2007Costs | _2007Costs | _2007Costs | _2010Costs | _2010Costs | _2010Costs | _2010Costs
[7 empty] | Cost range column index values |  |  | 9 | 10 | 11 | 20 | 10 | 11 | 12 | 22 |  |  | 9 | 10 | 11 | 20 | 10 | 11 | 12 | 22 |  |  | 9 | 10 | 11 | 20 | 10 | 11 | 12 | 22 |  |  | 9 | 10 | 11 | 20 | 10 | 11 | 12 | 22 |  |  | 9 | 10 | 11 | 20 | 10 | 11 | 12 | 22
[8 empty] | Climate Zone 1 | 2A | Base Code | 2019 |  |  | Target Code | 2022 |  |  | Climate Zone 2 | 3A | Base Code | 2019 |  |  | Target Code | 2022 |  |  | Climate Zone 3 | 3B | Base Code | 2019 |  |  | Target Code | 2022 |  |  | Climate Zone 4 | 4A | Base Code | 2019 |  |  | Target Code | 2022 |  |  | Climate Zone 5 | 5A | Base Code | 2019 |  |  | Target Code | 2022 |  |  |  | First cost difference |  | 2019 | vs | 2022
Costs row marked x, other rows not marked | [7 empty] | 2019 | 2022 | [8 empty] | 2019 | 2022 | [8 empty] | Bzse | Target | [8 empty] | 2019 | 2022 | [8 empty] | 2019 | 2022 | [9 empty] | Total new construction (added cost)
| Addendum or general | Key Word | Description | Model | Type | Parameters | Lookup Value in HVAC Data, Current_HVAC_Data | Prototype | Prototype | Total New | Maintenance | Replacement Life | Total | Total New | Maintenance | Replacement Life | Total | Prototype | Prototype | Total New | Maintenance | Replacement Life | Total | Total New | Maintenance | Replacement Life | Total | Prototype | Prototype | Total New | Maintenance | Replacement Life | Total | Total New | Maintenance | Replacement Life | Total | Prototype | Prototype | Total New | Maintenance | Replacement Life | Total | Total New | Maintenance | Replacement Life | Total | Prototype | Prototype | Total New | Maintenance | Replacement Life | Total | Total New | Maintenance | Replacement Life | Total |  | 2A | 3A | 3B | 4A | 5A
| load change |  |  | Object |  |  |  | Data | Data | Construction |  |  | Replacement Cost | Construction |  |  | Replacement Cost | Data | Data | Construction |  |  | Replacement Cost | Construction |  |  | Replacement Cost | Data | Data | Construction |  |  | Replacement Cost | Construction |  |  | Replacement Cost | Data | Data | Construction |  |  | Replacement Cost | Construction |  |  | Replacement Cost | Data | Data | Construction |  |  | Replacement Cost | Construction |  |  | Replacement Cost
| HVAC System - General load change | Supply air units | lookup based on cooling tons |  |  | HVAC System - General Load Change
x |  | CAV_DX |  | SAC_MEETINGROOM | CAVDX | SAC_FRONTOFFICE Cooling Capacity [ton] | US_SH_SAC_FRONTOFFICE Cooling Capacity [ton] | 2.4822 | 2.3852 | 6070.8944 | 0 | 15 | 8444.8396 | 5916.9622 | 0 | 15 | 8246.5887 | 2.3242 | 2.23 | 5820.1993 | 0 | 15 | 8121.9667 | 5670.8267 | 0 | 15 | 7929.5882 | 2.3038 | 2.1979 | 5787.8082 | 0 | 15 | 8080.2498 | 5619.8813 | 0 | 15 | 7863.9751 | 2.2421 | 2.0767 | 5689.9132 | 0 | 15 | 7954.1699 | 5427.5822 | 0 | 15 | 7616.311 | 2.1015 | 2 | 5466.9864 | 0 | 15 | 7667.0601 | 5305.994 | 0 | 15 | 7459.7164 |  | -153.9322 | -149.3726 | -167.9269 | -262.3311 | -160.9924
x |  | CAV_DX |  | SAC_FRONTLOUNGE | CAVDX | SAC_FRONTLOUNGE Cooling Capacity [ton] | US_SH_SAC_FRONTLOUNGE Cooling Capacity [ton] | 6.2755 | 6.0879 | 9950.8065 | 0 | 15 | 13555.0635 | 9714.6625 | 0 | 15 | 13279.6481 | 6.3408 | 6.144 | 10032.9551 | 0 | 15 | 13650.8735 | 9785.2892 | 0 | 15 | 13362.0202 | 6.1201 | 5.7757 | 9755.2036 | 0 | 15 | 13326.9313 | 9412.5082 | 0 | 15 | 12897.5614 | 6.0679 | 5.7836 | 9689.5077 | 0 | 15 | 13250.31 | 9419.2493 | 0 | 15 | 12906.4682 | 5.7091 | 5.525 | 9355.66 | 0 | 15 | 12822.4511 | 9198.4279 | 0 | 15 | 12614.7089 |  | -236.144 | -247.6659 | -342.6955 | -270.2584 | -157.2321
x |  | CAV_DX |  | SAC_FRONTOFFICE | CAVDX | SAC_MEETINGROOM Cooling Capacity [ton] | US_SH_SAC_MEETINGROOM Cooling Capacity [ton] | 2.8867 | 2.7775 | 6493.7646 | 0 | 15 | 9030.5546 | 6382.3047 | 0 | 15 | 8875.3995 | 2.9279 | 2.8141 | 6535.7633 | 0 | 15 | 9089.018 | 6419.666 | 0 | 15 | 8927.4074 | 3.124 | 3.0237 | 6770.9292 | 0 | 15 | 9406.1395 | 6640.1944 | 0 | 15 | 9232.4354 | 2.8132 | 2.6688 | 6418.7141 | 0 | 15 | 8926.0823 | 6271.2947 | 0 | 15 | 8720.8705 | 2.8193 | 2.6747 | 6424.8984 | 0 | 15 | 8934.691 | 6277.3165 | 0 | 15 | 8729.253 |  | -111.4598 | -116.0974 | -130.7348 | -147.4194 | -147.5819
x |  | CAV_DX |  | SAC_EXC_EMPLGE_RESTRM | CAVDX | SAC_EXC_EMPLGE_RESTRM Cooling Capacity [ton] | US_SH_SAC_EXC_EMPLGE_RESTRM Cooling Capacity [ton] | 5.8622 | 5.7063 | 9486.3816 | 0 | 15 | 12995.1664 | 9353.2753 | 0 | 15 | 12819.3004 | 5.8208 | 5.6535 | 9451.0707 | 0 | 15 | 12948.512 | 9308.1975 | 0 | 15 | 12759.7415 | 5.9275 | 5.8099 | 9542.1321 | 0 | 15 | 13068.8265 | 9441.7287 | 0 | 15 | 12936.169 | 5.6095 | 5.415 | 9270.5578 | 0 | 15 | 12710.0102 | 9104.4888 | 0 | 15 | 12490.5924 | 5.4108 | 5.286 | 9100.8875 | 0 | 15 | 12485.8342 | 8994.3209 | 0 | 15 | 12345.0336 |  | -133.1063 | -142.8732 | -100.4034 | -166.069 | -106.5666
x |  | Air Distribution | curve fit from Solarc cost calculations |  |  | sum of 4 system Supply Flow Rate [cfm] values from HVAC data (not the sum of the cooling capacity) |  | 5657.4096 | 5424.3328 | 110641.2456 | 0 | 30 | 178916.5995 | 108440.0444 | 0 | 30 | 175302.9042 | 5678.5984 | 5487.8992 | 110841.3548 | 0 | 30 | 179245.1173 | 109040.372 | 0 | 30 | 176288.4575 | 6504.9616 | 6208.3184 | 118645.6138 | 0 | 30 | 192057.31 | 115844.085 | 0 | 30 | 187458.0613 | 5551.4656 | 5276.0112 | 109640.6996 | 0 | 30 | 177274.0107 | 107039.2799 | 0 | 30 | 173003.2798 | 5572.6544 | 5276.0112 | 109840.8088 | 0 | 30 | 177602.5285 | 107039.2799 | 0 | 30 | 173003.2798 |  | -2201.2013 | -1800.9828 | -2801.5289 | -2601.4197 | -2801.5289
|  |  |  | Material |  | SAC_FO_ADDAQ SUPPLY FAN Supply Flow Rate [cfm] | US_SH_SAC_FO_ADDAQ SUPPLY FAN Supply Flow Rate [cfm] | 805.1744 | 762.7968 | [8 empty] | 783.9856 | 741.608 | [8 empty] | 911.1184 | 847.552 | [8 empty] | 783.9856 | 699.2304 | [8 empty] | 762.7968 | 699.2304
|  |  |  | y = 0.7074x + 6086.9 |  | SAC_FL_ADDAQ SUPPLY FAN Supply Flow Rate [cfm] | US_SH_SAC_FL_ADDAQ SUPPLY FAN Supply Flow Rate [cfm] | 1885.8032 | 1822.2368 | [8 empty] | 1906.992 | 1843.4256 | [8 empty] | 2182.4464 | 2097.6912 | [8 empty] | 1822.2368 | 1737.4816 | [8 empty] | 1822.2368 | 1737.4816
|  |  |  | Labor |  | SAC_MR_ADDAQ SUPPLY FAN Supply Flow Rate [cfm] | US_SH_SAC_MR_ADDAQ SUPPLY FAN Supply Flow Rate [cfm] | 868.7408 | 826.3632 | [8 empty] | 868.7408 | 847.552 | [8 empty] | 995.8736 | 953.496 | [8 empty] | 847.552 | 805.1744 | [8 empty] | 847.552 | 805.1744
|  |  |  | y = 2.9572x + 16341 |  | SAC_EXC_ADDAQ SUPPLY FAN Supply Flow Rate [cfm] | US_SH_SAC_EXC_ADDAQ SUPPLY FAN Supply Flow Rate [cfm] | 2097.6912 | 2012.936 | [8 empty] | 2118.88 | 2055.3136 | [8 empty] | 2415.5232 | 2309.5792 | [8 empty] | 2097.6912 | 2034.1248 | [8 empty] | 2140.0688 | 2034.1248
| 90.1-13 d | Hotel Room Controls: setback & ventilation | Increase in controls cost to shut off ventilation & setback unrented rooms; Basis: 50% central systems | Basis: 90.1 cost effectiveness analysis; adjusted to 2018 $. Cost curve fit: |  | Number_of_Rooms | US_SH_Number_of_Rooms | #N/A | #N/A | 0 | 0 | 15 | 0 | #N/A | 0 | 15 | #N/A | #N/A | #N/A | 0 | 0 | 15 | 0 | #N/A | 0 | 15 | #N/A | #N/A | #N/A | 0 | 0 | 15 | 0 | #N/A | 0 | 15 | #N/A | #N/A | #N/A | 0 | 0 | 15 | 0 | #N/A | 0 | 15 | #N/A | #N/A | #N/A | 0 | 0 | 15 | 0 | #N/A | 0 | 15 | #N/A | #N/A
|  |  |  | Material x | 280.6
|  |  |  | Material intercept | 2497.5
|  |  |  | Labor x | 49.056
|  |  |  | Labor intercept | 688.68
| 90.1-10bk | PTAC_Efficiency | lookup cost values times quantity |  |  | Quantities are the same for all climates and are hard-coded, no lookup needed
|  | PTAC_Efficiency |  | PTAC |  | Type (PTAC, PTHP) |  | PTAC | PTAC | [8 empty] | PTAC | PTAC | [8 empty] | PTAC | PTAC | [8 empty] | PTAC | PTAC | [8 empty] | PTAC | PTAC
0 |  | PTAC_Efficiency |  |  |  | Quantity |  | 85 | 85 | 124747.5728 | 0 | 15 | 160084.4009 | 129213.9189 | 0 | 15 | 164997.3816 | 85 | 85 | 124747.5728 | 0 | 15 | 160084.4009 | 129213.9189 | 0 | 15 | 164997.3816 | 85 | 85 | 124747.5728 | 0 | 15 | 160084.4009 | 129213.9189 | 0 | 15 | 164997.3816 | 85 | 85 | 124747.5728 | 0 | 15 | 160084.4009 | 129213.9189 | 0 | 15 | 164997.3816 | 85 | 85 | 124747.5728 | 0 | 15 | 160084.4009 | 129213.9189 | 0 | 15 | 164997.3816
| 90.1-13by SHW runout insulation | SHW_runout | Additional insulation required on SHW runouts | SHW piping heat loss |  | SHW_runout_Insul | US_SH_SHW_runout_Insul | #N/A | #N/A | #N/A | #N/A | 0 | #N/A | #N/A | #N/A | 35 | #N/A | #N/A | #N/A | #N/A | #N/A | 0 | #N/A | #N/A | #N/A | 35 | #N/A | #N/A | #N/A | #N/A | #N/A | 0 | #N/A | #N/A | #N/A | 35 | #N/A | #N/A | #N/A | #N/A | #N/A | 0 | #N/A | #N/A | #N/A | 35 | #N/A | #N/A | #N/A | #N/A | #N/A | 0 | #N/A | #N/A | #N/A | 35 | #N/A | 416
0 |  | Door_Switch_Control | Increase in controls cost to accommodate door switch through addenda 90.1-10ba |  |  | Door count: Basis: 0.7% of small hotel guest rooms have exterior sliding doors which translates to (1) door for the prototype analyzed | US_SH_Door count: Basis: 0.7% of small hotel guest rooms have exterior sliding doors which translates to (1) door for the prototype analyzed | 1 | 1 | 507.1803 | 0 | 15 | 664.2375 | 762.3411 | 0 | 15 | 852.5621 | 1 | 1 | 507.1803 | 0 | 15 | 664.2375 | 762.3411 | 0 | 15 | 852.5621 | 1 | 1 | 507.1803 | 0 | 15 | 664.2375 | 762.3411 | 0 | 15 | 852.5621 | 1 | 1 | 507.1803 | 0 | 15 | 664.2375 | 762.3411 | 0 | 15 | 852.5621 | 1 | 1 | 507.1803 | 0 | 15 | 664.2375 | 762.3411 | 0 | 15 | 852.5621 | 511
No diff for 2010-13 so HIDE | N. Carolina hotel room HVAC control amendment |  | include cost lookup in all base code fields with *IF(State_Abb = "NC",1,0), only included for NC. Cost is a credit so will show as a negative value in the base code case
Not in 2013 |  | NC_hotel_HVAC | no data needed - conditional on state per above |  |  |  |  | 81 | 81 | [8 empty] | 81 | 81 | [8 empty] | 81 | 81 | [8 empty] | 81 | 81 | [8 empty] | 81 | 81
90.1-16 bo furnace efficiency
|  | Furnace_eff | 4 units |  |  | Furnace heating capacity [Btuh] | US_SH_Furnace heating capacity [Btuh] | 4 | 4 | 18325.3686 | 0 | 60 | 21783.0772 | 18925.8857 | 0 | 60 | 22443.646 | 4 | 4 | 18325.3686 | 0 | 60 | 21783.0772 | 18925.8857 | 0 | 60 | 22443.646 | 4 | 4 | 18325.3686 | 0 | 60 | 21783.0772 | 18925.8857 | 0 | 60 | 22443.646 | 4 | 4 | 18325.3686 | 0 | 60 | 21783.0772 | 18925.8857 | 0 | 60 | 22443.646 | 4 | 4 | 18325.3686 | 0 | 60 | 21783.0772 | 18925.8857 | 0 | 60 | 22443.646
| 90.1-16a low leak RA damper | Outdoor_Air_Dampers | Motorized return air damper
|  | Outdoor_Air_Dampers | system cost | SAC_FRONTLOUNGE | CAVDX | SAC_FrontLounge OA Damper [gravity, motorized] | US_SH_SAC_FrontLounge OA Damper [gravity, motorized] | motorized | motorized | 421.6492 | 0 | 20 | 405.1126 | 493.0432 | 0 | 20 | 565.5854 | motorized | motorized | 421.6492 | 0 | 20 | 405.1126 | 493.0432 | 0 | 20 | 565.5854 | motorized | motorized | 421.6492 | 0 | 20 | 405.1126 | 493.0432 | 0 | 20 | 565.5854 | motorized | motorized | 421.6492 | 0 | 20 | 405.1126 | 493.0432 | 0 | 20 | 565.5854 | motorized | motorized | 421.6492 | 0 | 20 | 405.1126 | 493.0432 | 0 | 20 | 565.5854
|  | Outdoor_Air_Dampers_Gravity | item cost |  |  | SAC_FRONTLOUNGE OA Rate [cfm] | US_SH_SAC_FRONTLOUNGE OA Rate [cfm] | 500.204 | 500.204 | 316.664 | 105.8415 | 20 | 322.1318 | 343.6026 | 105.8415 | 20 | 408.9244 | 500.204 | 500.204 | 316.664 | 105.8415 | 20 | 322.1318 | 343.6026 | 105.8415 | 20 | 408.9244 | 500.204 | 500.204 | 316.664 | 105.8415 | 20 | 322.1318 | 343.6026 | 105.8415 | 20 | 408.9244 | 500.204 | 500.204 | 316.664 | 105.8415 | 20 | 322.1318 | 343.6026 | 105.8415 | 20 | 408.9244 | 500.204 | 500.204 | 316.664 | 105.8415 | 20 | 322.1318 | 343.6026 | 105.8415 | 20 | 408.9244
|  | Outdoor_Air_Dampers_Motorized | item cost |  | CAVDX | SAC_FrontLounge OA Rate [cfm] | US_SH_SAC_FrontLounge OA Rate [cfm] | 500.204 | 500.204 | 738.3131 | 105.8415 | 20 | 727.2444 | 836.6458 | 105.8415 | 20 | 974.5098 | 500.204 | 500.204 | 738.3131 | 105.8415 | 20 | 727.2444 | 836.6458 | 105.8415 | 20 | 974.5098 | 500.204 | 500.204 | 738.3131 | 105.8415 | 20 | 727.2444 | 836.6458 | 105.8415 | 20 | 974.5098 | 500.204 | 500.204 | 738.3131 | 105.8415 | 20 | 727.2444 | 836.6458 | 105.8415 | 20 | 974.5098 | 500.204 | 500.204 | 738.3131 | 105.8415 | 20 | 727.2444 | 836.6458 | 105.8415 | 20 | 974.5098
| 90.1-16g occ standby controls | occ_standby | 54 conditioned zones |  |  |  |  | 0 | 54 | 0 | 0 | 0 | 0 | 1800.3379 | 0 | 810 | 3159.3806 | 0 | 54 | 0 | 0 | 0 | 0 | 1800.3379 | 0 | 810 | 3159.3806 | 0 | 54 | 0 | 0 | 0 | 0 | 1800.3379 | 0 | 810 | 3159.3806 | 0 | 54 | 0 | 0 | 0 | 0 | 1800.3379 | 0 | 810 | 3159.3806 | 0 | 54 | 0 | 0 | 0 | 0 | 1800.3379 | 0 | 810 | 3159.3806
x | 90.1-19 b - DCV |  | DCV modeled in more spaces, climates; exceptions removed; manual calc pasted here |  |  | Count of zones where DCV is newly required | 365 | 0 | 4 | 0 | 0 | 15 | 0 | 1460 | 0 | 15 | 1460 | 0 | 4 | 0 | 0 | 15 | 0 | 1460 | 0 | 15 | 1460 | 0 | 4 | 0 | 0 | 15 | 0 | 1460 | 0 | 15 | 1460 | 0 | 4 | 0 | 0 | 15 | 0 | 1460 | 0 | 15 | 1460 | 0 | 4 | 0 | 0 | 15 | 0 | 1460 | 0 | 15 | 1460 |  | 1460 | 1460 | 1460 | 1460 | 1460
x | 90.1-19 ci - lowers economizer threshold | DX_Economizer | 2.75 to 5.5 tons is the new range; only the first 3 CZs qualify in that range | SAC_MEETINGROOM | CAVDX | SAC_MeetingRoom OA Rate [cfm] | US_SH_SAC_MeetingRoom OA Rate [cfm] | 0 | 267.8688 | 0 | 0 | 15 | 0 | 1570.6412 | 134.8431 | 15 | 1768.7122 | 0 | 267.8688 | 0 | 0 | 15 | 0 | 1570.6412 | 134.8431 | 15 | 1768.7122 | 0 | 267.8688 | 0 | 0 | 15 | 0 | 1570.6412 | 134.8431 | 15 | 1768.7122 | [21 empty] | 1570.6412 | 1570.6412 | 1570.6412 | 0 | 0
| Differences in economizer size and requirements based on load changes | DX_Economizer | cost applied if any value other than "No" 1ookup cost based on outside air cfm
x |  | DX_Economizer |  | SAC_MEETINGROOM | CAVDX | SAC_MeetingRoom (economizer) | US_SH_SAC_MeetingRoom (economizer) | No | DifferentialEnthalpy | 0 | 0 | 0 | 0 | 2331.3178 | 134.8431 | 15 | 2615.9011 | No | DifferentialEnthalpy | 0 | 0 | 0 | 0 | 2363.3454 | 134.8431 | 15 | 2651.4569 | No | DifferentialDryBulb | 0 | 0 | 0 | 0 | 2523.4832 | 134.8431 | 15 | 2829.2355 | No | No | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | No | No | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | DX_Economizer |  |  | CAVDX | SAC_MR_ADDAQ SUPPLY FAN Supply Flow Rate [cfm] | US_SH_SAC_MR_ADDAQ SUPPLY FAN Supply Flow Rate [cfm] | 868.7408 | 826.3632 | 2395.3729 | 134.8431 | 15 | 2687.0126 | 2331.3178 | 134.8431 | 15 | 2615.9011 | 868.7408 | 847.552 | 2395.3729 | 134.8431 | 15 | 2687.0126 | 2363.3454 | 134.8431 | 15 | 2651.4569 | 995.8736 | 953.496 | 2587.5383 | 134.8431 | 15 | 2900.347 | 2523.4832 | 134.8431 | 15 | 2829.2355 | 847.552 | 805.1744 | 2363.3454 | 134.8431 | 15 | 2651.4569 | 2299.2902 | 134.8431 | 15 | 2580.3454 | 847.552 | 805.1744 | 2363.3454 | 134.8431 | 15 | 2651.4569 | 2299.2902 | 134.8431 | 15 | 2580.3454
x |  | DX_Economizer |  | SAC_FRONTLOUNGE | CAVDX | SAC_FrontLounge (economizer) | US_SH_SAC_FrontLounge (economizer) | DifferentialEnthalpy | DifferentialEnthalpy | 3358.145 | 146.6128 | 15 | 3757.6869 | 3303.2928 | 145.7682 | 15 | 3696.66 | DifferentialEnthalpy | DifferentialEnthalpy | 3376.429 | 146.8943 | 15 | 3778.0292 | 3321.5769 | 146.0497 | 15 | 3717.0023 | DifferentialDryBulb | DifferentialDryBulb | 3572.3113 | 150.5543 | 15 | 3996.3322 | 3518.5981 | 149.4281 | 15 | 3936.4005 | DifferentialEnthalpy | DifferentialEnthalpy | 3303.2928 | 145.7682 | 15 | 3696.66 | 3230.1566 | 144.642 | 15 | 3615.2907 | DifferentialDryBulb | DifferentialDryBulb | 3303.2928 | 145.7682 | 15 | 3696.66 | 3230.1566 | 144.642 | 15 | 3615.2907
|  | DX_Economizer |  |  | CAVDX | SAC_FL_ADDAQ SUPPLY FAN Supply Flow Rate [cfm] | US_SH_SAC_FL_ADDAQ SUPPLY FAN Supply Flow Rate [cfm] | 1885.8032 | 1822.2368 | 3358.145 | 146.6128 | 15 | 3757.6869 | 3303.2928 | 145.7682 | 15 | 3696.66 | 1906.992 | 1843.4256 | 3376.429 | 146.8943 | 15 | 3778.0292 | 3321.5769 | 146.0497 | 15 | 3717.0023 | 2182.4464 | 2097.6912 | 3572.3113 | 150.5543 | 15 | 3996.3322 | 3518.5981 | 149.4281 | 15 | 3936.4005 | 1822.2368 | 1737.4816 | 3303.2928 | 145.7682 | 15 | 3696.66 | 3230.1566 | 144.642 | 15 | 3615.2907 | 1822.2368 | 1737.4816 | 3303.2928 | 145.7682 | 15 | 3696.66 | 3230.1566 | 144.642 | 15 | 3615.2907
x |  | DX_Economizer |  | SAC_FRONTOFFICE | CAVDX | SAC_FrontOffice (economizer) | US_SH_SAC_FrontOffice (economizer) | No | No | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | No | No | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | No | No | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | No | No | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | No | No | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | DX_Economizer |  |  | CAVDX | SAC_FO_ADDAQ SUPPLY FAN Supply Flow Rate [cfm] | US_SH_SAC_FO_ADDAQ SUPPLY FAN Supply Flow Rate [cfm] | 805.1744 | 762.7968 | 2299.2902 | 134.8431 | 15 | 2580.3454 | 2235.2351 | 134.8431 | 15 | 2509.2339 | 783.9856 | 741.608 | 2267.2627 | 134.8431 | 15 | 2544.7896 | 2203.2075 | 134.8431 | 15 | 2473.6782 | 911.1184 | 847.552 | 2459.4281 | 134.8431 | 15 | 2758.1241 | 2363.3454 | 134.8431 | 15 | 2651.4569 | 783.9856 | 699.2304 | 2267.2627 | 134.8431 | 15 | 2544.7896 | 2139.1524 | 134.8431 | 15 | 2402.5667 | 762.7968 | 699.2304 | 2235.2351 | 134.8431 | 15 | 2509.2339 | 2139.1524 | 134.8431 | 15 | 2402.5667
x |  | DX_Economizer |  | SAC_EXC_EMPLGE_RESTRM | CAVDX | SAC_Exc_EmpLge_RestRm (economizer) | US_SH_SAC_Exc_EmpLge_RestRm (economizer) | DifferentialEnthalpy | DifferentialEnthalpy | 3518.5981 | 149.4281 | 15 | 3936.4005 | 3464.8848 | 148.302 | 15 | 3876.4688 | DifferentialEnthalpy | DifferentialEnthalpy | 3532.0264 | 149.7097 | 15 | 3951.3834 | 3491.7414 | 148.8651 | 15 | 3906.4347 | DifferentialDryBulb | DifferentialDryBulb | 3720.0228 | 153.6512 | 15 | 4161.1444 | 3652.8812 | 152.2435 | 15 | 4086.2298 | DifferentialEnthalpy | DifferentialEnthalpy | 3518.5981 | 149.4281 | 15 | 3936.4005 | 3478.3131 | 148.5835 | 15 | 3891.4518 | DifferentialDryBulb | DifferentialDryBulb | 3545.4547 | 149.9912 | 15 | 3966.3664 | 3478.3131 | 148.5835 | 15 | 3891.4518
|  | DX_Economizer |  |  | CAVDX | SAC_EXC_ADDAQ SUPPLY FAN Supply Flow Rate [cfm] | US_SH_SAC_EXC_ADDAQ SUPPLY FAN Supply Flow Rate [cfm] | 2097.6912 | 2012.936 | 3518.5981 | 149.4281 | 15 | 3936.4005 | 3464.8848 | 148.302 | 15 | 3876.4688 | 2118.88 | 2055.3136 | 3532.0264 | 149.7097 | 15 | 3951.3834 | 3491.7414 | 148.8651 | 15 | 3906.4347 | 2415.5232 | 2309.5792 | 3720.0228 | 153.6512 | 15 | 4161.1444 | 3652.8812 | 152.2435 | 15 | 4086.2298 | 2097.6912 | 2034.1248 | 3518.5981 | 149.4281 | 15 | 3936.4005 | 3478.3131 | 148.5835 | 15 | 3891.4518 | 2140.0688 | 2034.1248 | 3545.4547 | 149.9912 | 15 | 3966.3664 | 3478.3131 | 148.5835 | 15 | 3891.4518
No diff for 2010-13 so HIDE | 90.1-07aj | Motor_Efficiency | lookup cost based on the next motor size hp greater than 1.1 times the supply fan motor hp
Not in 2013 |  | Motor_Efficiency |  | SAC_FRONTLOUNGE | CAVDX | SAC_FRONTLOUNGE Fan Power [hp] | US_SH_SAC_FRONTLOUNGE Fan Power [hp] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
Not in 2013 |  | Motor_Efficiency |  | SAC_EXC_EMPLGE_RESTRM | CAVDX | SAC_EXC_EMPLGE_RESTRM Fan Power [hp] | US_SH_SAC_EXC_EMPLGE_RESTRM Fan Power [hp] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
[10 empty] | 149519.8358 |  |  | 230636.311 | 151937.3859 |  |  | 231941.5829 |  |  | 149589.7986 |  |  | 230784.9002 | 152431.6564 |  |  | 232770.8208 |  |  | 157794.0211 |  |  | 244096.9338 | 159684.0012 |  |  | 244468.7803 |  |  | 147531.2833 |  |  | 227747.6436 | 145430.3647 |  |  | 223704.2644 |  |  | 147037.9887 |  |  | 227175.5913 | 144983.809 |  |  | 223118.7342
[9 empty] | 230636.311 |  |  |  | 231941.5829 | [5 empty] | 230784.9002 |  |  |  | 232770.8208 | [5 empty] | 244096.9338 |  |  |  | 244468.7803 | [5 empty] | 227747.6436 |  |  |  | 223704.2644 | [5 empty] | 227175.5913 |  |  |  | 223118.7342

## HVAC Mid-rise Apartment Proto
90.1 Cost Effectiveness - Cost Estimate - HVAC - Mid-rise Apartment |  |  |  | Split system Inflation adjustment to 2023$ (Mat/Labor): | 1.042 | 1.321 |  | Mid-rise Apartment |  | Note: For mid-rise apartment, material, labor and project cost adjustments made on tis sheet for total new construction rather than on HVAC Comp sheet.
[10 empty] | $AP | $AQ | $AR | $BA | $BK | $BL | $BM | $BW |  |  | $AP | $AQ | $AR | $BA | $BK | $BL | $BM | $BW |  |  | $AP | $AQ | $AR | $BA | $BK | $BL | $BM | $BW |  |  | $AP | $AQ | $AR | $BA | $BK | $BL | $BM | $BW |  |  | $AP | $AQ | $AR | $BA | $BK | $BL | $BM | $BW | Find Row
|  |  | YES |  |  |  |  | 3 | 4 | [8 empty] | 5 | 6 | [8 empty] | 7 | 8 | [8 empty] | 9 | 10 | [8 empty] | 11 | 12
This is all new, now have lookup for mid-rise apartment cooling capacity change | [6 empty] | City-year parameter column |  |  | I | I | I | I | J | J | J | J |  |  | S | S | S | S | T | T | T | T |  |  | AC | AC | AC | AC | AD | AD | AD | AD |  |  | AM | AM | AM | AM | AN | AN | AN | AN |  |  | AW | AW | AW | AW | AX | AX | AX | AX
[7 empty] | Parameter range lookup extension |  |  | _2007Par | _2007Par | _2007Par | _2007Par | _2010Par | _2010Par | _2010Par | _2010Par |  |  | _2007Par | _2007Par | _2007Par | _2007Par | _2010Par | _2010Par | _2010Par | _2010Par |  |  | _2007Par | _2007Par | _2007Par | _2007Par | _2010Par | _2010Par | _2010Par | _2010Par |  |  | _2007Par | _2007Par | _2007Par | _2007Par | _2010Par | _2010Par | _2010Par | _2010Par |  |  | _2007Par | _2007Par | _2007Par | _2007Par | _2010Par | _2010Par | _2010Par | _2010Par
All "SPLIT MXX" named cooling capacities are divided by 2 and resulting costs multiplied by 2. These zones include 2 apartments | [6 empty] | Cost range lookup extension |  |  | _2007Costs | _2007Costs | _2007Costs | _2007Costs | _2010Costs | _2010Costs | _2010Costs | _2010Costs |  |  | _2007Costs | _2007Costs | _2007Costs | _2007Costs | _2010Costs | _2010Costs | _2010Costs | _2010Costs |  |  | _2007Costs | _2007Costs | _2007Costs | _2007Costs | _2010Costs | _2010Costs | _2010Costs | _2010Costs |  |  | _2007Costs | _2007Costs | _2007Costs | _2007Costs | _2010Costs | _2010Costs | _2010Costs | _2010Costs |  |  | _2007Costs | _2007Costs | _2007Costs | _2007Costs | _2010Costs | _2010Costs | _2010Costs | _2010Costs
[7 empty] | Cost range column index values |  |  | 9 | 10 | 11 | 20 | 10 | 11 | 12 | 22 |  |  | 9 | 10 | 11 | 20 | 10 | 11 | 12 | 22 |  |  | 9 | 10 | 11 | 20 | 10 | 11 | 12 | 22 |  |  | 9 | 10 | 11 | 20 | 10 | 11 | 12 | 22 |  |  | 9 | 10 | 11 | 20 | 10 | 11 | 12 | 22 | Unit
[8 empty] | Climate Zone 1 | 2A | Base Code | 2019 |  |  | Target Code | 2022 |  |  | Climate Zone 2 | 3A | Base Code | 2019 |  |  | Target Code | 2022 |  |  | Climate Zone 3 | 3B | Base Code | 2019 |  |  | Target Code | 2022 |  |  | Climate Zone 4 | 4A | Base Code | 2019 |  |  | Target Code | 2022 |  |  | Climate Zone 5 | 5A | Base Code | 2019 |  |  | Target Code | 2022 |  |  | Mult | First cost difference |  | 2019 | vs | 2022
Costs row marked x, other rows not marked | [7 empty] | 2019 | 2022 | [8 empty] | 2019 | 2022 | [8 empty] | 2019 | 2022 | [8 empty] | 2019 | 2022 | [8 empty] | 2019 | 2022 | [9 empty] | Total new construction (added cost)
| Addendum or general | Key Word | Description | Model | Type | Parameters | Lookup Value in HVAC Data, Current_HVAC_Data | Prototype | Prototype | Total New | Maintenance | Replacement Life | Total | Total New | Maintenance | Replacement Life | Total | Prototype | Prototype | Total New | Maintenance | Replacement Life | Total | Total New | Maintenance | Replacement Life | Total | Prototype | Prototype | Total New | Maintenance | Replacement Life | Total | Total New | Maintenance | Replacement Life | Total | Prototype | Prototype | Total New | Maintenance | Replacement Life | Total | Total New | Maintenance | Replacement Life | Total | Prototype | Prototype | Total New | Maintenance | Replacement Life | Total | Total New | Maintenance | Replacement Life | Total |  | 2A | 3A | 3B | 4A | 5A
| load change |  |  | Object |  |  |  | Data | Data | Construction |  |  | Replacement Cost | Construction |  |  | Replacement Cost | Data | Data | Construction |  |  | Replacement Cost | Construction |  |  | Replacement Cost | Data | Data | Construction |  |  | Replacement Cost | Construction |  |  | Replacement Cost | Data | Data | Construction |  |  | Replacement Cost | Construction |  |  | Replacement Cost | Data | Data | Construction |  |  | Replacement Cost | Construction |  |  | Replacement Cost
0 |  | Door_Switch_Control | Increase in controls cost to accommodate door switch through addenda 90.1-10ba |  |  | Door count: Basis: 11.6% of apartments have exterior sliding doors which translates to (4) doors for the prototype analyzed | US_SH_Door count: Basis: 11.6% of apartments have exterior sliding doors which translates to (4) doors for the prototype analyzed | 4 | 4 | 2028.7211 | 0 | 15 | 2656.9501 | 3049.3643 | 0 | 15 | 3410.2484 | 4 | 4 | 2028.7211 | 0 | 15 | 2656.9501 | 3049.3643 | 0 | 15 | 3410.2484 | 4 | 4 | 2028.7211 | 0 | 15 | 2656.9501 | 3049.3643 | 0 | 15 | 3410.2484 | 4 | 4 | 2028.7211 | 0 | 15 | 2656.9501 | 3049.3643 | 0 | 15 | 3410.2484 | 4 | 4 | 2028.7211 | 0 | 15 | 2656.9501 | 3049.3643 | 0 | 15 | 3410.2484 | 511
| HVAC System - General load change |  | curve fits for labor and material | [54 empty] | unit count
x |  | Split-System_W_Furnace |  | SPLIT GN1 COOLING COIL | Split System | SPLIT GN1 COOLING COIL Cooling Capacity [ton] | US_MA_SPLIT GN1 COOLING COIL Cooling Capacity [ton] | 0.91377 | 0.83301 | 8673.3247 | 0 | 15 | 12866.3965 | 7936.3839 | 0 | 15 | 11769.0077 | 0.85287 | 0.76943 | 8118.0921 | 0 | 15 | 12039.5205 | 7352.5582 | 0 | 15 | 10900.1712 | 0.85571 | 0.75622 | 8144.1059 | 0 | 15 | 12078.2515 | 7230.7976 | 0 | 15 | 10719.0308 | 0.81034 | 0.71356 | 7728.6581 | 0 | 15 | 11459.8191 | 6836.741 | 0 | 15 | 10132.947 | 0.71209 | 0.61994 | 6823.159 | 0 | 15 | 10112.7503 | 5966.378 | 0 | 15 | 8839.2341 | 1 | -736.9408 | -765.5339 | -913.3083 | -891.917 | -856.781
x |  | Split-System_W_Furnace |  | SPLIT GN2 COOLING COIL | Split System | SPLIT GN2 COOLING COIL Cooling Capacity [ton] | US_MA_SPLIT GN2 COOLING COIL Cooling Capacity [ton] | 0.91186 | 0.83112 | 8655.925 | 0 | 15 | 12840.4775 | 7919.1199 | 0 | 15 | 11743.3088 | 0.85112 | 0.76771 | 8102.0803 | 0 | 15 | 12015.6815 | 7336.7143 | 0 | 15 | 10876.5993 | 0.85369 | 0.75423 | 8125.5772 | 0 | 15 | 12050.6648 | 7212.5222 | 0 | 15 | 10691.8448 | 0.80808 | 0.71143 | 7707.9145 | 0 | 15 | 11428.9468 | 6817.0255 | 0 | 15 | 10103.6297 | 0.70963 | 0.61761 | 6800.334 | 0 | 15 | 10078.8097 | 5944.6585 | 0 | 15 | 8806.9641 | 1 | -736.8051 | -765.366 | -913.055 | -890.889 | -855.6755
x |  | Split-System_W_Furnace |  | SPLIT GNE COOLING COIL | Split System | SPLIT GNE COOLING COIL Cooling Capacity [ton] | US_MA_SPLIT GNE COOLING COIL Cooling Capacity [ton] | 1.0817 | 1.0013 | 10189.4462 | 0 | 15 | 15126.4768 | 9466.5119 | 0 | 15 | 14048.3982 | 0.99228 | 0.90981 | 9384.636 | 0 | 15 | 13926.3465 | 8637.281 | 0 | 15 | 12812.7055 | 1.0134 | 0.91521 | 9574.9059 | 0 | 15 | 14209.9948 | 8686.4049 | 0 | 15 | 12885.8814 | 0.95085 | 0.83768 | 9009.8619 | 0 | 15 | 13367.7937 | 7979.1799 | 0 | 15 | 11832.7148 | 0.83948 | 0.73416 | 7995.6792 | 0 | 15 | 11857.2767 | 7027.2754 | 0 | 15 | 10416.3028 | 1 | -722.9343 | -747.355 | -888.501 | -1030.6819 | -968.4039
x |  | Split-System_W_Furnace |  | SPLIT GNW COOLING COIL | Split System | SPLIT GNW COOLING COIL Cooling Capacity [ton] | US_MA_SPLIT GNW COOLING COIL Cooling Capacity [ton] | 1.1779 | 1.0973 | 11047.3562 | 0 | 15 | 16406.7796 | 10328.5897 | 0 | 15 | 15334.0587 | 1.0883 | 1.006 | 10248.37 | 0 | 15 | 15214.3793 | 9508.657 | 0 | 15 | 14111.2272 | 1.1333 | 1.0335 | 10650.037 | 0 | 15 | 15813.7136 | 9756.1856 | 0 | 15 | 14480.2877 | 1.0541 | 0.93561 | 9941.804 | 0 | 15 | 14757.0975 | 8871.6258 | 0 | 15 | 13161.8205 | 0.94349 | 0.83088 | 8943.1777 | 0 | 15 | 13268.4301 | 7916.9584 | 0 | 15 | 11740.0913 | 1 | -718.7665 | -739.713 | -893.8514 | -1070.1782 | -1026.2192
x |  | Split-System_W_Furnace |  | SPLIT GS1 COOLING COIL | Split System | SPLIT GS1 COOLING COIL Cooling Capacity [ton] | US_MA_SPLIT GS1 COOLING COIL Cooling Capacity [ton] | 1.0294 | 0.94574 | 9719.6679 | 0 | 15 | 14425.8351 | 8963.52 | 0 | 15 | 13298.7407 | 0.91441 | 0.83106 | 8679.1154 | 0 | 15 | 12875.0225 | 7918.599 | 0 | 15 | 11742.5335 | 0.89268 | 0.79288 | 8481.3524 | 0 | 15 | 12580.454 | 7568.2618 | 0 | 15 | 11221.1201 | 0.94956 | 0.83932 | 8998.1623 | 0 | 15 | 13350.3602 | 7994.222 | 0 | 15 | 11855.1074 | 0.87716 | 0.7702 | 8339.9208 | 0 | 15 | 12369.825 | 7359.6545 | 0 | 15 | 10910.7287 | 1 | -756.1479 | -760.5163 | -913.0906 | -1003.9403 | -980.2664
x |  | Split-System_W_Furnace |  | SPLIT GS2 COOLING COIL | Split System | SPLIT GS2 COOLING COIL Cooling Capacity [ton] | US_MA_SPLIT GS2 COOLING COIL Cooling Capacity [ton] | 1.0312 | 0.94992 | 9735.7403 | 0 | 15 | 14449.8009 | 9001.4095 | 0 | 15 | 13355.1988 | 0.91304 | 0.83214 | 8666.603 | 0 | 15 | 12856.3837 | 7928.4423 | 0 | 15 | 11757.1859 | 0.89089 | 0.79399 | 8465.0343 | 0 | 15 | 12556.1505 | 7578.4785 | 0 | 15 | 11236.3233 | 0.95013 | 0.84312 | 9003.3165 | 0 | 15 | 13358.0404 | 8028.956 | 0 | 15 | 11906.8159 | 0.87873 | 0.77408 | 8354.2101 | 0 | 15 | 12391.1043 | 7395.39 | 0 | 15 | 10963.896 | 1 | -734.3308 | -738.1607 | -886.5558 | -974.3604 | -958.8202
x |  | Split-System_W_Furnace |  | SPLIT GSW COOLING COIL | Split System | SPLIT GSW COOLING COIL Cooling Capacity [ton] | US_MA_SPLIT GSW COOLING COIL Cooling Capacity [ton] | 1.2618 | 1.1808 | 11791.5114 | 0 | 15 | 17518.1393 | 11073.5936 | 0 | 15 | 16445.951 | 1.1494 | 1.0663 | 10793.831 | 0 | 15 | 16028.3253 | 10051.2692 | 0 | 15 | 14920.3636 | 1.1782 | 1.0779 | 11050.4403 | 0 | 15 | 16411.384 | 10154.5555 | 0 | 15 | 15074.4292 | 1.1439 | 1.0167 | 10744.7379 | 0 | 15 | 15955.051 | 9604.5814 | 0 | 15 | 14254.2385 | 1.0469 | 0.9264 | 9877.0624 | 0 | 15 | 14660.5438 | 8788.0952 | 0 | 15 | 13037.3718 | 1 | -717.9178 | -742.5617 | -895.8848 | -1140.1565 | -1088.9672
x |  | Split-System_W_Furnace |  | SPLIT MN1 COOLING COIL | Split System | SPLIT MN1 COOLING COIL Cooling Capacity [ton] | US_MA_SPLIT MN1 COOLING COIL Cooling Capacity [ton] | 0.92649 | 0.84529 | 17577.7913 | 0 | 15 | 26077.1289 | 16097.553 | 0 | 15 | 23872.6468 | 0.91611 | 0.83341 | 17389.1455 | 0 | 15 | 25796.0973 | 15880.2143 | 0 | 15 | 23549.1001 | 0.91315 | 0.81496 | 17335.2485 | 0 | 15 | 25715.8098 | 15542.0908 | 0 | 15 | 23045.8108 | 0.9048 | 0.80666 | 17183.3826 | 0 | 15 | 25489.5946 | 15389.7581 | 0 | 15 | 22819.0935 | 0.81981 | 0.72648 | 15630.8709 | 0 | 15 | 23177.9502 | 13912.4833 | 0 | 15 | 20621.3159 | 2 | -1480.2383 | -1508.9312 | -1793.1577 | -1793.6245 | -1718.3876
x |  | Split-System_W_Furnace | All "SPLIT MXX" named cooling | SPLIT MN2 COOLING COIL | Split System | SPLIT MN2 COOLING COIL Cooling Capacity [ton] | US_MA_SPLIT MN2 COOLING COIL Cooling Capacity [ton] | 0.92419 | 0.84302 | 17535.9537 | 0 | 15 | 26014.7999 | 16056.0131 | 0 | 15 | 23810.8048 | 0.9139 | 0.83123 | 17348.9502 | 0 | 15 | 25736.2204 | 15840.297 | 0 | 15 | 23489.6799 | 0.91065 | 0.81252 | 17289.7676 | 0 | 15 | 25648.0611 | 15497.1776 | 0 | 15 | 22978.9647 | 0.90178 | 0.80378 | 17128.5263 | 0 | 15 | 25407.8861 | 15336.8495 | 0 | 15 | 22740.3533 | 0.81642 | 0.72325 | 15568.8462 | 0 | 15 | 23085.6327 | 13852.72 | 0 | 15 | 20532.4373 | 2 | -1479.9406 | -1508.6532 | -1792.59 | -1791.6768 | -1716.1262
x |  | Split-System_W_Furnace | capacities are divided by 2 and | SPLIT MNE COOLING COIL | Split System | SPLIT MNE COOLING COIL Cooling Capacity [ton] | US_MA_SPLIT MNE COOLING COIL Cooling Capacity [ton] | 1.1255 | 1.0441 | 21162.4074 | 0 | 15 | 31421.9808 | 19703.5158 | 0 | 15 | 29245.6144 | 1.108 | 1.0257 | 20849.3346 | 0 | 15 | 30954.8162 | 19372.1894 | 0 | 15 | 28751.5497 | 1.109 | 1.0117 | 20867.7169 | 0 | 15 | 30982.2442 | 19119.9507 | 0 | 15 | 28375.4698 | 1.1142 | 1.0011 | 20960.4944 | 0 | 15 | 31120.6801 | 18928.2516 | 0 | 15 | 28089.6823 | 1.0244 | 0.91489 | 19348.3516 | 0 | 15 | 28716.0063 | 17366.8904 | 0 | 15 | 25762.9449 | 2 | -1458.8915 | -1477.1452 | -1747.7663 | -2032.2428 | -1981.4611
x |  | Split-System_W_Furnace | resulting costs multiplied by 2. | SPLIT MNW COOLING COIL | Split System | SPLIT MNW COOLING COIL Cooling Capacity [ton] | US_MA_SPLIT MNW COOLING COIL Cooling Capacity [ton] | 1.245 | 1.1633 | 23285.4575 | 0 | 15 | 34591.7583 | 21835.3116 | 0 | 15 | 32426.312 | 1.2358 | 1.1532 | 23122.3964 | 0 | 15 | 34348.1939 | 21655.5602 | 0 | 15 | 32157.9966 | 1.2757 | 1.1762 | 23827.6244 | 0 | 15 | 35401.7234 | 22065.2086 | 0 | 15 | 32769.5122 | 1.2554 | 1.1313 | 23468.8733 | 0 | 15 | 34865.7483 | 21265.5387 | 0 | 15 | 31575.8874 | 1.176 | 1.0584 | 22062.5033 | 0 | 15 | 32765.4733 | 19960.9079 | 0 | 15 | 29629.4829 | 2 | -1450.1459 | -1466.8363 | -1762.4158 | -2203.3346 | -2101.5954
x |  | Split-System_W_Furnace | These zones include 2 apts. | SPLIT MS1 COOLING COIL | Split System | SPLIT MS1 COOLING COIL Cooling Capacity [ton] | US_MA_SPLIT MS1 COOLING COIL Cooling Capacity [ton] | 1.0588 | 0.97494 | 19966.5248 | 0 | 15 | 29637.8605 | 18455.9401 | 0 | 15 | 27385.6641 | 0.98379 | 0.90153 | 18615.825 | 0 | 15 | 27623.9678 | 17123.8681 | 0 | 15 | 25400.9477 | 0.96738 | 0.87741 | 18319.1958 | 0 | 15 | 27181.8649 | 16684.3284 | 0 | 15 | 24746.3315 | 1.0743 | 0.96192 | 20245.0949 | 0 | 15 | 30053.3665 | 18220.1832 | 0 | 15 | 27034.3079 | 1.0225 | 0.9137 | 19313.8575 | 0 | 15 | 28664.5747 | 17345.2276 | 0 | 15 | 25730.675 | 2 | -1510.5847 | -1491.9569 | -1634.8674 | -2024.9117 | -1968.6299
x |  | Split-System_W_Furnace |  | SPLIT MS2 COOLING COIL | Split System | SPLIT MS2 COOLING COIL Cooling Capacity [ton] | US_MA_SPLIT MS2 COOLING COIL Cooling Capacity [ton] | 1.0602 | 0.97639 | 19992.9993 | 0 | 15 | 29677.3466 | 18482.1933 | 0 | 15 | 27424.7924 | 1.0192 | 0.93428 | 19254.2542 | 0 | 15 | 28575.7065 | 17719.2023 | 0 | 15 | 26287.8096 | 0.96833 | 0.87838 | 18336.3838 | 0 | 15 | 27207.4806 | 16702.0929 | 0 | 15 | 24772.7859 | 1.0763 | 0.96395 | 20281.656 | 0 | 15 | 30107.9039 | 18256.9934 | 0 | 15 | 27089.1648 | 1.0248 | 0.91594 | 19354.9322 | 0 | 15 | 28725.8184 | 17385.9922 | 0 | 15 | 25791.4 | 2 | -1510.8061 | -1535.0519 | -1634.2909 | -2024.6625 | -1968.94
x |  | Split-System_W_Furnace | see unit mult in col BH | SPLIT MSE COOLING COIL | Split System | SPLIT MSE COOLING COIL Cooling Capacity [ton] | US_MA_SPLIT MSE COOLING COIL Cooling Capacity [ton] | 1.2667 | 1.1837 | 23668.0505 | 0 | 15 | 35163.3087 | 22198.2091 | 0 | 15 | 32968.0776 | 1.2319 | 1.1476 | 23053.3175 | 0 | 15 | 34245.0161 | 21555.9096 | 0 | 15 | 32009.2577 | 1.202 | 1.1038 | 22524.0228 | 0 | 15 | 33454.5581 | 20773.3224 | 0 | 15 | 30841.4016 | 1.308 | 1.1798 | 24396.7405 | 0 | 15 | 36252.1632 | 22129.5959 | 0 | 15 | 32865.6387 | 1.2387 | 1.1151 | 23173.6191 | 0 | 15 | 34424.7033 | 20976.2245 | 0 | 15 | 31144.152 | 2 | -1469.8413 | -1497.4078 | -1750.7004 | -2267.1446 | -2197.3946
x |  | Split-System_W_Furnace |  | SPLIT MSW COOLING COIL | Split System | SPLIT MSW COOLING COIL Cooling Capacity [ton] | US_MA_SPLIT MSW COOLING COIL Cooling Capacity [ton] | 1.3457 | 1.2635 | 25058.6662 | 0 | 15 | 37241.5646 | 23612.2226 | 0 | 15 | 35079.9021 | 1.3031 | 1.2202 | 24311.0403 | 0 | 15 | 36124.0859 | 22846.9579 | 0 | 15 | 33936.8123 | 1.3337 | 1.2338 | 24848.6193 | 0 | 15 | 36927.5689 | 23087.9226 | 0 | 15 | 34296.7026 | 1.3693 | 1.2368 | 25472.9953 | 0 | 15 | 37861.025 | 23139.8326 | 0 | 15 | 34374.2374 | 1.2908 | 1.1637 | 24093.1258 | 0 | 15 | 35798.4394 | 21842.9552 | 0 | 15 | 32437.722 | 2 | -1446.4436 | -1464.0824 | -1760.6967 | -2333.1627 | -2250.1706
x |  | Split-System_W_Furnace |  | SPLIT OFFICE COOLING C | Split System | SPLIT OFFICE COOLING COIL Cooling Capacity [ton] | US_MA_SPLIT OFFICE COOLING COIL Cooling Capacity [ton] | 1.3948 | 1.3643 | 12959.4741 | 0 | 15 | 19263.9469 | 12692.1586 | 0 | 15 | 18864.2166 | 1.2558 | 1.224 | 11738.343 | 0 | 15 | 17438.7098 | 11456.4013 | 0 | 15 | 17017.575 | 1.2237 | 1.1898 | 11454.4871 | 0 | 15 | 17014.7162 | 11153.3287 | 0 | 15 | 16564.9981 | 1.2373 | 1.1657 | 11574.6084 | 0 | 15 | 17194.1272 | 10939.6102 | 0 | 15 | 16245.929 | 1.1334 | 1.0658 | 10651.534 | 0 | 15 | 15815.9477 | 10046.3702 | 0 | 15 | 14913.0564 | 1 | -267.3155 | -281.9418 | -301.1585 | -634.9983 | -605.1638
x |  | Split-System_W_Furnace | curve fits for labor and material | SPLIT TN1 COOLING COIL | Split System | SPLIT TN1 COOLING COIL Cooling Capacity [ton] | US_MA_SPLIT TN1 COOLING COIL Cooling Capacity [ton] | 1.1335 | 1.0528 | 10651.9653 | 0 | 15 | 15816.5915 | 9929.4157 | 0 | 15 | 14738.6215 | 1.1111 | 1.0317 | 10452.0224 | 0 | 15 | 15518.2246 | 9739.758 | 0 | 15 | 14455.7919 | 1.1477 | 1.0521 | 10778.7024 | 0 | 15 | 16005.7447 | 9923.0805 | 0 | 15 | 14729.1732 | 1.1102 | 1.0035 | 10443.9894 | 0 | 15 | 15506.2386 | 9485.4959 | 0 | 15 | 14076.6989 | 0.9877 | 0.90916 | 9343.2631 | 0 | 15 | 13864.6758 | 8631.3587 | 0 | 15 | 12803.8838 | 1 | -722.5496 | -712.2644 | -855.6219 | -958.4935 | -711.9044
x |  | Split-System_W_Furnace | Material (2012 estimate) | SPLIT TN2 COOLING COIL | Split System | SPLIT TN2 COOLING COIL Cooling Capacity [ton] | US_MA_SPLIT TN2 COOLING COIL Cooling Capacity [ton] | 1.1351 | 1.0543 | 10666.3506 | 0 | 15 | 15838.0601 | 9943.3876 | 0 | 15 | 14759.4592 | 1.1061 | 1.0268 | 10407.7067 | 0 | 15 | 15452.1017 | 9695.5034 | 0 | 15 | 14389.8039 | 1.1446 | 1.048 | 10751.5824 | 0 | 15 | 15965.2665 | 9886.4669 | 0 | 15 | 14674.5691 | 1.1119 | 1.004 | 10459.3938 | 0 | 15 | 15529.2238 | 9490.7288 | 0 | 15 | 14084.5 | 1.0121 | 0.91055 | 9563.7306 | 0 | 15 | 14193.3336 | 8644.0046 | 0 | 15 | 12822.7209 | 1 | -722.963 | -712.2033 | -865.1154 | -968.665 | -919.726
x |  | Split-System_W_Furnace | y = 17.693x2 - 208.45x + 2690.6 | SPLIT TNE COOLING COIL | Split System | SPLIT TNE COOLING COIL Cooling Capacity [ton] | US_MA_SPLIT TNE COOLING COIL Cooling Capacity [ton] | 1.3647 | 1.2845 | 12696.0192 | 0 | 15 | 18869.9889 | 11991.3488 | 0 | 15 | 17816.715 | 1.3533 | 1.2742 | 12595.7753 | 0 | 15 | 18720.1133 | 11900.7065 | 0 | 15 | 17681.2803 | 1.42 | 1.3242 | 13179.82 | 0 | 15 | 19593.5126 | 12340.7648 | 0 | 15 | 18338.9052 | 1.3679 | 1.2307 | 12723.9858 | 0 | 15 | 18911.8046 | 11516.4773 | 0 | 15 | 17107.3011 | 1.2458 | 1.1183 | 11650.0576 | 0 | 15 | 17306.8268 | 10516.6197 | 0 | 15 | 15614.6146 | 1 | -704.6704 | -695.0688 | -839.0552 | -1207.5086 | -1133.4379
x |  | Split-System_W_Furnace | Labor | SPLIT TNW COOLING COIL | Split System | SPLIT TNW COOLING COIL Cooling Capacity [ton] | US_MA_SPLIT TNW COOLING COIL Cooling Capacity [ton] | 1.5124 | 1.4333 | 13982.6338 | 0 | 15 | 20794.802 | 13295.2354 | 0 | 15 | 19766.1622 | 1.5036 | 1.424 | 13906.7247 | 0 | 15 | 20681.1795 | 13214.313 | 0 | 15 | 19645.1088 | 1.6233 | 1.5267 | 14939.2983 | 0 | 15 | 22227.3984 | 14106.5057 | 0 | 15 | 20980.2326 | 1.5346 | 1.3898 | 14174.6141 | 0 | 15 | 21082.1963 | 12915.4582 | 0 | 15 | 19198.1212 | 1.434 | 1.2931 | 13301.5779 | 0 | 15 | 19775.6505 | 12066.84 | 0 | 15 | 17929.5202 | 1 | -687.3984 | -692.4117 | -832.7926 | -1259.156 | -1234.7379
x |  | Split-System_W_Furnace | y = 6.1014x2 - 73.657x + 2202.7 | SPLIT TS1 COOLING COIL | Split System | SPLIT TS1 COOLING COIL Cooling Capacity [ton] | US_MA_SPLIT TS1 COOLING COIL Cooling Capacity [ton] | 1.3291 | 1.2471 | 12383.5815 | 0 | 15 | 18402.9046 | 11661.4962 | 0 | 15 | 17323.9135 | 1.2886 | 1.2056 | 12027.5599 | 0 | 15 | 17870.8237 | 11293.6833 | 0 | 15 | 16774.5734 | 1.2896 | 1.1915 | 12036.2538 | 0 | 15 | 17883.8149 | 11168.1273 | 0 | 15 | 16587.0939 | 1.3708 | 1.2391 | 12749.2072 | 0 | 15 | 18949.5163 | 11590.5074 | 0 | 15 | 17217.875 | 1.3062 | 1.1776 | 12182.1955 | 0 | 15 | 18101.9084 | 11044.6512 | 0 | 15 | 16402.7412 | 1 | -722.0852 | -733.8766 | -868.1265 | -1158.6999 | -1137.5443
x |  | Split-System_W_Furnace | Updated to 2018 with labor and | SPLIT TS2 COOLING COIL | Split System | SPLIT TS2 COOLING COIL Cooling Capacity [ton] | US_MA_SPLIT TS2 COOLING COIL Cooling Capacity [ton] | 1.3315 | 1.2496 | 12404.4843 | 0 | 15 | 18434.1495 | 11683.0881 | 0 | 15 | 17356.1673 | 1.2926 | 1.2094 | 12062.9327 | 0 | 15 | 17923.6813 | 11327.7037 | 0 | 15 | 16825.3762 | 1.291 | 1.1929 | 12048.7549 | 0 | 15 | 17902.4952 | 11181.3837 | 0 | 15 | 16606.8873 | 1.3742 | 1.2421 | 12779.0025 | 0 | 15 | 18994.0683 | 11616.6903 | 0 | 15 | 17256.9846 | 1.3097 | 1.1809 | 12213.5671 | 0 | 15 | 18148.7936 | 11074.1749 | 0 | 15 | 16446.8189 | 1 | -721.3962 | -735.229 | -867.3711 | -1162.3122 | -1139.3922
x |  | Split-System_W_Furnace | material inflation multipliers. | SPLIT TSE COOLING COIL | Split System | SPLIT TSE COOLING COIL Cooling Capacity [ton] | US_MA_SPLIT TSE COOLING COIL Cooling Capacity [ton] | 1.57 | 1.4891 | 14480.0412 | 0 | 15 | 21539.5184 | 13780.1247 | 0 | 15 | 20491.6981 | 1.5382 | 1.456 | 14206.1093 | 0 | 15 | 21129.3491 | 13493.249 | 0 | 15 | 20062.4111 | 1.5761 | 1.4792 | 14533.1535 | 0 | 15 | 21619.0568 | 13694.6277 | 0 | 15 | 20363.7473 | 1.6373 | 1.4797 | 15059.1788 | 0 | 15 | 22407.001 | 13699.2447 | 0 | 15 | 20370.6567 | 1.5506 | 1.3988 | 14312.9974 | 0 | 15 | 21289.3855 | 12994.3566 | 0 | 15 | 19316.1155 | 1 | -699.9166 | -712.8603 | -838.5258 | -1359.9341 | -1318.6409
x |  | Split-System_W_Furnace | See cells F1:G1 | SPLIT TSW COOLING COIL | Split System | SPLIT TSW COOLING COIL Cooling Capacity [ton] | US_MA_SPLIT TSW COOLING COIL Cooling Capacity [ton] | 1.6543 | 1.5743 | 15205.5417 | 0 | 15 | 22626.3035 | 14517.4136 | 0 | 15 | 21595.485 | 1.6132 | 1.5324 | 14852.2377 | 0 | 15 | 22096.9776 | 14155.654 | 0 | 15 | 21053.8109 | 1.7216 | 1.6243 | 15781.0746 | 0 | 15 | 23488.9126 | 14948.2891 | 0 | 15 | 22240.8678 | 1.7115 | 1.5503 | 15694.5136 | 0 | 15 | 23359.1485 | 14310.6641 | 0 | 15 | 21285.8918 | 1.6166 | 1.4614 | 14881.8923 | 0 | 15 | 22141.4004 | 13540.2579 | 0 | 15 | 20132.7489 | 1 | -688.1281 | -696.5837 | -832.7855 | -1383.8495 | -1341.6343
x | 90.1-19c - Small unit setback controls |  | Programmable thermostat modeled in apartment units |  |  | Count of zones where this is required | 6.5 | 0 | 31 | 0 | 0 | 15 | 0 | 201.5 | 0 | 15 | 201.5 | 0 | 31 | 0 | 0 | 15 | 0 | 201.5 | 0 | 15 | 201.5 | 0 | 31 | 0 | 0 | 15 | 0 | 201.5 | 0 | 15 | 201.5 | 0 | 31 | 0 | 0 | 15 | 0 | 201.5 | 0 | 15 | 201.5 | 0 | 31 | 0 | 0 | 15 | 0 | 201.5 | 0 | 15 | 201.5 |  | 201.5 | 201.5 | 201.5 | 201.5 | 201.5
| 90.1-16g occ standby controls | occ_standby | 32 conditioned zones |  |  |  |  | 0 | 32 | 0 | 0 | 0 | 0 | 1066.8669 | 0 | 15 | 1872.2255 | 0 | 32 | 0 | 0 | 0 | 0 | 1066.8669 | 0 | 15 | 1872.2255 | 0 | 32 | 0 | 0 | 0 | 0 | 1066.8669 | 0 | 15 | 1872.2255 | 0 | 32 | 0 | 0 | 0 | 0 | 1066.8669 | 0 | 15 | 1872.2255 | 0 | 32 | 0 | 0 | 0 | 0 | 1066.8669 | 0 | 15 | 1872.2255
90.1-16 bo furnace efficiency
|  | Furnace_eff_apt | 32 units |  |  | Furnace heating capacity [Btuh] | US_MA_Furnace heating capacity [Btuh] | 32 | 32 | 50695.5605 | 0 | 15 | 68766.4905 | 51848.5533 | 0 | 15 | 70034.7827 | 32 | 32 | 50695.5605 | 0 | 15 | 68766.4905 | 51848.5533 | 0 | 15 | 70034.7827 | 32 | 32 | 50695.5605 | 0 | 15 | 68766.4905 | 51848.5533 | 0 | 15 | 70034.7827 | 32 | 32 | 50695.5605 | 0 | 15 | 68766.4905 | 51848.5533 | 0 | 15 | 70034.7827 | 32 | 32 | 50695.5605 | 0 | 15 | 68766.4905 | 51848.5533 | 0 | 15 | 70034.7827
90.1-16 ay & h - ERV
|  | ERV_multifamily | [5 empty] | 32 | 32 | 65461.6582 | 0 | 15 | 70609.9422 | 76007.1675 | 480 | 15 | 82606.4508 | 32 | 32 | 65461.6582 | 0 | 15 | 70609.9422 | 76007.1675 | 480 | 15 | 82606.4508 | 32 | 32 | 65461.6582 | 0 | 15 | 70609.9422 | 76007.1675 | 480 | 15 | 82606.4508 | 32 | 32 | 65461.6582 | 0 | 15 | 70609.9422 | 78720 | 480 | 15 | 85600 | 32 | 32 | 65461.6582 | 0 | 15 | 70609.9422 | 78720 | 480 | 15 | 85600
[8 empty] | 92.7856 | 153.8826 | 469648.1327 |  |  |  | 459747.8434 |  |  |  | 91.5358 | 152.6138 | 456343.6219 |  |  |  | 446128.7797
[10 empty] | 353490.914 |  |  | 525045.9196 | 330825.2557 |  |  | 491122.4164 |  |  | 340186.4032 |  |  | 505190.924 | 317206.1919 |  |  | 470811.1711 |  |  | 343343.1591 |  |  | 509920.8422 | 316263.3746 |  |  | 469423.871 |  |  | 347930.7123 |  |  | 516768.801 | 314565.7116 |  |  | 466881.0975 |  |  | 323780.4655 |  |  | 480735.2608 | 291801.9448 |  |  | 432948.4393
The regressions for bare costs + 10% (subcontractor cost level) are:
|  | material | labor
| C | 2690.6 | 2202.7
| x | -208.45 | -73.657
| x^2 | 17.693 | 6.1014

## Int Ltg LPD Methodology
90. 1 Cost Effectiveness - Interior Lighting Power Density Allowance Cost Calculation – Methodology
90.1-2022, Chapter 9, includes requirements for maximum lighting power density (LPD). There are both mandatory and prescriptive requirements. A total of three compliance paths exist, but the primary compliance paths are Table 9.5.1, which includes LPDs that are applied to an entire building area and Table 9.5.2.1, which allows assignment of maximum LPDs to specific space types.
Addenda to 90.1-19 updated the values in Table 9.5.2.1 of the standard. The maximum allowed LPD values decrease generally with some exceptions.
Part of the basis for the cost development is the use of the existing set of building space models that are used by the 90.1 lighting subcommittee to develop the LPD values in the Standard.
The models incorporate the various interior lighting design elements including:
• IES recommended light levels
• More surface reflectance options
• Light fixture efficacy
• Light loss factors
• Fixture coefficient of utilization (CU) related to expected room geometry
• Committee design expertise
In the development of LPD values for Standard 90.1-2022, the IES light level recommendations set the amount of light needed for the each space type. 90.1 Lighting Subcommittee design experts then determine an appropriate application mix of fixture types and lighting sources and what portion of the recommended light level(s) is provided by each combination. The mix of lighting technology for each space type is defined for both the baseline 90.1-2019 and the 90.1-2022, which is an aggressive yet achievable and realistic design model for typical spaces that strives to implement the 90.1 required LPD (W/ft2) maximum achievable energy efficiency while retaining reasonable and necessary design flexibility.
Finally, the combined fixture efficacy, loss factors, and CU values for the various fixtures and sources is used to calculate the wattage needed to provide the recommended level of lighting based on the efficacy of the sources and efficiency of fixtures involved. Each space type in the model has a total footcandle requirement to meet recommended light levels. There are up to four lighting systems that can be used in each space type and each system provides an assigned percentage of the overall total footcandles for that space. These percentages determine the amount of each luminaire type and its wattage needed to provide the required light levels. Note the worksheets that define the 90.1 lighting model are not included. Worksheets shown begin with the fixture costs by fixture ID, and the Int Lighting LPD Cost Detail contains the information on how these fixtures are applied to the different space types based on the LPD levels determined in the lighting models.
For cost development, the same basic modeling process is used but modified to produce realistic cost data that parallels the LPD development and therefore most effectively represents costs directly related to energy code requirements. To implement this, the LPD model process is first modified to calculate quantities of complete luminaires (fixture plus lighting source or lamp) needed to provide the recommended light levels. Then, costs for the specified luminaires are applied to generate a cost per square foot value for each space type within each Standard for comparison. The resulting calculations provide a $/ft2 value that is considered directly relatable to the LPD requirements in each standard.
The development of the costs for the luminaires used in the models first involved extracting a list of all the unique products used within both the 2019 and 2022 90.1 sets of lighting building models. Reputable sources, easily accessible to the general public, were used to cost these lighting components and appropriate installation labor. RS Means, an accepted authority within the construction industry, was used for labor costs (RS Means 2023). Fixture and lamp costs were determined using Grainger’s on-line catalog. The cost, lamp life, and complete luminaire wattage were noted. Fixture Cost per Watt ($/W) was calculated by dividing the fixture wattage by total luminaire cost (lamp, fixture, labor).
Modifying the LPD model process to calculate costs per square foot involved changing the wattage portion of the calculation explained above to cost. In this cost analysis, these same percentages are applied to the luminaire cost data to determine the total space cost associated with meeting the requirements in the Standard.
The basic cost calculation for each luminaire type within a space takes the form of:
Cost per square foot = (total space footcandles x percent of footcandles provided by lighting system x Fixture Cost per Watt)/ (efficacy of the lighting system in Lumens per Watt)
Costs are developed for each fixture including fixture cost, lamp cost, installation cost, replacement lamp cost and installation cost, and hours of lamp life for each lamp type. When the costs are combined by space type for each prototype, the replacement cycle is determined by dividing the annual full load equivalent hours from the corresponding energy model schedule, which include fractions of full load operation during each hour of the day.
The database of real building details available for development of the LPDs includes approximately 250 buildings. However, for this cost estimate, only those buildings that are classified as one of the 16 prototypes were used to calculate average whole building $/sqft for both Standard years.
Once the costs are assigned to each prototype and its corresponding space types, these are summed up for each prototype. The cost for each prototype is totaled and the incremental cost is the difference between the 90.1-2019 and 90.1-2022 costs. Replacement cost incremental costs have to be kept separated into the replacement lives, e.g. year 5 replacement if any for 90.1-2019 and 90.1-2022.
Cost estimation for the IECC models - methodology
The 2006, 2009 and the high efficiency lighting option in the 2012 IECC (modeled option for this case) include only whole building LPDs. In order to implement these LPDs, the following procedure was used:
- whole building LPDs were calculated for the 90.1-2004 cases from the space-by-space LPDs and zones areas
- Scaling factors were then calculated based on the 90.1-2004 calculated whole building LPDs, to match the IECC requirements
- The scaling factors were then used to scale each space-by-space LPD such that it yielded the correct whole building level LPD
For cost estimation, a similar strategy is used, in that the space-by-space LPDs are scaled to match the modeled space-by-space LPD from above. Because different prototypes have different IECC scaling factors, the IECC LPD for the same space type is different in different prototypes. Hence, the costs for the same space type also vary by prototype.
Once the required space-by-sapce LPDs are calculated, the methodology for determining the fixture type and counts remains the same as 90.1.
Note about Apartments:
- The 2009 and 2012 IECC require 50% and 75% respectively of all permanently installed fixtures to have high efficacy lamps. These requirements do not exist in 90.1.
- The baseline 2006 IECC in simulation is kept the same as 90.1-2004. 90.1-2004 uses Building America Benchmark definition for the LPD (refer 90.1 LPD Requirement spreadsheet under _p.require). This baseline includes an assumption of % flourescent. These fractions are adjusted to match the 2009 and 2012 IECC requirements. The LPD is used in conjunction with a lighting usage profile to yield lighting energy.
- While this approach results in an accurate representation of the energy profile, it is not very useful in determining incremental costs due to the normalization of the LPD for modeling purposes. In reality, home have many more connected fixtures (higher connected LPD) and only a subset operates at any given time.
- Thus, in order to cost out lighting requirements, a detailed lighting fixture sheet is derived from the NC3 data. The fixtures are then changed to high efficacy fixtures to meet the IECC requirements. The calculations are detailed in the dwelling_units tab in this workbook.
- NC3 data had two apartments - one a basic low-end apartment with minimal fixtures and another high-end apartment with more detailed fixtures. This sheet includes costs for the high-end apartment.
Note about changes since the 90.1 cost estimate: (Per Eric's note - email dtd. 5/6/2013)
The initial 90.1-2007 to 90.1-2010 cost effectiveness analysis considered slightly different equipment options for costing based on the fact that current federal rulemakings have eliminated some specific incandescent products. In the 2007 timeframe, the standard incandescent lamps were available (60, 75, 100) but for a timeframe where 90.1-2010 would typically be adopted, these would effectively be replaced with more efficient and therefore lower wattage and different cost options. The costs associated with these equipment were used for costing the 90.1-2010 option.
However, for cost comparison of options, the costs for applicable equipment should be the same for any and all options for the same equipment. Therefore, for the current analysis, the costs associated with the newer technologies available in the 2010 adoption timeframe were applied to both options.
Internal Instructions for LPD tabs:
[Int Lighting Comp]
Fixture and lamp cost, life and wattage information
Note that the NEW table reads from the BASE table, so fixture IDs are identical
Each line in BASE table is assigned a lookup fixture ID
[Int Ltg LPD Space Type Comp]
The BASE code information is entered it the top table, the NEW code information in the lower table
Each line is assigned a lookup space name (first line) plus fixture ID [col B]
Unused lines must have ID 0
ASHRAE LSC model # entered in [col D] space LPD [col E] - first line of space
and W/sf in [col O] for each fixture ID [col F]
The rest of the cost factors/sf are calculated.
A current quirk is that BASE allows 3 fixt ID/space, and NEW allows 4
[Int Ltg LPD Proto]
Aligned in groups of 4, BASE and NEW space/fixture codes are entered [col B/C]
Prototypes affected marked [col H-M]; climates not necessary.
BASE descriptive comments may be added [Col V]
EFLH in [col X] for BASE and [col AD] for NEW for each building
Note - this is not by space type as noted, but by building type except for small hotel where it is by space
Area in protototypes BASE in first line each space [col Z]
Area in protototypes NEW in first line each space [col AE]
Remainder of cells appear to be calculated

## Int Ltg LPD Summary
Commercial Energy Code Cost Effectiveness - Interior Lighting LPD - Cost Summary Depending on Choice of Base Code and Target Code
Interior Lighting - Summary of Total New Construction, Maintenance, and Replacement Costs By Replacement Year by Prototype | [42 empty] | Costs for Addendum br – Dwelling unit lighting efficacy and control: | 318
[43 empty] | # of dwelling units: | 31
Small Office | [7 empty] | Large Office | [7 empty] | Standalone Retail | [7 empty] | Primary School | [7 empty] | Small Hotel | [7 empty] | Mid-rise Apartment
Base Code | 2019 |  | Target Code | 2022 |  | Incremental Cost |  | Base Code | 2019 |  | Target Code | 2022 |  | Incremental Cost |  | Base Code | 2019 |  | Target Code | 2022 |  | Incremental Cost |  | Base Code | 2019 |  | Target Code | 2022 |  | Incremental Cost |  | Base Code | 2019 |  | Target Code | 2022 |  | Incremental Cost |  | Base Code | 2019 |  | Target Code | 2022 |  | Incremental Cost
Category | All Costs, First Replacement Only | With Repeated Replacements | Category | Replacement First Year | With Repeated Replacements | 30 Year | 40 Year | Category | All Costs, First Replacement Only | With Repeated Replacements | Category | Replacement First Year | With Repeated Replacements | 30 Year | 40 Year | Category | All Costs, First Replacement Only | With Repeated Replacements | Category | Replacement First Year | With Repeated Replacements | 30 Year | 40 Year | Category | All Costs, First Replacement Only | With Repeated Replacements | Category | Replacement First Year | With Repeated Replacements | 30 Year | 40 Year | Category | All Costs, First Replacement Only | With Repeated Replacements | Category | Replacement First Year | With Repeated Replacements | 30 Year | 40 Year | Category | All Costs, First Replacement Only | With Repeated Replacements | Category | Replacement First Year | With Repeated Replacements | 30 Year | 40 Year
New Construction | 0 | 0 | New Construction | 0 | 0 | 0 | 0 | New Construction | 0 | 0 | New Construction | 0 | 0 | 0 | 0 | New Construction | 0 | 0 | New Construction | 0 | 0 | 0 | 0 | New Construction | 0 | 0 | New Construction | 0 | 0 | 0 | 0 | New Construction | 0 | 0 | New Construction | 0 | 0 | 0 | 0 | New Construction | 0 | 0 | New Construction | 0 | 9858 | 9858 | 9858
Replacement - Year |  |  | Replacement - Year | 0 | 0 | 0 | 0 | Replacement - Year |  |  | Replacement - Year | 0 | 0 | 0 | 0 | Replacement - Year |  |  | Replacement - Year | 0 | 0 | 0 | 0 | Replacement - Year |  |  | Replacement - Year | 0 | 0 | 0 | 0 | Replacement - Year |  |  | Replacement - Year | 0 | 0 | 0 | 0 | Replacement - Year |  |  | Replacement - Year | 0 | 0 | 0 | 0
1 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 0
2 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 0 | 0
3 | 0 | 0 | 3 | 0 | 0 | 0 | 0 | 3 | 0 | 0 | 3 | 0 | 0 | 0 | 0 | 3 | 0 | 0 | 3 | 0 | 0 | 0 | 0 | 3 | 0 | 0 | 3 | 0 | 0 | 0 | 0 | 3 | 0 | 0 | 3 | 0 | 0 | 0 | 0 | 3 | 0 | 0 | 3 | 0 | 0 | 0 | 0
4 | 0 | 0 | 4 | 0 | 0 | 0 | 0 | 4 | 0 | 0 | 4 | 0 | 0 | 0 | 0 | 4 | 0 | 0 | 4 | 0 | 0 | 0 | 0 | 4 | 0 | 0 | 4 | 0 | 0 | 0 | 0 | 4 | 0 | 0 | 4 | 0 | 0 | 0 | 0 | 4 | 0 | 0 | 4 | 0 | 0 | 0 | 0
5 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 5 | 0 | 0 | 0 | 0
6 | 0 | 0 | 6 | 0 | 0 | 0 | 0 | 6 | 0 | 0 | 6 | 0 | 0 | 0 | 0 | 6 | 0 | 0 | 6 | 0 | 0 | 0 | 0 | 6 | 0 | 0 | 6 | 0 | 0 | 0 | 0 | 6 | 0 | 0 | 6 | 0 | 0 | 0 | 0 | 6 | 0 | 0 | 6 | 0 | 0 | 0 | 0
7 | 0 | 0 | 7 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 7 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 7 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 7 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 7 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 7 | 0 | 0 | 0 | 0
8 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 8 | 0 | 0 | 0 | 0
9 | 0 | 0 | 9 | 0 | 0 | 0 | 0 | 9 | 0 | 0 | 9 | 0 | 0 | 0 | 0 | 9 | 0 | 0 | 9 | 0 | 0 | 0 | 0 | 9 | 0 | 0 | 9 | 0 | 0 | 0 | 0 | 9 | 0 | 0 | 9 | 0 | 0 | 0 | 0 | 9 | 0 | 0 | 9 | 0 | 0 | 0 | 0
10 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 10 | 0 | 0 | 0 | 0
11 | 0 | 0 | 11 | 0 | 0 | 0 | 0 | 11 | 0 | 0 | 11 | 0 | 0 | 0 | 0 | 11 | 0 | 0 | 11 | 0 | 0 | 0 | 0 | 11 | 0 | 0 | 11 | 0 | 0 | 0 | 0 | 11 | 0 | 0 | 11 | 0 | 0 | 0 | 0 | 11 | 0 | 0 | 11 | 0 | 0 | 0 | 0
12 | 0 | 0 | 12 | 0 | 0 | 0 | 0 | 12 | 0 | 0 | 12 | 0 | 0 | 0 | 0 | 12 | 0 | 0 | 12 | 0 | 0 | 0 | 0 | 12 | 0 | 0 | 12 | 0 | 0 | 0 | 0 | 12 | 0 | 0 | 12 | 0 | 0 | 0 | 0 | 12 | 0 | 0 | 12 | 0 | 0 | 0 | 0
13 | 0 | 0 | 13 | 0 | 0 | 0 | 0 | 13 | 0 | 0 | 13 | 0 | 0 | 0 | 0 | 13 | 0 | 0 | 13 | 0 | 0 | 0 | 0 | 13 | 0 | 0 | 13 | 0 | 0 | 0 | 0 | 13 | 0 | 0 | 13 | 0 | 0 | 0 | 0 | 13 | 0 | 0 | 13 | 0 | 0 | 0 | 0
14 | 0 | 0 | 14 | 0 | 0 | 0 | 0 | 14 | 0 | 0 | 14 | 0 | 0 | 0 | 0 | 14 | 0 | 0 | 14 | 0 | 0 | 0 | 0 | 14 | 0 | 0 | 14 | 0 | 0 | 0 | 0 | 14 | 0 | 0 | 14 | 0 | 0 | 0 | 0 | 14 | 0 | 0 | 14 | 0 | 0 | 0 | 0
15 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 15 | 0 | 0 | 0 | 0
16 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 16 | 0 | 0 | 0 | 0
17 | 0 | 0 | 17 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 17 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 17 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 17 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 17 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 17 | 0 | 0 | 0 | 0
18 | 0 | 0 | 18 | 0 | 0 | 0 | 0 | 18 | 0 | 0 | 18 | 0 | 0 | 0 | 0 | 18 | 0 | 0 | 18 | 0 | 0 | 0 | 0 | 18 | 0 | 0 | 18 | 0 | 0 | 0 | 0 | 18 | 0 | 0 | 18 | 0 | 0 | 0 | 0 | 18 | 0 | 0 | 18 | 0 | 0 | 0 | 0
19 | 0 | 0 | 19 | 0 | 0 | 0 | 0 | 19 | 0 | 0 | 19 | 0 | 0 | 0 | 0 | 19 | 0 | 0 | 19 | 0 | 0 | 0 | 0 | 19 | 0 | 0 | 19 | 0 | 0 | 0 | 0 | 19 | 0 | 0 | 19 | 0 | 0 | 0 | 0 | 19 | 0 | 0 | 19 | 0 | 0 | 0 | 0
20 | 0 | 0 | 20 | 0 | 0 | 0 | 0 | 20 | 0 | 0 | 20 | 0 | 0 | 0 | 0 | 20 | 0 | 0 | 20 | 0 | 0 | 0 | 0 | 20 | 0 | 0 | 20 | 0 | 0 | 0 | 0 | 20 | 0 | 0 | 20 | 0 | 0 | 0 | 0 | 20 | 0 | 0 | 20 | 0 | 0 | 0 | 0
21 | 0 | 0 | 21 | 0 | 0 | 0 | 0 | 21 | 0 | 0 | 21 | 0 | 0 | 0 | 0 | 21 | 0 | 0 | 21 | 0 | 0 | 0 | 0 | 21 | 0 | 0 | 21 | 0 | 0 | 0 | 0 | 21 | 0 | 0 | 21 | 0 | 0 | 0 | 0 | 21 | 0 | 0 | 21 | 0 | 0 | 0 | 0
22 | 0 | 0 | 22 | 0 | 0 | 0 | 0 | 22 | 0 | 0 | 22 | 0 | 0 | 0 | 0 | 22 | 0 | 0 | 22 | 0 | 0 | 0 | 0 | 22 | 0 | 0 | 22 | 0 | 0 | 0 | 0 | 22 | 0 | 0 | 22 | 0 | 0 | 0 | 0 | 22 | 0 | 0 | 22 | 0 | 0 | 0 | 0
23 | 0 | 0 | 23 | 0 | 0 | 0 | 0 | 23 | 0 | 0 | 23 | 0 | 0 | 0 | 0 | 23 | 0 | 0 | 23 | 0 | 0 | 0 | 0 | 23 | 0 | 0 | 23 | 0 | 0 | 0 | 0 | 23 | 0 | 0 | 23 | 0 | 0 | 0 | 0 | 23 | 0 | 0 | 23 | 0 | 0 | 0 | 0
24 | 0 | 0 | 24 | 0 | 0 | 0 | 0 | 24 | 0 | 0 | 24 | 0 | 0 | 0 | 0 | 24 | 0 | 0 | 24 | 0 | 0 | 0 | 0 | 24 | 0 | 0 | 24 | 0 | 0 | 0 | 0 | 24 | 0 | 0 | 24 | 0 | 0 | 0 | 0 | 24 | 0 | 0 | 24 | 0 | 0 | 0 | 0
25 | 0 | 0 | 25 | 0 | 0 | 0 | 0 | 25 | 0 | 0 | 25 | 0 | 0 | 0 | 0 | 25 | 0 | 0 | 25 | 0 | 0 | 0 | 0 | 25 | 0 | 0 | 25 | 0 | 0 | 0 | 0 | 25 | 0 | 0 | 25 | 0 | 0 | 0 | 0 | 25 | 0 | 0 | 25 | 0 | 0 | 0 | 0
26 | 0 | 0 | 26 | 0 | 0 | 0 | 0 | 26 | 0 | 0 | 26 | 0 | 0 | 0 | 0 | 26 | 0 | 0 | 26 | 0 | 0 | 0 | 0 | 26 | 0 | 0 | 26 | 0 | 0 | 0 | 0 | 26 | 0 | 0 | 26 | 0 | 0 | 0 | 0 | 26 | 0 | 0 | 26 | 0 | 0 | 0 | 0
27 | 0 | 0 | 27 | 0 | 0 | 0 | 0 | 27 | 0 | 0 | 27 | 0 | 0 | 0 | 0 | 27 | 0 | 0 | 27 | 0 | 0 | 0 | 0 | 27 | 0 | 0 | 27 | 0 | 0 | 0 | 0 | 27 | 0 | 0 | 27 | 0 | 0 | 0 | 0 | 27 | 0 | 0 | 27 | 0 | 0 | 0 | 0
28 | 0 | 0 | 28 | 0 | 0 | 0 | 0 | 28 | 0 | 0 | 28 | 0 | 0 | 0 | 0 | 28 | 0 | 0 | 28 | 0 | 0 | 0 | 0 | 28 | 0 | 0 | 28 | 0 | 0 | 0 | 0 | 28 | 0 | 0 | 28 | 0 | 0 | 0 | 0 | 28 | 0 | 0 | 28 | 0 | 0 | 0 | 0
29 | 0 | 0 | 29 | 0 | 0 | 0 | 0 | 29 | 0 | 0 | 29 | 0 | 0 | 0 | 0 | 29 | 0 | 0 | 29 | 0 | 0 | 0 | 0 | 29 | 0 | 0 | 29 | 0 | 0 | 0 | 0 | 29 | 0 | 0 | 29 | 0 | 0 | 0 | 0 | 29 | 0 | 0 | 29 | 0 | 0 | 0 | 0
30 | 0 | 0 | 30 | 0 | 0 | 0 | 0 | 30 | 0 | 0 | 30 | 0 | 0 | 0 | 0 | 30 | 0 | 0 | 30 | 0 | 0 | 0 | 0 | 30 | 0 | 0 | 30 | 0 | 0 | 0 | 0 | 30 | 0 | 0 | 30 | 0 | 0 | 0 | 0 | 30 | 0 | 0 | 30 | 0 | 0 | 0 | 0
31 | 0 | 0 | 31 | 0 | 0 |  | 0 | 31 | 0 | 0 | 31 | 0 | 0 |  | 0 | 31 | 0 | 0 | 31 | 0 | 0 |  | 0 | 31 | 0 | 0 | 31 | 0 | 0 |  | 0 | 31 | 0 | 0 | 31 | 0 | 0 |  | 0 | 31 | 0 | 0 | 31 | 0 | 0 |  | 0
32 | 0 | 0 | 32 | 0 | 0 |  | 0 | 32 | 0 | 0 | 32 | 0 | 0 |  | 0 | 32 | 0 | 0 | 32 | 0 | 0 |  | 0 | 32 | 0 | 0 | 32 | 0 | 0 |  | 0 | 32 | 0 | 0 | 32 | 0 | 0 |  | 0 | 32 | 0 | 0 | 32 | 0 | 0 |  | 0
33 | 0 | 0 | 33 | 0 | 0 |  | 0 | 33 | 0 | 0 | 33 | 0 | 0 |  | 0 | 33 | 0 | 0 | 33 | 0 | 0 |  | 0 | 33 | 0 | 0 | 33 | 0 | 0 |  | 0 | 33 | 0 | 0 | 33 | 0 | 0 |  | 0 | 33 | 0 | 0 | 33 | 0 | 0 |  | 0
34 | 0 | 0 | 34 | 0 | 0 |  | 0 | 34 | 0 | 0 | 34 | 0 | 0 |  | 0 | 34 | 0 | 0 | 34 | 0 | 0 |  | 0 | 34 | 0 | 0 | 34 | 0 | 0 |  | 0 | 34 | 0 | 0 | 34 | 0 | 0 |  | 0 | 34 | 0 | 0 | 34 | 0 | 0 |  | 0
35 | 0 | 0 | 35 | 0 | 0 |  | 0 | 35 | 0 | 0 | 35 | 0 | 0 |  | 0 | 35 | 0 | 0 | 35 | 0 | 0 |  | 0 | 35 | 0 | 0 | 35 | 0 | 0 |  | 0 | 35 | 0 | 0 | 35 | 0 | 0 |  | 0 | 35 | 0 | 0 | 35 | 0 | 0 |  | 0
36 | 0 | 0 | 36 | 0 | 0 |  | 0 | 36 | 0 | 0 | 36 | 0 | 0 |  | 0 | 36 | 0 | 0 | 36 | 0 | 0 |  | 0 | 36 | 0 | 0 | 36 | 0 | 0 |  | 0 | 36 | 0 | 0 | 36 | 0 | 0 |  | 0 | 36 | 0 | 0 | 36 | 0 | 0 |  | 0
37 | 0 | 0 | 37 | 0 | 0 |  | 0 | 37 | 0 | 0 | 37 | 0 | 0 |  | 0 | 37 | 0 | 0 | 37 | 0 | 0 |  | 0 | 37 | 0 | 0 | 37 | 0 | 0 |  | 0 | 37 | 0 | 0 | 37 | 0 | 0 |  | 0 | 37 | 0 | 0 | 37 | 0 | 0 |  | 0
38 | 0 | 0 | 38 | 0 | 0 |  | 0 | 38 | 0 | 0 | 38 | 0 | 0 |  | 0 | 38 | 0 | 0 | 38 | 0 | 0 |  | 0 | 38 | 0 | 0 | 38 | 0 | 0 |  | 0 | 38 | 0 | 0 | 38 | 0 | 0 |  | 0 | 38 | 0 | 0 | 38 | 0 | 0 |  | 0
39 | 0 | 0 | 39 | 0 | 0 |  | 0 | 39 | 0 | 0 | 39 | 0 | 0 |  | 0 | 39 | 0 | 0 | 39 | 0 | 0 |  | 0 | 39 | 0 | 0 | 39 | 0 | 0 |  | 0 | 39 | 0 | 0 | 39 | 0 | 0 |  | 0 | 39 | 0 | 0 | 39 | 0 | 0 |  | 0
40 | 0 | 0 | 40 | 0 | 0 |  | 0 | 40 | 0 | 0 | 40 | 0 | 0 |  | 0 | 40 | 0 | 0 | 40 | 0 | 0 |  | 0 | 40 | 0 | 0 | 40 | 0 | 0 |  | 0 | 40 | 0 | 0 | 40 | 0 | 0 |  | 0 | 40 | 0 | 0 | 40 | 0 | 0 |  | 0
Residual Year 30 |  | 0 | Residual Year 30 | 0 | 0 |  | 0 | Residual Year 30 |  | 0 | Residual Year 30 | 0 | 0 |  | 0 | Residual Year 30 |  | 0 | Residual Year 30 | 0 | 0 |  | 0 | Residual Year 30 |  | 0 | Residual Year 30 | 0 | 0 |  | 0 | Residual Year 30 |  | 0 | Residual Year 30 | 0 | 0 |  | 0 | Residual Year 30 |  | 0 | Residual Year 30 | 0 | 0 |  | 0
Residual Year 40 |  | 0 | Residual Year 40 | 0 | 0 |  | 0 | Residual Year 40 |  | 0 | Residual Year 40 | 0 | 0 |  | 0 | Residual Year 40 |  | 0 | Residual Year 40 | 0 | 0 |  | 0 | Residual Year 40 |  | 0 | Residual Year 40 | 0 | 0 |  | 0 | Residual Year 40 |  | 0 | Residual Year 40 | 0 | 0 |  | 0 | Residual Year 40 |  | 0 | Residual Year 40 | 0 | 0 |  | 0

## Int Ltg LPD Proto 90_1 (hidden)
[16 empty] | Commercial Energy Code Cost Effectiveness - Interior Lighting Power Density - 90.1 2016 and 2019 - Costs Totals for Each Prototype | [20 empty] | Warning! Formulas below are different in greyed areas for ballast replacements | [23 empty] | Warning! Formulas below are different in greyed areas for ballast replacements | [23 empty] | 90.1 Cost Effectiveness - Interior Lighting Power Density 90.1-07by and 90.1-07de Costs - Prototype
Summary
Addenda 90.1-10bh, co, cr, dj, and dl change the interior lighting power allowances in Tables 9.5.1 for the building area method and Table 9.6.1 for the space by space method.
The cost of interior lighting for the prototypes that meets the lighting power allowances for 90.1-2019 and 90.1-2022 are shown below.
Interior Lighting - Summary of Total New Construction, Maintenance, and Replacement Costs By Replacement Year by Prototype
[16 empty] | Col22 | LPD2013 | Fixture ID Numbers | Col25 | area2013 | Col27 | LPD2016 | Col29 | Col30 | area2016 | Col32 | Col33 | Col34 | Col35 | Col36 | Mat2013 | Col38 | Col39 | Lab2013 | Col41 | Col42 | Col43 | Col44 | Tot2013 | Col46 | Col47 | Col48 | Col49 | Col50 | Col51 | Col52 | Col53 | Col54 | Col55 | Col56 | Rep2010 | Col58 | Mat2016 | Col60 | Col61 | Lab2016 | Col63 | Col64 | Col65 | Col66 | Tot2016 | Col68 | Col69 | Col70 | Col71 | Col72 | Col73 | Col74 | Col75 | Col76 | Col77 | Col78 | Repl2016 | Incremental | Repl | Col82 | Proto | Space | Col85 | Col86 | Col87 | Col88 | Col89 | Col90
[16 empty] | 90.1-2019 |  |  |  |  | 90.1-2022 | [8 empty] | 90.1-2019 Baseline Costs - without implementation of the addenda. | [21 empty] | 90.1-2022 - costs with addendum | [21 empty] | Incremental Costs | Incremental Costs | [9 empty] | Small Office | [7 empty] | Large Office | [7 empty] | Standalone Retail | [7 empty] | Primary School | [7 empty] | Small Hotel | [7 empty] | Mid-rise Apartment
|  | Prototypes Affected (X) | [5 empty] | Not Used | [5 empty] | Name of Item | [11 empty] | LPA |  |  |  | New Construction Costs | [9 empty] | Replacement Costs | [11 empty] | New Construction Costs | [9 empty] | Replacement Costs | [22 empty] | 90.1-2019 |  |  | 90.1-2022 |  |  | Incremental Cost |  | 90.1-2019 |  |  | 90.1-2022 |  |  | Incremental Cost |  | 90.1-2019 |  |  | 90.1-2022 |  |  | Incremental Cost |  | 90.1-2019 |  |  | 90.1-2022 |  |  | Incremental Cost |  | 90.1-2019 |  |  | 90.1-2022 |  |  | Incremental Cost |  | 90.1-2019 |  |  | 90.1-2022 |  |  | Incremental Cost
90.1-2019 Lookup | 90.1-2022 Lookup | Small Office | Large Office | Standalone Retail | Primary School | Small Hotel | Mid-rise Apartment | [5 empty] | Not Used | Interior Lighting Power Density | Not Used | Costs to provide lighting fixtures, lamps and ballasts to meet space by space lighting power density (LPD) maximum allowed LPD values under 90.1-2019. Fixtures, lamps and ballasts and quantities defined from 90.1 development interior lighting models and additional input from 90.1 Lighting Subcommittee. Costs are for equipment etc. at today's prices that just meet the 90.1-2019 requirements. Costs by 90.1-2019 Prototype and Lighting Space Type | 90.1-2019 Allowed Maximum LPD W/ft2 | Fixture ID Numbers | Annual Full Load Equivalent Operating Hours for Space Type Lamp Life for Fixtures (Used to Calculate Replacement Life) | Area of Space Type In Prototype Models | Costs to provide lighting fixtures, lamps and ballasts to meet space by space maximum allowed LPD values under 90.1-2022 Table 9.6.1. Fixtures, lamps and ballasts and quantities defined from 90.1 development interior lighting models and additional input from 90.1 Lighting Subcommittee. Costs by 90.1-2022 Prototype and Lighting Space Type | 90.1-2022 Allowed Maximum LPD W/ft2 | Fixture ID Numbers | Annual Full Load Equivalent (BLE) Operating Hours | Area of Space Type, ft2 | Baseline # of fixtures | Baseline Sq. Ft. per fixture | NEW # of fixtures | Baseline Sq. Ft. per fixture | Material Cost/ft2 | Material Subtotal Cost/ft2 × area for space type | Labor Crew Type Not Used | Labor Cost/ft2 | Labor Subtotal Cost/ft2 × Area | Construction Equipment Subtotal | Cost Adjustments | Not Used | Not Used | Total | Replacement Life (hours of operation/ component life) | Replacement Period (costs assigned to a 1 year period) | Material Cost/ft2 | Material Subtotal Cost/ft2 × area for space type | Labor Crew Type Not Used | Labor Cost/ft2 | Labor Subtotal Cost/ft2 × Area | Construction Equipment Subtotal | Cost Adjustments (with added replacement labor hours) | Not Used | Subtotal | Total (adjusted for actual quantity of replacements in replacement period) | Material Cost/ft2 | Material Subtotal Cost/ft2 × area for space type | Labor Crew Type Not Used | Labor Cost/ft2 | Labor Subtotal Cost/ft2 × Area | Construction Equipment Subtotal | Cost Adjustments | Not Used | Not Used | Total | Replacement Life (hours of operation/ component life) | Replacement Period (costs assigned to a 1 year period) | Material Cost/ft2 | Material Subtotal Cost/ft2 × area for space type | Labor Crew Type Not Used | Labor Cost/ft2 | Labor Subtotal Cost/ft2 × Area | Construction Equipment Subtotal | Cost Adjustments (with added replacement labor hours) | Incremental Added Design with OH&P | Subtotal | Total (adjusted for actual quantity of replacements in replacement period) | New Construction Costs 90.1-2022 minus 90.1-2019 | Replacement Costs 90.1-2022 minus 90.1-2019 | line item repl costs |  | Space Name |  |  | 2013 Fixture in Space | 2016 Fixture in Space |  |  | Category | All Costs, First Replacement Only | With Repeated Replacements | Category | Replacement First Year | With Repeated Replacements | 30 Year | 40 Year | Category | All Costs, First Replacement Only | With Repeated Replacements | Category | Replacement First Year | With Repeated Replacements | 30 Year | 40 Year | Category | All Costs, First Replacement Only | With Repeated Replacements | Category | Replacement First Year | With Repeated Replacements | 30 Year | 40 Year | Category | All Costs, First Replacement Only | With Repeated Replacements | Category | Replacement First Year | With Repeated Replacements | 30 Year | 40 Year | Category | All Costs, First Replacement Only | With Repeated Replacements | Category | Replacement First Year | With Repeated Replacements | 30 Year | 40 Year | Category | All Costs, First Replacement Only | With Repeated Replacements | Category | Replacement First Year | With Repeated Replacements | 30 Year | 40 Year
[85 empty] | New Construction | 129222.8711 | 129222.8711 | New Construction | 119063.0126 | 119063.0126 | -10159.8584 | -10159.8584 | New Construction | 11714643.2162 | 11714643.2162 | New Construction | 10793603.292 | 10793603.292 | -921039.9243 | -921039.9243 | New Construction | 361422.0139 | 361422.0139 | New Construction | 331349.3403 | 331349.3403 | -30072.6736 | -30072.6736 | New Construction | 924822.8814 | 924822.8814 | New Construction | 778120.4685 | 778120.4685 | -146702.413 | -146702.413 | New Construction | 381178.8247 | 381178.8247 | New Construction | 410803.5574 | 410803.5574 | 29624.7327 | 29624.7327 | New Construction | 69812.6818 | 69812.6818 | New Construction | 47622.0429 | 47622.0429 | -22190.6389 | -22190.6389
[85 empty] | Replacement - Year |  |  | Replacement - Year |  |  | 0 | 0 | Replacement - Year |  |  | Replacement - Year |  |  | 0 | 0 | Replacement - Year |  |  | Replacement - Year |  |  | 0 | 0 | Replacement - Year |  |  | Replacement - Year |  |  | 0 | 0 | Replacement - Year |  |  | Replacement - Year |  |  | 0 | 0 | Replacement - Year |  |  | Replacement - Year |  |  | 0 | 0
[85 empty] | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 20971.7044 | 20971.7044 | 1 | 0 | 0 | -20971.7044 | -20971.7044 | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 0
[85 empty] | 2 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 2 | 0 | 20971.7044 | 2 | 0 | 0 | -20971.7044 | -20971.7044 | 2 | 536.0379 | 536.0379 | 2 | 69.1662 | 69.1662 | -466.8718 | -466.8718
[16 empty] | Scroll down to row 60 for space by space analysis; scroll right for 40 year cost tabulations by building type | [68 empty] | 3 | 0 | 0 | 3 | 0 | 0 | 0 | 0 | 3 | 0 | 0 | 3 | 0 | 0 | 0 | 0 | 3 | 0 | 0 | 3 | 0 | 0 | 0 | 0 | 3 | 0 | 0 | 3 | 0 | 0 | 0 | 0 | 3 | 38226.3677 | 59198.0721 | 3 | 0 | 0 | -59198.0721 | -59198.0721 | 3 | 0 | 0 | 3 | 0 | 0 | 0 | 0
[85 empty] | 4 | 0 | 0 | 4 | 0 | 0 | 0 | 0 | 4 | 0 | 0 | 4 | 0 | 0 | 0 | 0 | 4 | 0 | 0 | 4 | 0 | 0 | 0 | 0 | 4 | 0 | 0 | 4 | 0 | 0 | 0 | 0 | 4 | 0 | 20971.7044 | 4 | 0 | 0 | -20971.7044 | -20971.7044 | 4 | 0 | 536.0379 | 4 | 0 | 69.1662 | -466.8718 | -466.8718
[85 empty] | 5 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | 5 | 233.4385 | 21205.1429 | 5 | 0 | 0 | -21205.1429 | -21205.1429 | 5 | 0 | 0 | 5 | 0 | 0 | 0 | 0
[85 empty] | 6 | 0 | 0 | 6 | 0 | 0 | 0 | 0 | 6 | 0 | 0 | 6 | 0 | 0 | 0 | 0 | 6 | 0 | 0 | 6 | 0 | 0 | 0 | 0 | 6 | 0 | 0 | 6 | 0 | 0 | 0 | 0 | 6 | 136647.3142 | 195845.3863 | 6 | 95053.5802 | 95053.5802 | -100791.8061 | -100791.8061 | 6 | 63629.1594 | 64165.1973 | 6 | 44052.3383 | 44121.5045 | -20043.6928 | -20043.6928
[85 empty] | 7 | 0 | 0 | 7 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 7 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 7 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 7 | 0 | 0 | 0 | 0 | 7 | 7737.1134 | 28708.8178 | 7 | 17154.8643 | 17154.8643 | -11553.9535 | -11553.9535 | 7 | 0 | 0 | 7 | 0 | 0 | 0 | 0
[85 empty] | 8 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 8 | 0 | 20971.7044 | 8 | 0 | 0 | -20971.7044 | -20971.7044 | 8 | 0 | 536.0379 | 8 | 0 | 69.1662 | -466.8718 | -466.8718
[85 empty] | 9 | 0 | 0 | 9 | 0 | 0 | 0 | 0 | 9 | 0 | 0 | 9 | 0 | 0 | 0 | 0 | 9 | 0 | 0 | 9 | 0 | 0 | 0 | 0 | 9 | 0 | 0 | 9 | 0 | 0 | 0 | 0 | 9 | 28615.6436 | 87813.7157 | 9 | 21559.5477 | 21559.5477 | -66254.168 | -66254.168 | 9 | 0 | 0 | 9 | 0 | 0 | 0 | 0
[85 empty] | 10 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 10 | 17.4203 | 17.4203 | 10 | 0 | 0 | -17.4203 | -17.4203 | 10 | 2297.3255 | 2297.3255 | 10 | 0 | 0 | -2297.3255 | -2297.3255 | 10 | 0 | 21205.1429 | 10 | 0 | 0 | -21205.1429 | -21205.1429 | 10 | 0 | 536.0379 | 10 | 0 | 69.1662 | -466.8718 | -466.8718
[85 empty] | 11 | 0 | 0 | 11 | 0 | 0 | 0 | 0 | 11 | 0 | 0 | 11 | 0 | 0 | 0 | 0 | 11 | 0 | 0 | 11 | 0 | 0 | 0 | 0 | 11 | 0 | 0 | 11 | 0 | 0 | 0 | 0 | 11 | 0 | 20971.7044 | 11 | 0 | 0 | -20971.7044 | -20971.7044 | 11 | 0 | 0 | 11 | 0 | 0 | 0 | 0
[85 empty] | 12 | 0 | 0 | 12 | 0 | 0 | 0 | 0 | 12 | 0 | 0 | 12 | 0 | 0 | 0 | 0 | 12 | 0 | 0 | 12 | 0 | 0 | 0 | 0 | 12 | 0 | 0 | 12 | 0 | 0 | 0 | 0 | 12 | 12458.1003 | 208303.4866 | 12 | 14110.2051 | 109163.7853 | -99139.7013 | -99139.7013 | 12 | 0 | 64165.1973 | 12 | 0 | 44121.5045 | -20043.6928 | -20043.6928
[85 empty] | 13 | 0 | 0 | 13 | 0 | 0 | 0 | 0 | 13 | 0 | 0 | 13 | 0 | 0 | 0 | 0 | 13 | 0 | 0 | 13 | 0 | 0 | 0 | 0 | 13 | 0 | 0 | 13 | 0 | 0 | 0 | 0 | 13 | 4581.5873 | 25553.2917 | 13 | 8721.9153 | 8721.9153 | -16831.3763 | -16831.3763 | 13 | 0 | 0 | 13 | 0 | 0 | 0 | 0
[85 empty] | 14 | 125699.6671 | 125699.6671 | 14 | 115842.6084 | 115842.6084 | -9857.0587 | -9857.0587 | 14 | 0 | 0 | 14 | 0 | 0 | 0 | 0 | 14 | 423396.8584 | 423396.8584 | 14 | 377683.766 | 377683.766 | -45713.0924 | -45713.0924 | 14 | 1036945.5408 | 1036945.5408 | 14 | 892273.5987 | 892273.5987 | -144671.9421 | -144671.9421 | 14 | 43218.0153 | 71926.833 | 14 | 255349.6356 | 272504.4999 | 200577.6669 | 200577.6669 | 14 | 0 | 536.0379 | 14 | 0 | 69.1662 | -466.8718 | -466.8718
[85 empty] | 15 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 15 | 0 | 59431.5106 | 15 | 0 | 0 | -59431.5106 | -59431.5106 | 15 | 0 | 0 | 15 | 0 | 0 | 0 | 0
[85 empty] | 16 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 16 | 5317.6313 | 26289.3356 | 16 | 6448.1164 | 6448.1164 | -19841.2192 | -19841.2192 | 16 | 15787.1382 | 16323.1762 | 16 | 8760.71 | 8829.8761 | -7493.3 | -7493.3
[85 empty] | 17 | 0 | 0 | 17 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 17 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 17 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 17 | 0 | 0 | 0 | 0 | 17 | 0 | 20971.7044 | 17 | 0 | 0 | -20971.7044 | -20971.7044 | 17 | 0 | 0 | 17 | 0 | 0 | 0 | 0
[16 empty] | Scroll down to row 60 for space by space analysis; scroll right for 40 year cost tabulations by building type | [68 empty] | 18 | 0 | 0 | 18 | 0 | 0 | 0 | 0 | 18 | 11818980.9231 | 11818980.9231 | 18 | 10892165.5068 | 10892165.5068 | -926815.4163 | -926815.4163 | 18 | 0 | 0 | 18 | 0 | 0 | 0 | 0 | 18 | 0 | 0 | 18 | 0 | 0 | 0 | 0 | 18 | 0 | 224461.0299 | 18 | 0 | 116613.1279 | -107847.902 | -107847.902 | 18 | 0 | 64165.1973 | 18 | 0 | 44121.5045 | -20043.6928 | -20043.6928
[85 empty] | 19 | 0 | 0 | 19 | 0 | 0 | 0 | 0 | 19 | 0 | 0 | 19 | 0 | 0 | 0 | 0 | 19 | 0 | 0 | 19 | 0 | 0 | 0 | 0 | 19 | 0 | 0 | 19 | 0 | 0 | 0 | 0 | 19 | 0 | 20971.7044 | 19 | 0 | 0 | -20971.7044 | -20971.7044 | 19 | 0 | 0 | 19 | 0 | 0 | 0 | 0
[85 empty] | 20 | 0 | 0 | 20 | 0 | 0 | 0 | 0 | 20 | 0 | 0 | 20 | 0 | 0 | 0 | 0 | 20 | 0 | 17.4203 | 20 | 0 | 0 | -17.4203 | -17.4203 | 20 | 0 | 2297.3255 | 20 | 0 | 0 | -2297.3255 | -2297.3255 | 20 | 0 | 21205.1429 | 20 | 0 | 0 | -21205.1429 | -21205.1429 | 20 | 391.6827 | 927.7206 | 20 | 1398.8667 | 1468.0329 | 540.3123 | 540.3123
[85 empty] | 21 | 0 | 0 | 21 | 0 | 0 | 0 | 0 | 21 | 0 | 0 | 21 | 0 | 0 | 0 | 0 | 21 | 0 | 0 | 21 | 0 | 0 | 0 | 0 | 21 | 0 | 0 | 21 | 0 | 0 | 0 | 0 | 21 | 0 | 66935.1855 | 21 | 0 | 17154.8643 | -49780.3212 | -49780.3212 | 21 | 0 | 0 | 21 | 0 | 0 | 0 | 0
[85 empty] | 22 | 0 | 0 | 22 | 0 | 0 | 0 | 0 | 22 | 0 | 0 | 22 | 0 | 0 | 0 | 0 | 22 | 0 | 0 | 22 | 0 | 0 | 0 | 0 | 22 | 0 | 0 | 22 | 0 | 0 | 0 | 0 | 22 | 0 | 20971.7044 | 22 | 0 | 0 | -20971.7044 | -20971.7044 | 22 | 0 | 536.0379 | 22 | 0 | 69.1662 | -466.8718 | -466.8718
[85 empty] | 23 | 0 | 0 | 23 | 0 | 0 | 0 | 0 | 23 | 0 | 0 | 23 | 0 | 0 | 0 | 0 | 23 | 0 | 0 | 23 | 0 | 0 | 0 | 0 | 23 | 0 | 0 | 23 | 0 | 0 | 0 | 0 | 23 | 0 | 20971.7044 | 23 | 0 | 0 | -20971.7044 | -20971.7044 | 23 | 0 | 0 | 23 | 0 | 0 | 0 | 0
[85 empty] | 24 | 0 | 0 | 24 | 0 | 0 | 0 | 0 | 24 | 0 | 0 | 24 | 0 | 0 | 0 | 0 | 24 | 0 | 0 | 24 | 0 | 0 | 0 | 0 | 24 | 0 | 0 | 24 | 0 | 0 | 0 | 0 | 24 | 12009.7983 | 220313.2849 | 24 | 9004.9896 | 118168.7748 | -102144.5101 | -102144.5101 | 24 | 0 | 64165.1973 | 24 | 0 | 44121.5045 | -20043.6928 | -20043.6928
[85 empty] | 25 | 0 | 0 | 25 | 0 | 0 | 0 | 0 | 25 | 0 | 0 | 25 | 0 | 0 | 0 | 0 | 25 | 0 | 0 | 25 | 0 | 0 | 0 | 0 | 25 | 0 | 0 | 25 | 0 | 0 | 0 | 0 | 25 | 0 | 21205.1429 | 25 | 0 | 0 | -21205.1429 | -21205.1429 | 25 | 0 | 0 | 25 | 0 | 0 | 0 | 0
[85 empty] | 26 | 0 | 0 | 26 | 0 | 0 | 0 | 0 | 26 | 0 | 0 | 26 | 0 | 0 | 0 | 0 | 26 | 0 | 0 | 26 | 0 | 0 | 0 | 0 | 26 | 0 | 0 | 26 | 0 | 0 | 0 | 0 | 26 | 0 | 25553.2917 | 26 | 0 | 8721.9153 | -16831.3763 | -16831.3763 | 26 | 0 | 536.0379 | 26 | 0 | 69.1662 | -466.8718 | -466.8718
[85 empty] | 27 | 0 | 0 | 27 | 0 | 0 | 0 | 0 | 27 | 0 | 0 | 27 | 0 | 0 | 0 | 0 | 27 | 0 | 0 | 27 | 0 | 0 | 0 | 0 | 27 | 0 | 0 | 27 | 0 | 0 | 0 | 0 | 27 | 0 | 87813.7157 | 27 | 0 | 21559.5477 | -66254.168 | -66254.168 | 27 | 0 | 0 | 27 | 0 | 0 | 0 | 0
[85 empty] | 28 | 0 | 125699.6671 | 28 | 0 | 115842.6084 | -9857.0587 | -9857.0587 | 28 | 0 | 0 | 28 | 0 | 0 | 0 | 0 | 28 | 0 | 423396.8584 | 28 | 0 | 377683.766 | -45713.0924 | -45713.0924 | 28 | 0 | 1036945.5408 | 28 | 0 | 892273.5987 | -144671.9421 | -144671.9421 | 28 | 0 | 71926.833 | 28 | 0 | 272504.4999 | 200577.6669 | 200577.6669 | 28 | 0 | 536.0379 | 28 | 0 | 69.1662 | -466.8718 | -466.8718
[85 empty] | 29 | 0 | 0 | 29 | 0 | 0 | 0 | 0 | 29 | 0 | 0 | 29 | 0 | 0 | 0 | 0 | 29 | 0 | 0 | 29 | 0 | 0 | 0 | 0 | 29 | 0 | 0 | 29 | 0 | 0 | 0 | 0 | 29 | 0 | 20971.7044 | 29 | 0 | 0 | -20971.7044 | -20971.7044 | 29 | 0 | 0 | 29 | 0 | 0 | 0 | 0
[16 empty] | Scroll down to row 60 for space by space analysis; scroll right for 40 year cost tabulations by building type | [68 empty] | 30 | 0 | 0 | 30 | 0 | 0 | 8448.9075 | 0 | 30 | 0 | 0 | 30 | 0 | 0 | 308938.4721 | 0 | 30 | 0 | 17.4203 | 30 | 0 | 0 | 39182.6506 | -17.4203 | 30 | 0 | 2297.3255 | 30 | 0 | 0 | 124004.5218 | -2297.3255 | 30 | 0 | 196078.8248 | 30 | 0 | 95053.5802 | -185430.1416 | -101025.2446 | 30 | 0 | 64165.1973 | 30 | 0 | 44121.5045 | 374.7115 | -20043.6928
[85 empty] | 31 | 0 | 0 | 31 | 0 | 0 |  | 0 | 31 | 0 | 0 | 31 | 0 | 0 |  | 0 | 31 | 0 | 0 | 31 | 0 | 0 |  | 0 | 31 | 0 | 0 | 31 | 0 | 0 |  | 0 | 31 | 0 | 20971.7044 | 31 | 0 | 0 |  | -20971.7044 | 31 | 0 | 0 | 31 | 0 | 0 |  | 0
[85 empty] | 32 | 0 | 0 | 32 | 0 | 0 |  | 0 | 32 | 0 | 0 | 32 | 0 | 0 |  | 0 | 32 | 0 | 0 | 32 | 0 | 0 |  | 0 | 32 | 0 | 0 | 32 | 0 | 0 |  | 0 | 32 | 0 | 26289.3356 | 32 | 0 | 6448.1164 |  | -19841.2192 | 32 | 0 | 16323.1762 | 32 | 0 | 8829.8761 |  | -7493.3
[85 empty] | 33 | 0 | 0 | 33 | 0 | 0 |  | 0 | 33 | 0 | 0 | 33 | 0 | 0 |  | 0 | 33 | 0 | 0 | 33 | 0 | 0 |  | 0 | 33 | 0 | 0 | 33 | 0 | 0 |  | 0 | 33 | 0 | 59198.0721 | 33 | 0 | 0 |  | -59198.0721 | 33 | 0 | 0 | 33 | 0 | 0 |  | 0
[85 empty] | 34 | 0 | 0 | 34 | 0 | 0 |  | 0 | 34 | 0 | 0 | 34 | 0 | 0 |  | 0 | 34 | 0 | 0 | 34 | 0 | 0 |  | 0 | 34 | 0 | 0 | 34 | 0 | 0 |  | 0 | 34 | 0 | 20971.7044 | 34 | 0 | 0 |  | -20971.7044 | 34 | 0 | 536.0379 | 34 | 0 | 69.1662 |  | -466.8718
[85 empty] | 35 | 0 | 0 | 35 | 0 | 0 |  | 0 | 35 | 0 | 0 | 35 | 0 | 0 |  | 0 | 35 | 0 | 0 | 35 | 0 | 0 |  | 0 | 35 | 0 | 0 | 35 | 0 | 0 |  | 0 | 35 | 0 | 28942.2563 | 35 | 0 | 17154.8643 |  | -11787.392 | 35 | 0 | 0 | 35 | 0 | 0 |  | 0
[85 empty] | 36 | 0 | 0 | 36 | 0 | 0 |  | 0 | 36 | 0 | 11818980.9231 | 36 | 0 | 10892165.5068 |  | -926815.4163 | 36 | 0 | 0 | 36 | 0 | 0 |  | 0 | 36 | 0 | 0 | 36 | 0 | 0 |  | 0 | 36 | 0 | 236919.1302 | 36 | 0 | 130723.333 |  | -106195.7972 | 36 | 0 | 64165.1973 | 36 | 0 | 44121.5045 |  | -20043.6928
[85 empty] | 37 | 0 | 0 | 37 | 0 | 0 |  | 0 | 37 | 0 | 0 | 37 | 0 | 0 |  | 0 | 37 | 0 | 0 | 37 | 0 | 0 |  | 0 | 37 | 0 | 0 | 37 | 0 | 0 |  | 0 | 37 | 0 | 20971.7044 | 37 | 0 | 0 |  | -20971.7044 | 37 | 0 | 0 | 37 | 0 | 0 |  | 0
[85 empty] | 38 | 0 | 0 | 38 | 0 | 0 |  | 0 | 38 | 0 | 0 | 38 | 0 | 0 |  | 0 | 38 | 0 | 0 | 38 | 0 | 0 |  | 0 | 38 | 0 | 0 | 38 | 0 | 0 |  | 0 | 38 | 0 | 20971.7044 | 38 | 0 | 0 |  | -20971.7044 | 38 | 0 | 536.0379 | 38 | 0 | 69.1662 |  | -466.8718
[85 empty] | 39 | 0 | 0 | 39 | 0 | 0 |  | 0 | 39 | 0 | 0 | 39 | 0 | 0 |  | 0 | 39 | 0 | 0 | 39 | 0 | 0 |  | 0 | 39 | 0 | 0 | 39 | 0 | 0 |  | 0 | 39 | 0 | 63779.6594 | 39 | 0 | 8721.9153 |  | -55057.7441 | 39 | 0 | 0 | 39 | 0 | 0 |  | 0
[85 empty] | 40 | 0 | 0 | 40 | 0 | 0 |  | 1408.1512 | 40 | 0 | 0 | 40 | 0 | 0 |  | 720856.4349 | 40 | 0 | 0 | 40 | 0 | 0 |  | 6530.4418 | 40 | 0 | 0 | 40 | 0 | 0 |  | 20667.4203 | 40 | 0 | 0 | 40 | 0 | 0 |  | 5786.6892 | 40 | 0 | 0 | 40 | 0 | 0 |  | 10038.8212
[85 empty] | Residual Year 30 |  | -107742.5718 | Residual Year 30 |  | -99293.6643 |  | 8448.9075 | Residual Year 30 |  | -3939660.3077 | Residual Year 30 |  | -3630721.8356 |  | 308938.4721 | Residual Year 30 |  | -362911.5929 | Residual Year 30 |  | -323728.9423 |  | 39182.6506 | Residual Year 30 |  | -888810.4635 | Residual Year 30 |  | -764805.9417 |  | 124004.5218 | Residual Year 30 |  | -80720.5893 | Residual Year 30 |  | -266150.7309 |  | -185430.1416 | Residual Year 30 |  | -2169.2336 | Residual Year 30 |  | -1794.5221 |  | 374.7115
[85 empty] | Residual Year 40 |  | -17957.0953 | Residual Year 40 |  | -16548.9441 |  | 1408.1512 | Residual Year 40 |  | -9192540.718 | Residual Year 40 |  | -8471684.2831 |  | 720856.4349 | Residual Year 40 |  | -60485.2655 | Residual Year 40 |  | -53954.8237 |  | 6530.4418 | Residual Year 40 |  | -148135.0773 | Residual Year 40 |  | -127467.657 |  | 20667.4203 | Residual Year 40 |  | -114512.1751 | Residual Year 40 |  | -108725.4859 |  | 5786.6892 | Residual Year 40 |  | -29103.2889 | Residual Year 40 |  | -19064.4678 |  | 10038.8212
Scroll down to row 60 for space by space analysis; scroll right for 40 year cost tabulations by building type
[16 empty] | Col22 | LPD2010 | Fixture ID Numbers | Col25 | area2010 | Col27 | LPD2013 | Col29 | Col30 | area2013 | Col32 | Col33 | Col34 | Col35 | Col36 | Mat2010 | Col38 | Col39 | Lab2010 | Col41 | Col42 | Col43 | Col44 | Tot2010 | Col46 | Col47 | Col48 | Col49 | Col50 | Col51 | Col52 | Col53 | Col54 | Col55 | Col56 | Rep2010 | Col58 | Mat2013 | Col60 | Col61 | Lab2013 | Col63 | Col64 | Col65 | Col66 | Tot2013 | Col68 | Col69 | Col70 | Col71 | Col72 | Col73 | Col74 | Col75 | Col76 | Col77 | Col78 | Repl2013 | Incremental | Repl | Col82 | Proto | Space | Col85 | Col86 | Col87 | Col88 | Col89 | Col90
[16 empty] | 90.1-2019 |  |  |  |  | 90.1-2022 | [8 empty] | 90.1-2019 Baseline Costs - without implementation of the addenda. | [21 empty] | 90.1-2022 - costs with addendum | [21 empty] | Incremental Costs | Incremental Costs
|  | Prototypes Affected (X) | [5 empty] | Not Used | [5 empty] | Name of Item | [11 empty] | 4510 | 4345 |  |  | New Construction Costs | [9 empty] | Replacement Costs | [11 empty] | New Construction Costs | [9 empty] | Replacement Costs
90.1-2019 Lookup | 90.1-2022 Lookup | Small Office | Large Office | Standalone Retail | Primary School | Small Hotel | Mid-rise Apartment | [5 empty] | Not Used | Interior Lighting Power Density | Not Used | Costs to provide lighting fixtures, lamps and ballasts to meet space by space lighting power density (LPD) maximum allowed LPD values under 90.1-2019. Fixtures, lamps and ballasts and quantities defined from 90.1 development interior lighting models and additional input from 90.1 Lighting Subcommittee. Costs are for equipment etc. at today's prices that just meet the 90.1-2019 requirements. Costs by 90.1-2019 Prototype and Lighting Space Type | 90.1-2019 Allowed Maximum LPD W/ft2 | Fixture ID Numbers | Annual Full Load Equivalent Operating Hours for Space Type Lamp Life for Fixtures (Used to Calculate Replacement Life) | Area of Space Type In Prototype Models | Costs to provide lighting fixtures, lamps and ballasts to meet space by space maximum allowed LPD values under 90.1-2022 Table 9.6.1. Fixtures, lamps and ballasts and quantities defined from 90.1 development interior lighting models and additional input from 90.1 Lighting Subcommittee. Costs by 90.1-2022 Prototype and Lighting Space Type | 90.1-2022 Allowed Maximum LPD W/ft2 | Fixture ID Numbers | Annual Full Load Equivalent (BLE) Operating Hours | Area of Space Type, ft2 | LPA |  |  |  | Material Cost/ft2 | Material Subtotal Cost/ft2 × area for space type | Labor Crew Type Not Used | Labor Cost/ft2 | Labor Subtotal Cost/ft2 × Area | Construction Equipment Subtotal | Cost Adjustments | Not Used | Not Used | Total | Replacement Life (hours of operation/ component life) | Replacement Period (costs assigned to a 1 year period) | Material Cost/ft2 | Material Subtotal Cost/ft2 × area for space type | Labor Crew Type Not Used | Labor Cost/ft2 | Labor Subtotal Cost/ft2 × Area | Construction Equipment Subtotal | Cost Adjustments (with added replacement labor hours) | Not Used | Subtotal | Total (adjusted for actual quantity of replacements in replacement period) | Material Cost/ft2 | Material Subtotal Cost/ft2 × area for space type | Labor Crew Type Not Used | Labor Cost/ft2 | Labor Subtotal Cost/ft2 × Area | Construction Equipment Subtotal | Cost Adjustments | Not Used | Not Used | Total | Replacement Life (hours of operation/ component life) | Replacement Period (costs assigned to a 1 year period) | Material Cost/ft2 | Material Subtotal Cost/ft2 × area for space type | Labor Crew Type Not Used | Labor Cost/ft2 | Labor Subtotal Cost/ft2 × Area | Construction Equipment Subtotal | Cost Adjustments (with added replacement labor hours) | Incremental Added Design with OH&P | Subtotal | Total (adjusted for actual quantity of replacements in replacement period) | New Construction Costs 90.1-2022 minus 90.1-2019 | Replacement Costs 90.1-2022 minus 90.1-2019
Small Office |  | X | [5 empty] | X | X | X | X | X |  | Small _Office_Interior_Lighting_LPD |  | Small Office |  |  | 3642 |  | Small Office |  |  | 3642
Office-BLDG-SO | Office-BLDG-SO | X | [13 empty] | Office-BLDG-SO | 0.79 |  | 3642 | 5500 | Office-BLDG-SO | 0.64 |  | 3642 | 5500 | 110.2926 |  | 101.1494 | [45 empty] | -10159.8584 | -33.968 |  | SmOfc | Office-BLDG-SO |  |  | Office-BLDG-SO | Office-BLDG-SO
Office-BLDG-SO735 | Office-BLDG-SOID701 | X | [13 empty] | replacement costs shown are for lamps |  | 735 |  | 5500 |  |  | ID701 |  | 5500 | 105.6579 | 52.0548 | 93.8666 | 58.5938 | 12.8649 | 70756.9789 |  | 1.5489 | 8518.8263 |  | 43694.7886 |  |  | 122970.5938 | 13.7287 | 14 | 0.0073 | 40.15 |  | 0.011814 | 64.9796 |  | 185.3026 |  | 290.4322 | 296.1712 | 11.4284 | 62855.936 |  | 1.376 | 7568.1408 |  | 38816.1773 |  |  | 109240.2541 | 13.7287 | 14 | 0.005632 | 30.976 |  | 0.010496 | 57.728 |  | 161.5658 |  | 250.2698 | 255.2152 | -13730.3397 |  | -40.956 | SmOfc | Office-BLDG-SO |  |  | Office-BLDG-SO735 | Office-BLDG-SOID701
Office-BLDG-SO0 | Office-BLDG-SO0 | X | [15 empty] | 0 |  | 5500 |  |  | 0 |  | 5500 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0 |  | 0 | SmOfc | Office-BLDG-SO |  |  | Office-BLDG-SO0 | Office-BLDG-SO0
Office-BLDG-SO0 | Office-BLDG-SO0 | X | [15 empty] | 0 |  | 5500 |  |  | 0 |  | 5500 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0 |  | 0 | SmOfc | Office-BLDG-SO |  |  | Office-BLDG-SO0 | Office-BLDG-SO0
Office-BLDG-SO703 | Office-BLDG-SOWW714 | X | [15 empty] | 703 |  | 5500 |  |  | WW714 |  | 5500 | 4.6347 | 1186.7089 | 7.2828 | 755.2085 | 0.64864 | 3567.5347 |  | 0.082918 | 456.0512 |  | 2228.6914 |  |  | 6252.2773 | 13.7287 | 14 | 0.000632 | 3.476 |  | 0.00051824 | 2.8503 |  | 9.2453 |  | 15.5717 | 15.8794 | 1.019 | 5604.6654 |  | 0.1303 | 716.6234 |  | 3501.4697 |  |  | 9822.7586 | 13.7287 | 14 | 0.000768 | 4.224 |  | 0.00081434 | 4.4789 |  | 13.7213 |  | 22.4242 | 22.8673 | 3570.4813 |  | 6.988 | SmOfc | Office-BLDG-SO |  |  | Office-BLDG-SO703 | Office-BLDG-SOWW714
Office-BLDG-SO735 | Office-BLDG-SOID701 | X | [13 empty] | ballast replacement |  | 735 |  | 5500 |  |  | ID701 |  | 5500 | 65.7 |  | 55.7568 | [11 empty] | 13.7287 | 14 | 9.6432 | 53037.6217 |  | 1.5489 | 8518.8263 |  | 55414.1837 |  | 116970.6317 | 119281.9713 | [10 empty] | 13.7287 | 14 | 8.567 | 47118.72 |  | 1.376 | 7568.1408 |  | 49230.062 |  | 103916.9228 | 105970.3212 | 0 | -9823.0907 | -13311.6501 | SmOfc | Office-BLDG-SO |  |  | Office-BLDG-SO735 | Office-BLDG-SOID701
Office-BLDG-SO0 | Office-BLDG-SO0 | X | [15 empty] | 0 |  | 5500 |  |  | 0 |  | 5500 | 1e-07 |  | 1e-05 | [11 empty] | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | [10 empty] | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0 |  | 0 | SmOfc | Office-BLDG-SO |  |  | Office-BLDG-SO0 | Office-BLDG-SO0
Office-BLDG-SO0 | Office-BLDG-SO0 | X | [15 empty] | 0 |  | 5500 |  |  | 0 |  | 5500 | 1e-07 |  | 1e-05 | [11 empty] | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | [10 empty] | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0 |  | 0 | SmOfc | Office-BLDG-SO |  |  | Office-BLDG-SO0 | Office-BLDG-SO0
Office-BLDG-SO703 | Office-BLDG-SOWW714 | X | [15 empty] | 703 |  | 5500 |  |  | WW714 |  | 5500 | 3.9816 |  | 6.2899 | [11 empty] | 13.7287 | 14 | 0.48601 | 2673.044 |  | 0.082918 | 456.0512 |  | 2858.2403 |  | 5987.3355 | 6105.6452 | [10 empty] | 13.7287 | 14 | 0.7637 | 4200.331 |  | 0.1303 | 716.6234 |  | 4491.3422 |  | 9408.2967 | 9594.2047 | 0 |  | 3488.5594 | SmOfc | Office-BLDG-SO |  |  | Office-BLDG-SO703 | Office-BLDG-SOWW714
Office - Open Plan (Including Other)-whole | Office - Open Plan (Including Other)-whole | 0 | [13 empty] | Office - Open Plan (Including Other)-whole-small | 0.81 |  | 3642 | 1100 | Office - Open Plan (Including Other)-whole | 0.61 |  | 3642 | 1100 | 33.3204 |  | 19.6149 | [45 empty] | -1158.5799 | -33.3521 |  |  | Office - Open Plan (Including Other)-whole-small |  |  | Office - Open Plan (Including Other)-whole-small | Office - Open Plan (Including Other)-whole-small
Office - Open Plan (Including Other)735-whole-Small | Office - Open Plan (Including Other)id701-whole-Small | 0 | [13 empty] | replacement costs shown are for lamps |  | 735 |  | 1100 |  |  | ID701 |  | 1100 | 14.4737 | 76 | 18.6667 | 58.9286 | 8.8116 | 9692.7368 |  | 1.0609 | 1166.9625 |  | 5985.5875 |  |  | 16845.2868 | 13.7287 | 14 | 0.005 | 5.5 |  | 0.0080921 | 8.9013 |  | 25.3839 |  | 39.7852 | 40.5714 | 11.3634 | 12499.76 |  | 1.3682 | 1505.028 |  | 7719.1262 |  |  | 21723.9142 | 13.7287 | 14 | 0.0056 | 6.16 |  | 0.010436 | 11.48 |  | 32.1296 |  | 49.7696 | 50.753 | 4878.6273 |  |  |  | Office - Open Plan (Including Other)-whole-small |  |  | Office - Open Plan (Including Other)-whole-small735 | Office - Open Plan (Including Other)-whole-smallID701
Office - Open Plan (Including Other)739-whole-Small | Office - Open Plan (Including Other)0-whole-Small | 0 | [15 empty] | 739 |  | 1100 |  |  | 0 |  | 1100 | 16.5 | 66.6667 | 0 | 0 | 1.9215 | 2113.65 |  | 0.45203 | 497.2275 |  | 1539.6247 |  |  | 4150.5022 | 13.7287 | 14 | 0.0015 | 1.65 |  | 0.009225 | 10.1475 |  | 25.9281 |  | 37.7256 | 38.4711 | 0 | 0 |  | 0 | 0 |  | 0 |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | -4150.5022 |  |  |  | Office - Open Plan (Including Other)-whole-small |  |  | Office - Open Plan (Including Other)-whole-small739 | Office - Open Plan (Including Other)-whole-small0
Office - Open Plan (Including Other)0-whole-Small | Office - Open Plan (Including Other)0-whole-Small | 0 | [15 empty] | 0 |  | 1100 |  |  | 0 |  | 1100 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0 |  |  |  | Office - Open Plan (Including Other)-whole-small |  |  | Office - Open Plan (Including Other)-whole-small0 | Office - Open Plan (Including Other)-whole-small0
Office - Open Plan (Including Other)703-whole-Small | Office - Open Plan (Including Other)ww714-whole-Small | 0 | [15 empty] | 703 |  | 1100 |  |  | WW714 |  | 1100 | 2.3467 | 468.75 | 0.94828 | 1160.0002 | 1.6421 | 1806.3467 |  | 0.20992 | 230.912 |  | 1128.4513 |  |  | 3165.71 | 13.7287 | 14 | 0.0016 | 1.76 |  | 0.001312 | 1.4432 |  | 4.6812 |  | 7.8844 | 8.0402 | 0.66343 | 729.7741 |  | 0.084828 | 93.3103 |  | 455.9205 |  |  | 1279.005 | 13.7287 | 14 | 0.0005 | 0.55 |  | 0.00053017 | 0.58319 |  | 1.7866 |  | 2.9198 | 2.9775 | -1886.705 |  |  |  | Office - Open Plan (Including Other)-whole-small |  |  | Office - Open Plan (Including Other)-whole-small703 | Office - Open Plan (Including Other)-whole-smallWW714
Office - Open Plan (Including Other)735-whole-Small | Office - Open Plan (Including Other)id701-whole-Small | 0 | [13 empty] | ballast replacement |  | 735 |  | 1100 |  |  | ID701 |  | 1100 | 45 |  | 55.44 | [11 empty] | 13.7287 | 14 | 6.6049 | 7265.4276 |  | 1.0609 | 1166.9625 |  | 7590.9841 |  | 16023.3742 | 16339.9961 | [10 empty] | 13.7287 | 14 | 8.5184 | 9370.2 |  | 1.3682 | 1505.028 |  | 9790.0691 |  | 20665.2971 | 21073.6434 | 0 | -1525.041 |  |  | Office - Open Plan (Including Other)-whole-small |  |  | Office - Open Plan (Including Other)-whole-small735 | Office - Open Plan (Including Other)-whole-smallID701
Office - Open Plan (Including Other)739-whole-Small | Office - Open Plan (Including Other)0-whole-Small | 0 | [15 empty] | 739 |  | 1100 |  |  | 0 |  | 1100 | 9.18 |  | 1e-05 | [11 empty] | 13.7287 | 14 | 1.44 | 1584 |  | 0.45203 | 497.2275 |  | 2249.662 |  | 4330.8895 | 4416.4678 | [10 empty] | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0 |  |  |  | Office - Open Plan (Including Other)-whole-small |  |  | Office - Open Plan (Including Other)-whole-small739 | Office - Open Plan (Including Other)-whole-small0
Office - Open Plan (Including Other)0-whole-Small | Office - Open Plan (Including Other)0-whole-Small | 0 | [15 empty] | 0 |  | 1100 |  |  | 0 |  | 1100 | 1e-07 |  | 1e-05 | [11 empty] | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | [10 empty] | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0 |  |  |  | Office - Open Plan (Including Other)-whole-small |  |  | Office - Open Plan (Including Other)-whole-small0 | Office - Open Plan (Including Other)-whole-small0
Office - Open Plan (Including Other)703-whole-Small | Office - Open Plan (Including Other)ww714-whole-Small | 0 | [15 empty] | 703 |  | 1100 |  |  | WW714 |  | 1100 | 10.08 |  | 4.095 | [11 empty] | 13.7287 | 14 | 1.2304 | 1353.44 |  | 0.20992 | 230.912 |  | 1447.2103 |  | 3031.5623 | 3091.4659 | [10 empty] | 13.7287 | 14 | 0.4972 | 546.9181 |  | 0.084828 | 93.3103 |  | 584.8102 |  | 1225.0386 | 1249.2454 | 0 |  |  |  | Office - Open Plan (Including Other)-whole-small |  |  | Office - Open Plan (Including Other)-whole-small703 | Office - Open Plan (Including Other)-whole-smallWW714
Office-Enclosed-whole | Office-Enclosed-whole-small | 0 | [13 empty] | Office-Enclosed-whole-small | 0.878 |  | 3642 | 1595 | Office-Enclosed-whole | 0.74 |  | 3642 | 1595 | 66.6356 |  | 36.8844 | [45 empty] | -8573.4633 |  |  |  | Office-Enclosed-whole-small |  |  | Office-Enclosed-whole-small | Office-Enclosed-whole-small
Office-Enclosed700-whole-Small | Office-Enclosed731-whole-Small | 0 | [13 empty] | lamp replacement |  | 700 |  | 1595 |  |  | TR701 |  | 1595 | 28.3556 | 56.25 | 36.8844 | 43.2433 | 2.4597 | 3923.2747 |  | 1.6498 | 2631.4948 |  | 4507.386 |  |  | 11062.1555 | 13.7287 | 14 | 0.0064 | 10.208 |  | 0.010933 | 17.4387 |  | 49.3605 |  | 77.0072 | 78.5288 | 3.1987 | 5101.8467 |  | 1.4222 | 2268.3891 |  | 4747.6215 |  |  | 12117.8573 | 13.7287 | 14 | 0.0074 | 11.803 |  | 0.014222 | 22.6839 |  | 63.2461 |  | 97.733 | 99.6642 | 1055.7018 | -68.1175 |  |  | Office-Enclosed-whole-small |  |  | Office-Enclosed-whole-small700 | Office-Enclosed-whole-smallTR701
Office-Enclosed739-whole-Small | Office-Enclosed0-whole-small | 0 | [15 empty] | 739 |  | 1595 |  |  | 0 |  | 1595 | 38.28 | 41.6667 | 0 | 0 | 3.0744 | 4903.668 |  | 0.72324 | 1153.5678 |  | 3571.9293 |  |  | 9629.1651 | 13.7287 | 14 | 0.0024 | 3.828 |  | 0.01476 | 23.5422 |  | 60.1532 |  | 87.5234 | 89.2529 | 0 | 0 |  | 0 | 0 |  | 0 |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | -9629.1651 |  |  |  | Office-Enclosed-whole-small |  |  | Office-Enclosed-whole-small739 | Office-Enclosed-whole-small0
Office-Enclosed0-whole-Small | Office-Enclosed0-whole-small | 0 | [15 empty] | 0 |  | 1595 |  |  | 0 |  | 1595 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0 |  |  |  | Office-Enclosed-whole-small |  |  | Office-Enclosed-whole-small0 | Office-Enclosed-whole-small0
Office-Enclosed0-whole-Small | Office-Enclosed0-whole-small | 0 | [15 empty] | 0 |  | 1595 |  |  | 0 |  | 1595 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0 |  |  |  | Office-Enclosed-whole-small |  |  | Office-Enclosed-whole-small0 | Office-Enclosed-whole-small0
Office-Enclosed700-whole-Small | Office-Enclosed731-whole-Small | 0 | [13 empty] | ballast replacement |  | 700 |  | 1595 |  |  | TR701 |  | 1595 | 59.328 |  | 76.59 | [11 empty] | 13.7287 | 14 | 1.84 | 2934.8 |  | 1.6498 | 2631.4948 |  | 8356.8495 |  | 13923.1443 | 14198.2657 | [10 empty] | 13.7287 | 14 | 2.3934 | 3817.5328 |  | 1.4222 | 2268.3891 |  | 8042.5627 |  | 14128.4846 | 14407.6635 | 0 | -10036.8076 |  |  | Office-Enclosed-whole-small |  |  | Office-Enclosed-whole-small700 | Office-Enclosed-whole-smallTR701
Office-Enclosed739-whole-Small | Office-Enclosed0-whole-small | 0 | [15 empty] | 739 |  | 1595 |  |  | 0 |  | 1595 | 14.688 |  | 1e-05 | [11 empty] | 13.7287 | 14 | 2.304 | 3674.88 |  | 0.72324 | 1153.5678 |  | 5219.2158 |  | 10047.6636 | 10246.2054 | [10 empty] | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0 |  |  |  | Office-Enclosed-whole-small |  |  | Office-Enclosed-whole-small739 | Office-Enclosed-whole-small0
Office-Enclosed0-whole-Small | Office-Enclosed0-whole-small | 0 | [15 empty] | 0 |  | 1595 |  |  | 0 |  | 1595 | 1e-07 |  | 1e-05 | [11 empty] | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | [10 empty] | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0 |  |  |  | Office-Enclosed-whole-small |  |  | Office-Enclosed-whole-small0 | Office-Enclosed-whole-small0
Office-Enclosed0-whole-Small | Office-Enclosed0-whole-small | 0 | [15 empty] | 0 |  | 1595 |  |  | 0 |  | 1595 | 1e-07 |  | 1e-05 | [11 empty] | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | [10 empty] | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0 |  |  |  | Office-Enclosed-whole-small |  |  | Office-Enclosed-whole-small0 | Office-Enclosed-whole-small0
Conference/Meeting/Multipurpose | Conference/Meeting/Multipurpose | 0 | [13 empty] | Conference/Meeting/Multipurpose | 1.07 |  | 3642 | 440 | Conference/Meeting/Multipurpose | 0.97 |  | 3642 | 440 | 12.3567 |  | 11.9442 | [45 empty] | -71.854 |  |  |  | Conference/Meeting/Multipurpose |  |  | Conference/Meeting/Multipurpose | Conference/Meeting/Multipurpose
Conference/Meeting/Multipurpose731 | Conference/Meeting/MultipurposeTR704 | 0 | [13 empty] | lamp replacement |  | 731 |  | 440 |  |  | TR704 |  | 440 | 4.95 | 88.8889 | 6.7375 | 65.3061 | 4.302 | 1892.88 |  | 0.90705 | 399.1012 |  | 1334.2145 |  |  | 3626.1957 | 13.7287 | 14 | 0.0045 | 1.98 |  | 0.0069188 | 3.0442 |  | 8.7458 |  | 13.77 | 14.0421 | 2.118 | 931.931 |  | 0.94172 | 414.3562 |  | 867.2263 |  |  | 2213.5135 | 13.7287 | 14 | 0.0049 | 2.156 |  | 0.0094172 | 4.1436 |  | 11.5529 |  | 17.8524 | 18.2052 | -1412.6821 | -245.2878 |  |  | Conference/Meeting/Multipurpose |  |  | Conference/Meeting/Multipurpose731 | Conference/Meeting/MultipurposeTR704
Conference/Meeting/Multipurpose511 | Conference/Meeting/MultipurposeDL702 | 0 | [15 empty] | 511 |  | 440 |  |  | DL702 |  | 440 | 3.2267 | 136.3636 | 2.9333 | 150.0001 | 0.42871 | 188.6309 |  | 0.451 | 198.44 |  | 286.1508 |  |  | 673.2217 | 1.1532 | 2 | 0.15679 | 68.9861 |  | 0.02134 | 9.3896 |  | 67.9361 |  | 146.3118 | 253.7465 | 1.2021 | 528.9363 |  | 0.41 | 180.4 |  | 439.326 |  |  | 1148.6623 | 13.7287 | 14 | 0.0016 | 0.704 |  | 0.0041 | 1.804 |  | 4.877 |  | 7.385 | 7.5309 | 475.4406 |  |  |  | Conference/Meeting/Multipurpose |  |  | Conference/Meeting/Multipurpose511 | Conference/Meeting/MultipurposeDL702
Conference/Meeting/Multipurpose0 | Conference/Meeting/Multipurpose0 | 0 | [15 empty] | 0 |  | 440 |  |  | 0 |  | 440 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0 |  |  |  | Conference/Meeting/Multipurpose |  |  | Conference/Meeting/Multipurpose0 | Conference/Meeting/Multipurpose0
Conference/Meeting/Multipurpose727-1 | Conference/Meeting/MultipurposeWW704 | 0 | [15 empty] | 727-1 |  | 440 |  |  | WW704 |  | 440 | 4.18 | 105.2632 | 2.2733 | 193.5484 | 2.5669 | 1129.436 |  | 0.58425 | 257.07 |  | 814.3761 |  |  | 2200.8821 | 13.7287 | 14 | 0.0019 | 0.836 |  | 0.0058425 | 2.5707 |  | 6.8407 |  | 10.2474 | 10.4499 | 3.9763 | 1749.5573 |  | 0.5084 | 223.696 |  | 1093.0163 |  |  | 3066.2696 | 13.7287 | 14 | 0.0031 | 1.364 |  | 0.0031775 | 1.3981 |  | 4.3128 |  | 7.0749 | 7.2147 | 865.3875 |  |  |  | Conference/Meeting/Multipurpose |  |  | Conference/Meeting/Multipurpose727-1 | Conference/Meeting/MultipurposeWW704
Conference/Meeting/Multipurpose731 | Conference/Meeting/MultipurposeTR704 | 0 | [13 empty] | ballast replacement |  | 731 |  | 440 |  |  | TR704 |  | 440 | 35.64 |  | 48.951 | [11 empty] | 13.7287 | 14 | 3.2231 | 1418.175 |  | 0.90705 | 399.1012 |  | 1901.3089 |  | 3718.5851 | 3792.0644 | [10 empty] | 13.7287 | 14 | 1.5848 | 697.3312 |  | 0.94172 | 414.3562 |  | 1469.0981 |  | 2580.7856 | 2631.782 | 0 | 806.6108 |  |  | Conference/Meeting/Multipurpose |  |  | Conference/Meeting/Multipurpose731 | Conference/Meeting/MultipurposeTR704
Conference/Meeting/Multipurpose511 | Conference/Meeting/MultipurposeDL702 | 0 | [15 empty] | 511 |  | 440 |  |  | DL702 |  | 440 | 2.4651 |  | 8.64 | [11 empty] | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | [10 empty] | 13.7287 | 14 | 0.9004 | 396.1742 |  | 0.41 | 180.4 |  | 699.9123 |  | 1276.4865 | 1301.7099 | 0 |  |  |  | Conference/Meeting/Multipurpose |  |  | Conference/Meeting/Multipurpose511 | Conference/Meeting/MultipurposeDL702
Conference/Meeting/Multipurpose0 | Conference/Meeting/Multipurpose0 | 0 | [15 empty] | 0 |  | 440 |  |  | 0 |  | 440 | 1e-07 |  | 1e-05 | [11 empty] | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | [10 empty] | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0 |  |  |  | Conference/Meeting/Multipurpose |  |  | Conference/Meeting/Multipurpose0 | Conference/Meeting/Multipurpose0
Conference/Meeting/Multipurpose727-1 | Conference/Meeting/MultipurposeWW704 | 0 | [15 empty] | 727-1 |  | 440 |  |  | WW704 |  | 440 | 17.1 |  | 13.113 | [11 empty] | 13.7287 | 14 | 1.9238 | 846.45 |  | 0.58425 | 257.07 |  | 1181.012 |  | 2284.532 | 2329.6743 | [10 empty] | 13.7287 | 14 | 2.9799 | 1311.145 |  | 0.5084 | 223.696 |  | 1401.985 |  | 2936.826 | 2994.8576 | 0 |  |  |  | Conference/Meeting/Multipurpose |  |  | Conference/Meeting/Multipurpose727-1 | Conference/Meeting/MultipurposeWW704
Corridor/Transition | Corridor/Transition | 0 | [13 empty] | Corridor/Transition | 0.66 |  | 3642 | 660 | Corridor/Transition | 0.41 |  | 3642 | 660 | 23.364 |  | 15.317 | [45 empty] | -3307.7576 |  |  |  | Corridor/Transition |  |  | Corridor/Transition | Corridor/Transition
Corridor/Transition701 | Corridor/TransitionDL706 | 0 | [13 empty] | replacement costs are for lamps |  | 701 |  | 660 |  |  | DL706 |  | 660 | 20.9 | 31.5789 | 13.2 | 50 | 5.2271 | 3449.8961 |  | 1.9475 | 1285.35 |  | 2970.3981 |  |  | 7705.6442 | 13.7287 | 14 | 0.0038 | 2.508 |  | 0.019475 | 12.8535 |  | 33.1146 |  | 48.4761 | 49.4339 | 3.3013 | 2178.8818 |  | 1.23 | 811.8 |  | 1876.0409 |  |  | 4866.7227 | 13.7287 | 14 | 0.0024 | 1.584 |  | 0.0123 | 8.118 |  | 20.9145 |  | 30.6165 | 31.2214 | -2838.9215 | -20.1858 |  |  | Corridor/Transition |  |  | Corridor/Transition701 | Corridor/TransitionDL706
Corridor/Transition0 | Corridor/Transition0 | 0 | [15 empty] | 0 |  | 660 |  |  | 0 |  | 660 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0 |  |  |  | Corridor/Transition |  |  | Corridor/Transition0 | Corridor/Transition0
Corridor/Transition0 | Corridor/Transition0 | 0 | [15 empty] | 0 |  | 660 |  |  | 0 |  | 660 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0 |  |  |  | Corridor/Transition |  |  | Corridor/Transition0 | Corridor/Transition0
Corridor/Transition703 | Corridor/TransitionWW708 | 0 | [15 empty] | 703 |  | 660 |  |  | WW708 |  | 660 | 2.464 | 267.8571 | 2.117 | 311.7648 | 2.8737 | 1896.664 |  | 0.36736 | 242.4576 |  | 1184.8739 |  |  | 3323.9955 | 13.7287 | 14 | 0.0028 | 1.848 |  | 0.002296 | 1.5154 |  | 4.9152 |  | 8.2786 | 8.4422 | 2.4683 | 1629.0805 |  | 0.31562 | 208.3109 |  | 1017.768 |  |  | 2855.1595 | 13.7287 | 14 | 0.0017 | 1.122 |  | 0.0019726 | 1.3019 |  | 3.9196 |  | 6.3436 | 6.4689 | -468.836 |  |  |  | Corridor/Transition |  |  | Corridor/Transition703 | Corridor/TransitionWW708
Corridor/Transition701 | Corridor/TransitionDL706 | 0 | [13 empty] | replacement costs are for ballasts |  | 701 |  | 660 |  |  | DL706 |  | 660 | 23.256 |  | 14.688 | [11 empty] | 13.7287 | 14 | 3.9175 | 2585.5411 |  | 1.9475 | 1285.35 |  | 4832.3573 |  | 8703.2484 | 8875.2245 | [10 empty] | 13.7287 | 14 | 2.4742 | 1632.9733 |  | 1.23 | 811.8 |  | 3052.0151 |  | 5496.7884 | 5605.405 | 0 | -3726.9774 |  |  | Corridor/Transition |  |  | Corridor/Transition701 | Corridor/TransitionDL706
Corridor/Transition0 | Corridor/Transition0 | 0 | [15 empty] | 0 |  | 660 |  |  | 0 |  | 660 | 1e-07 |  | 1e-05 | [11 empty] | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | [10 empty] | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0 |  |  |  | Corridor/Transition |  |  | Corridor/Transition0 | Corridor/Transition0
Corridor/Transition0 | Corridor/Transition0 | 0 | [15 empty] | 0 |  | 660 |  |  | 0 |  | 660 | 1e-07 |  | 1e-05 | [11 empty] | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | [10 empty] | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0 |  |  |  | Corridor/Transition |  |  | Corridor/Transition0 | Corridor/Transition0
Corridor/Transition703 | Corridor/TransitionWW708 | 0 | [15 empty] | 703 |  | 660 |  |  | WW708 |  | 660 | 17.64 |  | 15.147 | [11 empty] | 13.7287 | 14 | 2.1532 | 1421.112 |  | 0.36736 | 242.4576 |  | 1519.5708 |  | 3183.1404 | 3246.0392 | [10 empty] | 13.7287 | 14 | 1.85 | 1220.9689 |  | 0.31562 | 208.3109 |  | 1305.5612 |  | 2734.841 | 2788.8814 | 0 |  |  |  | Corridor/Transition |  |  | Corridor/Transition703 | Corridor/TransitionWW708
Storage | Storage | 0 | [13 empty] | Storage | 0.46 |  | 3642 | 770 | Storage | 0.38 |  | 3642 | 770 | 9.3211 |  | 7.9081 | [45 empty] | -1629.8706 |  |  |  | Storage |  |  | Storage | Storage
Storage738 | StorageLB702 | 0 | [13 empty] | replacement costs are for lamps |  | 738 |  | 770 |  |  | LB702 |  | 770 | 9.3211 | 82.6087 | 7.9081 | 97.3684 | 3.0309 | 2333.8052 |  | 0.70055 | 539.4233 |  | 1690.7264 |  |  | 4563.9549 | 13.7287 | 14 | 0.0046 | 3.542 |  | 0.0074447 | 5.7324 |  | 16.3472 |  | 25.6217 | 26.128 | 1.76 | 1355.2125 |  | 0.59436 | 457.6541 |  | 1121.2178 |  |  | 2934.0843 | 13.7287 | 14 | 0.0038 | 2.926 |  | 0.0063162 | 4.8635 |  | 13.8177 |  | 21.6072 | 22.0342 | -1629.8706 | -4.0938 |  |  | Storage |  |  | Storage738 | StorageLB702
Storage0 | Storage0 | 0 | [15 empty] | 0 |  | 770 |  |  | 0 |  | 770 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0 |  |  |  | Storage |  |  | Storage0 | Storage0
Storage0 | Storage0 | 0 | [15 empty] | 0 |  | 770 |  |  | 0 |  | 770 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0 |  |  |  | Storage |  |  | Storage0 | Storage0
Storage0 | Storage0 | 0 | [15 empty] | 0 |  | 770 |  |  | 0 |  | 770 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0 |  |  |  | Storage |  |  | Storage0 | Storage0
Storage738 | StorageLB702 | 0 | [13 empty] | ballast replacement |  | 738 |  | 770 |  |  | LB702 |  | 770 | 47.61 |  | 35.226 | [11 empty] | 13.7287 | 14 | 2.2697 | 1747.6974 |  | 0.70055 | 539.4233 |  | 2459.644 |  | 4746.7646 | 4840.5607 | [10 empty] | 13.7287 | 14 | 1.3172 | 1014.2149 |  | 0.59436 | 457.6541 |  | 1781.5681 |  | 3253.4371 | 3317.725 | 0 | -1522.8357 |  |  | Storage |  |  | Storage738 | StorageLB702
Storage0 | Storage0 | 0 | [15 empty] | 0 |  | 770 |  |  | 0 |  | 770 | 1e-07 |  | 1e-05 | [11 empty] | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | [10 empty] | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0 |  |  |  | Storage |  |  | Storage0 | Storage0
Storage0 | Storage0 | 0 | [15 empty] | 0 |  | 770 |  |  | 0 |  | 770 | 1e-07 |  | 1e-05 | [11 empty] | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | [10 empty] | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0 |  |  |  | Storage |  |  | Storage0 | Storage0
Storage0 | Storage0 | 0 | [15 empty] | 0 |  | 770 |  |  | 0 |  | 770 | 1e-07 |  | 1e-05 | [11 empty] | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | [10 empty] | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0 |  |  |  | Storage |  |  | Storage0 | Storage0
Restrooms | Restrooms | 0 | [13 empty] | Restrooms | 0.85 |  | 3642 | 220 | Restrooms | 0.63 |  | 3642 | 220 | 6.931 |  | 7.0718 | [45 empty] | -1003.7106 |  |  |  | Restrooms |  |  | Restrooms | Restrooms
Restrooms604 | RestroomsDL709 | 0 | [13 empty] | replacement costs are for lamps |  | 604 |  | 220 |  |  | DL709 |  | 220 | 2.6552 | 82.8571 | 3.894 | 56.4972 | 4.2525 | 935.55 |  | 0.3637 | 80.0136 |  | 546.2367 |  |  | 1561.8003 | 9.8847 | 10 | 0.040431 | 8.8948 |  | 0.065978 | 14.5151 |  | 41.3447 |  | 64.7547 | 65.5101 | 3.5159 | 773.4987 |  | 1.0885 | 239.481 |  | 618.9654 |  |  | 1631.9451 | 13.7287 | 14 | 0.003717 | 0.81774 |  | 0.010885 | 2.3948 |  | 6.3981 |  | 9.6106 | 9.8005 | 70.1448 | -109.0911 |  |  | Restrooms |  |  | Restrooms604 | RestroomsDL709
Restrooms720 | Restrooms0 | 0 | [15 empty] | 720 |  | 220 |  |  | 0 |  | 220 | 2 | 110 | 0 | 0 | 1.5353 | 337.774 |  | 0.55909 | 123 |  | 288.0787 |  |  | 748.8527 | 13.7287 | 14 | 0.002 | 0.44 |  | 0.0055909 | 1.23 |  | 3.2991 |  | 4.9691 | 5.0673 | 0 | 0 |  | 0 | 0 |  | 0 |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | -748.8527 |  |  |  | Restrooms |  |  | Restrooms720 | Restrooms0
Restrooms0 | Restrooms0 | 0 | [15 empty] | 0 |  | 220 |  |  | 0 |  | 220 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0 |  |  |  | Restrooms |  |  | Restrooms0 | Restrooms0
Restrooms534-2 | RestroomsWG701 | 0 | [15 empty] | 534-2 |  | 220 |  |  | WG701 |  | 220 | 2.2759 | 96.6667 | 3.1778 | 69.2308 | 3.9657 | 872.4517 |  | 0.59867 | 131.7076 |  | 564.5158 |  |  | 1568.6751 | 9.8847 | 10 | 0.034655 | 7.6241 |  | 0.056552 | 12.4415 |  | 35.4383 |  | 55.504 | 56.1516 | 2.6025 | 572.5402 |  | 0.88833 | 195.4333 |  | 475.6988 |  |  | 1243.6724 | 13.7287 | 14 | 0.0026 | 0.572 |  | 0.0088833 | 1.9543 |  | 5.1592 |  | 7.6855 | 7.8374 | -325.0027 |  |  |  | Restrooms |  |  | Restrooms534-2 | RestroomsWG701
Restrooms604 | RestroomsDL709 | 0 | [13 empty] | ballast replacement |  | 604 |  | 220 |  |  | DL709 |  | 220 | 24.2393 |  | 28.7696 | [11 empty] | 13.7287 | 14 | 0.36207 | 79.6552 |  | 0.74224 | 163.2931 |  | 451.8265 |  | 694.7748 | 708.5036 | [10 empty] | 13.7287 | 14 | 2.6341 | 579.5107 |  | 1.0885 | 239.481 |  | 964.0429 |  | 1783.0346 | 1818.2673 | 0 | 1053.6014 |  |  | Restrooms |  |  | Restrooms604 | RestroomsDL709
Restrooms720 | Restrooms0 | 0 | [15 empty] | 720 |  | 220 |  |  | 0 |  | 220 | 12.6 |  | 1e-05 | [11 empty] | 13.7287 | 14 | 1.15 | 253.0005 |  | 0.55909 | 123 |  | 466.0617 |  | 842.0622 | 858.7013 | [10 empty] | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0 |  |  |  | Restrooms |  |  | Restrooms720 | Restrooms0
Restrooms0 | Restrooms0 | 0 | [15 empty] | 0 |  | 220 |  |  | 0 |  | 220 | 1e-07 |  | 1e-05 | [11 empty] | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | [10 empty] | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0 |  |  |  | Restrooms |  |  | Restrooms0 | Restrooms0
Restrooms534-2 | RestroomsWG701 | 0 | [15 empty] | 534-2 |  | 220 |  |  | WG701 |  | 220 | 24.3 |  | 24.102 | [11 empty] | 13.7287 | 14 | 0.31034 | 68.2759 |  | 0.63621 | 139.9655 |  | 387.2799 |  | 595.5213 | 607.2888 | [10 empty] | 13.7287 | 14 | 1.9499 | 428.9762 |  | 0.88833 | 195.4333 |  | 758.0998 |  | 1382.5093 | 1409.8277 | 0 |  |  |  | Restrooms |  |  | Restrooms534-2 | RestroomsWG701
Lounge/Recreation - Break room | Lounge/Recreation - Break room | 0 | [13 empty] | Lounge/Recreation - Break room | #N/A |  | 3642 | 110 | Lounge/Recreation - Break room | #N/A |  | 3642 | 110 | 3.3477 |  | 5.5611 | [45 empty] | 143.4181 |  |  |  | #N/A |  |  | #N/A | #N/A
Lounge/Recreation - Breakroom522 | Lounge/Recreation - BreakroomDL707 | 0 | [13 empty] | replacement costs are for lamps |  | 522 |  | 110 |  |  | DL707 |  | 110 | 2.0717 | 53.0973 | 3.85 | 28.5715 | 2.9226 | 321.4812 |  | 1.1583 | 127.4075 |  | 284.1666 |  |  | 733.0554 | 13.7287 | 14 | 0.00339 | 0.3729 |  | 0.011583 | 1.2741 |  | 3.3634 |  | 5.0104 | 5.1094 | 7.1431 | 785.7423 |  | 2.1525 | 236.775 |  | 622.4904 |  |  | 1645.0076 | 13.7287 | 14 | 0.0028 | 0.308 |  | 0.021525 | 2.3678 |  | 5.9997 |  | 8.6755 | 8.8469 | 911.9523 | 4.6602 |  |  | #N/A |  |  | #N/A | #N/A
Lounge/Recreation - Breakroom0 | Lounge/Recreation - Breakroom0 | 0 | [15 empty] | 0 |  | 110 |  |  | 0 |  | 110 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0 |  |  |  | #N/A |  |  | #N/A | #N/A
Lounge/Recreation - Breakroom0 | Lounge/Recreation - Breakroom0 | 0 | [15 empty] | 0 |  | 110 |  |  | 0 |  | 110 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0 |  |  |  | #N/A |  |  | #N/A | #N/A
Lounge/Recreation - Breakroom727-2 | Lounge/Recreation - BreakroomWG702 | 0 | [15 empty] | 727-2 |  | 110 |  |  | WG702 |  | 110 | 1.276 | 86.2069 | 1.7111 | 64.2857 | 7.7749 | 855.239 |  | 0.7134 | 78.474 |  | 504.4909 |  |  | 1438.2039 | 13.7287 | 14 | 0.0029 | 0.319 |  | 0.007134 | 0.78474 |  | 2.1298 |  | 3.2335 | 3.2974 | 2.8026 | 308.2909 |  | 0.95667 | 105.2333 |  | 256.1455 |  |  | 669.6697 | 13.7287 | 14 | 0.0028 | 0.308 |  | 0.0095667 | 1.0523 |  | 2.778 |  | 4.1383 | 4.2201 | -768.5341 |  |  |  | #N/A |  |  | #N/A | #N/A
Lounge/Recreation - Breakroom522 | Lounge/Recreation - BreakroomDL707 | 0 | [13 empty] | ballast replacement |  | 522 |  | 110 |  |  | DL707 |  | 110 | 16.0178 |  | 22.428 | [11 empty] | 0 | 0 | 2.1894 | 240.8313 |  | 1.1583 | 127.4075 |  | 468.9292 |  | 837.1679 | 0 | [10 empty] | 13.7287 | 14 | 5.3552 | 589.0757 |  | 2.1525 | 236.775 |  | 963.6462 |  | 1789.4969 | 1824.8573 | 0 | 1228.1756 |  |  | #N/A |  |  | #N/A | #N/A
Lounge/Recreation - Breakroom0 | Lounge/Recreation - Breakroom0 | 0 | [15 empty] | 0 |  | 110 |  |  | 0 |  | 110 | 1e-07 |  | 1e-05 | [11 empty] | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | [10 empty] | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0 |  |  |  | #N/A |  |  | #N/A | #N/A
Lounge/Recreation - Breakroom0 | Lounge/Recreation - Breakroom0 | 0 | [15 empty] | 0 |  | 110 |  |  | 0 |  | 110 | 1e-07 |  | 1e-05 | [11 empty] | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | [10 empty] | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0 |  |  |  | #N/A |  |  | #N/A | #N/A
Lounge/Recreation - Breakroom727-2 | Lounge/Recreation - BreakroomWG702 | 0 | [15 empty] | 727-2 |  | 110 |  |  | WG702 |  | 110 | 26.1 |  | 22.176 | [11 empty] | 13.7287 | 14 | 5.829 | 641.19 |  | 0.7134 | 78.474 |  | 609.8838 |  | 1329.5478 | 1355.8197 | [10 empty] | 13.7287 | 14 | 2.0999 | 230.9872 |  | 0.95667 | 105.2333 |  | 408.2076 |  | 744.4281 | 759.138 | 0 |  |  |  | #N/A |  |  | #N/A | #N/A
Electrical/Mechanical | Electrical/Mechanical | 0 | [13 empty] | Electrical/Mechanical | 0.43 |  | 3642 | 110 | Electrical/Mechanical | 0.43 |  | 3642 | 110 | 2.8658 |  | 2.8838 | [45 empty] | -72.2978 |  |  |  | Electrical/Mechanical |  |  | Electrical/Mechanical | Electrical/Mechanical
Electrical/Mechanical738 | Electrical/MechanicalLB702 | 0 | [13 empty] | replacement costs are for lamps |  | 738 |  | 110 |  |  | LB702 |  | 110 | 0.66579 | 165.2174 | 0.68378 | 160.8696 | 1.5155 | 166.7004 |  | 0.35027 | 38.5302 |  | 120.7662 |  |  | 325.9968 | 13.7287 | 14 | 0.0023 | 0.253 |  | 0.0037224 | 0.40946 |  | 1.1677 |  | 1.8301 | 1.8663 | 1.0653 | 117.18 |  | 0.35974 | 39.5716 |  | 96.9474 |  |  | 253.699 | 13.7287 | 14 | 0.0023 | 0.253 |  | 0.003823 | 0.42053 |  | 1.1948 |  | 1.8683 | 1.9052 | -72.2978 | 0.038925 |  |  | Electrical/Mechanical |  |  | Electrical/Mechanical738 | Electrical/MechanicalLB702
Electrical/Mechanical739 | Electrical/MechanicalTL702 | 0 | [15 empty] | 739 |  | 110 |  |  | TL702 |  | 110 | 2.2 | 50 | 2.2 | 50.0001 | 2.562 | 281.82 |  | 0.6027 | 66.297 |  | 205.2833 |  |  | 553.4003 | 13.7287 | 14 | 0.002 | 0.22 |  | 0.0123 | 1.353 |  | 3.4571 |  | 5.0301 | 5.1295 | 2.562 | 281.82 |  | 0.6027 | 66.297 |  | 205.2833 |  |  | 553.4003 | 13.7287 | 14 | 0.002 | 0.22 |  | 0.0123 | 1.353 |  | 3.4571 |  | 5.0301 | 5.1295 | 0 |  |  |  | Electrical/Mechanical |  |  | Electrical/Mechanical739 | Electrical/MechanicalTL702
Electrical/Mechanical0 | Electrical/Mechanical0 | 0 | [15 empty] | 0 |  | 110 |  |  | 0 |  | 110 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0 |  |  |  | Electrical/Mechanical |  |  | Electrical/Mechanical0 | Electrical/Mechanical0
Electrical/Mechanical0 | Electrical/Mechanical0 | 0 | [15 empty] | 0 |  | 110 |  |  | 0 |  | 110 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0 |  |  |  | Electrical/Mechanical |  |  | Electrical/Mechanical0 | Electrical/Mechanical0
Electrical/Mechanical738 | Electrical/MechanicalLB702 | 0 | [13 empty] | ballast replacement |  | 738 |  | 110 |  |  | LB702 |  | 110 | 23.805 |  | 21.321 | [11 empty] | 13.7287 | 14 | 1.1349 | 124.8355 |  | 0.35027 | 38.5302 |  | 175.6889 |  | 339.0546 | 345.7543 | [10 empty] | 13.7287 | 14 | 0.79723 | 87.6953 |  | 0.35974 | 39.5716 |  | 154.0454 |  | 281.3122 | 286.871 | 0 | -58.8834 |  |  | Electrical/Mechanical |  |  | Electrical/Mechanical738 | Electrical/MechanicalLB702
Electrical/Mechanical739 | Electrical/MechanicalTL702 | 0 | [15 empty] | 739 |  | 110 |  |  | TL702 |  | 110 | 12.24 |  | 12.24 | [11 empty] | 13.7287 | 14 | 1.92 | 211.2 |  | 0.6027 | 66.297 |  | 299.9549 |  | 577.4519 | 588.8624 | [10 empty] | 13.7287 | 14 | 1.92 | 211.2 |  | 0.6027 | 66.297 |  | 299.9549 |  | 577.4519 | 588.8624 | 0 |  |  |  | Electrical/Mechanical |  |  | Electrical/Mechanical739 | Electrical/MechanicalTL702
Electrical/Mechanical0 | Electrical/Mechanical0 | 0 | [15 empty] | 0 |  | 110 |  |  | 0 |  | 110 | 1e-07 |  | 1e-05 | [11 empty] | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | [10 empty] | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0 |  |  |  | Electrical/Mechanical |  |  | Electrical/Mechanical0 | Electrical/Mechanical0
Electrical/Mechanical0 | Electrical/Mechanical0 | 0 | [15 empty] | 0 |  | 110 |  |  | 0 |  | 110 | 1e-07 |  | 1e-05 | [11 empty] | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | [10 empty] | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0 |  |  |  | Electrical/Mechanical |  |  | Electrical/Mechanical0 | Electrical/Mechanical0
Stairway | Stairway | 0 | [13 empty] | Stairway | 0.58 |  | 3642 | 165 | Stairway | 0.49 |  | 3642 | 165 | 3.7147 |  | 3.2746 | [45 empty] | -802.5605 |  |  |  | Stairway |  |  | Stairway | Stairway
Stairway731 | StairwayTR703 | 0 | [13 empty] | replacement costs are for lamps |  | 731 |  | 165 |  |  | TR703 |  | 165 | 1.1962 | 137.931 | 1.2304 | 134.0997 | 2.7724 | 457.446 |  | 0.58454 | 96.4495 |  | 322.4352 |  |  | 876.3306 | 13.7287 | 14 | 0.0029 | 0.4785 |  | 0.0044588 | 0.73569 |  | 2.1136 |  | 3.3278 | 3.3935 | 1.0317 | 170.2298 |  | 0.45861 | 75.6714 |  | 158.3948 |  |  | 404.2959 | 13.7287 | 14 | 0.00261 | 0.43065 |  | 0.0045861 | 0.75671 |  | 2.1339 |  | 3.3212 | 3.3869 | -472.0347 | -1.2187 |  |  | Stairway |  |  | Stairway731 | StairwayTR703
Stairway702 | StairwayWG703 | 0 | [15 empty] | 702 |  | 165 |  |  | WG703 |  | 165 | 2.5184 | 65.5172 | 2.0442 | 80.7175 | 2.5976 | 428.6101 |  | 1.5019 | 247.8126 |  | 454.1193 |  |  | 1130.542 | 13.7287 | 14 | 0.0029 | 0.4785 |  | 0.0093868 | 1.5488 |  | 4.1051 |  | 6.1324 | 6.2536 | 2.2321 | 368.2975 |  | 0.76192 | 125.7163 |  | 306.0024 |  |  | 800.0162 | 13.7287 | 14 | 0.00223 | 0.36795 |  | 0.0076192 | 1.2572 |  | 3.3187 |  | 4.9438 | 5.0415 | -330.5258 |  |  |  | Stairway |  |  | Stairway702 | StairwayWG703
Stairway0 | Stairway0 | 0 | [15 empty] | 0 |  | 165 |  |  | 0 |  | 165 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0 |  |  |  | Stairway |  |  | Stairway0 | Stairway0
Stairway0 | Stairway0 | 0 | [15 empty] | 0 |  | 165 |  |  | 0 |  | 165 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0 |  |  |  | Stairway |  |  | Stairway0 | Stairway0
Stairway731 | StairwayTR703 | 0 | [13 empty] | ballast replacement |  | 731 |  | 165 |  |  | TR703 |  | 165 | 22.968 |  | 26.0739 | [11 empty] | 13.7287 | 14 | 2.0771 | 342.7256 |  | 0.58454 | 96.4495 |  | 459.483 |  | 898.6581 | 916.4156 | [10 empty] | 13.7287 | 14 | 0.77181 | 127.3494 |  | 0.45861 | 75.6714 |  | 268.2924 |  | 471.3132 | 480.6263 | 0 | -941.2833 |  |  | Stairway |  |  | Stairway731 | StairwayTR703
Stairway702 | StairwayWG703 | 0 | [15 empty] | 702 |  | 165 |  |  | WG703 |  | 165 | 21.924 |  | 17.6616 | [11 empty] | 13.7287 | 14 | 1.9461 | 321.0987 |  | 1.5019 | 247.8126 |  | 816.1134 |  | 1385.0247 | 1412.3928 | [10 empty] | 13.7287 | 14 | 1.6724 | 275.9472 |  | 0.76192 | 125.7163 |  | 487.6623 |  | 889.3257 | 906.8988 | 0 |  |  |  | Stairway |  |  | Stairway702 | StairwayWG703
Stairway0 | Stairway0 | 0 | [15 empty] | 0 |  | 165 |  |  | 0 |  | 165 | 1e-07 |  | 1e-05 | [11 empty] | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | [10 empty] | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0 |  |  |  | Stairway |  |  | Stairway0 | Stairway0
Stairway0 | Stairway0 | 0 | [15 empty] | 0 |  | 165 |  |  | 0 |  | 165 | 1e-07 |  | 1e-05 | [11 empty] | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | [10 empty] | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0 |  |  |  | Stairway |  |  | Stairway0 | Stairway0
Lobby | Lobby | 0 | [13 empty] | Lobby | 1 |  | 3642 | 330 | Lobby | 0.84 |  | 3642 | 330 | 9.1859 |  | 8.6456 | [45 empty] | -764.2178 |  |  |  | Lobby |  |  | Lobby | Lobby
Lobby723 | LobbyIP701 | 0 | [13 empty] | replacement costs are for lamps |  | 723 |  | 330 |  |  | IP701 |  | 330 | 5.1652 | 63.8889 | 5.0368 | 65.5173 | 9.962 | 3287.4543 |  | 1.262 | 416.4534 |  | 2050.0579 |  |  | 5753.9656 | 13.7287 | 14 | 0.0072 | 2.376 |  | 0.0096261 | 3.1766 |  | 9.3279 |  | 14.8805 | 15.1746 | 9.7132 | 3205.3456 |  | 1.2306 | 406.103 |  | 1998.9042 |  |  | 5610.3527 | 13.7287 | 14 | 0.0058 | 1.914 |  | 0.0093868 | 3.0977 |  | 8.8336 |  | 13.8453 | 14.1188 | -143.6129 | -42.1515 |  |  | Lobby |  |  | Lobby723 | LobbyIP701
Lobby522 | LobbyDL701 | 0 | [15 empty] | 522 |  | 330 |  |  | DL701 |  | 330 | 2.2 | 150 | 1.0421 | 316.6667 | 1.0345 | 341.396 |  | 0.41 | 135.3 |  | 301.7699 |  |  | 778.4659 | 13.7287 | 14 | 0.0012 | 0.396 |  | 0.0041 | 1.353 |  | 3.5717 |  | 5.3207 | 5.4259 | 0.56987 | 188.0575 |  | 0.19421 | 64.0895 |  | 156.1495 |  |  | 408.2964 | 13.7287 | 14 | 0.0012 | 0.396 |  | 0.0019421 | 0.64089 |  | 1.8276 |  | 2.8645 | 2.9211 | -370.1694 |  |  |  | Lobby |  |  | Lobby522 | LobbyDL701
Lobby0 | Lobby0 | 0 | [15 empty] | 0 |  | 330 |  |  | 0 |  | 330 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0 |  |  |  | Lobby |  |  | Lobby0 | Lobby0
Lobby534-2 | LobbyWG701 | 0 | [15 empty] | 534-2 |  | 330 |  |  | WG701 |  | 330 | 1.8207 | 181.25 | 2.5667 | 128.5715 | 2.115 | 697.9614 |  | 0.31929 | 105.366 |  | 451.6127 |  |  | 1254.9401 | 9.8847 | 10 | 0.018483 | 6.0993 |  | 0.030161 | 9.9532 |  | 28.3507 |  | 44.4032 | 44.9212 | 1.4013 | 462.4363 |  | 0.47833 | 157.85 |  | 384.2183 |  |  | 1004.5046 | 13.7287 | 14 | 0.0014 | 0.462 |  | 0.0047833 | 1.5785 |  | 4.167 |  | 6.2075 | 6.3302 | -250.4355 |  |  |  | Lobby |  |  | Lobby534-2 | LobbyWG701
Lobby723 | LobbyIP701 | 0 | [13 empty] | ballast replacement |  | 723 |  | 330 |  |  | IP701 |  | 330 | 45.36 |  | 44.37 | [11 empty] | 13.7287 | 14 | 7.4661 | 2463.8087 |  | 1.262 | 416.4534 |  | 2624.9569 |  | 5505.219 | 5614.0021 | [10 empty] | 13.7287 | 14 | 7.2805 | 2402.5737 |  | 1.2306 | 406.103 |  | 2559.7167 |  | 5368.3934 | 5474.4728 | 0 | 975.7962 |  |  | Lobby |  |  | Lobby723 | LobbyIP701
Lobby522 | LobbyDL701 | 0 | [15 empty] | 522 |  | 330 |  |  | DL701 |  | 330 | 5.67 |  | 6.48 | [11 empty] | 0 | 0 | 0.775 | 255.75 |  | 0.41 | 135.3 |  | 497.9779 |  | 889.0279 | 0 | [10 empty] | 13.7287 | 14 | 0.4265 | 140.7461 |  | 0.19421 | 64.0895 |  | 248.653 |  | 453.4886 | 462.4496 | 0 |  |  |  | Lobby |  |  | Lobby522 | LobbyDL701
Lobby0 | Lobby0 | 0 | [15 empty] | 0 |  | 330 |  |  | 0 |  | 330 | 1e-07 |  | 1e-05 | [11 empty] | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | [10 empty] | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0 |  |  |  | Lobby |  |  | Lobby0 | Lobby0
Lobby534-2 | LobbyWG701 | 0 | [15 empty] | 534-2 |  | 330 |  |  | WG701 |  | 330 | 12.96 |  | 12.978 | [11 empty] | 13.7287 | 14 | 0.16552 | 54.6207 |  | 0.33931 | 111.9724 |  | 309.8239 |  | 476.417 | 485.831 | [10 empty] | 13.7287 | 14 | 1.0499 | 346.4808 |  | 0.47833 | 157.85 |  | 612.3114 |  | 1116.6421 | 1138.707 | 0 |  |  |  | Lobby |  |  | Lobby534-2 | LobbyWG701
|  | 0 | [75 empty] | Lobby |  |  | Lobby | Lobby
Large Office | [13 empty] | Large_Office_Interior Lighting LPD |  | Large Office |  |  | 2938 |  | Large Office |  |  | 2938
Office-BLDG-LO | Office-BLDG-LO |  | X | [12 empty] | Office-BLDG-LO | 0.79 |  | 2938 | 498600 | Office-BLDG-LO | 0.64 |  | 2938 | 498600 | 9998.522 |  | 9169.6525 | [45 empty] | -921039.9243 |  |  | LgOfc | Office-BLDG-LO |  |  | Office-BLDG-LO | Office-BLDG-LO
Office-BLDG-LO735 | Office-BLDG-LOID701 |  | X | [12 empty] | replacement costs are for lamps |  | 735 |  | 498600 |  |  | ID701 |  | 498600 | 9578.3684 | 52.0548 | 8509.4374 | 58.5938 | 12.8649 | 6414441.7642 |  | 1.5489 | 772270.3215 | 2 | 3961131.7766 |  |  | 11147845.8623 | 17.0184 | 18 | 0.0073 | 3639.78 |  | 0.011814 | 5890.6966 |  | 16798.5248 |  | 26329.0013 | 27847.6581 | 11.4284 | 5698176.3072 |  | 1.376 | 686086.3642 |  | 3518862.9075 |  |  | 9903125.5789 | 17.0184 | 18 | 0.005632 | 2808.1152 |  | 0.010496 | 5233.3056 |  | 14646.6782 |  | 22688.099 | 23996.7486 | -1244720.2834 | -3193.8632 | -3850.9096 | LgOfc | Office-BLDG-LO |  |  | Office-BLDG-LO735 | Office-BLDG-LOID701
Office-BLDG-LO0 | Office-BLDG-LO0 |  | X | [14 empty] | 0 |  | 498600 |  |  | 0 |  | 498600 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0 |  | 0 | LgOfc | Office-BLDG-LO |  |  | Office-BLDG-LO0 | Office-BLDG-LO0
Office-BLDG-LO0 | Office-BLDG-LO0 |  | X | [14 empty] | 0 |  | 498600 |  |  | 0 |  | 498600 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0 |  | 0 | LgOfc | Office-BLDG-LO |  |  | Office-BLDG-LO0 | Office-BLDG-LO0
Office-BLDG-LO703 | Office-BLDG-LOWW714 |  | X | [14 empty] | 703 |  | 498600 |  |  | WW714 |  | 498600 | 420.1536 | 1186.7089 | 660.2151 | 755.2085 | 0.64864 | 323413.2336 |  | 0.082918 | 41343.1142 |  | 202041.0061 |  |  | 566797.3539 | 17.0184 | 18 | 0.000632 | 315.1152 |  | 0.00051824 | 258.3945 |  | 838.1326 |  | 1411.6423 | 1493.0658 | 1.019 | 508088.3924 |  | 0.1303 | 64965.173 |  | 317424.1478 |  |  | 890477.7131 | 17.0184 | 18 | 0.000768 | 382.9248 |  | 0.00081434 | 406.0323 |  | 1243.8999 |  | 2032.857 | 2150.1122 | 323680.3592 |  | 657.0464 | LgOfc | Office-BLDG-LO |  |  | Office-BLDG-LO703 | Office-BLDG-LOWW714
Office-BLDG-LO735 | Office-BLDG-LOID701 |  | X | [12 empty] | ballast replacement |  | 735 |  | 498600 |  |  | ID701 |  | 498600 | 65.7 |  | 55.7568 | [11 empty] | 17.0184 | 18 | 9.6432 | 4808101.4882 |  | 1.5489 | 772270.3215 |  | 5023547.6348 |  | 10603919.4444 | 11215553.518 | [10 empty] | 17.0184 | 18 | 8.567 | 4271526.144 |  | 1.376 | 686086.3642 |  | 4462928.8942 |  | 9420541.4023 | 9963918.2304 | 0 | -923621.5531 | -1251635.2876 | LgOfc | Office-BLDG-LO |  |  | Office-BLDG-LO735 | Office-BLDG-LOID701
Office-BLDG-LO0 | Office-BLDG-LO0 |  | X | [14 empty] | 0 |  | 498600 |  |  | 0 |  | 498600 | 1e-07 |  | 1e-05 | [11 empty] | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | [10 empty] | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0 |  | 0 | LgOfc | Office-BLDG-LO |  |  | Office-BLDG-LO0 | Office-BLDG-LO0
Office-BLDG-LO0 | Office-BLDG-LO0 |  | X | [14 empty] | 0 |  | 498600 |  |  | 0 |  | 498600 | 1e-07 |  | 1e-05 | [11 empty] | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | [10 empty] | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0 |  | 0 | LgOfc | Office-BLDG-LO |  |  | Office-BLDG-LO0 | Office-BLDG-LO0
Office-BLDG-LO703 | Office-BLDG-LOWW714 |  | X | [14 empty] | 703 |  | 498600 |  |  | WW714 |  | 498600 | 3.9816 |  | 6.2899 | [11 empty] | 17.0184 | 18 | 0.48601 | 242323.5888 |  | 0.082918 | 41343.1142 |  | 259112.4751 |  | 542779.1781 | 574086.6811 | [10 empty] | 17.0184 | 18 | 0.7637 | 380779.1007 |  | 0.1303 | 64965.173 |  | 407160.5894 |  | 852904.8631 | 902100.4156 | 0 |  | 328013.7344 | LgOfc | Office-BLDG-LO |  |  | Office-BLDG-LO703 | Office-BLDG-LOWW714
Office - Open Plan (Including Other)-whole-large | Office - Open Plan (Including Other)-whole-large |  | 0 | [12 empty] | Office - Open Plan (Including Other)-whole | 0.81 |  | 2938 | 285144 | Office - Open Plan (Including Other)-whole-large | 0.61 |  | 2938 | 285144 | 8637.3619 |  | 5084.6196 | [45 empty] | -300331.7537 |  |  |  | Office - Open Plan (Including Other)-whole |  |  | Office - Open Plan (Including Other)-whole | Office - Open Plan (Including Other)-whole
Office - Open Plan (Including Other)735-whole-Large | Office - Open Plan (Including Other)ID701-whole-large |  | 0 | [12 empty] | replacement costs are for lamps |  | 735 |  | 285144 |  |  | ID701 |  | 285144 | 3751.8947 | 76 | 4838.8058 | 58.9286 | 8.8116 | 2512568.8674 |  | 1.0609 | 302502.141 | 2 | 1551595.4458 |  |  | 4366668.4542 | 17.0184 | 18 | 0.005 | 1425.72 |  | 0.0080921 | 2307.4153 |  | 6580.066 |  | 10313.2013 | 10908.0667 | 11.3634 | 3240210.514 |  | 1.3682 | 390136.0946 |  | 2000965.9188 |  |  | 5631312.5275 | 17.0184 | 18 | 0.0056 | 1596.8064 |  | 0.010436 | 2975.8665 |  | 8328.6859 |  | 12901.3588 | 13645.5092 | 1264644.0733 | -8967.0801 | 2737.4424 |  | Office - Open Plan (Including Other)-whole |  |  | Office - Open Plan (Including Other)-whole735 | Office - Open Plan (Including Other)-wholeID701
Office - Open Plan (Including Other)739-whole-large | Office - Open Plan (Including Other)0-whole-large |  | 0 | [14 empty] | 739 |  | 285144 |  |  | 0 |  | 285144 | 4277.16 | 66.6667 | 0 | 0 | 1.9215 | 547904.196 |  | 0.45203 | 128892.2166 |  | 399104.317 |  |  | 1075900.7296 | 17.0184 | 18 | 0.0015 | 427.716 |  | 0.009225 | 2630.4534 |  | 6721.1291 |  | 9779.2985 | 10343.3684 | 0 | 0 |  | 0 | 0 |  | 0 |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | -1075900.7296 |  | -10343.3684 |  | Office - Open Plan (Including Other)-whole |  |  | Office - Open Plan (Including Other)-whole739 | Office - Open Plan (Including Other)-whole0
Office - Open Plan (Including Other)0-whole-large | Office - Open Plan (Including Other)0-whole-large |  | 0 | [14 empty] | 0 |  | 285144 |  |  | 0 |  | 285144 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0 |  | 0 |  | Office - Open Plan (Including Other)-whole |  |  | Office - Open Plan (Including Other)-whole0 | Office - Open Plan (Including Other)-whole0
Office - Open Plan (Including Other)703-whole-large | Office - Open Plan (Including Other)WW714-whole-large |  | 0 | [14 empty] | 703 |  | 285144 |  |  | WW714 |  | 285144 | 608.3072 | 468.75 | 245.8138 | 1160.0002 | 1.6421 | 468244.4672 |  | 0.20992 | 59857.4285 |  | 292519.209 |  |  | 820621.1046 | 17.0184 | 18 | 0.0016 | 456.2304 |  | 0.001312 | 374.1089 |  | 1213.466 |  | 2043.8053 | 2161.692 | 0.66343 | 189173.3789 |  | 0.084828 | 24188.0772 |  | 118184.5511 |  |  | 331546.0073 | 17.0184 | 18 | 0.0005 | 142.572 |  | 0.00053017 | 151.1755 |  | 463.1335 |  | 756.881 | 800.5379 | -489075.0974 |  | -1361.1542 |  | Office - Open Plan (Including Other)-whole |  |  | Office - Open Plan (Including Other)-whole703 | Office - Open Plan (Including Other)-wholeWW714
Office - Open Plan (Including Other)735-whole-Large | Office - Open Plan (Including Other)ID701-whole-large |  | 0 | [12 empty] | ballast replacement |  | 735 |  | 285144 |  |  | ID701 |  | 285144 | 45 |  | 55.44 | [11 empty] | 17.0184 | 18 | 6.6049 | 1883357.3605 |  | 1.0609 | 302502.141 |  | 1967748.6919 |  | 4153608.1934 | 4393188.314 | [10 empty] | 17.0184 | 18 | 8.5184 | 2428960.2807 |  | 1.3682 | 390136.0946 |  | 2537799.5251 |  | 5356895.9004 | 5665881.6559 | 0 | -410024.1195 | 1272693.3419 |  | Office - Open Plan (Including Other)-whole |  |  | Office - Open Plan (Including Other)-whole735 | Office - Open Plan (Including Other)-wholeID701
Office - Open Plan (Including Other)739-whole-large | Office - Open Plan (Including Other)0-whole-large |  | 0 | [14 empty] | 739 |  | 285144 |  |  | 0 |  | 285144 | 9.18 |  | 1e-05 | [11 empty] | 17.0184 | 18 | 1.44 | 410607.36 |  | 0.45203 | 128892.2166 |  | 583161.4659 |  | 1122661.0425 | 1187416.1314 | [10 empty] | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0 |  | -1187416.1314 |  | Office - Open Plan (Including Other)-whole |  |  | Office - Open Plan (Including Other)-whole739 | Office - Open Plan (Including Other)-whole0
Office - Open Plan (Including Other)0-whole-large | Office - Open Plan (Including Other)0-whole-large |  | 0 | [14 empty] | 0 |  | 285144 |  |  | 0 |  | 285144 | 1e-07 |  | 1e-05 | [11 empty] | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | [10 empty] | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0 |  | 0 |  | Office - Open Plan (Including Other)-whole |  |  | Office - Open Plan (Including Other)-whole0 | Office - Open Plan (Including Other)-whole0
Office - Open Plan (Including Other)703-whole-large | Office - Open Plan (Including Other)WW714-whole-large |  | 0 | [14 empty] | 703 |  | 285144 |  |  | WW714 |  | 285144 | 10.08 |  | 4.095 | [11 empty] | 17.0184 | 18 | 1.2304 | 350841.1776 |  | 0.20992 | 59857.4285 |  | 375148.4796 |  | 785847.0856 | 831174.7455 | [10 empty] | 17.0184 | 18 | 0.4972 | 141773.1052 |  | 0.084828 | 24188.0772 |  | 151595.5602 |  | 317556.7426 | 335873.4155 | 0 |  | -495301.33 |  | Office - Open Plan (Including Other)-whole |  |  | Office - Open Plan (Including Other)-whole703 | Office - Open Plan (Including Other)-wholeWW714
Office-Enclosed-whole-large | Office-Enclosed-whole-Large |  | 0 | [12 empty] | Office-Enclosed-whole-large | 0.826 |  | 2938 | 92363 | Office-Enclosed-whole-large | 0.74 |  | 2938 | 92363 | 3663.7323 |  | 2135.8937 | [45 empty] | -433200.6176 |  |  |  | Office-Enclosed-whole-large |  |  | Office-Enclosed-whole-large | Office-Enclosed-whole-large
Office-Enclosed700-whole-large | Office-EnclosedTR701-whole-large |  | 0 | [12 empty] | replacement costs are for lamps |  | 700 |  | 92363 |  |  | TR701 |  | 92363 | 1539.3833 | 60 | 2135.8937 | 43.2433 | 2.306 | 212989.078 |  | 1.5467 | 142860.1612 |  | 244699.6626 |  |  | 600548.9017 | 17.0184 | 18 | 0.006 | 554.178 |  | 0.01025 | 946.7207 |  | 2679.7119 |  | 4180.6106 | 4421.7482 | 3.1987 | 295436.91 |  | 1.4222 | 131357.5041 |  | 274924.4897 |  |  | 701718.9037 | 17.0184 | 18 | 0.0074 | 683.4862 |  | 0.014222 | 1313.575 |  | 3662.4455 |  | 5659.5067 | 5985.9471 | 101170.002 | -3573.0708 |  |  | Office-Enclosed-whole-large |  |  | Office-Enclosed-whole-large700 | Office-Enclosed-whole-largeTR701
Office-Enclosed739-whole-large | Office-Enclosed0-whole-large |  | 0 | [14 empty] | 739 |  | 92363 |  |  | 0 |  | 92363 | 2124.349 | 43.4783 | 0 | 0 | 2.9463 | 272129.1069 |  | 0.6931 | 64017.2571 |  | 198224.2555 |  |  | 534370.6195 | 17.0184 | 18 | 0.0023 | 212.4349 |  | 0.014145 | 1306.4746 |  | 3338.2019 |  | 4857.1115 | 5137.2697 | 0 | 0 |  | 0 | 0 |  | 0 |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | -534370.6195 |  |  |  | Office-Enclosed-whole-large |  |  | Office-Enclosed-whole-large739 | Office-Enclosed-whole-large0
Office-Enclosed0-whole-large | Office-Enclosed0-whole-large |  | 0 | [14 empty] | 0 |  | 92363 |  |  | 0 |  | 92363 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0 |  |  |  | Office-Enclosed-whole-large |  |  | Office-Enclosed-whole-large0 | Office-Enclosed-whole-large0
Office-Enclosed0-whole-large | Office-Enclosed0-whole-large |  | 0 | [14 empty] | 0 |  | 92363 |  |  | 0 |  | 92363 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0 |  |  |  | Office-Enclosed-whole-large |  |  | Office-Enclosed-whole-large0 | Office-Enclosed-whole-large0
Office-Enclosed700-whole-large | Office-EnclosedTR701-whole-large |  | 0 | [12 empty] | ballast replacement |  | 700 |  | 92363 |  |  | TR701 |  | 92363 | 55.62 |  | 76.59 | [11 empty] | 17.0184 | 18 | 1.725 | 159326.175 |  | 1.5467 | 142860.1612 |  | 453681.6379 |  | 755867.9741 | 799466.4388 | [10 empty] | 17.0184 | 18 | 2.3934 | 221065.0678 |  | 1.4222 | 131357.5041 |  | 465727.4127 |  | 818149.9846 | 865340.8757 | 0 | -523882.8487 |  |  | Office-Enclosed-whole-large |  |  | Office-Enclosed-whole-large700 | Office-Enclosed-whole-largeTR701
Office-Enclosed739-whole-large | Office-Enclosed0-whole-large |  | 0 | [14 empty] | 739 |  | 92363 |  |  | 0 |  | 92363 | 14.076 |  | 1e-05 | [11 empty] | 17.0184 | 18 | 2.208 | 203937.504 |  | 0.6931 | 64017.2571 |  | 289640.4336 |  | 557595.1947 | 589757.2855 | [10 empty] | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0 |  |  |  | Office-Enclosed-whole-large |  |  | Office-Enclosed-whole-large739 | Office-Enclosed-whole-large0
Office-Enclosed0-whole-large | Office-Enclosed0-whole-large |  | 0 | [14 empty] | 0 |  | 92363 |  |  | 0 |  | 92363 | 1e-07 |  | 1e-05 | [11 empty] | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | [10 empty] | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0 |  |  |  | Office-Enclosed-whole-large |  |  | Office-Enclosed-whole-large0 | Office-Enclosed-whole-large0
Office-Enclosed0-whole-large | Office-Enclosed0-whole-large |  | 0 | [14 empty] | 0 |  | 92363 |  |  | 0 |  | 92363 | 1e-07 |  | 1e-05 | [11 empty] | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | [10 empty] | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0 |  |  |  | Office-Enclosed-whole-large |  |  | Office-Enclosed-whole-large0 | Office-Enclosed-whole-large0
Conference/Meeting/Multipurpose | Conference/Meeting/Multipurpose |  | 0 | [12 empty] | Conference/Meeting/Multipurpose | 1.07 |  | 2938 | 9628 | Conference/Meeting/Multipurpose | 0.97 |  | 2938 | 9628 | 270.3863 |  | 261.36 | [45 empty] | -1572.2968 |  |  |  | Conference/Meeting/Multipurpose |  |  | Conference/Meeting/Multipurpose | Conference/Meeting/Multipurpose
Conference/Meeting/Multipurpose731 | Conference/Meeting/MultipurposeTR704 |  | 0 | [12 empty] | replacement costs are for lamps |  | 731 |  | 9628 |  |  | TR704 |  | 9628 | 108.315 | 88.8889 | 147.4287 | 65.3061 | 4.302 | 41419.656 |  | 0.90705 | 8733.0593 |  | 29195.0393 |  |  | 79347.7547 | 17.0184 | 18 | 0.0045 | 43.326 |  | 0.0069188 | 66.6137 |  | 191.3738 |  | 301.3135 | 318.6933 | 2.118 | 20392.3447 |  | 0.94172 | 9066.8681 |  | 18976.4879 |  |  | 48435.7008 | 17.0184 | 18 | 0.0049 | 47.1772 |  | 0.0094172 | 90.6687 |  | 252.798 |  | 390.6438 | 413.1762 | -30912.0539 | -4287.1733 |  |  | Conference/Meeting/Multipurpose |  |  | Conference/Meeting/Multipurpose731 | Conference/Meeting/MultipurposeTR704
Conference/Meeting/Multipurpose511 | Conference/Meeting/MultipurposeDL702 |  | 0 | [14 empty] | 511 |  | 9628 |  |  | DL702 |  | 9628 | 70.6053 | 136.3636 | 64.1866 | 150.0001 | 0.42871 | 4127.5878 |  | 0.451 | 4342.228 |  | 6261.4991 |  |  | 14731.3149 | 1.4295 | 2 | 0.15679 | 1509.542 |  | 0.02134 | 205.4615 |  | 1486.5653 |  | 3201.5688 | 4479.1472 | 1.2021 | 11574.0884 |  | 0.41 | 3947.48 |  | 9613.2517 |  |  | 25134.8201 | 17.0184 | 18 | 0.0016 | 15.4048 |  | 0.0041 | 39.4748 |  | 106.7167 |  | 161.5963 | 170.9172 | 10403.5053 |  |  |  | Conference/Meeting/Multipurpose |  |  | Conference/Meeting/Multipurpose511 | Conference/Meeting/MultipurposeDL702
Conference/Meeting/Multipurpose0 | Conference/Meeting/Multipurpose0 |  | 0 | [14 empty] | 0 |  | 9628 |  |  | 0 |  | 9628 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0 |  |  |  | Conference/Meeting/Multipurpose |  |  | Conference/Meeting/Multipurpose0 | Conference/Meeting/Multipurpose0
Conference/Meeting/Multipurpose727-1 | Conference/Meeting/MultipurposeWW704 |  | 0 | [14 empty] | 727-1 |  | 9628 |  |  | WW704 |  | 9628 | 91.466 | 105.2632 | 49.7447 | 193.5484 | 2.5669 | 24714.1132 |  | 0.58425 | 5625.159 |  | 17820.0305 |  |  | 48159.3027 | 17.0184 | 18 | 0.0019 | 18.2932 |  | 0.0058425 | 56.2516 |  | 149.688 |  | 224.2328 | 237.1665 | 3.9763 | 38283.4955 |  | 0.5084 | 4894.8752 |  | 23917.1839 |  |  | 67095.5546 | 17.0184 | 18 | 0.0031 | 29.8468 |  | 0.0031775 | 30.593 |  | 94.3712 |  | 154.8109 | 163.7404 | 18936.2519 |  |  |  | Conference/Meeting/Multipurpose |  |  | Conference/Meeting/Multipurpose727-1 | Conference/Meeting/MultipurposeWW704
Conference/Meeting/Multipurpose731 | Conference/Meeting/MultipurposeTR704 |  | 0 | [12 empty] | ballast replacement |  | 731 |  | 9628 |  |  | TR704 |  | 9628 | 35.64 |  | 48.951 | [11 empty] | 17.0184 | 18 | 3.2231 | 31032.2475 |  | 0.90705 | 8733.0593 |  | 41604.0967 |  | 81369.4035 | 86062.7907 | [10 empty] | 17.0184 | 18 | 1.5848 | 15258.8756 |  | 0.94172 | 9066.8681 |  | 32146.5383 |  | 56472.282 | 59729.6033 | 0 | 18306.4339 |  |  | Conference/Meeting/Multipurpose |  |  | Conference/Meeting/Multipurpose731 | Conference/Meeting/MultipurposeTR704
Conference/Meeting/Multipurpose511 | Conference/Meeting/MultipurposeDL702 |  | 0 | [14 empty] | 511 |  | 9628 |  |  | DL702 |  | 9628 | 2.4651 |  | 8.64 | [11 empty] | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | [10 empty] | 17.0184 | 18 | 0.9004 | 8669.0127 |  | 0.41 | 3947.48 |  | 15315.3527 |  | 27931.8454 | 29542.9542 | 0 |  |  |  | Conference/Meeting/Multipurpose |  |  | Conference/Meeting/Multipurpose511 | Conference/Meeting/MultipurposeDL702
Conference/Meeting/Multipurpose0 | Conference/Meeting/Multipurpose0 |  | 0 | [14 empty] | 0 |  | 9628 |  |  | 0 |  | 9628 | 1e-07 |  | 1e-05 | [11 empty] | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | [10 empty] | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0 |  |  |  | Conference/Meeting/Multipurpose |  |  | Conference/Meeting/Multipurpose0 | Conference/Meeting/Multipurpose0
Conference/Meeting/Multipurpose727-1 | Conference/Meeting/MultipurposeWW704 |  | 0 | [14 empty] | 727-1 |  | 9628 |  |  | WW704 |  | 9628 | 17.1 |  | 13.113 | [11 empty] | 17.0184 | 18 | 1.9238 | 18521.865 |  | 0.58425 | 5625.159 |  | 25842.689 |  | 49989.713 | 52873.1196 | [10 empty] | 17.0184 | 18 | 2.9799 | 28690.2365 |  | 0.5084 | 4894.8752 |  | 30677.9799 |  | 64263.0916 | 67969.7867 | 0 |  |  |  | Conference/Meeting/Multipurpose |  |  | Conference/Meeting/Multipurpose727-1 | Conference/Meeting/MultipurposeWW704
Corridor/Transition | Corridor/Transition |  | 0 | [12 empty] | Corridor/Transition | 0.66 |  | 2938 | 21304 | Corridor/Transition | 0.41 |  | 2938 | 21304 | 754.1616 |  | 494.4132 | [45 empty] | -106770.4056 |  |  |  | Corridor/Transition |  |  | Corridor/Transition | Corridor/Transition
Corridor/Transition701 | Corridor/TransitionDL706 |  | 0 | [12 empty] | replacement costs are for lamps |  | 701 |  | 21304 |  |  | DL706 |  | 21304 | 674.6267 | 31.5789 | 426.0796 | 50 | 5.2271 | 111358.4651 |  | 1.9475 | 41489.54 |  | 95880.8497 |  |  | 248728.8548 | 17.0184 | 18 | 0.0038 | 80.9552 |  | 0.019475 | 414.8954 |  | 1068.8977 |  | 1564.7483 | 1655.0029 | 3.3013 | 70331.6621 |  | 1.23 | 26203.92 |  | 60556.3262 |  |  | 157091.9083 | 17.0184 | 18 | 0.0024 | 51.1296 |  | 0.0123 | 262.0392 |  | 675.0933 |  | 988.2621 | 1045.265 | -91636.9465 | -675.8017 |  |  | Corridor/Transition |  |  | Corridor/Transition701 | Corridor/TransitionDL706
Corridor/Transition0 | Corridor/Transition0 |  | 0 | [14 empty] | 0 |  | 21304 |  |  | 0 |  | 21304 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0 |  |  |  | Corridor/Transition |  |  | Corridor/Transition0 | Corridor/Transition0
Corridor/Transition0 | Corridor/Transition0 |  | 0 | [14 empty] | 0 |  | 21304 |  |  | 0 |  | 21304 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0 |  |  |  | Corridor/Transition |  |  | Corridor/Transition0 | Corridor/Transition0
Corridor/Transition703 | Corridor/TransitionWW708 |  | 0 | [14 empty] | 703 |  | 21304 |  |  | WW708 |  | 21304 | 79.5349 | 267.8571 | 68.3336 | 311.7648 | 2.8737 | 61222.0149 |  | 0.36736 | 7826.2374 |  | 38246.2936 |  |  | 107294.546 | 17.0184 | 18 | 0.0028 | 59.6512 |  | 0.002296 | 48.914 |  | 158.6582 |  | 267.2234 | 282.6368 | 2.4683 | 52584.7436 |  | 0.31562 | 6724.0248 |  | 32852.3186 |  |  | 92161.0869 | 17.0184 | 18 | 0.0017 | 36.2168 |  | 0.0019726 | 42.0252 |  | 126.5204 |  | 204.7624 | 216.5731 | -15133.4591 |  |  |  | Corridor/Transition |  |  | Corridor/Transition703 | Corridor/TransitionWW708
Corridor/Transition701 | Corridor/TransitionDL706 |  | 0 | [12 empty] | ballast replacement |  | 701 |  | 21304 |  |  | DL706 |  | 21304 | 23.256 |  | 14.688 | [11 empty] | 17.0184 | 18 | 3.9175 | 83458.1324 |  | 1.9475 | 41489.54 |  | 155982.635 |  | 280930.3074 | 297134.3675 | [10 empty] | 17.0184 | 18 | 2.4742 | 52710.3994 |  | 1.23 | 26203.92 |  | 98515.3484 |  | 177429.6678 | 187663.811 | 0 | -124775.7804 |  |  | Corridor/Transition |  |  | Corridor/Transition701 | Corridor/TransitionDL706
Corridor/Transition0 | Corridor/Transition0 |  | 0 | [14 empty] | 0 |  | 21304 |  |  | 0 |  | 21304 | 1e-07 |  | 1e-05 | [11 empty] | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | [10 empty] | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0 |  |  |  | Corridor/Transition |  |  | Corridor/Transition0 | Corridor/Transition0
Corridor/Transition0 | Corridor/Transition0 |  | 0 | [14 empty] | 0 |  | 21304 |  |  | 0 |  | 21304 | 1e-07 |  | 1e-05 | [11 empty] | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | [10 empty] | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0 |  |  |  | Corridor/Transition |  |  | Corridor/Transition0 | Corridor/Transition0
Corridor/Transition703 | Corridor/TransitionWW708 |  | 0 | [14 empty] | 703 |  | 21304 |  |  | WW708 |  | 21304 | 17.64 |  | 15.147 | [11 empty] | 17.0184 | 18 | 2.1532 | 45871.7728 |  | 0.36736 | 7826.2374 |  | 49049.9033 |  | 102747.9135 | 108674.4131 | [10 empty] | 17.0184 | 18 | 1.85 | 39411.3951 |  | 0.31562 | 6724.0248 |  | 42141.9317 |  | 88277.3516 | 93369.1892 | 0 |  |  |  | Corridor/Transition |  |  | Corridor/Transition703 | Corridor/TransitionWW708
Storage | Storage |  | 0 | [12 empty] | Storage | 0.46 |  | 2938 | 11866 | Storage | 0.38 |  | 2938 | 11866 | 143.6411 |  | 121.867 | [45 empty] | -25116.9402 |  |  |  | Storage |  |  | Storage | Storage
Storage738 | StorageLB702 |  | 0 | [12 empty] | replacement costs are for lamps |  | 738 |  | 11866 |  |  | LB702 |  | 11866 | 143.6411 | 82.6087 | 121.867 | 97.3684 | 3.0309 | 35964.8468 |  | 0.70055 | 8312.7232 |  | 26054.7532 |  |  | 70332.3231 | 17.0184 | 18 | 0.0046 | 54.5836 |  | 0.0074447 | 88.3392 |  | 251.9174 |  | 394.8403 | 417.6146 | 1.76 | 20884.3524 |  | 0.59436 | 7052.6277 |  | 17278.4029 |  |  | 45215.3829 | 17.0184 | 18 | 0.0038 | 45.0908 |  | 0.0063162 | 74.9482 |  | 212.9363 |  | 332.9753 | 352.1813 | -25116.9402 | -65.4333 |  |  | Storage |  |  | Storage738 | StorageLB702
Storage0 | Storage0 |  | 0 | [14 empty] | 0 |  | 11866 |  |  | 0 |  | 11866 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0 |  |  |  | Storage |  |  | Storage0 | Storage0
Storage0 | Storage0 |  | 0 | [14 empty] | 0 |  | 11866 |  |  | 0 |  | 11866 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0 |  |  |  | Storage |  |  | Storage0 | Storage0
Storage0 | Storage0 |  | 0 | [14 empty] | 0 |  | 11866 |  |  | 0 |  | 11866 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0 |  |  |  | Storage |  |  | Storage0 | Storage0
Storage738 | StorageLB702 |  | 0 | [12 empty] | ballast replacement |  | 738 |  | 11866 |  |  | LB702 |  | 11866 | 47.61 |  | 35.226 | [11 empty] | 17.0184 | 18 | 2.2697 | 26932.6974 |  | 0.70055 | 8312.7232 |  | 37904.072 |  | 73149.4926 | 77368.7553 | [10 empty] | 17.0184 | 18 | 1.3172 | 15629.4462 |  | 0.59436 | 7052.6277 |  | 27454.6592 |  | 50136.7331 | 53028.6198 | 0 | -24340.1355 |  |  | Storage |  |  | Storage738 | StorageLB702
Storage0 | Storage0 |  | 0 | [14 empty] | 0 |  | 11866 |  |  | 0 |  | 11866 | 1e-07 |  | 1e-05 | [11 empty] | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | [10 empty] | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0 |  |  |  | Storage |  |  | Storage0 | Storage0
Storage0 | Storage0 |  | 0 | [14 empty] | 0 |  | 11866 |  |  | 0 |  | 11866 | 1e-07 |  | 1e-05 | [11 empty] | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | [10 empty] | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0 |  |  |  | Storage |  |  | Storage0 | Storage0
Storage0 | Storage0 |  | 0 | [14 empty] | 0 |  | 11866 |  |  | 0 |  | 11866 | 1e-07 |  | 1e-05 | [11 empty] | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | [10 empty] | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0 |  |  |  | Storage |  |  | Storage0 | Storage0
Restrooms | Restrooms |  | 0 | [12 empty] | Restrooms | 0.85 |  | 2938 | 15505 | Restrooms | 0.63 |  | 2938 | 15505 | 488.4804 |  | 498.3994 | [45 empty] | -70738.7881 |  |  |  | Restrooms |  |  | Restrooms | Restrooms
Restrooms604 | RestroomsDL709 |  | 0 | [12 empty] | replacement costs are for lamps |  | 604 |  | 15505 |  |  | DL709 |  | 15505 | 187.1293 | 82.8571 | 274.4384 | 56.4972 | 4.2525 | 65935.0125 |  | 0.3637 | 5639.1418 |  | 38497.2707 |  |  | 110071.425 | 12.2532 | 13 | 0.040431 | 626.8832 |  | 0.065978 | 1022.9864 |  | 2913.8633 |  | 4563.7329 | 4841.867 | 3.5159 | 54514.0794 |  | 1.0885 | 16877.9677 |  | 43622.9908 |  |  | 115015.038 | 17.0184 | 18 | 0.003717 | 57.6321 |  | 0.010885 | 168.7797 |  | 450.9179 |  | 677.3297 | 716.3981 | 4943.613 | -8073.1568 |  |  | Restrooms |  |  | Restrooms604 | RestroomsDL709
Restrooms720 | Restrooms0 |  | 0 | [14 empty] | 720 |  | 15505 |  |  | 0 |  | 15505 | 140.9545 | 110 | 0 | 0 | 1.5353 | 23805.3903 |  | 0.55909 | 8668.7045 |  | 20303.001 |  |  | 52777.0958 | 17.0184 | 18 | 0.002 | 31.01 |  | 0.0055909 | 86.687 |  | 232.5145 |  | 350.2115 | 370.4117 | 0 | 0 |  | 0 | 0 |  | 0 |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | -52777.0958 |  |  |  | Restrooms |  |  | Restrooms720 | Restrooms0
Restrooms0 | Restrooms0 |  | 0 | [14 empty] | 0 |  | 15505 |  |  | 0 |  | 15505 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0 |  |  |  | Restrooms |  |  | Restrooms0 | Restrooms0
Restrooms534-2 | RestroomsWG701 |  | 0 | [14 empty] | 534-2 |  | 15505 |  |  | WG701 |  | 15505 | 160.3966 | 96.6667 | 223.961 | 69.2308 | 3.9657 | 61488.0181 |  | 0.59867 | 9282.389 |  | 39785.536 |  |  | 110555.9431 | 12.2532 | 13 | 0.034655 | 537.3284 |  | 0.056552 | 876.8454 |  | 2497.5971 |  | 3911.771 | 4150.1717 | 2.6025 | 40351.0734 |  | 0.88833 | 13773.6083 |  | 33525.9561 |  |  | 87650.6378 | 17.0184 | 18 | 0.0026 | 40.313 |  | 0.0088833 | 137.7361 |  | 363.6039 |  | 541.653 | 572.8956 | -22905.3053 |  |  |  | Restrooms |  |  | Restrooms534-2 | RestroomsWG701
Restrooms604 | RestroomsDL709 |  | 0 | [12 empty] | ballast replacement |  | 604 |  | 15505 |  |  | DL709 |  | 15505 | 24.2393 |  | 28.7696 | [11 empty] | 17.0184 | 18 | 0.36207 | 5613.8793 |  | 0.74224 | 11508.4526 |  | 31843.5024 |  | 48965.8343 | 51790.1836 | [10 empty] | 17.0184 | 18 | 2.6341 | 40842.3355 |  | 1.0885 | 16877.9677 |  | 67943.111 |  | 125663.4143 | 132911.68 | 0 | 77016.1372 |  |  | Restrooms |  |  | Restrooms604 | RestroomsDL709
Restrooms720 | Restrooms0 |  | 0 | [14 empty] | 720 |  | 15505 |  |  | 0 |  | 15505 | 12.6 |  | 1e-05 | [11 empty] | 17.0184 | 18 | 1.15 | 17830.7852 |  | 0.55909 | 8668.7045 |  | 32846.7549 |  | 59346.2447 | 62769.3361 | [10 empty] | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0 |  |  |  | Restrooms |  |  | Restrooms720 | Restrooms0
Restrooms0 | Restrooms0 |  | 0 | [14 empty] | 0 |  | 15505 |  |  | 0 |  | 15505 | 1e-07 |  | 1e-05 | [11 empty] | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | [10 empty] | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0 |  |  |  | Restrooms |  |  | Restrooms0 | Restrooms0
Restrooms534-2 | RestroomsWG701 |  | 0 | [14 empty] | 534-2 |  | 15505 |  |  | WG701 |  | 15505 | 24.3 |  | 24.102 | [11 empty] | 17.0184 | 18 | 0.31034 | 4811.8966 |  | 0.63621 | 9864.3879 |  | 27294.4306 |  | 41970.7151 | 44391.586 | [10 empty] | 17.0184 | 18 | 1.9499 | 30233.0703 |  | 0.88833 | 13773.6083 |  | 53428.8056 |  | 97435.4842 | 103055.5629 | 0 |  |  |  | Restrooms |  |  | Restrooms534-2 | RestroomsWG701
Lounge/Recreation - Break room | Lounge/Recreation - Break room |  | 0 | [12 empty] | Lounge/Recreation - Break room | #N/A |  | 2938 | 9530 | Lounge/Recreation - Break room | #N/A |  | 2938 | 9530 | 290.0297 |  | 481.7939 | [45 empty] | 12425.2262 |  |  |  | #N/A |  |  | #N/A | #N/A
Lounge/Recreation - Breakroom522 | Lounge/Recreation - BreakroomDL707 |  | 0 | [12 empty] | replacement costs are for lamps |  | 522 |  | 9530 |  |  | DL707 |  | 9530 | 179.4817 | 53.0973 | 333.5496 | 28.5715 | 2.9226 | 27851.965 |  | 1.1583 | 11038.1225 |  | 24619.1644 |  |  | 63509.2519 | 17.0184 | 18 | 0.00339 | 32.3067 |  | 0.011583 | 110.3812 |  | 291.3909 |  | 434.0789 | 459.1165 | 7.1431 | 68073.8526 |  | 2.1525 | 20513.325 |  | 53930.3013 |  |  | 142517.4789 | 17.0184 | 18 | 0.0028 | 26.684 |  | 0.021525 | 205.1333 |  | 519.7948 |  | 751.6121 | 794.9651 | 79008.227 | 418.7601 |  |  | #N/A |  |  | #N/A | #N/A
Lounge/Recreation - Breakroom0 | Lounge/Recreation - Breakroom0 |  | 0 | [14 empty] | 0 |  | 9530 |  |  | 0 |  | 9530 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0 |  |  |  | #N/A |  |  | #N/A | #N/A
Lounge/Recreation - Breakroom0 | Lounge/Recreation - Breakroom0 |  | 0 | [14 empty] | 0 |  | 9530 |  |  | 0 |  | 9530 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0 |  |  |  | #N/A |  |  | #N/A | #N/A
Lounge/Recreation - Breakroom727-2 | Lounge/Recreation - BreakroomWG702 |  | 0 | [14 empty] | 727-2 |  | 9530 |  |  | WG702 |  | 9530 | 110.548 | 86.2069 | 148.2444 | 64.2857 | 7.7749 | 74094.797 |  | 0.7134 | 6798.702 |  | 43707.2535 |  |  | 124600.7525 | 17.0184 | 18 | 0.0029 | 27.637 |  | 0.007134 | 67.987 |  | 184.5171 |  | 280.1412 | 296.2997 | 2.8026 | 26709.2016 |  | 0.95667 | 9117.0333 |  | 22191.5167 |  |  | 58017.7516 | 17.0184 | 18 | 0.0028 | 26.684 |  | 0.0095667 | 91.1703 |  | 240.6769 |  | 358.5312 | 379.2113 | -66583.0008 |  |  |  | #N/A |  |  | #N/A | #N/A
Lounge/Recreation - Breakroom522 | Lounge/Recreation - BreakroomDL707 |  | 0 | [12 empty] | ballast replacement |  | 522 |  | 9530 |  |  | DL707 |  | 9530 | 16.0178 |  | 22.428 | [11 empty] | 0 | 0 | 2.1894 | 20864.7438 |  | 1.1583 | 11038.1225 |  | 40626.32 |  | 72529.1862 | 0 | [10 empty] | 17.0184 | 18 | 5.3552 | 51035.3764 |  | 2.1525 | 20513.325 |  | 83486.7985 |  | 155035.4999 | 163977.9475 | 0 | 110361.3496 |  |  | #N/A |  |  | #N/A | #N/A
Lounge/Recreation - Breakroom0 | Lounge/Recreation - Breakroom0 |  | 0 | [14 empty] | 0 |  | 9530 |  |  | 0 |  | 9530 | 1e-07 |  | 1e-05 | [11 empty] | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | [10 empty] | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0 |  |  |  | #N/A |  |  | #N/A | #N/A
Lounge/Recreation - Breakroom0 | Lounge/Recreation - Breakroom0 |  | 0 | [14 empty] | 0 |  | 9530 |  |  | 0 |  | 9530 | 1e-07 |  | 1e-05 | [11 empty] | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | [10 empty] | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0 |  |  |  | #N/A |  |  | #N/A | #N/A
Lounge/Recreation - Breakroom727-2 | Lounge/Recreation - BreakroomWG702 |  | 0 | [14 empty] | 727-2 |  | 9530 |  |  | WG702 |  | 9530 | 26.1 |  | 22.176 | [11 empty] | 17.0184 | 18 | 5.829 | 55550.37 |  | 0.7134 | 6798.702 |  | 52838.1158 |  | 115187.1878 | 121831.1848 | [10 empty] | 17.0184 | 18 | 2.0999 | 20011.8882 |  | 0.95667 | 9117.0333 |  | 35365.6202 |  | 64494.5417 | 68214.5869 | 0 |  |  |  | #N/A |  |  | #N/A | #N/A
Electrical/Mechanical | Electrical/Mechanical |  | 0 | [12 empty] | Electrical/Mechanical | 0.43 |  | 2938 | 31023 | Electrical/Mechanical | 0.43 |  | 2938 | 31023 | 808.2308 |  | 813.305 | [45 empty] | -20389.9389 |  |  |  | Electrical/Mechanical |  |  | Electrical/Mechanical | Electrical/Mechanical
Electrical/Mechanical738 | Electrical/MechanicalLB702 |  | 0 | [12 empty] | replacement costs are for lamps |  | 738 |  | 31023 |  |  | LB702 |  | 31023 | 187.7708 | 165.2174 | 192.8456 | 160.8696 | 1.5155 | 47014.0503 |  | 0.35027 | 10866.5772 |  | 34059.3548 |  |  | 91939.9823 | 17.0184 | 18 | 0.0023 | 71.3529 |  | 0.0037224 | 115.479 |  | 329.3121 |  | 516.144 | 545.9152 | 1.0653 | 33047.9634 |  | 0.35974 | 11160.2685 |  | 27341.8115 |  |  | 71550.0434 | 17.0184 | 18 | 0.0023 | 71.3529 |  | 0.003823 | 118.6001 |  | 336.9561 |  | 526.9091 | 557.3013 | -20389.9389 | 11.3861 |  |  | Electrical/Mechanical |  |  | Electrical/Mechanical738 | Electrical/MechanicalLB702
Electrical/Mechanical739 | Electrical/MechanicalTL702 |  | 0 | [14 empty] | 739 |  | 31023 |  |  | TL702 |  | 31023 | 620.46 | 50 | 620.4594 | 50.0001 | 2.562 | 79480.926 |  | 0.6027 | 18697.5621 |  | 57895.4878 |  |  | 156073.9759 | 17.0184 | 18 | 0.002 | 62.046 |  | 0.0123 | 381.5829 |  | 974.9908 |  | 1418.6197 | 1500.4457 | 2.562 | 79480.926 |  | 0.6027 | 18697.5621 |  | 57895.4878 |  |  | 156073.9759 | 17.0184 | 18 | 0.002 | 62.046 |  | 0.0123 | 381.5829 |  | 974.9908 |  | 1418.6197 | 1500.4457 | 0 |  |  |  | Electrical/Mechanical |  |  | Electrical/Mechanical739 | Electrical/MechanicalTL702
Electrical/Mechanical0 | Electrical/Mechanical0 |  | 0 | [14 empty] | 0 |  | 31023 |  |  | 0 |  | 31023 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0 |  |  |  | Electrical/Mechanical |  |  | Electrical/Mechanical0 | Electrical/Mechanical0
Electrical/Mechanical0 | Electrical/Mechanical0 |  | 0 | [14 empty] | 0 |  | 31023 |  |  | 0 |  | 31023 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0 |  |  |  | Electrical/Mechanical |  |  | Electrical/Mechanical0 | Electrical/Mechanical0
Electrical/Mechanical738 | Electrical/MechanicalLB702 |  | 0 | [12 empty] | ballast replacement |  | 738 |  | 31023 |  |  | LB702 |  | 31023 | 23.805 |  | 21.321 | [11 empty] | 17.0184 | 18 | 1.1349 | 35207.023 |  | 0.35027 | 10866.5772 |  | 49549.0488 |  | 95622.6491 | 101138.1635 | [10 empty] | 17.0184 | 18 | 0.79723 | 24732.4579 |  | 0.35974 | 11160.2685 |  | 43444.9944 |  | 79337.7208 | 83913.9205 | 0 | -17224.2429 |  |  | Electrical/Mechanical |  |  | Electrical/Mechanical738 | Electrical/MechanicalLB702
Electrical/Mechanical739 | Electrical/MechanicalTL702 |  | 0 | [14 empty] | 739 |  | 31023 |  |  | TL702 |  | 31023 | 12.24 |  | 12.24 | [11 empty] | 17.0184 | 18 | 1.92 | 59564.16 |  | 0.6027 | 18697.5621 |  | 84595.4706 |  | 162857.1927 | 172250.7956 | [10 empty] | 17.0184 | 18 | 1.92 | 59564.16 |  | 0.6027 | 18697.5621 |  | 84595.4706 |  | 162857.1927 | 172250.7956 | 0 |  |  |  | Electrical/Mechanical |  |  | Electrical/Mechanical739 | Electrical/MechanicalTL702
Electrical/Mechanical0 | Electrical/Mechanical0 |  | 0 | [14 empty] | 0 |  | 31023 |  |  | 0 |  | 31023 | 1e-07 |  | 1e-05 | [11 empty] | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | [10 empty] | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0 |  |  |  | Electrical/Mechanical |  |  | Electrical/Mechanical0 | Electrical/Mechanical0
Electrical/Mechanical0 | Electrical/Mechanical0 |  | 0 | [14 empty] | 0 |  | 31023 |  |  | 0 |  | 31023 | 1e-07 |  | 1e-05 | [11 empty] | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | [10 empty] | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0 |  |  |  | Electrical/Mechanical |  |  | Electrical/Mechanical0 | Electrical/Mechanical0
Stairway | Stairway |  | 0 | [12 empty] | Stairway | 0.58 |  | 2938 | 8484 | Stairway | 0.49 |  | 2938 | 8484 | 191.0016 |  | 168.3737 | [45 empty] | -41266.2026 |  |  |  | Stairway |  |  | Stairway | Stairway
Stairway731 | StairwayTR703 |  | 0 | [12 empty] | replacement costs are for lamps |  | 731 |  | 8484 |  |  | TR703 |  | 8484 | 61.509 | 137.931 | 63.2664 | 134.0997 | 2.7724 | 23521.0416 |  | 0.58454 | 4959.2554 |  | 16579.0304 |  |  | 45059.3274 | 17.0184 | 18 | 0.0029 | 24.6036 |  | 0.0044588 | 37.828 |  | 108.6757 |  | 171.1074 | 180.9768 | 1.0317 | 8752.9064 |  | 0.45861 | 3890.8836 |  | 8144.3704 |  |  | 20788.1604 | 17.0184 | 18 | 0.00261 | 22.1432 |  | 0.0045861 | 38.9088 |  | 109.7201 |  | 170.7722 | 180.6223 | -24271.1669 | -64.9943 |  |  | Stairway |  |  | Stairway731 | StairwayTR703
Stairway702 | StairwayWG703 |  | 0 | [14 empty] | 702 |  | 8484 |  |  | WG703 |  | 8484 | 129.4926 | 65.5172 | 105.1073 | 80.7175 | 2.5976 | 22038.351 |  | 1.5019 | 12742.0749 |  | 23349.9871 |  |  | 58130.413 | 17.0184 | 18 | 0.0029 | 24.6036 |  | 0.0093868 | 79.638 |  | 211.0766 |  | 315.3182 | 333.5057 | 2.2321 | 18937.1882 |  | 0.76192 | 6464.101 |  | 15734.0881 |  |  | 41135.3773 | 17.0184 | 18 | 0.00223 | 18.9193 |  | 0.0076192 | 64.641 |  | 170.6432 |  | 254.2035 | 268.866 | -16995.0357 |  |  |  | Stairway |  |  | Stairway702 | StairwayWG703
Stairway0 | Stairway0 |  | 0 | [14 empty] | 0 |  | 8484 |  |  | 0 |  | 8484 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0 |  |  |  | Stairway |  |  | Stairway0 | Stairway0
Stairway0 | Stairway0 |  | 0 | [14 empty] | 0 |  | 8484 |  |  | 0 |  | 8484 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0 |  |  |  | Stairway |  |  | Stairway0 | Stairway0
Stairway731 | StairwayTR703 |  | 0 | [12 empty] | ballast replacement |  | 731 |  | 8484 |  |  | TR703 |  | 8484 | 22.968 |  | 26.0739 | [11 empty] | 17.0184 | 18 | 2.0771 | 17622.3285 |  | 0.58454 | 4959.2554 |  | 23625.7802 |  | 46207.3641 | 48872.6048 | [10 empty] | 17.0184 | 18 | 0.77181 | 6548.0724 |  | 0.45861 | 3890.8836 |  | 13795.1095 |  | 24234.0655 | 25631.8864 | 0 | -50198.8042 |  |  | Stairway |  |  | Stairway731 | StairwayTR703
Stairway702 | StairwayWG703 |  | 0 | [14 empty] | 702 |  | 8484 |  |  | WG703 |  | 8484 | 21.924 |  | 17.6616 | [11 empty] | 17.0184 | 18 | 1.9461 | 16510.3105 |  | 1.5019 | 12742.0749 |  | 41963.0657 |  | 71215.4512 | 75323.1584 | [10 empty] | 17.0184 | 18 | 1.6724 | 14188.7017 |  | 0.76192 | 6464.101 |  | 25074.7072 |  | 45727.5098 | 48365.0726 | 0 |  |  |  | Stairway |  |  | Stairway702 | StairwayWG703
Stairway0 | Stairway0 |  | 0 | [14 empty] | 0 |  | 8484 |  |  | 0 |  | 8484 | 1e-07 |  | 1e-05 | [11 empty] | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | [10 empty] | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0 |  |  |  | Stairway |  |  | Stairway0 | Stairway0
Stairway0 | Stairway0 |  | 0 | [14 empty] | 0 |  | 8484 |  |  | 0 |  | 8484 | 1e-07 |  | 1e-05 | [11 empty] | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | [10 empty] | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0 |  |  |  | Stairway |  |  | Stairway0 | Stairway0
Lobby | Lobby |  | 0 | [12 empty] | Lobby | 1 |  | 2938 | 13792 | Lobby | 0.84 |  | 2938 | 13792 | 383.9152 |  | 361.3341 | [45 empty] | -31939.6712 |  |  |  | Lobby |  |  | Lobby | Lobby
Lobby723 | LobbyIP701 |  | 0 | [12 empty] | replacement costs are for lamps |  | 723 |  | 13792 |  |  | IP701 |  | 13792 | 215.8748 | 63.8889 | 210.5094 | 65.5173 | 9.962 | 137395.6641 |  | 1.262 | 17405.2282 |  | 85679.9961 |  |  | 240480.8884 | 17.0184 | 18 | 0.0072 | 99.3024 |  | 0.0096261 | 132.763 |  | 389.8508 |  | 621.9162 | 657.7884 | 9.7132 | 133964.0189 |  | 1.2306 | 16972.6421 |  | 83542.0804 |  |  | 234478.7413 | 17.0184 | 18 | 0.0058 | 79.9936 |  | 0.0093868 | 129.4633 |  | 369.1911 |  | 578.6481 | 612.0245 | -6002.1471 | -1848.8227 |  |  | Lobby |  |  | Lobby723 | LobbyIP701
Lobby522 | LobbyDL701 |  | 0 | [14 empty] | 522 |  | 13792 |  |  | DL701 |  | 13792 | 91.9467 | 150 | 43.5537 | 316.6667 | 1.0345 | 14268.2837 |  | 0.41 | 5654.72 |  | 12612.1522 |  |  | 32535.1559 | 17.0184 | 18 | 0.0012 | 16.5504 |  | 0.0041 | 56.5472 |  | 149.2767 |  | 222.3743 | 235.2008 | 0.56987 | 7859.663 |  | 0.19421 | 2678.5516 |  | 6526.1019 |  |  | 17064.3165 | 17.0184 | 18 | 0.0012 | 16.5504 |  | 0.0019421 | 26.7855 |  | 76.3844 |  | 119.7203 | 126.6258 | -15470.8395 |  |  |  | Lobby |  |  | Lobby522 | LobbyDL701
Lobby0 | Lobby0 |  | 0 | [14 empty] | 0 |  | 13792 |  |  | 0 |  | 13792 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0 |  |  |  | Lobby |  |  | Lobby0 | Lobby0
Lobby534-2 | LobbyWG701 |  | 0 | [14 empty] | 534-2 |  | 13792 |  |  | WG701 |  | 13792 | 76.0938 | 181.25 | 107.2711 | 128.5715 | 2.115 | 29170.5556 |  | 0.31929 | 4403.6619 |  | 18874.6723 |  |  | 52448.8898 | 12.2532 | 13 | 0.018483 | 254.9142 |  | 0.030161 | 415.9846 |  | 1184.8861 |  | 1855.7849 | 1968.8847 | 1.4013 | 19327.0361 |  | 0.47833 | 6597.1733 |  | 16057.9957 |  |  | 41982.2051 | 17.0184 | 18 | 0.0014 | 19.3088 |  | 0.0047833 | 65.9717 |  | 174.1561 |  | 259.4367 | 274.401 | -10466.6846 |  |  |  | Lobby |  |  | Lobby534-2 | LobbyWG701
Lobby723 | LobbyIP701 |  | 0 | [12 empty] | ballast replacement |  | 723 |  | 13792 |  |  | IP701 |  | 13792 | 45.36 |  | 44.37 | [11 empty] | 17.0184 | 18 | 7.4661 | 102972.2713 |  | 1.262 | 17405.2282 |  | 109707.289 |  | 230084.7885 | 243356.0791 | [10 empty] | 17.0184 | 18 | 7.2805 | 100413.0189 |  | 1.2306 | 16972.6421 |  | 106980.6459 |  | 224366.3069 | 237307.7555 | 0 | 42298.8692 |  |  | Lobby |  |  | Lobby723 | LobbyIP701
Lobby522 | LobbyDL701 |  | 0 | [14 empty] | 522 |  | 13792 |  |  | DL701 |  | 13792 | 5.67 |  | 6.48 | [11 empty] | 0 | 0 | 0.775 | 10688.8 |  | 0.41 | 5654.72 |  | 20812.4583 |  | 37155.9783 | 0 | [10 empty] | 17.0184 | 18 | 0.4265 | 5882.3345 |  | 0.19421 | 2678.5516 |  | 10392.19 |  | 18953.076 | 20046.2895 | 0 |  |  |  | Lobby |  |  | Lobby522 | LobbyDL701
Lobby0 | Lobby0 |  | 0 | [14 empty] | 0 |  | 13792 |  |  | 0 |  | 13792 | 1e-07 |  | 1e-05 | [11 empty] | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | [10 empty] | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0 |  |  |  | Lobby |  |  | Lobby0 | Lobby0
Lobby534-2 | LobbyWG701 |  | 0 | [14 empty] | 534-2 |  | 13792 |  |  | WG701 |  | 13792 | 12.96 |  | 12.978 | [11 empty] | 17.0184 | 18 | 0.16552 | 2282.8138 |  | 0.33931 | 4679.7683 |  | 12948.7619 |  | 19911.344 | 21059.8303 | [10 empty] | 17.0184 | 18 | 1.0499 | 14480.7955 |  | 0.47833 | 6597.1733 |  | 25590.9042 |  | 46668.873 | 49360.7336 | 0 |  |  |  | Lobby |  |  | Lobby534-2 | LobbyWG701
Standalone Retail | [13 empty] | Standalone_Retail_Interior Lighting LPD |  | Standalone Retail |  |  | 3613 |  | Standalone Retail |  |  | 3613 |  | 886.3411 | 216.207 | 873.9625 | 203.1931
Storage | Storage |  |  | X | [11 empty] | Storage | 0.46 |  | 3613 | 4088 | Storage | 0.38 |  | 3613 | 4088 | 49.4863 |  | 41.9849 | [45 empty] | -8653.1309 |  |  | SoRtl | Storage |  |  | Storage | Storage
Storage738 | StorageLB702 |  |  | X | [11 empty] | replacement costs are for lamps |  | 738 |  | 4088 |  |  | LB702 |  | 4088 | 49.4863 | 82.6087 | 41.9849 | 97.3684 | 3.0309 | 12390.3837 |  | 0.70055 | 2863.8473 |  | 8976.2204 |  |  | 24230.4515 | 13.8389 | 14 | 0.0046 | 18.8048 |  | 0.0074447 | 30.4341 |  | 86.789 |  | 136.0279 | 137.6113 | 1.76 | 7194.9463 |  | 0.59436 | 2429.7271 |  | 5952.6471 |  |  | 15577.3205 | 13.8389 | 14 | 0.0038 | 15.5344 |  | 0.0063162 | 25.8207 |  | 73.3595 |  | 114.7146 | 116.0498 | -8653.1309 | -21.5614 |  | SoRtl | Storage |  |  | Storage738 | StorageLB702
Storage0 | Storage0 |  |  | X | [13 empty] | 0 |  | 4088 |  |  | 0 |  | 4088 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0 |  |  | SoRtl | Storage |  |  | Storage0 | Storage0
Storage0 | Storage0 |  |  | X | [13 empty] | 0 |  | 4088 |  |  | 0 |  | 4088 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0 |  |  | SoRtl | Storage |  |  | Storage0 | Storage0
Storage0 | Storage0 |  |  | X | [13 empty] | 0 |  | 4088 |  |  | 0 |  | 4088 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0 |  |  | SoRtl | Storage |  |  | Storage0 | Storage0
Storage738 | StorageLB702 |  |  | X | [11 empty] | ballast replacement |  | 738 |  | 4088 |  |  | LB702 |  | 4088 | 47.61 |  | 35.226 | [11 empty] | 13.8389 | 14 | 2.2697 | 9278.6842 |  | 0.70055 | 2863.8473 |  | 13058.4735 |  | 25201.005 | 25494.3447 | [10 empty] | 13.8389 | 14 | 1.3172 | 5384.5589 |  | 0.59436 | 2429.7271 |  | 9458.5072 |  | 17272.7933 | 17473.8486 | 0 | -8020.4962 |  | SoRtl | Storage |  |  | Storage738 | StorageLB702
Storage0 | Storage0 |  |  | X | [13 empty] | 0 |  | 4088 |  |  | 0 |  | 4088 | 1e-07 |  | 1e-05 | [11 empty] | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | [10 empty] | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0 |  |  | SoRtl | Storage |  |  | Storage0 | Storage0
Storage0 | Storage0 |  |  | X | [13 empty] | 0 |  | 4088 |  |  | 0 |  | 4088 | 1e-07 |  | 1e-05 | [11 empty] | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | [10 empty] | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0 |  |  | SoRtl | Storage |  |  | Storage0 | Storage0
Storage0 | Storage0 |  |  | X | [13 empty] | 0 |  | 4088 |  |  | 0 |  | 4088 | 1e-07 |  | 1e-05 | [11 empty] | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | [10 empty] | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0 |  |  | SoRtl | Storage |  |  | Storage0 | Storage0
Retail - Sales Area | Retail - Sales Area |  |  | X | [11 empty] | Retail - Sales Area | 1.22 |  | 3613 | 20467 | Retail - Sales Area | 1.05 |  | 3613 | 20467 | 833.264 |  | 828.598 | [45 empty] | -21120.803 |  |  | SoRtl | Retail - Sales Area |  |  | Retail - Sales Area | Retail - Sales Area
Retail - Sales Area700 | Retail - Sales AreaTR701 |  |  | X | [11 empty] | replacement costs are for lamps |  | 700 |  | 20467 |  |  | TR701 |  | 20467 | 415.0253 | 49.3151 | 402.9439 | 50.7937 | 2.8056 | 57422.8974 |  | 1.8818 | 38515.7984 |  | 65972.2262 |  |  | 161910.922 | 13.8389 | 14 | 0.0073 | 149.4091 |  | 0.012471 | 255.2405 |  | 722.4634 |  | 1127.1131 | 1140.2327 | 2.7232 | 55735.2227 |  | 1.2108 | 24781.0598 |  | 51865.4818 |  |  | 132381.7643 | 13.8389 | 14 | 0.0063 | 128.9421 |  | 0.012108 | 247.8106 |  | 690.9333 |  | 1067.686 | 1080.1139 | -29529.1576 | 393.5406 |  | SoRtl | Retail - Sales Area |  |  | Retail - Sales Area700 | Retail - Sales AreaTR701
Retail - Sales Area741 | Retail - Sales AreaDL703 |  |  | X | [13 empty] | 741 |  | 20467 |  |  | DL703 |  | 20467 | 204.67 | 100 | 186.8725 | 109.5239 | 1.6519 | 33808.7824 |  | 0.615 | 12587.205 |  | 29100.8946 |  |  | 75496.8819 | 13.8389 | 14 | 0.0024 | 49.1208 |  | 0.00615 | 125.8721 |  | 340.2841 |  | 515.277 | 521.2748 | 2.1026 | 43033.0804 |  | 0.56152 | 11492.6654 |  | 32668.2039 |  |  | 87193.9498 | 13.8389 | 14 | 0.0021 | 42.9807 |  | 0.0056152 | 114.9267 |  | 309.4769 |  | 467.3842 | 472.8246 | 11697.0678 |  |  | SoRtl | Retail - Sales Area |  |  | Retail - Sales Area741 | Retail - Sales AreaDL703
Retail - Sales Area0 | Retail - Sales Area0 |  |  | X | [13 empty] | 0 |  | 20467 |  |  | 0 |  | 20467 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0 |  |  | SoRtl | Retail - Sales Area |  |  | Retail - Sales Area0 | Retail - Sales Area0
Retail - Sales Area537-1_LED | Retail - Sales AreaWG701 |  |  | X | [13 empty] | 537-1_LED |  | 20467 |  |  | WG701 |  | 20467 | 213.5687 | 95.8333 | 238.7815 | 85.7143 | 1.8806 | 38489.3503 |  | 0.96838 | 19819.9224 |  | 38430.3315 |  |  | 96739.6043 | 13.8389 | 14 | 0.0024 | 49.1208 |  | 6.4174e-07 | 0.013134 |  | 32.0305 |  | 81.1645 | 82.1092 | 2.102 | 43021.2929 |  | 0.7175 | 14685.0725 |  | 35744.5256 |  |  | 93450.891 | 13.8389 | 14 | 0.0021 | 42.9807 |  | 0.007175 | 146.8507 |  | 387.6653 |  | 577.4967 | 584.2188 | -3288.7132 |  |  | SoRtl | Retail - Sales Area |  |  | Retail - Sales Area537-1_LED | Retail - Sales AreaWG701
Retail - Sales Area700 | Retail - Sales AreaTR701 |  |  | X | [11 empty] | ballast replacement |  | 700 |  | 20467 |  |  | TR701 |  | 20467 | 67.671 |  | 65.205 | [11 empty] | 13.8389 | 14 | 2.0987 | 42955.1162 |  | 1.8818 | 38515.7984 |  | 122314.7891 |  | 203785.7037 | 206157.7693 | [10 empty] | 13.8389 | 14 | 2.0377 | 41704.7105 |  | 1.2108 | 24781.0598 |  | 87861.1311 |  | 154346.9014 | 156143.4993 | 0 | -38444.0598 |  | SoRtl | Retail - Sales Area |  |  | Retail - Sales Area700 | Retail - Sales AreaTR701
Retail - Sales Area741 | Retail - Sales AreaDL703 |  |  | X | [13 empty] | 741 |  | 20467 |  |  | DL703 |  | 20467 | 14.688 |  | 19.467 | [11 empty] | 13.8389 | 14 | 1.2371 | 25319.7462 |  | 0.615 | 12587.205 |  | 47322.4192 |  | 85229.3703 | 86221.4402 | [10 empty] | 13.8389 | 14 | 1.5753 | 32242.5748 |  | 0.56152 | 11492.6654 |  | 49151.3567 |  | 92886.5969 | 93967.7969 | 0 |  |  | SoRtl | Retail - Sales Area |  |  | Retail - Sales Area741 | Retail - Sales AreaDL703
Retail - Sales Area0 | Retail - Sales Area0 |  |  | X | [13 empty] | 0 |  | 20467 |  |  | 0 |  | 20467 | 1e-07 |  | 1e-05 | [11 empty] | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | [10 empty] | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0 |  |  | SoRtl | Retail - Sales Area |  |  | Retail - Sales Area0 | Retail - Sales Area0
Retail - Sales Area537-1_LED | Retail - Sales AreaWG701 |  |  | X | [13 empty] | 537-1_LED |  | 20467 |  |  | WG701 |  | 20467 | 22.248 |  | 19.467 | [11 empty] | 13.8389 | 14 | 0.93908 | 19220.1148 |  | 0.96838 | 19819.9224 |  | 61063.3533 |  | 100103.3905 | 101268.5939 | [10 empty] | 13.8389 | 14 | 1.5749 | 32233.7341 |  | 0.7175 | 14685.0725 |  | 56964.4398 |  | 103883.2465 | 105092.4475 | 0 |  |  | SoRtl | Retail - Sales Area |  |  | Retail - Sales Area537-1_LED | Retail - Sales AreaWG701
Lobby | Lobby |  |  | X | [11 empty] | Lobby | 1 |  | 3613 | 129 | Lobby | 0.84 |  | 3613 | 129 | 3.5909 |  | 3.3796 | [45 empty] | -298.7397 |  |  | SoRtl | Lobby |  |  | Lobby | Lobby
Lobby723 | LobbyIP701 |  |  | X | [11 empty] | replacement costs are for lamps |  | 723 |  | 129 |  |  | IP701 |  | 129 | 2.0191 | 63.8889 | 1.9689 | 65.5173 | 9.962 | 1285.0958 |  | 1.262 | 162.7954 |  | 801.3863 |  |  | 2249.2775 | 13.8389 | 14 | 0.0072 | 0.9288 |  | 0.0096261 | 1.2418 |  | 3.6464 |  | 5.8169 | 5.8846 | 9.7132 | 1252.9987 |  | 1.2306 | 158.7493 |  | 781.3898 |  |  | 2193.1379 | 13.8389 | 14 | 0.0058 | 0.7482 |  | 0.0093868 | 1.2109 |  | 3.4531 |  | 5.4122 | 5.4752 | -56.1396 | -16.3462 |  | SoRtl | Lobby |  |  | Lobby723 | LobbyIP701
Lobby522 | LobbyDL701 |  |  | X | [13 empty] | 522 |  | 129 |  |  | DL701 |  | 129 | 0.86 | 150 | 0.40737 | 316.6667 | 1.0345 | 133.4548 |  | 0.41 | 52.89 |  | 117.9646 |  |  | 304.3094 | 13.8389 | 14 | 0.0012 | 0.1548 |  | 0.0041 | 0.5289 |  | 1.3962 |  | 2.0799 | 2.1041 | 0.56987 | 73.5134 |  | 0.19421 | 25.0532 |  | 61.0403 |  |  | 159.6068 | 13.8389 | 14 | 0.0012 | 0.1548 |  | 0.0019421 | 0.25053 |  | 0.71444 |  | 1.1198 | 1.1328 | -144.7026 |  |  | SoRtl | Lobby |  |  | Lobby522 | LobbyDL701
Lobby0 | Lobby0 |  |  | X | [13 empty] | 0 |  | 129 |  |  | 0 |  | 129 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0 |  |  | SoRtl | Lobby |  |  | Lobby0 | Lobby0
Lobby534-2 | LobbyWG701 |  |  | X | [13 empty] | 534-2 |  | 129 |  |  | WG701 |  | 129 | 0.71172 | 181.25 | 1.0033 | 128.5715 | 2.115 | 272.8394 |  | 0.31929 | 41.1885 |  | 176.5395 |  |  | 490.5675 | 9.964 | 10 | 0.018483 | 2.3843 |  | 0.030161 | 3.8908 |  | 11.0825 |  | 17.3576 | 17.4203 | 1.4013 | 180.7706 |  | 0.47833 | 61.705 |  | 150.1944 |  |  | 392.67 | 13.8389 | 14 | 0.0014 | 0.1806 |  | 0.0047833 | 0.61705 |  | 1.6289 |  | 2.4266 | 2.4548 | -97.8975 |  |  | SoRtl | Lobby |  |  | Lobby534-2 | LobbyWG701
Lobby723 | LobbyIP701 |  |  | X | [11 empty] | ballast replacement |  | 723 |  | 129 |  |  | IP701 |  | 129 | 45.36 |  | 44.37 | [11 empty] | 13.8389 | 14 | 7.4661 | 963.1252 |  | 1.262 | 162.7954 |  | 1026.1195 |  | 2152.0401 | 2177.0899 | [10 empty] | 13.8389 | 14 | 7.2805 | 939.1879 |  | 1.2306 | 158.7493 |  | 1000.6165 |  | 2098.5538 | 2122.9809 | 0 | 378.4103 |  | SoRtl | Lobby |  |  | Lobby723 | LobbyIP701
Lobby522 | LobbyDL701 |  |  | X | [13 empty] | 522 |  | 129 |  |  | DL701 |  | 129 | 5.67 |  | 6.48 | [11 empty] | 0 | 0 | 0.775 | 99.975 |  | 0.41 | 52.89 |  | 194.6641 |  | 347.5291 | 0 | [10 empty] | 13.8389 | 14 | 0.4265 | 55.0189 |  | 0.19421 | 25.0532 |  | 97.2007 |  | 177.2728 | 179.3363 | 0 |  |  | SoRtl | Lobby |  |  | Lobby522 | LobbyDL701
Lobby0 | Lobby0 |  |  | X | [13 empty] | 0 |  | 129 |  |  | 0 |  | 129 | 1e-07 |  | 1e-05 | [11 empty] | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | [10 empty] | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0 |  |  | SoRtl | Lobby |  |  | Lobby0 | Lobby0
Lobby534-2 | LobbyWG701 |  |  | X | [13 empty] | 534-2 |  | 129 |  |  | WG701 |  | 129 | 12.96 |  | 12.978 | [11 empty] | 13.8389 | 14 | 0.16552 | 21.3517 |  | 0.33931 | 43.771 |  | 121.113 |  | 186.2357 | 188.4035 | [10 empty] | 13.8389 | 14 | 1.0499 | 135.4425 |  | 0.47833 | 61.705 |  | 239.3581 |  | 436.5056 | 441.5865 | 0 |  |  | SoRtl | Lobby |  |  | Lobby534-2 | LobbyWG701
Primary School | [13 empty] | Primary_School_Interior Lighting LPD |  | Primary School |  |  | 3774 |  | Primary School |  |  | 3774 |  | 2068.2367 | 593.6292 | 1911.6951 | 629.133
Restrooms | Restrooms |  |  |  | X | [10 empty] | Restrooms | 0.85 |  | 3774 | 2044 | Restrooms | 0.63 |  | 3774 | 2044 | 64.3956 |  | 65.7032 | [45 empty] | -9325.3843 |  |  | PriSch | Restrooms |  |  | Restrooms | Restrooms
Restrooms604 | RestroomsDL709 |  |  |  | X | [10 empty] | replacement costs are for lamps |  | 604 |  | 2044 |  |  | DL709 |  | 2044 | 24.669 | 82.8571 | 36.1788 | 56.4972 | 4.2525 | 8692.11 |  | 0.3637 | 743.3993 |  | 5075.0352 |  |  | 14510.5445 | 9.539 | 10 | 0.040431 | 82.641 |  | 0.065978 | 134.8587 |  | 384.1301 |  | 601.6298 | 630.7086 | 3.5159 | 7186.5062 |  | 1.0885 | 2224.9962 |  | 5750.7509 |  |  | 15162.2533 | 13.2485 | 14 | 0.003717 | 7.5975 |  | 0.010885 | 22.25 |  | 59.4438 |  | 89.2913 | 94.3559 | 651.7088 | -1050.2911 |  | PriSch | Restrooms |  |  | Restrooms604 | RestroomsDL709
Restrooms720 | Restrooms0 |  |  |  | X | [12 empty] | 720 |  | 2044 |  |  | 0 |  | 2044 | 18.5818 | 110 | 0 | 0 | 1.5353 | 3138.2275 |  | 0.55909 | 1142.7818 |  | 2676.513 |  |  | 6957.5223 | 13.2485 | 14 | 0.002 | 4.088 |  | 0.0055909 | 11.4278 |  | 30.652 |  | 46.1678 | 48.7865 | 0 | 0 |  | 0 | 0 |  | 0 |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | -6957.5223 |  |  | PriSch | Restrooms |  |  | Restrooms720 | Restrooms0
Restrooms0 | Restrooms0 |  |  |  | X | [12 empty] | 0 |  | 2044 |  |  | 0 |  | 2044 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0 |  |  | PriSch | Restrooms |  |  | Restrooms0 | Restrooms0
Restrooms534-2 | RestroomsWG701 |  |  |  | X | [12 empty] | 534-2 |  | 2044 |  |  | WG701 |  | 2044 | 21.1448 | 96.6667 | 29.5244 | 69.2308 | 3.9657 | 8105.8697 |  | 0.59867 | 1223.6829 |  | 5244.8652 |  |  | 14574.4178 | 9.539 | 10 | 0.034655 | 70.8352 |  | 0.056552 | 115.5932 |  | 329.2543 |  | 515.6827 | 540.6073 | 2.6025 | 5319.4192 |  | 0.88833 | 1815.7533 |  | 4419.6746 |  |  | 11554.8471 | 13.2485 | 14 | 0.0026 | 5.3144 |  | 0.0088833 | 18.1575 |  | 47.9333 |  | 71.4053 | 75.4554 | -3019.5707 |  |  | PriSch | Restrooms |  |  | Restrooms534-2 | RestroomsWG701
Restrooms604 | RestroomsDL709 |  |  |  | X | [10 empty] | ballast replacement |  | 604 |  | 2044 |  |  | DL709 |  | 2044 | 24.2393 |  | 28.7696 | [11 empty] | 13.2485 | 14 | 0.36207 | 740.069 |  | 0.74224 | 1517.1414 |  | 4197.8793 |  | 6455.0897 | 6821.2224 | [10 empty] | 13.2485 | 14 | 2.6341 | 5384.1815 |  | 1.0885 | 2224.9962 |  | 8956.8345 |  | 16566.0122 | 17505.6364 | 0 | 10143.7021 |  | PriSch | Restrooms |  |  | Restrooms604 | RestroomsDL709
Restrooms720 | Restrooms0 |  |  |  | X | [12 empty] | 720 |  | 2044 |  |  | 0 |  | 2044 | 12.6 |  | 1e-05 | [11 empty] | 13.2485 | 14 | 1.15 | 2350.6046 |  | 0.55909 | 1142.7818 |  | 4330.1365 |  | 7823.523 | 8267.2732 | [10 empty] | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0 |  |  | PriSch | Restrooms |  |  | Restrooms720 | Restrooms0
Restrooms0 | Restrooms0 |  |  |  | X | [12 empty] | 0 |  | 2044 |  |  | 0 |  | 2044 | 1e-07 |  | 1e-05 | [11 empty] | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | [10 empty] | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0 |  |  | PriSch | Restrooms |  |  | Restrooms0 | Restrooms0
Restrooms534-2 | RestroomsWG701 |  |  |  | X | [12 empty] | 534-2 |  | 2044 |  |  | WG701 |  | 2044 | 24.3 |  | 24.102 | [11 empty] | 13.2485 | 14 | 0.31034 | 634.3448 |  | 0.63621 | 1300.4069 |  | 3598.1823 |  | 5532.934 | 5846.762 | [10 empty] | 13.2485 | 14 | 1.9499 | 3985.5786 |  | 0.88833 | 1815.7533 |  | 7043.4362 |  | 12844.7681 | 13573.3234 | 0 |  |  | PriSch | Restrooms |  |  | Restrooms534-2 | RestroomsWG701
Dining Area | Dining Area |  |  |  | X | [10 empty] | Dining Area | 0.63 |  | 3774 | 3389 | Dining Area | 0.43 |  | 3774 | 3389 | 81.336 |  | 77.4941 | [45 empty] | 6769.6714 |  |  | PriSch | Dining Area |  |  | Dining Area | Dining Area
Dining Area731 | Dining AreaTR704 |  |  |  | X | [10 empty] | replacement costs are for lamps |  | 731 |  | 3389 |  |  | TR704 |  | 3389 | 13.556 | 250 | 19.0631 | 177.7778 | 1.5296 | 5183.8144 |  | 0.32251 | 1092.9728 |  | 3653.861 |  |  | 9930.6482 | 13.2485 | 14 | 0.0016 | 5.4224 |  | 0.00246 | 8.3369 |  | 23.9511 |  | 37.7104 | 39.8494 | 0.77805 | 2636.8115 |  | 0.34594 | 1172.3822 |  | 2453.7355 |  |  | 6262.9292 | 13.2485 | 14 | 0.0018 | 6.1002 |  | 0.0034594 | 11.7238 |  | 32.6878 |  | 50.5118 | 53.3768 | -3667.7191 | -793.7838 |  | PriSch | Dining Area |  |  | Dining Area731 | Dining AreaTR704
Dining Area522 | Dining AreaDL707 |  |  |  | X | [12 empty] | 522 |  | 3389 |  |  | DL707 |  | 3389 | 33.89 | 100 | 50.8349 | 66.6667 | 1.5518 | 5259.0502 |  | 0.615 | 2084.235 |  | 4648.6279 |  |  | 11991.9131 | 13.2485 | 14 | 0.0018 | 6.1002 |  | 0.00615 | 20.8423 |  | 55.0209 |  | 81.9634 | 86.6124 | 3.0613 | 10374.8592 |  | 0.9225 | 3126.3525 |  | 8219.2981 |  |  | 21720.5098 | 13.2485 | 14 | 0.0012 | 4.0668 |  | 0.009225 | 31.2635 |  | 79.2198 |  | 114.5501 | 121.0474 | 9728.5967 |  |  | PriSch | Dining Area |  |  | Dining Area522 | Dining AreaDL707
Dining Area0 | Dining Area0 |  |  |  | X | [12 empty] | 0 |  | 3389 |  |  | 0 |  | 3389 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0 |  |  | PriSch | Dining Area |  |  | Dining Area0 | Dining Area0
Dining Area537-1 | Dining AreaWW714 |  |  |  | X | [12 empty] | 537-1 |  | 3389 |  |  | WW714 |  | 3389 | 33.89 | 100 | 7.596 | 446.1539 | 1.0692 | 3623.5188 |  | 0.615 | 2084.235 |  | 3828.7478 |  |  | 9536.5016 | 9.539 | 10 | 0.0335 | 113.5315 |  | 0.054667 | 185.2676 |  | 527.7144 |  | 826.5135 | 866.4617 | 1.7249 | 5845.7562 |  | 0.22055 | 747.4498 |  | 3652.0893 |  |  | 10245.2953 | 13.2485 | 14 | 0.0013 | 4.4057 |  | 0.0013784 | 4.6716 |  | 14.3116 |  | 23.3888 | 24.7154 | 708.7938 |  |  | PriSch | Dining Area |  |  | Dining Area537-1 | Dining AreaWW714
Dining Area731 | Dining AreaTR704 |  |  |  | X | [10 empty] | ballast replacement |  | 731 |  | 3389 |  |  | TR704 |  | 3389 | 12.672 |  | 17.982 | [11 empty] | 13.2485 | 14 | 1.146 | 3883.794 |  | 0.32251 | 1092.9728 |  | 5206.8978 |  | 10183.6646 | 10761.2821 | [10 empty] | 13.2485 | 14 | 0.58219 | 1973.0334 |  | 0.34594 | 1172.3822 |  | 4156.6755 |  | 7302.0912 | 7716.2658 | 0 | 22922.1786 |  | PriSch | Dining Area |  |  | Dining Area731 | Dining AreaTR704
Dining Area522 | Dining AreaDL707 |  |  |  | X | [12 empty] | 522 |  | 3389 |  |  | DL707 |  | 3389 | 8.505 |  | 9.612 | [11 empty] | 0 | 0 | 1.1625 | 3939.7125 |  | 0.615 | 2084.235 |  | 7671.1232 |  | 13695.0707 | 0 | [10 empty] | 13.2485 | 14 | 2.2951 | 7778.0943 |  | 0.9225 | 3126.3525 |  | 12723.8837 |  | 23628.3305 | 24968.5294 | 0 |  |  | PriSch | Dining Area |  |  | Dining Area522 | Dining AreaDL707
Dining Area0 | Dining Area0 |  |  |  | X | [12 empty] | 0 |  | 3389 |  |  | 0 |  | 3389 | 1e-07 |  | 1e-05 | [11 empty] | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | [10 empty] | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0 |  |  | PriSch | Dining Area |  |  | Dining Area0 | Dining Area0
Dining Area537-1 | Dining AreaWW714 |  |  |  | X | [12 empty] | 537-1 |  | 3389 |  |  | WW714 |  | 3389 | 20.084 |  | 10.647 | [11 empty] | 13.2485 | 14 | 0.3 | 1016.7 |  | 0.615 | 2084.235 |  | 5767.0084 |  | 8867.9434 | 9370.9331 | [10 empty] | 13.2485 | 14 | 1.2927 | 4381.0129 |  | 0.22055 | 747.4498 |  | 4684.5423 |  | 9813.0049 | 10369.5986 | 0 |  |  | PriSch | Dining Area |  |  | Dining Area537-1 | Dining AreaWW714
Classroom/Lecture/Training | Classroom/Lecture/Training |  |  |  | X | [10 empty] | Classroom/Lecture/Training | 0.92 |  | 3774 | 37187 | Classroom/Lecture/Training | 0.71 |  | 3774 | 37187 | 944.2399 |  | 969.346 | [45 empty] | -84160.3423 |  |  | PriSch | Classroom/Lecture/Training |  |  | Classroom/Lecture/Training | Classroom/Lecture/Training
Classroom/Lecture/Training600_LED | Classroom/Lecture/TrainingTR701 |  |  |  | X | [10 empty] | replacement costs are for lamps |  | 600_LED |  | 37187 |  |  | TR701 |  | 37187 | 655.4209 | 56.7376 | 639.1514 | 58.1818 | 3.0385 | 112994.5589 |  | 1.6357 | 60825.3512 |  | 115369.5054 |  |  | 289189.4155 | 13.2485 | 14 | 0.00705 | 262.1683 |  | 0.010839 | 403.0838 |  | 1158.015 |  | 1823.2672 | 1926.6829 | 2.3774 | 88407.4441 |  | 1.057 | 39307.8211 |  | 82269.2448 |  |  | 209984.51 | 13.2485 | 14 | 0.0055 | 204.5285 |  | 0.01057 | 393.0782 |  | 1095.9614 |  | 1693.5681 | 1789.6273 | -79204.9055 | -73.5111 |  | PriSch | Classroom/Lecture/Training |  |  | Classroom/Lecture/Training600_LED | Classroom/Lecture/TrainingTR701
Classroom/Lecture/Training701 | Classroom/Lecture/TrainingDL706 |  |  |  | X | [12 empty] | 701 |  | 37187 |  |  | DL706 |  | 37187 | 216.9242 | 171.4286 | 278.9023 | 133.3334 | 0.96289 | 35806.978 |  | 0.35875 | 13340.8363 |  | 30830.1976 |  |  | 79978.0119 | 13.2485 | 14 | 0.0007 | 26.0309 |  | 0.0035875 | 133.4084 |  | 343.7008 |  | 503.1401 | 531.6782 | 1.238 | 46037.5432 |  | 0.46125 | 17152.5037 |  | 39638.8255 |  |  | 102828.8724 | 13.2485 | 14 | 0.0009 | 33.4683 |  | 0.0046125 | 171.525 |  | 441.901 |  | 646.8944 | 683.5862 | 22850.8605 |  |  | PriSch | Classroom/Lecture/Training |  |  | Classroom/Lecture/Training701 | Classroom/Lecture/TrainingDL706
Classroom/Lecture/Training0 | Classroom/Lecture/Training0 |  |  |  | X | [12 empty] | 0 |  | 37187 |  |  | 0 |  | 37187 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0 |  |  | PriSch | Classroom/Lecture/Training |  |  | Classroom/Lecture/Training0 | Classroom/Lecture/Training0
Classroom/Lecture/Training703 | Classroom/Lecture/TrainingWW714 |  |  |  | X | [12 empty] | 703 |  | 37187 |  |  | WW714 |  | 37187 | 71.8949 | 517.2414 | 51.2924 | 725.0001 | 1.4882 | 55341.0736 |  | 0.19024 | 7074.4549 |  | 34572.383 |  |  | 96987.9115 | 13.2485 | 14 | 0.00145 | 53.9211 |  | 0.001189 | 44.2153 |  | 143.4176 |  | 241.5541 | 255.2551 | 1.0615 | 39473.6158 |  | 0.13572 | 5047.1735 |  | 24660.8249 |  |  | 69181.6142 | 13.2485 | 14 | 0.0008 | 29.7496 |  | 0.00084828 | 31.5448 |  | 96.6391 |  | 157.9336 | 166.8916 | -27806.2974 |  |  | PriSch | Classroom/Lecture/Training |  |  | Classroom/Lecture/Training703 | Classroom/Lecture/TrainingWW714
Classroom/Lecture/Training600_LED | Classroom/Lecture/TrainingTR701 |  |  |  | X | [10 empty] | ballast replacement |  | 600_LED |  | 37187 |  |  | TR701 |  | 37187 | 63.45 |  | 56.925 | [11 empty] | 13.2485 | 14 | 2.2736 | 84549.2929 |  | 1.6357 | 60825.3512 |  | 204050.702 |  | 349425.346 | 369244.7517 | [10 empty] | 13.2485 | 14 | 1.7789 | 66152.1867 |  | 1.057 | 39307.8211 |  | 139365.6948 |  | 244825.7026 | 258712.2164 | 0 | -111384.5014 |  | PriSch | Classroom/Lecture/Training |  |  | Classroom/Lecture/Training600_LED | Classroom/Lecture/TrainingTR701
Classroom/Lecture/Training701 | Classroom/Lecture/TrainingDL706 |  |  |  | X | [12 empty] | 701 |  | 37187 |  |  | DL706 |  | 37187 | 4.284 |  | 5.508 | [11 empty] | 13.2485 | 14 | 0.72164 | 26835.7104 |  | 0.35875 | 13340.8363 |  | 50155.7451 |  | 90332.2917 | 95455.9392 | [10 empty] | 13.2485 | 14 | 0.92783 | 34503.0562 |  | 0.46125 | 17152.5037 |  | 64485.9579 |  | 116141.5179 | 122729.0647 | 0 |  |  | PriSch | Classroom/Lecture/Training |  |  | Classroom/Lecture/Training701 | Classroom/Lecture/TrainingDL706
Classroom/Lecture/Training0 | Classroom/Lecture/Training0 |  |  |  | X | [12 empty] | 0 |  | 37187 |  |  | 0 |  | 37187 | 1e-07 |  | 1e-05 | [11 empty] | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | [10 empty] | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0 |  |  | PriSch | Classroom/Lecture/Training |  |  | Classroom/Lecture/Training0 | Classroom/Lecture/Training0
Classroom/Lecture/Training703 | Classroom/Lecture/TrainingWW714 |  |  |  | X | [12 empty] | 703 |  | 37187 |  |  | WW714 |  | 37187 | 9.135 |  | 6.552 | [11 empty] | 13.2485 | 14 | 1.1151 | 41465.3644 |  | 0.19024 | 7074.4549 |  | 44338.206 |  | 92878.0252 | 98146.0668 | [10 empty] | 13.2485 | 14 | 0.79552 | 29582.8997 |  | 0.13572 | 5047.1735 |  | 31632.4894 |  | 66262.5626 | 70020.9751 | 0 |  |  | PriSch | Classroom/Lecture/Training |  |  | Classroom/Lecture/Training703 | Classroom/Lecture/TrainingWW714
Corridor/Transition | Corridor/Transition |  |  |  | X | [10 empty] | Corridor/Transition | 0.66 |  | 3774 | 12073 | Corridor/Transition | 0.41 |  | 3774 | 12073 | 427.3842 |  | 280.1845 | [45 empty] | -60506.9051 |  |  | PriSch | Corridor/Transition |  |  | Corridor/Transition | Corridor/Transition
Corridor/Transition701 | Corridor/TransitionDL706 |  |  |  | X | [10 empty] | replacement costs are for lamps |  | 701 |  | 12073 |  |  | DL706 |  | 12073 | 382.3117 | 31.5789 | 241.4598 | 50 | 5.2271 | 63106.9634 |  | 1.9475 | 23512.1675 |  | 54335.782 |  |  | 140954.9129 | 13.2485 | 14 | 0.0038 | 45.8774 |  | 0.019475 | 235.1217 |  | 605.7455 |  | 886.7445 | 937.0407 | 3.3013 | 39857.0295 |  | 1.23 | 14849.79 |  | 34317.336 |  |  | 89024.1555 | 13.2485 | 14 | 0.0024 | 28.9752 |  | 0.0123 | 148.4979 |  | 382.5761 |  | 560.0492 | 591.8152 | -51930.7574 | -382.63 |  | PriSch | Corridor/Transition |  |  | Corridor/Transition701 | Corridor/TransitionDL706
Corridor/Transition0 | Corridor/Transition0 |  |  |  | X | [12 empty] | 0 |  | 12073 |  |  | 0 |  | 12073 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0 |  |  | PriSch | Corridor/Transition |  |  | Corridor/Transition0 | Corridor/Transition0
Corridor/Transition0 | Corridor/Transition0 |  |  |  | X | [12 empty] | 0 |  | 12073 |  |  | 0 |  | 12073 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0 |  |  | PriSch | Corridor/Transition |  |  | Corridor/Transition0 | Corridor/Transition0
Corridor/Transition703 | Corridor/TransitionWW708 |  |  |  | X | [12 empty] | 703 |  | 12073 |  |  | WW708 |  | 12073 | 45.0725 | 267.8571 | 38.7247 | 311.7648 | 2.8737 | 34694.5825 |  | 0.36736 | 4435.1373 |  | 21674.2162 |  |  | 60803.9361 | 13.2485 | 14 | 0.0028 | 33.8044 |  | 0.002296 | 27.7196 |  | 89.9118 |  | 151.4358 | 160.0252 | 2.4683 | 29799.8315 |  | 0.31562 | 3810.5122 |  | 18617.4447 |  |  | 52227.7883 | 13.2485 | 14 | 0.0017 | 20.5241 |  | 0.0019726 | 23.8157 |  | 71.6993 |  | 116.0391 | 122.6208 | -8576.1477 |  |  | PriSch | Corridor/Transition |  |  | Corridor/Transition703 | Corridor/TransitionWW708
Corridor/Transition701 | Corridor/TransitionDL706 |  |  |  | X | [10 empty] | ballast replacement |  | 701 |  | 12073 |  |  | DL706 |  | 12073 | 23.256 |  | 14.688 | [11 empty] | 13.2485 | 14 | 3.9175 | 47295.8145 |  | 1.9475 | 23512.1675 |  | 88395.5291 |  | 159203.5111 | 168233.5343 | [10 empty] | 13.2485 | 14 | 2.4742 | 29871.0407 |  | 1.23 | 14849.79 |  | 55828.7552 |  | 100549.586 | 106252.7585 | 0 | -70646.3904 |  | PriSch | Corridor/Transition |  |  | Corridor/Transition701 | Corridor/TransitionDL706
Corridor/Transition0 | Corridor/Transition0 |  |  |  | X | [12 empty] | 0 |  | 12073 |  |  | 0 |  | 12073 | 1e-07 |  | 1e-05 | [11 empty] | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | [10 empty] | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0 |  |  | PriSch | Corridor/Transition |  |  | Corridor/Transition0 | Corridor/Transition0
Corridor/Transition0 | Corridor/Transition0 |  |  |  | X | [12 empty] | 0 |  | 12073 |  |  | 0 |  | 12073 | 1e-07 |  | 1e-05 | [11 empty] | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | [10 empty] | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0 |  |  | PriSch | Corridor/Transition |  |  | Corridor/Transition0 | Corridor/Transition0
Corridor/Transition703 | Corridor/TransitionWW708 |  |  |  | X | [12 empty] | 703 |  | 12073 |  |  | WW708 |  | 12073 | 17.64 |  | 15.147 | [11 empty] | 13.2485 | 14 | 2.1532 | 25995.5836 |  | 0.36736 | 4435.1373 |  | 27796.6336 |  | 58227.3545 | 61530.01 | [10 empty] | 13.2485 | 14 | 1.85 | 22334.4805 |  | 0.31562 | 3810.5122 |  | 23881.8786 |  | 50026.8713 | 52864.3954 | 0 |  |  | PriSch | Corridor/Transition |  |  | Corridor/Transition703 | Corridor/TransitionWW708
Gymnasium/Fitness-Fitness Area | Gymnasium/Fitness-Fitness Area |  |  |  | X | [10 empty] | Gymnasium/Fitness-Fitness Area | 0.5 |  | 3774 | 3841 | Gymnasium/Fitness-Fitness Area | 0.7 |  | 3774 | 3841 | 50.5395 |  | 81.4757 | [45 empty] | 35999.2693 |  |  | PriSch | Gymnasium/Fitness-Fitness Area |  |  | Gymnasium/Fitness-Fitness Area | Gymnasium/Fitness-Fitness Area
Gymnasium/Fitness-Fitness Area735 | Gymnasium/Fitness-Fitness AreaID701 |  |  |  | X | [10 empty] | replacement costs are for lamps |  | 735 |  | 3841 |  |  | ID701 |  | 3841 | 50.5395 | 76 | 81.4757 | 47.1429 | 8.8116 | 33845.2747 |  | 1.0609 | 4074.8209 |  | 20900.5832 |  |  | 58820.6788 | 13.2485 | 14 | 0.005 | 19.205 |  | 0.0080921 | 31.0818 |  | 88.636 |  | 138.9228 | 146.8025 | 14.2043 | 54558.6115 |  | 1.7103 | 6569.1052 |  | 33692.2314 |  |  | 94819.9481 | 13.2485 | 14 | 0.007 | 26.887 |  | 0.013045 | 50.1076 |  | 140.2383 |  | 217.2329 | 229.5543 | 35999.2693 | 82.7518 |  | PriSch | Gymnasium/Fitness-Fitness Area |  |  | Gymnasium/Fitness-Fitness Area735 | Gymnasium/Fitness-Fitness AreaID701
Gymnasium/Fitness-Fitness Area0 | Gymnasium/Fitness-Fitness Area0 |  |  |  | X | [12 empty] | 0 |  | 3841 |  |  | 0 |  | 3841 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0 |  |  | PriSch | Gymnasium/Fitness-Fitness Area |  |  | Gymnasium/Fitness-Fitness Area0 | Gymnasium/Fitness-Fitness Area0
Gymnasium/Fitness-Fitness Area0 | Gymnasium/Fitness-Fitness Area0 |  |  |  | X | [12 empty] | 0 |  | 3841 |  |  | 0 |  | 3841 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0 |  |  | PriSch | Gymnasium/Fitness-Fitness Area |  |  | Gymnasium/Fitness-Fitness Area0 | Gymnasium/Fitness-Fitness Area0
Gymnasium/Fitness-Fitness Area0 | Gymnasium/Fitness-Fitness Area0 |  |  |  | X | [12 empty] | 0 |  | 3841 |  |  | 0 |  | 3841 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0 |  |  | PriSch | Gymnasium/Fitness-Fitness Area |  |  | Gymnasium/Fitness-Fitness Area0 | Gymnasium/Fitness-Fitness Area0
Gymnasium/Fitness-Fitness Area735 | Gymnasium/Fitness-Fitness AreaID701 |  |  |  | X | [10 empty] | ballast replacement |  | 735 |  | 3841 |  |  | ID701 |  | 3841 | 45 |  | 69.3 | [11 empty] | 13.2485 | 14 | 6.6049 | 25369.5523 |  | 1.0609 | 4074.8209 |  | 26506.3362 |  | 55950.7094 | 59124.2336 | [10 empty] | 13.2485 | 14 | 10.648 | 40898.7934 |  | 1.7103 | 6569.1052 |  | 42731.4268 |  | 90199.3254 | 95315.4311 | 0 | 36191.1975 |  | PriSch | Gymnasium/Fitness-Fitness Area |  |  | Gymnasium/Fitness-Fitness Area735 | Gymnasium/Fitness-Fitness AreaID701
Gymnasium/Fitness-Fitness Area0 | Gymnasium/Fitness-Fitness Area0 |  |  |  | X | [12 empty] | 0 |  | 3841 |  |  | 0 |  | 3841 | 1e-07 |  | 1e-05 | [11 empty] | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | [10 empty] | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0 |  |  | PriSch | Gymnasium/Fitness-Fitness Area |  |  | Gymnasium/Fitness-Fitness Area0 | Gymnasium/Fitness-Fitness Area0
Gymnasium/Fitness-Fitness Area0 | Gymnasium/Fitness-Fitness Area0 |  |  |  | X | [12 empty] | 0 |  | 3841 |  |  | 0 |  | 3841 | 1e-07 |  | 1e-05 | [11 empty] | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | [10 empty] | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0 |  |  | PriSch | Gymnasium/Fitness-Fitness Area |  |  | Gymnasium/Fitness-Fitness Area0 | Gymnasium/Fitness-Fitness Area0
Gymnasium/Fitness-Fitness Area0 | Gymnasium/Fitness-Fitness Area0 |  |  |  | X | [12 empty] | 0 |  | 3841 |  |  | 0 |  | 3841 | 1e-07 |  | 1e-05 | [11 empty] | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | [10 empty] | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0 |  |  | PriSch | Gymnasium/Fitness-Fitness Area |  |  | Gymnasium/Fitness-Fitness Area0 | Gymnasium/Fitness-Fitness Area0
Food Preparation | Food Preparation |  |  |  | 0 | [10 empty] | Food Preparation | 1.06 |  | 3774 | 1808 | Food Preparation | 1.09 |  | 3774 | 1808 | 47.8582 |  | 60.7133 | [45 empty] | -12784.102 |  |  |  | Food Preparation |  |  | Food Preparation | Food Preparation
Food Preparation731 | Food PreparationTR704 |  |  |  | 0 | [10 empty] | replacement costs are for lamps |  | 731 |  | 1808 |  |  | TR704 |  | 1808 | 40.68 | 44.4444 | 51.415 | 35.1648 | 8.604 | 15556.032 |  | 1.8141 | 3279.886 |  | 10964.8174 |  |  | 29800.7355 | 13.2485 | 14 | 0.009 | 16.272 |  | 0.013838 | 25.0182 |  | 71.8745 |  | 113.1647 | 119.5834 | 3.9335 | 7111.7228 |  | 1.7489 | 3162.0225 |  | 6617.9502 |  |  | 16891.6955 | 13.2485 | 14 | 0.0091 | 16.4528 |  | 0.017489 | 31.6202 |  | 88.162 |  | 136.235 | 143.9622 | -12909.0399 | 29.7998 |  |  | Food Preparation |  |  | Food Preparation731 | Food PreparationTR704
Food Preparation730 | Food PreparationTR703 |  |  |  | 0 | [10 empty] | Not included in costs, as increase due to IES, not 90.1 |  | 730 |  | 1808 |  |  | TR703 |  | 1808 | 7.1782 | 251.875 | 9.2983 | 194.4445 | 0.7599 | 1373.9005 |  | 0.24417 | 441.4571 |  | 1114.948 |  |  | 2930.3056 | 13.2485 | 14 | 0.0015881 | 2.8713 |  | 0.0024417 | 4.4146 |  | 12.6826 |  | 19.9684 | 21.101 | 0.71151 | 1286.4178 |  | 0.31629 | 571.8446 |  | 1196.9811 |  |  | 3055.2435 | 13.2485 | 14 | 0.0018 | 3.2544 |  | 0.0031629 | 5.7184 |  | 16.1256 |  | 25.0984 | 26.522 | 124.9379 | -11476.4734 |  |  | Food Preparation |  |  | Food Preparation730 | Food PreparationTR703
Food Preparation0 | Food Preparation0 |  |  |  | 0 | [12 empty] | 0 |  | 1808 |  |  | 0 |  | 1808 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0 |  |  |  | Food Preparation |  |  | Food Preparation0 | Food Preparation0
Food Preparation0 | Food Preparation0 |  |  |  | 0 | [12 empty] | 0 |  | 1808 |  |  | 0 |  | 1808 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0 |  |  |  | Food Preparation |  |  | Food Preparation0 | Food Preparation0
Food Preparation731 | Food PreparationTR704 |  |  |  | 0 | [10 empty] | ballast replacement |  | 731 |  | 1808 |  |  | TR704 |  | 1808 | 71.28 |  | 90.909 | [11 empty] | 13.2485 | 14 | 6.4463 | 11654.82 |  | 1.8141 | 3279.886 |  | 15625.3026 |  | 30560.0086 | 32293.3723 | [10 empty] | 13.2485 | 14 | 2.9433 | 5321.4525 |  | 1.7489 | 3162.0225 |  | 11210.9359 |  | 19694.4109 | 20811.4779 | 0 | -11121.6535 |  |  | Food Preparation |  |  | Food Preparation731 | Food PreparationTR704
Food Preparation730 | Food PreparationTR703 |  |  |  | 0 | [12 empty] | 730 |  | 1808 |  |  | TR703 |  | 1808 | 13.968 |  | 17.982 | [11 empty] | 13.2485 | 14 | 0.56873 | 1028.272 |  | 0.24417 | 441.4571 |  | 1751.0555 |  | 3220.7846 | 3403.4675 | [10 empty] | 13.2485 | 14 | 0.53229 | 962.3726 |  | 0.31629 | 571.8446 |  | 2027.4722 |  | 3561.6894 | 3763.7084 | 0 |  |  |  | Food Preparation |  |  | Food Preparation730 | Food PreparationTR703
Food Preparation0 | Food Preparation0 |  |  |  | 0 | [12 empty] | 0 |  | 1808 |  |  | 0 |  | 1808 | 1e-07 |  | 1e-05 | [11 empty] | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | [10 empty] | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0 |  |  |  | Food Preparation |  |  | Food Preparation0 | Food Preparation0
Food Preparation0 | Food Preparation0 |  |  |  | 0 | [12 empty] | 0 |  | 1808 |  |  | 0 |  | 1808 | 1e-07 |  | 1e-05 | [11 empty] | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | [10 empty] | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0 |  |  |  | Food Preparation |  |  | Food Preparation0 | Food Preparation0
Library | Library |  |  |  | 0 | [10 empty] | Library | 0.82 |  | 3774 | 4293 | Library | 0.96 |  | 3774 | 4293 | 118.9305 |  | 147.746 | [45 empty] | 33344.4237 |  |  |  | Library |  |  | Library | Library
Library735 | LibraryID701 |  |  |  | 0 | [10 empty] | replacement costs are for lamps |  | 735 |  | 4293 |  |  | ID701 |  | 4293 | 56.4868 | 76 | 81.3068 | 52.8 | 8.8116 | 37828.1084 |  | 1.0609 | 4554.3364 |  | 23360.1155 |  |  | 65742.5603 | 13.2485 | 14 | 0.005 | 21.465 |  | 0.0080921 | 34.7394 |  | 99.0665 |  | 155.2709 | 164.0779 | 12.6824 | 54445.4847 |  | 1.527 | 6555.4842 |  | 33622.3708 |  |  | 94623.3396 | 13.2485 | 14 | 0.00625 | 26.8313 |  | 0.011648 | 50.0037 |  | 139.9475 |  | 216.7824 | 229.0783 | 28880.7793 | 74.3316 |  |  | Library |  |  | Library735 | LibraryID701
Library720 | LibraryDL709 |  |  |  | 0 | [10 empty] | Not included in costs, as increase due to IES, not 90.1 |  | 720 |  | 4293 |  |  | DL709 |  | 4293 | 62.4436 | 68.75 | 66.4393 | 64.6154 | 2.4565 | 10545.9184 |  | 0.89455 | 3840.2836 |  | 8994.3407 |  |  | 23380.5428 | 13.2485 | 14 | 0.0032 | 13.7376 |  | 0.0089455 | 38.4028 |  | 103.0052 |  | 155.1456 | 163.9455 | 3.0742 | 13197.4067 |  | 0.95179 | 4086.0161 |  | 10560.7644 |  |  | 27844.1872 | 13.2485 | 14 | 0.00325 | 13.9522 |  | 0.0095179 | 40.8602 |  | 109.1635 |  | 163.9759 | 173.2766 | 4463.6444 | 29045.2897 |  |  | Library |  |  | Library720 | LibraryDL709
Library0 | Library0 |  |  |  | 0 | [12 empty] | 0 |  | 4293 |  |  | 0 |  | 4293 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0 |  |  |  | Library |  |  | Library0 | Library0
Library0 | Library0 |  |  |  | 0 | [12 empty] | 0 |  | 4293 |  |  | 0 |  | 4293 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0 |  |  |  | Library |  |  | Library0 | Library0
Library735 | LibraryID701 |  |  |  | 0 | [10 empty] | ballast replacement |  | 735 |  | 4293 |  |  | ID701 |  | 4293 | 45 |  | 61.875 | [11 empty] | 13.2485 | 14 | 6.6049 | 28354.9826 |  | 1.0609 | 4554.3364 |  | 29625.5405 |  | 62534.8595 | 66081.8367 | [10 empty] | 13.2485 | 14 | 9.5071 | 40813.9901 |  | 1.527 | 6555.4842 |  | 42642.8235 |  | 90012.2978 | 95117.7953 | 0 | 33401.6483 |  |  | Library |  |  | Library735 | LibraryID701
Library720 | LibraryDL709 |  |  |  | 0 | [12 empty] | 720 |  | 4293 |  |  | DL709 |  | 4293 | 20.16 |  | 25.155 | [11 empty] | 13.2485 | 14 | 1.84 | 7899.1356 |  | 0.89455 | 3840.2836 |  | 14551.2925 |  | 26290.7117 | 27781.9209 | [10 empty] | 13.2485 | 14 | 2.3032 | 9887.5908 |  | 0.95179 | 4086.0161 |  | 16448.4639 |  | 30422.0708 | 32147.6107 | 0 |  |  |  | Library |  |  | Library720 | LibraryDL709
Library0 | Library0 |  |  |  | 0 | [12 empty] | 0 |  | 4293 |  |  | 0 |  | 4293 | 1e-07 |  | 1e-05 | [11 empty] | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | [10 empty] | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0 |  |  |  | Library |  |  | Library0 | Library0
Library0 | Library0 |  |  |  | 0 | [12 empty] | 0 |  | 4293 |  |  | 0 |  | 4293 | 1e-07 |  | 1e-05 | [11 empty] | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | [10 empty] | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0 |  |  |  | Library |  |  | Library0 | Library0
Lobby | Lobby |  |  |  | X | [10 empty] | Lobby | 1 |  | 3774 | 1840 | Lobby | 0.84 |  | 3774 | 1840 | 51.2184 |  | 48.2058 | [45 empty] | -4261.093 |  |  | PriSch | Lobby |  |  | Lobby | Lobby
Lobby723 | LobbyIP701 |  |  |  | X | [10 empty] | replacement costs are for lamps |  | 723 |  | 1840 |  |  | IP701 |  | 1840 | 28.8 | 63.8889 | 28.0842 | 65.5173 | 9.962 | 18330.048 |  | 1.262 | 2322.0432 |  | 11430.6259 |  |  | 32082.7171 | 13.2485 | 14 | 0.0072 | 13.248 |  | 0.0096261 | 17.712 |  | 52.0103 |  | 82.9703 | 87.6763 | 9.7132 | 17872.2299 |  | 1.2306 | 2264.3316 |  | 11145.4052 |  |  | 31281.9666 | 13.2485 | 14 | 0.0058 | 10.672 |  | 0.0093868 | 17.2718 |  | 49.254 |  | 77.1978 | 81.5765 | -800.7505 | -243.5449 |  | PriSch | Lobby |  |  | Lobby723 | LobbyIP701
Lobby522 | LobbyDL701 |  |  |  | X | [12 empty] | 522 |  | 1840 |  |  | DL701 |  | 1840 | 12.2667 | 150 | 5.8105 | 316.6667 | 1.0345 | 1903.5413 |  | 0.41 | 754.4 |  | 1682.5957 |  |  | 4340.537 | 13.2485 | 14 | 0.0012 | 2.208 |  | 0.0041 | 7.544 |  | 19.9151 |  | 29.6671 | 31.3498 | 0.56987 | 1048.5629 |  | 0.19421 | 357.3474 |  | 870.6516 |  |  | 2276.5619 | 13.2485 | 14 | 0.0012 | 2.208 |  | 0.0019421 | 3.5735 |  | 10.1905 |  | 15.972 | 16.8779 | -2063.9751 |  |  | PriSch | Lobby |  |  | Lobby522 | LobbyDL701
Lobby0 | Lobby0 |  |  |  | X | [12 empty] | 0 |  | 1840 |  |  | 0 |  | 1840 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0 |  |  | PriSch | Lobby |  |  | Lobby0 | Lobby0
Lobby534-2 | LobbyWG701 |  |  |  | X | [12 empty] | 534-2 |  | 1840 |  |  | WG701 |  | 1840 | 10.1517 | 181.25 | 14.3111 | 128.5715 | 2.115 | 3891.6634 |  | 0.31929 | 587.4955 |  | 2518.0827 |  |  | 6997.2417 | 9.539 | 10 | 0.018483 | 34.0083 |  | 0.030161 | 55.4968 |  | 158.0764 |  | 247.5815 | 259.5479 | 1.4013 | 2578.4329 |  | 0.47833 | 880.1333 |  | 2142.308 |  |  | 5600.8742 | 13.2485 | 14 | 0.0014 | 2.576 |  | 0.0047833 | 8.8013 |  | 23.2343 |  | 34.6116 | 36.5748 | -1396.3674 |  |  | PriSch | Lobby |  |  | Lobby534-2 | LobbyWG701
Lobby723 | LobbyIP701 |  |  |  | X | [10 empty] | ballast replacement |  | 723 |  | 1840 |  |  | IP701 |  | 1840 | 45.36 |  | 44.37 | [11 empty] | 13.2485 | 14 | 7.4661 | 13737.6 |  | 1.262 | 2322.0432 |  | 14636.1232 |  | 30695.7664 | 32436.8303 | [10 empty] | 13.2485 | 14 | 7.2805 | 13396.1684 |  | 1.2306 | 2264.3316 |  | 14272.3599 |  | 29932.86 | 31630.6518 | 0 | 5637.9986 |  | PriSch | Lobby |  |  | Lobby723 | LobbyIP701
Lobby522 | LobbyDL701 |  |  |  | X | [12 empty] | 522 |  | 1840 |  |  | DL701 |  | 1840 | 5.67 |  | 6.48 | [11 empty] | 0 | 0 | 0.775 | 1426 |  | 0.41 | 754.4 |  | 2776.6041 |  | 4957.0041 | 0 | [10 empty] | 13.2485 | 14 | 0.4265 | 784.7662 |  | 0.19421 | 357.3474 |  | 1386.4291 |  | 2528.5426 | 2671.9616 | 0 |  |  | PriSch | Lobby |  |  | Lobby522 | LobbyDL701
Lobby0 | Lobby0 |  |  |  | X | [12 empty] | 0 |  | 1840 |  |  | 0 |  | 1840 | 1e-07 |  | 1e-05 | [11 empty] | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | [10 empty] | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0 |  |  | PriSch | Lobby |  |  | Lobby0 | Lobby0
Lobby534-2 | LobbyWG701 |  |  |  | X | [12 empty] | 534-2 |  | 1840 |  |  | WG701 |  | 1840 | 12.96 |  | 12.978 | [11 empty] | 13.2485 | 14 | 0.16552 | 304.5517 |  | 0.33931 | 624.331 |  | 1727.503 |  | 2656.3858 | 2807.056 | [10 empty] | 13.2485 | 14 | 1.0499 | 1931.8927 |  | 0.47833 | 880.1333 |  | 3414.0997 |  | 6226.1257 | 6579.2716 | 0 |  |  | PriSch | Lobby |  |  | Lobby534-2 | LobbyWG701
Electrical/Mechanical | Electrical/Mechanical |  |  |  | X | [10 empty] | Electrical/Mechanical | 0.43 |  | 3774 | 2712 | Electrical/Mechanical | 0.43 |  | 3774 | 2712 | 70.6547 |  | 71.0983 | [45 empty] | -1782.4683 |  |  | PriSch | Electrical/Mechanical |  |  | Electrical/Mechanical | Electrical/Mechanical
Electrical/Mechanical738 | Electrical/MechanicalLB702 |  |  |  | X | [10 empty] | replacement costs are for lamps |  | 738 |  | 2712 |  |  | LB702 |  | 2712 | 16.4147 | 165.2174 | 16.8584 | 160.8696 | 1.5155 | 4109.9218 |  | 0.35027 | 949.9454 |  | 2977.4351 |  |  | 8037.3024 | 13.2485 | 14 | 0.0023 | 6.2376 |  | 0.0037224 | 10.0951 |  | 28.7881 |  | 45.1208 | 47.68 | 1.0653 | 2889.0203 |  | 0.35974 | 975.6196 |  | 2390.1941 |  |  | 6254.8341 | 13.2485 | 14 | 0.0023 | 6.2376 |  | 0.003823 | 10.3679 |  | 29.4564 |  | 46.0619 | 48.6745 | -1782.4683 | 0.99446 |  | PriSch | Electrical/Mechanical |  |  | Electrical/Mechanical738 | Electrical/MechanicalLB702
Electrical/Mechanical739 | Electrical/MechanicalTL702 |  |  |  | X | [12 empty] | 739 |  | 2712 |  |  | TL702 |  | 2712 | 54.24 | 50 | 54.2399 | 50.0001 | 2.562 | 6948.144 |  | 0.6027 | 1634.5224 |  | 5061.1663 |  |  | 13643.8327 | 13.2485 | 14 | 0.002 | 5.424 |  | 0.0123 | 33.3576 |  | 85.2327 |  | 124.0143 | 131.0484 | 2.562 | 6948.144 |  | 0.6027 | 1634.5224 |  | 5061.1663 |  |  | 13643.8327 | 13.2485 | 14 | 0.002 | 5.424 |  | 0.0123 | 33.3576 |  | 85.2327 |  | 124.0143 | 131.0484 | 0 |  |  | PriSch | Electrical/Mechanical |  |  | Electrical/Mechanical739 | Electrical/MechanicalTL702
Electrical/Mechanical0 | Electrical/Mechanical0 |  |  |  | X | [12 empty] | 0 |  | 2712 |  |  | 0 |  | 2712 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0 |  |  | PriSch | Electrical/Mechanical |  |  | Electrical/Mechanical0 | Electrical/Mechanical0
Electrical/Mechanical0 | Electrical/Mechanical0 |  |  |  | X | [12 empty] | 0 |  | 2712 |  |  | 0 |  | 2712 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0 |  |  | PriSch | Electrical/Mechanical |  |  | Electrical/Mechanical0 | Electrical/Mechanical0
Electrical/Mechanical738 | Electrical/MechanicalLB702 |  |  |  | X | [10 empty] | ballast replacement |  | 738 |  | 2712 |  |  | LB702 |  | 2712 | 23.805 |  | 21.321 | [11 empty] | 13.2485 | 14 | 1.1349 | 3077.7632 |  | 0.35027 | 949.9454 |  | 4331.5289 |  | 8359.2375 | 8833.3734 | [10 empty] | 13.2485 | 14 | 0.79723 | 2162.087 |  | 0.35974 | 975.6196 |  | 3797.9185 |  | 6935.6251 | 7329.0138 | 0 | -1504.3596 |  | PriSch | Electrical/Mechanical |  |  | Electrical/Mechanical738 | Electrical/MechanicalLB702
Electrical/Mechanical739 | Electrical/MechanicalTL702 |  |  |  | X | [12 empty] | 739 |  | 2712 |  |  | TL702 |  | 2712 | 12.24 |  | 12.24 | [11 empty] | 13.2485 | 14 | 1.92 | 5207.04 |  | 0.6027 | 1634.5224 |  | 7395.2524 |  | 14236.8148 | 15044.327 | [10 empty] | 13.2485 | 14 | 1.92 | 5207.04 |  | 0.6027 | 1634.5224 |  | 7395.2524 |  | 14236.8148 | 15044.327 | 0 |  |  | PriSch | Electrical/Mechanical |  |  | Electrical/Mechanical739 | Electrical/MechanicalTL702
Electrical/Mechanical0 | Electrical/Mechanical0 |  |  |  | X | [12 empty] | 0 |  | 2712 |  |  | 0 |  | 2712 | 1e-07 |  | 1e-05 | [11 empty] | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | [10 empty] | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0 |  |  | PriSch | Electrical/Mechanical |  |  | Electrical/Mechanical0 | Electrical/Mechanical0
Electrical/Mechanical0 | Electrical/Mechanical0 |  |  |  | X | [12 empty] | 0 |  | 2712 |  |  | 0 |  | 2712 | 1e-07 |  | 1e-05 | [11 empty] | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | [10 empty] | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0 |  |  | PriSch | Electrical/Mechanical |  |  | Electrical/Mechanical0 | Electrical/Mechanical0
Office-Enclosed | Office-Enclosed |  |  |  | X | [10 empty] | Office-Enclosed | 0.93 |  | 3774 | 4745 | Office-Enclosed | 0.74 |  | 3774 | 4745 | 211.6797 |  | 109.7281 | [45 empty] | -29435.1606 |  |  | PriSch | Office-Enclosed |  |  | Office-Enclosed | Office-Enclosed
Office-Enclosed700 | Office-EnclosedTR701 |  |  |  | X | [10 empty] | replacement costs are for lamps |  | 700 |  | 4745 |  |  | TR701 |  | 4745 | 88.3097 | 53.7313 | 109.7281 | 43.2433 | 2.575 | 12218.5332 |  | 1.7272 | 8195.4513 |  | 14037.6726 |  |  | 34451.6571 | 13.2485 | 14 | 0.0067 | 31.7915 |  | 0.011446 | 54.3105 |  | 153.7269 |  | 239.8289 | 253.432 | 3.1987 | 15177.5943 |  | 1.4222 | 6748.2797 |  | 14123.8018 |  |  | 36049.6757 | 13.2485 | 14 | 0.0074 | 35.113 |  | 0.014222 | 67.4828 |  | 188.1522 |  | 290.748 | 307.2392 | 1598.0186 | -244.2651 |  | PriSch | Office-Enclosed |  |  | Office-Enclosed700 | Office-EnclosedTR701
Office-Enclosed739 | Office-Enclosed0 |  |  |  | X | [12 empty] | 739 |  | 4745 |  |  | 0 |  | 4745 | 123.37 | 38.4615 | 0 | 0 | 3.3306 | 15803.697 |  | 0.78351 | 3717.755 |  | 11511.7273 |  |  | 31033.1793 | 13.2485 | 14 | 0.0026 | 12.337 |  | 0.01599 | 75.8726 |  | 193.8636 |  | 282.0732 | 298.0724 | 0 | 0 |  | 0 | 0 |  | 0 |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | -31033.1793 |  |  | PriSch | Office-Enclosed |  |  | Office-Enclosed739 | Office-Enclosed0
Office-Enclosed0 | Office-Enclosed0 |  |  |  | X | [12 empty] | 0 |  | 4745 |  |  | 0 |  | 4745 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0 |  |  | PriSch | Office-Enclosed |  |  | Office-Enclosed0 | Office-Enclosed0
Office-Enclosed0 | Office-Enclosed0 |  |  |  | X | [12 empty] | 0 |  | 4745 |  |  | 0 |  | 4745 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0 |  |  | PriSch | Office-Enclosed |  |  | Office-Enclosed0 | Office-Enclosed0
Office-Enclosed700 | Office-EnclosedTR701 |  |  |  | X | [10 empty] | ballast replacement |  | 700 |  | 4745 |  |  | TR701 |  | 4745 | 62.109 |  | 76.59 | [11 empty] | 13.2485 | 14 | 1.9263 | 9140.0562 |  | 1.7272 | 8195.4513 |  | 26026.3305 |  | 43361.8381 | 45821.3215 | [10 empty] | 13.2485 | 14 | 2.3934 | 11356.8609 |  | 1.4222 | 6748.2797 |  | 23925.9939 |  | 42031.1345 | 44415.1405 | 0 | -35624.8134 |  | PriSch | Office-Enclosed |  |  | Office-Enclosed700 | Office-EnclosedTR701
Office-Enclosed739 | Office-Enclosed0 |  |  |  | X | [12 empty] | 739 |  | 4745 |  |  | 0 |  | 4745 | 15.912 |  | 1e-05 | [11 empty] | 13.2485 | 14 | 2.496 | 11843.52 |  | 0.78351 | 3717.755 |  | 16820.6544 |  | 32381.9293 | 34218.6324 | [10 empty] | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0 |  |  | PriSch | Office-Enclosed |  |  | Office-Enclosed739 | Office-Enclosed0
Office-Enclosed0 | Office-Enclosed0 |  |  |  | X | [12 empty] | 0 |  | 4745 |  |  | 0 |  | 4745 | 1e-07 |  | 1e-05 | [11 empty] | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | [10 empty] | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0 |  |  | PriSch | Office-Enclosed |  |  | Office-Enclosed0 | Office-Enclosed0
Office-Enclosed0 | Office-Enclosed0 |  |  |  | X | [12 empty] | 0 |  | 4745 |  |  | 0 |  | 4745 | 1e-07 |  | 1e-05 | [11 empty] | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | [10 empty] | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0 |  |  | PriSch | Office-Enclosed |  |  | Office-Enclosed0 | Office-Enclosed0
Small Hotel | [13 empty] | Small_Hotel_Interior Lighting LPD |  | Small Hotel |  |  |  |  | Small Hotel |  |  |  |  | 1021.0561 | 537.6309 | 593.773 | 574.4356
Highway Lodging Guest Rooms | Highway Lodging Guest Rooms |  |  |  |  | X | [9 empty] | Highway Lodging Guest Rooms | 0.77 |  | 3588 | 27933 | Highway Lodging Guest Rooms | 0.41 |  | 3588 | 27933 | 595.7738 |  | 263.4161 |  | 2.7561 | [21 empty] | 5.1471 | [21 empty] | 71267.1299 |  |  | SmHtl | Highway Lodging Guest Rooms |  |  | Highway Lodging Guest Rooms | Highway Lodging Guest Rooms
Highway Lodging Guest Rooms524 | Highway Lodging Guest Roomsww714 |  |  |  |  | X | [9 empty] | replacement costs are for lamps |  | 524 |  | 27933 |  |  | WW714 |  | 27933 | 494.1992 | 56.5217 | 154.1131 | 181.25 | 2.142 | 59832.7009 |  | 1.0881 | 30393.2527 |  | 59338.0229 |  |  | 149563.9765 | 2.7871 | 3 | 0.55554 | 15517.8558 |  | 0.10262 | 2866.3555 |  | 17128.9508 |  | 35513.1622 | 38226.3677 | 4.246 | 118602.3622 |  | 0.5429 | 15164.7294 |  | 74095.8744 |  |  | 207862.966 | 13.9353 | 14 | 0.0032 | 89.3856 |  | 0.0033931 | 94.7796 |  | 290.3618 |  | 474.527 | 476.7288 | 58298.9895 | -37728.5344 |  | SmHtl | Highway Lodging Guest Rooms |  |  | Highway Lodging Guest Rooms524 | Highway Lodging Guest RoomsWW714
Highway Lodging Guest Rooms720 | Highway Lodging Guest RoomsDL703 |  |  |  |  | X | [11 empty] | 720 |  | 27933 |  |  | DL703 |  | 27933 | 101.5745 | 275 | 109.303 | 255.5557 | 0.61413 | 17154.6203 |  | 0.22364 | 6246.8345 |  | 14630.7314 |  |  | 38032.1862 | 13.9353 | 14 | 0.0008 | 22.3464 |  | 0.0022364 | 62.4683 |  | 167.5544 |  | 252.3691 | 253.5401 | 0.9011 | 25170.3376 |  | 0.24065 | 6722.1372 |  | 19107.8518 |  |  | 51000.3266 | 13.9353 | 14 | 0.0009 | 25.1397 |  | 0.0024065 | 67.2214 |  | 181.0151 |  | 273.3762 | 274.6446 | 12968.1404 |  |  | SmHtl | Highway Lodging Guest Rooms |  |  | Highway Lodging Guest Rooms720 | Highway Lodging Guest RoomsDL703
Highway Lodging Guest Rooms0 | Highway Lodging Guest Rooms0 |  |  |  |  | X | [11 empty] | 0 |  | 27933 |  |  | 0 |  | 27933 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0 |  |  | SmHtl | Highway Lodging Guest Rooms |  |  | Highway Lodging Guest Rooms0 | Highway Lodging Guest Rooms0
Highway Lodging Guest Rooms0 | Highway Lodging Guest Rooms0 |  |  |  |  | X | [11 empty] | 0 |  | 27933 |  |  | 0 |  | 27933 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0 |  |  | SmHtl | Highway Lodging Guest Rooms |  |  | Highway Lodging Guest Rooms0 | Highway Lodging Guest Rooms0
Highway Lodging Guest Rooms524 | Highway Lodging Guest Roomsww714 |  |  |  |  | X | [9 empty] | ballast replacement |  | 524 |  | 27933 |  |  | WW714 |  | 27933 | 14.3358 |  | 26.208 | [11 empty] | 13.9353 | 14 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | [10 empty] | 13.9353 | 14 | 3.1821 | 88884.7324 |  | 0.5429 | 15164.7294 |  | 95042.9264 |  | 199092.3882 | 200016.1769 | 0 | 211633.7871 |  | SmHtl | Highway Lodging Guest Rooms |  |  | Highway Lodging Guest Rooms524 | Highway Lodging Guest RoomsWW714
Highway Lodging Guest Rooms720 | Highway Lodging Guest RoomsDL703 |  |  |  |  | X | [11 empty] | 720 |  | 27933 |  |  | DL703 |  | 27933 | 5.04 |  | 8.343 | [11 empty] | 13.9353 | 14 | 0.46 | 12849.2054 |  | 0.22364 | 6246.8345 |  | 23670.0008 |  | 42766.0407 | 42964.4751 | [10 empty] | 13.9353 | 14 | 0.67515 | 18858.8985 |  | 0.24065 | 6722.1372 |  | 28748.9585 |  | 54329.9942 | 54582.0853 | 0 |  |  | SmHtl | Highway Lodging Guest Rooms |  |  | Highway Lodging Guest Rooms720 | Highway Lodging Guest RoomsDL703
Highway Lodging Guest Rooms0 | Highway Lodging Guest Rooms0 |  |  |  |  | X | [11 empty] | 0 |  | 27933 |  |  | 0 |  | 27933 | 1e-07 |  | 1e-05 | [11 empty] | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | [10 empty] | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0 |  |  | SmHtl | Highway Lodging Guest Rooms |  |  | Highway Lodging Guest Rooms0 | Highway Lodging Guest Rooms0
Highway Lodging Guest Rooms0 | Highway Lodging Guest Rooms0 |  |  |  |  | X | [11 empty] | 0 |  | 27933 |  |  | 0 |  | 27933 | 1e-07 |  | 1e-05 | [11 empty] | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | [10 empty] | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0 |  |  | SmHtl | Highway Lodging Guest Rooms |  |  | Highway Lodging Guest Rooms0 | Highway Lodging Guest Rooms0
Corridor/Transition | Corridor/Transition |  |  |  |  | X | [9 empty] | Corridor/Transition | 0.66 |  | 8760 | 5668 | Corridor/Transition | 0.41 |  | 8760 | 5668 | 200.6472 |  | 131.5403 |  | 8.1008 | [21 empty] | 5.7696 | [21 empty] | -28406.6212 |  |  | SmHtl | Corridor/Transition |  |  | Corridor/Transition | Corridor/Transition
Corridor/Transition701 | Corridor/TransitionDL706 |  |  |  |  | X | [9 empty] | replacement costs are for lamps |  | 701 |  | 5668 |  |  | DL706 |  | 5668 | 179.4867 | 31.5789 | 113.3599 | 50 | 5.2271 | 29627.2897 |  | 1.9475 | 11038.43 |  | 25509.4187 |  |  | 66175.1384 | 5.7078 | 6 | 0.0038 | 21.5384 |  | 0.019475 | 110.3843 |  | 284.3838 |  | 416.3065 | 437.6214 | 3.3013 | 18711.9724 |  | 1.23 | 6971.64 |  | 16111.2118 |  |  | 41794.8243 | 5.7078 | 6 | 0.0024 | 13.6032 |  | 0.0123 | 69.7164 |  | 179.6108 |  | 262.9304 | 276.3924 | -24380.3142 | -178.6977 |  | SmHtl | Corridor/Transition |  |  | Corridor/Transition701 | Corridor/TransitionDL706
Corridor/Transition0 | Corridor/Transition0 |  |  |  |  | X | [11 empty] | 0 |  | 5668 |  |  | 0 |  | 5668 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0 |  |  | SmHtl | Corridor/Transition |  |  | Corridor/Transition0 | Corridor/Transition0
Corridor/Transition0 | Corridor/Transition0 |  |  |  |  | X | [11 empty] | 0 |  | 5668 |  |  | 0 |  | 5668 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0 |  |  | SmHtl | Corridor/Transition |  |  | Corridor/Transition0 | Corridor/Transition0
Corridor/Transition703 | Corridor/TransitionWW708 |  |  |  |  | X | [11 empty] | 703 |  | 5668 |  |  | WW708 |  | 5668 | 21.1605 | 267.8571 | 18.1804 | 311.7648 | 2.8737 | 16288.3205 |  | 0.36736 | 2082.1965 |  | 10175.5535 |  |  | 28546.0705 | 5.7078 | 6 | 0.0028 | 15.8704 |  | 0.002296 | 13.0137 |  | 42.2115 |  | 71.0957 | 74.7358 | 2.4683 | 13990.3458 |  | 0.31562 | 1788.9491 |  | 8740.4685 |  |  | 24519.7635 | 5.7078 | 6 | 0.0017 | 9.6356 |  | 0.0019726 | 11.1809 |  | 33.6612 |  | 54.4777 | 57.267 | -4026.3071 |  |  | SmHtl | Corridor/Transition |  |  | Corridor/Transition703 | Corridor/TransitionWW708
Corridor/Transition701 | Corridor/TransitionDL706 |  |  |  |  | X | [9 empty] | ballast replacement |  | 701 |  | 5668 |  |  | DL706 |  | 5668 | 23.256 |  | 14.688 | [11 empty] | 5.7078 | 6 | 3.9175 | 22204.3135 |  | 1.9475 | 11038.43 |  | 41499.6984 |  | 74742.4419 | 78569.2549 | [10 empty] | 5.7078 | 6 | 2.4742 | 14023.7769 |  | 1.23 | 6971.64 |  | 26210.3358 |  | 47205.7528 | 49622.6873 | 0 | -32993.6257 |  | SmHtl | Corridor/Transition |  |  | Corridor/Transition701 | Corridor/TransitionDL706
Corridor/Transition0 | Corridor/Transition0 |  |  |  |  | X | [11 empty] | 0 |  | 5668 |  |  | 0 |  | 5668 | 1e-07 |  | 1e-05 | [11 empty] | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | [10 empty] | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0 |  |  | SmHtl | Corridor/Transition |  |  | Corridor/Transition0 | Corridor/Transition0
Corridor/Transition0 | Corridor/Transition0 |  |  |  |  | X | [11 empty] | 0 |  | 5668 |  |  | 0 |  | 5668 | 1e-07 |  | 1e-05 | [11 empty] | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | [10 empty] | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0 |  |  | SmHtl | Corridor/Transition |  |  | Corridor/Transition0 | Corridor/Transition0
Corridor/Transition703 | Corridor/TransitionWW708 |  |  |  |  | X | [11 empty] | 703 |  | 5668 |  |  | WW708 |  | 5668 | 17.64 |  | 15.147 | [11 empty] | 5.7078 | 6 | 2.1532 | 12204.3376 |  | 0.36736 | 2082.1965 |  | 13049.8898 |  | 27336.4239 | 28736.0488 | [10 empty] | 5.7078 | 6 | 1.85 | 10485.5326 |  | 0.31562 | 1788.9491 |  | 11212.001 |  | 23486.4828 | 24688.9907 | 0 |  |  | SmHtl | Corridor/Transition |  |  | Corridor/Transition703 | Corridor/TransitionWW708
Stairway | Stairway |  |  |  |  | X | [9 empty] | Stairway | 0.58 |  | 8760 | 1728 | Stairway | 0.49 |  | 8760 | 1728 | 38.9027 |  | 34.2939 |  | 5.37 | [21 empty] | 3.2638 | [21 empty] | -8404.9974 |  |  | SmHtl | Stairway |  |  | Stairway | Stairway
Stairway731 | StairwayTR703 |  |  |  |  | X | [9 empty] | replacement costs are for lamps |  | 731 |  | 1728 |  |  | TR703 |  | 1728 | 12.528 | 137.931 | 12.8859 | 134.0997 | 2.7724 | 4790.7072 |  | 0.58454 | 1010.0888 |  | 3376.7756 |  |  | 9177.5716 | 5.7078 | 6 | 0.0029 | 5.0112 |  | 0.0044588 | 7.7047 |  | 22.1348 |  | 34.8507 | 36.6351 | 1.0317 | 1782.7702 |  | 0.45861 | 792.4855 |  | 1658.8251 |  |  | 4234.0808 | 5.7078 | 6 | 0.00261 | 4.5101 |  | 0.0045861 | 7.9249 |  | 22.3475 |  | 34.7825 | 36.5633 | -4943.4909 | -13.1568 |  | SmHtl | Stairway |  |  | Stairway731 | StairwayTR703
Stairway702 | StairwayWG703 |  |  |  |  | X | [11 empty] | 702 |  | 1728 |  |  | WG703 |  | 1728 | 26.3747 | 65.5172 | 21.408 | 80.7175 | 2.5976 | 4488.7165 |  | 1.5019 | 2595.2741 |  | 4755.8672 |  |  | 11839.8578 | 5.7078 | 6 | 0.0029 | 5.0112 |  | 0.0093868 | 16.2205 |  | 42.9916 |  | 64.2232 | 67.5115 | 2.2321 | 3857.0794 |  | 0.76192 | 1316.592 |  | 3204.6799 |  |  | 8378.3512 | 5.7078 | 6 | 0.00223 | 3.8534 |  | 0.0076192 | 13.1659 |  | 34.7562 |  | 51.7755 | 54.4264 | -3461.5066 |  |  | SmHtl | Stairway |  |  | Stairway702 | StairwayWG703
Stairway0 | Stairway0 |  |  |  |  | X | [11 empty] | 0 |  | 1728 |  |  | 0 |  | 1728 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0 |  |  | SmHtl | Stairway |  |  | Stairway0 | Stairway0
Stairway0 | Stairway0 |  |  |  |  | X | [11 empty] | 0 |  | 1728 |  |  | 0 |  | 1728 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0 |  |  | SmHtl | Stairway |  |  | Stairway0 | Stairway0
Stairway731 | StairwayTR703 |  |  |  |  | X | [9 empty] | ballast replacement |  | 731 |  | 1728 |  |  | TR703 |  | 1728 | 22.968 |  | 26.0739 | [11 empty] | 5.7078 | 6 | 2.0771 | 3589.272 |  | 0.58454 | 1010.0888 |  | 4812.0401 |  | 9411.4009 | 9893.2646 | [10 empty] | 5.7078 | 6 | 0.77181 | 1333.6951 |  | 0.45861 | 792.4855 |  | 2809.7536 |  | 4935.9341 | 5188.654 | 0 | -10161.7267 |  | SmHtl | Stairway |  |  | Stairway731 | StairwayTR703
Stairway702 | StairwayWG703 |  |  |  |  | X | [11 empty] | 702 |  | 1728 |  |  | WG703 |  | 1728 | 21.924 |  | 17.6616 | [11 empty] | 5.7078 | 6 | 1.9461 | 3362.7789 |  | 1.5019 | 2595.2741 |  | 8546.9328 |  | 14504.9858 | 15247.6411 | [10 empty] | 5.7078 | 6 | 1.6724 | 2889.9194 |  | 0.76192 | 1316.592 |  | 5107.1539 |  | 9313.6654 | 9790.525 | 0 |  |  | SmHtl | Stairway |  |  | Stairway702 | StairwayWG703
Stairway0 | Stairway0 |  |  |  |  | X | [11 empty] | 0 |  | 1728 |  |  | 0 |  | 1728 | 1e-07 |  | 1e-05 | [11 empty] | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | [10 empty] | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0 |  |  | SmHtl | Stairway |  |  | Stairway0 | Stairway0
Stairway0 | Stairway0 |  |  |  |  | X | [11 empty] | 0 |  | 1728 |  |  | 0 |  | 1728 | 1e-07 |  | 1e-05 | [11 empty] | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | [10 empty] | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0 |  |  | SmHtl | Stairway |  |  | Stairway0 | Stairway0
Lobby - Hotel | Lobby - Hotel |  |  |  |  | X | [9 empty] | Lobby - Hotel | 1.06 |  | 7170 | 1755 | Lobby - Hotel | 0.51 |  | 7170 | 1755 | 35.1 |  | 32.5613 |  | 2.753 | [21 empty] | 4.4573 | [21 empty] | 4423.7348 |  |  | SmHtl | Lobby - Hotel |  |  | Lobby - Hotel | Lobby - Hotel
Lobby - Hotel572 | Lobby - HotelDL702 |  |  |  |  | X | [9 empty] | replacement costs are for lamps |  | 572 |  | 1755 |  |  | DL702 |  | 1755 | 21.06 | 83.3333 | 29.25 | 60 | 0.59136 | 1037.8368 |  | 0.738 | 1295.19 |  | 1770.7505 |  |  | 4103.7773 | 0.11855 | 1 | 0.25656 | 450.2628 |  | 0.282 | 494.91 |  | 1505.4445 |  | 2450.6173 | 20671.6777 | 3.0053 | 5274.3366 |  | 1.025 | 1798.875 |  | 4380.7792 |  |  | 11453.9908 | 6.9735 | 7 | 0.004 | 7.02 |  | 0.01025 | 17.9887 |  | 48.631 |  | 73.6398 | 73.9196 | 7350.2135 | -20622.3485 |  | SmHtl | Lobby - Hotel |  |  | Lobby - Hotel572 | Lobby - HotelDL702
Lobby - Hotel0 | Lobby - Hotel0 |  |  |  |  | X | [11 empty] | 0 |  | 1755 |  |  | 0 |  | 1755 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0 |  |  | SmHtl | Lobby - Hotel |  |  | Lobby - Hotel0 | Lobby - Hotel0
Lobby - Hotel0 | Lobby - Hotel0 |  |  |  |  | X | [11 empty] | 0 |  | 1755 |  |  | 0 |  | 1755 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0 |  |  | SmHtl | Lobby - Hotel |  |  | Lobby - Hotel0 | Lobby - Hotel0
Lobby - Hotel727-1 | Lobby - HotelWW703 |  |  |  |  | X | [11 empty] | 727-1 |  | 1755 |  |  | WW703 |  | 1755 | 14.04 | 125 | 3.3113 | 530.0001 | 2.1616 | 3793.608 |  | 0.492 | 863.46 |  | 2735.3686 |  |  | 7392.4366 | 6.9735 | 7 | 0.0016 | 2.808 |  | 0.00492 | 8.6346 |  | 22.9771 |  | 34.4197 | 34.5504 | 1.4519 | 2548.1607 |  | 0.18566 | 325.834 |  | 1591.9634 |  |  | 4465.958 | 6.9735 | 7 | 0.001 | 1.755 |  | 0.0011604 | 2.0365 |  | 6.1309 |  | 9.9224 | 9.9601 | -2926.4786 |  |  | SmHtl | Lobby - Hotel |  |  | Lobby - Hotel727-1 | Lobby - HotelWW703
Lobby - Hotel572 | Lobby - HotelDL702 |  |  |  |  | X | [9 empty] | ballast replacement |  | 572 |  | 1755 |  |  | DL702 |  | 1755 | 15.39 |  | 21.6 | [11 empty] | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | [10 empty] | 6.9735 | 7 | 2.251 | 3950.4875 |  | 1.025 | 1798.875 |  | 6979.2387 |  | 12728.6011 | 12776.9698 | 0 | 9368.4216 |  | SmHtl | Lobby - Hotel |  |  | Lobby - Hotel572 | Lobby - HotelDL702
Lobby - Hotel0 | Lobby - Hotel0 |  |  |  |  | X | [11 empty] | 0 |  | 1755 |  |  | 0 |  | 1755 | 1e-07 |  | 1e-05 | [11 empty] | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | [10 empty] | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0 |  |  | SmHtl | Lobby - Hotel |  |  | Lobby - Hotel0 | Lobby - Hotel0
Lobby - Hotel0 | Lobby - Hotel0 |  |  |  |  | X | [11 empty] | 0 |  | 1755 |  |  | 0 |  | 1755 | 1e-07 |  | 1e-05 | [11 empty] | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | [10 empty] | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0 |  |  | SmHtl | Lobby - Hotel |  |  | Lobby - Hotel0 | Lobby - Hotel0
Lobby - Hotel727-1 | Lobby - HotelWW703 |  |  |  |  | X | [11 empty] | 727-1 |  | 1755 |  |  | WW703 |  | 1755 | 14.4 |  | 8.91 | [11 empty] | 6.9735 | 7 | 1.62 | 2843.1 |  | 0.492 | 863.46 |  | 3966.844 |  | 7673.404 | 7702.5629 | [10 empty] | 6.9735 | 7 | 1.0882 | 1909.8042 |  | 0.18566 | 325.834 |  | 2042.1211 |  | 4277.7593 | 4294.0148 | 0 |  |  | SmHtl | Lobby - Hotel |  |  | Lobby - Hotel727-1 | Lobby - HotelWW703
Storage | Storage |  |  |  |  | X | [9 empty] | Storage | 0.46 |  | 2148 | 1404 | Storage | 0.38 |  | 2148 | 1404 | 16.9958 |  | 14.4195 |  | 3.0309 | [21 empty] | 1.76 | [21 empty] | -2971.8679 |  |  | SmHtl | Storage |  |  | Storage | Storage
Storage738 | StorageLB702 |  |  |  |  | X | [9 empty] | replacement costs are for lamps |  | 738 |  | 1404 |  |  | LB702 |  | 1404 | 16.9958 | 82.6087 | 14.4195 | 97.3684 | 3.0309 | 4255.4058 |  | 0.70055 | 983.5718 |  | 3082.8311 |  |  | 8321.8087 | 23.2775 | 24 | 0.0046 | 6.4584 |  | 0.0074447 | 10.4524 |  | 29.8072 |  | 46.718 | 48.1681 | 1.76 | 2471.0628 |  | 0.59436 | 834.4757 |  | 2044.4023 |  |  | 5349.9408 | 23.2775 | 24 | 0.0038 | 5.3352 |  | 0.0063162 | 8.868 |  | 25.1949 |  | 39.3981 | 40.621 | -2971.8679 | -7.5471 |  | SmHtl | Storage |  |  | Storage738 | StorageLB702
Storage0 | Storage0 |  |  |  |  | X | [11 empty] | 0 |  | 1404 |  |  | 0 |  | 1404 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0 |  |  | SmHtl | Storage |  |  | Storage0 | Storage0
Storage0 | Storage0 |  |  |  |  | X | [11 empty] | 0 |  | 1404 |  |  | 0 |  | 1404 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0 |  |  | SmHtl | Storage |  |  | Storage0 | Storage0
Storage0 | Storage0 |  |  |  |  | X | [11 empty] | 0 |  | 1404 |  |  | 0 |  | 1404 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0 |  |  | SmHtl | Storage |  |  | Storage0 | Storage0
Storage738 | StorageLB702 |  |  |  |  | X | [9 empty] | ballast replacement |  | 738 |  | 1404 |  |  | LB702 |  | 1404 | 47.61 |  | 35.226 | [11 empty] | 23.2775 | 24 | 2.2697 | 3186.7105 |  | 0.70055 | 983.5718 |  | 4484.8573 |  | 8655.1397 | 8923.7952 | [10 empty] | 23.2775 | 24 | 1.3172 | 1849.2957 |  | 0.59436 | 834.4757 |  | 3248.4697 |  | 5932.2411 | 6116.3779 | 0 | -2807.4173 |  | SmHtl | Storage |  |  | Storage738 | StorageLB702
Storage0 | Storage0 |  |  |  |  | X | [11 empty] | 0 |  | 1404 |  |  | 0 |  | 1404 | 1e-07 |  | 1e-05 | [11 empty] | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | [10 empty] | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0 |  |  | SmHtl | Storage |  |  | Storage0 | Storage0
Storage0 | Storage0 |  |  |  |  | X | [11 empty] | 0 |  | 1404 |  |  | 0 |  | 1404 | 1e-07 |  | 1e-05 | [11 empty] | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | [10 empty] | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0 |  |  | SmHtl | Storage |  |  | Storage0 | Storage0
Storage0 | Storage0 |  |  |  |  | X | [11 empty] | 0 |  | 1404 |  |  | 0 |  | 1404 | 1e-07 |  | 1e-05 | [11 empty] | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | [10 empty] | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0 |  |  | SmHtl | Storage |  |  | Storage0 | Storage0
Office-Enclosed | Office-Enclosed |  |  |  |  | X | [9 empty] | Office-Enclosed | 0.93 |  | 5722 | 1404 | Office-Enclosed | 0.74 |  | 5722 | 1404 | 62.634 |  | 32.4675 |  | 5.9056 | [21 empty] | 3.1987 | [21 empty] | -8709.5818 |  |  | SmHtl | Office-Enclosed |  |  | Office-Enclosed | Office-Enclosed
Office-Enclosed700 | Office-EnclosedTR701 |  |  |  |  | X | [9 empty] | replacement costs are for lamps |  | 700 |  | 1404 |  |  | TR701 |  | 1404 | 26.13 | 53.7313 | 32.4675 | 43.2433 | 2.575 | 3615.3468 |  | 1.7272 | 2424.9555 |  | 4153.6127 |  |  | 10193.915 | 8.7382 | 9 | 0.0067 | 9.4068 |  | 0.011446 | 16.0699 |  | 45.4863 |  | 70.9631 | 73.0891 | 3.1987 | 4490.9046 |  | 1.4222 | 1996.7513 |  | 4179.0975 |  |  | 10666.7534 | 8.7382 | 9 | 0.0074 | 10.3896 |  | 0.014222 | 19.9675 |  | 55.6724 |  | 86.0296 | 88.607 | 472.8384 | -70.4454 |  | SmHtl | Office-Enclosed |  |  | Office-Enclosed700 | Office-EnclosedTR701
Office-Enclosed739 | Office-Enclosed0 |  |  |  |  | X | [11 empty] | 739 |  | 1404 |  |  | 0 |  | 1404 | 36.504 | 38.4615 | 0 | 0 | 3.3306 | 4676.1624 |  | 0.78351 | 1100.048 |  | 3406.2097 |  |  | 9182.4202 | 8.7382 | 9 | 0.0026 | 3.6504 |  | 0.01599 | 22.45 |  | 57.3624 |  | 83.4627 | 85.9633 | 0 | 0 |  | 0 | 0 |  | 0 |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | -9182.4202 |  |  | SmHtl | Office-Enclosed |  |  | Office-Enclosed739 | Office-Enclosed0
Office-Enclosed0 | Office-Enclosed0 |  |  |  |  | X | [11 empty] | 0 |  | 1404 |  |  | 0 |  | 1404 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0 |  |  | SmHtl | Office-Enclosed |  |  | Office-Enclosed0 | Office-Enclosed0
Office-Enclosed0 | Office-Enclosed0 |  |  |  |  | X | [11 empty] | 0 |  | 1404 |  |  | 0 |  | 1404 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0 |  |  | SmHtl | Office-Enclosed |  |  | Office-Enclosed0 | Office-Enclosed0
Office-Enclosed700 | Office-EnclosedTR701 |  |  |  |  | X | [9 empty] | ballast replacement |  | 700 |  | 1404 |  |  | TR701 |  | 1404 | 62.109 |  | 76.59 | [11 empty] | 8.7382 | 9 | 1.9263 | 2704.455 |  | 1.7272 | 2424.9555 |  | 7700.9416 |  | 12830.3521 | 13214.7494 | [10 empty] | 8.7382 | 9 | 2.3934 | 3360.3863 |  | 1.4222 | 1996.7513 |  | 7079.4722 |  | 12436.6097 | 12809.2105 | 0 | -10274.1031 |  | SmHtl | Office-Enclosed |  |  | Office-Enclosed700 | Office-EnclosedTR701
Office-Enclosed739 | Office-Enclosed0 |  |  |  |  | X | [11 empty] | 739 |  | 1404 |  |  | 0 |  | 1404 | 15.912 |  | 1e-05 | [11 empty] | 8.7382 | 9 | 2.496 | 3504.384 |  | 0.78351 | 1100.048 |  | 4977.0703 |  | 9581.5024 | 9868.5642 | [10 empty] | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0 |  |  | SmHtl | Office-Enclosed |  |  | Office-Enclosed739 | Office-Enclosed0
Office-Enclosed0 | Office-Enclosed0 |  |  |  |  | X | [11 empty] | 0 |  | 1404 |  |  | 0 |  | 1404 | 1e-07 |  | 1e-05 | [11 empty] | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | [10 empty] | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0 |  |  | SmHtl | Office-Enclosed |  |  | Office-Enclosed0 | Office-Enclosed0
Office-Enclosed0 | Office-Enclosed0 |  |  |  |  | X | [11 empty] | 0 |  | 1404 |  |  | 0 |  | 1404 | 1e-07 |  | 1e-05 | [11 empty] | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | [10 empty] | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0 |  |  | SmHtl | Office-Enclosed |  |  | Office-Enclosed0 | Office-Enclosed0
Laundry-washing | Laundry-washing |  |  |  |  | X | [9 empty] | Laundry-washing | 0.43 |  | 3276 | 1053 | Laundry-Washing | 0.53 |  | 3276 | 1053 | 11.2355 |  | 15.9454 |  | 2.0422 | [21 empty] | 2.095 | [21 empty] | 652.7659 |  |  | SmHtl | Laundry-washing |  |  | Laundry-washing | Laundry-washing
Laundry-washing730 | Laundry-washingTR703 |  |  |  |  | X | [9 empty] | replacement costs are for lamps |  | 730 |  | 1053 |  |  | TR703 |  | 1053 | 11.2355 | 93.7209 | 15.9454 | 66.0378 | 2.0422 | 2150.4716 |  | 0.6562 | 690.9823 |  | 1745.151 |  |  | 4586.6049 | 15.2625 | 16 | 0.004268 | 4.4942 |  | 0.006562 | 6.9098 |  | 19.8512 |  | 31.2552 | 32.7654 | 2.095 | 2206.05 |  | 0.93129 | 980.6439 |  | 2052.6769 |  |  | 5239.3708 | 15.2625 | 16 | 0.0053 | 5.5809 |  | 0.0093129 | 9.8064 |  | 27.6534 |  | 43.0408 | 45.1205 | 652.7659 | 12.3551 |  | SmHtl | Laundry-washing |  |  | Laundry-washing730 | Laundry-washingTR703
Laundry-washing0 | Laundry-washing0 |  |  |  |  | X | [11 empty] | 0 |  | 1053 |  |  | 0 |  | 1053 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0 |  |  | SmHtl | Laundry-washing |  |  | Laundry-washing0 | Laundry-washing0
Laundry-washing0 | Laundry-washing0 |  |  |  |  | X | [11 empty] | 0 |  | 1053 |  |  | 0 |  | 1053 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0 |  |  | SmHtl | Laundry-washing |  |  | Laundry-washing0 | Laundry-washing0
Laundry-washing0 | Laundry-washing0 |  |  |  |  | X | [11 empty] | 0 |  | 1053 |  |  | 0 |  | 1053 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0 |  |  | SmHtl | Laundry-washing |  |  | Laundry-washing0 | Laundry-washing0
Laundry-washing730 | Laundry-washingTR703 |  |  |  |  | X | [9 empty] | ballast replacement |  | 730 |  | 1053 |  |  | TR703 |  | 1053 | 37.539 |  | 52.947 | [11 empty] | 15.2625 | 16 | 1.5285 | 1609.4831 |  | 0.6562 | 690.9823 |  | 2740.8063 |  | 5041.2716 | 5284.8658 | [10 empty] | 15.2625 | 16 | 1.5673 | 1650.3519 |  | 0.93129 | 980.6439 |  | 3476.8682 |  | 6107.8639 | 6402.9959 | 0 | 1118.13 |  | SmHtl | Laundry-washing |  |  | Laundry-washing730 | Laundry-washingTR703
Laundry-washing0 | Laundry-washing0 |  |  |  |  | X | [11 empty] | 0 |  | 1053 |  |  | 0 |  | 1053 | 1e-07 |  | 1e-05 | [11 empty] | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | [10 empty] | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0 |  |  | SmHtl | Laundry-washing |  |  | Laundry-washing0 | Laundry-washing0
Laundry-washing0 | Laundry-washing0 |  |  |  |  | X | [11 empty] | 0 |  | 1053 |  |  | 0 |  | 1053 | 1e-07 |  | 1e-05 | [11 empty] | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | [10 empty] | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0 |  |  | SmHtl | Laundry-washing |  |  | Laundry-washing0 | Laundry-washing0
Laundry-washing0 | Laundry-washing0 |  |  |  |  | X | [11 empty] | 0 |  | 1053 |  |  | 0 |  | 1053 | 1e-07 |  | 1e-05 | [11 empty] | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | [10 empty] | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0 |  |  | SmHtl | Laundry-washing |  |  | Laundry-washing0 | Laundry-washing0
Conference/Meeting/Multipurpose | Conference/Meeting/Multipurpose |  |  |  |  | X | [9 empty] | Conference/Meeting/Multipurpose | 1.07 |  | 4386 | 864 | Conference/Meeting/Multipurpose | 0.97 |  | 4386 | 864 | 24.264 |  | 23.454 |  | 7.2976 | [21 empty] | 7.2964 | [21 empty] | -141.0952 |  |  | SmHtl | Conference/Meeting/Multipurpose |  |  | Conference/Meeting/Multipurpose | Conference/Meeting/Multipurpose
Conference/Meeting/Multipurpose731 | Conference/Meeting/MultipurposeTR704 |  |  |  |  | X | [9 empty] | replacement costs are for lamps |  | 731 |  | 864 |  |  | TR704 |  | 864 | 9.72 | 88.8889 | 13.23 | 65.3061 | 4.302 | 3716.928 |  | 0.90705 | 783.6896 |  | 2619.9121 |  |  | 7120.5297 | 11.3999 | 12 | 0.0045 | 3.888 |  | 0.0069188 | 5.9778 |  | 17.1736 |  | 27.0394 | 28.4627 | 2.118 | 1829.9736 |  | 0.94172 | 813.645 |  | 1702.9171 |  |  | 4346.5357 | 11.3999 | 12 | 0.0049 | 4.2336 |  | 0.0094172 | 8.1364 |  | 22.6857 |  | 35.0557 | 36.901 | -2773.994 | -282.8813 |  | SmHtl | Conference/Meeting/Multipurpose |  |  | Conference/Meeting/Multipurpose731 | Conference/Meeting/MultipurposeTR704
Conference/Meeting/Multipurpose511 | Conference/Meeting/MultipurposeDL702 |  |  |  |  | X | [11 empty] | 511 |  | 864 |  |  | DL702 |  | 864 | 6.336 | 136.3636 | 5.76 | 150.0001 | 0.42871 | 370.4026 |  | 0.451 | 389.664 |  | 561.8961 |  |  | 1321.9626 | 0.95759 | 1 | 0.15679 | 135.4637 |  | 0.02134 | 18.4378 |  | 133.4018 |  | 287.3032 | 300.0267 | 1.2021 | 1038.6386 |  | 0.41 | 354.24 |  | 862.6765 |  |  | 2255.5551 | 11.3999 | 12 | 0.0016 | 1.3824 |  | 0.0041 | 3.5424 |  | 9.5766 |  | 14.5014 | 15.2647 | 933.5925 |  |  | SmHtl | Conference/Meeting/Multipurpose |  |  | Conference/Meeting/Multipurpose511 | Conference/Meeting/MultipurposeDL702
Conference/Meeting/Multipurpose0 | Conference/Meeting/Multipurpose0 |  |  |  |  | X | [11 empty] | 0 |  | 864 |  |  | 0 |  | 864 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0 |  |  | SmHtl | Conference/Meeting/Multipurpose |  |  | Conference/Meeting/Multipurpose0 | Conference/Meeting/Multipurpose0
Conference/Meeting/Multipurpose727-1 | Conference/Meeting/MultipurposeWW704 |  |  |  |  | X | [11 empty] | 727-1 |  | 864 |  |  | WW704 |  | 864 | 8.208 | 105.2632 | 4.464 | 193.5484 | 2.5669 | 2217.8016 |  | 0.58425 | 504.792 |  | 1599.1386 |  |  | 4321.7322 | 11.3999 | 12 | 0.0019 | 1.6416 |  | 0.0058425 | 5.0479 |  | 13.4327 |  | 20.1223 | 21.1815 | 3.9763 | 3435.4944 |  | 0.5084 | 439.2576 |  | 2146.2865 |  |  | 6021.0385 | 11.3999 | 12 | 0.0031 | 2.6784 |  | 0.0031775 | 2.7454 |  | 8.4687 |  | 13.8925 | 14.6238 | 1699.3064 |  |  | SmHtl | Conference/Meeting/Multipurpose |  |  | Conference/Meeting/Multipurpose727-1 | Conference/Meeting/MultipurposeWW704
Conference/Meeting/Multipurpose731 | Conference/Meeting/MultipurposeTR704 |  |  |  |  | X | [9 empty] | ballast replacement |  | 731 |  | 864 |  |  | TR704 |  | 864 | 35.64 |  | 48.951 | [11 empty] | 11.3999 | 12 | 3.2231 | 2784.78 |  | 0.90705 | 783.6896 |  | 3733.4794 |  | 7301.949 | 7686.3236 | [10 empty] | 11.3999 | 12 | 1.5848 | 1369.305 |  | 0.94172 | 813.645 |  | 2884.7745 |  | 5067.7245 | 5334.4895 | 0 | 1634.9595 |  | SmHtl | Conference/Meeting/Multipurpose |  |  | Conference/Meeting/Multipurpose731 | Conference/Meeting/MultipurposeTR704
Conference/Meeting/Multipurpose511 | Conference/Meeting/MultipurposeDL702 |  |  |  |  | X | [11 empty] | 511 |  | 864 |  |  | DL702 |  | 864 | 2.4651 |  | 8.64 | [11 empty] | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | [10 empty] | 11.3999 | 12 | 0.9004 | 777.9421 |  | 0.41 | 354.24 |  | 1374.3732 |  | 2506.5553 | 2638.5004 | 0 |  |  | SmHtl | Conference/Meeting/Multipurpose |  |  | Conference/Meeting/Multipurpose511 | Conference/Meeting/MultipurposeDL702
Conference/Meeting/Multipurpose0 | Conference/Meeting/Multipurpose0 |  |  |  |  | X | [11 empty] | 0 |  | 864 |  |  | 0 |  | 864 | 1e-07 |  | 1e-05 | [11 empty] | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | [10 empty] | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0 |  |  | SmHtl | Conference/Meeting/Multipurpose |  |  | Conference/Meeting/Multipurpose0 | Conference/Meeting/Multipurpose0
Conference/Meeting/Multipurpose727-1 | Conference/Meeting/MultipurposeWW704 |  |  |  |  | X | [11 empty] | 727-1 |  | 864 |  |  | WW704 |  | 864 | 17.1 |  | 13.113 | [11 empty] | 11.3999 | 12 | 1.9238 | 1662.12 |  | 0.58425 | 504.792 |  | 2319.078 |  | 4485.99 | 4722.1325 | [10 empty] | 11.3999 | 12 | 2.9799 | 2574.612 |  | 0.5084 | 439.2576 |  | 2752.9886 |  | 5766.8582 | 6070.4257 | 0 |  |  | SmHtl | Conference/Meeting/Multipurpose |  |  | Conference/Meeting/Multipurpose727-1 | Conference/Meeting/MultipurposeWW704
Restrooms | Restrooms |  |  |  |  | X | [9 empty] | Restrooms | 0.85 |  | 8760 | 351 | Restrooms | 0.63 |  | 8760 | 351 | 11.0582 |  | 11.2827 |  | 9.7535 | [21 empty] | 6.1184 | [21 empty] | -1601.3747 |  |  | SmHtl | Restrooms |  |  | Restrooms | Restrooms
Restrooms604 | RestroomsDL709 |  |  |  |  | X | [9 empty] | replacement costs are for lamps |  | 604 |  | 351 |  |  | DL709 |  | 351 | 4.2362 | 82.8571 | 6.2127 | 56.4972 | 4.2525 | 1492.6275 |  | 0.3637 | 127.6581 |  | 871.4958 |  |  | 2491.7814 | 4.1096 | 5 | 0.040431 | 14.1913 |  | 0.065978 | 23.1582 |  | 65.9636 |  | 103.3131 | 125.6977 | 3.5159 | 1234.082 |  | 1.0885 | 382.0811 |  | 987.5311 |  |  | 2603.6942 | 5.7078 | 6 | 0.003717 | 1.3047 |  | 0.010885 | 3.8208 |  | 10.2078 |  | 15.3333 | 16.1184 | 111.9128 | -212.7644 |  | SmHtl | Restrooms |  |  | Restrooms604 | RestroomsDL709
Restrooms720 | Restrooms0 |  |  |  |  | X | [11 empty] | 720 |  | 351 |  |  | 0 |  | 351 | 3.1909 | 110 | 0 | 0 | 1.5353 | 538.9031 |  | 0.55909 | 196.2409 |  | 459.6165 |  |  | 1194.7604 | 5.7078 | 6 | 0.002 | 0.702 |  | 0.0055909 | 1.9624 |  | 5.2636 |  | 7.928 | 8.334 | 0 | 0 |  | 0 | 0 |  | 0 |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | -1194.7604 |  |  | SmHtl | Restrooms |  |  | Restrooms720 | Restrooms0
Restrooms0 | Restrooms0 |  |  |  |  | X | [11 empty] | 0 |  | 351 |  |  | 0 |  | 351 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0 |  |  | SmHtl | Restrooms |  |  | Restrooms0 | Restrooms0
Restrooms534-2 | RestroomsWG701 |  |  |  |  | X | [11 empty] | 534-2 |  | 351 |  |  | WG701 |  | 351 | 3.631 | 96.6667 | 5.07 | 69.2308 | 3.9657 | 1391.9571 |  | 0.59867 | 210.1334 |  | 900.6593 |  |  | 2502.7498 | 4.1096 | 5 | 0.034655 | 12.164 |  | 0.056552 | 19.8499 |  | 56.5403 |  | 88.5541 | 107.7408 | 2.6025 | 913.4619 |  | 0.88833 | 311.805 |  | 758.9559 |  |  | 1984.2228 | 5.7078 | 6 | 0.0026 | 0.9126 |  | 0.0088833 | 3.1181 |  | 8.2312 |  | 12.2619 | 12.8897 | -518.5271 |  |  | SmHtl | Restrooms |  |  | Restrooms534-2 | RestroomsWG701
Restrooms604 | RestroomsDL709 |  |  |  |  | X | [9 empty] | ballast replacement |  | 604 |  | 351 |  |  | DL709 |  | 351 | 24.2393 |  | 28.7696 | [11 empty] | 5.7078 | 6 | 0.36207 | 127.0862 |  | 0.74224 | 260.5267 |  | 720.8687 |  | 1108.4816 | 1165.2359 | [10 empty] | 5.7078 | 6 | 2.6341 | 924.583 |  | 1.0885 | 382.0811 |  | 1538.0866 |  | 2844.7506 | 2990.4019 | 0 | 1732.7988 |  | SmHtl | Restrooms |  |  | Restrooms604 | RestroomsDL709
Restrooms720 | Restrooms0 |  |  |  |  | X | [11 empty] | 720 |  | 351 |  |  | 0 |  | 351 | 12.6 |  | 1e-05 | [11 empty] | 5.7078 | 6 | 1.15 | 403.6508 |  | 0.55909 | 196.2409 |  | 743.5802 |  | 1343.4719 | 1412.2577 | [10 empty] | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0 |  |  | SmHtl | Restrooms |  |  | Restrooms720 | Restrooms0
Restrooms0 | Restrooms0 |  |  |  |  | X | [11 empty] | 0 |  | 351 |  |  | 0 |  | 351 | 1e-07 |  | 1e-05 | [11 empty] | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | [10 empty] | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0 |  |  | SmHtl | Restrooms |  |  | Restrooms0 | Restrooms0
Restrooms534-2 | RestroomsWG701 |  |  |  |  | X | [11 empty] | 534-2 |  | 351 |  |  | WG701 |  | 351 | 24.3 |  | 24.102 | [11 empty] | 5.7078 | 6 | 0.31034 | 108.931 |  | 0.63621 | 223.3086 |  | 617.8875 |  | 950.1271 | 998.7736 | [10 empty] | 5.7078 | 6 | 1.9499 | 684.412 |  | 0.88833 | 311.805 |  | 1209.5138 |  | 2205.7307 | 2318.6641 | 0 |  |  | SmHtl | Restrooms |  |  | Restrooms534-2 | RestroomsWG701
Gymnasium/Fitness-Fitness Area | Gymnasium/Fitness-Fitness Area |  |  |  |  | X | [9 empty] | Gymnasium/Fitness-Fitness Area | 0.5 |  | 5824 | 351 | Gymnasium/Fitness-Fitness Area | 0.7 |  | 5824 | 351 | 4.6184 |  | 7.4455 |  | 8.8116 | [21 empty] | 14.2043 | [21 empty] | 3289.7015 |  |  | SmHtl | Gymnasium/Fitness-Fitness Area |  |  | Gymnasium/Fitness-Fitness Area | Gymnasium/Fitness-Fitness Area
Gymnasium/Fitness-Fitness Area735 | Gymnasium/Fitness-Fitness AreaID701 |  |  |  |  | X | [9 empty] | replacement costs are for lamps |  | 735 |  | 351 |  |  | ID701 |  | 351 | 4.6184 | 76 | 7.4455 | 47.1429 | 8.8116 | 3092.8642 |  | 1.0609 | 372.3671 |  | 1909.9466 |  |  | 5375.1779 | 8.5852 | 9 | 0.005 | 1.755 |  | 0.0080921 | 2.8403 |  | 8.0998 |  | 12.6951 | 13.3085 | 14.2043 | 4985.6997 |  | 1.7103 | 600.3009 |  | 3078.8787 |  |  | 8664.8794 | 8.5852 | 9 | 0.007 | 2.457 |  | 0.013045 | 4.579 |  | 12.8153 |  | 19.8513 | 20.8105 | 3289.7015 | 7.502 |  | SmHtl | Gymnasium/Fitness-Fitness Area |  |  | Gymnasium/Fitness-Fitness Area735 | Gymnasium/Fitness-Fitness AreaID701
Gymnasium/Fitness-Fitness Area0 | Gymnasium/Fitness-Fitness Area0 |  |  |  |  | X | [11 empty] | 0 |  | 351 |  |  | 0 |  | 351 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0 |  |  | SmHtl | Gymnasium/Fitness-Fitness Area |  |  | Gymnasium/Fitness-Fitness Area0 | Gymnasium/Fitness-Fitness Area0
Gymnasium/Fitness-Fitness Area0 | Gymnasium/Fitness-Fitness Area0 |  |  |  |  | X | [11 empty] | 0 |  | 351 |  |  | 0 |  | 351 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0 |  |  | SmHtl | Gymnasium/Fitness-Fitness Area |  |  | Gymnasium/Fitness-Fitness Area0 | Gymnasium/Fitness-Fitness Area0
Gymnasium/Fitness-Fitness Area0 | Gymnasium/Fitness-Fitness Area0 |  |  |  |  | X | [11 empty] | 0 |  | 351 |  |  | 0 |  | 351 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0 |  |  | SmHtl | Gymnasium/Fitness-Fitness Area |  |  | Gymnasium/Fitness-Fitness Area0 | Gymnasium/Fitness-Fitness Area0
Gymnasium/Fitness-Fitness Area735 | Gymnasium/Fitness-Fitness AreaID701 |  |  |  |  | X | [9 empty] | ballast replacement |  | 735 |  | 351 |  |  | ID701 |  | 351 | 45 |  | 69.3 | [11 empty] | 8.5852 | 9 | 6.6049 | 2318.3319 |  | 1.0609 | 372.3671 |  | 2422.214 |  | 5112.913 | 5359.969 | [10 empty] | 8.5852 | 9 | 10.648 | 3737.432 |  | 1.7103 | 600.3009 |  | 3904.9026 |  | 8242.6356 | 8640.9197 | 0 | 3280.9507 |  | SmHtl | Gymnasium/Fitness-Fitness Area |  |  | Gymnasium/Fitness-Fitness Area735 | Gymnasium/Fitness-Fitness AreaID701
Gymnasium/Fitness-Fitness Area0 | Gymnasium/Fitness-Fitness Area0 |  |  |  |  | X | [11 empty] | 0 |  | 351 |  |  | 0 |  | 351 | 1e-07 |  | 1e-05 | [11 empty] | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | [10 empty] | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0 |  |  | SmHtl | Gymnasium/Fitness-Fitness Area |  |  | Gymnasium/Fitness-Fitness Area0 | Gymnasium/Fitness-Fitness Area0
Gymnasium/Fitness-Fitness Area0 | Gymnasium/Fitness-Fitness Area0 |  |  |  |  | X | [11 empty] | 0 |  | 351 |  |  | 0 |  | 351 | 1e-07 |  | 1e-05 | [11 empty] | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | [10 empty] | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0 |  |  | SmHtl | Gymnasium/Fitness-Fitness Area |  |  | Gymnasium/Fitness-Fitness Area0 | Gymnasium/Fitness-Fitness Area0
Gymnasium/Fitness-Fitness Area0 | Gymnasium/Fitness-Fitness Area0 |  |  |  |  | X | [11 empty] | 0 |  | 351 |  |  | 0 |  | 351 | 1e-07 |  | 1e-05 | [11 empty] | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | [10 empty] | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0 |  |  | SmHtl | Gymnasium/Fitness-Fitness Area |  |  | Gymnasium/Fitness-Fitness Area0 | Gymnasium/Fitness-Fitness Area0
Lounge/Recreation - Break room | Lounge/Recreation - Break room |  |  |  |  | X | [9 empty] | Lounge/Recreation - Breakroom | 0.62 |  | 4128 | 351 | Lounge/Recreation - Breakroom | 0.59 |  | 4128 | 351 | 10.6821 |  | 17.745 |  | 10.6975 | [21 empty] | 9.9458 | [21 empty] | 457.6342 |  |  | SmHtl | Lounge/Recreation - Breakroom |  |  | Lounge/Recreation - Breakroom | Lounge/Recreation - Breakroom
Lounge/Recreation - Breakroom522 | Lounge/Recreation - BreakroomDL707 |  |  |  |  | X | [9 empty] | replacement costs are for lamps |  | 522 |  | 351 |  |  | DL707 |  | 351 | 6.6105 | 53.0973 | 12.285 | 28.5715 | 2.9226 | 1025.8174 |  | 1.1583 | 406.5457 |  | 906.7499 |  |  | 2339.1131 | 12.1124 | 13 | 0.00339 | 1.1899 |  | 0.011583 | 4.0655 |  | 10.7322 |  | 15.9876 | 17.1592 | 7.1431 | 2507.2321 |  | 2.1525 | 755.5275 |  | 1986.3102 |  |  | 5249.0698 | 12.1124 | 13 | 0.0028 | 0.9828 |  | 0.021525 | 7.5553 |  | 19.1446 |  | 27.6827 | 29.7113 | 2909.9567 | 15.6509 |  | SmHtl | Lounge/Recreation - Breakroom |  |  | Lounge/Recreation - Breakroom522 | Lounge/Recreation - BreakroomDL707
Lounge/Recreation - Breakroom0 | Lounge/Recreation - Breakroom0 |  |  |  |  | X | [11 empty] | 0 |  | 351 |  |  | 0 |  | 351 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0 |  |  | SmHtl | Lounge/Recreation - Breakroom |  |  | Lounge/Recreation - Breakroom0 | Lounge/Recreation - Breakroom0
Lounge/Recreation - Breakroom0 | Lounge/Recreation - Breakroom0 |  |  |  |  | X | [11 empty] | 0 |  | 351 |  |  | 0 |  | 351 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0 |  |  | SmHtl | Lounge/Recreation - Breakroom |  |  | Lounge/Recreation - Breakroom0 | Lounge/Recreation - Breakroom0
Lounge/Recreation - Breakroom727-2 | Lounge/Recreation - BreakroomWG702 |  |  |  |  | X | [11 empty] | 727-2 |  | 351 |  |  | WG702 |  | 351 | 4.0716 | 86.2069 | 5.46 | 64.2857 | 7.7749 | 2728.9899 |  | 0.7134 | 250.4034 |  | 1609.7845 |  |  | 4589.1778 | 12.1124 | 13 | 0.0029 | 1.0179 |  | 0.007134 | 2.504 |  | 6.796 |  | 10.3179 | 11.074 | 2.8026 | 983.7282 |  | 0.95667 | 335.79 |  | 817.3371 |  |  | 2136.8553 | 12.1124 | 13 | 0.0028 | 0.9828 |  | 0.0095667 | 3.3579 |  | 8.8644 |  | 13.2051 | 14.1728 | -2452.3225 |  |  | SmHtl | Lounge/Recreation - Breakroom |  |  | Lounge/Recreation - Breakroom727-2 | Lounge/Recreation - BreakroomWG702
Lounge/Recreation - Breakroom522 | Lounge/Recreation - BreakroomDL707 |  |  |  |  | X | [9 empty] | ballast replacement |  | 522 |  | 351 |  |  | DL707 |  | 351 | 16.0178 |  | 22.428 | [11 empty] | 0 | 0 | 2.1894 | 768.4706 |  | 1.1583 | 406.5457 |  | 1496.3104 |  | 2671.3268 | 0 | [10 empty] | 12.1124 | 13 | 5.3552 | 1879.687 |  | 2.1525 | 755.5275 |  | 3074.9073 |  | 5710.1218 | 6128.5595 | 0 | 4124.6772 |  | SmHtl | Lounge/Recreation - Breakroom |  |  | Lounge/Recreation - Breakroom522 | Lounge/Recreation - BreakroomDL707
Lounge/Recreation - Breakroom0 | Lounge/Recreation - Breakroom0 |  |  |  |  | X | [11 empty] | 0 |  | 351 |  |  | 0 |  | 351 | 1e-07 |  | 1e-05 | [11 empty] | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | [10 empty] | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0 |  |  | SmHtl | Lounge/Recreation - Breakroom |  |  | Lounge/Recreation - Breakroom0 | Lounge/Recreation - Breakroom0
Lounge/Recreation - Breakroom0 | Lounge/Recreation - Breakroom0 |  |  |  |  | X | [11 empty] | 0 |  | 351 |  |  | 0 |  | 351 | 1e-07 |  | 1e-05 | [11 empty] | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | [10 empty] | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0 |  |  | SmHtl | Lounge/Recreation - Breakroom |  |  | Lounge/Recreation - Breakroom0 | Lounge/Recreation - Breakroom0
Lounge/Recreation - Breakroom727-2 | Lounge/Recreation - BreakroomWG702 |  |  |  |  | X | [11 empty] | 727-2 |  | 351 |  |  | WG702 |  | 351 | 26.1 |  | 22.176 | [11 empty] | 12.1124 | 13 | 5.829 | 2045.979 |  | 0.7134 | 250.4034 |  | 1946.0838 |  | 4242.4662 | 4553.3541 | [10 empty] | 12.1124 | 13 | 2.0999 | 737.059 |  | 0.95667 | 335.79 |  | 1302.5533 |  | 2375.4023 | 2549.4718 | 0 |  |  | SmHtl | Lounge/Recreation - Breakroom |  |  | Lounge/Recreation - Breakroom727-2 | Lounge/Recreation - BreakroomWG702
Electrical/Mechanical | Electrical/Mechanical |  |  |  |  | X | [9 empty] | Electrical/Mechanical | 0.43 |  | 2148 | 351 | Electrical/Mechanical | 0.43 |  | 2148 | 351 | 9.1445 |  | 9.2019 |  | 4.0775 | [21 empty] | 3.6273 | [21 empty] | -230.6956 |  |  | SmHtl | Electrical/Mechanical |  |  | Electrical/Mechanical | Electrical/Mechanical
Electrical/Mechanical738 | Electrical/MechanicalLB702 |  |  |  |  | X | [9 empty] | replacement costs are for lamps |  | 738 |  | 351 |  |  | LB702 |  | 351 | 2.1245 | 165.2174 | 2.1819 | 160.8696 | 1.5155 | 531.9257 |  | 0.35027 | 122.9465 |  | 385.3539 |  |  | 1040.2261 | 23.2775 | 24 | 0.0023 | 0.8073 |  | 0.0037224 | 1.3066 |  | 3.7259 |  | 5.8397 | 6.021 | 1.0653 | 373.9108 |  | 0.35974 | 126.2694 |  | 309.3503 |  |  | 809.5305 | 23.2775 | 24 | 0.0023 | 0.8073 |  | 0.003823 | 1.3419 |  | 3.8124 |  | 5.9615 | 6.1466 | -230.6956 | 0.12558 |  | SmHtl | Electrical/Mechanical |  |  | Electrical/Mechanical738 | Electrical/MechanicalLB702
Electrical/Mechanical739 | Electrical/MechanicalTL702 |  |  |  |  | X | [11 empty] | 739 |  | 351 |  |  | TL702 |  | 351 | 7.02 | 50 | 7.02 | 50.0001 | 2.562 | 899.262 |  | 0.6027 | 211.5477 |  | 655.0403 |  |  | 1765.85 | 23.2775 | 24 | 0.002 | 0.702 |  | 0.0123 | 4.3173 |  | 11.0312 |  | 16.0505 | 16.5487 | 2.562 | 899.262 |  | 0.6027 | 211.5477 |  | 655.0403 |  |  | 1765.85 | 23.2775 | 24 | 0.002 | 0.702 |  | 0.0123 | 4.3173 |  | 11.0312 |  | 16.0505 | 16.5487 | 0 |  |  | SmHtl | Electrical/Mechanical |  |  | Electrical/Mechanical739 | Electrical/MechanicalTL702
Electrical/Mechanical0 | Electrical/Mechanical0 |  |  |  |  | X | [11 empty] | 0 |  | 351 |  |  | 0 |  | 351 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0 |  |  | SmHtl | Electrical/Mechanical |  |  | Electrical/Mechanical0 | Electrical/Mechanical0
Electrical/Mechanical0 | Electrical/Mechanical0 |  |  |  |  | X | [11 empty] | 0 |  | 351 |  |  | 0 |  | 351 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0 |  |  | SmHtl | Electrical/Mechanical |  |  | Electrical/Mechanical0 | Electrical/Mechanical0
Electrical/Mechanical738 | Electrical/MechanicalLB702 |  |  |  |  | X | [9 empty] | ballast replacement |  | 738 |  | 351 |  |  | LB702 |  | 351 | 23.805 |  | 21.321 | [11 empty] | 23.2775 | 24 | 1.1349 | 398.3388 |  | 0.35027 | 122.9465 |  | 560.6072 |  | 1081.8925 | 1115.4744 | [10 empty] | 23.2775 | 24 | 0.79723 | 279.8276 |  | 0.35974 | 126.2694 |  | 491.5448 |  | 897.6417 | 925.5045 | 0 | -189.9699 |  | SmHtl | Electrical/Mechanical |  |  | Electrical/Mechanical738 | Electrical/MechanicalLB702
Electrical/Mechanical739 | Electrical/MechanicalTL702 |  |  |  |  | X | [11 empty] | 739 |  | 351 |  |  | TL702 |  | 351 | 12.24 |  | 12.24 | [11 empty] | 23.2775 | 24 | 1.92 | 673.92 |  | 0.6027 | 211.5477 |  | 957.1289 |  | 1842.5966 | 1899.7908 | [10 empty] | 23.2775 | 24 | 1.92 | 673.92 |  | 0.6027 | 211.5477 |  | 957.1289 |  | 1842.5966 | 1899.7908 | 0 |  |  | SmHtl | Electrical/Mechanical |  |  | Electrical/Mechanical739 | Electrical/MechanicalTL702
Electrical/Mechanical0 | Electrical/Mechanical0 |  |  |  |  | X | [11 empty] | 0 |  | 351 |  |  | 0 |  | 351 | 1e-07 |  | 1e-05 | [11 empty] | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | [10 empty] | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0 |  |  | SmHtl | Electrical/Mechanical |  |  | Electrical/Mechanical0 | Electrical/Mechanical0
Electrical/Mechanical0 | Electrical/Mechanical0 |  |  |  |  | X | [11 empty] | 0 |  | 351 |  |  | 0 |  | 351 | 1e-07 |  | 1e-05 | [11 empty] | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | [10 empty] | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0 |  |  | SmHtl | Electrical/Mechanical |  |  | Electrical/Mechanical0 | Electrical/Mechanical0
Mid-rise Apartment | [13 empty] | Mid-rise Apartment_Interior Lighting LPD |  | Mid-rise Apartment |  |  |  |  | Mid-rise Apartment |  |  |  |  | 625.6828 | 127.8576 | 563.7046 | 116.473
Office-Enclosed | Office-Enclosed | [5 empty] | X | [8 empty] | Office-Enclosed | 0.93 |  | 3231 | 950 | Office-Enclosed | 0.74 |  | 3231 | 950 | 42.3806 |  | 21.9687 | [45 empty] | -5893.2355 |  |  | MrApt | Office-Enclosed |  |  | Office-Enclosed | Office-Enclosed
Office-Enclosed700 | Office-EnclosedTR701 | [5 empty] | X | [8 empty] | replacement costs are for lamps |  | 700 |  | 950 |  |  | TR701 |  | 950 | 17.6806 | 53.7313 | 21.9687 | 43.2433 | 2.575 | 2446.2817 |  | 1.7272 | 1640.8174 |  | 2810.4929 |  |  | 6897.592 | 15.4751 | 16 | 0.0067 | 6.365 |  | 0.011446 | 10.8735 |  | 30.7778 |  | 48.0163 | 49.645 | 3.1987 | 3038.7175 |  | 1.4222 | 1351.0781 |  | 2827.7369 |  |  | 7217.5325 | 15.4751 | 16 | 0.0074 | 7.03 |  | 0.014222 | 13.5108 |  | 37.6701 |  | 58.2109 | 60.1854 | 319.9405 | -47.8493 |  | MrApt | Office-Enclosed |  |  | Office-Enclosed700 | Office-EnclosedTR701
Office-Enclosed739 | Office-Enclosed0 | [5 empty] | X | [10 empty] | 739 |  | 950 |  |  | 0 |  | 950 | 24.7 | 38.4615 | 0 | 0 | 3.3306 | 3164.07 |  | 0.78351 | 744.3345 |  | 2304.7715 |  |  | 6213.176 | 15.4751 | 16 | 0.0026 | 2.47 |  | 0.01599 | 15.1905 |  | 38.8136 |  | 56.4741 | 58.3897 | 0 | 0 |  | 0 | 0 |  | 0 |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | -6213.176 |  |  | MrApt | Office-Enclosed |  |  | Office-Enclosed739 | Office-Enclosed0
Office-Enclosed0 | Office-Enclosed0 | [5 empty] | X | [10 empty] | 0 |  | 950 |  |  | 0 |  | 950 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0 |  |  | MrApt | Office-Enclosed |  |  | Office-Enclosed0 | Office-Enclosed0
Office-Enclosed0 | Office-Enclosed0 | [5 empty] | X | [10 empty] | 0 |  | 950 |  |  | 0 |  | 950 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0 |  |  | MrApt | Office-Enclosed |  |  | Office-Enclosed0 | Office-Enclosed0
Office-Enclosed700 | Office-EnclosedTR701 | [5 empty] | X | [8 empty] | ballast replacement |  | 700 |  | 950 |  |  | TR701 |  | 950 | 62.109 |  | 76.59 | [11 empty] | 15.4751 | 16 | 1.9263 | 1829.9375 |  | 1.7272 | 1640.8174 |  | 5210.7511 |  | 8681.506 | 8975.9827 | [10 empty] | 15.4751 | 16 | 2.3934 | 2273.7656 |  | 1.4222 | 1351.0781 |  | 4790.2411 |  | 8415.0849 | 8700.5246 | 0 | -6978.579 |  | MrApt | Office-Enclosed |  |  | Office-Enclosed700 | Office-EnclosedTR701
Office-Enclosed739 | Office-Enclosed0 | [5 empty] | X | [10 empty] | 739 |  | 950 |  |  | 0 |  | 950 | 15.912 |  | 1e-05 | [11 empty] | 15.4751 | 16 | 2.496 | 2371.2 |  | 0.78351 | 744.3345 |  | 3367.6758 |  | 6483.2103 | 6703.1208 | [10 empty] | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0 |  |  | MrApt | Office-Enclosed |  |  | Office-Enclosed739 | Office-Enclosed0
Office-Enclosed0 | Office-Enclosed0 | [5 empty] | X | [10 empty] | 0 |  | 950 |  |  | 0 |  | 950 | 1e-07 |  | 1e-05 | [11 empty] | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | [10 empty] | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0 |  |  | MrApt | Office-Enclosed |  |  | Office-Enclosed0 | Office-Enclosed0
Office-Enclosed0 | Office-Enclosed0 | [5 empty] | X | [10 empty] | 0 |  | 950 |  |  | 0 |  | 950 | 1e-07 |  | 1e-05 | [11 empty] | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | [10 empty] | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0 |  |  | MrApt | Office-Enclosed |  |  | Office-Enclosed0 | Office-Enclosed0
Corridor/Transition | Corridor/Transition | [5 empty] | X | [8 empty] | Corridor/Transition | 0.66 |  | 8760 | 3345 | Corridor/Transition | 0.41 |  | 8760 | 3345 | 118.413 |  | 77.6292 | [45 empty] | -16764.3169 |  |  | MrApt | Corridor/Transition |  |  | Corridor/Transition | Corridor/Transition
Corridor/Transition701 | Corridor/TransitionDL706 | [5 empty] | X | [8 empty] | replacement costs are for lamps |  | 701 |  | 3345 |  |  | DL706 |  | 3345 | 105.925 | 31.5789 | 66.8999 | 50 | 5.2271 | 17484.7008 |  | 1.9475 | 6514.3875 |  | 15054.5176 |  |  | 39053.6059 | 5.7078 | 6 | 0.0038 | 12.711 |  | 0.019475 | 65.1439 |  | 167.8306 |  | 245.6855 | 258.2645 | 3.3013 | 11042.9689 |  | 1.23 | 4114.35 |  | 9508.1164 |  |  | 24665.4353 | 5.7078 | 6 | 0.0024 | 8.028 |  | 0.0123 | 41.1435 |  | 105.9983 |  | 155.1698 | 163.1145 | -14388.1706 | -105.4594 |  | MrApt | Corridor/Transition |  |  | Corridor/Transition701 | Corridor/TransitionDL706
Corridor/Transition0 | Corridor/Transition0 | [5 empty] | X | [10 empty] | 0 |  | 3345 |  |  | 0 |  | 3345 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0 |  |  | MrApt | Corridor/Transition |  |  | Corridor/Transition0 | Corridor/Transition0
Corridor/Transition0 | Corridor/Transition0 | [5 empty] | X | [10 empty] | 0 |  | 3345 |  |  | 0 |  | 3345 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0 |  |  | MrApt | Corridor/Transition |  |  | Corridor/Transition0 | Corridor/Transition0
Corridor/Transition703 | Corridor/TransitionWW708 | [5 empty] | X | [10 empty] | 703 |  | 3345 |  |  | WW708 |  | 3345 | 12.488 | 267.8571 | 10.7292 | 311.7648 | 2.8737 | 9612.638 |  | 0.36736 | 1228.8192 |  | 6005.1564 |  |  | 16846.6136 | 5.7078 | 6 | 0.0028 | 9.366 |  | 0.002296 | 7.6801 |  | 24.9114 |  | 41.9575 | 44.1057 | 2.4683 | 8256.4761 |  | 0.31562 | 1055.7577 |  | 5158.2335 |  |  | 14470.4673 | 5.7078 | 6 | 0.0017 | 5.6865 |  | 0.0019726 | 6.5985 |  | 19.8653 |  | 32.1503 | 33.7964 | -2376.1463 |  |  | MrApt | Corridor/Transition |  |  | Corridor/Transition703 | Corridor/TransitionWW708
Corridor/Transition701 | Corridor/TransitionDL706 | [5 empty] | X | [8 empty] | ballast replacement |  | 701 |  | 3345 |  |  | DL706 |  | 3345 | 23.256 |  | 14.688 | [11 empty] | 5.7078 | 6 | 3.9175 | 13103.9923 |  | 1.9475 | 6514.3875 |  | 24491.2652 |  | 44109.645 | 46368.0589 | [10 empty] | 5.7078 | 6 | 2.4742 | 8276.2057 |  | 1.23 | 4114.35 |  | 15468.1675 |  | 27858.7232 | 29285.0898 | 0 | -19471.3617 |  | MrApt | Corridor/Transition |  |  | Corridor/Transition701 | Corridor/TransitionDL706
Corridor/Transition0 | Corridor/Transition0 | [5 empty] | X | [10 empty] | 0 |  | 3345 |  |  | 0 |  | 3345 | 1e-07 |  | 1e-05 | [11 empty] | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | [10 empty] | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0 |  |  | MrApt | Corridor/Transition |  |  | Corridor/Transition0 | Corridor/Transition0
Corridor/Transition0 | Corridor/Transition0 | [5 empty] | X | [10 empty] | 0 |  | 3345 |  |  | 0 |  | 3345 | 1e-07 |  | 1e-05 | [11 empty] | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | [10 empty] | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0 |  |  | MrApt | Corridor/Transition |  |  | Corridor/Transition0 | Corridor/Transition0
Corridor/Transition703 | Corridor/TransitionWW708 | [5 empty] | X | [10 empty] | 703 |  | 3345 |  |  | WW708 |  | 3345 | 17.64 |  | 15.147 | [11 empty] | 5.7078 | 6 | 2.1532 | 7202.454 |  | 0.36736 | 1228.8192 |  | 7701.4611 |  | 16132.7343 | 16958.7303 | [10 empty] | 5.7078 | 6 | 1.85 | 6188.0922 |  | 0.31562 | 1055.7577 |  | 6616.8213 |  | 13860.6713 | 14570.3376 | 0 |  |  | MrApt | Corridor/Transition |  |  | Corridor/Transition703 | Corridor/TransitionWW708
Dwelling-Unit | Dwelling-Unit | [5 empty] | X | [8 empty] | Dwelling-Unit | 0.29 |  | 526 | 29450 | Dwelling-Unit | 0.2905 |  | 526 | 29450 | 464.8893 |  | 464.1067 | [45 empty] | 466.9135 |  |  | MrApt | Dwelling-Unit |  |  | Dwelling-Unit | Dwelling-Unit
Dwelling-Unit301 | Dwelling-Unit301 | [5 empty] | X | [8 empty] | replacement costs are for lamps |  | 301 |  | 29450 |  |  | 301 |  | 29450 | 44.175 | 666.6667 | 44.7332 | 658.3478 | 0.010477 | 308.5473 |  | 0 | 0 |  | 154.6725 |  |  | 463.2198 | 1.9011 | 2 | 0.010477 | 308.5473 |  | 0 | 0 |  | 200.9945 |  | 509.5418 | 536.0379 | 0.0013519 | 39.8126 |  | 0 | 0 |  | 19.9577 |  |  | 59.7703 | 1.9011 | 2 | 0.0013519 | 39.8126 |  | 0 | 0 |  | 25.9348 |  | 65.7473 | 69.1662 | -403.4495 | 540.3123 |  | MrApt | Dwelling-Unit |  |  | Dwelling-Unit301 | Dwelling-Unit301
Dwelling-Unit302 | Dwelling-Unit302 | [5 empty] | X | [10 empty] | 302 |  | 29450 |  |  | 302 |  | 29450 | 420.7143 | 70 | 419.3735 | 70.2238 | 0.0076555 | 225.4553 |  | 0 | 0 |  | 113.0191 |  |  | 338.4745 | 19.0114 | 20 | 0.0076555 | 225.4553 |  | 0 | 0 |  | 146.8666 |  | 372.3219 | 391.6827 | 0.027341 | 805.1976 |  | 0 | 0 |  | 403.6398 |  |  | 1208.8374 | 19.0114 | 20 | 0.027341 | 805.1976 |  | 0 | 0 |  | 524.5235 |  | 1329.7212 | 1398.8667 | 870.3629 |  |  | MrApt | Dwelling-Unit |  |  | Dwelling-Unit302 | Dwelling-Unit302
Dwelling-Unit303 | Dwelling-Unit303 | [5 empty] | X | [10 empty] | 303 |  | 29450 |  |  | 303 |  | 29450 | 0 | #DIV/0! | 0 | #DIV/0! | 0 | 0 |  | 0 | 0 |  | 0 |  |  | 0 | 28.5171 | 29 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  |  | 0 | 28.5171 | 29 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0 |  |  | MrApt | Dwelling-Unit |  |  | Dwelling-Unit303 | Dwelling-Unit303
Dwelling-Unit0 | Dwelling-Unit0 | [5 empty] | X | [10 empty] | 0 |  | 29450 |  |  | 0 |  | 29450 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0 |  |  | MrApt | Dwelling-Unit |  |  | Dwelling-Unit0 | Dwelling-Unit0
Dwelling-Unit301 | Dwelling-Unit301 | [5 empty] | X | [8 empty] | ballast replacement |  | 301 |  | 29450 |  |  | 301 |  | 29450 | 6.3568 |  | 0.82025 | [11 empty] | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | [10 empty] | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0 | 0 |  | MrApt | Dwelling-Unit |  |  | Dwelling-Unit301 | Dwelling-Unit301
Dwelling-Unit302 | Dwelling-Unit302 | [5 empty] | X | [10 empty] | 302 |  | 29450 |  |  | 302 |  | 29450 | 2.5837 |  | 9.2277 | [11 empty] | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | [10 empty] | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0 |  |  | MrApt | Dwelling-Unit |  |  | Dwelling-Unit302 | Dwelling-Unit302
Dwelling-Unit303 | Dwelling-Unit303 | [5 empty] | X | [10 empty] | 303 |  | 29450 |  |  | 303 |  | 29450 | 1e-07 |  | 1e-05 | [11 empty] | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | [10 empty] | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0 |  |  | MrApt | Dwelling-Unit |  |  | Dwelling-Unit303 | Dwelling-Unit303
Dwelling-Unit0 | Dwelling-Unit0 | [5 empty] | X | [10 empty] | 0 |  | 29450 |  |  | 0 |  | 29450 | 1e-07 |  | 1e-05 | [11 empty] | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | [10 empty] | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0 |  |  | MrApt | Dwelling-Unit |  |  | Dwelling-Unit0 | Dwelling-Unit0
Where there was no LPD difference between 2016 and 2019; 2013 LSC designs were used for both 2013 and 2019.
Where there was an increase in LPD, the space was not included in the cost estimate, as the added cost is not required by 90.1.

## Int Ltg LPD Proto IECC (hidden)
| #VALUE! | [18 empty] | State Commercial Energy Code Cost Effectiveness - Interior Lighting Power Density - IECC 2009 and IECC 2012 - Costs Totals for Each Prototype | [54 empty] | 90.1 Cost Effectiveness - Interior Lighting Power Density 90.1-07by and 90.1-07de Costs - Prototype
Summary
IECC 2012 has changes to interior lighting power allowances, generally significantly lower that for IECC 2009
The cost of interior lighting for the prototypes that meets the lighting power allowances for IECC 2009 and IECC 2012 are shown below.
Interior Lighting - Summary of Total New Construction, Maintenance, and Replacement Costs By Replacement Year by Prototype
[7 empty] | Cost Parameters | [30 empty] | #N/A
[20 empty] | 2009 IECC |  |  |  |  | 2012 IECC | [5 empty] | IECC 2009 Baseline Costs - without implementation of the addenda. | [21 empty] | IECC 2012 - costs with addendum | [20 empty] | Incremental Costs | Small Office | [7 empty] | Large Office | [7 empty] | Standalone Retail | [7 empty] | Primary School | [7 empty] | Small Hotel | [7 empty] | Mid-rise Apartment
|  | Related 90.1-07 Addenda and IECC 2012 Sections |  |  |  | Prototypes Affected | [5 empty] | Climate Location | [5 empty] | Name of Item | [12 empty] | New Construction Costs | [9 empty] | Replacement Costs | [11 empty] | New Construction Costs | [9 empty] | Replacement Costs | [11 empty] | IECC 2009 |  |  | IECC 2012 |  |  | Incremental Cost |  | IECC 2009 |  |  | IECC 2012 |  |  | Incremental Cost |  | IECC 2009 |  |  | IECC 2012 |  |  | Incremental Cost |  | IECC 2009 |  |  | IECC 2012 |  |  | Incremental Cost |  | IECC 2009 |  |  | IECC 2012 |  |  | Incremental Cost |  | IECC 2009 |  |  | IECC 2012 |  |  | Incremental Cost
2009 Lookup | 2012 Lookup | 90.1 Addenda | IECC 2009 Chapter(s) Affected | IECC 2012 Section(s) affected | Affected Items | Small Office | Large Office | Standalone Retail | Primary School | Small Hotel | Mid-rise Apartment | 2A Houston | 3A Memphis | 3B El Paso | 4A Baltimore | 5A Chicago | Not Used | Interior Lighting Power Density | Not Used | Costs to provide lighting fixtures, lamps and ballasts to meet space by space lighting power density (LPD) maximum allowed LPD values under IECC 2009. Fixtures, lamps and ballasts and quantities defined from 90.1 development interior lighting models and additional input from 90.1 Lighting Subcommittee. Costs are for equipment etc. at today's prices that just meet the IECC 2009 requirements. Costs by IECC 2009 Prototype and Lighting Space Type | IECC 2009 Allowed Maximum LPD W/ft2 | Fixture ID Numbers | Annual Full Load Equivalent Operating Hours for Space Type Lamp Life for Fixtures (Used to Calculate Replacement Life) | Area of Space Type In Prototype Models | Costs to provide lighting fixtures, lamps and ballasts to meet space by space maximum allowed LPD values under IECC 2012 Table 9.6.1. Fixtures, lamps and ballasts and quantities defined from 90.1 development interior lighting models and additional input from 90.1 Lighting Subcommittee. Costs by IECC 2012 Prototype and Lighting Space Type | IECC 2012 Allowed Maximum LPD W/ft2 | Fixture ID Numbers | Annual Full Load Equivalent (FLE) Operating Hours | Area of Space Type, ft2 | Not Used | Material Cost/ft2 | Material Subtotal Cost/ft2 × area for space type | Labor Crew Type Not Used | Labor Cost/ft2 | Labor Subtotal Cost/ft2 × Area | Construction Equipment Subtotal | Cost Adjustments | Not Used | Not Used | Total | Replacement Life (hours of operation/ component life) | Replacement Period (costs assigned to a 1 year period) | Material Cost/ft2 | Material Subtotal Cost/ft2 × area for space type | Labor Crew Type Not Used | Labor Cost/ft2 | Labor Subtotal Cost/ft2 × Area | Construction Equipment Subtotal | Cost Adjustments | Not Used | Subtotal | Total (adjusted for actual quantity of replacements in replacement period) | Material Cost/ft2 | Material Subtotal Cost/ft2 × area for space type | Labor Crew Type Not Used | Labor Cost/ft2 | Labor Subtotal Cost/ft2 × Area | Construction Equipment Subtotal | Cost Adjustments | Not Used | Not Used | Total | Replacement Life (hours of operation/ component life) | Replacement Period (costs assigned to a 1 year period) | Material Cost/ft2 | Material Subtotal Cost/ft2 × area for space type | Labor Crew Type Not Used | Labor Cost/ft2 | Labor Subtotal Cost/ft2 × Area | Construction Equipment Subtotal | Cost Adjustments | Subtotal | Total (adjusted for actual quantity of replacements in replacement period) | New Construction Costs 2010 minus 2007 | Category | All Costs, First Replacement Only | With Repeated Replacements | Category | Replacement First Year | With Repeated Replacements | 30 Year | 40 Year | Category | All Costs, First Replacement Only | With Repeated Replacements | Category | Replacement First Year | With Repeated Replacements | 30 Year | 40 Year | Category | All Costs, First Replacement Only | With Repeated Replacements | Category | Replacement First Year | With Repeated Replacements | 30 Year | 40 Year | Category | All Costs, First Replacement Only | With Repeated Replacements | Category | Replacement First Year | With Repeated Replacements | 30 Year | 40 Year | Category | All Costs, First Replacement Only | With Repeated Replacements | Category | Replacement First Year | With Repeated Replacements | 30 Year | 40 Year | Category | All Costs, First Replacement Only | With Repeated Replacements | Category | Replacement First Year | With Repeated Replacements | 30 Year | 40 Year
[6 empty] | n | [5 empty] | X | X | X | X | X |  | Small _Office_Interior_Lighting_LPD |  | Small Office |  |  | 3642 |  | Small Office |  |  | 3642 | [46 empty] | New Construction | 0 | 0 | New Construction | 0 | 0 | 0 | 0 | New Construction | 0 | 0 | New Construction | 0 | 0 | 0 | 0 | New Construction | 0 | 0 | New Construction | 0 | 0 | 0 | 0 | New Construction | 0 | 0 | New Construction | 0 | 0 | 0 | 0 | New Construction | 0 | 0 | New Construction | 0 | 0 | 0 | 0 | New Construction | 0 | 0 | New Construction | 0 | 0 | 0 | 0
Office - Open Plan (Including Other) | Office - Open Plan (Including Other) |  |  |  |  | n | [13 empty] | Office - Open Plan (Including Other) | 1.1 |  |  | 1100 | Office - Open Plan (Including Other) | 0.9555 |  |  | 1100 | [45 empty] | Maintenance | 0 | 0 | Maintenance | 0 | 0 | 0 | 0 | Maintenance | 0 | 0 | Maintenance | 0 | 0 | 0 | 0 | Maintenance | 0 | 0 | Maintenance | 0 | 0 | 0 | 0 | Maintenance | 0 | 0 | Maintenance | 0 | 0 | 0 | 0 | Maintenance | 0 | 0 | Maintenance | 0 | 0 | 0 | 0 | Maintenance | 0 | 0 | Maintenance | 0 | 0 | 0 | 0
Office - Open Plan (Including Other)535 | Office - Open Plan (Including Other)535 |  |  |  |  | n | [13 empty] | replacement costs shown are for lamps |  | 535 |  | 1100 |  |  | 535 |  | 1100 |  | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A | #N/A | #N/A | #N/A | Replacement - Year |  |  | Replacement - Year |  |  | 0 | 0 | Replacement - Year |  |  | Replacement - Year |  |  | 0 | 0 | Replacement - Year |  |  | Replacement - Year |  |  | 0 | 0 | Replacement - Year |  |  | Replacement - Year |  |  | 0 | 0 | Replacement - Year |  |  | Replacement - Year |  |  | 0 | 0 | Replacement - Year |  |  | Replacement - Year |  |  | 0 | 0
Office - Open Plan (Including Other)539 | Office - Open Plan (Including Other)539 |  |  |  |  | n | [15 empty] | 539 |  | 1100 |  |  | 539 |  | 1100 |  | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A | #N/A | #N/A | #N/A | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 0
Office - Open Plan (Including Other)524 | Office - Open Plan (Including Other)0 |  |  |  |  | n | [15 empty] | 524 |  | 1100 |  |  | 0 |  | 1100 |  | 0.14484 | 159.3197 |  | 0.099336 | 109.2691 |  | 185.3638 |  |  | 453.9527 | 2.7457 | 3 | 0.050718 | 55.7894 |  | 0.0093682 | 10.3051 |  | 47.5794 |  | 113.6738 | 124.2 | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | 0 | 0 | 0 | 0 |  | #N/A | #N/A |  | #N/A | #N/A | 0 | #N/A | 2 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 0 | 0
Office - Open Plan (Including Other) | Office - Open Plan (Including Other)537-1 |  |  |  |  | n | [20 empty] | 537-1 |  | 1100 | [23 empty] | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A | #N/A | #N/A | #N/A | 3 | 0 | 0 | 3 | 0 | 0 | 0 | 0 | 3 | 0 | 0 | 3 | 0 | 0 | 0 | 0 | 3 | 0 | 0 | 3 | 0 | 0 | 0 | 0 | 3 | 0 | 0 | 3 | 0 | 0 | 0 | 0 | 3 | 0 | 0 | 3 | 0 | 0 | 0 | 0 | 3 | 0 | 0 | 3 | 0 | 0 | 0 | 0
Office - Open Plan (Including Other)535 | Office - Open Plan (Including Other)535 |  |  |  |  | n | [13 empty] | ballast replacement |  | 535 |  | 1100 |  |  | 535 |  | 1100 | [11 empty] | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  | #N/A | #N/A | [10 empty] | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A | #N/A | #N/A | 0 | 4 | 0 | 0 | 4 | 0 | 0 | 0 | 0 | 4 | 0 | 0 | 4 | 0 | 0 | 0 | 0 | 4 | 0 | 0 | 4 | 0 | 0 | 0 | 0 | 4 | 0 | 0 | 4 | 0 | 0 | 0 | 0 | 4 | 0 | 0 | 4 | 0 | 0 | 0 | 0 | 4 | 0 | 0 | 4 | 0 | 0 | 0 | 0
Office - Open Plan (Including Other)539 | Office - Open Plan (Including Other)539 |  |  |  |  | n | [15 empty] | 539 |  | 1100 |  |  | 539 |  | 1100 | [11 empty] | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  | #N/A | #N/A | [10 empty] | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A | #N/A | #N/A | 0 | 5 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 5 | 0 | 0 | 0 | 0
Office - Open Plan (Including Other)524 | Office - Open Plan (Including Other)0 |  |  |  |  | n | [15 empty] | 524 |  | 1100 |  |  | 0 |  | 1100 | [11 empty] | 13.7287 | 14 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | [10 empty] | #N/A | #N/A | 0 | 0 |  | 0 | 0 |  | 0 | 0 | #N/A | 0 | 6 | 0 | 0 | 6 | 0 | 0 | 0 | 0 | 6 | 0 | 0 | 6 | 0 | 0 | 0 | 0 | 6 | 0 | 0 | 6 | 0 | 0 | 0 | 0 | 6 | 0 | 0 | 6 | 0 | 0 | 0 | 0 | 6 | 0 | 0 | 6 | 0 | 0 | 0 | 0 | 6 | 0 | 0 | 6 | 0 | 0 | 0 | 0
Office - Open Plan (Including Other) | Office - Open Plan (Including Other)537-1 |  |  |  |  | n | [20 empty] | 537-1 |  | 1100 | [33 empty] | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A | #N/A | #N/A | 0 | 7 | 0 | 0 | 7 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 7 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 7 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 7 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 7 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 7 | 0 | 0 | 0 | 0
Office-Enclosed | Office-Enclosed |  |  |  |  | n | [13 empty] | Office-Enclosed | 1.1 |  |  | 1595 | Office-Enclosed | 1.0822 |  |  | 1595 | [45 empty] | 8 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 8 | 0 | 0 | 0 | 0
Office-Enclosed535 | Office-Enclosed531 |  |  |  |  | n | [13 empty] | lamp replacement |  | 535 |  | 1595 |  |  | 531 |  | 1595 |  | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A | #N/A | #N/A | #N/A | 9 | 0 | 0 | 9 | 0 | 0 | 0 | 0 | 9 | 0 | 0 | 9 | 0 | 0 | 0 | 0 | 9 | 0 | 0 | 9 | 0 | 0 | 0 | 0 | 9 | 0 | 0 | 9 | 0 | 0 | 0 | 0 | 9 | 0 | 0 | 9 | 0 | 0 | 0 | 0 | 9 | 0 | 0 | 9 | 0 | 0 | 0 | 0
Office-Enclosed539 | Office-Enclosed539 |  |  |  |  | n | [15 empty] | 539 |  | 1595 |  |  | 539 |  | 1595 |  | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A | #N/A | #N/A | #N/A | 10 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 10 | 0 | 0 | 0 | 0
Office-Enclosed537-2 | Office-Enclosed0 |  |  |  |  | n | [15 empty] | 537-2 |  | 1595 |  |  | 0 |  | 1595 |  | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | 0 | 0 | 0 | 0 |  | #N/A | #N/A |  | #N/A | #N/A | 0 | #N/A | 11 | 0 | 0 | 11 | 0 | 0 | 0 | 0 | 11 | 0 | 0 | 11 | 0 | 0 | 0 | 0 | 11 | 0 | 0 | 11 | 0 | 0 | 0 | 0 | 11 | 0 | 0 | 11 | 0 | 0 | 0 | 0 | 11 | 0 | 0 | 11 | 0 | 0 | 0 | 0 | 11 | 0 | 0 | 11 | 0 | 0 | 0 | 0
Office-Enclosed | Office-Enclosed537-1 |  |  |  |  | n | [20 empty] | 537-1 |  | 1595 | [23 empty] | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A | #N/A | #N/A | #N/A | 12 | 0 | 0 | 12 | 0 | 0 | 0 | 0 | 12 | 0 | 0 | 12 | 0 | 0 | 0 | 0 | 12 | 0 | 0 | 12 | 0 | 0 | 0 | 0 | 12 | 0 | 0 | 12 | 0 | 0 | 0 | 0 | 12 | 0 | 0 | 12 | 0 | 0 | 0 | 0 | 12 | 0 | 0 | 12 | 0 | 0 | 0 | 0
Office-Enclosed535 | Office-Enclosed531 |  |  |  |  | n | [13 empty] | ballast replacement |  | 535 |  | 1595 |  |  | 531 |  | 1595 | [11 empty] | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  | #N/A | #N/A | [10 empty] | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A | #N/A | #N/A | 0 | 13 | 0 | 0 | 13 | 0 | 0 | 0 | 0 | 13 | 0 | 0 | 13 | 0 | 0 | 0 | 0 | 13 | 0 | 0 | 13 | 0 | 0 | 0 | 0 | 13 | 0 | 0 | 13 | 0 | 0 | 0 | 0 | 13 | 0 | 0 | 13 | 0 | 0 | 0 | 0 | 13 | 0 | 0 | 13 | 0 | 0 | 0 | 0
Office-Enclosed539 | Office-Enclosed539 |  |  |  |  | n | [15 empty] | 539 |  | 1595 |  |  | 539 |  | 1595 | [11 empty] | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  | #N/A | #N/A | [10 empty] | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A | #N/A | #N/A | 0 | 14 | 0 | 0 | 14 | 0 | 0 | 0 | 0 | 14 | 0 | 0 | 14 | 0 | 0 | 0 | 0 | 14 | 0 | 0 | 14 | 0 | 0 | 0 | 0 | 14 | 0 | 0 | 14 | 0 | 0 | 0 | 0 | 14 | 0 | 0 | 14 | 0 | 0 | 0 | 0 | 14 | 0 | 0 | 14 | 0 | 0 | 0 | 0
Office-Enclosed537-2 | Office-Enclosed0 |  |  |  |  | n | [15 empty] | 537-2 |  | 1595 |  |  | 0 |  | 1595 | [11 empty] | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  | #N/A | #N/A | [10 empty] | #N/A | #N/A | 0 | 0 |  | 0 | 0 |  | 0 | 0 | #N/A | 0 | 15 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 15 | 0 | 0 | 0 | 0
Office-Enclosed | Office-Enclosed537-1 |  |  |  |  | n | [20 empty] | 537-1 |  | 1595 | [33 empty] | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A | #N/A | #N/A | 0 | 16 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 16 | 0 | 0 | 0 | 0
Conference/Meeting/Multipurpose | Conference/Meeting/Multipurpose |  |  |  |  | n | [13 empty] | Conference/Meeting/Multipurpose | 1.3 |  |  | 550 | Conference/Meeting/Multipurpose | 1.1992 |  |  | 550 | [45 empty] | 17 | 0 | 0 | 17 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 17 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 17 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 17 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 17 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 17 | 0 | 0 | 0 | 0
Conference/Meeting/Multipurpose535 | Conference/Meeting/Multipurpose535 |  |  |  |  | n | [13 empty] | lamp replacement |  | 535 |  | 550 |  |  | 535 |  | 550 |  | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A | #N/A | #N/A | #N/A | 18 | 0 | 0 | 18 | 0 | 0 | 0 | 0 | 18 | 0 | 0 | 18 | 0 | 0 | 0 | 0 | 18 | 0 | 0 | 18 | 0 | 0 | 0 | 0 | 18 | 0 | 0 | 18 | 0 | 0 | 0 | 0 | 18 | 0 | 0 | 18 | 0 | 0 | 0 | 0 | 18 | 0 | 0 | 18 | 0 | 0 | 0 | 0
Conference/Meeting/Multipurpose537-1 | Conference/Meeting/Multipurpose511 |  |  |  |  | n | [15 empty] | 537-1 |  | 550 |  |  | 511 |  | 550 |  | 1.3501 | 742.5691 |  | 0.80171 | 440.9385 |  | 797.9654 |  |  | 1981.473 | 9.8847 | 10 | 0.04367 | 24.0186 |  | 0.071264 | 39.195 |  | 58.3854 |  | 121.5991 | 123.0177 | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A | #N/A | #N/A | #N/A | 19 | 0 | 0 | 19 | 0 | 0 | 0 | 0 | 19 | 0 | 0 | 19 | 0 | 0 | 0 | 0 | 19 | 0 | 0 | 19 | 0 | 0 | 0 | 0 | 19 | 0 | 0 | 19 | 0 | 0 | 0 | 0 | 19 | 0 | 0 | 19 | 0 | 0 | 0 | 0 | 19 | 0 | 0 | 19 | 0 | 0 | 0 | 0
Conference/Meeting/Multipurpose511 | Conference/Meeting/Multipurpose0 |  |  |  |  | n | [15 empty] | 511 |  | 550 |  |  | 0 |  | 550 |  | 0.1594 | 87.6705 |  | 0.26438 | 145.4082 |  | 184.3385 |  |  | 417.4173 | 1.1532 | 2 | 0.091909 | 50.5501 |  | 0.01251 | 6.8803 |  | 40.4319 |  | 97.8622 | 169.721 | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | 0 | 0 | 0 | 0 |  | #N/A | #N/A |  | #N/A | #N/A | 0 | #N/A | 20 | 0 | 0 | 20 | 0 | 0 | 0 | 0 | 20 | 0 | 0 | 20 | 0 | 0 | 0 | 0 | 20 | 0 | 0 | 20 | 0 | 0 | 0 | 0 | 20 | 0 | 0 | 20 | 0 | 0 | 0 | 0 | 20 | 0 | 0 | 20 | 0 | 0 | 0 | 0 | 20 | 0 | 0 | 20 | 0 | 0 | 0 | 0
Conference/Meeting/Multipurpose | Conference/Meeting/Multipurpose527-1 |  |  |  |  | n | [20 empty] | 527-1 |  | 550 | [23 empty] | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A | #N/A | #N/A | #N/A | 21 | 0 | 0 | 21 | 0 | 0 | 0 | 0 | 21 | 0 | 0 | 21 | 0 | 0 | 0 | 0 | 21 | 0 | 0 | 21 | 0 | 0 | 0 | 0 | 21 | 0 | 0 | 21 | 0 | 0 | 0 | 0 | 21 | 0 | 0 | 21 | 0 | 0 | 0 | 0 | 21 | 0 | 0 | 21 | 0 | 0 | 0 | 0
Conference/Meeting/Multipurpose535 | Conference/Meeting/Multipurpose535 |  |  |  |  | n | [13 empty] | ballast replacement |  | 535 |  | 550 |  |  | 535 |  | 550 | [11 empty] | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  | #N/A | #N/A | [10 empty] | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A | #N/A | #N/A | 0 | 22 | 0 | 0 | 22 | 0 | 0 | 0 | 0 | 22 | 0 | 0 | 22 | 0 | 0 | 0 | 0 | 22 | 0 | 0 | 22 | 0 | 0 | 0 | 0 | 22 | 0 | 0 | 22 | 0 | 0 | 0 | 0 | 22 | 0 | 0 | 22 | 0 | 0 | 0 | 0 | 22 | 0 | 0 | 22 | 0 | 0 | 0 | 0
Conference/Meeting/Multipurpose537-1 | Conference/Meeting/Multipurpose511 |  |  |  |  | n | [15 empty] | 537-1 |  | 550 |  |  | 511 |  | 550 | [11 empty] | 13.7287 | 14 | 0.39108 | 215.092 |  | 0.80171 | 440.9385 |  | 620.9256 |  | 1276.956 | 1302.1887 | [10 empty] | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A | #N/A | #N/A | 0 | 23 | 0 | 0 | 23 | 0 | 0 | 0 | 0 | 23 | 0 | 0 | 23 | 0 | 0 | 0 | 0 | 23 | 0 | 0 | 23 | 0 | 0 | 0 | 0 | 23 | 0 | 0 | 23 | 0 | 0 | 0 | 0 | 23 | 0 | 0 | 23 | 0 | 0 | 0 | 0 | 23 | 0 | 0 | 23 | 0 | 0 | 0 | 0
Conference/Meeting/Multipurpose511 | Conference/Meeting/Multipurpose0 |  |  |  |  | n | [15 empty] | 511 |  | 550 |  |  | 0 |  | 550 | [11 empty] | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | [10 empty] | #N/A | #N/A | 0 | 0 |  | 0 | 0 |  | 0 | 0 | #N/A | 0 | 24 | 0 | 0 | 24 | 0 | 0 | 0 | 0 | 24 | 0 | 0 | 24 | 0 | 0 | 0 | 0 | 24 | 0 | 0 | 24 | 0 | 0 | 0 | 0 | 24 | 0 | 0 | 24 | 0 | 0 | 0 | 0 | 24 | 0 | 0 | 24 | 0 | 0 | 0 | 0 | 24 | 0 | 0 | 24 | 0 | 0 | 0 | 0
Conference/Meeting/Multipurpose | Conference/Meeting/Multipurpose527-1 |  |  |  |  | n | [20 empty] | 527-1 |  | 550 | [33 empty] | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A | #N/A | #N/A | 0 | 25 | 0 | 0 | 25 | 0 | 0 | 0 | 0 | 25 | 0 | 0 | 25 | 0 | 0 | 0 | 0 | 25 | 0 | 0 | 25 | 0 | 0 | 0 | 0 | 25 | 0 | 0 | 25 | 0 | 0 | 0 | 0 | 25 | 0 | 0 | 25 | 0 | 0 | 0 | 0 | 25 | 0 | 0 | 25 | 0 | 0 | 0 | 0
Corridor/Transition | Corridor/Transition |  |  |  |  | n | [13 empty] | Corridor/Transition | 0.5 |  |  | 660 | Corridor/Transition | 0.6435 |  |  | 660 | [45 empty] | 26 | 0 | 0 | 26 | 0 | 0 | 0 | 0 | 26 | 0 | 0 | 26 | 0 | 0 | 0 | 0 | 26 | 0 | 0 | 26 | 0 | 0 | 0 | 0 | 26 | 0 | 0 | 26 | 0 | 0 | 0 | 0 | 26 | 0 | 0 | 26 | 0 | 0 | 0 | 0 | 26 | 0 | 0 | 26 | 0 | 0 | 0 | 0
Corridor/Transition530 | Corridor/Transition521 |  |  |  |  | n | [13 empty] | replacement costs are for lamps |  | 530 |  | 660 |  |  | 521 |  | 660 |  | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A | #N/A | #N/A | #N/A | 27 | 0 | 0 | 27 | 0 | 0 | 0 | 0 | 27 | 0 | 0 | 27 | 0 | 0 | 0 | 0 | 27 | 0 | 0 | 27 | 0 | 0 | 0 | 0 | 27 | 0 | 0 | 27 | 0 | 0 | 0 | 0 | 27 | 0 | 0 | 27 | 0 | 0 | 0 | 0 | 27 | 0 | 0 | 27 | 0 | 0 | 0 | 0
Corridor/Transition537-2 | Corridor/Transition0 |  |  |  |  | n | [15 empty] | 537-2 |  | 660 |  |  | 0 |  | 660 |  | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | 0 | 0 | 0 | 0 |  | #N/A | #N/A |  | #N/A | #N/A | 0 | #N/A | 28 | 0 | 0 | 28 | 0 | 0 | 0 | 0 | 28 | 0 | 0 | 28 | 0 | 0 | 0 | 0 | 28 | 0 | 0 | 28 | 0 | 0 | 0 | 0 | 28 | 0 | 0 | 28 | 0 | 0 | 0 | 0 | 28 | 0 | 0 | 28 | 0 | 0 | 0 | 0 | 28 | 0 | 0 | 28 | 0 | 0 | 0 | 0
Corridor/Transition0 | Corridor/Transition0 |  |  |  |  | n | [15 empty] | 0 |  | 660 |  |  | 0 |  | 660 |  | 0 | 0 |  | 0 | 0 |  | 0 |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | 0 | 0 | 0 | 0 |  | #N/A | #N/A |  | #N/A | #N/A | 0 | #N/A | 29 | 0 | 0 | 29 | 0 | 0 | 0 | 0 | 29 | 0 | 0 | 29 | 0 | 0 | 0 | 0 | 29 | 0 | 0 | 29 | 0 | 0 | 0 | 0 | 29 | 0 | 0 | 29 | 0 | 0 | 0 | 0 | 29 | 0 | 0 | 29 | 0 | 0 | 0 | 0 | 29 | 0 | 0 | 29 | 0 | 0 | 0 | 0
Corridor/Transition | Corridor/Transition527-2 |  |  |  |  | n | [20 empty] | 0 |  | 660 | [23 empty] | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | 0 | 0 | 0 | 0 |  | #N/A | #N/A |  | #N/A | #N/A | 0 | #N/A | 30 | 0 | 0 | 30 | 0 | 0 | 0 | 0 | 30 | 0 | 0 | 30 | 0 | 0 | 0 | 0 | 30 | 0 | 0 | 30 | 0 | 0 | 0 | 0 | 30 | 0 | 0 | 30 | 0 | 0 | 0 | 0 | 30 | 0 | 0 | 30 | 0 | 0 | 0 | 0 | 30 | 0 | 0 | 30 | 0 | 0 | 0 | 0
Corridor/Transition530 | Corridor/Transition521 |  |  |  |  | n | [13 empty] | replacement costs are for ballasts |  | 530 |  | 660 |  |  | 521 |  | 660 | [11 empty] | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  | #N/A | #N/A | [10 empty] | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A | #N/A | #N/A | 0 | 31 | 0 | 0 | 31 | 0 | 0 |  | 0 | 31 | 0 | 0 | 31 | 0 | 0 |  | 0 | 31 | 0 | 0 | 31 | 0 | 0 |  | 0 | 31 | 0 | 0 | 31 | 0 | 0 |  | 0 | 31 | 0 | 0 | 31 | 0 | 0 |  | 0 | 31 | 0 | 0 | 31 | 0 | 0 |  | 0
Corridor/Transition537-2 | Corridor/Transition0 |  |  |  |  | n | [15 empty] | 537-2 |  | 660 |  |  | 0 |  | 660 | [11 empty] | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  | #N/A | #N/A | [10 empty] | #N/A | #N/A | 0 | 0 |  | 0 | 0 |  | 0 | 0 | #N/A | 0 | 32 | 0 | 0 | 32 | 0 | 0 |  | 0 | 32 | 0 | 0 | 32 | 0 | 0 |  | 0 | 32 | 0 | 0 | 32 | 0 | 0 |  | 0 | 32 | 0 | 0 | 32 | 0 | 0 |  | 0 | 32 | 0 | 0 | 32 | 0 | 0 |  | 0 | 32 | 0 | 0 | 32 | 0 | 0 |  | 0
Corridor/Transition0 | Corridor/Transition0 |  |  |  |  | n | [15 empty] | 0 |  | 660 |  |  | 0 |  | 660 | [11 empty] | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | [10 empty] | #N/A | #N/A | 0 | 0 |  | 0 | 0 |  | 0 | 0 | #N/A | 0 | 33 | 0 | 0 | 33 | 0 | 0 |  | 0 | 33 | 0 | 0 | 33 | 0 | 0 |  | 0 | 33 | 0 | 0 | 33 | 0 | 0 |  | 0 | 33 | 0 | 0 | 33 | 0 | 0 |  | 0 | 33 | 0 | 0 | 33 | 0 | 0 |  | 0 | 33 | 0 | 0 | 33 | 0 | 0 |  | 0
Corridor/Transition | Corridor/Transition527-2 |  |  |  |  | n | [20 empty] | 0 |  | 660 | [33 empty] | #N/A | #N/A | 0 | 0 |  | 0 | 0 |  | 0 | 0 | #N/A | 0 | 34 | 0 | 0 | 34 | 0 | 0 |  | 0 | 34 | 0 | 0 | 34 | 0 | 0 |  | 0 | 34 | 0 | 0 | 34 | 0 | 0 |  | 0 | 34 | 0 | 0 | 34 | 0 | 0 |  | 0 | 34 | 0 | 0 | 34 | 0 | 0 |  | 0 | 34 | 0 | 0 | 34 | 0 | 0 |  | 0
Conference/Meeting/Multipurpose | Conference/Meeting/Multipurpose |  |  |  |  | n | [13 empty] | Conference/Meeting/Multipurpose | 1.3 |  |  | 440 | Conference/Meeting/Multipurpose |  |  |  | 550 | [45 empty] | 35 | 0 | 0 | 35 | 0 | 0 |  | 0 | 35 | 0 | 0 | 35 | 0 | 0 |  | 0 | 35 | 0 | 0 | 35 | 0 | 0 |  | 0 | 35 | 0 | 0 | 35 | 0 | 0 |  | 0 | 35 | 0 | 0 | 35 | 0 | 0 |  | 0 | 35 | 0 | 0 | 35 | 0 | 0 |  | 0
Conference/Meeting/Multipurpose535 | Conference/Meeting/Multipurpose535 |  |  |  |  | n | [13 empty] | replacement costs are for lamps |  | 535 |  | 440 |  |  | 535 |  | 550 |  | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A | #N/A | #N/A | #N/A | 36 | 0 | 0 | 36 | 0 | 0 |  | 0 | 36 | 0 | 0 | 36 | 0 | 0 |  | 0 | 36 | 0 | 0 | 36 | 0 | 0 |  | 0 | 36 | 0 | 0 | 36 | 0 | 0 |  | 0 | 36 | 0 | 0 | 36 | 0 | 0 |  | 0 | 36 | 0 | 0 | 36 | 0 | 0 |  | 0
Conference/Meeting/Multipurpose537-1 | Conference/Meeting/Multipurpose511 |  |  |  |  | n | [15 empty] | 537-1 |  | 440 |  |  | 511 |  | 550 |  | 1.3501 | 594.0553 |  | 0.80171 | 352.7508 |  | 638.3723 |  |  | 1585.1784 | 9.8847 | 10 | 0.04367 | 19.2149 |  | 0.071264 | 31.356 |  | 46.7084 |  | 97.2793 | 98.4142 | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A | #N/A | #N/A | #N/A | 37 | 0 | 0 | 37 | 0 | 0 |  | 0 | 37 | 0 | 0 | 37 | 0 | 0 |  | 0 | 37 | 0 | 0 | 37 | 0 | 0 |  | 0 | 37 | 0 | 0 | 37 | 0 | 0 |  | 0 | 37 | 0 | 0 | 37 | 0 | 0 |  | 0 | 37 | 0 | 0 | 37 | 0 | 0 |  | 0
Conference/Meeting/Multipurpose511 | Conference/Meeting/Multipurpose0 |  |  |  |  | n | [15 empty] | 511 |  | 440 |  |  | 0 |  | 550 |  | 0.1594 | 70.1364 |  | 0.26438 | 116.3266 |  | 147.4708 |  |  | 333.9338 | 1.1532 | 2 | 0.091909 | 40.44 |  | 0.01251 | 5.5042 |  | 32.3455 |  | 78.2898 | 135.7768 | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | 0 | 0 | 0 | 0 |  | #N/A | #N/A |  | #N/A | #N/A | 0 | #N/A | 38 | 0 | 0 | 38 | 0 | 0 |  | 0 | 38 | 0 | 0 | 38 | 0 | 0 |  | 0 | 38 | 0 | 0 | 38 | 0 | 0 |  | 0 | 38 | 0 | 0 | 38 | 0 | 0 |  | 0 | 38 | 0 | 0 | 38 | 0 | 0 |  | 0 | 38 | 0 | 0 | 38 | 0 | 0 |  | 0
Conference/Meeting/Multipurpose | Conference/Meeting/Multipurpose527-1 |  |  |  |  | n | [17 empty] | 440 |  |  | 527-1 |  | 550 | [23 empty] | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A | #N/A | #N/A | #N/A | 39 | 0 | 0 | 39 | 0 | 0 |  | 0 | 39 | 0 | 0 | 39 | 0 | 0 |  | 0 | 39 | 0 | 0 | 39 | 0 | 0 |  | 0 | 39 | 0 | 0 | 39 | 0 | 0 |  | 0 | 39 | 0 | 0 | 39 | 0 | 0 |  | 0 | 39 | 0 | 0 | 39 | 0 | 0 |  | 0
Conference/Meeting/Multipurpose535 | Conference/Meeting/Multipurpose535 |  |  |  |  | n | [13 empty] | ballast replacement |  | 535 |  | 440 |  |  | 535 |  | 550 | [11 empty] | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  | #N/A | #N/A | [10 empty] | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A | #N/A | #N/A | 0 | 40 | 0 | 0 | 40 | 0 | 0 |  | 0 | 40 | 0 | 0 | 40 | 0 | 0 |  | 0 | 40 | 0 | 0 | 40 | 0 | 0 |  | 0 | 40 | 0 | 0 | 40 | 0 | 0 |  | 0 | 40 | 0 | 0 | 40 | 0 | 0 |  | 0 | 40 | 0 | 0 | 40 | 0 | 0 |  | 0
Conference/Meeting/Multipurpose537-1 | Conference/Meeting/Multipurpose511 |  |  |  |  | n | [15 empty] | 537-1 |  | 440 |  |  | 511 |  | 550 | [11 empty] | 13.7287 | 14 | 0.39108 | 172.0736 |  | 0.80171 | 352.7508 |  | 496.7405 |  | 1021.5648 | 1041.7509 | [10 empty] | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A | #N/A | #N/A | 0 | Residual Year 30 |  | 0 | Residual Year 30 |  | 0 |  | 0 | Residual Year 30 |  | 0 | Residual Year 30 |  | 0 |  | 0 | Residual Year 30 |  | 0 | Residual Year 30 |  | 0 |  | 0 | Residual Year 30 |  | 0 | Residual Year 30 |  | 0 |  | 0 | Residual Year 30 |  | 0 | Residual Year 30 |  | 0 |  | 0 | Residual Year 30 |  | 0 | Residual Year 30 |  | 0 |  | 0
Conference/Meeting/Multipurpose511 | Conference/Meeting/Multipurpose0 |  |  |  |  | n | [15 empty] | 511 |  | 440 |  |  | 0 |  | 550 | [11 empty] | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | [10 empty] | #N/A | #N/A | 0 | 0 |  | 0 | 0 |  | 0 | 0 | #N/A | 0 | Residual Year 40 |  | 0 | Residual Year 40 |  | 0 |  | 0 | Residual Year 40 |  | 0 | Residual Year 40 |  | 0 |  | 0 | Residual Year 40 |  | 0 | Residual Year 40 |  | 0 |  | 0 | Residual Year 40 |  | 0 | Residual Year 40 |  | 0 |  | 0 | Residual Year 40 |  | 0 | Residual Year 40 |  | 0 |  | 0 | Residual Year 40 |  | 0 | Residual Year 40 |  | 0 |  | 0
Conference/Meeting/Multipurpose | Conference/Meeting/Multipurpose527-1 |  |  |  |  | n | [17 empty] | 440 |  |  | 527-1 |  | 550 | [33 empty] | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A | #N/A | #N/A | 0
Storage | Storage |  |  |  |  | n | [13 empty] | Storage | 0.8 |  |  | 770 | Storage | 0.61425 |  |  | 770
Storage530 | Storage538 |  |  |  |  | n | [13 empty] | replacement costs are for lamps |  | 530 |  | 770 |  |  | 538 |  | 770 |  | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A | #N/A | #N/A | #N/A
Storage553 | Storage0 |  |  |  |  | n | [15 empty] | 0 |  | 770 |  |  | 0 |  | 770 |  | 0 | 0 |  | 0 | 0 |  | 0 |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | 0 | 0 | 0 | 0 |  | #N/A | #N/A |  | #N/A | #N/A | 0 | #N/A
Storage0 | Storage0 |  |  |  |  | n | [15 empty] | 0 |  | 770 |  |  | 0 |  | 770 |  | 0 | 0 |  | 0 | 0 |  | 0 |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | 0 | 0 | 0 | 0 |  | #N/A | #N/A |  | #N/A | #N/A | 0 | #N/A
Storage | Storage0 |  |  |  |  | n | [20 empty] | 0 |  | 770 | [23 empty] | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | 0 | 0 | 0 | 0 |  | #N/A | #N/A |  | #N/A | #N/A | 0 | #N/A
Storage530 | Storage538 |  |  |  |  | n | [13 empty] | ballast replacement |  | 530 |  | 770 |  |  | 538 |  | 770 | [11 empty] | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  | #N/A | #N/A | [10 empty] | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A | #N/A | #N/A | 0
Storage553 | Storage0 |  |  |  |  | n | [15 empty] | 0 |  | 770 |  |  | 0 |  | 770 | [11 empty] | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | [10 empty] | #N/A | #N/A | 0 | 0 |  | 0 | 0 |  | 0 | 0 | #N/A | 0
Storage0 | Storage0 |  |  |  |  | n | [15 empty] | 0 |  | 770 |  |  | 0 |  | 770 | [11 empty] | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | [10 empty] | #N/A | #N/A | 0 | 0 |  | 0 | 0 |  | 0 | 0 | #N/A | 0
Storage | Storage0 |  |  |  |  | n | [20 empty] | 0 |  | 770 | [33 empty] | #N/A | #N/A | 0 | 0 |  | 0 | 0 |  | 0 | 0 | #N/A | 0
Restrooms | Restrooms |  |  |  |  | n | [13 empty] | Restrooms | 0.9 |  |  | 220 | Restrooms | 0.9555 |  |  | 220
Restrooms521 | Restrooms604 |  |  |  |  | n | [13 empty] | replacement costs are for lamps |  | 521 |  | 220 |  |  | 604 |  | 220 |  | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A | #N/A | #N/A | #N/A
Restrooms537-1 | Restrooms520 |  |  |  |  | n | [15 empty] | 537-1 |  | 220 |  |  | 520 |  | 220 |  | 1.2172 | 267.7936 |  | 0.7228 | 159.0162 |  | 287.7712 |  |  | 714.581 | 9.8847 | 10 | 0.039372 | 8.6619 |  | 0.06425 | 14.1349 |  | 21.0556 |  | 43.8524 | 44.364 | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A | #N/A | #N/A | #N/A
Restrooms524 | Restrooms0 |  |  |  |  | n | [15 empty] | 524 |  | 220 |  |  | 0 |  | 220 |  | 0.3093 | 68.0465 |  | 0.21213 | 46.6696 |  | 79.1701 |  |  | 193.8862 | 2.7457 | 3 | 0.10831 | 23.828 |  | 0.020006 | 4.4014 |  | 20.3215 |  | 48.5509 | 53.0467 | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | 0 | 0 | 0 | 0 |  | #N/A | #N/A |  | #N/A | #N/A | 0 | #N/A
Restrooms | Restrooms534-2 |  |  |  |  | n | [20 empty] | 534-2 |  | 220 | [23 empty] | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A | #N/A | #N/A | #N/A
Restrooms521 | Restrooms604 |  |  |  |  | n | [13 empty] | ballast replacement |  | 521 |  | 220 |  |  | 604 |  | 220 | [11 empty] | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  | #N/A | #N/A | [10 empty] | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A | #N/A | #N/A | 0
Restrooms537-1 | Restrooms520 |  |  |  |  | n | [15 empty] | 537-1 |  | 220 |  |  | 520 |  | 220 | [11 empty] | 13.7287 | 14 | 0.35259 | 77.5689 |  | 0.7228 | 159.0162 |  | 223.9251 |  | 460.5102 | 469.6099 | [10 empty] | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A | #N/A | #N/A | 0
Restrooms524 | Restrooms0 |  |  |  |  | n | [15 empty] | 524 |  | 220 |  |  | 0 |  | 220 | [11 empty] | 13.7287 | 14 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | [10 empty] | #N/A | #N/A | 0 | 0 |  | 0 | 0 |  | 0 | 0 | #N/A | 0
Restrooms | Restrooms534-2 |  |  |  |  | n | [20 empty] | 534-2 |  | 220 | [33 empty] | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A | #N/A | #N/A | 0
Lounge/Recreation - Break room | Lounge/Recreation - Break room |  |  |  |  | n | [13 empty] | Lounge/Recreation - Break room | 1.2 |  |  | 110 | Lounge/Recreation - Break room | 0.71175 |  |  | 110
Lounge/Recreation - Breakroom537-1 | Lounge/Recreation - Breakroom521 |  |  |  |  | n | [13 empty] | replacement costs are for lamps |  | 537-1 |  | 110 |  |  | 521 |  | 110 |  | 1.3506 | 148.5678 |  | 0.802 | 88.2197 |  | 159.6511 |  |  | 396.4386 | 9.8847 | 10 | 0.043686 | 4.8055 |  | 0.07129 | 7.8419 |  | 11.6813 |  | 24.3286 | 24.6125 | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A | #N/A | #N/A | #N/A
Lounge/Recreation - Breakroom572 | Lounge/Recreation - Breakroom0 |  |  |  |  | n | [15 empty] | 0 |  | 110 |  |  | 0 |  | 110 |  | 0 | 0 |  | 0 | 0 |  | 0 |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | 0 | 0 | 0 | 0 |  | #N/A | #N/A |  | #N/A | #N/A | 0 | #N/A
Lounge/Recreation - Breakroom521 | Lounge/Recreation - Breakroom0 |  |  |  |  | n | [15 empty] | 521 |  | 110 |  |  | 0 |  | 110 |  | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | 0 | 0 | 0 | 0 |  | #N/A | #N/A |  | #N/A | #N/A | 0 | #N/A
Lounge/Recreation - Break room | Lounge/Recreation - Breakroom527-2 |  |  |  |  | n | [17 empty] | 110 |  |  | 527-2 |  | 110 | [23 empty] | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A | #N/A | #N/A | #N/A
Lounge/Recreation - Breakroom537-1 | Lounge/Recreation - Breakroom521 |  |  |  |  | n | [13 empty] | ballast replacement |  | 537-1 |  | 110 |  |  | 521 |  | 110 | [11 empty] | 13.7287 | 14 | 0.39122 | 43.034 |  | 0.802 | 88.2197 |  | 124.2302 |  | 255.484 | 260.5324 | [10 empty] | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A | #N/A | #N/A | 0
Lounge/Recreation - Breakroom572 | Lounge/Recreation - Breakroom0 |  |  |  |  | n | [15 empty] | 0 |  | 110 |  |  | 0 |  | 110 | [11 empty] | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | [10 empty] | #N/A | #N/A | 0 | 0 |  | 0 | 0 |  | 0 | 0 | #N/A | 0
Lounge/Recreation - Breakroom521 | Lounge/Recreation - Breakroom0 |  |  |  |  | n | [15 empty] | 521 |  | 110 |  |  | 0 |  | 110 | [11 empty] | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  | #N/A | #N/A | [10 empty] | #N/A | #N/A | 0 | 0 |  | 0 | 0 |  | 0 | 0 | #N/A | 0
Lounge/Recreation - Break room | Lounge/Recreation - Breakroom527-2 |  |  |  |  | n | [17 empty] | 110 |  |  | 527-2 |  | 110 | [33 empty] | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A | #N/A | #N/A | 0
Electrical/Mechanical | Electrical/Mechanical |  |  |  |  | n | [13 empty] | Electrical/Mechanical | 1.5 |  |  | 110 | Electrical/Mechanical | 0.92625 |  |  | 110
Electrical/Mechanical538 | Electrical/Mechanical538 |  |  |  |  | n | [13 empty] | replacement costs are for lamps |  | 538 |  | 110 |  |  | 538 |  | 110 |  | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A | #N/A | #N/A | #N/A
Electrical/Mechanical0 | Electrical/Mechanical0 |  |  |  |  | n | [15 empty] | 0 |  | 110 |  |  | 0 |  | 110 |  | 0 | 0 |  | 0 | 0 |  | 0 |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | 0 | 0 | 0 | 0 |  | #N/A | #N/A |  | #N/A | #N/A | 0 | #N/A
Electrical/Mechanical0 | Electrical/Mechanical0 |  |  |  |  | n | [15 empty] | 0 |  | 110 |  |  | 0 |  | 110 |  | 0 | 0 |  | 0 | 0 |  | 0 |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | 0 | 0 | 0 | 0 |  | #N/A | #N/A |  | #N/A | #N/A | 0 | #N/A
Electrical/Mechanical | Electrical/Mechanical0 |  |  |  |  | n | [17 empty] | 110 |  |  | 0 |  | 110 | [23 empty] | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | 0 | 0 | 0 | 0 |  | #N/A | #N/A |  | #N/A | #N/A | 0 | #N/A
Electrical/Mechanical538 | Electrical/Mechanical538 |  |  |  |  | n | [13 empty] | ballast replacement |  | 538 |  | 110 |  |  | 538 |  | 110 | [11 empty] | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  | #N/A | #N/A | [10 empty] | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A | #N/A | #N/A | 0
Electrical/Mechanical0 | Electrical/Mechanical0 |  |  |  |  | n | [15 empty] | 0 |  | 110 |  |  | 0 |  | 110 | [11 empty] | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | [10 empty] | #N/A | #N/A | 0 | 0 |  | 0 | 0 |  | 0 | 0 | #N/A | 0
Electrical/Mechanical0 | Electrical/Mechanical0 |  |  |  |  | n | [15 empty] | 0 |  | 110 |  |  | 0 |  | 110 | [11 empty] | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | [10 empty] | #N/A | #N/A | 0 | 0 |  | 0 | 0 |  | 0 | 0 | #N/A | 0
Electrical/Mechanical | Electrical/Mechanical0 |  |  |  |  | n | [17 empty] | 110 |  |  | 0 |  | 110 | [33 empty] | #N/A | #N/A | 0 | 0 |  | 0 | 0 |  | 0 | 0 | #N/A | 0
Stairway | Stairway |  |  |  |  | n | [13 empty] | Stairway | 0.6 |  |  | 165 | Stairway | 0.67275 |  |  | 165
Stairway530 | Stairway530 |  |  |  |  | n | [13 empty] | replacement costs are for lamps |  | 530 |  | 165 |  |  | 530 |  | 165 |  | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A | #N/A | #N/A | #N/A
Stairway0 | Stairway602 |  |  |  |  | n | [15 empty] | 0 |  | 165 |  |  | 602 |  | 165 |  | 0 | 0 |  | 0 | 0 |  | 0 |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A | #N/A | #N/A | #N/A
Stairway0 | Stairway0 |  |  |  |  | n | [15 empty] | 0 |  | 165 |  |  | 0 |  | 165 |  | 0 | 0 |  | 0 | 0 |  | 0 |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | 0 | 0 | 0 | 0 |  | #N/A | #N/A |  | #N/A | #N/A | 0 | #N/A
Stairway | Stairway0 |  |  |  |  | n | [17 empty] | 165 |  |  | 0 |  | 165 | [23 empty] | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | 0 | 0 | 0 | 0 |  | #N/A | #N/A |  | #N/A | #N/A | 0 | #N/A
Stairway530 | Stairway530 |  |  |  |  | n | [13 empty] | ballast replacement |  | 530 |  | 165 |  |  | 530 |  | 165 | [11 empty] | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  | #N/A | #N/A | [10 empty] | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A | #N/A | #N/A | 0
Stairway0 | Stairway602 |  |  |  |  | n | [15 empty] | 0 |  | 165 |  |  | 602 |  | 165 | [11 empty] | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | [10 empty] | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A | #N/A | #N/A | 0
Stairway0 | Stairway0 |  |  |  |  | n | [15 empty] | 0 |  | 165 |  |  | 0 |  | 165 | [11 empty] | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | [10 empty] | #N/A | #N/A | 0 | 0 |  | 0 | 0 |  | 0 | 0 | #N/A | 0
Stairway | Stairway0 |  |  |  |  | n | [17 empty] | 165 |  |  | 0 |  | 165 | [33 empty] | #N/A | #N/A | 0 | 0 |  | 0 | 0 |  | 0 | 0 | #N/A | 0
Lobby | Lobby |  |  |  |  | n | [13 empty] | Lobby | 1.3 |  |  | 330 | Lobby | 0.8775 |  |  | 330
Lobby534-2 | Lobby523 |  |  |  |  | n | [13 empty] | replacement costs are for lamps |  | 534-2 |  | 330 |  |  | 523 |  | 330 |  | 3.4171 | 1127.6332 |  | 0.5204 | 171.7311 |  | 731.0787 |  |  | 2030.4431 | 9.8847 | 10 | 0.030124 | 9.941 |  | 0.049158 | 16.2223 |  | 24.165 |  | 50.3282 | 50.9154 | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A | #N/A | #N/A | #N/A
Lobby523 | Lobby521 |  |  |  |  | n | [15 empty] | 523 |  | 330 |  |  | 521 |  | 330 |  | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A | #N/A | #N/A | #N/A
Lobby521 | Lobby0 |  |  |  |  | n | [15 empty] | 521 |  | 330 |  |  | 0 |  | 330 |  | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | 0 | 0 | 0 | 0 |  | #N/A | #N/A |  | #N/A | #N/A | 0 | #N/A
Lobby | Lobby534-2 |  |  |  |  | n | [17 empty] | 330 |  |  | 534-2 |  | 330 | [23 empty] | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A | #N/A | #N/A | #N/A
Lobby534-2 | Lobby523 |  |  |  |  | n | [13 empty] | ballast replacement |  | 534-2 |  | 330 |  |  | 523 |  | 330 | [11 empty] | 13.7287 | 14 | 0.26977 | 89.0237 |  | 0.55303 | 182.4985 |  | 256.9928 |  | 528.515 | 538.9584 | [10 empty] | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A | #N/A | #N/A | 0
Lobby523 | Lobby521 |  |  |  |  | n | [15 empty] | 523 |  | 330 |  |  | 521 |  | 330 | [11 empty] | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  | #N/A | #N/A | [10 empty] | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A | #N/A | #N/A | 0
Lobby521 | Lobby0 |  |  |  |  | n | [15 empty] | 521 |  | 330 |  |  | 0 |  | 330 | [11 empty] | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  | #N/A | #N/A | [10 empty] | #N/A | #N/A | 0 | 0 |  | 0 | 0 |  | 0 | 0 | #N/A | 0
Lobby | Lobby534-2 |  |  |  |  | n | [20 empty] | 534-2 |  | 330 | [33 empty] | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A | #N/A | #N/A | 0
n
[18 empty] | Large_Office_Interior Lighting LPD |  | Large Office |  |  | 2938 |  | Large Office |  |  | 2938
Office - Open Plan (Including Other) | Office - Open Plan (Including Other) | [18 empty] | Office - Open Plan (Including Other) | 1.1 |  |  | 285144 | Office - Open Plan (Including Other) | 0.97216 |  |  | 285144 | [27 empty] | 0
Office - Open Plan (Including Other)535 | Office - Open Plan (Including Other)535 | [5 empty] | n | [12 empty] | replacement costs are for lamps |  | 535 |  | 285144 |  |  | 535 |  | 285144 |  | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A | #N/A | #N/A | #N/A
Office - Open Plan (Including Other)539 | Office - Open Plan (Including Other)539 | [5 empty] | n | [14 empty] | 539 |  | 285144 |  |  | 539 |  | 285144 |  | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A | #N/A | #N/A | #N/A
Office - Open Plan (Including Other)524 | Office - Open Plan (Including Other)0 | [5 empty] | n | [14 empty] | 524 |  | 285144 |  |  | 0 |  | 285144 |  | 0.14484 | 41299.1443 |  | 0.099336 | 28324.94 |  | 48050.3534 |  |  | 117674.4377 | 2.7457 | 3 | 0.050718 | 14461.8393 |  | 0.0093682 | 2671.2952 |  | 12333.6058 |  | 29466.7402 | 32195.3604 | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | 0 | 0 | 0 | 0 |  | #N/A | #N/A |  | #N/A | #N/A | 0 | #N/A
Office - Open Plan (Including Other) | Office - Open Plan (Including Other)537-1 | [5 empty] | n | [19 empty] | 537-1 |  | 285144 | [23 empty] | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A | #N/A | #N/A | #N/A
Office - Open Plan (Including Other)535 | Office - Open Plan (Including Other)535 | [5 empty] | n | [12 empty] | ballast replacement |  | 535 |  | 285144 |  |  | 535 |  | 285144 | [11 empty] | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  | #N/A | #N/A | [10 empty] | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A | #N/A | #N/A | 0
Office - Open Plan (Including Other)539 | Office - Open Plan (Including Other)539 | [5 empty] | n | [14 empty] | 539 |  | 285144 |  |  | 539 |  | 285144 | [11 empty] | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  | #N/A | #N/A | [10 empty] | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A | #N/A | #N/A | 0
Office - Open Plan (Including Other)524 | Office - Open Plan (Including Other)0 | [5 empty] | n | [14 empty] | 524 |  | 285144 |  |  | 0 |  | 285144 | [11 empty] | 13.7287 | 14 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | [10 empty] | #N/A | #N/A | 0 | 0 |  | 0 | 0 |  | 0 | 0 | #N/A | 0
Office - Open Plan (Including Other) | Office - Open Plan (Including Other)537-1 | [5 empty] | n | [19 empty] | 537-1 |  | 285144 | [33 empty] | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A | #N/A | #N/A | 0
Office-Enclosed | Office-Enclosed | [5 empty] | n | [12 empty] | Office-Enclosed | 1.1 |  |  | 92363 | Office-Enclosed | 1.1011 |  |  | 92363 | [27 empty] | 0
Office-Enclosed535 | Office-Enclosed531 | [5 empty] | n | [12 empty] | replacement costs are for lamps |  | 535 |  | 92363 |  |  | 531 |  | 92363 |  | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A | #N/A | #N/A | #N/A
Office-Enclosed539 | Office-Enclosed539 | [5 empty] | n | [14 empty] | 539 |  | 92363 |  |  | 539 |  | 92363 |  | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A | #N/A | #N/A | #N/A
Office-Enclosed537-2 | Office-Enclosed0 | [5 empty] | n | [14 empty] | 537-2 |  | 92363 |  |  | 0 |  | 92363 |  | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | 0 | 0 | 0 | 0 |  | #N/A | #N/A |  | #N/A | #N/A | 0 | #N/A
Office-Enclosed | Office-Enclosed537-1 | [5 empty] | n | [19 empty] | 537-1 |  | 92363 | [23 empty] | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A | #N/A | #N/A | #N/A
Office-Enclosed535 | Office-Enclosed531 | [5 empty] | n | [12 empty] | ballast replacement |  | 535 |  | 92363 |  |  | 531 |  | 92363 | [11 empty] | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  | #N/A | #N/A | [10 empty] | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A | #N/A | #N/A | 0
Office-Enclosed539 | Office-Enclosed539 | [5 empty] | n | [14 empty] | 539 |  | 92363 |  |  | 539 |  | 92363 | [11 empty] | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  | #N/A | #N/A | [10 empty] | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A | #N/A | #N/A | 0
Office-Enclosed537-2 | Office-Enclosed0 | [5 empty] | n | [14 empty] | 537-2 |  | 92363 |  |  | 0 |  | 92363 | [11 empty] | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  | #N/A | #N/A | [10 empty] | #N/A | #N/A | 0 | 0 |  | 0 | 0 |  | 0 | 0 | #N/A | 0
Office-Enclosed | Office-Enclosed537-1 | [5 empty] | n | [19 empty] | 537-1 |  | 92363 | [33 empty] | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A | #N/A | #N/A | 0
Conference/Meeting/Multipurpose | Conference/Meeting/Multipurpose | [5 empty] | n | [12 empty] | Conference/Meeting/Multipurpose | 1.3 |  |  | 9628 | Conference/Meeting/Multipurpose | 1.2202 |  |  | 9628
Conference/Meeting/Multipurpose535 | Conference/Meeting/Multipurpose535 | [5 empty] | n | [12 empty] | replacement costs are for lamps |  | 535 |  | 9628 |  |  | 535 |  | 9628 |  | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A | #N/A | #N/A | #N/A
Conference/Meeting/Multipurpose537-1 | Conference/Meeting/Multipurpose511 | [5 empty] | n | [14 empty] | 537-1 |  | 9628 |  |  | 511 |  | 9628 |  | 1.3501 | 12999.0098 |  | 0.80171 | 7718.8288 |  | 13968.7467 |  |  | 34686.5853 | 9.8847 | 10 | 0.04367 | 420.4565 |  | 0.071264 | 686.1267 |  | 1022.0637 |  | 2128.6469 | 2153.4811 | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A | #N/A | #N/A | #N/A
Conference/Meeting/Multipurpose511 | Conference/Meeting/Multipurpose0 | [5 empty] | n | [14 empty] | 511 |  | 9628 |  |  | 0 |  | 9628 |  | 0.1594 | 1534.7125 |  | 0.26438 | 2545.4373 |  | 3226.9295 |  |  | 7307.0793 | 1.1532 | 2 | 0.091909 | 884.9016 |  | 0.01251 | 120.4426 |  | 707.778 |  | 1713.1223 | 2971.0435 | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | 0 | 0 | 0 | 0 |  | #N/A | #N/A |  | #N/A | #N/A | 0 | #N/A
Conference/Meeting/Multipurpose | Conference/Meeting/Multipurpose527-1 | [5 empty] | n | [19 empty] | 527-1 |  | 9628 | [23 empty] | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A | #N/A | #N/A | #N/A
Conference/Meeting/Multipurpose535 | Conference/Meeting/Multipurpose535 | [5 empty] | n | [12 empty] | ballast replacement |  | 535 |  | 9628 |  |  | 535 |  | 9628 | [11 empty] | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  | #N/A | #N/A | [10 empty] | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A | #N/A | #N/A | 0
Conference/Meeting/Multipurpose537-1 | Conference/Meeting/Multipurpose511 | [5 empty] | n | [14 empty] | 537-1 |  | 9628 |  |  | 511 |  | 9628 | [11 empty] | 13.7287 | 14 | 0.39108 | 3765.2824 |  | 0.80171 | 7718.8288 |  | 10869.5843 |  | 22353.6955 | 22795.4045 | [10 empty] | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A | #N/A | #N/A | 0
Conference/Meeting/Multipurpose511 | Conference/Meeting/Multipurpose0 | [5 empty] | n | [14 empty] | 511 |  | 9628 |  |  | 0 |  | 9628 | [11 empty] | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | [10 empty] | #N/A | #N/A | 0 | 0 |  | 0 | 0 |  | 0 | 0 | #N/A | 0
Conference/Meeting/Multipurpose | Conference/Meeting/Multipurpose527-1 | [5 empty] | n | [19 empty] | 527-1 |  | 9628 | [33 empty] | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A | #N/A | #N/A | 0
Corridor/Transition | Corridor/Transition | [5 empty] | n | [12 empty] | Corridor/Transition | 0.5 |  |  | 21304 | Corridor/Transition | 0.65472 |  |  | 21304
Corridor/Transition530 | Corridor/Transition521 | [5 empty] | n | [12 empty] | replacement costs are for lamps |  | 530 |  | 21304 |  |  | 521 |  | 21304 |  | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A | #N/A | #N/A | #N/A
Corridor/Transition537-2 | Corridor/Transition0 | [5 empty] | n | [14 empty] | 537-2 |  | 21304 |  |  | 0 |  | 21304 |  | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | 0 | 0 | 0 | 0 |  | #N/A | #N/A |  | #N/A | #N/A | 0 | #N/A
Corridor/Transition0 | Corridor/Transition0 | [5 empty] | n | [14 empty] | 0 |  | 21304 |  |  | 0 |  | 21304 |  | 0 | 0 |  | 0 | 0 |  | 0 |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | 0 | 0 | 0 | 0 |  | #N/A | #N/A |  | #N/A | #N/A | 0 | #N/A
Corridor/Transition | Corridor/Transition527-2 | [5 empty] | n | [19 empty] | 0 |  | 21304 | [23 empty] | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | 0 | 0 | 0 | 0 |  | #N/A | #N/A |  | #N/A | #N/A | 0 | #N/A
Corridor/Transition530 | Corridor/Transition521 | [5 empty] | n | [12 empty] | ballast replacement |  | 530 |  | 21304 |  |  | 521 |  | 21304 | [11 empty] | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  | #N/A | #N/A | [10 empty] | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A | #N/A | #N/A | 0
Corridor/Transition537-2 | Corridor/Transition0 | [5 empty] | n | [14 empty] | 537-2 |  | 21304 |  |  | 0 |  | 21304 | [11 empty] | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  | #N/A | #N/A | [10 empty] | #N/A | #N/A | 0 | 0 |  | 0 | 0 |  | 0 | 0 | #N/A | 0
Corridor/Transition0 | Corridor/Transition0 | [5 empty] | n | [14 empty] | 0 |  | 21304 |  |  | 0 |  | 21304 | [11 empty] | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | [10 empty] | #N/A | #N/A | 0 | 0 |  | 0 | 0 |  | 0 | 0 | #N/A | 0
Corridor/Transition | Corridor/Transition527-2 | [5 empty] | n | [19 empty] | 0 |  | 21304 | [33 empty] | #N/A | #N/A | 0 | 0 |  | 0 | 0 |  | 0 | 0 | #N/A | 0
Storage | Storage | [5 empty] | n | [12 empty] | Storage | 0.8 |  |  | 11866 | Storage | 0.62496 |  |  | 11866
Storage530 | Storage538 | [5 empty] | n | [12 empty] | replacement costs are for lamps |  | 530 |  | 11866 |  |  | 538 |  | 11866 |  | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A | #N/A | #N/A | #N/A
Storage553 | Storage0 | [5 empty] | n | [14 empty] | 0 |  | 11866 |  |  | 0 |  | 11866 |  | 0 | 0 |  | 0 | 0 |  | 0 |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | 0 | 0 | 0 | 0 |  | #N/A | #N/A |  | #N/A | #N/A | 0 | #N/A
Storage0 | Storage0 | [5 empty] | n | [14 empty] | 0 |  | 11866 |  |  | 0 |  | 11866 |  | 0 | 0 |  | 0 | 0 |  | 0 |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | 0 | 0 | 0 | 0 |  | #N/A | #N/A |  | #N/A | #N/A | 0 | #N/A
Storage | Storage0 | [5 empty] | n | [19 empty] | 0 |  | 11866 | [23 empty] | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | 0 | 0 | 0 | 0 |  | #N/A | #N/A |  | #N/A | #N/A | 0 | #N/A
Storage530 | Storage538 | [5 empty] | n | [12 empty] | ballast replacement |  | 530 |  | 11866 |  |  | 538 |  | 11866 | [11 empty] | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  | #N/A | #N/A | [10 empty] | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A | #N/A | #N/A | 0
Storage553 | Storage0 | [5 empty] | n | [14 empty] | 0 |  | 11866 |  |  | 0 |  | 11866 | [11 empty] | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | [10 empty] | #N/A | #N/A | 0 | 0 |  | 0 | 0 |  | 0 | 0 | #N/A | 0
Storage0 | Storage0 | [5 empty] | n | [14 empty] | 0 |  | 11866 |  |  | 0 |  | 11866 | [11 empty] | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | [10 empty] | #N/A | #N/A | 0 | 0 |  | 0 | 0 |  | 0 | 0 | #N/A | 0
Storage | Storage0 | [5 empty] | n | [19 empty] | 0 |  | 11866 | [33 empty] | #N/A | #N/A | 0 | 0 |  | 0 | 0 |  | 0 | 0 | #N/A | 0
Restrooms | Restrooms | [5 empty] | n | [12 empty] | Restrooms | 0.9 |  |  | 15505 | Restrooms | 0.97216 |  |  | 15505
Restrooms521 | Restrooms604 | [5 empty] | n | [12 empty] | replacement costs are for lamps |  | 521 |  | 15505 |  |  | 604 |  | 15505 |  | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A | #N/A | #N/A | #N/A
Restrooms537-1 | Restrooms520 | [5 empty] | n | [14 empty] | 537-1 |  | 15505 |  |  | 520 |  | 15505 |  | 1.2172 | 18873.3619 |  | 0.7228 | 11207.0267 |  | 20281.3302 |  |  | 50361.7188 | 9.8847 | 10 | 0.039372 | 610.4641 |  | 0.06425 | 996.1926 |  | 1483.9421 |  | 3090.5987 | 3126.6557 | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A | #N/A | #N/A | #N/A
Restrooms524 | Restrooms0 | [5 empty] | n | [14 empty] | 524 |  | 15505 |  |  | 0 |  | 15505 |  | 0.3093 | 4795.7329 |  | 0.21213 | 3289.1444 |  | 5579.6958 |  |  | 13664.5731 | 2.7457 | 3 | 0.10831 | 1679.3355 |  | 0.020006 | 310.1957 |  | 1432.2011 |  | 3421.7323 | 3738.5847 | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | 0 | 0 | 0 | 0 |  | #N/A | #N/A |  | #N/A | #N/A | 0 | #N/A
Restrooms | Restrooms534-2 | [5 empty] | n | [19 empty] | 534-2 |  | 15505 | [23 empty] | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A | #N/A | #N/A | #N/A
Restrooms521 | Restrooms604 | [5 empty] | n | [12 empty] | ballast replacement |  | 521 |  | 15505 |  |  | 604 |  | 15505 | [11 empty] | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  | #N/A | #N/A | [10 empty] | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A | #N/A | #N/A | 0
Restrooms537-1 | Restrooms520 | [5 empty] | n | [14 empty] | 537-1 |  | 15505 |  |  | 520 |  | 15505 | [11 empty] | 13.7287 | 14 | 0.35259 | 5466.8423 |  | 0.7228 | 11207.0267 |  | 15781.6327 |  | 32455.5017 | 33096.8224 | [10 empty] | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A | #N/A | #N/A | 0
Restrooms524 | Restrooms0 | [5 empty] | n | [14 empty] | 524 |  | 15505 |  |  | 0 |  | 15505 | [11 empty] | 13.7287 | 14 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | [10 empty] | #N/A | #N/A | 0 | 0 |  | 0 | 0 |  | 0 | 0 | #N/A | 0
Restrooms | Restrooms534-2 | [5 empty] | n | [19 empty] | 534-2 |  | 15505 | [33 empty] | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A | #N/A | #N/A | 0
Lounge/Recreation - Break room | Lounge/Recreation - Break room | [5 empty] | n | [12 empty] | Lounge/Recreation - Break room | 1.2 |  |  | 9530 | Lounge/Recreation - Break room | 0.72416 |  |  | 9530
Lounge/Recreation - Breakroom537-1 | Lounge/Recreation - Breakroom521 | [5 empty] | n | [12 empty] | replacement costs are for lamps |  | 537-1 |  | 9530 |  |  | 521 |  | 9530 |  | 1.3506 | 12871.3726 |  | 0.802 | 7643.0377 |  | 13831.5876 |  |  | 34345.9979 | 9.8847 | 10 | 0.043686 | 416.3281 |  | 0.07129 | 679.3896 |  | 1012.028 |  | 2107.7457 | 2132.3361 | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A | #N/A | #N/A | #N/A
Lounge/Recreation - Breakroom572 | Lounge/Recreation - Breakroom0 | [5 empty] | n | [14 empty] | 0 |  | 9530 |  |  | 0 |  | 9530 |  | 0 | 0 |  | 0 | 0 |  | 0 |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | 0 | 0 | 0 | 0 |  | #N/A | #N/A |  | #N/A | #N/A | 0 | #N/A
Lounge/Recreation - Breakroom521 | Lounge/Recreation - Breakroom0 | [5 empty] | n | [14 empty] | 521 |  | 9530 |  |  | 0 |  | 9530 |  | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | 0 | 0 | 0 | 0 |  | #N/A | #N/A |  | #N/A | #N/A | 0 | #N/A
Lounge/Recreation - Breakroom | Lounge/Recreation - Breakroom527-2 | [5 empty] | n | [19 empty] | 527-2 |  | 9530 | [23 empty] | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A | #N/A | #N/A | #N/A
Lounge/Recreation - Breakroom537-1 | Lounge/Recreation - Breakroom521 | [5 empty] | n | [12 empty] | ballast replacement |  | 537-1 |  | 9530 |  |  | 521 |  | 9530 | [11 empty] | 13.7287 | 14 | 0.39122 | 3728.3111 |  | 0.802 | 7643.0377 |  | 10762.8559 |  | 22134.2047 | 22571.5766 | [10 empty] | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A | #N/A | #N/A | 0
Lounge/Recreation - Breakroom572 | Lounge/Recreation - Breakroom0 | [5 empty] | n | [14 empty] | 0 |  | 9530 |  |  | 0 |  | 9530 | [11 empty] | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | [10 empty] | #N/A | #N/A | 0 | 0 |  | 0 | 0 |  | 0 | 0 | #N/A | 0
Lounge/Recreation - Breakroom521 | Lounge/Recreation - Breakroom0 | [5 empty] | n | [14 empty] | 521 |  | 9530 |  |  | 0 |  | 9530 | [11 empty] | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  | #N/A | #N/A | [10 empty] | #N/A | #N/A | 0 | 0 |  | 0 | 0 |  | 0 | 0 | #N/A | 0
Lounge/Recreation - Breakroom | Lounge/Recreation - Breakroom527-2 | [5 empty] | n | [19 empty] | 527-2 |  | 9530 | [33 empty] | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A | #N/A | #N/A | 0
Electrical/Mechanical | Electrical/Mechanical | [5 empty] | n | [12 empty] | Electrical/Mechanical | 1.5 |  |  | 31023 | Electrical/Mechanical | 0.9424 |  |  | 31023
Electrical/Mechanical538 | Electrical/Mechanical538 | [5 empty] | n | [12 empty] | replacement costs are for lamps |  | 538 |  | 31023 |  |  | 538 |  | 31023 |  | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A | #N/A | #N/A | #N/A
Electrical/Mechanical0 | Electrical/Mechanical0 | [5 empty] | n | [14 empty] | 0 |  | 31023 |  |  | 0 |  | 31023 |  | 0 | 0 |  | 0 | 0 |  | 0 |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | 0 | 0 | 0 | 0 |  | #N/A | #N/A |  | #N/A | #N/A | 0 | #N/A
Electrical/Mechanical0 | Electrical/Mechanical0 | [5 empty] | n | [14 empty] | 0 |  | 31023 |  |  | 0 |  | 31023 |  | 0 | 0 |  | 0 | 0 |  | 0 |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | 0 | 0 | 0 | 0 |  | #N/A | #N/A |  | #N/A | #N/A | 0 | #N/A
Electrical/Mechanical | Electrical/Mechanical0 | [5 empty] | n | [19 empty] | 0 |  | 31023 | [23 empty] | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | 0 | 0 | 0 | 0 |  | #N/A | #N/A |  | #N/A | #N/A | 0 | #N/A
Electrical/Mechanical538 | Electrical/Mechanical538 | [5 empty] | n | [12 empty] | ballast replacement |  | 538 |  | 31023 |  |  | 538 |  | 31023 | [11 empty] | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  | #N/A | #N/A | [10 empty] | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A | #N/A | #N/A | 0
Electrical/Mechanical0 | Electrical/Mechanical0 | [5 empty] | n | [14 empty] | 0 |  | 31023 |  |  | 0 |  | 31023 | [11 empty] | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | [10 empty] | #N/A | #N/A | 0 | 0 |  | 0 | 0 |  | 0 | 0 | #N/A | 0
Electrical/Mechanical0 | Electrical/Mechanical0 | [5 empty] | n | [14 empty] | 0 |  | 31023 |  |  | 0 |  | 31023 | [11 empty] | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | [10 empty] | #N/A | #N/A | 0 | 0 |  | 0 | 0 |  | 0 | 0 | #N/A | 0
Electrical/Mechanical | Electrical/Mechanical0 | [5 empty] | n | [19 empty] | 0 |  | 31023 | [33 empty] | #N/A | #N/A | 0 | 0 |  | 0 | 0 |  | 0 | 0 | #N/A | 0
Stairway | Stairway | [5 empty] | n | [12 empty] | Stairway | 0.6 |  |  | 8484 | Stairway | 0.68448 |  |  | 8484
Stairway530 | Stairway530 | [5 empty] | n | [12 empty] | replacement costs are for lamps |  | 530 |  | 8484 |  |  | 530 |  | 8484 |  | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A | #N/A | #N/A | #N/A
Stairway0 | Stairway602 | [5 empty] | n | [14 empty] | 0 |  | 8484 |  |  | 602 |  | 8484 |  | 0 | 0 |  | 0 | 0 |  | 0 |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A | #N/A | #N/A | #N/A
Stairway0 | Stairway0 | [5 empty] | n | [14 empty] | 0 |  | 8484 |  |  | 0 |  | 8484 |  | 0 | 0 |  | 0 | 0 |  | 0 |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | 0 | 0 | 0 | 0 |  | #N/A | #N/A |  | #N/A | #N/A | 0 | #N/A
Stairway | Stairway0 | [5 empty] | n | [19 empty] | 0 |  | 8484 | [23 empty] | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | 0 | 0 | 0 | 0 |  | #N/A | #N/A |  | #N/A | #N/A | 0 | #N/A
Stairway530 | Stairway530 | [5 empty] | n | [12 empty] | ballast replacement |  | 530 |  | 8484 |  |  | 530 |  | 8484 | [11 empty] | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  | #N/A | #N/A | [10 empty] | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A | #N/A | #N/A | 0
Stairway0 | Stairway602 | [5 empty] | n | [14 empty] | 0 |  | 8484 |  |  | 602 |  | 8484 | [11 empty] | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | [10 empty] | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A | #N/A | #N/A | 0
Stairway0 | Stairway0 | [5 empty] | n | [14 empty] | 0 |  | 8484 |  |  | 0 |  | 8484 | [11 empty] | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | [10 empty] | #N/A | #N/A | 0 | 0 |  | 0 | 0 |  | 0 | 0 | #N/A | 0
Stairway | Stairway0 | [5 empty] | n | [19 empty] | 0 |  | 8484 | [33 empty] | #N/A | #N/A | 0 | 0 |  | 0 | 0 |  | 0 | 0 | #N/A | 0
Lobby | Lobby | [5 empty] | n | [12 empty] | Lobby | 1.3 |  |  | 13792 | Lobby | 0.8928 |  |  | 13792
Lobby534-2 | Lobby523 | [5 empty] | n | [12 empty] | replacement costs are for lamps |  | 534-2 |  | 13792 |  |  | 523 |  | 13792 |  | 3.4171 | 47128.2336 |  | 0.5204 | 7177.3199 |  | 30554.6604 |  |  | 84860.2139 | 9.8847 | 10 | 0.030124 | 415.4726 |  | 0.049158 | 677.9936 |  | 1009.9485 |  | 2103.4147 | 2127.9545 | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A | #N/A | #N/A | #N/A
Lobby523 | Lobby521 | [5 empty] | n | [14 empty] | 523 |  | 13792 |  |  | 521 |  | 13792 |  | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A | #N/A | #N/A | #N/A
Lobby521 | Lobby0 | [5 empty] | n | [14 empty] | 521 |  | 13792 |  |  | 0 |  | 13792 |  | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | 0 | 0 | 0 | 0 |  | #N/A | #N/A |  | #N/A | #N/A | 0 | #N/A
Lobby | Lobby534-2 | [5 empty] | n | [19 empty] | 534-2 |  | 13792 | [23 empty] | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A | #N/A | #N/A | #N/A
Lobby534-2 | Lobby523 | [5 empty] | n | [12 empty] | ballast replacement |  | 534-2 |  | 13792 |  |  | 523 |  | 13792 | [11 empty] | 13.7287 | 14 | 0.26977 | 3720.65 |  | 0.55303 | 7627.3325 |  | 10740.74 |  | 22088.7226 | 22525.1957 | [10 empty] | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A | #N/A | #N/A | 0
Lobby523 | Lobby521 | [5 empty] | n | [14 empty] | 523 |  | 13792 |  |  | 521 |  | 13792 | [11 empty] | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  | #N/A | #N/A | [10 empty] | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A | #N/A | #N/A | 0
Lobby521 | Lobby0 | [5 empty] | n | [14 empty] | 521 |  | 13792 |  |  | 0 |  | 13792 | [11 empty] | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  | #N/A | #N/A | [10 empty] | #N/A | #N/A | 0 | 0 |  | 0 | 0 |  | 0 | 0 | #N/A | 0
Lobby | Lobby534-2 | [5 empty] | n | [19 empty] | 534-2 |  | 13792 | [33 empty] | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A | #N/A | #N/A | 0
[18 empty] | Standalone_Retail_Interior Lighting LPD |  | Standalone Retail |  |  | 3613 |  | Standalone Retail |  |  | 3613 | [28 empty] | 0
Storage | Storage | [6 empty] | n | [11 empty] | Storage | 0.7752 |  |  | 4088 | Storage | 0.58716 |  |  | 4088 | [27 empty] | 0
Storage530 | Storage538 | [6 empty] | n | [11 empty] | replacement costs are for lamps |  | 530 |  | 4088 |  |  | 538 |  | 4088 |  | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A | #N/A | #N/A | #N/A
Storage553 | Storage0 | [6 empty] | n | [13 empty] | 0 |  | 4088 |  |  | 0 |  | 4088 |  | 0 | 0 |  | 0 | 0 |  | 0 |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | 0 | 0 | 0 | 0 |  | #N/A | #N/A |  | #N/A | #N/A | 0 | #N/A
Storage0 | Storage0 | [6 empty] | n | [13 empty] | 0 |  | 4088 |  |  | 0 |  | 4088 |  | 0 | 0 |  | 0 | 0 |  | 0 |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | 0 | 0 | 0 | 0 |  | #N/A | #N/A |  | #N/A | #N/A | 0 | #N/A
Storage | Storage0 | [6 empty] | n | [18 empty] | 0 |  | 4088 | [23 empty] | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | 0 | 0 | 0 | 0 |  | #N/A | #N/A |  | #N/A | #N/A | 0 | #N/A
Storage530 | Storage538 | [6 empty] | n | [11 empty] | ballast replacement |  | 530 |  | 4088 |  |  | 538 |  | 4088 | [11 empty] | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  | #N/A | #N/A | [10 empty] | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A | #N/A | #N/A | 0
Storage553 | Storage0 | [6 empty] | n | [13 empty] | 0 |  | 4088 |  |  | 0 |  | 4088 | [11 empty] | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | [10 empty] | #N/A | #N/A | 0 | 0 |  | 0 | 0 |  | 0 | 0 | #N/A | 0
Storage0 | Storage0 | [6 empty] | n | [13 empty] | 0 |  | 4088 |  |  | 0 |  | 4088 | [11 empty] | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | [10 empty] | #N/A | #N/A | 0 | 0 |  | 0 | 0 |  | 0 | 0 | #N/A | 0
Storage | Storage0 | [6 empty] | n | [18 empty] | 0 |  | 4088 | [33 empty] | #N/A | #N/A | 0 | 0 |  | 0 | 0 |  | 0 | 0 | #N/A | 0
Retail - Sales Area | Retail - Sales Area | [6 empty] | n | [11 empty] | Retail - Sales Area | 1.6473 |  |  | 20467 | Retail - Sales Area | 1.5658 |  |  | 20467 | [27 empty] | 0
Retail - Sales Area535 | Retail - Sales Area535 | [6 empty] | n | [11 empty] | replacement costs are for lamps |  | 535 |  | 20467 |  |  | 535 |  | 20467 |  | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A | #N/A | #N/A | #N/A
Retail - Sales Area541 | Retail - Sales Area541 | [6 empty] | n | [13 empty] | 541 |  | 20467 |  |  | 541 |  | 20467 |  | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A | #N/A | #N/A | #N/A
Retail - Sales Area572 | Retail - Sales Area0 | [6 empty] | n | [13 empty] | 0 |  | 20467 |  |  | 0 |  | 20467 |  | 0 | 0 |  | 0 | 0 |  | 0 |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | 0 | 0 | 0 | 0 |  | #N/A | #N/A |  | #N/A | #N/A | 0 | #N/A
Retail - Sales Area | Retail - Sales Area537-1 | [6 empty] | n | [18 empty] | 537-1 |  | 20467 | [23 empty] | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A | #N/A | #N/A | #N/A
Retail - Sales Area535 | Retail - Sales Area535 | [6 empty] | n | [11 empty] | ballast replacement |  | 535 |  | 20467 |  |  | 535 |  | 20467 | [11 empty] | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  | #N/A | #N/A | [10 empty] | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A | #N/A | #N/A | 0
Retail - Sales Area541 | Retail - Sales Area541 | [6 empty] | n | [13 empty] | 541 |  | 20467 |  |  | 541 |  | 20467 | [11 empty] | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  | #N/A | #N/A | [10 empty] | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A | #N/A | #N/A | 0
Retail - Sales Area572 | Retail - Sales Area0 | [6 empty] | n | [13 empty] | 0 |  | 20467 |  |  | 0 |  | 20467 | [11 empty] | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | [10 empty] | #N/A | #N/A | 0 | 0 |  | 0 | 0 |  | 0 | 0 | #N/A | 0
Retail - Sales Area | Retail - Sales Area537-1 | [6 empty] | n | [18 empty] | 537-1 |  | 20467 | [33 empty] | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A | #N/A | #N/A | 0
Lobby | Lobby | [6 empty] | n | [11 empty] | Lobby | 1.2597 |  |  | 129 | Lobby | 0.8388 |  |  | 129 | [27 empty] | 0
Lobby534-2 | Lobby523 | [6 empty] | n | [11 empty] | replacement costs are for lamps |  | 534-2 |  | 129 |  |  | 523 |  | 129 |  | 3.3111 | 427.1372 |  | 0.50427 | 65.0502 |  | 276.926 |  |  | 769.1134 | 9.8847 | 10 | 0.02919 | 3.7656 |  | 0.047635 | 6.1449 |  | 9.1535 |  | 19.0639 | 19.2863 | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A | #N/A | #N/A | #N/A
Lobby523 | Lobby521 | [6 empty] | n | [13 empty] | 523 |  | 129 |  |  | 521 |  | 129 |  | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A | #N/A | #N/A | #N/A
Lobby521 | Lobby0 | [6 empty] | n | [13 empty] | 521 |  | 129 |  |  | 0 |  | 129 |  | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | 0 | 0 | 0 | 0 |  | #N/A | #N/A |  | #N/A | #N/A | 0 | #N/A
Lobby | Lobby534-2 | [6 empty] | n | [18 empty] | 534-2 |  | 129 | [23 empty] | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A | #N/A | #N/A | #N/A
Lobby534-2 | Lobby523 | [6 empty] | n | [11 empty] | ballast replacement |  | 534-2 |  | 129 |  |  | 523 |  | 129 | [11 empty] | 13.7287 | 14 | 0.26141 | 33.7214 |  | 0.53588 | 69.1288 |  | 97.3465 |  | 200.1967 | 204.1526 | [10 empty] | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A | #N/A | #N/A | 0
Lobby523 | Lobby521 | [6 empty] | n | [13 empty] | 523 |  | 129 |  |  | 521 |  | 129 | [11 empty] | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  | #N/A | #N/A | [10 empty] | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A | #N/A | #N/A | 0
Lobby521 | Lobby0 | [6 empty] | n | [13 empty] | 521 |  | 129 |  |  | 0 |  | 129 | [11 empty] | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  | #N/A | #N/A | [10 empty] | #N/A | #N/A | 0 | 0 |  | 0 | 0 |  | 0 | 0 | #N/A | 0
Lobby | Lobby534-2 | [6 empty] | n | [18 empty] | 534-2 |  | 129 | [33 empty] | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A | #N/A | #N/A | 0
0
[18 empty] | Primary_School_Interior Lighting LPD |  | Primary School |  |  | 3774 |  | Primary School |  |  | 3774 | [28 empty] | 0
Restrooms | Restrooms | [7 empty] | n | [10 empty] | Restrooms | 0.9099 |  |  | 2044 | Restrooms | 0.9212 |  |  | 2044 | [27 empty] | 0
Restrooms521 | Restrooms604 | [7 empty] | n | [10 empty] | replacement costs are for lamps |  | 521 |  | 2044 |  |  | 604 |  | 2044 |  | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A | #N/A | #N/A | #N/A
Restrooms537-1 | Restrooms520 | [7 empty] | n | [12 empty] | 537-1 |  | 2044 |  |  | 520 |  | 2044 |  | 1.2306 | 2515.4144 |  | 0.73075 | 1493.6563 |  | 2703.0664 |  |  | 6712.1371 | 9.8847 | 10 | 0.039805 | 81.3618 |  | 0.064957 | 132.7711 |  | 197.7777 |  | 411.9105 | 416.7162 | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A | #N/A | #N/A | #N/A
Restrooms524 | Restrooms0 | [7 empty] | n | [12 empty] | 524 |  | 2044 |  |  | 0 |  | 2044 |  | 0.3127 | 639.1684 |  | 0.21447 | 438.3724 |  | 743.6538 |  |  | 1821.1946 | 2.7457 | 3 | 0.1095 | 223.8194 |  | 0.020226 | 41.3424 |  | 190.8817 |  | 456.0435 | 498.2732 | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | 0 | 0 | 0 | 0 |  | #N/A | #N/A |  | #N/A | #N/A | 0 | #N/A
Restrooms | Restrooms534-2 | [7 empty] | n | [17 empty] | 534-2 |  | 2044 | [23 empty] | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A | #N/A | #N/A | #N/A
Restrooms521 | Restrooms604 | [7 empty] | n | [10 empty] | ballast replacement |  | 521 |  | 2044 |  |  | 604 |  | 2044 | [11 empty] | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  | #N/A | #N/A | [10 empty] | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A | #N/A | #N/A | 0
Restrooms537-1 | Restrooms520 | [7 empty] | n | [12 empty] | 537-1 |  | 2044 |  |  | 520 |  | 2044 | [11 empty] | 13.7287 | 14 | 0.35646 | 728.6128 |  | 0.73075 | 1493.6563 |  | 2103.3532 |  | 4325.6224 | 4411.0967 | [10 empty] | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A | #N/A | #N/A | 0
Restrooms524 | Restrooms0 | [7 empty] | n | [12 empty] | 524 |  | 2044 |  |  | 0 |  | 2044 | [11 empty] | 13.7287 | 14 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | [10 empty] | #N/A | #N/A | 0 | 0 |  | 0 | 0 |  | 0 | 0 | #N/A | 0
Restrooms | Restrooms534-2 | [7 empty] | n | [17 empty] | 534-2 |  | 2044 | [33 empty] | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A | #N/A | #N/A | 0
Dining Area | Dining Area | [7 empty] | n | [10 empty] | Dining Area | 0.9099 |  |  | 3389 | Dining Area | 0.611 |  |  | 3389 | [27 empty] | 0
Dining Area531 | Dining Area535 | [7 empty] | n | [10 empty] | replacement costs are for lamps |  | 531 |  | 3389 |  |  | 535 |  | 3389 |  | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A | #N/A | #N/A | #N/A
Dining Area524 | Dining Area521 | [7 empty] | n | [12 empty] | 524 |  | 3389 |  |  | 521 |  | 3389 |  | 0.48745 | 1651.9735 |  | 0.33432 | 1133.0029 |  | 1922.0232 |  |  | 4706.9997 | 2.7457 | 3 | 0.17069 | 578.4763 |  | 0.031529 | 106.8523 |  | 493.3466 |  | 1178.6752 | 1287.8205 | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A | #N/A | #N/A | #N/A
Dining Area0 | Dining Area0 | [7 empty] | n | [12 empty] | 0 |  | 3389 |  |  | 0 |  | 3389 |  | 0 | 0 |  | 0 | 0 |  | 0 |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | 0 | 0 | 0 | 0 |  | #N/A | #N/A |  | #N/A | #N/A | 0 | #N/A
Dining Area | Dining Area537-1 | [7 empty] | n | [17 empty] | 537-1 |  | 3389 | [23 empty] | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A | #N/A | #N/A | #N/A
Dining Area531 | Dining Area535 | [7 empty] | n | [10 empty] | ballast replacement |  | 531 |  | 3389 |  |  | 535 |  | 3389 | [11 empty] | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  | #N/A | #N/A | [10 empty] | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A | #N/A | #N/A | 0
Dining Area524 | Dining Area521 | [7 empty] | n | [12 empty] | 524 |  | 3389 |  |  | 521 |  | 3389 | [11 empty] | 13.7287 | 14 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | [10 empty] | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A | #N/A | #N/A | 0
Dining Area0 | Dining Area0 | [7 empty] | n | [12 empty] | 0 |  | 3389 |  |  | 0 |  | 3389 | [11 empty] | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | [10 empty] | #N/A | #N/A | 0 | 0 |  | 0 | 0 |  | 0 | 0 | #N/A | 0
Dining Area | Dining Area537-1 | [7 empty] | n | [17 empty] | 537-1 |  | 3389 | [33 empty] | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A | #N/A | #N/A | 0
Classroom/Lecture/Training | Classroom/Lecture/Training | [7 empty] | n | [10 empty] | Classroom/Lecture/Training | 1.4154 |  |  | 37187 | Classroom/Lecture/Training | 1.1656 |  |  | 37187 | [27 empty] | 0
Classroom/Lecture/Training535 | Classroom/Lecture/Training535 | [7 empty] | n | [10 empty] | replacement costs are for lamps |  | 535 |  | 37187 |  |  | 535 |  | 37187 |  | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A | #N/A | #N/A | #N/A
Classroom/Lecture/Training537-2 | Classroom/Lecture/Training521 | [7 empty] | n | [12 empty] | 537-2 |  | 37187 |  |  | 521 |  | 37187 |  | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A | #N/A | #N/A | #N/A
Classroom/Lecture/Training0 | Classroom/Lecture/Training0 | [7 empty] | n | [12 empty] | 0 |  | 37187 |  |  | 0 |  | 37187 |  | 0 | 0 |  | 0 | 0 |  | 0 |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | 0 | 0 | 0 | 0 |  | #N/A | #N/A |  | #N/A | #N/A | 0 | #N/A
Classroom/Lecture/Training | Classroom/Lecture/Training537-1 | [7 empty] | n | [17 empty] | 537-1 |  | 37187 | [23 empty] | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A | #N/A | #N/A | #N/A
Classroom/Lecture/Training535 | Classroom/Lecture/Training535 | [7 empty] | n | [10 empty] | ballast replacement |  | 535 |  | 37187 |  |  | 535 |  | 37187 | [11 empty] | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  | #N/A | #N/A | [10 empty] | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A | #N/A | #N/A | 0
Classroom/Lecture/Training537-2 | Classroom/Lecture/Training521 | [7 empty] | n | [12 empty] | 537-2 |  | 37187 |  |  | 521 |  | 37187 | [11 empty] | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  | #N/A | #N/A | [10 empty] | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A | #N/A | #N/A | 0
Classroom/Lecture/Training0 | Classroom/Lecture/Training0 | [7 empty] | n | [12 empty] | 0 |  | 37187 |  |  | 0 |  | 37187 | [11 empty] | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | [10 empty] | #N/A | #N/A | 0 | 0 |  | 0 | 0 |  | 0 | 0 | #N/A | 0
Classroom/Lecture/Training | Classroom/Lecture/Training537-1 | [7 empty] | n | [17 empty] | 537-1 |  | 37187 | [33 empty] | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A | #N/A | #N/A | 0
Corridor/Transition | Corridor/Transition | [7 empty] | n | [10 empty] | Corridor/Transition | 0.5055 |  |  | 12073 | Corridor/Transition | 0.6204 |  |  | 12073 | [27 empty] | 0
Corridor/Transition530 | Corridor/Transition521 | [7 empty] | n | [10 empty] | replacement costs are for lamps |  | 530 |  | 12073 |  |  | 521 |  | 12073 |  | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A | #N/A | #N/A | #N/A
Corridor/Transition537-2 | Corridor/Transition0 | [7 empty] | n | [12 empty] | 537-2 |  | 12073 |  |  | 0 |  | 12073 |  | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | 0 | 0 | 0 | 0 |  | #N/A | #N/A |  | #N/A | #N/A | 0 | #N/A
Corridor/Transition0 | Corridor/Transition0 | [7 empty] | n | [12 empty] | 0 |  | 12073 |  |  | 0 |  | 12073 |  | 0 | 0 |  | 0 | 0 |  | 0 |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | 0 | 0 | 0 | 0 |  | #N/A | #N/A |  | #N/A | #N/A | 0 | #N/A
Corridor/Transition | Corridor/Transition527-2 | [7 empty] | n | [17 empty] | 0 |  | 12073 | [23 empty] | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | 0 | 0 | 0 | 0 |  | #N/A | #N/A |  | #N/A | #N/A | 0 | #N/A
Corridor/Transition530 | Corridor/Transition521 | [7 empty] | n | [10 empty] | ballast replacement |  | 530 |  | 12073 |  |  | 521 |  | 12073 | [11 empty] | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  | #N/A | #N/A | [10 empty] | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A | #N/A | #N/A | 0
Corridor/Transition537-2 | Corridor/Transition0 | [7 empty] | n | [12 empty] | 537-2 |  | 12073 |  |  | 0 |  | 12073 | [11 empty] | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  | #N/A | #N/A | [10 empty] | #N/A | #N/A | 0 | 0 |  | 0 | 0 |  | 0 | 0 | #N/A | 0
Corridor/Transition0 | Corridor/Transition0 | [7 empty] | n | [12 empty] | 0 |  | 12073 |  |  | 0 |  | 12073 | [11 empty] | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | [10 empty] | #N/A | #N/A | 0 | 0 |  | 0 | 0 |  | 0 | 0 | #N/A | 0
Corridor/Transition | Corridor/Transition527-2 | [7 empty] | n | [17 empty] | 0 |  | 12073 | [33 empty] | #N/A | #N/A | 0 | 0 |  | 0 | 0 |  | 0 | 0 | #N/A | 0
Gymnasium/Fitness-Fitness Area | Gymnasium/Fitness-Fitness Area | [7 empty] | n | [10 empty] | Gymnasium/Fitness-Fitness Area | 0.9099 |  |  | 3841 | Gymnasium/Fitness-Fitness Area | 0.6768 |  |  | 3841 | [27 empty] | 0
Gymnasium/Fitness-Fitness Area535 | Gymnasium/Fitness-Fitness Area535 | [7 empty] | n | [10 empty] | replacement costs are for lamps |  | 535 |  | 3841 |  |  | 535 |  | 3841 |  | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A | #N/A | #N/A | #N/A
Gymnasium/Fitness-Fitness Area0 | Gymnasium/Fitness-Fitness Area0 | [7 empty] | n | [12 empty] | 0 |  | 3841 |  |  | 0 |  | 3841 |  | 0 | 0 |  | 0 | 0 |  | 0 |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | 0 | 0 | 0 | 0 |  | #N/A | #N/A |  | #N/A | #N/A | 0 | #N/A
Gymnasium/Fitness-Fitness Area0 | Gymnasium/Fitness-Fitness Area0 | [7 empty] | n | [12 empty] | 0 |  | 3841 |  |  | 0 |  | 3841 |  | 0 | 0 |  | 0 | 0 |  | 0 |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | 0 | 0 | 0 | 0 |  | #N/A | #N/A |  | #N/A | #N/A | 0 | #N/A
Gymnasium/Fitness-Fitness Area | Gymnasium/Fitness-Fitness Area0 | [7 empty] | n | [17 empty] | 0 |  | 3841 | [23 empty] | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | 0 | 0 | 0 | 0 |  | #N/A | #N/A |  | #N/A | #N/A | 0 | #N/A
Gymnasium/Fitness-Fitness Area535 | Gymnasium/Fitness-Fitness Area535 | [7 empty] | n | [10 empty] | ballast replacement |  | 535 |  | 3841 |  |  | 535 |  | 3841 | [11 empty] | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  | #N/A | #N/A | [10 empty] | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A | #N/A | #N/A | 0
Gymnasium/Fitness-Fitness Area0 | Gymnasium/Fitness-Fitness Area0 | [7 empty] | n | [12 empty] | 0 |  | 3841 |  |  | 0 |  | 3841 | [11 empty] | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | [10 empty] | #N/A | #N/A | 0 | 0 |  | 0 | 0 |  | 0 | 0 | #N/A | 0
Gymnasium/Fitness-Fitness Area0 | Gymnasium/Fitness-Fitness Area0 | [7 empty] | n | [12 empty] | 0 |  | 3841 |  |  | 0 |  | 3841 | [11 empty] | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | [10 empty] | #N/A | #N/A | 0 | 0 |  | 0 | 0 |  | 0 | 0 | #N/A | 0
Gymnasium/Fitness-Fitness Area | Gymnasium/Fitness-Fitness Area0 | [7 empty] | n | [17 empty] | 0 |  | 3841 | [33 empty] | #N/A | #N/A | 0 | 0 |  | 0 | 0 |  | 0 | 0 | #N/A | 0
Food Preparation | Food Preparation | [7 empty] | n | [10 empty] | Food Preparation | 1.2132 |  |  | 1808 | Food Preparation | 0.9306 |  |  | 1808 | [27 empty] | 0
Food Preparation530 | Food Preparation530 | [7 empty] | n | [10 empty] | replacement costs are for lamps |  | 530 |  | 1808 |  |  | 530 |  | 1808 |  | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A | #N/A | #N/A | #N/A
Food Preparation0 | Food Preparation0 | [7 empty] | n | [12 empty] | 0 |  | 1808 |  |  | 0 |  | 1808 |  | 0 | 0 |  | 0 | 0 |  | 0 |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | 0 | 0 | 0 | 0 |  | #N/A | #N/A |  | #N/A | #N/A | 0 | #N/A
Food Preparation0 | Food Preparation0 | [7 empty] | n | [12 empty] | 0 |  | 1808 |  |  | 0 |  | 1808 |  | 0 | 0 |  | 0 | 0 |  | 0 |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | 0 | 0 | 0 | 0 |  | #N/A | #N/A |  | #N/A | #N/A | 0 | #N/A
Food Preparation | Food Preparation0 | [7 empty] | n | [17 empty] | 0 |  | 1808 | [23 empty] | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | 0 | 0 | 0 | 0 |  | #N/A | #N/A |  | #N/A | #N/A | 0 | #N/A
Food Preparation530 | Food Preparation530 | [7 empty] | n | [10 empty] | ballast replacement |  | 530 |  | 1808 |  |  | 530 |  | 1808 | [11 empty] | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  | #N/A | #N/A | [10 empty] | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A | #N/A | #N/A | 0
Food Preparation0 | Food Preparation0 | [7 empty] | n | [12 empty] | 0 |  | 1808 |  |  | 0 |  | 1808 | [11 empty] | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | [10 empty] | #N/A | #N/A | 0 | 0 |  | 0 | 0 |  | 0 | 0 | #N/A | 0
Food Preparation0 | Food Preparation0 | [7 empty] | n | [12 empty] | 0 |  | 1808 |  |  | 0 |  | 1808 | [11 empty] | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | [10 empty] | #N/A | #N/A | 0 | 0 |  | 0 | 0 |  | 0 | 0 | #N/A | 0
Food Preparation | Food Preparation0 | [7 empty] | n | [17 empty] | 0 |  | 1808 | [33 empty] | #N/A | #N/A | 0 | 0 |  | 0 | 0 |  | 0 | 0 | #N/A | 0
Library | Library | [7 empty] | n | [10 empty] | Library | 1.2132 |  |  | 4293 | Library | 0.8742 |  |  | 4293 | [27 empty] | 0
Library535 | Library535 | [7 empty] | n | [10 empty] | replacement costs are for lamps |  | 535 |  | 4293 |  |  | 535 |  | 4293 |  | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A | #N/A | #N/A | #N/A
Library520 | Library520 | [7 empty] | n | [12 empty] | 520 |  | 4293 |  |  | 520 |  | 4293 |  | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A | #N/A | #N/A | #N/A
Library529 | Library0 | [7 empty] | n | [12 empty] | 529 |  | 4293 |  |  | 0 |  | 4293 |  | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | 0 | 0 | 0 | 0 |  | #N/A | #N/A |  | #N/A | #N/A | 0 | #N/A
Library | Library0 | [7 empty] | n | [17 empty] | 0 |  | 4293 | [23 empty] | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | 0 | 0 | 0 | 0 |  | #N/A | #N/A |  | #N/A | #N/A | 0 | #N/A
Library535 | Library535 | [7 empty] | n | [10 empty] | ballast replacement |  | 535 |  | 4293 |  |  | 535 |  | 4293 | [11 empty] | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  | #N/A | #N/A | [10 empty] | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A | #N/A | #N/A | 0
Library520 | Library520 | [7 empty] | n | [12 empty] | 520 |  | 4293 |  |  | 520 |  | 4293 | [11 empty] | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  | #N/A | #N/A | [10 empty] | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A | #N/A | #N/A | 0
Library529 | Library0 | [7 empty] | n | [12 empty] | 529 |  | 4293 |  |  | 0 |  | 4293 | [11 empty] | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  | #N/A | #N/A | [10 empty] | #N/A | #N/A | 0 | 0 |  | 0 | 0 |  | 0 | 0 | #N/A | 0
Library | Library0 | [7 empty] | n | [17 empty] | 0 |  | 4293 | [33 empty] | #N/A | #N/A | 0 | 0 |  | 0 | 0 |  | 0 | 0 | #N/A | 0
Lobby | Lobby | [7 empty] | n | [10 empty] | Lobby | 1.3143 |  |  | 1840 | Lobby | 0.846 |  |  | 1840 | [27 empty] | 0
Lobby534-2 | Lobby523 | [7 empty] | n | [10 empty] | replacement costs are for lamps |  | 534-2 |  | 1840 |  |  | 523 |  | 1840 |  | 3.4547 | 6356.5709 |  | 0.52612 | 968.0639 |  | 4121.1573 |  |  | 11445.7921 | 9.8847 | 10 | 0.030456 | 56.0382 |  | 0.049699 | 91.4465 |  | 136.22 |  | 283.7048 | 287.0147 | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A | #N/A | #N/A | #N/A
Lobby523 | Lobby521 | [7 empty] | n | [12 empty] | 523 |  | 1840 |  |  | 521 |  | 1840 |  | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A | #N/A | #N/A | #N/A
Lobby521 | Lobby0 | [7 empty] | n | [12 empty] | 521 |  | 1840 |  |  | 0 |  | 1840 |  | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | 0 | 0 | 0 | 0 |  | #N/A | #N/A |  | #N/A | #N/A | 0 | #N/A
Lobby | Lobby534-2 | [7 empty] | n | [17 empty] | 534-2 |  | 1840 | [23 empty] | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A | #N/A | #N/A | #N/A
Lobby534-2 | Lobby523 | [7 empty] | n | [10 empty] | ballast replacement |  | 534-2 |  | 1840 |  |  | 523 |  | 1840 | [11 empty] | 13.7287 | 14 | 0.27274 | 501.8345 |  | 0.55911 | 1028.7608 |  | 1448.6916 |  | 2979.2869 | 3038.1576 | [10 empty] | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A | #N/A | #N/A | 0
Lobby523 | Lobby521 | [7 empty] | n | [12 empty] | 523 |  | 1840 |  |  | 521 |  | 1840 | [11 empty] | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  | #N/A | #N/A | [10 empty] | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A | #N/A | #N/A | 0
Lobby521 | Lobby0 | [7 empty] | n | [12 empty] | 521 |  | 1840 |  |  | 0 |  | 1840 | [11 empty] | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  | #N/A | #N/A | [10 empty] | #N/A | #N/A | 0 | 0 |  | 0 | 0 |  | 0 | 0 | #N/A | 0
Lobby | Lobby534-2 | [7 empty] | n | [17 empty] | 534-2 |  | 1840 | [33 empty] | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A | #N/A | #N/A | 0
Electrical/Mechanical | Electrical/Mechanical | [7 empty] | n | [10 empty] | Electrical/Mechanical | 1.5165 |  |  | 2712 | Electrical/Mechanical | 0.893 |  |  | 2712 | [27 empty] | 0
Electrical/Mechanical538 | Electrical/Mechanical538 | [7 empty] | n | [10 empty] | replacement costs are for lamps |  | 538 |  | 2712 |  |  | 538 |  | 2712 |  | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A | #N/A | #N/A | #N/A
Electrical/Mechanical0 | Electrical/Mechanical0 | [7 empty] | n | [12 empty] | 0 |  | 2712 |  |  | 0 |  | 2712 |  | 0 | 0 |  | 0 | 0 |  | 0 |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | 0 | 0 | 0 | 0 |  | #N/A | #N/A |  | #N/A | #N/A | 0 | #N/A
Electrical/Mechanical0 | Electrical/Mechanical0 | [7 empty] | n | [12 empty] | 0 |  | 2712 |  |  | 0 |  | 2712 |  | 0 | 0 |  | 0 | 0 |  | 0 |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | 0 | 0 | 0 | 0 |  | #N/A | #N/A |  | #N/A | #N/A | 0 | #N/A
Electrical/Mechanical | Electrical/Mechanical0 | [7 empty] | n | [17 empty] | 0 |  | 2712 | [23 empty] | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | 0 | 0 | 0 | 0 |  | #N/A | #N/A |  | #N/A | #N/A | 0 | #N/A
Electrical/Mechanical538 | Electrical/Mechanical538 | [7 empty] | n | [10 empty] | ballast replacement |  | 538 |  | 2712 |  |  | 538 |  | 2712 | [11 empty] | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  | #N/A | #N/A | [10 empty] | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A | #N/A | #N/A | 0
Electrical/Mechanical0 | Electrical/Mechanical0 | [7 empty] | n | [12 empty] | 0 |  | 2712 |  |  | 0 |  | 2712 | [11 empty] | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | [10 empty] | #N/A | #N/A | 0 | 0 |  | 0 | 0 |  | 0 | 0 | #N/A | 0
Electrical/Mechanical0 | Electrical/Mechanical0 | [7 empty] | n | [12 empty] | 0 |  | 2712 |  |  | 0 |  | 2712 | [11 empty] | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | [10 empty] | #N/A | #N/A | 0 | 0 |  | 0 | 0 |  | 0 | 0 | #N/A | 0
Electrical/Mechanical | Electrical/Mechanical0 | [7 empty] | n | [17 empty] | 0 |  | 2712 | [33 empty] | #N/A | #N/A | 0 | 0 |  | 0 | 0 |  | 0 | 0 | #N/A | 0
Office-Enclosed | Office-Enclosed | [7 empty] | n | [10 empty] | Office-Enclosed | 1.1121 |  |  | 4745 | Office-Enclosed | 1.0434 |  |  | 4745 | [27 empty] | 0
Office-Enclosed535 | Office-Enclosed531 | [7 empty] | n | [10 empty] | replacement costs are for lamps |  | 535 |  | 4745 |  |  | 531 |  | 4745 |  | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A | #N/A | #N/A | #N/A
Office-Enclosed539 | Office-Enclosed539 | [7 empty] | n | [12 empty] | 539 |  | 4745 |  |  | 539 |  | 4745 |  | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A | #N/A | #N/A | #N/A
Office-Enclosed537-2 | Office-Enclosed0 | [7 empty] | n | [12 empty] | 537-2 |  | 4745 |  |  | 0 |  | 4745 |  | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | 0 | 0 | 0 | 0 |  | #N/A | #N/A |  | #N/A | #N/A | 0 | #N/A
Office-Enclosed | Office-Enclosed537-1 | [7 empty] | n | [17 empty] | 537-1 |  | 4745 | [23 empty] | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A | #N/A | #N/A | #N/A
Office-Enclosed535 | Office-Enclosed531 | [7 empty] | n | [10 empty] | ballast replacement |  | 535 |  | 4745 |  |  | 531 |  | 4745 | [11 empty] | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  | #N/A | #N/A | [10 empty] | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A | #N/A | #N/A | 0
Office-Enclosed539 | Office-Enclosed539 | [7 empty] | n | [12 empty] | 539 |  | 4745 |  |  | 539 |  | 4745 | [11 empty] | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  | #N/A | #N/A | [10 empty] | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A | #N/A | #N/A | 0
Office-Enclosed537-2 | Office-Enclosed0 | [7 empty] | n | [12 empty] | 537-2 |  | 4745 |  |  | 0 |  | 4745 | [11 empty] | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  | #N/A | #N/A | [10 empty] | #N/A | #N/A | 0 | 0 |  | 0 | 0 |  | 0 | 0 | #N/A | 0
Office-Enclosed | Office-Enclosed537-1 | [7 empty] | n | [17 empty] | 537-1 |  | 4745 | [33 empty] | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A | #N/A | #N/A | 0
0
[18 empty] | Small_Hotel_Interior Lighting LPD |  | Small Hotel |  |  |  |  | Small Hotel
Highway Lodging Guest Rooms | Highway Lodging Guest Rooms | [8 empty] | n | [9 empty] | Highway Lodging Guest Rooms | 1.1 |  | 3588 | 27933 | Highway Lodging Guest Rooms | 0.75 |  | 3588 | 27933 | [27 empty] | 0
Highway Lodging Guest Rooms524 | Highway Lodging Guest Rooms529 | [8 empty] | n | [9 empty] | replacement costs are for lamps |  | 524 |  | 27933 |  |  | 529 |  | 27933 |  | 0.3851 | 10757.0452 |  | 0.26412 | 7377.6991 |  | 12515.5093 |  |  | 30650.2537 | 2.7457 | 3 | 0.13485 | 3766.8253 |  | 0.024909 | 695.783 |  | 3212.4916 |  | 7675.0999 | 8385.8141 | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A | #N/A | #N/A | #N/A
Highway Lodging Guest Rooms520 | Highway Lodging Guest Rooms520 | [8 empty] | n | [11 empty] | 520 |  | 27933 |  |  | 520 |  | 27933 |  | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A | #N/A | #N/A | #N/A
Highway Lodging Guest Rooms0 | Highway Lodging Guest Rooms0 | [8 empty] | n | [11 empty] | 0 |  | 27933 |  |  | 0 |  | 27933 |  | 0 | 0 |  | 0 | 0 |  | 0 |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | 0 | 0 | 0 | 0 |  | #N/A | #N/A |  | #N/A | #N/A | 0 | #N/A
Highway Lodging Guest Rooms | Highway Lodging Guest Rooms0 | [8 empty] | n | [16 empty] | 0 |  | 27933 | [23 empty] | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | 0 | 0 | 0 | 0 |  | #N/A | #N/A |  | #N/A | #N/A | 0 | #N/A
Highway Lodging Guest Rooms524 | Highway Lodging Guest Rooms529 | [8 empty] | n | [9 empty] | ballast replacement |  | 524 |  | 27933 |  |  | 529 |  | 27933 | [11 empty] | 13.7287 | 14 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | [10 empty] | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A | #N/A | #N/A | 0
Highway Lodging Guest Rooms520 | Highway Lodging Guest Rooms520 | [8 empty] | n | [11 empty] | 520 |  | 27933 |  |  | 520 |  | 27933 | [11 empty] | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  | #N/A | #N/A | [10 empty] | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A | #N/A | #N/A | 0
Highway Lodging Guest Rooms0 | Highway Lodging Guest Rooms0 | [8 empty] | n | [11 empty] | 0 |  | 27933 |  |  | 0 |  | 27933 | [11 empty] | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | [10 empty] | #N/A | #N/A | 0 | 0 |  | 0 | 0 |  | 0 | 0 | #N/A | 0
Highway Lodging Guest Rooms | Highway Lodging Guest Rooms0 | [8 empty] | n | [16 empty] | 0 |  | 27933 | [33 empty] | #N/A | #N/A | 0 | 0 |  | 0 | 0 |  | 0 | 0 | #N/A | 0
Corridor/Transition | Corridor/Transition | [8 empty] | n | [9 empty] | Corridor/Transition | 0.6475 |  | 8760 | 5668 | Corridor/Transition | 0.74514 |  | 8760 | 5668 | [27 empty] | 0
Corridor/Transition530 | Corridor/Transition521 | [8 empty] | n | [9 empty] | replacement costs are for lamps |  | 530 |  | 5668 |  |  | 521 |  | 5668 |  | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A | #N/A | #N/A | #N/A
Corridor/Transition537-2 | Corridor/Transition0 | [8 empty] | n | [11 empty] | 537-2 |  | 5668 |  |  | 0 |  | 5668 |  | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | 0 | 0 | 0 | 0 |  | #N/A | #N/A |  | #N/A | #N/A | 0 | #N/A
Corridor/Transition0 | Corridor/Transition0 | [8 empty] | n | [11 empty] | 0 |  | 5668 |  |  | 0 |  | 5668 |  | 0 | 0 |  | 0 | 0 |  | 0 |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | 0 | 0 | 0 | 0 |  | #N/A | #N/A |  | #N/A | #N/A | 0 | #N/A
Corridor/Transition | Corridor/Transition527-2 | [8 empty] | n | [16 empty] | 0 |  | 5668 | [23 empty] | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | 0 | 0 | 0 | 0 |  | #N/A | #N/A |  | #N/A | #N/A | 0 | #N/A
Corridor/Transition530 | Corridor/Transition521 | [8 empty] | n | [9 empty] | ballast replacement |  | 530 |  | 5668 |  |  | 521 |  | 5668 | [11 empty] | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  | #N/A | #N/A | [10 empty] | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A | #N/A | #N/A | 0
Corridor/Transition537-2 | Corridor/Transition0 | [8 empty] | n | [11 empty] | 537-2 |  | 5668 |  |  | 0 |  | 5668 | [11 empty] | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  | #N/A | #N/A | [10 empty] | #N/A | #N/A | 0 | 0 |  | 0 | 0 |  | 0 | 0 | #N/A | 0
Corridor/Transition0 | Corridor/Transition0 | [8 empty] | n | [11 empty] | 0 |  | 5668 |  |  | 0 |  | 5668 | [11 empty] | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | [10 empty] | #N/A | #N/A | 0 | 0 |  | 0 | 0 |  | 0 | 0 | #N/A | 0
Corridor/Transition | Corridor/Transition527-2 | [8 empty] | n | [16 empty] | 0 |  | 5668 | [33 empty] | #N/A | #N/A | 0 | 0 |  | 0 | 0 |  | 0 | 0 | #N/A | 0
Stairway | Stairway | [8 empty] | n | [9 empty] | Stairway | 0.777 |  | 8760 | 1728 | Stairway | 0.77901 |  | 8760 | 1728
Stairway530 | Stairway530 | [8 empty] | n | [9 empty] | replacement costs are for lamps |  | 530 |  | 1728 |  |  | 530 |  | 1728 |  | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A | #N/A | #N/A | #N/A
Stairway0 | Stairway602 | [8 empty] | n | [11 empty] | 0 |  | 1728 |  |  | 602 |  | 1728 |  | 0 | 0 |  | 0 | 0 |  | 0 |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A | #N/A | #N/A | #N/A
Stairway0 | Stairway0 | [8 empty] | n | [11 empty] | 0 |  | 1728 |  |  | 0 |  | 1728 |  | 0 | 0 |  | 0 | 0 |  | 0 |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | 0 | 0 | 0 | 0 |  | #N/A | #N/A |  | #N/A | #N/A | 0 | #N/A
Stairway | Stairway0 | [8 empty] | n | [16 empty] | 0 |  | 1728 | [23 empty] | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | 0 | 0 | 0 | 0 |  | #N/A | #N/A |  | #N/A | #N/A | 0 | #N/A
Stairway530 | Stairway530 | [8 empty] | n | [9 empty] | ballast replacement |  | 530 |  | 1728 |  |  | 530 |  | 1728 | [11 empty] | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  | #N/A | #N/A | [10 empty] | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A | #N/A | #N/A | 0
Stairway0 | Stairway602 | [8 empty] | n | [11 empty] | 0 |  | 1728 |  |  | 602 |  | 1728 | [11 empty] | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | [10 empty] | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A | #N/A | #N/A | 0
Stairway0 | Stairway0 | [8 empty] | n | [11 empty] | 0 |  | 1728 |  |  | 0 |  | 1728 | [11 empty] | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | [10 empty] | #N/A | #N/A | 0 | 0 |  | 0 | 0 |  | 0 | 0 | #N/A | 0
Stairway | Stairway0 | [8 empty] | n | [16 empty] | 0 |  | 1728 | [33 empty] | #N/A | #N/A | 0 | 0 |  | 0 | 0 |  | 0 | 0 | #N/A | 0
Lobby | Lobby - Hotel | [8 empty] | n | [9 empty] | Lobby - Hotel | 1.4245 |  | 7170 | 1755 | Lobby - Hotel | 1.1967 |  | 7170 | 1755
Lobby - Hotel535 | Lobby - Hotel572 | [8 empty] | n | [9 empty] | replacement costs are for lamps |  | 535 |  | 1755 |  |  | 572 |  | 1755 |  | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A | #N/A | #N/A | #N/A
Lobby - Hotel572 | Lobby - Hotel0 | [8 empty] | n | [11 empty] | 572 |  | 1755 |  |  | 0 |  | 1755 |  | 0.46241 | 811.5244 |  | 1.0193 | 1788.8441 |  | 2133.9188 |  |  | 4734.2873 | 0.23339 | 1 | 0.35435 | 621.8778 |  | 0.38948 | 683.5421 |  | 1150.4556 |  | 2455.8755 | 10522.7042 | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | 0 | 0 | 0 | 0 |  | #N/A | #N/A |  | #N/A | #N/A | 0 | #N/A
Lobby - Hotel524 | Lobby - Hotel0 | [8 empty] | n | [11 empty] | 524 |  | 1755 |  |  | 0 |  | 1755 |  | 0.33528 | 588.4132 |  | 0.22995 | 403.5621 |  | 684.6017 |  |  | 1676.577 | 2.7457 | 3 | 0.11741 | 206.0463 |  | 0.021686 | 38.0595 |  | 175.7241 |  | 419.83 | 458.7063 | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | 0 | 0 | 0 | 0 |  | #N/A | #N/A |  | #N/A | #N/A | 0 | #N/A
Lobby | Lobby - Hotel527-1 | [8 empty] | n | [16 empty] | 527-1 |  | 1755 | [23 empty] | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | #N/A |  | #N/A | #N/A |  | #N/A | #N/A |  | #N/A | #N/A | 0 | #N/A
Lobby - Hotel535 | Lobby - Hotel572 | [8 empty] | n | [9 empty] | ballast replacement |  | 535 |  | 1755 |  |  | 572 |  | 1755 | [11 empty] | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  | #N/A | #N/A | [10 empty] | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A | #N/A | #N/A | 0
Lobby - Hotel572 | Lobby - Hotel0 | [8 empty] | n | [11 empty] | 572 |  | 1755 |  |  | 0 |  | 1755 | [11 empty] | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | [10 empty] | #N/A | #N/A | 0 | 0 |  | 0 | 0 |  | 0 | 0 | #N/A | 0
Lobby - Hotel524 | Lobby - Hotel0 | [8 empty] | n | [11 empty] | 524 |  | 1755 |  |  | 0 |  | 1755 | [11 empty] | 13.7287 | 14 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | [10 empty] | #N/A | #N/A | 0 | 0 |  | 0 | 0 |  | 0 | 0 | #N/A | 0
Lobby | Lobby - Hotel527-1 | [8 empty] | n | [16 empty] | 527-1 |  | 1755 | [33 empty] | #N/A |  | #N/A | #N/A |  | #N/A | #N/A |  | #N/A | #N/A | 0 | 0
Storage | Storage | [8 empty] | n | [9 empty] | Storage | 1.036 |  | 2148 | 1404 | Storage | 0.71127 |  | 2148 | 1404
Storage530 | Storage538 | [8 empty] | n | [9 empty] | replacement costs are for lamps |  | 530 |  | 1404 |  |  | 538 |  | 1404 |  | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A | #N/A | #N/A | #N/A
Storage553 | Storage0 | [8 empty] | n | [11 empty] | 0 |  | 1404 |  |  | 0 |  | 1404 |  | 0 | 0 |  | 0 | 0 |  | 0 |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | 0 | 0 | 0 | 0 |  | #N/A | #N/A |  | #N/A | #N/A | 0 | #N/A
Storage0 | Storage0 | [8 empty] | n | [11 empty] | 0 |  | 1404 |  |  | 0 |  | 1404 |  | 0 | 0 |  | 0 | 0 |  | 0 |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | 0 | 0 | 0 | 0 |  | #N/A | #N/A |  | #N/A | #N/A | 0 | #N/A
Storage | Storage0 | [8 empty] | n | [16 empty] | 0 |  | 1404 | [23 empty] | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | 0 |  | 0 | 0 |  | #N/A | #N/A |  | #N/A | #N/A | 0 | #N/A
Storage530 | Storage538 | [8 empty] | n | [9 empty] | ballast replacement |  | 530 |  | 1404 |  |  | 538 |  | 1404 | [11 empty] | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  | #N/A | #N/A | [10 empty] | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A | #N/A | #N/A | 0
Storage553 | Storage0 | [8 empty] | n | [11 empty] | 0 |  | 1404 |  |  | 0 |  | 1404 | [11 empty] | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | [10 empty] | #N/A | #N/A | 0 | 0 |  | 0 | 0 |  | 0 | 0 | #N/A | 0
Storage0 | Storage0 | [8 empty] | n | [11 empty] | 0 |  | 1404 |  |  | 0 |  | 1404 | [11 empty] | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | [10 empty] | #N/A | #N/A | 0 | 0 |  | 0 | 0 |  | 0 | 0 | #N/A | 0
Storage | Storage0 | [8 empty] | n | [16 empty] | 0 |  | 1404 | [33 empty] | #N/A |  | 0 | 0 |  | 0 | 0 |  | 0 | 0 | 0 | 0
Office-Enclosed | Office-Enclosed | [8 empty] | n | [9 empty] | Office-Enclosed | 1.4245 |  | 5722 | 1404 | Office-Enclosed | 1.2532 |  | 5722 | 1404
Office-Enclosed535 | Office-Enclosed531 | [8 empty] | n | [9 empty] | replacement costs are for lamps |  | 535 |  | 1404 |  |  | 531 |  | 1404 |  | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A | #N/A | #N/A | #N/A
Office-Enclosed539 | Office-Enclosed539 | [8 empty] | n | [11 empty] | 539 |  | 1404 |  |  | 539 |  | 1404 |  | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A | #N/A | #N/A | #N/A
Office-Enclosed537-2 | Office-Enclosed0 | [8 empty] | n | [11 empty] | 537-2 |  | 1404 |  |  | 0 |  | 1404 |  | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | 0 | 0 | 0 | 0 |  | #N/A | #N/A |  | #N/A | #N/A | 0 | #N/A
Office-Enclosed | Office-Enclosed537-1 | [8 empty] | n | [16 empty] | 537-1 |  | 1404 | [23 empty] | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | #N/A |  | #N/A | #N/A |  | #N/A | #N/A |  | #N/A | #N/A | 0 | #N/A
Office-Enclosed535 | Office-Enclosed531 | [8 empty] | n | [9 empty] | ballast replacement |  | 535 |  | 1404 |  |  | 531 |  | 1404 | [11 empty] | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  | #N/A | #N/A | [10 empty] | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A | #N/A | #N/A | 0
Office-Enclosed539 | Office-Enclosed539 | [8 empty] | n | [11 empty] | 539 |  | 1404 |  |  | 539 |  | 1404 | [11 empty] | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  | #N/A | #N/A | [10 empty] | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A | #N/A | #N/A | 0
Office-Enclosed537-2 | Office-Enclosed0 | [8 empty] | n | [11 empty] | 537-2 |  | 1404 |  |  | 0 |  | 1404 | [11 empty] | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  | #N/A | #N/A | [10 empty] | #N/A | #N/A | 0 | 0 |  | 0 | 0 |  | 0 | 0 | #N/A | 0
Office-Enclosed | Office-Enclosed537-1 | [8 empty] | n | [16 empty] | 537-1 |  | 1404 | [33 empty] | #N/A |  | #N/A | #N/A |  | #N/A | #N/A |  | #N/A | #N/A | 0 | 0
Hospital - Laundry-washing | Hospital - Laundry-washing | [8 empty] | n | [9 empty] | Hospital - Laundry/Washing | 0.777 |  | 3276 | 1053 | Hospital - Laundry/Washing | 0.6774 |  | 3276 | 1053
Hospital - Laundry-washing530 | Hospital - Laundry-washing530 | [8 empty] | n | [9 empty] | replacement costs are for lamps |  | 530 |  | 1053 |  |  | 530 |  | 1053 |  | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A | #N/A | #N/A | #N/A
Hospital - Laundry-washing0 | Hospital - Laundry-washing0 | [8 empty] | n | [11 empty] | 0 |  | 1053 |  |  | 0 |  | 1053 |  | 0 | 0 |  | 0 | 0 |  | 0 |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | 0 | 0 | 0 | 0 |  | #N/A | #N/A |  | #N/A | #N/A | 0 | #N/A
Hospital - Laundry-washing0 | Hospital - Laundry-washing0 | [8 empty] | n | [11 empty] | 0 |  | 1053 |  |  | 0 |  | 1053 |  | 0 | 0 |  | 0 | 0 |  | 0 |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | 0 | 0 | 0 | 0 |  | #N/A | #N/A |  | #N/A | #N/A | 0 | #N/A
Hospital - Laundry-washing | Hospital - Laundry-washing0 | [8 empty] | n | [16 empty] | 0 |  | 1053 | [23 empty] | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | 0 |  | 0 | 0 |  | #N/A | #N/A |  | #N/A | #N/A | 0 | #N/A
Hospital - Laundry-washing530 | Hospital - Laundry-washing530 | [8 empty] | n | [9 empty] | ballast replacement |  | 530 |  | 1053 |  |  | 530 |  | 1053 | [11 empty] | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  | #N/A | #N/A | [10 empty] | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A | #N/A | #N/A | 0
Hospital - Laundry-washing0 | Hospital - Laundry-washing0 | [8 empty] | n | [11 empty] | 0 |  | 1053 |  |  | 0 |  | 1053 | [11 empty] | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | [10 empty] | #N/A | #N/A | 0 | 0 |  | 0 | 0 |  | 0 | 0 | #N/A | 0
Hospital - Laundry-washing0 | Hospital - Laundry-washing0 | [8 empty] | n | [11 empty] | 0 |  | 1053 |  |  | 0 |  | 1053 | [11 empty] | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | [10 empty] | #N/A | #N/A | 0 | 0 |  | 0 | 0 |  | 0 | 0 | #N/A | 0
Hospital - Laundry-washing | Hospital - Laundry-washing0 | [8 empty] | n | [16 empty] | 0 |  | 1053 | [33 empty] | #N/A |  | 0 | 0 |  | 0 | 0 |  | 0 | 0 | 0 | 0
Conference/Meeting/Multipurpose | Conference/Meeting/Multipurpose | [8 empty] | n | [9 empty] | Conference/Meeting/Multipurpose | 1.6835 |  | 4386 | 864 | Conference/Meeting/Multipurpose | 1.3887 |  | 4386 | 864
Conference/Meeting/Multipurpose535 | Conference/Meeting/Multipurpose535 | [8 empty] | n | [9 empty] | replacement costs are for lamps |  | 535 |  | 864 |  |  | 535 |  | 864 |  | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A | #N/A | #N/A | #N/A
Conference/Meeting/Multipurpose537-1 | Conference/Meeting/Multipurpose511 | [8 empty] | n | [11 empty] | 537-1 |  | 864 |  |  | 511 |  | 864 |  | 1.7484 | 1510.6286 |  | 1.0382 | 897.0132 |  | 1623.3227 |  |  | 4030.9645 | 9.8847 | 10 | 0.056553 | 48.8617 |  | 0.092286 | 79.7355 |  | 118.7751 |  | 247.3723 | 250.2583 | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A | #N/A | #N/A | #N/A
Conference/Meeting/Multipurpose511 | Conference/Meeting/Multipurpose0 | [8 empty] | n | [11 empty] | 511 |  | 864 |  |  | 0 |  | 864 |  | 0.20642 | 178.3505 |  | 0.34237 | 295.8079 |  | 375.0049 |  |  | 849.1634 | 1.1532 | 2 | 0.11902 | 102.8353 |  | 0.0162 | 13.9968 |  | 82.2516 |  | 199.0837 | 345.2681 | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | 0 | 0 | 0 | 0 |  | #N/A | #N/A |  | #N/A | #N/A | 0 | #N/A
Conference/Meeting/Multipurpose | Conference/Meeting/Multipurpose527-1 | [8 empty] | n | [18 empty] | 864 | [23 empty] | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | #N/A |  | #N/A | #N/A |  | #N/A | #N/A |  | #N/A | #N/A | 0 | #N/A
Conference/Meeting/Multipurpose535 | Conference/Meeting/Multipurpose535 | [8 empty] | n | [9 empty] | ballast replacement |  | 535 |  | 864 |  |  | 535 |  | 864 | [11 empty] | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  | #N/A | #N/A | [10 empty] | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A | #N/A | #N/A | 0
Conference/Meeting/Multipurpose537-1 | Conference/Meeting/Multipurpose511 | [8 empty] | n | [11 empty] | 537-1 |  | 864 |  |  | 511 |  | 864 | [11 empty] | 13.7287 | 14 | 0.50644 | 437.5674 |  | 1.0382 | 897.0132 |  | 1263.1658 |  | 2597.7465 | 2649.0779 | [10 empty] | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A | #N/A | #N/A | 0
Conference/Meeting/Multipurpose511 | Conference/Meeting/Multipurpose0 | [8 empty] | n | [11 empty] | 511 |  | 864 |  |  | 0 |  | 864 | [11 empty] | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | [10 empty] | #N/A | #N/A | 0 | 0 |  | 0 | 0 |  | 0 | 0 | #N/A | 0
Conference/Meeting/Multipurpose | Conference/Meeting/Multipurpose527-1 | [8 empty] | n | [16 empty] | 527-1 |  | 864 | [33 empty] | #N/A |  | #N/A | #N/A |  | #N/A | #N/A |  | #N/A | #N/A | 0 | 0
Restrooms | Restrooms | [8 empty] | n | [9 empty] | Restrooms | 1.1655 |  | 8760 | 351 | Restrooms | 1.1064 |  | 8760 | 351
Restrooms521 | Restrooms604 | [8 empty] | n | [9 empty] | replacement costs are for lamps |  | 521 |  | 351 |  |  | 604 |  | 351 |  | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A | #N/A | #N/A | #N/A
Restrooms537-1 | Restrooms520 | [8 empty] | n | [11 empty] | 537-1 |  | 351 |  |  | 520 |  | 351 |  | 1.5763 | 553.292 |  | 0.93603 | 328.5455 |  | 594.568 |  |  | 1476.4055 | 9.8847 | 10 | 0.050987 | 17.8964 |  | 0.083203 | 29.2044 |  | 43.5033 |  | 90.6041 | 91.6611 | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A | #N/A | #N/A | #N/A
Restrooms524 | Restrooms0 | [8 empty] | n | [11 empty] | 524 |  | 351 |  |  | 0 |  | 351 |  | 0.40055 | 140.5918 |  | 0.27471 | 96.4246 |  | 163.5745 |  |  | 400.591 | 2.7457 | 3 | 0.14026 | 49.2314 |  | 0.025908 | 9.0937 |  | 41.9864 |  | 100.3116 | 109.6005 | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | 0 | 0 | 0 | 0 |  | #N/A | #N/A |  | #N/A | #N/A | 0 | #N/A
Restrooms | Restrooms534-2 | [8 empty] | n | [16 empty] | 534-2 |  | 351 | [23 empty] | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | #N/A |  | #N/A | #N/A |  | #N/A | #N/A |  | #N/A | #N/A | 0 | #N/A
Restrooms521 | Restrooms604 | [8 empty] | n | [9 empty] | ballast replacement |  | 521 |  | 351 |  |  | 604 |  | 351 | [11 empty] | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  | #N/A | #N/A | [10 empty] | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A | #N/A | #N/A | 0
Restrooms537-1 | Restrooms520 | [8 empty] | n | [11 empty] | 537-1 |  | 351 |  |  | 520 |  | 351 | [11 empty] | 13.7287 | 14 | 0.4566 | 160.2661 |  | 0.93603 | 328.5455 |  | 462.6548 |  | 951.4664 | 970.2673 | [10 empty] | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A | #N/A | #N/A | 0
Restrooms524 | Restrooms0 | [8 empty] | n | [11 empty] | 524 |  | 351 |  |  | 0 |  | 351 | [11 empty] | 13.7287 | 14 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | [10 empty] | #N/A | #N/A | 0 | 0 |  | 0 | 0 |  | 0 | 0 | #N/A | 0
Restrooms | Restrooms534-2 | [8 empty] | n | [16 empty] | 534-2 |  | 351 | [33 empty] | #N/A |  | #N/A | #N/A |  | #N/A | #N/A |  | #N/A | #N/A | 0 | 0
Gymnasium/Fitness-Fitness Area | Gymnasium/Fitness-Fitness Area | [8 empty] | n | [9 empty] | Gymnasium/Fitness-Fitness Area | 1.1655 |  | 5824 | 351 | Gymnasium/Fitness-Fitness Area | 0.81288 |  | 5824 | 351
Gymnasium/Fitness-Fitness Area535 | Gymnasium/Fitness-Fitness Area535 | [8 empty] | n | [9 empty] | replacement costs are for lamps |  | 535 |  | 351 |  |  | 535 |  | 351 |  | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A | #N/A | #N/A | #N/A
Gymnasium/Fitness-Fitness Area0 | Gymnasium/Fitness-Fitness Area0 | [8 empty] | n | [11 empty] | 0 |  | 351 |  |  | 0 |  | 351 |  | 0 | 0 |  | 0 | 0 |  | 0 |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | 0 | 0 | 0 | 0 |  | #N/A | #N/A |  | #N/A | #N/A | 0 | #N/A
Gymnasium/Fitness-Fitness Area0 | Gymnasium/Fitness-Fitness Area0 | [8 empty] | n | [11 empty] | 0 |  | 351 |  |  | 0 |  | 351 |  | 0 | 0 |  | 0 | 0 |  | 0 |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | 0 | 0 | 0 | 0 |  | #N/A | #N/A |  | #N/A | #N/A | 0 | #N/A
Gymnasium/Fitness-Fitness Area | Gymnasium/Fitness-Fitness Area0 | [8 empty] | n | [16 empty] | 0 |  | 351 | [23 empty] | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | 0 |  | 0 | 0 |  | #N/A | #N/A |  | #N/A | #N/A | 0 | #N/A
Gymnasium/Fitness-Fitness Area535 | Gymnasium/Fitness-Fitness Area535 | [8 empty] | n | [9 empty] | ballast replacement |  | 535 |  | 351 |  |  | 535 |  | 351 | [11 empty] | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  | #N/A | #N/A | [10 empty] | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A | #N/A | #N/A | 0
Gymnasium/Fitness-Fitness Area0 | Gymnasium/Fitness-Fitness Area0 | [8 empty] | n | [11 empty] | 0 |  | 351 |  |  | 0 |  | 351 | [11 empty] | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | [10 empty] | #N/A | #N/A | 0 | 0 |  | 0 | 0 |  | 0 | 0 | #N/A | 0
Gymnasium/Fitness-Fitness Area0 | Gymnasium/Fitness-Fitness Area0 | [8 empty] | n | [11 empty] | 0 |  | 351 |  |  | 0 |  | 351 | [11 empty] | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | [10 empty] | #N/A | #N/A | 0 | 0 |  | 0 | 0 |  | 0 | 0 | #N/A | 0
Gymnasium/Fitness-Fitness Area | Gymnasium/Fitness-Fitness Area0 | [8 empty] | n | [16 empty] | 0 |  | 351 | [33 empty] | #N/A |  | 0 | 0 |  | 0 | 0 |  | 0 | 0 | 0 | 0
Lounge/Recreation - Breakroom | Lounge/Recreation - Breakroom | [8 empty] | n | [9 empty] | Lounge/Recreation - Break room | 1.554 |  | 4128 | 351 | Lounge/Recreation - Break room | 0.82417 |  | 4128 | 351
Lounge/Recreation - Breakroom537-1 | Lounge/Recreation - Breakroom521 | [8 empty] | n | [9 empty] | replacement costs are for lamps |  | 537-1 |  | 351 |  |  | 521 |  | 351 |  | 1.749 | 613.9159 |  | 1.0386 | 364.544 |  | 659.7145 |  |  | 1638.1744 | 9.8847 | 10 | 0.056573 | 19.8573 |  | 0.09232 | 32.4043 |  | 48.2699 |  | 100.5315 | 101.7044 | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A | #N/A | #N/A | #N/A
Lounge/Recreation - Breakroom572 | Lounge/Recreation - Breakroom0 | [8 empty] | n | [11 empty] | 0 |  | 351 |  |  | 0 |  | 351 |  | 0 | 0 |  | 0 | 0 |  | 0 |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | 0 | 0 | 0 | 0 |  | #N/A | #N/A |  | #N/A | #N/A | 0 | #N/A
Lounge/Recreation - Breakroom521 | Lounge/Recreation - Breakroom0 | [8 empty] | n | [11 empty] | 521 |  | 351 |  |  | 0 |  | 351 |  | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | 0 | 0 | 0 | 0 |  | #N/A | #N/A |  | #N/A | #N/A | 0 | #N/A
Lounge/Recreation - Breakroom | Lounge/Recreation - Breakroom527-2 | [8 empty] | n | [16 empty] | 527-2 |  | 351 | [23 empty] | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | #N/A |  | #N/A | #N/A |  | #N/A | #N/A |  | #N/A | #N/A | 0 | #N/A
Lounge/Recreation - Breakroom537-1 | Lounge/Recreation - Breakroom521 | [8 empty] | n | [9 empty] | ballast replacement |  | 537-1 |  | 351 |  |  | 521 |  | 351 | [11 empty] | 13.7287 | 14 | 0.50663 | 177.8264 |  | 1.0386 | 364.544 |  | 513.3476 |  | 1055.718 | 1076.5789 | [10 empty] | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A | #N/A | #N/A | 0
Lounge/Recreation - Breakroom572 | Lounge/Recreation - Breakroom0 | [8 empty] | n | [11 empty] | 0 |  | 351 |  |  | 0 |  | 351 | [11 empty] | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | [10 empty] | #N/A | #N/A | 0 | 0 |  | 0 | 0 |  | 0 | 0 | #N/A | 0
Lounge/Recreation - Breakroom521 | Lounge/Recreation - Breakroom0 | [8 empty] | n | [11 empty] | 521 |  | 351 |  |  | 0 |  | 351 | [11 empty] | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  | #N/A | #N/A | [10 empty] | #N/A | #N/A | 0 | 0 |  | 0 | 0 |  | 0 | 0 | #N/A | 0
Lounge/Recreation - Breakroom | Lounge/Recreation - Breakroom527-2 | [8 empty] | n | [16 empty] | 527-2 |  | 351 | [33 empty] | #N/A |  | #N/A | #N/A |  | #N/A | #N/A |  | #N/A | #N/A | 0 | 0
Electrical/Mechanical | Electrical/Mechanical | [8 empty] | n | [9 empty] | Electrical/Mechanical | 1.9425 |  | 2148 | 351 | Electrical/Mechanical | 1.0725 |  | 2148 | 351
Electrical/Mechanical538 | Electrical/Mechanical538 | [8 empty] | n | [9 empty] | replacement costs are for lamps |  | 538 |  | 351 |  |  | 538 |  | 351 |  | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A | #N/A | #N/A | #N/A
Electrical/Mechanical0 | Electrical/Mechanical0 | [8 empty] | n | [11 empty] | 0 |  | 351 |  |  | 0 |  | 351 |  | 0 | 0 |  | 0 | 0 |  | 0 |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | 0 | 0 | 0 | 0 |  | #N/A | #N/A |  | #N/A | #N/A | 0 | #N/A
Electrical/Mechanical0 | Electrical/Mechanical0 | [8 empty] | n | [11 empty] | 0 |  | 351 |  |  | 0 |  | 351 |  | 0 | 0 |  | 0 | 0 |  | 0 |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | 0 | 0 | 0 | 0 |  | #N/A | #N/A |  | #N/A | #N/A | 0 | #N/A
Electrical/Mechanical | Electrical/Mechanical0 | [8 empty] | n | [16 empty] | 0 |  | 351 | [23 empty] | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | 0 |  | 0 | 0 |  | #N/A | #N/A |  | #N/A | #N/A | 0 | #N/A
Electrical/Mechanical538 | Electrical/Mechanical538 | [8 empty] | n | [9 empty] | ballast replacement |  | 538 |  | 351 |  |  | 538 |  | 351 | [11 empty] | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  | #N/A | #N/A | [10 empty] | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A | #N/A | #N/A | 0
Electrical/Mechanical0 | Electrical/Mechanical0 | [8 empty] | n | [11 empty] | 0 |  | 351 |  |  | 0 |  | 351 | [11 empty] | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | [10 empty] | #N/A | #N/A | 0 | 0 |  | 0 | 0 |  | 0 | 0 | #N/A | 0
Electrical/Mechanical0 | Electrical/Mechanical0 | [8 empty] | n | [11 empty] | 0 |  | 351 |  |  | 0 |  | 351 | [11 empty] | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | [10 empty] | #N/A | #N/A | 0 | 0 |  | 0 | 0 |  | 0 | 0 | #N/A | 0
Electrical/Mechanical | Electrical/Mechanical0 | [8 empty] | n | [16 empty] | 0 |  | 351 | [33 empty] | #N/A |  | 0 | 0 |  | 0 | 0 |  | 0 | 0 | 0 | 0
[18 empty] | Mid-rise Apartment_Interior Lighting LPD |  | Mid-rise Apartment |  |  |  |  | Mid-rise Apartment
Office-Enclosed | Office-Enclosed | [9 empty] | n | [8 empty] | Office-Enclosed | 1.2166 |  | 3231 | 950 | Office-Enclosed | 0.86802 |  | 3231 | 950
Office-Enclosed535 | Office-Enclosed531 | [9 empty] | n | [8 empty] | replacement costs are for lamps |  | 535 |  | 950 |  |  | 531 |  | 950 |  | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A | #N/A | #N/A | #N/A
Office-Enclosed539 | Office-Enclosed539 | [9 empty] | n | [10 empty] | 539 |  | 950 |  |  | 539 |  | 950 |  | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A | #N/A | #N/A | #N/A
Office-Enclosed537-2 | Office-Enclosed0 | [9 empty] | n | [10 empty] | 537-2 |  | 950 |  |  | 0 |  | 950 |  | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | 0 | 0 | 0 | 0 |  | #N/A | #N/A |  | #N/A | #N/A | 0 | #N/A
Office-Enclosed | Office-Enclosed537-1 | [9 empty] | n | [15 empty] | 537-1 |  | 950 | [23 empty] | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A | #N/A | #N/A | #N/A
Office-Enclosed535 | Office-Enclosed531 | [9 empty] | n | [8 empty] | ballast replacement |  | 535 |  | 950 |  |  | 531 |  | 950 | [11 empty] | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  | #N/A | #N/A | [10 empty] | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A | #N/A | #N/A | 0
Office-Enclosed539 | Office-Enclosed539 | [9 empty] | n | [10 empty] | 539 |  | 950 |  |  | 539 |  | 950 | [11 empty] | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  | #N/A | #N/A | [10 empty] | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A | #N/A | #N/A | 0
Office-Enclosed537-2 | Office-Enclosed0 | [9 empty] | n | [10 empty] | 537-2 |  | 950 |  |  | 0 |  | 950 | [11 empty] | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  | #N/A | #N/A | [10 empty] | #N/A | #N/A | 0 | 0 |  | 0 | 0 |  | 0 | 0 | #N/A | 0
Office-Enclosed | Office-Enclosed537-1 | [9 empty] | n | [15 empty] | 537-1 |  | 950 | [33 empty] | #N/A |  | #N/A | #N/A |  | #N/A | #N/A |  | #N/A | #N/A | 0 | 0
Corridor/Transition | Corridor/Transition | [9 empty] | n | [8 empty] | Corridor/Transition | 0.553 |  | 8760 | 3345 | Corridor/Transition | 0.51612 |  | 8760 | 3345
Corridor/Transition530 | Corridor/Transition521 | [9 empty] | n | [8 empty] | replacement costs are for lamps |  | 530 |  | 3345 |  |  | 521 |  | 3345 |  | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A | #N/A | #N/A | #N/A
Corridor/Transition537-2 | Corridor/Transition0 | [9 empty] | n | [10 empty] | 537-2 |  | 3345 |  |  | 0 |  | 3345 |  | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | 0 | 0 | 0 | 0 |  | #N/A | #N/A |  | #N/A | #N/A | 0 | #N/A
Corridor/Transition0 | Corridor/Transition0 | [9 empty] | n | [10 empty] | 0 |  | 3345 |  |  | 0 |  | 3345 |  | 0 | 0 |  | 0 | 0 |  | 0 |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | 0 | 0 | 0 | 0 |  | #N/A | #N/A |  | #N/A | #N/A | 0 | #N/A
| Corridor/Transition527-2 | [9 empty] | n | [15 empty] | 0 |  | 3345 | [23 empty] | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | 0 | 0 | 0 | 0 |  | #N/A | #N/A |  | #N/A | #N/A | 0 | #N/A
Corridor/Transition530 | Corridor/Transition521 | [9 empty] | n | [8 empty] | ballast replacement |  | 530 |  | 3345 |  |  | 521 |  | 3345 | [11 empty] | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  | #N/A | #N/A | [10 empty] | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A | #N/A | #N/A | 0
Corridor/Transition537-2 | Corridor/Transition0 | [9 empty] | n | [10 empty] | 537-2 |  | 3345 |  |  | 0 |  | 3345 | [11 empty] | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  | #N/A | #N/A | [10 empty] | #N/A | #N/A | 0 | 0 |  | 0 | 0 |  | 0 | 0 | #N/A | 0
Corridor/Transition0 | Corridor/Transition0 | [9 empty] | n | [10 empty] | 0 |  | 3345 |  |  | 0 |  | 3345 | [11 empty] | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | [10 empty] | #N/A | #N/A | 0 | 0 |  | 0 | 0 |  | 0 | 0 | #N/A | 0
| Corridor/Transition527-2 | [9 empty] | n | [12 empty] | 2508 |  |  | 0 |  | 3345 | [33 empty] | #N/A | #N/A | 0 | 0 |  | 0 | 0 |  | 0 | 0 | #N/A | 0
[11 empty] | n | [8 empty] | Dwelling Units Average | 0.585 |  |  | 29450 | Dwelling Units Average | 0.46 |  |  | 29450
Averages of low and high end apartment | [10 empty] | n | [8 empty] | 50% of low end and high end for new construction and replacements |  | Average New Construction |  |  | 50% of low end and high end for new construction and replacements |  | Average New Construction | [12 empty] | #N/A | [21 empty] | #N/A | [11 empty] | #N/A
[11 empty] | n | [8 empty] | replacement costs are for lamps, 50% of each low-end |  | 501 |  |  | replacement costs are for lamps, 50% of each low-end |  | 501 | [14 empty] | #N/A | [9 empty] | #N/A | [11 empty] | #N/A | [8 empty] | #N/A
[11 empty] | n | [10 empty] | 700 |  |  |  |  | 700 | [14 empty] | #N/A | [9 empty] | #N/A | [11 empty] | #N/A | [8 empty] | #N/A
[11 empty] | n | [10 empty] | 530 |  |  |  |  | 530 | [14 empty] | #N/A | [9 empty] | #N/A | [11 empty] | #N/A | [8 empty] | #N/A
[11 empty] | n | [8 empty] | high-end |  | 505 |  |  | high-end |  | 505 | [14 empty] | #N/A | [9 empty] | #N/A | [11 empty] | #N/A | [8 empty] | #N/A
[11 empty] | n | [10 empty] | 501 |  |  |  |  | 501 | [14 empty] | #N/A | [9 empty] | #N/A | [11 empty] | #N/A | [8 empty] | #N/A
[11 empty] | n | [10 empty] | 500 |  |  |  |  | 500 | [14 empty] | #N/A | [9 empty] | #N/A | [11 empty] | #N/A | [8 empty] | #N/A
[11 empty] | n | [10 empty] | 700 |  |  |  |  | 700 | [14 empty] | #N/A | [9 empty] | #N/A | [11 empty] | #N/A | [8 empty] | #N/A
[11 empty] | n | [10 empty] | 530 |  |  |  |  | 530 | [14 empty] | #N/A | [9 empty] | #N/A | [11 empty] | #N/A | [8 empty] | #N/A
[11 empty] | n | [8 empty] | replacement costs are for ballasts, 50% of each low-end |  | 501 |  |  | replacement costs are for ballasts, 50% of each low-end |  | 501
[11 empty] | n | [10 empty] | 700 |  |  |  |  | 700 | [14 empty] | #N/A | [9 empty] | #N/A | [11 empty] | #N/A | [8 empty] | #N/A
[11 empty] | n | [10 empty] | 530 |  |  |  |  | 530 | [14 empty] | #N/A | [9 empty] | #N/A | [11 empty] | #N/A | [8 empty] | #N/A
[11 empty] | n | [8 empty] | high-end |  | 505 |  |  | high-end |  | 505 | [14 empty] | #N/A | [9 empty] | #N/A | [11 empty] | #N/A | [8 empty] | #N/A
[11 empty] | n | [10 empty] | 501 |  |  |  |  | 501 | [14 empty] | #N/A | [9 empty] | #N/A | [11 empty] | #N/A | [8 empty] | #N/A
[11 empty] | n | [10 empty] | 500 |  |  |  |  | 500 | [14 empty] | #N/A | [9 empty] | #N/A | [11 empty] | #N/A | [8 empty] | #N/A
[11 empty] | n | [10 empty] | 700 |  |  |  |  | 700 | [14 empty] | #N/A | [9 empty] | #N/A | [11 empty] | #N/A | [8 empty] | #N/A
[11 empty] | n | [10 empty] | 530 |  |  |  |  | 530 | [14 empty] | #N/A | [9 empty] | #N/A | [11 empty] | #N/A | [8 empty] | #N/A
[11 empty] | n | [30 empty] | #N/A | [9 empty] | #N/A | [11 empty] | #N/A | [8 empty] | #N/A
Dwelling Units | Dwelling Units | [18 empty] | Dwelling Units Low End | 0.39 |  | 2875 | 29450 | Dwelling Units Low End | 0.3 | sub-total | 2875 | 29450 | [10 empty] | #N/A | [21 empty] | #N/A
DwellingUnits501_Low | DwellingUnits501_Low | [18 empty] | replacement costs are for lamps |  | 501 |  | 29450 |  |  | 501 |  | 29450 |  | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A | #N/A | #N/A | #N/A
DwellingUnits700_Low | DwellingUnits700_Low | [20 empty] | 700 |  | 29450 |  |  | 700 |  | 29450 |  | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A | #N/A | #N/A | #N/A
DwellingUnits530_Low | DwellingUnits530_Low | [20 empty] | 530 |  | 29450 |  |  | 530 |  | 29450 |  | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A | #N/A | #N/A | #N/A
[24 empty] | 29450 |  |  |  |  | 29450 | [43 empty] | 0
DwellingUnits501_Low | DwellingUnits501_Low | [18 empty] | ballast replacement |  | 501 |  | 29450 |  |  | 501 |  | 29450 | [11 empty] | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  | #N/A | #N/A | [10 empty] | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A | #N/A | #N/A | 0
DwellingUnits700_Low | DwellingUnits700_Low | [20 empty] | 700 |  | 29450 |  |  | 700 |  | 29450 | [11 empty] | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  | #N/A | #N/A | [10 empty] | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A | #N/A | #N/A | 0
DwellingUnits530_Low | DwellingUnits530_Low | [20 empty] | 530 |  | 29450 |  |  | 530 |  | 29450 | [11 empty] | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  | #N/A | #N/A | [10 empty] | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A | #N/A | #N/A | 0
Dwelling Units | Dwelling Units | [18 empty] | Dwelling Units High End | 0.78 |  | 2875 | 29450 | Dwelling Units High End | 0.62 |  | 2875 | 29450 | [10 empty] | #N/A | [21 empty] | #N/A | [10 empty] | 0
DwellingUnits505_High | DwellingUnits505_High | [18 empty] | replacement costs are for lamps |  | 505 |  | 29450 |  |  | 505 |  | 29450 |  | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A | #N/A | #N/A | #N/A
DwellingUnits501_High | DwellingUnits500_High | [20 empty] | 501 |  | 29450 |  |  | 500 |  | 29450 |  | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A | #N/A | #N/A | #N/A
DwellingUnits500_High | DwellingUnits700_High | [20 empty] | 500 |  | 29450 |  |  | 700 |  | 29450 |  | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A | #N/A | #N/A | #N/A
DwellingUnits700_High | DwellingUnits701_High | [20 empty] | 700 |  | 29450 |  |  | 701 |  | 29450 |  | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A | #N/A | #N/A | #N/A
DwellingUnits530_High | DwellingUnits530_High | [20 empty] | 530 |  | 29450 |  |  | 530 |  | 29450 |  | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A | #N/A | #N/A | #N/A
DwellingUnits505_High | DwellingUnits505_High | [18 empty] | ballast replacement |  | 505 |  | 29450 |  |  | 505 |  | 29450 | [11 empty] | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  | #N/A | #N/A | [10 empty] | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A | #N/A | #N/A | 0
DwellingUnits501_High | DwellingUnits500_High | [20 empty] | 501 |  | 29450 |  |  | 500 |  | 29450 | [11 empty] | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  | #N/A | #N/A | [10 empty] | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A | #N/A | #N/A | 0
DwellingUnits500_High | DwellingUnits700_High | [20 empty] | 500 |  | 29450 |  |  | 700 |  | 29450 | [11 empty] | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  | #N/A | #N/A | [10 empty] | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A | #N/A | #N/A | 0
DwellingUnits700_High | DwellingUnits701_High | [20 empty] | 700 |  | 29450 |  |  | 701 |  | 29450 | [11 empty] | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  | #N/A | #N/A | [10 empty] | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A | #N/A | #N/A | 0
DwellingUnits530_High | DwellingUnits530_High | [20 empty] | 530 |  | 29450 |  |  | 530 |  | 29450 | [11 empty] | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  | #N/A | #N/A | [10 empty] | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A | #N/A | #N/A | 0
Note on AR472: Brian Thornton: subtotal low end 2009
Note on AR480: Brian Thornton: subtotal high end 2009
Note on BN472: Brian Thornton: subtotal low end 2009
Note on BN480: Brian Thornton: subtotal high end 2009

## Int Ltg LPD Proto NC IECC (hidden)
| #VALUE! | [18 empty] | State Commercial Energy Code Cost Effectiveness - Interior Lighting Power Density - IECC 2009 and IECC 2010 - Costs Totals for Each Prototype | [55 empty] | 90.1 Cost Effectiveness - Interior Lighting Power Density 90.1-07by and 90.1-07de Costs - Prototype
Summary
IECC 2012 has changes to interior lighting power allowances, generally significantly lower that for IECC 2009
The cost of interior lighting for the prototypes that meets the lighting power allowances for IECC 2009 and IECC 2012 are shown below.
Interior Lighting - Summary of Total New Construction, Maintenance, and Replacement Costs By Replacement Year by Prototype
[7 empty] | Cost Parameters | [30 empty] | #N/A
[20 empty] | 2009 IECC |  |  |  |  | 2012 IECC | [5 empty] | IECC 2009 Baseline Costs - without implementation of the addenda. | [21 empty] | IECC 2012 - costs with addendum | [21 empty] | Incremental Costs | Small Office | [7 empty] | Large Office | [7 empty] | Standalone Retail | [7 empty] | Primary School | [7 empty] | Small Hotel | [7 empty] | Mid-rise Apartment
|  | Related 90.1-07 Addenda and IECC 2012 Sections |  |  |  | Prototypes Affected | [5 empty] | Climate Location | [5 empty] | Name of Item | [12 empty] | New Construction Costs | [9 empty] | Replacement Costs | [11 empty] | New Construction Costs | [9 empty] | Replacement Costs | [12 empty] | IECC 2009 |  |  | IECC 2012 |  |  | Incremental Cost |  | IECC 2009 |  |  | IECC 2012 |  |  | Incremental Cost |  | IECC 2009 |  |  | IECC 2012 |  |  | Incremental Cost |  | IECC 2009 |  |  | IECC 2012 |  |  | Incremental Cost |  | IECC 2009 |  |  | IECC 2012 |  |  | Incremental Cost |  | IECC 2009 |  |  | IECC 2012 |  |  | Incremental Cost
2009 Lookup | 2012 Lookup | 90.1 Addenda | IECC 2009 Chapter(s) Affected | IECC 2012 Section(s) affected | Affected Items | Small Office | Large Office | Standalone Retail | Primary School | Small Hotel | Mid-rise Apartment | 2A Houston | 3A Memphis | 3B El Paso | 4A Baltimore | 5A Chicago | Not Used | Interior Lighting Power Density | Not Used | Costs to provide lighting fixtures, lamps and ballasts to meet space by space lighting power density (LPD) maximum allowed LPD values under IECC 2009. Fixtures, lamps and ballasts and quantities defined from 90.1 development interior lighting models and additional input from 90.1 Lighting Subcommittee. Costs are for equipment etc. at today's prices that just meet the IECC 2009 requirements. Costs by IECC 2009 Prototype and Lighting Space Type | IECC 2009 Allowed Maximum LPD W/ft2 | Fixture ID Numbers | Annual Full Load Equivalent Operating Hours for Space Type Lamp Life for Fixtures (Used to Calculate Replacement Life) | Area of Space Type In Prototype Models | Costs to provide lighting fixtures, lamps and ballasts to meet space by space maximum allowed LPD values under IECC 2012 Table 9.6.1. Fixtures, lamps and ballasts and quantities defined from 90.1 development interior lighting models and additional input from 90.1 Lighting Subcommittee. Costs by IECC 2012 Prototype and Lighting Space Type | IECC 2012 Allowed Maximum LPD W/ft2 | Fixture ID Numbers | Annual Full Load Equivalent (FLE) Operating Hours | Area of Space Type, ft2 | Not Used | Material Cost/ft2 | Material Subtotal Cost/ft2 × area for space type | Labor Crew Type Not Used | Labor Cost/ft2 | Labor Subtotal Cost/ft2 × Area | Construction Equipment Subtotal | Cost Adjustments | Not Used | Not Used | Total | Replacement Life (hours of operation/ component life) | Replacement Period (costs assigned to a 1 year period) | Material Cost/ft2 | Material Subtotal Cost/ft2 × area for space type | Labor Crew Type Not Used | Labor Cost/ft2 | Labor Subtotal Cost/ft2 × Area | Construction Equipment Subtotal | Cost Adjustments | Not Used | Subtotal | Total (adjusted for actual quantity of replacements in replacement period) | Material Cost/ft2 | Material Subtotal Cost/ft2 × area for space type | Labor Crew Type Not Used | Labor Cost/ft2 | Labor Subtotal Cost/ft2 × Area | Construction Equipment Subtotal | Cost Adjustments | Not Used | Not Used | Total | Replacement Life (hours of operation/ component life) | Replacement Period (costs assigned to a 1 year period) | Material Cost/ft2 | Material Subtotal Cost/ft2 × area for space type | Labor Crew Type Not Used | Labor Cost/ft2 | Labor Subtotal Cost/ft2 × Area | Construction Equipment Subtotal | Cost Adjustments | Incremental Added Design with OH&P | Subtotal | Total (adjusted for actual quantity of replacements in replacement period) | New Construction Costs 2010 minus 2007 | Category | All Costs, First Replacement Only | With Repeated Replacements | Category | Replacement First Year | With Repeated Replacements | 30 Year | 40 Year | Category | All Costs, First Replacement Only | With Repeated Replacements | Category | Replacement First Year | With Repeated Replacements | 30 Year | 40 Year | Category | All Costs, First Replacement Only | With Repeated Replacements | Category | Replacement First Year | With Repeated Replacements | 30 Year | 40 Year | Category | All Costs, First Replacement Only | With Repeated Replacements | Category | Replacement First Year | With Repeated Replacements | 30 Year | 40 Year | Category | All Costs, First Replacement Only | With Repeated Replacements | Category | Replacement First Year | With Repeated Replacements | 30 Year | 40 Year | Category | All Costs, First Replacement Only | With Repeated Replacements | Category | Replacement First Year | With Repeated Replacements | 30 Year | 40 Year
[6 empty] | n | [5 empty] | X | X | X | X | X |  | Small _Office_Interior_Lighting_LPD |  | Small Office |  |  | 3642 |  | Small Office |  |  | 3642 | [47 empty] | New Construction | 0 | 0 | New Construction | 0 | 0 | 0 | 0 | New Construction | 0 | 0 | New Construction | 0 | 0 | 0 | 0 | New Construction | 0 | 0 | New Construction | 0 | 0 | 0 | 0 | New Construction | 0 | 0 | New Construction | 0 | 0 | 0 | 0 | New Construction | 0 | 0 | New Construction | 0 | 0 | 0 | 0 | New Construction | 0 | 0 | New Construction | 0 | 0 | 0 | 0
Office - Open Plan (Including Other) | Office - Open Plan (Including Other) |  |  |  |  | n | [13 empty] | Office - Open Plan (Including Other) | 0.979 |  |  | 1100 | Office - Open Plan (Including Other) | 0.9555 |  |  | 1100 | [46 empty] | Maintenance | 0 | 0 | Maintenance | 0 | 0 | 0 | 0 | Maintenance | 0 | 0 | Maintenance | 0 | 0 | 0 | 0 | Maintenance | 0 | 0 | Maintenance | 0 | 0 | 0 | 0 | Maintenance | 0 | 0 | Maintenance | 0 | 0 | 0 | 0 | Maintenance | 0 | 0 | Maintenance | 0 | 0 | 0 | 0 | Maintenance | 0 | 0 | Maintenance | 0 | 0 | 0 | 0
Office - Open Plan (Including Other)535 | Office - Open Plan (Including Other)535 |  |  |  |  | n | [13 empty] | replacement costs shown are for lamps |  | 535 |  | 1100 |  |  | 535 |  | 1100 |  | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  | #N/A | #N/A | #N/A | Replacement - Year |  |  | Replacement - Year |  |  | 0 | 0 | Replacement - Year |  |  | Replacement - Year |  |  | 0 | 0 | Replacement - Year |  |  | Replacement - Year |  |  | 0 | 0 | Replacement - Year |  |  | Replacement - Year |  |  | 0 | 0 | Replacement - Year |  |  | Replacement - Year |  |  | 0 | 0 | Replacement - Year |  |  | Replacement - Year |  |  | 0 | 0
Office - Open Plan (Including Other)539 | Office - Open Plan (Including Other)539 |  |  |  |  | n | [15 empty] | 539 |  | 1100 |  |  | 539 |  | 1100 |  | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  | #N/A | #N/A | #N/A | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 0
Office - Open Plan (Including Other)524 | Office - Open Plan (Including Other)0 |  |  |  |  | n | [15 empty] | 524 |  | 1100 |  |  | 0 |  | 1100 |  | 0.1289 | 141.7945 |  | 0.088409 | 97.2495 |  | 164.9738 |  |  | 404.0179 | 2.7457 | 3 | 0.045139 | 49.6526 |  | 0.0083377 | 9.1715 |  | 42.3456 |  | 101.1697 | 110.538 | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | 0 | 0 | 0 | 0 |  | #N/A | #N/A |  | #N/A |  | #N/A | 0 | #N/A | 2 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 0 | 0
Office - Open Plan (Including Other) | Office - Open Plan (Including Other)537-1 |  |  |  |  | n | [20 empty] | 537-1 |  | 1100 | [23 empty] | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  | #N/A | #N/A | #N/A | 3 | 0 | 0 | 3 | 0 | 0 | 0 | 0 | 3 | 0 | 0 | 3 | 0 | 0 | 0 | 0 | 3 | 0 | 0 | 3 | 0 | 0 | 0 | 0 | 3 | 0 | 0 | 3 | 0 | 0 | 0 | 0 | 3 | 0 | 0 | 3 | 0 | 0 | 0 | 0 | 3 | 0 | 0 | 3 | 0 | 0 | 0 | 0
Office - Open Plan (Including Other)535 | Office - Open Plan (Including Other)535 |  |  |  |  | n | [13 empty] | ballast replacement |  | 535 |  | 1100 |  |  | 535 |  | 1100 | [11 empty] | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  | #N/A | #N/A | [10 empty] | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  | #N/A | #N/A | 0 | 4 | 0 | 0 | 4 | 0 | 0 | 0 | 0 | 4 | 0 | 0 | 4 | 0 | 0 | 0 | 0 | 4 | 0 | 0 | 4 | 0 | 0 | 0 | 0 | 4 | 0 | 0 | 4 | 0 | 0 | 0 | 0 | 4 | 0 | 0 | 4 | 0 | 0 | 0 | 0 | 4 | 0 | 0 | 4 | 0 | 0 | 0 | 0
Office - Open Plan (Including Other)539 | Office - Open Plan (Including Other)539 |  |  |  |  | n | [15 empty] | 539 |  | 1100 |  |  | 539 |  | 1100 | [11 empty] | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  | #N/A | #N/A | [10 empty] | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  | #N/A | #N/A | 0 | 5 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 5 | 0 | 0 | 0 | 0
Office - Open Plan (Including Other)524 | Office - Open Plan (Including Other)0 |  |  |  |  | n | [15 empty] | 524 |  | 1100 |  |  | 0 |  | 1100 | [11 empty] | 13.7287 | 14 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | [10 empty] | #N/A | #N/A | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | #N/A | 0 | 6 | 0 | 0 | 6 | 0 | 0 | 0 | 0 | 6 | 0 | 0 | 6 | 0 | 0 | 0 | 0 | 6 | 0 | 0 | 6 | 0 | 0 | 0 | 0 | 6 | 0 | 0 | 6 | 0 | 0 | 0 | 0 | 6 | 0 | 0 | 6 | 0 | 0 | 0 | 0 | 6 | 0 | 0 | 6 | 0 | 0 | 0 | 0
Office - Open Plan (Including Other) | Office - Open Plan (Including Other)537-1 |  |  |  |  | n | [20 empty] | 537-1 |  | 1100 | [33 empty] | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  | #N/A | #N/A | 0 | 7 | 0 | 0 | 7 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 7 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 7 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 7 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 7 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 7 | 0 | 0 | 0 | 0
Office-Enclosed | Office-Enclosed |  |  |  |  | n | [13 empty] | Office-Enclosed | 1.1 |  |  | 1595 | Office-Enclosed | 1.0822 |  |  | 1595 | [46 empty] | 8 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 8 | 0 | 0 | 0 | 0
Office-Enclosed535 | Office-Enclosed531 |  |  |  |  | n | [13 empty] | lamp replacement |  | 535 |  | 1595 |  |  | 531 |  | 1595 |  | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  | #N/A | #N/A | #N/A | 9 | 0 | 0 | 9 | 0 | 0 | 0 | 0 | 9 | 0 | 0 | 9 | 0 | 0 | 0 | 0 | 9 | 0 | 0 | 9 | 0 | 0 | 0 | 0 | 9 | 0 | 0 | 9 | 0 | 0 | 0 | 0 | 9 | 0 | 0 | 9 | 0 | 0 | 0 | 0 | 9 | 0 | 0 | 9 | 0 | 0 | 0 | 0
Office-Enclosed539 | Office-Enclosed539 |  |  |  |  | n | [15 empty] | 539 |  | 1595 |  |  | 539 |  | 1595 |  | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  | #N/A | #N/A | #N/A | 10 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 10 | 0 | 0 | 0 | 0
Office-Enclosed537-2 | Office-Enclosed0 |  |  |  |  | n | [15 empty] | 537-2 |  | 1595 |  |  | 0 |  | 1595 |  | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | 0 | 0 | 0 | 0 |  | #N/A | #N/A |  | #N/A |  | #N/A | 0 | #N/A | 11 | 0 | 0 | 11 | 0 | 0 | 0 | 0 | 11 | 0 | 0 | 11 | 0 | 0 | 0 | 0 | 11 | 0 | 0 | 11 | 0 | 0 | 0 | 0 | 11 | 0 | 0 | 11 | 0 | 0 | 0 | 0 | 11 | 0 | 0 | 11 | 0 | 0 | 0 | 0 | 11 | 0 | 0 | 11 | 0 | 0 | 0 | 0
Office-Enclosed | Office-Enclosed537-1 |  |  |  |  | n | [20 empty] | 537-1 |  | 1595 | [23 empty] | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  | #N/A | #N/A | #N/A | 12 | 0 | 0 | 12 | 0 | 0 | 0 | 0 | 12 | 0 | 0 | 12 | 0 | 0 | 0 | 0 | 12 | 0 | 0 | 12 | 0 | 0 | 0 | 0 | 12 | 0 | 0 | 12 | 0 | 0 | 0 | 0 | 12 | 0 | 0 | 12 | 0 | 0 | 0 | 0 | 12 | 0 | 0 | 12 | 0 | 0 | 0 | 0
Office-Enclosed535 | Office-Enclosed531 |  |  |  |  | n | [13 empty] | ballast replacement |  | 535 |  | 1595 |  |  | 531 |  | 1595 | [11 empty] | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  | #N/A | #N/A | [10 empty] | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  | #N/A | #N/A | 0 | 13 | 0 | 0 | 13 | 0 | 0 | 0 | 0 | 13 | 0 | 0 | 13 | 0 | 0 | 0 | 0 | 13 | 0 | 0 | 13 | 0 | 0 | 0 | 0 | 13 | 0 | 0 | 13 | 0 | 0 | 0 | 0 | 13 | 0 | 0 | 13 | 0 | 0 | 0 | 0 | 13 | 0 | 0 | 13 | 0 | 0 | 0 | 0
Office-Enclosed539 | Office-Enclosed539 |  |  |  |  | n | [15 empty] | 539 |  | 1595 |  |  | 539 |  | 1595 | [11 empty] | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  | #N/A | #N/A | [10 empty] | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  | #N/A | #N/A | 0 | 14 | 0 | 0 | 14 | 0 | 0 | 0 | 0 | 14 | 0 | 0 | 14 | 0 | 0 | 0 | 0 | 14 | 0 | 0 | 14 | 0 | 0 | 0 | 0 | 14 | 0 | 0 | 14 | 0 | 0 | 0 | 0 | 14 | 0 | 0 | 14 | 0 | 0 | 0 | 0 | 14 | 0 | 0 | 14 | 0 | 0 | 0 | 0
Office-Enclosed537-2 | Office-Enclosed0 |  |  |  |  | n | [15 empty] | 537-2 |  | 1595 |  |  | 0 |  | 1595 | [11 empty] | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  | #N/A | #N/A | [10 empty] | #N/A | #N/A | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | #N/A | 0 | 15 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 15 | 0 | 0 | 0 | 0
Office-Enclosed | Office-Enclosed537-1 |  |  |  |  | n | [20 empty] | 537-1 |  | 1595 | [33 empty] | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  | #N/A | #N/A | 0 | 16 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 16 | 0 | 0 | 0 | 0
Conference/Meeting/Multipurpose | Conference/Meeting/Multipurpose |  |  |  |  | n | [13 empty] | Conference/Meeting/Multipurpose | 1.3 |  |  | 550 | Conference/Meeting/Multipurpose | 1.1992 |  |  | 550 | [46 empty] | 17 | 0 | 0 | 17 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 17 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 17 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 17 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 17 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 17 | 0 | 0 | 0 | 0
Conference/Meeting/Multipurpose535 | Conference/Meeting/Multipurpose535 |  |  |  |  | n | [13 empty] | lamp replacement |  | 535 |  | 550 |  |  | 535 |  | 550 |  | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  | #N/A | #N/A | #N/A | 18 | 0 | 0 | 18 | 0 | 0 | 0 | 0 | 18 | 0 | 0 | 18 | 0 | 0 | 0 | 0 | 18 | 0 | 0 | 18 | 0 | 0 | 0 | 0 | 18 | 0 | 0 | 18 | 0 | 0 | 0 | 0 | 18 | 0 | 0 | 18 | 0 | 0 | 0 | 0 | 18 | 0 | 0 | 18 | 0 | 0 | 0 | 0
Conference/Meeting/Multipurpose537-1 | Conference/Meeting/Multipurpose511 |  |  |  |  | n | [15 empty] | 537-1 |  | 550 |  |  | 511 |  | 550 |  | 1.2016 | 660.8865 |  | 0.71352 | 392.4353 |  | 710.1892 |  |  | 1763.511 | 9.8847 | 10 | 0.038866 | 21.3766 |  | 0.063425 | 34.8836 |  | 51.963 |  | 108.2232 | 109.4858 | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  | #N/A | #N/A | #N/A | 19 | 0 | 0 | 19 | 0 | 0 | 0 | 0 | 19 | 0 | 0 | 19 | 0 | 0 | 0 | 0 | 19 | 0 | 0 | 19 | 0 | 0 | 0 | 0 | 19 | 0 | 0 | 19 | 0 | 0 | 0 | 0 | 19 | 0 | 0 | 19 | 0 | 0 | 0 | 0 | 19 | 0 | 0 | 19 | 0 | 0 | 0 | 0
Conference/Meeting/Multipurpose511 | Conference/Meeting/Multipurpose0 |  |  |  |  | n | [15 empty] | 511 |  | 550 |  |  | 0 |  | 550 |  | 0.14187 | 78.0268 |  | 0.2353 | 129.4133 |  | 164.0613 |  |  | 371.5014 | 1.1532 | 2 | 0.081799 | 44.9895 |  | 0.011134 | 6.1235 |  | 35.9844 |  | 87.0974 | 151.0517 | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | 0 | 0 | 0 | 0 |  | #N/A | #N/A |  | #N/A |  | #N/A | 0 | #N/A | 20 | 0 | 0 | 20 | 0 | 0 | 0 | 0 | 20 | 0 | 0 | 20 | 0 | 0 | 0 | 0 | 20 | 0 | 0 | 20 | 0 | 0 | 0 | 0 | 20 | 0 | 0 | 20 | 0 | 0 | 0 | 0 | 20 | 0 | 0 | 20 | 0 | 0 | 0 | 0 | 20 | 0 | 0 | 20 | 0 | 0 | 0 | 0
Conference/Meeting/Multipurpose | Conference/Meeting/Multipurpose527-1 |  |  |  |  | n | [20 empty] | 527-1 |  | 550 | [23 empty] | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  | #N/A | #N/A | #N/A | 21 | 0 | 0 | 21 | 0 | 0 | 0 | 0 | 21 | 0 | 0 | 21 | 0 | 0 | 0 | 0 | 21 | 0 | 0 | 21 | 0 | 0 | 0 | 0 | 21 | 0 | 0 | 21 | 0 | 0 | 0 | 0 | 21 | 0 | 0 | 21 | 0 | 0 | 0 | 0 | 21 | 0 | 0 | 21 | 0 | 0 | 0 | 0
Conference/Meeting/Multipurpose535 | Conference/Meeting/Multipurpose535 |  |  |  |  | n | [13 empty] | ballast replacement |  | 535 |  | 550 |  |  | 535 |  | 550 | [11 empty] | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  | #N/A | #N/A | [10 empty] | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  | #N/A | #N/A | 0 | 22 | 0 | 0 | 22 | 0 | 0 | 0 | 0 | 22 | 0 | 0 | 22 | 0 | 0 | 0 | 0 | 22 | 0 | 0 | 22 | 0 | 0 | 0 | 0 | 22 | 0 | 0 | 22 | 0 | 0 | 0 | 0 | 22 | 0 | 0 | 22 | 0 | 0 | 0 | 0 | 22 | 0 | 0 | 22 | 0 | 0 | 0 | 0
Conference/Meeting/Multipurpose537-1 | Conference/Meeting/Multipurpose511 |  |  |  |  | n | [15 empty] | 537-1 |  | 550 |  |  | 511 |  | 550 | [11 empty] | 13.7287 | 14 | 0.34806 | 191.4318 |  | 0.71352 | 392.4353 |  | 552.6238 |  | 1136.4909 | 1158.9479 | [10 empty] | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  | #N/A | #N/A | 0 | 23 | 0 | 0 | 23 | 0 | 0 | 0 | 0 | 23 | 0 | 0 | 23 | 0 | 0 | 0 | 0 | 23 | 0 | 0 | 23 | 0 | 0 | 0 | 0 | 23 | 0 | 0 | 23 | 0 | 0 | 0 | 0 | 23 | 0 | 0 | 23 | 0 | 0 | 0 | 0 | 23 | 0 | 0 | 23 | 0 | 0 | 0 | 0
Conference/Meeting/Multipurpose511 | Conference/Meeting/Multipurpose0 |  |  |  |  | n | [15 empty] | 511 |  | 550 |  |  | 0 |  | 550 | [11 empty] | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | [10 empty] | #N/A | #N/A | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | #N/A | 0 | 24 | 0 | 0 | 24 | 0 | 0 | 0 | 0 | 24 | 0 | 0 | 24 | 0 | 0 | 0 | 0 | 24 | 0 | 0 | 24 | 0 | 0 | 0 | 0 | 24 | 0 | 0 | 24 | 0 | 0 | 0 | 0 | 24 | 0 | 0 | 24 | 0 | 0 | 0 | 0 | 24 | 0 | 0 | 24 | 0 | 0 | 0 | 0
Conference/Meeting/Multipurpose | Conference/Meeting/Multipurpose527-1 |  |  |  |  | n | [20 empty] | 527-1 |  | 550 | [33 empty] | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  | #N/A | #N/A | 0 | 25 | 0 | 0 | 25 | 0 | 0 | 0 | 0 | 25 | 0 | 0 | 25 | 0 | 0 | 0 | 0 | 25 | 0 | 0 | 25 | 0 | 0 | 0 | 0 | 25 | 0 | 0 | 25 | 0 | 0 | 0 | 0 | 25 | 0 | 0 | 25 | 0 | 0 | 0 | 0 | 25 | 0 | 0 | 25 | 0 | 0 | 0 | 0
Corridor/Transition | Corridor/Transition |  |  |  |  | n | [13 empty] | Corridor/Transition | 0.5 |  |  | 660 | Corridor/Transition | 0.6435 |  |  | 660 | [46 empty] | 26 | 0 | 0 | 26 | 0 | 0 | 0 | 0 | 26 | 0 | 0 | 26 | 0 | 0 | 0 | 0 | 26 | 0 | 0 | 26 | 0 | 0 | 0 | 0 | 26 | 0 | 0 | 26 | 0 | 0 | 0 | 0 | 26 | 0 | 0 | 26 | 0 | 0 | 0 | 0 | 26 | 0 | 0 | 26 | 0 | 0 | 0 | 0
Corridor/Transition530 | Corridor/Transition521 |  |  |  |  | n | [13 empty] | replacement costs are for lamps |  | 530 |  | 660 |  |  | 521 |  | 660 |  | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  | #N/A | #N/A | #N/A | 27 | 0 | 0 | 27 | 0 | 0 | 0 | 0 | 27 | 0 | 0 | 27 | 0 | 0 | 0 | 0 | 27 | 0 | 0 | 27 | 0 | 0 | 0 | 0 | 27 | 0 | 0 | 27 | 0 | 0 | 0 | 0 | 27 | 0 | 0 | 27 | 0 | 0 | 0 | 0 | 27 | 0 | 0 | 27 | 0 | 0 | 0 | 0
Corridor/Transition537-2 | Corridor/Transition0 |  |  |  |  | n | [15 empty] | 537-2 |  | 660 |  |  | 0 |  | 660 |  | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | 0 | 0 | 0 | 0 |  | #N/A | #N/A |  | #N/A |  | #N/A | 0 | #N/A | 28 | 0 | 0 | 28 | 0 | 0 | 0 | 0 | 28 | 0 | 0 | 28 | 0 | 0 | 0 | 0 | 28 | 0 | 0 | 28 | 0 | 0 | 0 | 0 | 28 | 0 | 0 | 28 | 0 | 0 | 0 | 0 | 28 | 0 | 0 | 28 | 0 | 0 | 0 | 0 | 28 | 0 | 0 | 28 | 0 | 0 | 0 | 0
Corridor/Transition0 | Corridor/Transition0 |  |  |  |  | n | [15 empty] | 0 |  | 660 |  |  | 0 |  | 660 |  | 0 | 0 |  | 0 | 0 |  | 0 |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | 0 | 0 | 0 | 0 |  | #N/A | #N/A |  | #N/A |  | #N/A | 0 | #N/A | 29 | 0 | 0 | 29 | 0 | 0 | 0 | 0 | 29 | 0 | 0 | 29 | 0 | 0 | 0 | 0 | 29 | 0 | 0 | 29 | 0 | 0 | 0 | 0 | 29 | 0 | 0 | 29 | 0 | 0 | 0 | 0 | 29 | 0 | 0 | 29 | 0 | 0 | 0 | 0 | 29 | 0 | 0 | 29 | 0 | 0 | 0 | 0
Corridor/Transition | Corridor/Transition527-2 |  |  |  |  | n | [20 empty] | 0 |  | 660 | [23 empty] | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | 0 | 0 | 0 | 0 |  | #N/A | #N/A |  | #N/A |  | #N/A | 0 | #N/A | 30 | 0 | 0 | 30 | 0 | 0 | 0 | 0 | 30 | 0 | 0 | 30 | 0 | 0 | 0 | 0 | 30 | 0 | 0 | 30 | 0 | 0 | 0 | 0 | 30 | 0 | 0 | 30 | 0 | 0 | 0 | 0 | 30 | 0 | 0 | 30 | 0 | 0 | 0 | 0 | 30 | 0 | 0 | 30 | 0 | 0 | 0 | 0
Corridor/Transition530 | Corridor/Transition521 |  |  |  |  | n | [13 empty] | replacement costs are for ballasts |  | 530 |  | 660 |  |  | 521 |  | 660 | [11 empty] | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  | #N/A | #N/A | [10 empty] | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  | #N/A | #N/A | 0 | 31 | 0 | 0 | 31 | 0 | 0 |  | 0 | 31 | 0 | 0 | 31 | 0 | 0 |  | 0 | 31 | 0 | 0 | 31 | 0 | 0 |  | 0 | 31 | 0 | 0 | 31 | 0 | 0 |  | 0 | 31 | 0 | 0 | 31 | 0 | 0 |  | 0 | 31 | 0 | 0 | 31 | 0 | 0 |  | 0
Corridor/Transition537-2 | Corridor/Transition0 |  |  |  |  | n | [15 empty] | 537-2 |  | 660 |  |  | 0 |  | 660 | [11 empty] | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  | #N/A | #N/A | [10 empty] | #N/A | #N/A | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | #N/A | 0 | 32 | 0 | 0 | 32 | 0 | 0 |  | 0 | 32 | 0 | 0 | 32 | 0 | 0 |  | 0 | 32 | 0 | 0 | 32 | 0 | 0 |  | 0 | 32 | 0 | 0 | 32 | 0 | 0 |  | 0 | 32 | 0 | 0 | 32 | 0 | 0 |  | 0 | 32 | 0 | 0 | 32 | 0 | 0 |  | 0
Corridor/Transition0 | Corridor/Transition0 |  |  |  |  | n | [15 empty] | 0 |  | 660 |  |  | 0 |  | 660 | [11 empty] | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | [10 empty] | #N/A | #N/A | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | #N/A | 0 | 33 | 0 | 0 | 33 | 0 | 0 |  | 0 | 33 | 0 | 0 | 33 | 0 | 0 |  | 0 | 33 | 0 | 0 | 33 | 0 | 0 |  | 0 | 33 | 0 | 0 | 33 | 0 | 0 |  | 0 | 33 | 0 | 0 | 33 | 0 | 0 |  | 0 | 33 | 0 | 0 | 33 | 0 | 0 |  | 0
Corridor/Transition | Corridor/Transition527-2 |  |  |  |  | n | [20 empty] | 0 |  | 660 | [33 empty] | #N/A | #N/A | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | #N/A | 0 | 34 | 0 | 0 | 34 | 0 | 0 |  | 0 | 34 | 0 | 0 | 34 | 0 | 0 |  | 0 | 34 | 0 | 0 | 34 | 0 | 0 |  | 0 | 34 | 0 | 0 | 34 | 0 | 0 |  | 0 | 34 | 0 | 0 | 34 | 0 | 0 |  | 0 | 34 | 0 | 0 | 34 | 0 | 0 |  | 0
Conference/Meeting/Multipurpose | Conference/Meeting/Multipurpose |  |  |  |  | n | [13 empty] | Conference/Meeting/Multipurpose | 1.3 |  |  | 440 | Conference/Meeting/Multipurpose |  |  |  | 550 | [46 empty] | 35 | 0 | 0 | 35 | 0 | 0 |  | 0 | 35 | 0 | 0 | 35 | 0 | 0 |  | 0 | 35 | 0 | 0 | 35 | 0 | 0 |  | 0 | 35 | 0 | 0 | 35 | 0 | 0 |  | 0 | 35 | 0 | 0 | 35 | 0 | 0 |  | 0 | 35 | 0 | 0 | 35 | 0 | 0 |  | 0
Conference/Meeting/Multipurpose535 | Conference/Meeting/Multipurpose535 |  |  |  |  | n | [13 empty] | replacement costs are for lamps |  | 535 |  | 440 |  |  | 535 |  | 550 |  | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  | #N/A | #N/A | #N/A | 36 | 0 | 0 | 36 | 0 | 0 |  | 0 | 36 | 0 | 0 | 36 | 0 | 0 |  | 0 | 36 | 0 | 0 | 36 | 0 | 0 |  | 0 | 36 | 0 | 0 | 36 | 0 | 0 |  | 0 | 36 | 0 | 0 | 36 | 0 | 0 |  | 0 | 36 | 0 | 0 | 36 | 0 | 0 |  | 0
Conference/Meeting/Multipurpose537-1 | Conference/Meeting/Multipurpose511 |  |  |  |  | n | [15 empty] | 537-1 |  | 440 |  |  | 511 |  | 550 |  | 1.2016 | 528.7092 |  | 0.71352 | 313.9482 |  | 568.1513 |  |  | 1410.8088 | 9.8847 | 10 | 0.038866 | 17.1012 |  | 0.063425 | 27.9069 |  | 41.5704 |  | 86.5785 | 87.5886 | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  | #N/A | #N/A | #N/A | 37 | 0 | 0 | 37 | 0 | 0 |  | 0 | 37 | 0 | 0 | 37 | 0 | 0 |  | 0 | 37 | 0 | 0 | 37 | 0 | 0 |  | 0 | 37 | 0 | 0 | 37 | 0 | 0 |  | 0 | 37 | 0 | 0 | 37 | 0 | 0 |  | 0 | 37 | 0 | 0 | 37 | 0 | 0 |  | 0
Conference/Meeting/Multipurpose511 | Conference/Meeting/Multipurpose0 |  |  |  |  | n | [15 empty] | 511 |  | 440 |  |  | 0 |  | 550 |  | 0.14187 | 62.4214 |  | 0.2353 | 103.5307 |  | 131.249 |  |  | 297.2011 | 1.1532 | 2 | 0.081799 | 35.9916 |  | 0.011134 | 4.8988 |  | 28.7875 |  | 69.6779 | 120.8414 | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | 0 | 0 | 0 | 0 |  | #N/A | #N/A |  | #N/A |  | #N/A | 0 | #N/A | 38 | 0 | 0 | 38 | 0 | 0 |  | 0 | 38 | 0 | 0 | 38 | 0 | 0 |  | 0 | 38 | 0 | 0 | 38 | 0 | 0 |  | 0 | 38 | 0 | 0 | 38 | 0 | 0 |  | 0 | 38 | 0 | 0 | 38 | 0 | 0 |  | 0 | 38 | 0 | 0 | 38 | 0 | 0 |  | 0
Conference/Meeting/Multipurpose | Conference/Meeting/Multipurpose527-1 |  |  |  |  | n | [17 empty] | 440 |  |  | 527-1 |  | 550 | [23 empty] | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  | #N/A | #N/A | #N/A | 39 | 0 | 0 | 39 | 0 | 0 |  | 0 | 39 | 0 | 0 | 39 | 0 | 0 |  | 0 | 39 | 0 | 0 | 39 | 0 | 0 |  | 0 | 39 | 0 | 0 | 39 | 0 | 0 |  | 0 | 39 | 0 | 0 | 39 | 0 | 0 |  | 0 | 39 | 0 | 0 | 39 | 0 | 0 |  | 0
Conference/Meeting/Multipurpose535 | Conference/Meeting/Multipurpose535 |  |  |  |  | n | [13 empty] | ballast replacement |  | 535 |  | 440 |  |  | 535 |  | 550 | [11 empty] | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  | #N/A | #N/A | [10 empty] | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  | #N/A | #N/A | 0 | 40 | 0 | 0 | 40 | 0 | 0 |  | 0 | 40 | 0 | 0 | 40 | 0 | 0 |  | 0 | 40 | 0 | 0 | 40 | 0 | 0 |  | 0 | 40 | 0 | 0 | 40 | 0 | 0 |  | 0 | 40 | 0 | 0 | 40 | 0 | 0 |  | 0 | 40 | 0 | 0 | 40 | 0 | 0 |  | 0
Conference/Meeting/Multipurpose537-1 | Conference/Meeting/Multipurpose511 |  |  |  |  | n | [15 empty] | 537-1 |  | 440 |  |  | 511 |  | 550 | [11 empty] | 13.7287 | 14 | 0.34806 | 153.1455 |  | 0.71352 | 313.9482 |  | 442.099 |  | 909.1927 | 927.1583 | [10 empty] | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  | #N/A | #N/A | 0 | Residual Year 30 |  | 0 | Residual Year 30 |  | 0 |  | 0 | Residual Year 30 |  | 0 | Residual Year 30 |  | 0 |  | 0 | Residual Year 30 |  | 0 | Residual Year 30 |  | 0 |  | 0 | Residual Year 30 |  | 0 | Residual Year 30 |  | 0 |  | 0 | Residual Year 30 |  | 0 | Residual Year 30 |  | 0 |  | 0 | Residual Year 30 |  | 0 | Residual Year 30 |  | 0 |  | 0
Conference/Meeting/Multipurpose511 | Conference/Meeting/Multipurpose0 |  |  |  |  | n | [15 empty] | 511 |  | 440 |  |  | 0 |  | 550 | [11 empty] | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | [10 empty] | #N/A | #N/A | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | #N/A | 0 | Residual Year 40 |  | 0 | Residual Year 40 |  | 0 |  | 0 | Residual Year 40 |  | 0 | Residual Year 40 |  | 0 |  | 0 | Residual Year 40 |  | 0 | Residual Year 40 |  | 0 |  | 0 | Residual Year 40 |  | 0 | Residual Year 40 |  | 0 |  | 0 | Residual Year 40 |  | 0 | Residual Year 40 |  | 0 |  | 0 | Residual Year 40 |  | 0 | Residual Year 40 |  | 0 |  | 0
Conference/Meeting/Multipurpose | Conference/Meeting/Multipurpose527-1 |  |  |  |  | n | [17 empty] | 440 |  |  | 527-1 |  | 550 | [33 empty] | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  | #N/A | #N/A | 0
Storage | Storage |  |  |  |  | n | [13 empty] | Storage | 0.8 |  |  | 770 | Storage | 0.61425 |  |  | 770
Storage530 | Storage538 |  |  |  |  | n | [13 empty] | replacement costs are for lamps |  | 530 |  | 770 |  |  | 538 |  | 770 |  | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  | #N/A | #N/A | #N/A
Storage553 | Storage0 |  |  |  |  | n | [15 empty] | 0 |  | 770 |  |  | 0 |  | 770 |  | 0 | 0 |  | 0 | 0 |  | 0 |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | 0 | 0 | 0 | 0 |  | #N/A | #N/A |  | #N/A |  | #N/A | 0 | #N/A
Storage0 | Storage0 |  |  |  |  | n | [15 empty] | 0 |  | 770 |  |  | 0 |  | 770 |  | 0 | 0 |  | 0 | 0 |  | 0 |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | 0 | 0 | 0 | 0 |  | #N/A | #N/A |  | #N/A |  | #N/A | 0 | #N/A
Storage | Storage0 |  |  |  |  | n | [20 empty] | 0 |  | 770 | [23 empty] | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | 0 | 0 | 0 | 0 |  | #N/A | #N/A |  | #N/A |  | #N/A | 0 | #N/A
Storage530 | Storage538 |  |  |  |  | n | [13 empty] | ballast replacement |  | 530 |  | 770 |  |  | 538 |  | 770 | [11 empty] | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  | #N/A | #N/A | [10 empty] | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  | #N/A | #N/A | 0
Storage553 | Storage0 |  |  |  |  | n | [15 empty] | 0 |  | 770 |  |  | 0 |  | 770 | [11 empty] | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | [10 empty] | #N/A | #N/A | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | #N/A | 0
Storage0 | Storage0 |  |  |  |  | n | [15 empty] | 0 |  | 770 |  |  | 0 |  | 770 | [11 empty] | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | [10 empty] | #N/A | #N/A | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | #N/A | 0
Storage | Storage0 |  |  |  |  | n | [20 empty] | 0 |  | 770 | [33 empty] | #N/A | #N/A | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | #N/A | 0
Restrooms | Restrooms |  |  |  |  | n | [13 empty] | Restrooms | 0.9 |  |  | 220 | Restrooms | 0.9555 |  |  | 220
Restrooms521 | Restrooms604 |  |  |  |  | n | [13 empty] | replacement costs are for lamps |  | 521 |  | 220 |  |  | 604 |  | 220 |  | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  | #N/A | #N/A | #N/A
Restrooms537-1 | Restrooms520 |  |  |  |  | n | [15 empty] | 537-1 |  | 220 |  |  | 520 |  | 220 |  | 1.0833 | 238.3363 |  | 0.64329 | 141.5244 |  | 256.1164 |  |  | 635.9771 | 9.8847 | 10 | 0.035041 | 7.7091 |  | 0.057182 | 12.5801 |  | 18.7395 |  | 39.0287 | 39.484 | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  | #N/A | #N/A | #N/A
Restrooms524 | Restrooms0 |  |  |  |  | n | [15 empty] | 524 |  | 220 |  |  | 0 |  | 220 |  | 0.27528 | 60.5614 |  | 0.1888 | 41.5359 |  | 70.4614 |  |  | 172.5587 | 2.7457 | 3 | 0.096395 | 21.207 |  | 0.017805 | 3.9172 |  | 18.0861 |  | 43.2103 | 47.2115 | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | 0 | 0 | 0 | 0 |  | #N/A | #N/A |  | #N/A |  | #N/A | 0 | #N/A
Restrooms | Restrooms534-2 |  |  |  |  | n | [20 empty] | 534-2 |  | 220 | [23 empty] | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  | #N/A | #N/A | #N/A
Restrooms521 | Restrooms604 |  |  |  |  | n | [13 empty] | ballast replacement |  | 521 |  | 220 |  |  | 604 |  | 220 | [11 empty] | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  | #N/A | #N/A | [10 empty] | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  | #N/A | #N/A | 0
Restrooms537-1 | Restrooms520 |  |  |  |  | n | [15 empty] | 537-1 |  | 220 |  |  | 520 |  | 220 | [11 empty] | 13.7287 | 14 | 0.3138 | 69.0363 |  | 0.64329 | 141.5244 |  | 199.2934 |  | 409.8541 | 417.9528 | [10 empty] | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  | #N/A | #N/A | 0
Restrooms524 | Restrooms0 |  |  |  |  | n | [15 empty] | 524 |  | 220 |  |  | 0 |  | 220 | [11 empty] | 13.7287 | 14 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | [10 empty] | #N/A | #N/A | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | #N/A | 0
Restrooms | Restrooms534-2 |  |  |  |  | n | [20 empty] | 534-2 |  | 220 | [33 empty] | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  | #N/A | #N/A | 0
Lounge/Recreation - Break room | Lounge/Recreation - Break room |  |  |  |  | n | [13 empty] | Lounge/Recreation - Break room | 1.2 |  |  | 110 | Lounge/Recreation - Break room | 0.71175 |  |  | 110
Lounge/Recreation - Breakroom537-1 | Lounge/Recreation - Breakroom521 |  |  |  |  | n | [13 empty] | replacement costs are for lamps |  | 537-1 |  | 110 |  |  | 521 |  | 110 |  | 1.202 | 132.2253 |  | 0.71378 | 78.5156 |  | 142.0894 |  |  | 352.8303 | 9.8847 | 10 | 0.038881 | 4.2769 |  | 0.063448 | 6.9792 |  | 10.3964 |  | 21.6525 | 21.9051 | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  | #N/A | #N/A | #N/A
Lounge/Recreation - Breakroom572 | Lounge/Recreation - Breakroom0 |  |  |  |  | n | [15 empty] | 0 |  | 110 |  |  | 0 |  | 110 |  | 0 | 0 |  | 0 | 0 |  | 0 |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | 0 | 0 | 0 | 0 |  | #N/A | #N/A |  | #N/A |  | #N/A | 0 | #N/A
Lounge/Recreation - Breakroom521 | Lounge/Recreation - Breakroom0 |  |  |  |  | n | [15 empty] | 521 |  | 110 |  |  | 0 |  | 110 |  | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | 0 | 0 | 0 | 0 |  | #N/A | #N/A |  | #N/A |  | #N/A | 0 | #N/A
Lounge/Recreation - Break room | Lounge/Recreation - Breakroom527-2 |  |  |  |  | n | [17 empty] | 110 |  |  | 527-2 |  | 110 | [23 empty] | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  | #N/A | #N/A | #N/A
Lounge/Recreation - Breakroom537-1 | Lounge/Recreation - Breakroom521 |  |  |  |  | n | [13 empty] | ballast replacement |  | 537-1 |  | 110 |  |  | 521 |  | 110 | [11 empty] | 13.7287 | 14 | 0.34818 | 38.3003 |  | 0.71378 | 78.5156 |  | 110.5649 |  | 227.3808 | 231.8738 | [10 empty] | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  | #N/A | #N/A | 0
Lounge/Recreation - Breakroom572 | Lounge/Recreation - Breakroom0 |  |  |  |  | n | [15 empty] | 0 |  | 110 |  |  | 0 |  | 110 | [11 empty] | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | [10 empty] | #N/A | #N/A | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | #N/A | 0
Lounge/Recreation - Breakroom521 | Lounge/Recreation - Breakroom0 |  |  |  |  | n | [15 empty] | 521 |  | 110 |  |  | 0 |  | 110 | [11 empty] | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  | #N/A | #N/A | [10 empty] | #N/A | #N/A | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | #N/A | 0
Lounge/Recreation - Break room | Lounge/Recreation - Breakroom527-2 |  |  |  |  | n | [17 empty] | 110 |  |  | 527-2 |  | 110 | [33 empty] | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  | #N/A | #N/A | 0
Electrical/Mechanical | Electrical/Mechanical |  |  |  |  | n | [13 empty] | Electrical/Mechanical | 1.5 |  |  | 110 | Electrical/Mechanical | 0.92625 |  |  | 110
Electrical/Mechanical538 | Electrical/Mechanical538 |  |  |  |  | n | [13 empty] | replacement costs are for lamps |  | 538 |  | 110 |  |  | 538 |  | 110 |  | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  | #N/A | #N/A | #N/A
Electrical/Mechanical0 | Electrical/Mechanical0 |  |  |  |  | n | [15 empty] | 0 |  | 110 |  |  | 0 |  | 110 |  | 0 | 0 |  | 0 | 0 |  | 0 |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | 0 | 0 | 0 | 0 |  | #N/A | #N/A |  | #N/A |  | #N/A | 0 | #N/A
Electrical/Mechanical0 | Electrical/Mechanical0 |  |  |  |  | n | [15 empty] | 0 |  | 110 |  |  | 0 |  | 110 |  | 0 | 0 |  | 0 | 0 |  | 0 |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | 0 | 0 | 0 | 0 |  | #N/A | #N/A |  | #N/A |  | #N/A | 0 | #N/A
Electrical/Mechanical | Electrical/Mechanical0 |  |  |  |  | n | [17 empty] | 110 |  |  | 0 |  | 110 | [23 empty] | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | 0 | 0 | 0 | 0 |  | #N/A | #N/A |  | #N/A |  | #N/A | 0 | #N/A
Electrical/Mechanical538 | Electrical/Mechanical538 |  |  |  |  | n | [13 empty] | ballast replacement |  | 538 |  | 110 |  |  | 538 |  | 110 | [11 empty] | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  | #N/A | #N/A | [10 empty] | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  | #N/A | #N/A | 0
Electrical/Mechanical0 | Electrical/Mechanical0 |  |  |  |  | n | [15 empty] | 0 |  | 110 |  |  | 0 |  | 110 | [11 empty] | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | [10 empty] | #N/A | #N/A | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | #N/A | 0
Electrical/Mechanical0 | Electrical/Mechanical0 |  |  |  |  | n | [15 empty] | 0 |  | 110 |  |  | 0 |  | 110 | [11 empty] | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | [10 empty] | #N/A | #N/A | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | #N/A | 0
Electrical/Mechanical | Electrical/Mechanical0 |  |  |  |  | n | [17 empty] | 110 |  |  | 0 |  | 110 | [33 empty] | #N/A | #N/A | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | #N/A | 0
Stairway | Stairway |  |  |  |  | n | [13 empty] | Stairway | 0.6 |  |  | 165 | Stairway | 0.67275 |  |  | 165
Stairway530 | Stairway530 |  |  |  |  | n | [13 empty] | replacement costs are for lamps |  | 530 |  | 165 |  |  | 530 |  | 165 |  | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  | #N/A | #N/A | #N/A
Stairway0 | Stairway602 |  |  |  |  | n | [15 empty] | 0 |  | 165 |  |  | 602 |  | 165 |  | 0 | 0 |  | 0 | 0 |  | 0 |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  | #N/A | #N/A | #N/A
Stairway0 | Stairway0 |  |  |  |  | n | [15 empty] | 0 |  | 165 |  |  | 0 |  | 165 |  | 0 | 0 |  | 0 | 0 |  | 0 |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | 0 | 0 | 0 | 0 |  | #N/A | #N/A |  | #N/A |  | #N/A | 0 | #N/A
Stairway | Stairway0 |  |  |  |  | n | [17 empty] | 165 |  |  | 0 |  | 165 | [23 empty] | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | 0 | 0 | 0 | 0 |  | #N/A | #N/A |  | #N/A |  | #N/A | 0 | #N/A
Stairway530 | Stairway530 |  |  |  |  | n | [13 empty] | ballast replacement |  | 530 |  | 165 |  |  | 530 |  | 165 | [11 empty] | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  | #N/A | #N/A | [10 empty] | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  | #N/A | #N/A | 0
Stairway0 | Stairway602 |  |  |  |  | n | [15 empty] | 0 |  | 165 |  |  | 602 |  | 165 | [11 empty] | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | [10 empty] | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  | #N/A | #N/A | 0
Stairway0 | Stairway0 |  |  |  |  | n | [15 empty] | 0 |  | 165 |  |  | 0 |  | 165 | [11 empty] | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | [10 empty] | #N/A | #N/A | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | #N/A | 0
Stairway | Stairway0 |  |  |  |  | n | [17 empty] | 165 |  |  | 0 |  | 165 | [33 empty] | #N/A | #N/A | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | #N/A | 0
Lobby | Lobby |  |  |  |  | n | [13 empty] | Lobby | 1.3 |  |  | 330 | Lobby | 0.8775 |  |  | 330
Lobby534-2 | Lobby523 |  |  |  |  | n | [13 empty] | replacement costs are for lamps |  | 534-2 |  | 330 |  |  | 523 |  | 330 |  | 3.0412 | 1003.5935 |  | 0.46315 | 152.8407 |  | 650.6601 |  |  | 1807.0943 | 9.8847 | 10 | 0.026811 | 8.8475 |  | 0.043751 | 14.4378 |  | 21.5068 |  | 44.7921 | 45.3147 | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  | #N/A | #N/A | #N/A
Lobby523 | Lobby521 |  |  |  |  | n | [15 empty] | 523 |  | 330 |  |  | 521 |  | 330 |  | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  | #N/A | #N/A | #N/A
Lobby521 | Lobby0 |  |  |  |  | n | [15 empty] | 521 |  | 330 |  |  | 0 |  | 330 |  | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | 0 | 0 | 0 | 0 |  | #N/A | #N/A |  | #N/A |  | #N/A | 0 | #N/A
Lobby | Lobby534-2 |  |  |  |  | n | [17 empty] | 330 |  |  | 534-2 |  | 330 | [23 empty] | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  | #N/A | #N/A | #N/A
Lobby534-2 | Lobby523 |  |  |  |  | n | [13 empty] | ballast replacement |  | 534-2 |  | 330 |  |  | 523 |  | 330 | [11 empty] | 13.7287 | 14 | 0.24009 | 79.2311 |  | 0.49219 | 162.4237 |  | 228.7236 |  | 470.3783 | 479.673 | [10 empty] | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  | #N/A | #N/A | 0
Lobby523 | Lobby521 |  |  |  |  | n | [15 empty] | 523 |  | 330 |  |  | 521 |  | 330 | [11 empty] | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  | #N/A | #N/A | [10 empty] | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  | #N/A | #N/A | 0
Lobby521 | Lobby0 |  |  |  |  | n | [15 empty] | 521 |  | 330 |  |  | 0 |  | 330 | [11 empty] | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  | #N/A | #N/A | [10 empty] | #N/A | #N/A | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | #N/A | 0
Lobby | Lobby534-2 |  |  |  |  | n | [20 empty] | 534-2 |  | 330 | [33 empty] | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  | #N/A | #N/A | 0
n
[18 empty] | Large_Office_Interior Lighting LPD |  | Large Office |  |  | 2938 |  | Large Office |  |  | 2938
Office - Open Plan (Including Other) | Office - Open Plan (Including Other) | [18 empty] | Office - Open Plan (Including Other) | 1.1 |  |  | 285144 | Office - Open Plan (Including Other) | 0.97216 |  |  | 285144 | [27 empty] | 0
Office - Open Plan (Including Other)535 | Office - Open Plan (Including Other)535 | [5 empty] | n | [12 empty] | replacement costs are for lamps |  | 535 |  | 285144 |  |  | 535 |  | 285144 |  | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  | #N/A | #N/A | #N/A
Office - Open Plan (Including Other)539 | Office - Open Plan (Including Other)539 | [5 empty] | n | [14 empty] | 539 |  | 285144 |  |  | 539 |  | 285144 |  | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  | #N/A | #N/A | #N/A
Office - Open Plan (Including Other)524 | Office - Open Plan (Including Other)0 | [5 empty] | n | [14 empty] | 524 |  | 285144 |  |  | 0 |  | 285144 |  | 0.1289 | 36756.2384 |  | 0.088409 | 25209.1966 |  | 42764.8145 |  |  | 104730.2495 | 2.7457 | 3 | 0.045139 | 12871.037 |  | 0.0083377 | 2377.4527 |  | 10976.9092 |  | 26225.3988 | 28653.8707 | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | 0 | 0 | 0 | 0 |  | #N/A | #N/A |  | #N/A |  | #N/A | 0 | #N/A
Office - Open Plan (Including Other) | Office - Open Plan (Including Other)537-1 | [5 empty] | n | [19 empty] | 537-1 |  | 285144 | [23 empty] | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  | #N/A | #N/A | #N/A
Office - Open Plan (Including Other)535 | Office - Open Plan (Including Other)535 | [5 empty] | n | [12 empty] | ballast replacement |  | 535 |  | 285144 |  |  | 535 |  | 285144 | [11 empty] | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  | #N/A | #N/A | [10 empty] | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  | #N/A | #N/A | 0
Office - Open Plan (Including Other)539 | Office - Open Plan (Including Other)539 | [5 empty] | n | [14 empty] | 539 |  | 285144 |  |  | 539 |  | 285144 | [11 empty] | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  | #N/A | #N/A | [10 empty] | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  | #N/A | #N/A | 0
Office - Open Plan (Including Other)524 | Office - Open Plan (Including Other)0 | [5 empty] | n | [14 empty] | 524 |  | 285144 |  |  | 0 |  | 285144 | [11 empty] | 13.7287 | 14 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | [10 empty] | #N/A | #N/A | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | #N/A | 0
Office - Open Plan (Including Other) | Office - Open Plan (Including Other)537-1 | [5 empty] | n | [19 empty] | 537-1 |  | 285144 | [33 empty] | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  | #N/A | #N/A | 0
Office-Enclosed | Office-Enclosed | [5 empty] | n | [12 empty] | Office-Enclosed | 1.1 |  |  | 92363 | Office-Enclosed | 1.1011 |  |  | 92363 | [27 empty] | 0
Office-Enclosed535 | Office-Enclosed531 | [5 empty] | n | [12 empty] | replacement costs are for lamps |  | 535 |  | 92363 |  |  | 531 |  | 92363 |  | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  | #N/A | #N/A | #N/A
Office-Enclosed539 | Office-Enclosed539 | [5 empty] | n | [14 empty] | 539 |  | 92363 |  |  | 539 |  | 92363 |  | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  | #N/A | #N/A | #N/A
Office-Enclosed537-2 | Office-Enclosed0 | [5 empty] | n | [14 empty] | 537-2 |  | 92363 |  |  | 0 |  | 92363 |  | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | 0 | 0 | 0 | 0 |  | #N/A | #N/A |  | #N/A |  | #N/A | 0 | #N/A
Office-Enclosed | Office-Enclosed537-1 | [5 empty] | n | [19 empty] | 537-1 |  | 92363 | [23 empty] | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  | #N/A | #N/A | #N/A
Office-Enclosed535 | Office-Enclosed531 | [5 empty] | n | [12 empty] | ballast replacement |  | 535 |  | 92363 |  |  | 531 |  | 92363 | [11 empty] | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  | #N/A | #N/A | [10 empty] | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  | #N/A | #N/A | 0
Office-Enclosed539 | Office-Enclosed539 | [5 empty] | n | [14 empty] | 539 |  | 92363 |  |  | 539 |  | 92363 | [11 empty] | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  | #N/A | #N/A | [10 empty] | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  | #N/A | #N/A | 0
Office-Enclosed537-2 | Office-Enclosed0 | [5 empty] | n | [14 empty] | 537-2 |  | 92363 |  |  | 0 |  | 92363 | [11 empty] | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  | #N/A | #N/A | [10 empty] | #N/A | #N/A | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | #N/A | 0
Office-Enclosed | Office-Enclosed537-1 | [5 empty] | n | [19 empty] | 537-1 |  | 92363 | [33 empty] | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  | #N/A | #N/A | 0
Conference/Meeting/Multipurpose | Conference/Meeting/Multipurpose | [5 empty] | n | [12 empty] | Conference/Meeting/Multipurpose | 1.3 |  |  | 9628 | Conference/Meeting/Multipurpose | 1.2202 |  |  | 9628
Conference/Meeting/Multipurpose535 | Conference/Meeting/Multipurpose535 | [5 empty] | n | [12 empty] | replacement costs are for lamps |  | 535 |  | 9628 |  |  | 535 |  | 9628 |  | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  | #N/A | #N/A | #N/A
Conference/Meeting/Multipurpose537-1 | Conference/Meeting/Multipurpose511 | [5 empty] | n | [14 empty] | 537-1 |  | 9628 |  |  | 511 |  | 9628 |  | 1.2016 | 11569.1187 |  | 0.71352 | 6869.7577 |  | 12432.1845 |  |  | 30871.0609 | 9.8847 | 10 | 0.038866 | 374.2063 |  | 0.063425 | 610.6528 |  | 909.6367 |  | 1894.4958 | 1916.5982 | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  | #N/A | #N/A | #N/A
Conference/Meeting/Multipurpose511 | Conference/Meeting/Multipurpose0 | [5 empty] | n | [14 empty] | 511 |  | 9628 |  |  | 0 |  | 9628 |  | 0.14187 | 1365.8941 |  | 0.2353 | 2265.4392 |  | 2871.9673 |  |  | 6503.3006 | 1.1532 | 2 | 0.081799 | 787.5624 |  | 0.011134 | 107.194 |  | 629.9224 |  | 1524.6788 | 2644.2287 | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | 0 | 0 | 0 | 0 |  | #N/A | #N/A |  | #N/A |  | #N/A | 0 | #N/A
Conference/Meeting/Multipurpose | Conference/Meeting/Multipurpose527-1 | [5 empty] | n | [19 empty] | 527-1 |  | 9628 | [23 empty] | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  | #N/A | #N/A | #N/A
Conference/Meeting/Multipurpose535 | Conference/Meeting/Multipurpose535 | [5 empty] | n | [12 empty] | ballast replacement |  | 535 |  | 9628 |  |  | 535 |  | 9628 | [11 empty] | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  | #N/A | #N/A | [10 empty] | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  | #N/A | #N/A | 0
Conference/Meeting/Multipurpose537-1 | Conference/Meeting/Multipurpose511 | [5 empty] | n | [14 empty] | 537-1 |  | 9628 |  |  | 511 |  | 9628 | [11 empty] | 13.7287 | 14 | 0.34806 | 3351.1013 |  | 0.71352 | 6869.7577 |  | 9673.93 |  | 19894.789 | 20287.91 | [10 empty] | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  | #N/A | #N/A | 0
Conference/Meeting/Multipurpose511 | Conference/Meeting/Multipurpose0 | [5 empty] | n | [14 empty] | 511 |  | 9628 |  |  | 0 |  | 9628 | [11 empty] | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | [10 empty] | #N/A | #N/A | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | #N/A | 0
Conference/Meeting/Multipurpose | Conference/Meeting/Multipurpose527-1 | [5 empty] | n | [19 empty] | 527-1 |  | 9628 | [33 empty] | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  | #N/A | #N/A | 0
Corridor/Transition | Corridor/Transition | [5 empty] | n | [12 empty] | Corridor/Transition | 0.5 |  |  | 21304 | Corridor/Transition | 0.65472 |  |  | 21304
Corridor/Transition530 | Corridor/Transition521 | [5 empty] | n | [12 empty] | replacement costs are for lamps |  | 530 |  | 21304 |  |  | 521 |  | 21304 |  | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  | #N/A | #N/A | #N/A
Corridor/Transition537-2 | Corridor/Transition0 | [5 empty] | n | [14 empty] | 537-2 |  | 21304 |  |  | 0 |  | 21304 |  | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | 0 | 0 | 0 | 0 |  | #N/A | #N/A |  | #N/A |  | #N/A | 0 | #N/A
Corridor/Transition0 | Corridor/Transition0 | [5 empty] | n | [14 empty] | 0 |  | 21304 |  |  | 0 |  | 21304 |  | 0 | 0 |  | 0 | 0 |  | 0 |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | 0 | 0 | 0 | 0 |  | #N/A | #N/A |  | #N/A |  | #N/A | 0 | #N/A
Corridor/Transition | Corridor/Transition527-2 | [5 empty] | n | [19 empty] | 0 |  | 21304 | [23 empty] | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | 0 | 0 | 0 | 0 |  | #N/A | #N/A |  | #N/A |  | #N/A | 0 | #N/A
Corridor/Transition530 | Corridor/Transition521 | [5 empty] | n | [12 empty] | ballast replacement |  | 530 |  | 21304 |  |  | 521 |  | 21304 | [11 empty] | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  | #N/A | #N/A | [10 empty] | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  | #N/A | #N/A | 0
Corridor/Transition537-2 | Corridor/Transition0 | [5 empty] | n | [14 empty] | 537-2 |  | 21304 |  |  | 0 |  | 21304 | [11 empty] | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  | #N/A | #N/A | [10 empty] | #N/A | #N/A | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | #N/A | 0
Corridor/Transition0 | Corridor/Transition0 | [5 empty] | n | [14 empty] | 0 |  | 21304 |  |  | 0 |  | 21304 | [11 empty] | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | [10 empty] | #N/A | #N/A | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | #N/A | 0
Corridor/Transition | Corridor/Transition527-2 | [5 empty] | n | [19 empty] | 0 |  | 21304 | [33 empty] | #N/A | #N/A | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | #N/A | 0
Storage | Storage | [5 empty] | n | [12 empty] | Storage | 0.8 |  |  | 11866 | Storage | 0.62496 |  |  | 11866
Storage530 | Storage538 | [5 empty] | n | [12 empty] | replacement costs are for lamps |  | 530 |  | 11866 |  |  | 538 |  | 11866 |  | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  | #N/A | #N/A | #N/A
Storage553 | Storage0 | [5 empty] | n | [14 empty] | 0 |  | 11866 |  |  | 0 |  | 11866 |  | 0 | 0 |  | 0 | 0 |  | 0 |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | 0 | 0 | 0 | 0 |  | #N/A | #N/A |  | #N/A |  | #N/A | 0 | #N/A
Storage0 | Storage0 | [5 empty] | n | [14 empty] | 0 |  | 11866 |  |  | 0 |  | 11866 |  | 0 | 0 |  | 0 | 0 |  | 0 |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | 0 | 0 | 0 | 0 |  | #N/A | #N/A |  | #N/A |  | #N/A | 0 | #N/A
Storage | Storage0 | [5 empty] | n | [19 empty] | 0 |  | 11866 | [23 empty] | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | 0 | 0 | 0 | 0 |  | #N/A | #N/A |  | #N/A |  | #N/A | 0 | #N/A
Storage530 | Storage538 | [5 empty] | n | [12 empty] | ballast replacement |  | 530 |  | 11866 |  |  | 538 |  | 11866 | [11 empty] | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  | #N/A | #N/A | [10 empty] | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  | #N/A | #N/A | 0
Storage553 | Storage0 | [5 empty] | n | [14 empty] | 0 |  | 11866 |  |  | 0 |  | 11866 | [11 empty] | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | [10 empty] | #N/A | #N/A | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | #N/A | 0
Storage0 | Storage0 | [5 empty] | n | [14 empty] | 0 |  | 11866 |  |  | 0 |  | 11866 | [11 empty] | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | [10 empty] | #N/A | #N/A | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | #N/A | 0
Storage | Storage0 | [5 empty] | n | [19 empty] | 0 |  | 11866 | [33 empty] | #N/A | #N/A | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | #N/A | 0
Restrooms | Restrooms | [5 empty] | n | [12 empty] | Restrooms | 0.9 |  |  | 15505 | Restrooms | 0.97216 |  |  | 15505
Restrooms521 | Restrooms604 | [5 empty] | n | [12 empty] | replacement costs are for lamps |  | 521 |  | 15505 |  |  | 604 |  | 15505 |  | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  | #N/A | #N/A | #N/A
Restrooms537-1 | Restrooms520 | [5 empty] | n | [14 empty] | 537-1 |  | 15505 |  |  | 520 |  | 15505 |  | 1.0833 | 16797.2921 |  | 0.64329 | 9974.2538 |  | 18050.3839 |  |  | 44821.9297 | 9.8847 | 10 | 0.035041 | 543.313 |  | 0.057182 | 886.6114 |  | 1320.7085 |  | 2750.6329 | 2782.7236 | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  | #N/A | #N/A | #N/A
Restrooms524 | Restrooms0 | [5 empty] | n | [14 empty] | 524 |  | 15505 |  |  | 0 |  | 15505 |  | 0.27528 | 4268.2023 |  | 0.1888 | 2927.3385 |  | 4965.9293 |  |  | 12161.4701 | 2.7457 | 3 | 0.096395 | 1494.6086 |  | 0.017805 | 276.0742 |  | 1274.659 |  | 3045.3418 | 3327.3404 | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | 0 | 0 | 0 | 0 |  | #N/A | #N/A |  | #N/A |  | #N/A | 0 | #N/A
Restrooms | Restrooms534-2 | [5 empty] | n | [19 empty] | 534-2 |  | 15505 | [23 empty] | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  | #N/A | #N/A | #N/A
Restrooms521 | Restrooms604 | [5 empty] | n | [12 empty] | ballast replacement |  | 521 |  | 15505 |  |  | 604 |  | 15505 | [11 empty] | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  | #N/A | #N/A | [10 empty] | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  | #N/A | #N/A | 0
Restrooms537-1 | Restrooms520 | [5 empty] | n | [14 empty] | 537-1 |  | 15505 |  |  | 520 |  | 15505 | [11 empty] | 13.7287 | 14 | 0.3138 | 4865.4896 |  | 0.64329 | 9974.2538 |  | 14045.6531 |  | 28885.3965 | 29456.1719 | [10 empty] | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  | #N/A | #N/A | 0
Restrooms524 | Restrooms0 | [5 empty] | n | [14 empty] | 524 |  | 15505 |  |  | 0 |  | 15505 | [11 empty] | 13.7287 | 14 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | [10 empty] | #N/A | #N/A | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | #N/A | 0
Restrooms | Restrooms534-2 | [5 empty] | n | [19 empty] | 534-2 |  | 15505 | [33 empty] | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  | #N/A | #N/A | 0
Lounge/Recreation - Break room | Lounge/Recreation - Break room | [5 empty] | n | [12 empty] | Lounge/Recreation - Break room | 1.2 |  |  | 9530 | Lounge/Recreation - Break room | 0.72416 |  |  | 9530
Lounge/Recreation - Breakroom537-1 | Lounge/Recreation - Breakroom521 | [5 empty] | n | [12 empty] | replacement costs are for lamps |  | 537-1 |  | 9530 |  |  | 521 |  | 9530 |  | 1.202 | 11455.5216 |  | 0.71378 | 6802.3036 |  | 12310.113 |  |  | 30567.9381 | 9.8847 | 10 | 0.038881 | 370.532 |  | 0.063448 | 604.6568 |  | 900.705 |  | 1875.8937 | 1897.7791 | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  | #N/A | #N/A | #N/A
Lounge/Recreation - Breakroom572 | Lounge/Recreation - Breakroom0 | [5 empty] | n | [14 empty] | 0 |  | 9530 |  |  | 0 |  | 9530 |  | 0 | 0 |  | 0 | 0 |  | 0 |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | 0 | 0 | 0 | 0 |  | #N/A | #N/A |  | #N/A |  | #N/A | 0 | #N/A
Lounge/Recreation - Breakroom521 | Lounge/Recreation - Breakroom0 | [5 empty] | n | [14 empty] | 521 |  | 9530 |  |  | 0 |  | 9530 |  | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | 0 | 0 | 0 | 0 |  | #N/A | #N/A |  | #N/A |  | #N/A | 0 | #N/A
Lounge/Recreation - Breakroom | Lounge/Recreation - Breakroom527-2 | [5 empty] | n | [19 empty] | 527-2 |  | 9530 | [23 empty] | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  | #N/A | #N/A | #N/A
Lounge/Recreation - Breakroom537-1 | Lounge/Recreation - Breakroom521 | [5 empty] | n | [12 empty] | ballast replacement |  | 537-1 |  | 9530 |  |  | 521 |  | 9530 | [11 empty] | 13.7287 | 14 | 0.34818 | 3318.1969 |  | 0.71378 | 6802.3036 |  | 9578.9417 |  | 19699.4422 | 20088.7031 | [10 empty] | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  | #N/A | #N/A | 0
Lounge/Recreation - Breakroom572 | Lounge/Recreation - Breakroom0 | [5 empty] | n | [14 empty] | 0 |  | 9530 |  |  | 0 |  | 9530 | [11 empty] | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | [10 empty] | #N/A | #N/A | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | #N/A | 0
Lounge/Recreation - Breakroom521 | Lounge/Recreation - Breakroom0 | [5 empty] | n | [14 empty] | 521 |  | 9530 |  |  | 0 |  | 9530 | [11 empty] | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  | #N/A | #N/A | [10 empty] | #N/A | #N/A | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | #N/A | 0
Lounge/Recreation - Breakroom | Lounge/Recreation - Breakroom527-2 | [5 empty] | n | [19 empty] | 527-2 |  | 9530 | [33 empty] | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  | #N/A | #N/A | 0
Electrical/Mechanical | Electrical/Mechanical | [5 empty] | n | [12 empty] | Electrical/Mechanical | 1.5 |  |  | 31023 | Electrical/Mechanical | 0.9424 |  |  | 31023
Electrical/Mechanical538 | Electrical/Mechanical538 | [5 empty] | n | [12 empty] | replacement costs are for lamps |  | 538 |  | 31023 |  |  | 538 |  | 31023 |  | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  | #N/A | #N/A | #N/A
Electrical/Mechanical0 | Electrical/Mechanical0 | [5 empty] | n | [14 empty] | 0 |  | 31023 |  |  | 0 |  | 31023 |  | 0 | 0 |  | 0 | 0 |  | 0 |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | 0 | 0 | 0 | 0 |  | #N/A | #N/A |  | #N/A |  | #N/A | 0 | #N/A
Electrical/Mechanical0 | Electrical/Mechanical0 | [5 empty] | n | [14 empty] | 0 |  | 31023 |  |  | 0 |  | 31023 |  | 0 | 0 |  | 0 | 0 |  | 0 |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | 0 | 0 | 0 | 0 |  | #N/A | #N/A |  | #N/A |  | #N/A | 0 | #N/A
Electrical/Mechanical | Electrical/Mechanical0 | [5 empty] | n | [19 empty] | 0 |  | 31023 | [23 empty] | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | 0 | 0 | 0 | 0 |  | #N/A | #N/A |  | #N/A |  | #N/A | 0 | #N/A
Electrical/Mechanical538 | Electrical/Mechanical538 | [5 empty] | n | [12 empty] | ballast replacement |  | 538 |  | 31023 |  |  | 538 |  | 31023 | [11 empty] | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  | #N/A | #N/A | [10 empty] | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  | #N/A | #N/A | 0
Electrical/Mechanical0 | Electrical/Mechanical0 | [5 empty] | n | [14 empty] | 0 |  | 31023 |  |  | 0 |  | 31023 | [11 empty] | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | [10 empty] | #N/A | #N/A | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | #N/A | 0
Electrical/Mechanical0 | Electrical/Mechanical0 | [5 empty] | n | [14 empty] | 0 |  | 31023 |  |  | 0 |  | 31023 | [11 empty] | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | [10 empty] | #N/A | #N/A | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | #N/A | 0
Electrical/Mechanical | Electrical/Mechanical0 | [5 empty] | n | [19 empty] | 0 |  | 31023 | [33 empty] | #N/A | #N/A | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | #N/A | 0
Stairway | Stairway | [5 empty] | n | [12 empty] | Stairway | 0.6 |  |  | 8484 | Stairway | 0.68448 |  |  | 8484
Stairway530 | Stairway530 | [5 empty] | n | [12 empty] | replacement costs are for lamps |  | 530 |  | 8484 |  |  | 530 |  | 8484 |  | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  | #N/A | #N/A | #N/A
Stairway0 | Stairway602 | [5 empty] | n | [14 empty] | 0 |  | 8484 |  |  | 602 |  | 8484 |  | 0 | 0 |  | 0 | 0 |  | 0 |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  | #N/A | #N/A | #N/A
Stairway0 | Stairway0 | [5 empty] | n | [14 empty] | 0 |  | 8484 |  |  | 0 |  | 8484 |  | 0 | 0 |  | 0 | 0 |  | 0 |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | 0 | 0 | 0 | 0 |  | #N/A | #N/A |  | #N/A |  | #N/A | 0 | #N/A
Stairway | Stairway0 | [5 empty] | n | [19 empty] | 0 |  | 8484 | [23 empty] | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | 0 | 0 | 0 | 0 |  | #N/A | #N/A |  | #N/A |  | #N/A | 0 | #N/A
Stairway530 | Stairway530 | [5 empty] | n | [12 empty] | ballast replacement |  | 530 |  | 8484 |  |  | 530 |  | 8484 | [11 empty] | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  | #N/A | #N/A | [10 empty] | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  | #N/A | #N/A | 0
Stairway0 | Stairway602 | [5 empty] | n | [14 empty] | 0 |  | 8484 |  |  | 602 |  | 8484 | [11 empty] | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | [10 empty] | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  | #N/A | #N/A | 0
Stairway0 | Stairway0 | [5 empty] | n | [14 empty] | 0 |  | 8484 |  |  | 0 |  | 8484 | [11 empty] | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | [10 empty] | #N/A | #N/A | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | #N/A | 0
Stairway | Stairway0 | [5 empty] | n | [19 empty] | 0 |  | 8484 | [33 empty] | #N/A | #N/A | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | #N/A | 0
Lobby | Lobby | [5 empty] | n | [12 empty] | Lobby | 1.3 |  |  | 13792 | Lobby | 0.8928 |  |  | 13792
Lobby534-2 | Lobby523 | [5 empty] | n | [12 empty] | replacement costs are for lamps |  | 534-2 |  | 13792 |  |  | 523 |  | 13792 |  | 3.0412 | 41944.1279 |  | 0.46315 | 6387.8147 |  | 27193.6478 |  |  | 75525.5904 | 9.8847 | 10 | 0.026811 | 369.7706 |  | 0.043751 | 603.4143 |  | 898.8542 |  | 1872.0391 | 1893.8795 | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  | #N/A | #N/A | #N/A
Lobby523 | Lobby521 | [5 empty] | n | [14 empty] | 523 |  | 13792 |  |  | 521 |  | 13792 |  | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  | #N/A | #N/A | #N/A
Lobby521 | Lobby0 | [5 empty] | n | [14 empty] | 521 |  | 13792 |  |  | 0 |  | 13792 |  | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | 0 | 0 | 0 | 0 |  | #N/A | #N/A |  | #N/A |  | #N/A | 0 | #N/A
Lobby | Lobby534-2 | [5 empty] | n | [19 empty] | 534-2 |  | 13792 | [23 empty] | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  | #N/A | #N/A | #N/A
Lobby534-2 | Lobby523 | [5 empty] | n | [12 empty] | ballast replacement |  | 534-2 |  | 13792 |  |  | 523 |  | 13792 | [11 empty] | 13.7287 | 14 | 0.24009 | 3311.3785 |  | 0.49219 | 6788.326 |  | 9559.2586 |  | 19658.9631 | 20047.4242 | [10 empty] | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  | #N/A | #N/A | 0
Lobby523 | Lobby521 | [5 empty] | n | [14 empty] | 523 |  | 13792 |  |  | 521 |  | 13792 | [11 empty] | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  | #N/A | #N/A | [10 empty] | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  | #N/A | #N/A | 0
Lobby521 | Lobby0 | [5 empty] | n | [14 empty] | 521 |  | 13792 |  |  | 0 |  | 13792 | [11 empty] | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  | #N/A | #N/A | [10 empty] | #N/A | #N/A | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | #N/A | 0
Lobby | Lobby534-2 | [5 empty] | n | [19 empty] | 534-2 |  | 13792 | [33 empty] | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  | #N/A | #N/A | 0
[18 empty] | Standalone_Retail_Interior Lighting LPD |  | Standalone Retail |  |  | 3613 |  | Standalone Retail |  |  | 3613 | [28 empty] | 0
Storage | Storage | [6 empty] | n | [11 empty] | Storage | 0.7752 |  |  | 4088 | Storage | 0.58716 |  |  | 4088 | [27 empty] | 0
Storage530 | Storage538 | [6 empty] | n | [11 empty] | replacement costs are for lamps |  | 530 |  | 4088 |  |  | 538 |  | 4088 |  | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  | #N/A | #N/A | #N/A
Storage553 | Storage0 | [6 empty] | n | [13 empty] | 0 |  | 4088 |  |  | 0 |  | 4088 |  | 0 | 0 |  | 0 | 0 |  | 0 |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | 0 | 0 | 0 | 0 |  | #N/A | #N/A |  | #N/A |  | #N/A | 0 | #N/A
Storage0 | Storage0 | [6 empty] | n | [13 empty] | 0 |  | 4088 |  |  | 0 |  | 4088 |  | 0 | 0 |  | 0 | 0 |  | 0 |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | 0 | 0 | 0 | 0 |  | #N/A | #N/A |  | #N/A |  | #N/A | 0 | #N/A
Storage | Storage0 | [6 empty] | n | [18 empty] | 0 |  | 4088 | [23 empty] | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | 0 | 0 | 0 | 0 |  | #N/A | #N/A |  | #N/A |  | #N/A | 0 | #N/A
Storage530 | Storage538 | [6 empty] | n | [11 empty] | ballast replacement |  | 530 |  | 4088 |  |  | 538 |  | 4088 | [11 empty] | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  | #N/A | #N/A | [10 empty] | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  | #N/A | #N/A | 0
Storage553 | Storage0 | [6 empty] | n | [13 empty] | 0 |  | 4088 |  |  | 0 |  | 4088 | [11 empty] | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | [10 empty] | #N/A | #N/A | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | #N/A | 0
Storage0 | Storage0 | [6 empty] | n | [13 empty] | 0 |  | 4088 |  |  | 0 |  | 4088 | [11 empty] | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | [10 empty] | #N/A | #N/A | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | #N/A | 0
Storage | Storage0 | [6 empty] | n | [18 empty] | 0 |  | 4088 | [33 empty] | #N/A | #N/A | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | #N/A | 0
Retail - Sales Area | Retail - Sales Area | [6 empty] | n | [11 empty] | Retail - Sales Area | 1.6473 |  |  | 20467 | Retail - Sales Area | 1.5658 |  |  | 20467 | [27 empty] | 0
Retail - Sales Area535 | Retail - Sales Area535 | [6 empty] | n | [11 empty] | replacement costs are for lamps |  | 535 |  | 20467 |  |  | 535 |  | 20467 |  | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  | #N/A | #N/A | #N/A
Retail - Sales Area541 | Retail - Sales Area541 | [6 empty] | n | [13 empty] | 541 |  | 20467 |  |  | 541 |  | 20467 |  | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  | #N/A | #N/A | #N/A
Retail - Sales Area572 | Retail - Sales Area0 | [6 empty] | n | [13 empty] | 0 |  | 20467 |  |  | 0 |  | 20467 |  | 0 | 0 |  | 0 | 0 |  | 0 |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | 0 | 0 | 0 | 0 |  | #N/A | #N/A |  | #N/A |  | #N/A | 0 | #N/A
Retail - Sales Area | Retail - Sales Area537-1 | [6 empty] | n | [18 empty] | 537-1 |  | 20467 | [23 empty] | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  | #N/A | #N/A | #N/A
Retail - Sales Area535 | Retail - Sales Area535 | [6 empty] | n | [11 empty] | ballast replacement |  | 535 |  | 20467 |  |  | 535 |  | 20467 | [11 empty] | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  | #N/A | #N/A | [10 empty] | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  | #N/A | #N/A | 0
Retail - Sales Area541 | Retail - Sales Area541 | [6 empty] | n | [13 empty] | 541 |  | 20467 |  |  | 541 |  | 20467 | [11 empty] | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  | #N/A | #N/A | [10 empty] | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  | #N/A | #N/A | 0
Retail - Sales Area572 | Retail - Sales Area0 | [6 empty] | n | [13 empty] | 0 |  | 20467 |  |  | 0 |  | 20467 | [11 empty] | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | [10 empty] | #N/A | #N/A | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | #N/A | 0
Retail - Sales Area | Retail - Sales Area537-1 | [6 empty] | n | [18 empty] | 537-1 |  | 20467 | [33 empty] | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  | #N/A | #N/A | 0
Lobby | Lobby | [6 empty] | n | [11 empty] | Lobby | 1.2597 |  |  | 129 | Lobby | 0.8388 |  |  | 129 | [27 empty] | 0
Lobby534-2 | Lobby523 | [6 empty] | n | [11 empty] | replacement costs are for lamps |  | 534-2 |  | 129 |  |  | 523 |  | 129 |  | 3.113 | 401.5707 |  | 0.47408 | 61.1566 |  | 260.3504 |  |  | 723.0777 | 9.8847 | 10 | 0.027443 | 3.5402 |  | 0.044783 | 5.7771 |  | 8.6056 |  | 17.9228 | 18.1319 | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  | #N/A | #N/A | #N/A
Lobby523 | Lobby521 | [6 empty] | n | [13 empty] | 523 |  | 129 |  |  | 521 |  | 129 |  | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  | #N/A | #N/A | #N/A
Lobby521 | Lobby0 | [6 empty] | n | [13 empty] | 521 |  | 129 |  |  | 0 |  | 129 |  | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | 0 | 0 | 0 | 0 |  | #N/A | #N/A |  | #N/A |  | #N/A | 0 | #N/A
Lobby | Lobby534-2 | [6 empty] | n | [18 empty] | 534-2 |  | 129 | [23 empty] | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  | #N/A | #N/A | #N/A
Lobby534-2 | Lobby523 | [6 empty] | n | [11 empty] | ballast replacement |  | 534-2 |  | 129 |  |  | 523 |  | 129 | [11 empty] | 13.7287 | 14 | 0.24576 | 31.7029 |  | 0.50381 | 64.991 |  | 91.5198 |  | 188.2138 | 191.9329 | [10 empty] | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  | #N/A | #N/A | 0
Lobby523 | Lobby521 | [6 empty] | n | [13 empty] | 523 |  | 129 |  |  | 521 |  | 129 | [11 empty] | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  | #N/A | #N/A | [10 empty] | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  | #N/A | #N/A | 0
Lobby521 | Lobby0 | [6 empty] | n | [13 empty] | 521 |  | 129 |  |  | 0 |  | 129 | [11 empty] | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  | #N/A | #N/A | [10 empty] | #N/A | #N/A | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | #N/A | 0
Lobby | Lobby534-2 | [6 empty] | n | [18 empty] | 534-2 |  | 129 | [33 empty] | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  | #N/A | #N/A | 0
0
[18 empty] | Primary_School_Interior Lighting LPD |  | Primary School |  |  | 3774 |  | Primary School |  |  | 3774 | [28 empty] | 0
Restrooms | Restrooms | [7 empty] | n | [10 empty] | Restrooms | 0.9099 |  |  | 2044 | Restrooms | 0.9212 |  |  | 2044 | [27 empty] | 0
Restrooms521 | Restrooms604 | [7 empty] | n | [10 empty] | replacement costs are for lamps |  | 521 |  | 2044 |  |  | 604 |  | 2044 |  | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  | #N/A | #N/A | #N/A
Restrooms537-1 | Restrooms520 | [7 empty] | n | [12 empty] | 537-1 |  | 2044 |  |  | 520 |  | 2044 |  | 1.0042 | 2052.6379 |  | 0.59631 | 1218.859 |  | 2205.7663 |  |  | 5477.2632 | 9.8847 | 10 | 0.032482 | 66.3931 |  | 0.053006 | 108.3444 |  | 161.3913 |  | 336.1288 | 340.0503 | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  | #N/A | #N/A | #N/A
Restrooms524 | Restrooms0 | [7 empty] | n | [12 empty] | 524 |  | 2044 |  |  | 0 |  | 2044 |  | 0.25517 | 521.5766 |  | 0.17501 | 357.7223 |  | 606.8392 |  |  | 1486.138 | 2.7457 | 3 | 0.089355 | 182.642 |  | 0.016505 | 33.7364 |  | 155.764 |  | 372.1424 | 406.6027 | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | 0 | 0 | 0 | 0 |  | #N/A | #N/A |  | #N/A |  | #N/A | 0 | #N/A
Restrooms | Restrooms534-2 | [7 empty] | n | [17 empty] | 534-2 |  | 2044 | [23 empty] | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  | #N/A | #N/A | #N/A
Restrooms521 | Restrooms604 | [7 empty] | n | [10 empty] | ballast replacement |  | 521 |  | 2044 |  |  | 604 |  | 2044 | [11 empty] | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  | #N/A | #N/A | [10 empty] | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  | #N/A | #N/A | 0
Restrooms537-1 | Restrooms520 | [7 empty] | n | [12 empty] | 537-1 |  | 2044 |  |  | 520 |  | 2044 | [11 empty] | 13.7287 | 14 | 0.29088 | 594.5654 |  | 0.59631 | 1218.859 |  | 1716.3861 |  | 3529.8105 | 3599.5596 | [10 empty] | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  | #N/A | #N/A | 0
Restrooms524 | Restrooms0 | [7 empty] | n | [12 empty] | 524 |  | 2044 |  |  | 0 |  | 2044 | [11 empty] | 13.7287 | 14 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | [10 empty] | #N/A | #N/A | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | #N/A | 0
Restrooms | Restrooms534-2 | [7 empty] | n | [17 empty] | 534-2 |  | 2044 | [33 empty] | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  | #N/A | #N/A | 0
Dining Area | Dining Area | [7 empty] | n | [10 empty] | Dining Area | 0.9099 |  |  | 3389 | Dining Area | 0.611 |  |  | 3389 | [27 empty] | 0
Dining Area531 | Dining Area535 | [7 empty] | n | [10 empty] | replacement costs are for lamps |  | 531 |  | 3389 |  |  | 535 |  | 3389 |  | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  | #N/A | #N/A | #N/A
Dining Area524 | Dining Area521 | [7 empty] | n | [12 empty] | 524 |  | 3389 |  |  | 521 |  | 3389 |  | 0.39777 | 1348.0496 |  | 0.27281 | 924.5573 |  | 1568.4165 |  |  | 3841.0235 | 2.7457 | 3 | 0.13929 | 472.0504 |  | 0.025729 | 87.194 |  | 402.5825 |  | 961.8269 | 1050.8921 | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  | #N/A | #N/A | #N/A
Dining Area0 | Dining Area0 | [7 empty] | n | [12 empty] | 0 |  | 3389 |  |  | 0 |  | 3389 |  | 0 | 0 |  | 0 | 0 |  | 0 |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | 0 | 0 | 0 | 0 |  | #N/A | #N/A |  | #N/A |  | #N/A | 0 | #N/A
Dining Area | Dining Area537-1 | [7 empty] | n | [17 empty] | 537-1 |  | 3389 | [23 empty] | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  | #N/A | #N/A | #N/A
Dining Area531 | Dining Area535 | [7 empty] | n | [10 empty] | ballast replacement |  | 531 |  | 3389 |  |  | 535 |  | 3389 | [11 empty] | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  | #N/A | #N/A | [10 empty] | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  | #N/A | #N/A | 0
Dining Area524 | Dining Area521 | [7 empty] | n | [12 empty] | 524 |  | 3389 |  |  | 521 |  | 3389 | [11 empty] | 13.7287 | 14 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | [10 empty] | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  | #N/A | #N/A | 0
Dining Area0 | Dining Area0 | [7 empty] | n | [12 empty] | 0 |  | 3389 |  |  | 0 |  | 3389 | [11 empty] | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | [10 empty] | #N/A | #N/A | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | #N/A | 0
Dining Area | Dining Area537-1 | [7 empty] | n | [17 empty] | 537-1 |  | 3389 | [33 empty] | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  | #N/A | #N/A | 0
Classroom/Lecture/Training | Classroom/Lecture/Training | [7 empty] | n | [10 empty] | Classroom/Lecture/Training | 1.4154 |  |  | 37187 | Classroom/Lecture/Training | 1.1656 |  |  | 37187 | [27 empty] | 0
Classroom/Lecture/Training535 | Classroom/Lecture/Training535 | [7 empty] | n | [10 empty] | replacement costs are for lamps |  | 535 |  | 37187 |  |  | 535 |  | 37187 |  | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  | #N/A | #N/A | #N/A
Classroom/Lecture/Training537-2 | Classroom/Lecture/Training521 | [7 empty] | n | [12 empty] | 537-2 |  | 37187 |  |  | 521 |  | 37187 |  | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  | #N/A | #N/A | #N/A
Classroom/Lecture/Training0 | Classroom/Lecture/Training0 | [7 empty] | n | [12 empty] | 0 |  | 37187 |  |  | 0 |  | 37187 |  | 0 | 0 |  | 0 | 0 |  | 0 |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | 0 | 0 | 0 | 0 |  | #N/A | #N/A |  | #N/A |  | #N/A | 0 | #N/A
Classroom/Lecture/Training | Classroom/Lecture/Training537-1 | [7 empty] | n | [17 empty] | 537-1 |  | 37187 | [23 empty] | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  | #N/A | #N/A | #N/A
Classroom/Lecture/Training535 | Classroom/Lecture/Training535 | [7 empty] | n | [10 empty] | ballast replacement |  | 535 |  | 37187 |  |  | 535 |  | 37187 | [11 empty] | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  | #N/A | #N/A | [10 empty] | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  | #N/A | #N/A | 0
Classroom/Lecture/Training537-2 | Classroom/Lecture/Training521 | [7 empty] | n | [12 empty] | 537-2 |  | 37187 |  |  | 521 |  | 37187 | [11 empty] | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  | #N/A | #N/A | [10 empty] | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  | #N/A | #N/A | 0
Classroom/Lecture/Training0 | Classroom/Lecture/Training0 | [7 empty] | n | [12 empty] | 0 |  | 37187 |  |  | 0 |  | 37187 | [11 empty] | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | [10 empty] | #N/A | #N/A | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | #N/A | 0
Classroom/Lecture/Training | Classroom/Lecture/Training537-1 | [7 empty] | n | [17 empty] | 537-1 |  | 37187 | [33 empty] | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  | #N/A | #N/A | 0
Corridor/Transition | Corridor/Transition | [7 empty] | n | [10 empty] | Corridor/Transition | 0.5055 |  |  | 12073 | Corridor/Transition | 0.6204 |  |  | 12073 | [27 empty] | 0
Corridor/Transition530 | Corridor/Transition521 | [7 empty] | n | [10 empty] | replacement costs are for lamps |  | 530 |  | 12073 |  |  | 521 |  | 12073 |  | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  | #N/A | #N/A | #N/A
Corridor/Transition537-2 | Corridor/Transition0 | [7 empty] | n | [12 empty] | 537-2 |  | 12073 |  |  | 0 |  | 12073 |  | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | 0 | 0 | 0 | 0 |  | #N/A | #N/A |  | #N/A |  | #N/A | 0 | #N/A
Corridor/Transition0 | Corridor/Transition0 | [7 empty] | n | [12 empty] | 0 |  | 12073 |  |  | 0 |  | 12073 |  | 0 | 0 |  | 0 | 0 |  | 0 |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | 0 | 0 | 0 | 0 |  | #N/A | #N/A |  | #N/A |  | #N/A | 0 | #N/A
Corridor/Transition | Corridor/Transition527-2 | [7 empty] | n | [17 empty] | 0 |  | 12073 | [23 empty] | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | 0 | 0 | 0 | 0 |  | #N/A | #N/A |  | #N/A |  | #N/A | 0 | #N/A
Corridor/Transition530 | Corridor/Transition521 | [7 empty] | n | [10 empty] | ballast replacement |  | 530 |  | 12073 |  |  | 521 |  | 12073 | [11 empty] | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  | #N/A | #N/A | [10 empty] | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  | #N/A | #N/A | 0
Corridor/Transition537-2 | Corridor/Transition0 | [7 empty] | n | [12 empty] | 537-2 |  | 12073 |  |  | 0 |  | 12073 | [11 empty] | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  | #N/A | #N/A | [10 empty] | #N/A | #N/A | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | #N/A | 0
Corridor/Transition0 | Corridor/Transition0 | [7 empty] | n | [12 empty] | 0 |  | 12073 |  |  | 0 |  | 12073 | [11 empty] | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | [10 empty] | #N/A | #N/A | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | #N/A | 0
Corridor/Transition | Corridor/Transition527-2 | [7 empty] | n | [17 empty] | 0 |  | 12073 | [33 empty] | #N/A | #N/A | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | #N/A | 0
Gymnasium/Fitness-Fitness Area | Gymnasium/Fitness-Fitness Area | [7 empty] | n | [10 empty] | Gymnasium/Fitness-Fitness Area | 0.9099 |  |  | 3841 | Gymnasium/Fitness-Fitness Area | 0.6768 |  |  | 3841 | [27 empty] | 0
Gymnasium/Fitness-Fitness Area535 | Gymnasium/Fitness-Fitness Area535 | [7 empty] | n | [10 empty] | replacement costs are for lamps |  | 535 |  | 3841 |  |  | 535 |  | 3841 |  | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  | #N/A | #N/A | #N/A
Gymnasium/Fitness-Fitness Area0 | Gymnasium/Fitness-Fitness Area0 | [7 empty] | n | [12 empty] | 0 |  | 3841 |  |  | 0 |  | 3841 |  | 0 | 0 |  | 0 | 0 |  | 0 |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | 0 | 0 | 0 | 0 |  | #N/A | #N/A |  | #N/A |  | #N/A | 0 | #N/A
Gymnasium/Fitness-Fitness Area0 | Gymnasium/Fitness-Fitness Area0 | [7 empty] | n | [12 empty] | 0 |  | 3841 |  |  | 0 |  | 3841 |  | 0 | 0 |  | 0 | 0 |  | 0 |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | 0 | 0 | 0 | 0 |  | #N/A | #N/A |  | #N/A |  | #N/A | 0 | #N/A
Gymnasium/Fitness-Fitness Area | Gymnasium/Fitness-Fitness Area0 | [7 empty] | n | [17 empty] | 0 |  | 3841 | [23 empty] | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | 0 | 0 | 0 | 0 |  | #N/A | #N/A |  | #N/A |  | #N/A | 0 | #N/A
Gymnasium/Fitness-Fitness Area535 | Gymnasium/Fitness-Fitness Area535 | [7 empty] | n | [10 empty] | ballast replacement |  | 535 |  | 3841 |  |  | 535 |  | 3841 | [11 empty] | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  | #N/A | #N/A | [10 empty] | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  | #N/A | #N/A | 0
Gymnasium/Fitness-Fitness Area0 | Gymnasium/Fitness-Fitness Area0 | [7 empty] | n | [12 empty] | 0 |  | 3841 |  |  | 0 |  | 3841 | [11 empty] | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | [10 empty] | #N/A | #N/A | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | #N/A | 0
Gymnasium/Fitness-Fitness Area0 | Gymnasium/Fitness-Fitness Area0 | [7 empty] | n | [12 empty] | 0 |  | 3841 |  |  | 0 |  | 3841 | [11 empty] | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | [10 empty] | #N/A | #N/A | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | #N/A | 0
Gymnasium/Fitness-Fitness Area | Gymnasium/Fitness-Fitness Area0 | [7 empty] | n | [17 empty] | 0 |  | 3841 | [33 empty] | #N/A | #N/A | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | #N/A | 0
Food Preparation | Food Preparation | [7 empty] | n | [10 empty] | Food Preparation | 1.2132 |  |  | 1808 | Food Preparation | 0.9306 |  |  | 1808 | [27 empty] | 0
Food Preparation530 | Food Preparation530 | [7 empty] | n | [10 empty] | replacement costs are for lamps |  | 530 |  | 1808 |  |  | 530 |  | 1808 |  | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  | #N/A | #N/A | #N/A
Food Preparation0 | Food Preparation0 | [7 empty] | n | [12 empty] | 0 |  | 1808 |  |  | 0 |  | 1808 |  | 0 | 0 |  | 0 | 0 |  | 0 |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | 0 | 0 | 0 | 0 |  | #N/A | #N/A |  | #N/A |  | #N/A | 0 | #N/A
Food Preparation0 | Food Preparation0 | [7 empty] | n | [12 empty] | 0 |  | 1808 |  |  | 0 |  | 1808 |  | 0 | 0 |  | 0 | 0 |  | 0 |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | 0 | 0 | 0 | 0 |  | #N/A | #N/A |  | #N/A |  | #N/A | 0 | #N/A
Food Preparation | Food Preparation0 | [7 empty] | n | [17 empty] | 0 |  | 1808 | [23 empty] | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | 0 | 0 | 0 | 0 |  | #N/A | #N/A |  | #N/A |  | #N/A | 0 | #N/A
Food Preparation530 | Food Preparation530 | [7 empty] | n | [10 empty] | ballast replacement |  | 530 |  | 1808 |  |  | 530 |  | 1808 | [11 empty] | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  | #N/A | #N/A | [10 empty] | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  | #N/A | #N/A | 0
Food Preparation0 | Food Preparation0 | [7 empty] | n | [12 empty] | 0 |  | 1808 |  |  | 0 |  | 1808 | [11 empty] | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | [10 empty] | #N/A | #N/A | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | #N/A | 0
Food Preparation0 | Food Preparation0 | [7 empty] | n | [12 empty] | 0 |  | 1808 |  |  | 0 |  | 1808 | [11 empty] | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | [10 empty] | #N/A | #N/A | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | #N/A | 0
Food Preparation | Food Preparation0 | [7 empty] | n | [17 empty] | 0 |  | 1808 | [33 empty] | #N/A | #N/A | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | #N/A | 0
Library | Library | [7 empty] | n | [10 empty] | Library | 1.2132 |  |  | 4293 | Library | 0.8742 |  |  | 4293 | [27 empty] | 0
Library535 | Library535 | [7 empty] | n | [10 empty] | replacement costs are for lamps |  | 535 |  | 4293 |  |  | 535 |  | 4293 |  | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  | #N/A | #N/A | #N/A
Library520 | Library520 | [7 empty] | n | [12 empty] | 520 |  | 4293 |  |  | 520 |  | 4293 |  | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  | #N/A | #N/A | #N/A
Library529 | Library0 | [7 empty] | n | [12 empty] | 529 |  | 4293 |  |  | 0 |  | 4293 |  | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | 0 | 0 | 0 | 0 |  | #N/A | #N/A |  | #N/A |  | #N/A | 0 | #N/A
Library | Library0 | [7 empty] | n | [17 empty] | 0 |  | 4293 | [23 empty] | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | 0 | 0 | 0 | 0 |  | #N/A | #N/A |  | #N/A |  | #N/A | 0 | #N/A
Library535 | Library535 | [7 empty] | n | [10 empty] | ballast replacement |  | 535 |  | 4293 |  |  | 535 |  | 4293 | [11 empty] | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  | #N/A | #N/A | [10 empty] | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  | #N/A | #N/A | 0
Library520 | Library520 | [7 empty] | n | [12 empty] | 520 |  | 4293 |  |  | 520 |  | 4293 | [11 empty] | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  | #N/A | #N/A | [10 empty] | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  | #N/A | #N/A | 0
Library529 | Library0 | [7 empty] | n | [12 empty] | 529 |  | 4293 |  |  | 0 |  | 4293 | [11 empty] | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  | #N/A | #N/A | [10 empty] | #N/A | #N/A | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | #N/A | 0
Library | Library0 | [7 empty] | n | [17 empty] | 0 |  | 4293 | [33 empty] | #N/A | #N/A | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | #N/A | 0
Lobby | Lobby | [7 empty] | n | [10 empty] | Lobby | 1.3143 |  |  | 1840 | Lobby | 0.846 |  |  | 1840 | [27 empty] | 0
Lobby534-2 | Lobby523 | [7 empty] | n | [10 empty] | replacement costs are for lamps |  | 534-2 |  | 1840 |  |  | 523 |  | 1840 |  | 2.8191 | 5187.1127 |  | 0.42933 | 789.9631 |  | 3362.9622 |  |  | 9340.038 | 9.8847 | 10 | 0.024852 | 45.7285 |  | 0.040556 | 74.6226 |  | 111.1588 |  | 231.5098 | 234.2108 | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  | #N/A | #N/A | #N/A
Lobby523 | Lobby521 | [7 empty] | n | [12 empty] | 523 |  | 1840 |  |  | 521 |  | 1840 |  | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  | #N/A | #N/A | #N/A
Lobby521 | Lobby0 | [7 empty] | n | [12 empty] | 521 |  | 1840 |  |  | 0 |  | 1840 |  | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | 0 | 0 | 0 | 0 |  | #N/A | #N/A |  | #N/A |  | #N/A | 0 | #N/A
Lobby | Lobby534-2 | [7 empty] | n | [17 empty] | 534-2 |  | 1840 | [23 empty] | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  | #N/A | #N/A | #N/A
Lobby534-2 | Lobby523 | [7 empty] | n | [10 empty] | ballast replacement |  | 534-2 |  | 1840 |  |  | 523 |  | 1840 | [11 empty] | 13.7287 | 14 | 0.22256 | 409.5089 |  | 0.45625 | 839.4932 |  | 1182.1667 |  | 2431.1689 | 2479.2088 | [10 empty] | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  | #N/A | #N/A | 0
Lobby523 | Lobby521 | [7 empty] | n | [12 empty] | 523 |  | 1840 |  |  | 521 |  | 1840 | [11 empty] | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  | #N/A | #N/A | [10 empty] | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  | #N/A | #N/A | 0
Lobby521 | Lobby0 | [7 empty] | n | [12 empty] | 521 |  | 1840 |  |  | 0 |  | 1840 | [11 empty] | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  | #N/A | #N/A | [10 empty] | #N/A | #N/A | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | #N/A | 0
Lobby | Lobby534-2 | [7 empty] | n | [17 empty] | 534-2 |  | 1840 | [33 empty] | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  | #N/A | #N/A | 0
Electrical/Mechanical | Electrical/Mechanical | [7 empty] | n | [10 empty] | Electrical/Mechanical | 1.5165 |  |  | 2712 | Electrical/Mechanical | 0.893 |  |  | 2712 | [27 empty] | 0
Electrical/Mechanical538 | Electrical/Mechanical538 | [7 empty] | n | [10 empty] | replacement costs are for lamps |  | 538 |  | 2712 |  |  | 538 |  | 2712 |  | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  | #N/A | #N/A | #N/A
Electrical/Mechanical0 | Electrical/Mechanical0 | [7 empty] | n | [12 empty] | 0 |  | 2712 |  |  | 0 |  | 2712 |  | 0 | 0 |  | 0 | 0 |  | 0 |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | 0 | 0 | 0 | 0 |  | #N/A | #N/A |  | #N/A |  | #N/A | 0 | #N/A
Electrical/Mechanical0 | Electrical/Mechanical0 | [7 empty] | n | [12 empty] | 0 |  | 2712 |  |  | 0 |  | 2712 |  | 0 | 0 |  | 0 | 0 |  | 0 |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | 0 | 0 | 0 | 0 |  | #N/A | #N/A |  | #N/A |  | #N/A | 0 | #N/A
Electrical/Mechanical | Electrical/Mechanical0 | [7 empty] | n | [17 empty] | 0 |  | 2712 | [23 empty] | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | 0 | 0 | 0 | 0 |  | #N/A | #N/A |  | #N/A |  | #N/A | 0 | #N/A
Electrical/Mechanical538 | Electrical/Mechanical538 | [7 empty] | n | [10 empty] | ballast replacement |  | 538 |  | 2712 |  |  | 538 |  | 2712 | [11 empty] | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  | #N/A | #N/A | [10 empty] | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  | #N/A | #N/A | 0
Electrical/Mechanical0 | Electrical/Mechanical0 | [7 empty] | n | [12 empty] | 0 |  | 2712 |  |  | 0 |  | 2712 | [11 empty] | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | [10 empty] | #N/A | #N/A | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | #N/A | 0
Electrical/Mechanical0 | Electrical/Mechanical0 | [7 empty] | n | [12 empty] | 0 |  | 2712 |  |  | 0 |  | 2712 | [11 empty] | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | [10 empty] | #N/A | #N/A | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | #N/A | 0
Electrical/Mechanical | Electrical/Mechanical0 | [7 empty] | n | [17 empty] | 0 |  | 2712 | [33 empty] | #N/A | #N/A | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | #N/A | 0
Office-Enclosed | Office-Enclosed | [7 empty] | n | [10 empty] | Office-Enclosed | 1.1121 |  |  | 4745 | Office-Enclosed | 1.0434 |  |  | 4745 | [27 empty] | 0
Office-Enclosed535 | Office-Enclosed531 | [7 empty] | n | [10 empty] | replacement costs are for lamps |  | 535 |  | 4745 |  |  | 531 |  | 4745 |  | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  | #N/A | #N/A | #N/A
Office-Enclosed539 | Office-Enclosed539 | [7 empty] | n | [12 empty] | 539 |  | 4745 |  |  | 539 |  | 4745 |  | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  | #N/A | #N/A | #N/A
Office-Enclosed537-2 | Office-Enclosed0 | [7 empty] | n | [12 empty] | 537-2 |  | 4745 |  |  | 0 |  | 4745 |  | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | 0 | 0 | 0 | 0 |  | #N/A | #N/A |  | #N/A |  | #N/A | 0 | #N/A
Office-Enclosed | Office-Enclosed537-1 | [7 empty] | n | [17 empty] | 537-1 |  | 4745 | [23 empty] | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  | #N/A | #N/A | #N/A
Office-Enclosed535 | Office-Enclosed531 | [7 empty] | n | [10 empty] | ballast replacement |  | 535 |  | 4745 |  |  | 531 |  | 4745 | [11 empty] | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  | #N/A | #N/A | [10 empty] | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  | #N/A | #N/A | 0
Office-Enclosed539 | Office-Enclosed539 | [7 empty] | n | [12 empty] | 539 |  | 4745 |  |  | 539 |  | 4745 | [11 empty] | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  | #N/A | #N/A | [10 empty] | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  | #N/A | #N/A | 0
Office-Enclosed537-2 | Office-Enclosed0 | [7 empty] | n | [12 empty] | 537-2 |  | 4745 |  |  | 0 |  | 4745 | [11 empty] | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  | #N/A | #N/A | [10 empty] | #N/A | #N/A | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | #N/A | 0
Office-Enclosed | Office-Enclosed537-1 | [7 empty] | n | [17 empty] | 537-1 |  | 4745 | [33 empty] | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  | #N/A | #N/A | 0
0
[18 empty] | Small_Hotel_Interior Lighting LPD |  | Small Hotel |  |  |  |  | Small Hotel
Highway Lodging Guest Rooms | Highway Lodging Guest Rooms | [8 empty] | n | [9 empty] | Highway Lodging Guest Rooms | 1.1 |  | 3588 | 27933 | Highway Lodging Guest Rooms | 0.75 |  | 3588 | 27933 | [27 empty] | 0
Highway Lodging Guest Rooms524 | Highway Lodging Guest Rooms529 | [8 empty] | n | [9 empty] | replacement costs are for lamps |  | 524 |  | 27933 |  |  | 529 |  | 27933 |  | 0.3851 | 10757.0452 |  | 0.26412 | 7377.6991 |  | 12515.5093 |  |  | 30650.2537 | 2.7457 | 3 | 0.13485 | 3766.8253 |  | 0.024909 | 695.783 |  | 3212.4916 |  | 7675.0999 | 8385.8141 | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  | #N/A | #N/A | #N/A
Highway Lodging Guest Rooms520 | Highway Lodging Guest Rooms520 | [8 empty] | n | [11 empty] | 520 |  | 27933 |  |  | 520 |  | 27933 |  | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  | #N/A | #N/A | #N/A
Highway Lodging Guest Rooms0 | Highway Lodging Guest Rooms0 | [8 empty] | n | [11 empty] | 0 |  | 27933 |  |  | 0 |  | 27933 |  | 0 | 0 |  | 0 | 0 |  | 0 |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | 0 | 0 | 0 | 0 |  | #N/A | #N/A |  | #N/A |  | #N/A | 0 | #N/A
Highway Lodging Guest Rooms | Highway Lodging Guest Rooms0 | [8 empty] | n | [16 empty] | 0 |  | 27933 | [23 empty] | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | 0 | 0 | 0 | 0 |  | #N/A | #N/A |  | #N/A |  | #N/A | 0 | #N/A
Highway Lodging Guest Rooms524 | Highway Lodging Guest Rooms529 | [8 empty] | n | [9 empty] | ballast replacement |  | 524 |  | 27933 |  |  | 529 |  | 27933 | [11 empty] | 13.7287 | 14 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | [10 empty] | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  | #N/A | #N/A | 0
Highway Lodging Guest Rooms520 | Highway Lodging Guest Rooms520 | [8 empty] | n | [11 empty] | 520 |  | 27933 |  |  | 520 |  | 27933 | [11 empty] | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  | #N/A | #N/A | [10 empty] | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  | #N/A | #N/A | 0
Highway Lodging Guest Rooms0 | Highway Lodging Guest Rooms0 | [8 empty] | n | [11 empty] | 0 |  | 27933 |  |  | 0 |  | 27933 | [11 empty] | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | [10 empty] | #N/A | #N/A | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | #N/A | 0
Highway Lodging Guest Rooms | Highway Lodging Guest Rooms0 | [8 empty] | n | [16 empty] | 0 |  | 27933 | [33 empty] | #N/A | #N/A | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | #N/A | 0
Corridor/Transition | Corridor/Transition | [8 empty] | n | [9 empty] | Corridor/Transition | 0.6475 |  | 8760 | 5668 | Corridor/Transition | 0.74514 |  | 8760 | 5668 | [27 empty] | 0
Corridor/Transition530 | Corridor/Transition521 | [8 empty] | n | [9 empty] | replacement costs are for lamps |  | 530 |  | 5668 |  |  | 521 |  | 5668 |  | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  | #N/A | #N/A | #N/A
Corridor/Transition537-2 | Corridor/Transition0 | [8 empty] | n | [11 empty] | 537-2 |  | 5668 |  |  | 0 |  | 5668 |  | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | 0 | 0 | 0 | 0 |  | #N/A | #N/A |  | #N/A |  | #N/A | 0 | #N/A
Corridor/Transition0 | Corridor/Transition0 | [8 empty] | n | [11 empty] | 0 |  | 5668 |  |  | 0 |  | 5668 |  | 0 | 0 |  | 0 | 0 |  | 0 |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | 0 | 0 | 0 | 0 |  | #N/A | #N/A |  | #N/A |  | #N/A | 0 | #N/A
Corridor/Transition | Corridor/Transition527-2 | [8 empty] | n | [16 empty] | 0 |  | 5668 | [23 empty] | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | 0 | 0 | 0 | 0 |  | #N/A | #N/A |  | #N/A |  | #N/A | 0 | #N/A
Corridor/Transition530 | Corridor/Transition521 | [8 empty] | n | [9 empty] | ballast replacement |  | 530 |  | 5668 |  |  | 521 |  | 5668 | [11 empty] | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  | #N/A | #N/A | [10 empty] | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  | #N/A | #N/A | 0
Corridor/Transition537-2 | Corridor/Transition0 | [8 empty] | n | [11 empty] | 537-2 |  | 5668 |  |  | 0 |  | 5668 | [11 empty] | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  | #N/A | #N/A | [10 empty] | #N/A | #N/A | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | #N/A | 0
Corridor/Transition0 | Corridor/Transition0 | [8 empty] | n | [11 empty] | 0 |  | 5668 |  |  | 0 |  | 5668 | [11 empty] | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | [10 empty] | #N/A | #N/A | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | #N/A | 0
Corridor/Transition | Corridor/Transition527-2 | [8 empty] | n | [16 empty] | 0 |  | 5668 | [33 empty] | #N/A | #N/A | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | #N/A | 0
Stairway | Stairway | [8 empty] | n | [9 empty] | Stairway | 0.777 |  | 8760 | 1728 | Stairway | 0.77901 |  | 8760 | 1728
Stairway530 | Stairway530 | [8 empty] | n | [9 empty] | replacement costs are for lamps |  | 530 |  | 1728 |  |  | 530 |  | 1728 |  | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  | #N/A | #N/A | #N/A
Stairway0 | Stairway602 | [8 empty] | n | [11 empty] | 0 |  | 1728 |  |  | 602 |  | 1728 |  | 0 | 0 |  | 0 | 0 |  | 0 |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  | #N/A | #N/A | #N/A
Stairway0 | Stairway0 | [8 empty] | n | [11 empty] | 0 |  | 1728 |  |  | 0 |  | 1728 |  | 0 | 0 |  | 0 | 0 |  | 0 |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | 0 | 0 | 0 | 0 |  | #N/A | #N/A |  | #N/A |  | #N/A | 0 | #N/A
Stairway | Stairway0 | [8 empty] | n | [16 empty] | 0 |  | 1728 | [23 empty] | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | 0 | 0 | 0 | 0 |  | #N/A | #N/A |  | #N/A |  | #N/A | 0 | #N/A
Stairway530 | Stairway530 | [8 empty] | n | [9 empty] | ballast replacement |  | 530 |  | 1728 |  |  | 530 |  | 1728 | [11 empty] | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  | #N/A | #N/A | [10 empty] | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  | #N/A | #N/A | 0
Stairway0 | Stairway602 | [8 empty] | n | [11 empty] | 0 |  | 1728 |  |  | 602 |  | 1728 | [11 empty] | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | [10 empty] | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  | #N/A | #N/A | 0
Stairway0 | Stairway0 | [8 empty] | n | [11 empty] | 0 |  | 1728 |  |  | 0 |  | 1728 | [11 empty] | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | [10 empty] | #N/A | #N/A | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | #N/A | 0
Stairway | Stairway0 | [8 empty] | n | [16 empty] | 0 |  | 1728 | [33 empty] | #N/A | #N/A | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | #N/A | 0
Lobby | Lobby - Hotel | [8 empty] | n | [9 empty] | Lobby - Hotel | 1.4245 |  | 7170 | 1755 | Lobby - Hotel | 1.1967 |  | 7170 | 1755
Lobby - Hotel535 | Lobby - Hotel572 | [8 empty] | n | [9 empty] | replacement costs are for lamps |  | 535 |  | 1755 |  |  | 572 |  | 1755 |  | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  | #N/A | #N/A | #N/A
Lobby - Hotel572 | Lobby - Hotel0 | [8 empty] | n | [11 empty] | 572 |  | 1755 |  |  | 0 |  | 1755 |  | 0.48526 | 851.6306 |  | 1.0697 | 1877.2503 |  | 2239.3789 |  |  | 4968.2598 | 0.23339 | 1 | 0.37186 | 652.6116 |  | 0.40873 | 717.3233 |  | 1207.3121 |  | 2577.2469 | 11042.7451 | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | 0 | 0 | 0 | 0 |  | #N/A | #N/A |  | #N/A |  | #N/A | 0 | #N/A
Lobby - Hotel524 | Lobby - Hotel0 | [8 empty] | n | [11 empty] | 524 |  | 1755 |  |  | 0 |  | 1755 |  | 0.35185 | 617.4931 |  | 0.24131 | 423.5065 |  | 718.4353 |  |  | 1759.4349 | 2.7457 | 3 | 0.12321 | 216.2293 |  | 0.022758 | 39.9404 |  | 184.4086 |  | 440.5784 | 481.3759 | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | 0 | 0 | 0 | 0 |  | #N/A | #N/A |  | #N/A |  | #N/A | 0 | #N/A
Lobby | Lobby - Hotel527-1 | [8 empty] | n | [16 empty] | 527-1 |  | 1755 | [23 empty] | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | #N/A |  | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  | #N/A | 0 | #N/A
Lobby - Hotel535 | Lobby - Hotel572 | [8 empty] | n | [9 empty] | ballast replacement |  | 535 |  | 1755 |  |  | 572 |  | 1755 | [11 empty] | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  | #N/A | #N/A | [10 empty] | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  | #N/A | #N/A | 0
Lobby - Hotel572 | Lobby - Hotel0 | [8 empty] | n | [11 empty] | 572 |  | 1755 |  |  | 0 |  | 1755 | [11 empty] | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | [10 empty] | #N/A | #N/A | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | #N/A | 0
Lobby - Hotel524 | Lobby - Hotel0 | [8 empty] | n | [11 empty] | 524 |  | 1755 |  |  | 0 |  | 1755 | [11 empty] | 13.7287 | 14 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | [10 empty] | #N/A | #N/A | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | #N/A | 0
Lobby | Lobby - Hotel527-1 | [8 empty] | n | [16 empty] | 527-1 |  | 1755 | [33 empty] | #N/A |  | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  | #N/A | 0 | 0
Storage | Storage | [8 empty] | n | [9 empty] | Storage | 1.036 |  | 2148 | 1404 | Storage | 0.71127 |  | 2148 | 1404
Storage530 | Storage538 | [8 empty] | n | [9 empty] | replacement costs are for lamps |  | 530 |  | 1404 |  |  | 538 |  | 1404 |  | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  | #N/A | #N/A | #N/A
Storage553 | Storage0 | [8 empty] | n | [11 empty] | 0 |  | 1404 |  |  | 0 |  | 1404 |  | 0 | 0 |  | 0 | 0 |  | 0 |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | 0 | 0 | 0 | 0 |  | #N/A | #N/A |  | #N/A |  | #N/A | 0 | #N/A
Storage0 | Storage0 | [8 empty] | n | [11 empty] | 0 |  | 1404 |  |  | 0 |  | 1404 |  | 0 | 0 |  | 0 | 0 |  | 0 |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | 0 | 0 | 0 | 0 |  | #N/A | #N/A |  | #N/A |  | #N/A | 0 | #N/A
Storage | Storage0 | [8 empty] | n | [16 empty] | 0 |  | 1404 | [23 empty] | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | 0 |  | 0 | 0 |  | #N/A | #N/A |  | #N/A |  | #N/A | 0 | #N/A
Storage530 | Storage538 | [8 empty] | n | [9 empty] | ballast replacement |  | 530 |  | 1404 |  |  | 538 |  | 1404 | [11 empty] | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  | #N/A | #N/A | [10 empty] | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  | #N/A | #N/A | 0
Storage553 | Storage0 | [8 empty] | n | [11 empty] | 0 |  | 1404 |  |  | 0 |  | 1404 | [11 empty] | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | [10 empty] | #N/A | #N/A | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | #N/A | 0
Storage0 | Storage0 | [8 empty] | n | [11 empty] | 0 |  | 1404 |  |  | 0 |  | 1404 | [11 empty] | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | [10 empty] | #N/A | #N/A | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | #N/A | 0
Storage | Storage0 | [8 empty] | n | [16 empty] | 0 |  | 1404 | [33 empty] | #N/A |  | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
Office-Enclosed | Office-Enclosed | [8 empty] | n | [9 empty] | Office-Enclosed | 1.4245 |  | 5722 | 1404 | Office-Enclosed | 1.2532 |  | 5722 | 1404
Office-Enclosed535 | Office-Enclosed531 | [8 empty] | n | [9 empty] | replacement costs are for lamps |  | 535 |  | 1404 |  |  | 531 |  | 1404 |  | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  | #N/A | #N/A | #N/A
Office-Enclosed539 | Office-Enclosed539 | [8 empty] | n | [11 empty] | 539 |  | 1404 |  |  | 539 |  | 1404 |  | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  | #N/A | #N/A | #N/A
Office-Enclosed537-2 | Office-Enclosed0 | [8 empty] | n | [11 empty] | 537-2 |  | 1404 |  |  | 0 |  | 1404 |  | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | 0 | 0 | 0 | 0 |  | #N/A | #N/A |  | #N/A |  | #N/A | 0 | #N/A
Office-Enclosed | Office-Enclosed537-1 | [8 empty] | n | [16 empty] | 537-1 |  | 1404 | [23 empty] | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | #N/A |  | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  | #N/A | 0 | #N/A
Office-Enclosed535 | Office-Enclosed531 | [8 empty] | n | [9 empty] | ballast replacement |  | 535 |  | 1404 |  |  | 531 |  | 1404 | [11 empty] | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  | #N/A | #N/A | [10 empty] | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  | #N/A | #N/A | 0
Office-Enclosed539 | Office-Enclosed539 | [8 empty] | n | [11 empty] | 539 |  | 1404 |  |  | 539 |  | 1404 | [11 empty] | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  | #N/A | #N/A | [10 empty] | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  | #N/A | #N/A | 0
Office-Enclosed537-2 | Office-Enclosed0 | [8 empty] | n | [11 empty] | 537-2 |  | 1404 |  |  | 0 |  | 1404 | [11 empty] | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  | #N/A | #N/A | [10 empty] | #N/A | #N/A | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | #N/A | 0
Office-Enclosed | Office-Enclosed537-1 | [8 empty] | n | [16 empty] | 537-1 |  | 1404 | [33 empty] | #N/A |  | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  | #N/A | 0 | 0
Hospital - Laundry-washing | Hospital - Laundry-washing | [8 empty] | n | [9 empty] | Hospital - Laundry/Washing | 0.777 |  | 3276 | 1053 | Hospital - Laundry/Washing | 0.6774 |  | 3276 | 1053
Hospital - Laundry-washing530 | Hospital - Laundry-washing530 | [8 empty] | n | [9 empty] | replacement costs are for lamps |  | 530 |  | 1053 |  |  | 530 |  | 1053 |  | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  | #N/A | #N/A | #N/A
Hospital - Laundry-washing0 | Hospital - Laundry-washing0 | [8 empty] | n | [11 empty] | 0 |  | 1053 |  |  | 0 |  | 1053 |  | 0 | 0 |  | 0 | 0 |  | 0 |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | 0 | 0 | 0 | 0 |  | #N/A | #N/A |  | #N/A |  | #N/A | 0 | #N/A
Hospital - Laundry-washing0 | Hospital - Laundry-washing0 | [8 empty] | n | [11 empty] | 0 |  | 1053 |  |  | 0 |  | 1053 |  | 0 | 0 |  | 0 | 0 |  | 0 |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | 0 | 0 | 0 | 0 |  | #N/A | #N/A |  | #N/A |  | #N/A | 0 | #N/A
Hospital - Laundry-washing | Hospital - Laundry-washing0 | [8 empty] | n | [16 empty] | 0 |  | 1053 | [23 empty] | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | 0 |  | 0 | 0 |  | #N/A | #N/A |  | #N/A |  | #N/A | 0 | #N/A
Hospital - Laundry-washing530 | Hospital - Laundry-washing530 | [8 empty] | n | [9 empty] | ballast replacement |  | 530 |  | 1053 |  |  | 530 |  | 1053 | [11 empty] | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  | #N/A | #N/A | [10 empty] | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  | #N/A | #N/A | 0
Hospital - Laundry-washing0 | Hospital - Laundry-washing0 | [8 empty] | n | [11 empty] | 0 |  | 1053 |  |  | 0 |  | 1053 | [11 empty] | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | [10 empty] | #N/A | #N/A | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | #N/A | 0
Hospital - Laundry-washing0 | Hospital - Laundry-washing0 | [8 empty] | n | [11 empty] | 0 |  | 1053 |  |  | 0 |  | 1053 | [11 empty] | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | [10 empty] | #N/A | #N/A | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | #N/A | 0
Hospital - Laundry-washing | Hospital - Laundry-washing0 | [8 empty] | n | [16 empty] | 0 |  | 1053 | [33 empty] | #N/A |  | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
Conference/Meeting/Multipurpose | Conference/Meeting/Multipurpose | [8 empty] | n | [9 empty] | Conference/Meeting/Multipurpose | 1.6835 |  | 4386 | 864 | Conference/Meeting/Multipurpose | 1.3887 |  | 4386 | 864
Conference/Meeting/Multipurpose535 | Conference/Meeting/Multipurpose535 | [8 empty] | n | [9 empty] | replacement costs are for lamps |  | 535 |  | 864 |  |  | 535 |  | 864 |  | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  | #N/A | #N/A | #N/A
Conference/Meeting/Multipurpose537-1 | Conference/Meeting/Multipurpose511 | [8 empty] | n | [11 empty] | 537-1 |  | 864 |  |  | 511 |  | 864 |  | 1.8348 | 1585.2851 |  | 1.0895 | 941.3444 |  | 1703.5487 |  |  | 4230.1782 | 9.8847 | 10 | 0.059348 | 51.2765 |  | 0.096847 | 83.6761 |  | 124.6451 |  | 259.5976 | 262.6263 | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  | #N/A | #N/A | #N/A
Conference/Meeting/Multipurpose511 | Conference/Meeting/Multipurpose0 | [8 empty] | n | [11 empty] | 511 |  | 864 |  |  | 0 |  | 864 |  | 0.21663 | 187.1648 |  | 0.35929 | 310.427 |  | 393.5379 |  |  | 891.1297 | 1.1532 | 2 | 0.1249 | 107.9176 |  | 0.017001 | 14.6885 |  | 86.3166 |  | 208.9226 | 362.3315 | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | 0 | 0 | 0 | 0 |  | #N/A | #N/A |  | #N/A |  | #N/A | 0 | #N/A
Conference/Meeting/Multipurpose | Conference/Meeting/Multipurpose527-1 | [8 empty] | n | [18 empty] | 864 | [23 empty] | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | #N/A |  | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  | #N/A | 0 | #N/A
Conference/Meeting/Multipurpose535 | Conference/Meeting/Multipurpose535 | [8 empty] | n | [9 empty] | ballast replacement |  | 535 |  | 864 |  |  | 535 |  | 864 | [11 empty] | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  | #N/A | #N/A | [10 empty] | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  | #N/A | #N/A | 0
Conference/Meeting/Multipurpose537-1 | Conference/Meeting/Multipurpose511 | [8 empty] | n | [11 empty] | 537-1 |  | 864 |  |  | 511 |  | 864 | [11 empty] | 13.7287 | 14 | 0.53147 | 459.1924 |  | 1.0895 | 941.3444 |  | 1325.5925 |  | 2726.1293 | 2779.9976 | [10 empty] | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  | #N/A | #N/A | 0
Conference/Meeting/Multipurpose511 | Conference/Meeting/Multipurpose0 | [8 empty] | n | [11 empty] | 511 |  | 864 |  |  | 0 |  | 864 | [11 empty] | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | [10 empty] | #N/A | #N/A | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | #N/A | 0
Conference/Meeting/Multipurpose | Conference/Meeting/Multipurpose527-1 | [8 empty] | n | [16 empty] | 527-1 |  | 864 | [33 empty] | #N/A |  | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  | #N/A | 0 | 0
Restrooms | Restrooms | [8 empty] | n | [9 empty] | Restrooms | 1.1655 |  | 8760 | 351 | Restrooms | 1.1064 |  | 8760 | 351
Restrooms521 | Restrooms604 | [8 empty] | n | [9 empty] | replacement costs are for lamps |  | 521 |  | 351 |  |  | 604 |  | 351 |  | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  | #N/A | #N/A | #N/A
Restrooms537-1 | Restrooms520 | [8 empty] | n | [11 empty] | 537-1 |  | 351 |  |  | 520 |  | 351 |  | 1.6542 | 580.6361 |  | 0.98229 | 344.7825 |  | 623.9521 |  |  | 1549.3707 | 9.8847 | 10 | 0.053507 | 18.7808 |  | 0.087315 | 30.6477 |  | 45.6533 |  | 95.0818 | 96.1911 | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  | #N/A | #N/A | #N/A
Restrooms524 | Restrooms0 | [8 empty] | n | [11 empty] | 524 |  | 351 |  |  | 0 |  | 351 |  | 0.42034 | 147.54 |  | 0.28829 | 101.19 |  | 171.6585 |  |  | 420.3885 | 2.7457 | 3 | 0.14719 | 51.6645 |  | 0.027188 | 9.5431 |  | 44.0615 |  | 105.2691 | 115.017 | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | 0 | 0 | 0 | 0 |  | #N/A | #N/A |  | #N/A |  | #N/A | 0 | #N/A
Restrooms | Restrooms534-2 | [8 empty] | n | [16 empty] | 534-2 |  | 351 | [23 empty] | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | #N/A |  | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  | #N/A | 0 | #N/A
Restrooms521 | Restrooms604 | [8 empty] | n | [9 empty] | ballast replacement |  | 521 |  | 351 |  |  | 604 |  | 351 | [11 empty] | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  | #N/A | #N/A | [10 empty] | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  | #N/A | #N/A | 0
Restrooms537-1 | Restrooms520 | [8 empty] | n | [11 empty] | 537-1 |  | 351 |  |  | 520 |  | 351 | [11 empty] | 13.7287 | 14 | 0.47916 | 168.1866 |  | 0.98229 | 344.7825 |  | 485.5196 |  | 998.4886 | 1018.2188 | [10 empty] | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  | #N/A | #N/A | 0
Restrooms524 | Restrooms0 | [8 empty] | n | [11 empty] | 524 |  | 351 |  |  | 0 |  | 351 | [11 empty] | 13.7287 | 14 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | [10 empty] | #N/A | #N/A | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | #N/A | 0
Restrooms | Restrooms534-2 | [8 empty] | n | [16 empty] | 534-2 |  | 351 | [33 empty] | #N/A |  | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  | #N/A | 0 | 0
Gymnasium/Fitness-Fitness Area | Gymnasium/Fitness-Fitness Area | [8 empty] | n | [9 empty] | Gymnasium/Fitness-Fitness Area | 1.1655 |  | 5824 | 351 | Gymnasium/Fitness-Fitness Area | 0.81288 |  | 5824 | 351
Gymnasium/Fitness-Fitness Area535 | Gymnasium/Fitness-Fitness Area535 | [8 empty] | n | [9 empty] | replacement costs are for lamps |  | 535 |  | 351 |  |  | 535 |  | 351 |  | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  | #N/A | #N/A | #N/A
Gymnasium/Fitness-Fitness Area0 | Gymnasium/Fitness-Fitness Area0 | [8 empty] | n | [11 empty] | 0 |  | 351 |  |  | 0 |  | 351 |  | 0 | 0 |  | 0 | 0 |  | 0 |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | 0 | 0 | 0 | 0 |  | #N/A | #N/A |  | #N/A |  | #N/A | 0 | #N/A
Gymnasium/Fitness-Fitness Area0 | Gymnasium/Fitness-Fitness Area0 | [8 empty] | n | [11 empty] | 0 |  | 351 |  |  | 0 |  | 351 |  | 0 | 0 |  | 0 | 0 |  | 0 |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | 0 | 0 | 0 | 0 |  | #N/A | #N/A |  | #N/A |  | #N/A | 0 | #N/A
Gymnasium/Fitness-Fitness Area | Gymnasium/Fitness-Fitness Area0 | [8 empty] | n | [16 empty] | 0 |  | 351 | [23 empty] | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | 0 |  | 0 | 0 |  | #N/A | #N/A |  | #N/A |  | #N/A | 0 | #N/A
Gymnasium/Fitness-Fitness Area535 | Gymnasium/Fitness-Fitness Area535 | [8 empty] | n | [9 empty] | ballast replacement |  | 535 |  | 351 |  |  | 535 |  | 351 | [11 empty] | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  | #N/A | #N/A | [10 empty] | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  | #N/A | #N/A | 0
Gymnasium/Fitness-Fitness Area0 | Gymnasium/Fitness-Fitness Area0 | [8 empty] | n | [11 empty] | 0 |  | 351 |  |  | 0 |  | 351 | [11 empty] | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | [10 empty] | #N/A | #N/A | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | #N/A | 0
Gymnasium/Fitness-Fitness Area0 | Gymnasium/Fitness-Fitness Area0 | [8 empty] | n | [11 empty] | 0 |  | 351 |  |  | 0 |  | 351 | [11 empty] | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | [10 empty] | #N/A | #N/A | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | #N/A | 0
Gymnasium/Fitness-Fitness Area | Gymnasium/Fitness-Fitness Area0 | [8 empty] | n | [16 empty] | 0 |  | 351 | [33 empty] | #N/A |  | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
Lounge/Recreation - Breakroom | Lounge/Recreation - Breakroom | [8 empty] | n | [9 empty] | Lounge/Recreation - Break room | 1.554 |  | 4128 | 351 | Lounge/Recreation - Break room | 0.82417 |  | 4128 | 351
Lounge/Recreation - Breakroom537-1 | Lounge/Recreation - Breakroom521 | [8 empty] | n | [9 empty] | replacement costs are for lamps |  | 537-1 |  | 351 |  |  | 521 |  | 351 |  | 1.8355 | 644.2561 |  | 1.0899 | 382.5601 |  | 692.3181 |  |  | 1719.1343 | 9.8847 | 10 | 0.059369 | 20.8386 |  | 0.096883 | 34.0058 |  | 50.6555 |  | 105.4999 | 106.7307 | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  | #N/A | #N/A | #N/A
Lounge/Recreation - Breakroom572 | Lounge/Recreation - Breakroom0 | [8 empty] | n | [11 empty] | 0 |  | 351 |  |  | 0 |  | 351 |  | 0 | 0 |  | 0 | 0 |  | 0 |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | 0 | 0 | 0 | 0 |  | #N/A | #N/A |  | #N/A |  | #N/A | 0 | #N/A
Lounge/Recreation - Breakroom521 | Lounge/Recreation - Breakroom0 | [8 empty] | n | [11 empty] | 521 |  | 351 |  |  | 0 |  | 351 |  | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | 0 | 0 | 0 | 0 |  | #N/A | #N/A |  | #N/A |  | #N/A | 0 | #N/A
Lounge/Recreation - Breakroom | Lounge/Recreation - Breakroom527-2 | [8 empty] | n | [16 empty] | 527-2 |  | 351 | [23 empty] | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | #N/A |  | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  | #N/A | 0 | #N/A
Lounge/Recreation - Breakroom537-1 | Lounge/Recreation - Breakroom521 | [8 empty] | n | [9 empty] | ballast replacement |  | 537-1 |  | 351 |  |  | 521 |  | 351 | [11 empty] | 13.7287 | 14 | 0.53167 | 186.6147 |  | 1.0899 | 382.5601 |  | 538.7176 |  | 1107.8924 | 1129.7844 | [10 empty] | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  | #N/A | #N/A | 0
Lounge/Recreation - Breakroom572 | Lounge/Recreation - Breakroom0 | [8 empty] | n | [11 empty] | 0 |  | 351 |  |  | 0 |  | 351 | [11 empty] | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | [10 empty] | #N/A | #N/A | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | #N/A | 0
Lounge/Recreation - Breakroom521 | Lounge/Recreation - Breakroom0 | [8 empty] | n | [11 empty] | 521 |  | 351 |  |  | 0 |  | 351 | [11 empty] | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  | #N/A | #N/A | [10 empty] | #N/A | #N/A | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | #N/A | 0
Lounge/Recreation - Breakroom | Lounge/Recreation - Breakroom527-2 | [8 empty] | n | [16 empty] | 527-2 |  | 351 | [33 empty] | #N/A |  | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  | #N/A | 0 | 0
Electrical/Mechanical | Electrical/Mechanical | [8 empty] | n | [9 empty] | Electrical/Mechanical | 1.9425 |  | 2148 | 351 | Electrical/Mechanical | 1.0725 |  | 2148 | 351
Electrical/Mechanical538 | Electrical/Mechanical538 | [8 empty] | n | [9 empty] | replacement costs are for lamps |  | 538 |  | 351 |  |  | 538 |  | 351 |  | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  | #N/A | #N/A | #N/A
Electrical/Mechanical0 | Electrical/Mechanical0 | [8 empty] | n | [11 empty] | 0 |  | 351 |  |  | 0 |  | 351 |  | 0 | 0 |  | 0 | 0 |  | 0 |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | 0 | 0 | 0 | 0 |  | #N/A | #N/A |  | #N/A |  | #N/A | 0 | #N/A
Electrical/Mechanical0 | Electrical/Mechanical0 | [8 empty] | n | [11 empty] | 0 |  | 351 |  |  | 0 |  | 351 |  | 0 | 0 |  | 0 | 0 |  | 0 |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | 0 | 0 | 0 | 0 |  | #N/A | #N/A |  | #N/A |  | #N/A | 0 | #N/A
Electrical/Mechanical | Electrical/Mechanical0 | [8 empty] | n | [16 empty] | 0 |  | 351 | [23 empty] | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | 0 |  | 0 | 0 |  | #N/A | #N/A |  | #N/A |  | #N/A | 0 | #N/A
Electrical/Mechanical538 | Electrical/Mechanical538 | [8 empty] | n | [9 empty] | ballast replacement |  | 538 |  | 351 |  |  | 538 |  | 351 | [11 empty] | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  | #N/A | #N/A | [10 empty] | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  | #N/A | #N/A | 0
Electrical/Mechanical0 | Electrical/Mechanical0 | [8 empty] | n | [11 empty] | 0 |  | 351 |  |  | 0 |  | 351 | [11 empty] | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | [10 empty] | #N/A | #N/A | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | #N/A | 0
Electrical/Mechanical0 | Electrical/Mechanical0 | [8 empty] | n | [11 empty] | 0 |  | 351 |  |  | 0 |  | 351 | [11 empty] | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | [10 empty] | #N/A | #N/A | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | #N/A | 0
Electrical/Mechanical | Electrical/Mechanical0 | [8 empty] | n | [16 empty] | 0 |  | 351 | [33 empty] | #N/A |  | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
[18 empty] | Mid-rise Apartment_Interior Lighting LPD |  | Mid-rise Apartment |  |  |  |  | Mid-rise Apartment
Office-Enclosed | Office-Enclosed | [9 empty] | n | [8 empty] | Office-Enclosed | 1.2166 |  | 3231 | 950 | Office-Enclosed | 0.86802 |  | 3231 | 950
Office-Enclosed535 | Office-Enclosed531 | [9 empty] | n | [8 empty] | replacement costs are for lamps |  | 535 |  | 950 |  |  | 531 |  | 950 |  | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  | #N/A | #N/A | #N/A
Office-Enclosed539 | Office-Enclosed539 | [9 empty] | n | [10 empty] | 539 |  | 950 |  |  | 539 |  | 950 |  | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  | #N/A | #N/A | #N/A
Office-Enclosed537-2 | Office-Enclosed0 | [9 empty] | n | [10 empty] | 537-2 |  | 950 |  |  | 0 |  | 950 |  | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | 0 | 0 | 0 | 0 |  | #N/A | #N/A |  | #N/A |  | #N/A | 0 | #N/A
Office-Enclosed | Office-Enclosed537-1 | [9 empty] | n | [15 empty] | 537-1 |  | 950 | [23 empty] | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  | #N/A | #N/A | #N/A
Office-Enclosed535 | Office-Enclosed531 | [9 empty] | n | [8 empty] | ballast replacement |  | 535 |  | 950 |  |  | 531 |  | 950 | [11 empty] | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  | #N/A | #N/A | [10 empty] | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  | #N/A | #N/A | 0
Office-Enclosed539 | Office-Enclosed539 | [9 empty] | n | [10 empty] | 539 |  | 950 |  |  | 539 |  | 950 | [11 empty] | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  | #N/A | #N/A | [10 empty] | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  | #N/A | #N/A | 0
Office-Enclosed537-2 | Office-Enclosed0 | [9 empty] | n | [10 empty] | 537-2 |  | 950 |  |  | 0 |  | 950 | [11 empty] | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  | #N/A | #N/A | [10 empty] | #N/A | #N/A | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | #N/A | 0
Office-Enclosed | Office-Enclosed537-1 | [9 empty] | n | [15 empty] | 537-1 |  | 950 | [33 empty] | #N/A |  | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  | #N/A | 0 | 0
Corridor/Transition | Corridor/Transition | [9 empty] | n | [8 empty] | Corridor/Transition | 0.553 |  | 8760 | 3345 | Corridor/Transition | 0.51612 |  | 8760 | 3345
Corridor/Transition530 | Corridor/Transition521 | [9 empty] | n | [8 empty] | replacement costs are for lamps |  | 530 |  | 3345 |  |  | 521 |  | 3345 |  | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  | #N/A | #N/A | #N/A
Corridor/Transition537-2 | Corridor/Transition0 | [9 empty] | n | [10 empty] | 537-2 |  | 3345 |  |  | 0 |  | 3345 |  | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | 0 | 0 | 0 | 0 |  | #N/A | #N/A |  | #N/A |  | #N/A | 0 | #N/A
Corridor/Transition0 | Corridor/Transition0 | [9 empty] | n | [10 empty] | 0 |  | 3345 |  |  | 0 |  | 3345 |  | 0 | 0 |  | 0 | 0 |  | 0 |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | 0 | 0 | 0 | 0 |  | #N/A | #N/A |  | #N/A |  | #N/A | 0 | #N/A
| Corridor/Transition527-2 | [9 empty] | n | [15 empty] | 0 |  | 3345 | [23 empty] | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | 0 | 0 | 0 | 0 |  | #N/A | #N/A |  | #N/A |  | #N/A | 0 | #N/A
Corridor/Transition530 | Corridor/Transition521 | [9 empty] | n | [8 empty] | ballast replacement |  | 530 |  | 3345 |  |  | 521 |  | 3345 | [11 empty] | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  | #N/A | #N/A | [10 empty] | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  | #N/A | #N/A | 0
Corridor/Transition537-2 | Corridor/Transition0 | [9 empty] | n | [10 empty] | 537-2 |  | 3345 |  |  | 0 |  | 3345 | [11 empty] | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  | #N/A | #N/A | [10 empty] | #N/A | #N/A | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | #N/A | 0
Corridor/Transition0 | Corridor/Transition0 | [9 empty] | n | [10 empty] | 0 |  | 3345 |  |  | 0 |  | 3345 | [11 empty] | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | [10 empty] | #N/A | #N/A | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | #N/A | 0
| Corridor/Transition527-2 | [9 empty] | n | [12 empty] | 2508 |  |  | 0 |  | 3345 | [33 empty] | #N/A | #N/A | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | #N/A | 0
[11 empty] | n | [8 empty] | Dwelling Units Average | 0.585 |  |  | 29450 | Dwelling Units Average | 0.46 |  |  | 29450
Averages of low and high end apartment | [10 empty] | n | [8 empty] | 50% of low end and high end for new construction and replacements |  | Average New Construction |  |  | 50% of low end and high end for new construction and replacements |  | Average New Construction | [12 empty] | #N/A | [21 empty] | #N/A | [12 empty] | #N/A
[11 empty] | n | [8 empty] | replacement costs are for lamps, 50% of each low-end |  | 501 |  |  | replacement costs are for lamps, 50% of each low-end |  | 501 | [14 empty] | #N/A | [9 empty] | #N/A | [11 empty] | #N/A | [9 empty] | #N/A
[11 empty] | n | [10 empty] | 700 |  |  |  |  | 700 | [14 empty] | #N/A | [9 empty] | #N/A | [11 empty] | #N/A | [9 empty] | #N/A
[11 empty] | n | [10 empty] | 530 |  |  |  |  | 530 | [14 empty] | #N/A | [9 empty] | #N/A | [11 empty] | #N/A | [9 empty] | #N/A
[11 empty] | n | [8 empty] | high-end |  | 505 |  |  | high-end |  | 505 | [14 empty] | #N/A | [9 empty] | #N/A | [11 empty] | #N/A | [9 empty] | #N/A
[11 empty] | n | [10 empty] | 501 |  |  |  |  | 501 | [14 empty] | #N/A | [9 empty] | #N/A | [11 empty] | #N/A | [9 empty] | #N/A
[11 empty] | n | [10 empty] | 500 |  |  |  |  | 500 | [14 empty] | #N/A | [9 empty] | #N/A | [11 empty] | #N/A | [9 empty] | #N/A
[11 empty] | n | [10 empty] | 700 |  |  |  |  | 700 | [14 empty] | #N/A | [9 empty] | #N/A | [11 empty] | #N/A | [9 empty] | #N/A
[11 empty] | n | [10 empty] | 530 |  |  |  |  | 530 | [14 empty] | #N/A | [9 empty] | #N/A | [11 empty] | #N/A | [9 empty] | #N/A
[11 empty] | n | [8 empty] | replacement costs are for ballasts, 50% of each low-end |  | 501 |  |  | replacement costs are for ballasts, 50% of each low-end |  | 501
[11 empty] | n | [10 empty] | 700 |  |  |  |  | 700 | [14 empty] | #N/A | [9 empty] | #N/A | [11 empty] | #N/A | [9 empty] | #N/A
[11 empty] | n | [10 empty] | 530 |  |  |  |  | 530 | [14 empty] | #N/A | [9 empty] | #N/A | [11 empty] | #N/A | [9 empty] | #N/A
[11 empty] | n | [8 empty] | high-end |  | 505 |  |  | high-end |  | 505 | [14 empty] | #N/A | [9 empty] | #N/A | [11 empty] | #N/A | [9 empty] | #N/A
[11 empty] | n | [10 empty] | 501 |  |  |  |  | 501 | [14 empty] | #N/A | [9 empty] | #N/A | [11 empty] | #N/A | [9 empty] | #N/A
[11 empty] | n | [10 empty] | 500 |  |  |  |  | 500 | [14 empty] | #N/A | [9 empty] | #N/A | [11 empty] | #N/A | [9 empty] | #N/A
[11 empty] | n | [10 empty] | 700 |  |  |  |  | 700 | [14 empty] | #N/A | [9 empty] | #N/A | [11 empty] | #N/A | [9 empty] | #N/A
[11 empty] | n | [10 empty] | 530 |  |  |  |  | 530 | [14 empty] | #N/A | [9 empty] | #N/A | [11 empty] | #N/A | [9 empty] | #N/A
[11 empty] | n | [30 empty] | #N/A | [9 empty] | #N/A | [11 empty] | #N/A | [9 empty] | #N/A
Dwelling Units | Dwelling Units | [18 empty] | Dwelling Units Low End | 0.39 |  | 2875 | 29450 | Dwelling Units Low End | 0.3 | sub-total | 2875 | 29450 | [10 empty] | #N/A | [21 empty] | #N/A
DwellingUnits501_Low | DwellingUnits501_Low | [18 empty] | replacement costs are for lamps |  | 501 |  | 29450 |  |  | 501 |  | 29450 |  | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  | #N/A | #N/A | #N/A
DwellingUnits700_Low | DwellingUnits700_Low | [20 empty] | 700 |  | 29450 |  |  | 700 |  | 29450 |  | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  | #N/A | #N/A | #N/A
DwellingUnits530_Low | DwellingUnits530_Low | [20 empty] | 530 |  | 29450 |  |  | 530 |  | 29450 |  | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  | #N/A | #N/A | #N/A
[24 empty] | 29450 |  |  |  |  | 29450 | [44 empty] | 0
DwellingUnits501_Low | DwellingUnits501_Low | [18 empty] | ballast replacement |  | 501 |  | 29450 |  |  | 501 |  | 29450 | [11 empty] | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  | #N/A | #N/A | [10 empty] | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  | #N/A | #N/A | 0
DwellingUnits700_Low | DwellingUnits700_Low | [20 empty] | 700 |  | 29450 |  |  | 700 |  | 29450 | [11 empty] | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  | #N/A | #N/A | [10 empty] | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  | #N/A | #N/A | 0
DwellingUnits530_Low | DwellingUnits530_Low | [20 empty] | 530 |  | 29450 |  |  | 530 |  | 29450 | [11 empty] | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  | #N/A | #N/A | [10 empty] | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  | #N/A | #N/A | 0
Dwelling Units | Dwelling Units | [18 empty] | Dwelling Units High End | 0.78 |  | 2875 | 29450 | Dwelling Units High End | 0.62 |  | 2875 | 29450 | [10 empty] | #N/A | [21 empty] | #N/A | [11 empty] | 0
DwellingUnits505_High | DwellingUnits505_High | [18 empty] | replacement costs are for lamps |  | 505 |  | 29450 |  |  | 505 |  | 29450 |  | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  | #N/A | #N/A | #N/A
DwellingUnits501_High | DwellingUnits500_High | [20 empty] | 501 |  | 29450 |  |  | 500 |  | 29450 |  | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  | #N/A | #N/A | #N/A
DwellingUnits500_High | DwellingUnits700_High | [20 empty] | 500 |  | 29450 |  |  | 700 |  | 29450 |  | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  | #N/A | #N/A | #N/A
DwellingUnits700_High | DwellingUnits701_High | [20 empty] | 700 |  | 29450 |  |  | 701 |  | 29450 |  | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  | #N/A | #N/A | #N/A
DwellingUnits530_High | DwellingUnits530_High | [20 empty] | 530 |  | 29450 |  |  | 530 |  | 29450 |  | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  | #N/A | #N/A | #N/A
DwellingUnits505_High | DwellingUnits505_High | [18 empty] | ballast replacement |  | 505 |  | 29450 |  |  | 505 |  | 29450 | [11 empty] | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  | #N/A | #N/A | [10 empty] | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  | #N/A | #N/A | 0
DwellingUnits501_High | DwellingUnits500_High | [20 empty] | 501 |  | 29450 |  |  | 500 |  | 29450 | [11 empty] | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  | #N/A | #N/A | [10 empty] | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  | #N/A | #N/A | 0
DwellingUnits500_High | DwellingUnits700_High | [20 empty] | 500 |  | 29450 |  |  | 700 |  | 29450 | [11 empty] | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  | #N/A | #N/A | [10 empty] | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  | #N/A | #N/A | 0
DwellingUnits700_High | DwellingUnits701_High | [20 empty] | 700 |  | 29450 |  |  | 701 |  | 29450 | [11 empty] | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  | #N/A | #N/A | [10 empty] | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  | #N/A | #N/A | 0
DwellingUnits530_High | DwellingUnits530_High | [20 empty] | 530 |  | 29450 |  |  | 530 |  | 29450 | [11 empty] | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  | #N/A | #N/A | [10 empty] | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  | #N/A | #N/A | 0
Note on AR472: Brian Thornton: subtotal low end 2009
Note on AR480: Brian Thornton: subtotal high end 2009
Note on BN472: Brian Thornton: subtotal low end 2009
Note on BN480: Brian Thornton: subtotal high end 2009

## Int Ltg LPD Space Type 90_1 All (hidden)
90.1 Cost Effectiveness - Interior Lighting Power Density - Fixture Costs per Square Foot for Each Space Type
90.1-2019 vs 90.1-2022
Interior lighting costs by space type and fixture type
Values come from "Int ighting Comp" worksheet in this workbook.
Interior Lighting Costs by Space Type, 90.1-2016
Entry=Blue | 90.1-2019 Lookup Values1 | 90.1-2019 Space Types2 | 90.1 Lighting Subcommittee Model Number3 | Space Type Lighting Power Allowance W/ft24 | Fixture ID Number5 | Fixture Type6 | Lamp Type17 | Lamp Wattage8 | Number of Lamps9 | Net Est. Fixture Lum/ft210 | Fixture Watts11 | Lamp Life Hours12 | Quantity of Fixtures/ft213 | Fixture Watts/ft214 | not used15 | not used16 | New_Fixture + Lamp Cost, $/ft2_17 | not used18 | not used19 | not used20 | Labor Cost $/ft221 | Not Used22 | Not Used23 | RepLmp_Lamp Cost $/ft224 | Not Used25 | Not Used26 | Not Used27 | Rep_Lmp_Labor Cost/ft228 | Not Used29 | Rep_Lmp_Total $/ft230 | RepBal_Ballast Life Hours31 | RepBal_Ballast Cost, $/ft232 | RepBal_Not Used33 | RepBal_Not Used34 | RepBal_Labor Cost/ft235 | Not Used36 | Not Used37 | case_data | Case | space
| 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33 | 34 | 35 | 36 | 37 | x | x | x
|  | Space Type Lighting Descriptions and Cost Parameters | [14 empty] | New Construction Cost | [6 empty] | Lamp Replacement Cost | [6 empty] | Ballast Replacement Cost | [6 empty] | x | x | x
| 90.1-2019 Lookup Values | 90.1-2019 Space Types | 90.1 Lighting Subcommittee Model Number | Space Type Lighting Power Allowance W/ft2 | Fixture ID Number | Fixture Type | Lamp Type1 | Lamp Wattage | Number of Lamps | Net Est. Fixture Lum/ft2 | Fixture Watts | Lamp Life Hours | Quantity of Fixtures/ft2 | Fixture Watts/ft2 | not used | not used | Fixture + Lamp Cost, $/ft2 | not used | not used | not used | Labor Cost $/ft2 | Not Used | Not Used | Lamp Cost $/ft2 | Not Used | Not Used | Not Used | Labor Cost/ft2 | Not Used | Total $/ft2 | Ballast Life Hours | Ballast Cost, $/ft2 | Not Used | Not Used | Labor Cost/ft2 | Not Used | Not Used | x | x | x
2016 | Classroom/Lecture/Training | Classroom/Lecture/Training |  | 0.92 |  |  | 47.15 |  |  | 76.869 | [6 empty] | 5.4896 | [20 empty] | x | 2013 | Classroom/Lecture/Training
2016 | Classroom/Lecture/Training600_LED |  | 3.1 | 0.92 | 600_LED | LED | High Perf Lensed | 1 | 40 | 63.45 | 40 | 50000 | 0.017625 | 0.705 |  |  | 3.0385 |  |  |  | 1.6357 |  |  | 0.00705 |  |  |  | 0.010839 |  | 0.017889 | 50000 | 2.2736 |  |  | 1.6357 |  |  | 2013 | 2013 | Classroom/Lecture/Training
2016 | Classroom/Lecture/Training701 |  | 3.1 | Match? | 701 | LED | Downlight open | 1 | 12 | 4.284 | 12 | 50000 | 0.0058333 | 0.07 |  |  | 0.96289 |  |  |  | 0.35875 |  |  | 0.0007 |  |  |  | 0.0035875 |  | 0.0042875 | 50000 | 0.72164 |  |  | 0.35875 |  |  | 2013 | 2013 | Classroom/Lecture/Training
2016 | Classroom/Lecture/Training0 |  | 3.1 | Yes | 0 | 0 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 |  |  |  | 0 |  |  | 0 |  |  |  | 0 |  | 0 | 0 | 0 |  |  | 0 |  |  | 2013 | 2013 | Classroom/Lecture/Training
2016 | Classroom/Lecture/Training703 |  | 3.1 |  | 703 | LED | Linear WW Open | 1 | 75 | 9.135 | 75 | 50000 | 0.0019333 | 0.145 |  |  | 1.4882 |  |  |  | 0.19024 |  |  | 0.00145 |  |  |  | 0.001189 |  | 0.002639 | 50000 | 1.1151 |  |  | 0.19024 |  |  | 2013 | 2013 | Classroom/Lecture/Training
2016 |  | Conference/Meeting/Multipurpose |  | 1.07 | [5 empty] | 55.2051 | [6 empty] | 7.2976 | [20 empty] | x | 2013 | Conference/Meeting/Multipurpose
2016 | Conference/Meeting/Multipurpose731 |  | 31 | 1.08 | 731 | LED | Narrow Linear | 1 | 40 | 35.64 | 40 | 50000 | 0.01125 | 0.45 |  |  | 4.302 |  |  |  | 0.90705 |  |  | 0.0045 |  |  |  | 0.0069188 |  | 0.011419 | 50000 | 3.2231 |  |  | 0.90705 |  |  | 2013 | 2013 | Conference/Meeting/Multipurpose
2016 | Conference/Meeting/Multipurpose511 |  | 31 | Match? | 511 | PAR30L | Downlight open - flood | 60 | 1 | 2.4651 | 60 | 4200 | 0.0073333 | 0.44 |  |  | 0.42871 |  |  |  | 0.451 |  |  | 0.15679 |  |  |  | 0.02134 |  | 0.17813 | 0 | 0 |  |  | 0 |  |  | 2013 | 2013 | Conference/Meeting/Multipurpose
2016 | Conference/Meeting/Multipurpose0 |  | 31 | Yes | 0 | 0 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 |  |  |  | 0 |  |  | 0 |  |  |  | 0 |  | 0 | 0 | 0 |  |  | 0 |  |  | 2013 | 2013 | Conference/Meeting/Multipurpose
2016 | Conference/Meeting/Multipurpose727-1 |  | 31 |  | 727-1 | LED | WW Open | 1 | 20 | 17.1 | 20 | 50000 | 0.0095 | 0.19 |  |  | 2.5669 |  |  |  | 0.58425 |  |  | 0.0019 |  |  |  | 0.0058425 |  | 0.0077425 | 50000 | 1.9238 |  |  | 0.58425 |  |  | 2013 | 2013 | Conference/Meeting/Multipurpose
2016 |  | Corridor/Transition |  | 0.66 | [5 empty] | 40.896 | [6 empty] | 8.1008 | [20 empty] | x | 2013 | Corridor/Transition
2016 | Corridor/Transition701 |  | 2 | 0.66 | 701 | LED | Downlight open | 1 | 12 | 23.256 | 12 | 50000 | 0.031667 | 0.38 |  |  | 5.2271 |  |  |  | 1.9475 |  |  | 0.0038 |  |  |  | 0.019475 |  | 0.023275 | 50000 | 3.9175 |  |  | 1.9475 |  |  | 2013 | 2013 | Corridor/Transition
2016 | Corridor/Transition0 |  | 2 | Match? | 0 | 0 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 |  |  |  | 0 |  |  | 0 |  |  |  | 0 |  | 0 | 0 | 0 |  |  | 0 |  |  | 2013 | 2013 | Corridor/Transition
2016 | Corridor/Transition0 |  | 2 | Yes | 0 | 0 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 |  |  |  | 0 |  |  | 0 |  |  |  | 0 |  | 0 | 0 | 0 |  |  | 0 |  |  | 2013 | 2013 | Corridor/Transition
2016 | Corridor/Transition703 |  | 2 |  | 703 | LED | Linear WW Open | 1 | 75 | 17.64 | 75 | 50000 | 0.0037333 | 0.28 |  |  | 2.8737 |  |  |  | 0.36736 |  |  | 0.0028 |  |  |  | 0.002296 |  | 0.005096 | 50000 | 2.1532 |  |  | 0.36736 |  |  | 2013 | 2013 | Corridor/Transition
2016 |  | Dining Area |  | 0.63 | [5 empty] | 41.261 | [6 empty] | 4.1506 | [20 empty] | x | 2013 | Dining Area
2016 | Dining Area731 |  | 6 | 0.63 | 731 | LED | Narrow Linear | 1 | 40 | 12.672 | 40 | 50000 | 0.004 | 0.16 | 0.25397 | 0.16 | 1.5296 |  |  |  | 0.32251 |  |  | 0.0016 |  |  |  | 0.00246 |  | 0.00406 | 50000 | 1.146 |  |  | 0.32251 |  |  | 2013 | 2013 | Dining Area
2016 | Dining Area522 |  | 6 | Match? | 522 | LED | Downlight open | 1 | 18 | 8.505 | 18 | 50000 | 0.01 | 0.18 | 0.28571 | 0.18 | 1.5518 |  |  |  | 0.615 |  |  | 0.0018 |  |  |  | 0.00615 |  | 0.00795 | 0 | 1.1625 |  |  | 0.615 |  |  | 2013 | 2013 | Dining Area
2016 | Dining Area0 |  | 6 | Yes | 0 | 0 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  | 0 |  |  | 0 |  |  |  | 0 |  | 0 | 0 | 0 |  |  | 0 |  |  | 2013 | 2013 | Dining Area
2016 | Dining Area537-1 |  | 6 |  | 537-1 | F32T8 - Bi-Pin Base | Linear WW Open | 32 | 1 | 20.084 | 29 | 36000 | 0.01 | 0.29 | 0.46032 | 0.29 | 1.0692 |  |  |  | 0.615 |  |  | 0.0335 |  |  |  | 0.054667 |  | 0.088167 | 50000 | 0.3 |  |  | 0.615 |  |  | 2013 | 2013 | Dining Area
2016 |  | Dwelling-Unit |  | 0.29 |  |  | "other lamps" not included |  |  | 8.9406 |  |  | 0.015759 |  |  | 48.3614 | 0.018133 | [20 empty] | x | 2013 | Dwelling-Unit
2016 | Dwelling-Unit301 |  | NA | 0.29 | 301 | A19 | Inc residential screw in lamp | 60 | 1 | 6.3568 | 60 | 1000 | 0.011772 | 0.09 | 0.74699 | 44.8193 | 0.010477 | 0.001519 | 0.011772 |  | 0 |  |  | 0.010477 |  |  |  | 0 |  | 0.010477 | 0 | 0 |  |  | 0 |  |  | 2013 | 2013 | Dwelling-Unit
2016 | Dwelling-Unit302 |  | NA | Match? | 302 | A19 | CFL residential screw in lamp | 14 | 1 | 2.5837 | 14 | 10000 | 0.0039873 | 0.2 | 0.25301 | 3.5422 | 0.0076555 | 0.01424 | 0.0039873 |  | 0 |  |  | 0.0076555 |  |  |  | 0 |  | 0.0076555 | 0 | 0 |  |  | 0 |  |  | 2013 | 2013 | Dwelling-Unit
2016 | Dwelling-Unit303 |  | NA | Yes | 303 | A19 | LEC residential screw in lamp | 9 | 1 | 0 | 9 | 15000 | 0 | 0 | 0 | 0 | 0 |  |  |  | 0 |  |  | 0 |  |  |  | 0 |  | 0 | 0 | 0 |  |  | 0 |  |  | 2013 | 2013 | Dwelling-Unit
2016 | Dwelling-Unit0 |  | NA |  | 0 | 0 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  | 0 |  |  | 0 |  |  |  | 0 |  | 0 | 0 | 0 |  |  | 0 |  |  | 2013 | 2013 | Dwelling-Unit
2016 |  | Electrical/Mechanical |  | 0.43 | [5 empty] | 36.045 | [6 empty] | 4.0775 | [20 empty] | x | 2013 | Electrical/Mechanical
2016 | Electrical/Mechanical738 |  | 4 | 0.43 | 738 | LED | Linear Industrial | 1 | 38 | 23.805 | 38 | 50000 | 0.0060526 | 0.23 | 0.53488 | 0.23 | 1.5155 |  |  |  | 0.35027 |  |  | 0.0023 |  |  |  | 0.0037224 |  | 0.0060224 | 50000 | 1.1349 |  |  | 0.35027 |  |  | 2013 | 2013 | Electrical/Mechanical
2016 | Electrical/Mechanical739 |  | 4 | Match? | 739 | LED | Task | 1 | 10 | 12.24 | 10 | 50000 | 0.02 | 0.2 | 0.46512 | 0.2 | 2.562 |  |  |  | 0.6027 |  |  | 0.002 |  |  |  | 0.0123 |  | 0.0143 | 50000 | 1.92 |  |  | 0.6027 |  |  | 2013 | 2013 | Electrical/Mechanical
2016 | Electrical/Mechanical0 |  | 4 | Yes | 0 | 0 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  | 0 |  |  | 0 |  |  |  | 0 |  | 0 | 0 | 0 |  |  | 0 |  |  | 2013 | 2013 | Electrical/Mechanical
2016 | Electrical/Mechanical0 |  | 4 |  | 0 | 0 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  | 0 |  |  | 0 |  |  |  | 0 |  | 0 | 0 | 0 |  |  | 0 |  |  | 2013 | 2013 | Electrical/Mechanical
2016 |  | Food Preparation |  | 1.06 | [5 empty] | 85.248 | [6 empty] | 9.3639 | [20 empty] | x | 2013 | Food Preparation
2016 | Food Preparation731 |  | 8 | 1.06 | 731 | LED | Narrow Linear | 1 | 40 | 71.28 | 40 | 50000 | 0.0225 | 0.9 |  |  | 8.604 |  |  |  | 1.8141 |  |  | 0.009 |  |  |  | 0.013838 |  | 0.022838 | 50000 | 6.4463 |  |  | 1.8141 |  |  | 2013 | 2013 | Food Preparation
2016 | Food Preparation730 |  | 8 | Match? | 730 | LED | Linear Direct Lensed | 1 | 40 | 13.968 | 40.3 | 50000 | 0.0039702 | 0.16 |  |  | 0.7599 |  |  |  | 0.24417 |  |  | 0.0015881 |  |  |  | 0.0024417 |  | 0.0040298 | 50000 | 0.56873 |  |  | 0.24417 |  |  | 2013 | 2013 | Food Preparation
2016 | Food Preparation0 |  | 8 | Yes | 0 | 0 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 |  |  |  | 0 |  |  | 0 |  |  |  | 0 |  | 0 | 0 | 0 |  |  | 0 |  |  | 2013 | 2013 | Food Preparation
2016 | Food Preparation0 |  | 8 |  | 0 | 0 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 |  |  |  | 0 |  |  | 0 |  |  |  | 0 |  | 0 | 0 | 0 |  |  | 0 |  |  | 2013 | 2013 | Food Preparation
2016 |  | Gymnasium/Fitness-Fitness Area |  | 0.5 | [5 empty] | 45 | [6 empty] | 8.8116 | [20 empty] | x | 2013 | Gymnasium/Fitness-Fitness Area
2016 | Gymnasium/Fitness-Fitness Area735 |  | 126 | 0.5 | 735 | LED | Linear Dir/Ind | 1 | 38 | 45 | 38 | 50000 | 0.013158 | 0.5 |  |  | 8.8116 |  |  |  | 1.0609 |  |  | 0.005 |  |  |  | 0.0080921 |  | 0.013092 | 50000 | 6.6049 |  |  | 1.0609 |  |  | 2013 | 2013 | Gymnasium/Fitness-Fitness Area
2016 | Gymnasium/Fitness-Fitness Area0 |  | 126 | Match? | 0 | 0 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 |  |  |  | 0 |  |  | 0 |  |  |  | 0 |  | 0 | 0 | 0 |  |  | 0 |  |  | 2013 | 2013 | Gymnasium/Fitness-Fitness Area
2016 | Gymnasium/Fitness-Fitness Area0 |  | 126 | Yes | 0 | 0 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 |  |  |  | 0 |  |  | 0 |  |  |  | 0 |  | 0 | 0 | 0 |  |  | 0 |  |  | 2013 | 2013 | Gymnasium/Fitness-Fitness Area
2016 | Gymnasium/Fitness-Fitness Area0 |  | 126 |  | 0 | 0 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 |  |  |  | 0 |  |  | 0 |  |  |  | 0 |  | 0 | 0 | 0 |  |  | 0 |  |  | 2013 | 2013 | Gymnasium/Fitness-Fitness Area
2016 |  | Highway Lodging Guest Rooms |  | 0.77 | [5 empty] | 19.3758 | [6 empty] | 2.7561 | [20 empty] | x | 2013 | Highway Lodging Guest Rooms
2016 | Highway Lodging Guest Rooms524 |  | 75.01 | 0.77 | 524 | Double Biax - 4 Pin | indirect Wall Scounce | 18 | 2 | 14.3358 | 39 | 10000 | 0.017692 | 0.69 |  |  | 2.142 |  |  |  | 1.0881 |  |  | 0.55554 |  |  |  | 0.10262 |  | 0.65815 | 50000 | 0 |  |  | 0 |  |  | 2013 | 2013 | Highway Lodging Guest Rooms
2016 | Highway Lodging Guest Rooms720 |  | 75.01 | Match? | 720 | LED | Downlight Lensed | 1 | 22 | 5.04 | 22 | 50000 | 0.0036364 | 0.08 |  |  | 0.61413 |  |  |  | 0.22364 |  |  | 0.0008 |  |  |  | 0.0022364 |  | 0.0030364 | 50000 | 0.46 |  |  | 0.22364 |  |  | 2013 | 2013 | Highway Lodging Guest Rooms
2016 | Highway Lodging Guest Rooms0 |  | 75.01 | Yes | 0 | 0 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 |  |  |  | 0 |  |  | 0 |  |  |  | 0 |  | 0 | 0 | 0 |  |  | 0 |  |  | 2013 | 2013 | Highway Lodging Guest Rooms
2016 | Highway Lodging Guest Rooms0 |  | 75.01 |  | 0 | 0 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 |  |  |  | 0 |  |  | 0 |  |  |  | 0 |  | 0 | 0 | 0 |  |  | 0 |  |  | 2013 | 2013 | Highway Lodging Guest Rooms
2016 |  | Laundry-Washing |  | 0.43 | [5 empty] | 37.539 | [6 empty] | 2.0422 | [20 empty] | x | 2013 | Laundry-Washing
2016 | Laundry-Washing730 |  | 82 | 0.43 | 730 | LED | Linear Direct Lensed | 1 | 40 | 37.539 | 40.3 | 50000 | 0.01067 | 0.43 |  |  | 2.0422 |  |  |  | 0.6562 |  |  | 0.004268 |  |  |  | 0.006562 |  | 0.01083 | 50000 | 1.5285 |  |  | 0.6562 |  |  | 2013 | 2013 | Laundry-Washing
2016 | Laundry-Washing0 |  | 82 | Match? | 0 | 0 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 |  |  |  | 0 |  |  | 0 |  |  |  | 0 |  | 0 | 0 | 0 |  |  | 0 |  |  | 2013 | 2013 | Laundry-Washing
2016 | Laundry-Washing0 |  | 82 | Yes | 0 | 0 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 |  |  |  | 0 |  |  | 0 |  |  |  | 0 |  | 0 | 0 | 0 |  |  | 0 |  |  | 2013 | 2013 | Laundry-Washing
2016 | Laundry-Washing0 |  | 82 |  | 0 | 0 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 1.0077e-07 |  |  | 0 |  |  |  | 0 |  |  | 0 |  |  |  | 0 |  | 0 | 0 | 0 |  |  | 0 |  |  | 2013 | 2013 | Laundry-Washing
2016 |  | Library |  | 0.82 | [5 empty] | 65.16 | [6 empty] | 11.2681 | [20 empty] | x | 2013 | Library
2016 | Library735 |  | 19 | 0.82 | 735 | LED | Linear Dir/Ind | 1 | 38 | 45 | 38 | 50000 | 0.013158 | 0.5 |  |  | 8.8116 |  |  |  | 1.0609 |  |  | 0.005 |  |  |  | 0.0080921 |  | 0.013092 | 50000 | 6.6049 |  |  | 1.0609 |  |  | 2013 | 2013 | Library
2016 | Library720 |  | 19 | Match? | 720 | LED | Downlight Lensed | 1 | 22 | 20.16 | 22 | 50000 | 0.014545 | 0.32 |  |  | 2.4565 |  |  |  | 0.89455 |  |  | 0.0032 |  |  |  | 0.0089455 |  | 0.012145 | 50000 | 1.84 |  |  | 0.89455 |  |  | 2013 | 2013 | Library
2016 | Library0 |  | 19 | Yes | 0 | 0 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 |  |  |  | 0 |  |  | 0 |  |  |  | 0 |  | 0 | 0 | 0 |  |  | 0 |  |  | 2013 | 2013 | Library
2016 | Library0 |  | 19 |  | 0 | 0 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 |  |  |  | 0 |  |  | 0 |  |  |  | 0 |  | 0 | 0 | 0 |  |  | 0 |  |  | 2013 | 2013 | Library
2016 |  | Lounge/Recreation - Breakroom |  | 0.62 | [5 empty] | 42.1178 | [6 empty] | 10.6975 | [20 empty] | x | 2013 | Lounge/Recreation - Breakroom
2016 | Lounge/Recreation - Breakroom522 |  | 9 | 0.629 | 522 | LED | Downlight open | 1 | 18 | 16.0177 | 18 | 50000 | 0.018833 | 0.339 |  |  | 2.9226 |  |  |  | 1.1583 |  |  | 0.00339 |  |  |  | 0.011583 |  | 0.014972 | 0 | 2.1894 |  |  | 1.1583 |  |  | 2013 | 2013 | Lounge/Recreation - Breakroom
2016 | Lounge/Recreation - Breakroom0 |  | 9 | Match? | 0 | 0 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 |  |  |  | 0 |  |  | 0 |  |  |  | 0 |  | 0 | 0 | 0 |  |  | 0 |  |  | 2013 | 2013 | Lounge/Recreation - Breakroom
2016 | Lounge/Recreation - Breakroom0 |  | 9 | Yes | 0 | 0 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 |  |  |  | 0 |  |  | 0 |  |  |  | 0 |  | 0 | 0 | 0 |  |  | 0 |  |  | 2013 | 2013 | Lounge/Recreation - Breakroom
2016 | Lounge/Recreation - Breakroom727-2 |  | 9 |  | 727-2 | LED | WW Open | 1 | 25 | 26.1 | 25 | 50000 | 0.0116 | 0.29 |  |  | 7.7749 |  |  |  | 0.7134 |  |  | 0.0029 |  |  |  | 0.007134 |  | 0.010034 | 50000 | 5.829 |  |  | 0.7134 |  |  | 2013 | 2013 | Lounge/Recreation - Breakroom
2016 |  | Lobby |  | 1 | [5 empty] | 63.99 | [6 empty] | 13.1116 | [14 empty] | #N/A | [5 empty] | x | 2013 | Lobby
2016 | Lobby723 |  | 20.1 | 1 | 723 | LED | Indirect Pendant | 1 | 46 | 45.36 | 46 | 50000 | 0.015652 | 0.72 | 0.69 | 0.69 | 9.962 |  |  |  | 1.262 |  |  | 0.0072 |  |  |  | 0.0096261 |  | 0.016826 | 50000 | 7.4661 |  |  | 1.262 |  |  | 2013 | 2013 | Lobby
2016 | Lobby522 |  | 20.1 | Match? | 522 | LED | Downlight open | 1 | 18 | 5.67 | 18 | 50000 | 0.0066667 | 0.12 | 0.14 | 0.14 | 1.0345 |  |  |  | 0.41 |  |  | 0.0012 |  |  |  | 0.0041 |  | 0.0053 | 0 | 0.775 |  |  | 0.41 |  |  | 2013 | 2013 | Lobby
2016 | Lobby0 |  | 20.1 | Yes | 0 | 0 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  | 0 |  |  | 0 |  |  |  | 0 |  | 0 | 0 | 0 |  |  | 0 |  |  | 2013 | 2013 | Lobby
2016 | Lobby534-2 |  | 20.1 |  | 534-2 | F32T8 - Bi-Pin Base | Linear Wall Cove | 32 | 1 | 12.96 | 29 | 36000 | 0.0055172 | 0.16 | 0.17 | 0.17 | 2.115 |  |  |  | 0.31929 |  |  | 0.018483 |  |  |  | 0.030161 |  | 0.048644 | 50000 | 0.16552 |  |  | 0.33931 |  |  | 2013 | 2013 | Lobby
2016 |  | Lobby - Hotel |  | 1.06 | [5 empty] | 29.79 | [6 empty] | 2.753 | [20 empty] | x | 2013 | Lobby - Hotel
2016 | Lobby - Hotel572 |  | 79 | 1.06 | 572 | PAR30 | Downlight open | 75 | 1 | 15.39 | 75 | 850 | 0.012 | 0.9 |  |  | 0.59136 |  |  |  | 0.738 |  |  | 0.25656 |  |  |  | 0.282 |  | 0.53856 | 0 | 0 |  |  | 0 |  |  | 2013 | 2013 | Lobby - Hotel
2016 | Lobby - Hotel0 |  | 79 | Match? | 0 | 0 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 |  |  |  | 0 |  |  | 0 |  |  |  | 0 |  | 0 | 0 | 0 |  |  | 0 |  |  | 2013 | 2013 | Lobby - Hotel
2016 | Lobby - Hotel0 |  | 79 | Yes | 0 | 0 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 |  |  |  | 0 |  |  | 0 |  |  |  | 0 |  | 0 | 0 | 0 |  |  | 0 |  |  | 2013 | 2013 | Lobby - Hotel
2016 | Lobby - Hotel727-1 |  | 79 |  | 727-1 | LED | WW Open | 1 | 20 | 14.4 | 20 | 50000 | 0.008 | 0.16 |  |  | 2.1616 |  |  |  | 0.492 |  |  | 0.0016 |  |  |  | 0.00492 |  | 0.00652 | 50000 | 1.62 |  |  | 0.492 |  |  | 2013 | 2013 | Lobby - Hotel
2016 |  | Office-BLDG-SO |  | 0.79 | [5 empty] | 69.6816 | [6 empty] | 13.5135 | [20 empty] | x | 2013 | Office-BLDG-SO
2016 | Office-BLDG-SO735 |  | 25 | 0.7932 | 735 | LED | Linear Dir/Ind | 1 | 38 | 65.7 | 38 | 50000 | 0.019211 | 0.73 | 0.92 | 0.7268 | 12.8649 |  |  |  | 1.5489 |  |  | 0.0073 |  |  |  | 0.011814 |  | 0.019114 | 50000 | 9.6432 |  |  | 1.5489 |  |  | 2013 | 2013 | Office-BLDG-SO
2016 | Office-BLDG-SO739 |  | 25 | Match? | 739 | LED | Task | 1 | 10 | 0 | 10 | 50000 | 0 | 0 | 0 | 0 | 0 |  |  |  | 0 |  |  | 0 |  |  |  | 0 |  | 0 | 50000 | 0 |  |  | 0 |  |  | 2013 | 2013 | Office-BLDG-SO
2016 | Office-BLDG-SO0 |  | 25 | Yes | 0 | 0 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  | 0 |  |  | 0 |  |  |  | 0 |  | 0 | 0 | 0 |  |  | 0 |  |  | 2013 | 2013 | Office-BLDG-SO
2016 | Office-BLDG-SO703 |  | 25 |  | 703 | LED | Linear WW Open | 1 | 75 | 3.9816 | 75 | 50000 | 0.00084267 | 0.0632 | 0.08 | 0.0632 | 0.64864 |  |  |  | 0.082918 |  |  | 0.000632 |  |  |  | 0.00051824 |  | 0.0011502 | 50000 | 0.48601 |  |  | 0.082918 |  |  | 2013 | 2013 | Office-BLDG-SO
2016 |  | Office-BLDG-LO |  | 0.79 | [5 empty] | 69.6816 | [6 empty] | 13.5135 | [20 empty] | x | 2013 | Office-BLDG-LO
2016 | Office-BLDG-LO735 |  | 27 | 0.7932 | 735 | LED | Linear Dir/Ind | 1 | 38 | 65.7 | 38 | 50000 | 0.019211 | 0.73 | 0.92 | 0.7268 | 12.8649 |  |  |  | 1.5489 |  |  | 0.0073 |  |  |  | 0.011814 |  | 0.019114 | 50000 | 9.6432 |  |  | 1.5489 |  |  | 2013 | 2013 | Office-BLDG-LO | 2007 encl
2016 | Office-BLDG-LO739 |  | 27 | Match? | 739 | LED | Task | 1 | 10 | 0 | 10 | 50000 | 0 | 0 | 0 | 0 | 0 |  |  |  | 0 |  |  | 0 |  |  |  | 0 |  | 0 | 50000 | 0 |  |  | 0 |  |  | 2013 | 2013 | Office-BLDG-LO | 2010 encl
2016 | Office-BLDG-LO0 |  | 27 | Yes | 0 | 0 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  | 0 |  |  | 0 |  |  |  | 0 |  | 0 | 0 | 0 |  |  | 0 |  |  | 2013 | 2013 | Office-BLDG-LO
2016 | Office-BLDG-LO703 |  | 27 |  | 703 | LED | Linear WW Open | 1 | 75 | 3.9816 | 75 | 50000 | 0.00084267 | 0.0632 | 0.08 | 0.0632 | 0.64864 |  |  |  | 0.082918 |  |  | 0.000632 |  |  |  | 0.00051824 |  | 0.0011502 | 50000 | 0.48601 |  |  | 0.082918 |  |  | 2013 | 2013 | Office-BLDG-LO
2016 |  | Office-Enclosed |  | 0.93 | [5 empty] | 78.021 | [6 empty] | 5.9056 | [20 empty] | x | 2013 | Office-Enclosed
2016 | Office-Enclosed700 |  | 25 | 0.93 | 700 | LED | Linear Rec Hi Perf Lensed | 1 | 36 | 62.109 | 36 | 50000 | 0.018611 | 0.67 | 0.68 | 0.6324 | 2.575 |  |  |  | 1.7272 |  |  | 0.0067 |  |  |  | 0.011446 |  | 0.018146 | 50000 | 1.9263 |  |  | 1.7272 |  |  | 2013 | 2013 | Office-Enclosed
2016 | Office-Enclosed739 |  | 25 | Match? | 739 | LED | Task | 1 | 10 | 15.912 | 10 | 50000 | 0.026 | 0.26 | 0.24 | 0.2232 | 3.3306 |  |  |  | 0.78351 |  |  | 0.0026 |  |  |  | 0.01599 |  | 0.01859 | 50000 | 2.496 |  |  | 0.78351 |  |  | 2013 | 2013 | Office-Enclosed
2016 | Office-Enclosed0 |  | 25 | Yes | 0 | 0 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  | 0 |  |  | 0 |  |  |  | 0 |  | 0 | 0 | 0 |  |  | 0 |  |  | 2013 | 2013 | Office-Enclosed
2016 | Office-Enclosed0 |  | 25 |  | 0 | 0 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  | 0 |  |  | 0 |  |  |  | 0 |  | 0 | 0 | 0 |  |  | 0 |  |  | 2013 | 2013 | Office-Enclosed
2016 |  | Office - Open Plan (Including Other) |  | 0.81 | [5 empty] | 64.26 | [6 empty] | 12.3752 | [20 empty] | x | 2013 | Office - Open Plan (Including Other)
2016 | Office - Open Plan (Including Other)735 |  | 27 | 0.81 | 735 | LED | Linear Dir/Ind | 1 | 38 | 45 | 38 | 50000 | 0.013158 | 0.5 | 0.6 | 0.486 | 8.8116 |  |  |  | 1.0609 |  |  | 0.005 |  |  |  | 0.0080921 |  | 0.013092 | 50000 | 6.6049 |  |  | 1.0609 |  |  | 2013 | 2013 | Office - Open Plan (Including Other) | 2007 encl
2016 | Office - Open Plan (Including Other)739 |  | 27 | Match? | 739 | LED | Task | 1 | 10 | 9.18 | 10 | 50000 | 0.015 | 0.15 | 0.2 | 0.162 | 1.9215 |  |  |  | 0.45203 |  |  | 0.0015 |  |  |  | 0.009225 |  | 0.010725 | 50000 | 1.44 |  |  | 0.45203 |  |  | 2013 | 2013 | Office - Open Plan (Including Other) | 2010 encl
2016 | Office - Open Plan (Including Other)0 |  | 27 | Yes | 0 | 0 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  | 0 |  |  | 0 |  |  |  | 0 |  | 0 | 0 | 0 |  |  | 0 |  |  | 2013 | 2013 | Office - Open Plan (Including Other)
2016 | Office - Open Plan (Including Other)703 |  | 27 |  | 703 | LED | Linear WW Open | 1 | 75 | 10.08 | 75 | 50000 | 0.0021333 | 0.16 | 0.2 | 0.162 | 1.6421 |  |  |  | 0.20992 |  |  | 0.0016 |  |  |  | 0.001312 |  | 0.002912 | 50000 | 1.2304 |  |  | 0.20992 |  |  | 2013 | 2013 | Office - Open Plan (Including Other)
2016 |  | Office-Enclosed-whole-small |  | 0.878 | [5 empty] | 74.016 | [6 empty] | 5.5341 | [20 empty] | x | 2013 | Office-Enclosed-whole-small
2016 | Office-Enclosed700-whole-Small |  | 25 | 0.88 | 700 | LED | Linear Rec Hi Perf Lensed | 1 | 36 | 59.328 | 36 | 50000 | 0.017778 | 0.64 | 0.56818 | 0.5 | 2.4597 |  |  |  | 1.6498 |  |  | 0.0064 |  |  |  | 0.010933 |  | 0.017333 | 50000 | 1.84 |  |  | 1.6498 |  |  | 2013 | 2013 | Office-Enclosed-whole-small
2016 | Office-Enclosed739-whole-Small |  | 25 | Match? | 739 | LED | Task | 1 | 10 | 14.688 | 10 | 50000 | 0.024 | 0.24 | 0.15909 | 0.14 | 3.0744 |  |  |  | 0.72324 |  |  | 0.0024 |  |  |  | 0.01476 |  | 0.01716 | 50000 | 2.304 |  |  | 0.72324 |  |  | 2013 | 2013 | Office-Enclosed-whole-small
2016 | Office-Enclosed0-whole-Small |  | 25 | Yes | 0 | 0 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  | 0 |  |  | 0 |  |  |  | 0 |  | 0 | 0 | 0 |  |  | 0 |  |  | 2013 | 2013 | Office-Enclosed-whole-small
2016 | Office-Enclosed0-whole-Small |  | 25 |  | 0 | 0 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.18 | 0 |  |  |  | 0 |  |  | 0 |  |  |  | 0 |  | 0 | 0 | 0 |  |  | 0 |  |  | 2013 | 2013 | Office-Enclosed-whole-small
2016 |  | Office - Open Plan (Including Other)-whole-small |  | 0.81 | [5 empty] | 64.26 | [6 empty] | 12.3752 | [20 empty] | x | 2013 | Office - Open Plan (Including Other)-whole-small
2016 | Office - Open Plan (Including Other)735-whole-Small |  | 27 | 0.81 | 735 | LED | Linear Dir/Ind | 1 | 38 | 45 | 38 | 50000 | 0.013158 | 0.5 | 0.6 | 0.486 | 8.8116 |  |  |  | 1.0609 |  |  | 0.005 |  |  |  | 0.0080921 |  | 0.013092 | 50000 | 6.6049 |  |  | 1.0609 |  |  | 2013 | 2013 | Office - Open Plan (Including Other)-whole-small | 2007 encl
2016 | Office - Open Plan (Including Other)739-whole-Small |  | 27 | Match? | 739 | LED | Task | 1 | 10 | 9.18 | 10 | 50000 | 0.015 | 0.15 | 0.2 | 0.162 | 1.9215 |  |  |  | 0.45203 |  |  | 0.0015 |  |  |  | 0.009225 |  | 0.010725 | 50000 | 1.44 |  |  | 0.45203 |  |  | 2013 | 2013 | Office - Open Plan (Including Other)-whole-small | 2010 encl
2016 | Office - Open Plan (Including Other)0-whole-small |  | 27 | Yes | 0 | 0 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  | 0 |  |  | 0 |  |  |  | 0 |  | 0 | 0 | 0 |  |  | 0 |  |  | 2013 | 2013 | Office - Open Plan (Including Other)-whole-small
2016 | Office - Open Plan (Including Other)703-whole-Small |  | 27 |  | 703 | LED | Linear WW Open | 1 | 75 | 10.08 | 75 | 50000 | 0.0021333 | 0.16 | 0.2 | 0.162 | 1.6421 |  |  |  | 0.20992 |  |  | 0.0016 |  |  |  | 0.001312 |  | 0.002912 | 50000 | 1.2304 |  |  | 0.20992 |  |  | 2013 | 2013 | Office - Open Plan (Including Other)-whole-small
2016 |  | Office-Enclosed-whole-large |  | 0.826 | [5 empty] | 69.696 | [6 empty] | 5.2523 | [20 empty] | x | 2013 | Office-Enclosed-whole-large
2016 | Office-Enclosed700-whole-Large |  | 25 | 0.83 | 700 | LED | Linear Rec Hi Perf Lensed | 1 | 36 | 55.62 | 36 | 50000 | 0.016667 | 0.6 |  |  | 2.306 |  |  |  | 1.5467 |  |  | 0.006 |  |  |  | 0.01025 |  | 0.01625 | 50000 | 1.725 |  |  | 1.5467 |  |  | 2013 | 2013 | Office-Enclosed-whole-large
2016 | Office-Enclosed739-whole-Large |  | 25 | Match? | 739 | LED | Task | 1 | 10 | 14.076 | 10 | 50000 | 0.023 | 0.23 |  |  | 2.9463 |  |  |  | 0.6931 |  |  | 0.0023 |  |  |  | 0.014145 |  | 0.016445 | 50000 | 2.208 |  |  | 0.6931 |  |  | 2013 | 2013 | Office-Enclosed-whole-large
2016 | Office-Enclosed0-whole-Large |  | 25 | Yes | 0 | 0 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 |  |  |  | 0 |  |  | 0 |  |  |  | 0 |  | 0 | 0 | 0 |  |  | 0 |  |  | 2013 | 2013 | Office-Enclosed-whole-large
2016 | Office-Enclosed0-whole-Large |  | 25 |  | 0 | 0 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 |  |  |  | 0 |  |  | 0 |  |  |  | 0 |  | 0 | 0 | 0 |  |  | 0 |  |  | 2013 | 2013 | Office-Enclosed-whole-large
2016 |  | Office - Open Plan (Including Other)-whole |  | 0.81 | [5 empty] | 64.26 | [6 empty] | 12.3752 | [20 empty] | x | 2013 | Office - Open Plan (Including Other)-whole
2016 | Office - Open Plan (Including Other)735-whole-Large |  | 27 | 0.81 | 735 | LED | Linear Dir/Ind | 1 | 38 | 45 | 38 | 50000 | 0.013158 | 0.5 | 0.6 | 0.486 | 8.8116 |  |  |  | 1.0609 |  |  | 0.005 |  |  |  | 0.0080921 |  | 0.013092 | 50000 | 6.6049 |  |  | 1.0609 |  |  | 2013 | 2013 | Office - Open Plan (Including Other)-whole | 2007 encl
2016 | Office - Open Plan (Including Other)739-whole-Large |  | 27 | Match? | 739 | LED | Task | 1 | 10 | 9.18 | 10 | 50000 | 0.015 | 0.15 | 0.2 | 0.162 | 1.9215 |  |  |  | 0.45203 |  |  | 0.0015 |  |  |  | 0.009225 |  | 0.010725 | 50000 | 1.44 |  |  | 0.45203 |  |  | 2013 | 2013 | Office - Open Plan (Including Other)-whole | 2010 encl
2016 | Office - Open Plan (Including Other)0-whole-Large |  | 27 | Yes | 0 | 0 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  | 0 |  |  | 0 |  |  |  | 0 |  | 0 | 0 | 0 |  |  | 0 |  |  | 2013 | 2013 | Office - Open Plan (Including Other)-whole
2016 | Office - Open Plan (Including Other)703-whole-Large |  | 27 |  | 703 | LED | Linear WW Open | 1 | 75 | 10.08 | 75 | 50000 | 0.0021333 | 0.16 | 0.2 | 0.162 | 1.6421 |  |  |  | 0.20992 |  |  | 0.0016 |  |  |  | 0.001312 |  | 0.002912 | 50000 | 1.2304 |  |  | 0.20992 |  |  | 2013 | 2013 | Office - Open Plan (Including Other)-whole
2016 |  | Restrooms |  | 0.85 | [5 empty] | 61.1392 | [6 empty] | 9.7535 | [20 empty] | x | 2013 | Restrooms
2016 | Restrooms604 |  | 12 | 0.85 | 604 | F32T8 - Bi-Pin Base | Wall Mounted Linear Direct/Indirect | 32 | 1 | 24.2392 | 29 | 36000 | 0.012069 | 0.35 |  |  | 4.2525 |  |  |  | 0.3637 |  |  | 0.040431 |  |  |  | 0.065978 |  | 0.10641 | 50000 | 0.36207 |  |  | 0.74224 |  |  | 2013 | 2013 | Restrooms
2016 | Restrooms720 |  | 12 | Match? | 720 | LED | Downlight Lensed | 1 | 22 | 12.6 | 22 | 50000 | 0.0090909 | 0.2 |  |  | 1.5353 |  |  |  | 0.55909 |  |  | 0.002 |  |  |  | 0.0055909 |  | 0.0075909 | 50000 | 1.15 |  |  | 0.55909 |  |  | 2013 | 2013 | Restrooms
2016 | Restrooms0 |  | 12 | Yes | 0 | 0 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 |  |  |  | 0 |  |  | 0 |  |  |  | 0 |  | 0 | 0 | 0 |  |  | 0 |  |  | 2013 | 2013 | Restrooms
2016 | Restrooms534-2 |  | 12 |  | 534-2 | F32T8 - Bi-Pin Base | Linear Wall Cove | 32 | 1 | 24.3 | 29 | 36000 | 0.010345 | 0.3 |  |  | 3.9657 |  |  |  | 0.59867 |  |  | 0.034655 |  |  |  | 0.056552 |  | 0.091208 | 50000 | 0.31034 |  |  | 0.63621 |  |  | 2013 | 2013 | Restrooms
2016 |  | Retail - Sales Area |  | 1.22 | [5 empty] | 104.607 | [6 empty] | 6.3381 | [20 empty] | x | 2013 | Retail - Sales Area
2016 | Retail - Sales Area700 |  | 97 | 1.21 | 700 | LED | Linear Rec Hi Perf Lensed | 1 | 36 | 67.671 | 36 | 50000 | 0.020278 | 0.73 | 0.6 | 0.732 | 2.8056 |  |  |  | 1.8818 |  |  | 0.0073 |  |  |  | 0.012471 |  | 0.019771 | 50000 | 2.0987 |  |  | 1.8818 |  |  | 2013 | 2013 | Retail - Sales Area
2016 | Retail - Sales Area741 |  | 97 | Match? | 741 | LED | Downlight open | 1 | 24 | 14.688 | 24 | 50000 | 0.01 | 0.24 | 0.2 | 0.244 | 1.6519 |  |  |  | 0.615 |  |  | 0.0024 |  |  |  | 0.00615 |  | 0.00855 | 50000 | 1.2371 |  |  | 0.615 |  |  | 2013 | 2013 | Retail - Sales Area
2016 | Retail - Sales Area0 |  | 97 | Yes | 0 | 0 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  | 0 |  |  | 0 |  |  |  | 0 |  | 0 | 0 | 0 |  |  | 0 |  |  | 2013 | 2013 | Retail - Sales Area
2016 | Retail - Sales Area537-1_LED |  | 97 |  | 537-1_LED | LED | Wallgrazing direct distribution | 1 | 23 | 22.248 | 23 | 50000 | 0.010435 | 0.24 | 0.2 | 0.244 | 1.8806 |  |  |  | 0.96838 |  |  | 0.0024 |  |  |  | 6.4174e-07 |  | 0.0024006 | 50000 | 0.93908 |  |  | 0.96838 |  |  | 2013 | 2013 | Retail - Sales Area
2016 |  | Stairway |  | 0.58 | [5 empty] | 44.892 | [6 empty] | 5.37 | [20 empty] | x | 2013 | Stairway
2016 | Stairway731 |  | 11 | 0.58 | 731 | LED | Narrow Linear | 1 | 40 | 22.968 | 40 | 50000 | 0.00725 | 0.29 |  |  | 2.7724 |  |  |  | 0.58454 |  |  | 0.0029 |  |  |  | 0.0044588 |  | 0.0073587 | 50000 | 2.0771 |  |  | 0.58454 |  |  | 2013 | 2013 | Stairway
2016 | Stairway702 |  | 11 | Match? | 702 | LED | Linear Wall Cove | 1 | 19 | 21.924 | 19 | 50000 | 0.015263 | 0.29 |  |  | 2.5976 |  |  |  | 1.5019 |  |  | 0.0029 |  |  |  | 0.0093868 |  | 0.012287 | 50000 | 1.9461 |  |  | 1.5019 |  |  | 2013 | 2013 | Stairway
2016 | Stairway0 |  | 11 | Yes | 0 | 0 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 |  |  |  | 0 |  |  | 0 |  |  |  | 0 |  | 0 | 0 | 0 |  |  | 0 |  |  | 2013 | 2013 | Stairway
2016 | Stairway0 |  | 11 |  | 0 | 0 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 9.9928e-08 |  |  | 0 |  |  |  | 0 |  |  | 0 |  |  |  | 0 |  | 0 | 0 | 0 |  |  | 0 |  |  | 2013 | 2013 | Stairway
2016 |  | Storage |  | 0.46 |  |  | 20 |  |  | 47.61 | [6 empty] | 3.0309 | [20 empty] | x | 2013 | Storage
2016 | Storage738 |  | 41 | 0.46 | 738 | LED | Linear Industrial | 1 | 38 | 47.61 | 38 | 50000 | 0.012105 | 0.46 | 1 | 0.46 | 3.0309 |  |  |  | 0.70055 |  |  | 0.0046 |  |  |  | 0.0074447 |  | 0.012045 | 50000 | 2.2697 |  |  | 0.70055 |  |  | 2013 | 2013 | Storage
2016 | Storage0 |  | 41 | Match? | 0 | 0 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  | 0 |  |  | 0 |  |  |  | 0 |  | 0 | 0 | 0 |  |  | 0 |  |  | 2013 | 2013 | Storage
2016 | Storage0 |  | 41 | Yes | 0 | 0 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  | 0 |  |  | 0 |  |  |  | 0 |  | 0 | 0 | 0 |  |  | 0 |  |  | 2013 | 2013 | Storage
2016 | Storage0 |  | 41 |  | 0 | 0 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 9.9297e-08 | 0 | 0 | 0 |  |  |  | 0 |  |  | 0 |  |  |  | 0 |  | 0 | 0 | 0 |  |  | 0 |  |  | 2013 | 2013 | Storage
|  | 1 FL linear fluorescent, CF compact fluorescent, MH metal halide | [35 empty] | x | x | x
|  | Interior Lighting Costs by Space Type, 90.1-2016 | [35 empty] | x | x | x
|  | Space Type Lighting Descriptions and Cost Parameters | [18 empty] | New Construction Cost |  |  | Lamp Replacement Cost | [6 empty] | Ballast Replacement Cost | [6 empty] | x | x | x
| 90.1-2022 Lookup Values | 90.1-2022 Space Types | Model Number | Lighting Power Allowance, LPD, W/ft2 | Fixtures - ID Number | Fixture type | Lamp Type | Lamp Wattage | Number of Lamps | Net Est. Fixture Lum/ft2 | Fixture Watts | Lamp Life, Hours | Quantity of Fixtures/ft2 | Fixture Watts/ft2 |  |  | Fixture + Lamp Cost, $/ft2 | not used | not used | not used | Labor Cost $/ft2 |  |  | Lamp Cost, $/ft2 | Labor Crew Type |  |  | Labor Cost/ft2 | Overhead and Profit, $/ft2 | Total $/ft2 | Ballast Life Hours | Ballast Cost, $/ft2 | Not Used | Not Used | Labor Cost/ft2 |  |  | x | x | x
| Classroom/Lecture/Training | Classroom/Lecture/Training |  | 0.71 |  |  | 47.15 |  |  | 68.985 | [6 empty] | 4.6769 | [13 empty] | 0 | 0 |  |  | 0 |  |  | x | 2016 | Classroom/Lecture/Training
2019 | Classroom/Lecture/TrainingTR701 |  | 3.1 | 0.71 | TR701 | LED | Linear Rec Hi Perf Lensed | 1 | 32 | 56.925 | 32 | 50000 | 0.017188 | 0.55 | 0.76 | 0.5396 | 2.3774 |  |  |  | 1.057 |  |  | 0.0055 |  |  |  | 0.01057 |  | 0.01607 | 50000 | 1.7789 |  |  | 1.057 |  |  | 2019 | 2019 | Classroom/Lecture/Training
2019 | Classroom/Lecture/TrainingDL706 |  | 3.1 | Match? | DL706 | LED | Downlight open | 1 | 12 | 5.508 | 12 | 50000 | 0.0075 | 0.09 | 0.07 | 0.0497 | 1.238 |  |  |  | 0.46125 |  |  | 0.0009 |  |  |  | 0.0046125 |  | 0.0055125 | 50000 | 0.92783 |  |  | 0.46125 |  |  | 2016 | 2016 | Classroom/Lecture/Training
2019 | Classroom/Lecture/Training0 |  | 3.1 | Yes | 0 | 0 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  | 0 |  |  | 0 |  |  |  | 0 |  | 0 | 0 | 0 |  |  | 0 |  |  | 2016 | 2016 | Classroom/Lecture/Training
2019 | Classroom/Lecture/TrainingWW714 |  | 3.1 |  | WW714 | LED | Linear WW Open | 1 | 58 | 6.552 | 58 | 50000 | 0.0013793 | 0.08 | 0.17 | 0.1207 | 1.0615 |  |  |  | 0.13572 |  |  | 0.0008 |  |  |  | 0.00084828 |  | 0.0016483 | 50000 | 0.79552 |  |  | 0.13572 |  |  | 2016 | 2016 | Classroom/Lecture/Training
|  | Conference/Meeting/Multipurpose |  | 0.97 | [5 empty] | 70.704 | [6 empty] | 7.2964 | [20 empty] | x | 2016 | Conference/Meeting/Multipurpose
2019 | Conference/Meeting/MultipurposeTR704 |  | 31 | 0.96 | TR704 | LED | Linear Rec Hi Perf Lensed | 1 | 32 | 48.951 | 32 | 50000 | 0.015312 | 0.49 | 0.5 | 0.485 | 2.118 |  |  |  | 0.94172 |  |  | 0.0049 |  |  |  | 0.0094172 |  | 0.014317 | 50000 | 1.5848 |  |  | 0.94172 |  |  | 2016 | 2016 | Conference/Meeting/Multipurpose
2019 | Conference/Meeting/MultipurposeDL702 |  | 31 | Match? | DL702 | LED | Downlight small 90 CRI | 1 | 24 | 8.64 | 24 | 50000 | 0.0066667 | 0.16 | 0.19 | 0.1843 | 1.2021 |  |  |  | 0.41 |  |  | 0.0016 |  |  |  | 0.0041 |  | 0.0057 | 50000 | 0.9004 |  |  | 0.41 |  |  | 2016 | 2016 | Conference/Meeting/Multipurpose
2019 | Conference/Meeting/Multipurpose0 |  | 31 |  | 0 | 0 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  | 0 |  |  | 0 |  |  |  | 0 |  | 0 | 0 | 0 |  |  | 0 |  |  | 2016 | 2016 | Conference/Meeting/Multipurpose
2019 | Conference/Meeting/MultipurposeWW704 |  | 31 |  | WW704 | LED | Linear WW Open | 1 | 60 | 13.113 | 60 | 50000 | 0.0051667 | 0.31 | 0.32 | 0.3104 | 3.9763 |  |  |  | 0.5084 |  |  | 0.0031 |  |  |  | 0.0031775 |  | 0.0062775 | 50000 | 2.9799 |  |  | 0.5084 |  |  | 2016 | 2016 | Conference/Meeting/Multipurpose
Input |  | Corridor/Transition |  | 0.41 | [5 empty] | 29.835 | [6 empty] | #N/A | [20 empty] | x | 2016 | Corridor/Transition
2019 | Corridor/TransitionDL706 |  | 2 | 0.41 | DL706 | LED | Downlight open | 1 | 12 | 14.688 | 12 | 50000 | 0.02 | 0.24 | 0.57576 | 0.23606 | 3.3013 |  |  |  | 1.23 |  |  | 0.0024 |  |  |  | 0.0123 |  | 0.0147 | 50000 | 2.4742 |  |  | 1.23 |  |  | 2016 | 2016 | Corridor/Transition
2019 | Corridor/Transition0 |  | 2 | Match? | 0 | 0 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  | 0 |  |  | 0 |  |  |  | 0 |  | 0 | 0 | 0 |  |  | 0 |  |  | 2016 | 2016 | Corridor/Transition
2019 | Corridor/Transition0 |  | 2 | Yes | 0 | 0 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  | 0 |  |  | 0 |  |  |  | 0 |  | 0 | 0 | 0 |  |  | 0 |  |  | 2016 | 2016 | Corridor/Transition
2019 | Corridor/TransitionWW708 |  | 2 |  | WW708 | LED | Linear WW Open | 1 | 53 | 15.147 | 53 | 50000 | 0.0032075 | 0.17 | 0.42424 | 0.17394 | 2.4683 |  |  |  | 0.31562 |  |  | 0.0017 |  |  |  | 0.0019726 |  | 0.0036726 | 50000 | 1.85 |  |  | 0.31562 |  |  | 2016 | 2016 | Corridor/Transition
Input |  | Dining Area |  | 0.43 | [5 empty] | 38.241 | [6 empty] | #N/A | [20 empty] | x | 2016 | Dining Area
2019 | Dining AreaTR704 |  | 6 | 0.43 | TR704 | LED | Linear Rec Hi Perf Lensed | 1 | 32 | 17.982 | 32 | 50000 | 0.005625 | 0.18 |  |  | 0.77805 |  |  |  | 0.34594 |  |  | 0.0018 |  |  |  | 0.0034594 |  | 0.0052594 | 50000 | 0.58219 |  |  | 0.34594 |  |  | 2016 | 2016 | Dining Area
2019 | Dining AreaDL707 |  | 6 | Match? | DL707 | LED | Downlight open | 1 | 8 | 9.612 | 8 | 50000 | 0.015 | 0.12 |  |  | 3.0613 |  |  |  | 0.9225 |  |  | 0.0012 |  |  |  | 0.009225 |  | 0.010425 | 50000 | 2.2951 |  |  | 0.9225 |  |  | 2016 | 2016 | Dining Area
2019 | Dining Area0 |  | 6 | Yes | 0 | 0 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 |  |  |  | 0 |  |  | 0 |  |  |  | 0 |  | 0 | 0 | 0 |  |  | 0 |  |  | 2016 | 2016 | Dining Area
2019 | Dining AreaWW714 |  | 6 |  | WW714 | LED | Linear WW Open | 1 | 58 | 10.647 | 58 | 50000 | 0.0022414 | 0.13 |  |  | 1.7249 |  |  |  | 0.22055 |  |  | 0.0013 |  |  |  | 0.0013784 |  | 0.0026784 | 50000 | 1.2927 |  |  | 0.22055 |  |  | 2016 | 2016 | Dining Area
2019 |  | Dwelling-Unit |  | 0.2905 |  |  | "other lamps" not included |  |  | 10.0479 |  |  | 0.015759 |  |  | 18.4337 | 0.028693 | [20 empty] | x | 2013 | Dwelling-Unit
2019 | Dwelling-Unit301 |  | 6 | 0.2905 | 301 | A19 | Inc residential screw in lamp | 60 | 1 | 0.82024 | 60 | 1000 | 0.001519 | 0.091137 | 0.096386 | 5.7831 | 0.0013519 |  |  |  | 0 |  |  | 0.0013519 |  |  |  | 0 |  | 0.0013519 | 0 | 0 |  |  | 0 |  |  | 2013 | 2013 | Dwelling-Unit
2019 | Dwelling-Unit302 |  | 6 | Match? | 302 | A19 | CFL residential screw in lamp | 14 | 1 | 9.2276 | 14 | 10000 | 0.01424 | 0.19936 | 0.90361 | 12.6506 | 0.027341 |  |  |  | 0 |  |  | 0.027341 |  |  |  | 0 |  | 0.027341 | 0 | 0 |  |  | 0 |  |  | 2013 | 2013 | Dwelling-Unit
2019 | Dwelling-Unit303 |  | 6 | Yes | 303 | A19 | LEC residential screw in lamp | 9 | 1 | 0 | 9 | 15000 | 0 | 0 | 0 | 0 | 0 |  |  |  | 0 |  |  | 0 |  |  |  | 0 |  | 0 | 0 | 0 |  |  | 0 |  |  | 2013 | 2013 | Dwelling-Unit
2019 | Dwelling-Unit0 |  | 6 |  | 0 | 0 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  | 0 |  |  | 0 |  |  |  | 0 |  | 0 | 0 | 0 |  |  | 0 |  |  | 2013 | 2013 | Dwelling-Unit
Input |  | Electrical/Mechanical |  | 0.43 | [5 empty] | 33.561 | [6 empty] | #N/A | [20 empty] | x | 2016 | Electrical/Mechanical
2019 | Electrical/MechanicalLB702 |  | 4 | 0.43 | LB702 | LED | Lowbay linear wrap | 1 | 37 | 21.321 | 37 | 50000 | 0.0062162 | 0.23 |  |  | 1.0653 |  |  |  | 0.35974 |  |  | 0.0023 |  |  |  | 0.003823 |  | 0.006123 | 50000 | 0.79723 |  |  | 0.35974 |  |  | 2016 | 2016 | Electrical/Mechanical
2019 | Electrical/MechanicalTL702 |  | 4 | Match? | TL702 | LED | Task | 1 | 10 | 12.24 | 10 | 50000 | 0.02 | 0.2 |  |  | 2.562 |  |  |  | 0.6027 |  |  | 0.002 |  |  |  | 0.0123 |  | 0.0143 | 50000 | 1.92 |  |  | 0.6027 |  |  | 2016 | 2016 | Electrical/Mechanical
2019 | Electrical/Mechanical0 |  | 4 | Yes | 0 | 0 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 |  |  |  | 0 |  |  | 0 |  |  |  | 0 |  | 0 | 0 | 0 |  |  | 0 |  |  | 2016 | 2016 | Electrical/Mechanical
2019 | Electrical/Mechanical0 |  | 4 |  | 0 | 0 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 |  |  |  | 0 |  |  | 0 |  |  |  | 0 |  | 0 | 0 | 0 |  |  | 0 |  |  | 2016 | 2016 | Electrical/Mechanical
2019 |  | Food Preparation |  | 1.09 | [5 empty] | 108.891 | [6 empty] | 4.645 | [20 empty] | x | 2016 | Food Preparation
2019 | Food PreparationTR704 |  | 8 | 1.09 | TR704 | LED | Linear Rec Hi Perf Lensed | 1 | 32 | 90.909 | 32 | 50000 | 0.028438 | 0.91 |  |  | 3.9335 |  |  |  | 1.7489 |  |  | 0.0091 |  |  |  | 0.017489 |  | 0.026589 | 50000 | 2.9433 |  |  | 1.7489 |  |  | 2016 | 2016 | Food Preparation
2019 | Food PreparationTR703 |  | 8 | Match? | TR703 | LED | Linear Rec Hi Perf Lensed | 1 | 35 | 17.982 | 35 | 50000 | 0.0051429 | 0.18 |  |  | 0.71151 |  |  |  | 0.31629 |  |  | 0.0018 |  |  |  | 0.0031629 |  | 0.0049629 | 50000 | 0.53229 |  |  | 0.31629 |  |  | 2016 | 2016 | Food Preparation
2019 | Food Preparation0 |  | 8 | Yes | 0 | 0 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 |  |  |  | 0 |  |  | 0 |  |  |  | 0 |  | 0 | 0 | 0 |  |  | 0 |  |  | 2016 | 2016 | Food Preparation
2019 | Food Preparation0 |  | 8 |  | 0 | 0 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 |  |  |  | 0 |  |  | 0 |  |  |  | 0 |  | 0 | 0 | 0 |  |  | 0 |  |  | 2016 | 2016 | Food Preparation
2019 |  | Gymnasium/Fitness-Fitness Area |  | 0.7 | [5 empty] | 69.3 | [6 empty] | #N/A | [20 empty] | x | 2016 | Gymnasium/Fitness-Fitness Area
2019 | Gymnasium/Fitness-Fitness AreaID701 |  | 126 | 0.7 | ID701 | LED | Linear Dir/Indir | 1 | 33 | 69.3 | 33 | 50000 | 0.021212 | 0.7 |  |  | 14.2043 |  |  |  | 1.7103 |  |  | 0.007 |  |  |  | 0.013045 |  | 0.020045 | 50000 | 10.648 |  |  | 1.7103 |  |  | 2016 | 2016 | Gymnasium/Fitness-Fitness Area
2019 | Gymnasium/Fitness-Fitness Area0 |  | 126 | Match? | 0 | 0 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 |  |  |  | 0 |  |  | 0 |  |  |  | 0 |  | 0 | 0 | 0 |  |  | 0 |  |  | 2016 | 2016 | Gymnasium/Fitness-Fitness Area
2019 | Gymnasium/Fitness-Fitness Area0 |  | 126 | Yes | 0 | 0 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 |  |  |  | 0 |  |  | 0 |  |  |  | 0 |  | 0 | 0 | 0 |  |  | 0 |  |  | 2016 | 2016 | Gymnasium/Fitness-Fitness Area
2019 | Gymnasium/Fitness-Fitness Area0 |  | 126 |  | 0 | 0 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 |  |  |  | 0 |  |  | 0 |  |  |  | 0 |  | 0 | 0 | 0 |  |  | 0 |  |  | 2016 | 2016 | Gymnasium/Fitness-Fitness Area
2019 |  | Highway Lodging Guest Rooms |  | 0.41 | [5 empty] | 34.551 | [6 empty] | 5.1471 | [20 empty] | x | 2016 | Highway Lodging Guest Rooms
2019 | Highway Lodging Guest RoomsWW714 |  | 75.01 | 0.41 | WW714 | LED | Linear WW Open | 1 | 58 | 26.208 | 58 | 50000 | 0.0055172 | 0.32 | 0.77 | 0.3157 | 4.246 |  |  |  | 0.5429 |  |  | 0.0032 |  |  |  | 0.0033931 |  | 0.0065931 | 50000 | 3.1821 |  |  | 0.5429 |  |  | 2016 | 2016 | Highway Lodging Guest Rooms
2019 | Highway Lodging Guest RoomsDL703 |  | 75.01 | Match? | DL703 | LED | Downlight open or lensed | 1 | 23 | 8.343 | 23 | 50000 | 0.003913 | 0.09 | 0.23 | 0.0943 | 0.9011 |  |  |  | 0.24065 |  |  | 0.0009 |  |  |  | 0.0024065 |  | 0.0033065 | 50000 | 0.67515 |  |  | 0.24065 |  |  | 2016 | 2016 | Highway Lodging Guest Rooms
2019 | Highway Lodging Guest Rooms0 |  | 75.01 | Yes | 0 | 0 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  | 0 |  |  | 0 |  |  |  | 0 |  | 0 | 0 | 0 |  |  | 0 |  |  | 2016 | 2016 | Highway Lodging Guest Rooms
2019 | Highway Lodging Guest Rooms0 |  | 75.01 |  | 0 | 0 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  | 0 |  |  | 0 |  |  |  | 0 |  | 0 | 0 | 0 |  |  | 0 |  |  | 2016 | 2016 | Highway Lodging Guest Rooms
2019 |  | Laundry-Washing |  | 0.53 | [5 empty] | 52.947 | [6 empty] | #N/A | [20 empty] | x | 2016 | Laundry-Washing
2019 | Laundry-WashingTR703 |  | 82 | 0.53 | TR703 | LED | Linear Rec Hi Perf Lensed | 1 | 35 | 52.947 | 35 | 50000 | 0.015143 | 0.53 |  |  | 2.095 |  |  |  | 0.93129 |  |  | 0.0053 |  |  |  | 0.0093129 |  | 0.014613 | 50000 | 1.5673 |  |  | 0.93129 |  |  | 2016 | 2016 | Laundry-Washing
2019 | Laundry-Washing0 |  | 82 | Match? | 0 | 0 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 |  |  |  | 0 |  |  | 0 |  |  |  | 0 |  | 0 | 0 | 0 |  |  | 0 |  |  | 2016 | 2016 | Laundry-Washing
2019 | Laundry-Washing0 |  | 82 | Yes | 0 | 0 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 |  |  |  | 0 |  |  | 0 |  |  |  | 0 |  | 0 | 0 | 0 |  |  | 0 |  |  | 2016 | 2016 | Laundry-Washing
2019 | Laundry-Washing0 |  | 82 |  | 0 | 0 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 1.0077e-07 |  |  | 0 |  |  |  | 0 |  |  | 0 |  |  |  | 0 |  | 0 | 0 | 0 |  |  | 0 |  |  | 2016 | 2016 | Laundry-Washing
2019 |  | Library |  | 0.96 | [5 empty] | 87.03 | [6 empty] | 15.7566 | [20 empty] | x | 2016 | Library
2019 | LibraryID701 |  | 19 | 0.95 | ID701 | LED | Linear Dir/Indir | 1 | 33 | 61.875 | 33 | 50000 | 0.018939 | 0.625 | 0.53 | 0.5088 | 12.6824 |  |  |  | 1.527 |  |  | 0.00625 |  |  |  | 0.011648 |  | 0.017898 | 50000 | 9.5071 |  |  | 1.527 |  |  | 2016 | 2016 | Library
2019 | LibraryDL709 |  | 19 | Match? | DL709 | LED | Downlight open | 1 | 21 | 25.155 | 21 | 50000 | 0.015476 | 0.325 | 0.37 | 0.3552 | 3.0742 |  |  |  | 0.95179 |  |  | 0.00325 |  |  |  | 0.0095179 |  | 0.012768 | 50000 | 2.3032 |  |  | 0.95179 |  |  | 2016 | 2016 | Library
2019 | Library0 |  | 19 | Yes | 0 | 0 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  | 0 |  |  | 0 |  |  |  | 0 |  | 0 | 0 | 0 |  |  | 0 |  |  | 2016 | 2016 | Library
2019 | Library0 |  | 19 |  | 0 | 0 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  | 0 |  |  | 0 |  |  |  | 0 |  | 0 | 0 | 0 |  |  | 0 |  |  | 2016 | 2016 | Library
2019 |  | Lounge/Recreation - Breakroom |  | 0.59 | [5 empty] | 44.604 | [6 empty] | #N/A | [20 empty] | x | 2016 | Lounge/Recreation - Breakroom
2019 | Lounge/Recreation - BreakroomDL707 |  | 9 | 0.56 | DL707 | LED | Downlight open | 1 | 8 | 22.428 | 8 | 50000 | 0.035 | 0.28 | 0.78571 | 0.44 | 7.1431 |  |  |  | 2.1525 |  |  | 0.0028 |  |  |  | 0.021525 |  | 0.024325 | 50000 | 5.3552 |  |  | 2.1525 |  |  | 2016 | 2016 | Lounge/Recreation - Breakroom
2019 | Lounge/Recreation - Breakroom0 |  | 9 | Match? | 0 | 0 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  | 0 |  |  | 0 |  |  |  | 0 |  | 0 | 0 | 0 |  |  | 0 |  |  | 2016 | 2016 | Lounge/Recreation - Breakroom
2019 | Lounge/Recreation - Breakroom0 |  | 9 | No | 0 | 0 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  | 0 |  |  | 0 |  |  |  | 0 |  | 0 | 0 | 0 |  |  | 0 |  |  | 2016 | 2016 | Lounge/Recreation - Breakroom
2019 | Lounge/Recreation - BreakroomWG702 |  | 9 |  | WG702 | LED | Wallgrazing direct distribution | 1 | 18 | 22.176 | 18 | 50000 | 0.015556 | 0.28 | 0.51786 | 0.29 | 2.8026 |  |  |  | 0.95667 |  |  | 0.0028 |  |  |  | 0.0095667 |  | 0.012367 | 50000 | 2.0999 |  |  | 0.95667 |  |  | 2016 | 2016 | Lounge/Recreation - Breakroom
2019 |  | Lobby |  | 0.84 | [5 empty] | 63.828 | [6 empty] | 11.6844 | [20 empty] | x | 2016 | Lobby
2019 | LobbyIP701 |  | 20.1 | 0.84 | IP701 | LED | indirect Pendant | 1 | 38 | 44.37 | 38 | 50000 | 0.015263 | 0.58 | 0.69 | 0.5796 | 9.7132 |  |  |  | 1.2306 |  |  | 0.0058 |  |  |  | 0.0093868 |  | 0.015187 | 50000 | 7.2805 |  |  | 1.2306 |  |  | 2016 | 2016 | Lobby
2019 | LobbyDL701 |  | 20.1 | Match? | DL701 | LED | Downlight small 90 CRI | 1 | 38 | 6.48 | 38 | 50000 | 0.0031579 | 0.12 | 0.14 | 0.1176 | 0.56987 |  |  |  | 0.19421 |  |  | 0.0012 |  |  |  | 0.0019421 |  | 0.0031421 | 50000 | 0.4265 |  |  | 0.19421 |  |  | 2016 | 2016 | Lobby
2019 | Lobby0 |  | 20.1 | Yes | 0 | 0 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  | 0 |  |  | 0 |  |  |  | 0 |  | 0 | 0 | 0 |  |  | 0 |  |  | 2016 | 2016 | Lobby
2019 | LobbyWG701 |  | 20.1 |  | WG701 | LED | Wallgrazing direct distribution | 1 | 18 | 12.978 | 18 | 50000 | 0.0077778 | 0.14 | 0.17 | 0.1428 | 1.4013 |  |  |  | 0.47833 |  |  | 0.0014 |  |  |  | 0.0047833 |  | 0.0061833 | 50000 | 1.0499 |  |  | 0.47833 |  |  | 2016 | 2016 | Lobby
2019 | Lobby | Lobby - Hotel |  | 0.51 | [5 empty] | 30.51 | [6 empty] | 4.4573 | [20 empty] | x | 2016 | Lobby - Hotel
2019 | Lobby - HotelDL702 |  | 79 | 0.5 | DL702 | LED | Downlight small 90 CRI | 1 | 24 | 21.6 | 24 | 50000 | 0.016667 | 0.4 |  |  | 3.0053 |  |  |  | 1.025 |  |  | 0.004 |  |  |  | 0.01025 |  | 0.01425 | 50000 | 2.251 |  |  | 1.025 |  |  | 2016 | 2016 | Lobby - Hotel
2019 | Lobby - Hotel0 |  | 79 | Match? | 0 | 0 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 |  |  |  | 0 |  |  | 0 |  |  |  | 0 |  | 0 | 0 | 0 |  |  | 0 |  |  | 2016 | 2016 | Lobby - Hotel
2019 | Lobby - Hotel0 |  | 79 | Yes | 0 | 0 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 |  |  |  | 0 |  |  | 0 |  |  |  | 0 |  | 0 | 0 | 0 |  |  | 0 |  |  | 2016 | 2016 | Lobby - Hotel
2019 | Lobby - HotelWW703 |  | 79 |  | WW703 | LED | Linear WW Open | 1 | 53 | 8.91 | 53 | 50000 | 0.0018868 | 0.1 |  |  | 1.4519 |  |  |  | 0.18566 |  |  | 0.001 |  |  |  | 0.0011604 |  | 0.0021604 | 50000 | 1.0882 |  |  | 0.18566 |  |  | 2016 | 2016 | Lobby - Hotel
2019 |  | Office-BLDG-SO |  | 0.64 | [5 empty] | 62.0467 | [6 empty] | 12.4474 | [20 empty] | x | 2016 | Office-BLDG-SO
2019 | Office-BLDG-SOID701 |  | 25 | 0.64 | ID701 | LED | Linear Dir/Indir | 1 | 33 | 55.7568 | 33 | 50000 | 0.017067 | 0.5632 | 0.88 |  | 11.4284 |  |  |  | 1.376 |  |  | 0.005632 |  |  |  | 0.010496 |  | 0.016128 | 50000 | 8.567 |  |  | 1.376 |  |  | 2016 | 2016 | Office-BLDG-SO
2019 | Office-BLDG-SO0 |  | 25 | Match? | 0 | 0 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  |  |  | 0 |  |  | 0 |  |  |  | 0 |  | 0 | 0 | 0 |  |  | 0 |  |  | 2016 | 2016 | Office-BLDG-SO
2019 | Office-BLDG-SO0 |  | 25 | Yes | 0 | 0 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  |  |  | 0 |  |  | 0 |  |  |  | 0 |  | 0 | 0 | 0 |  |  | 0 |  |  | 2016 | 2016 | Office-BLDG-SO
2019 | Office-BLDG-SOWW714 |  | 25 |  | WW714 | LED | Linear WW Open | 1 | 58 | 6.2899 | 58 | 50000 | 0.0013241 | 0.0768 | 0.12 |  | 1.019 |  |  |  | 0.1303 |  |  | 0.000768 |  |  |  | 0.00081434 |  | 0.0015823 | 50000 | 0.7637 |  |  | 0.1303 |  |  | 2016 | 2016 | Office-BLDG-SO
2019 |  | Office-BLDG-LO |  | 0.64 | [5 empty] | 62.0467 | [6 empty] | #N/A | [20 empty] | x | 2016 | Office-BLDG-LO
2019 | Office-BLDG-LOID701 |  | 27 | 0.64 | ID701 | LED | Linear Dir/Indir | 1 | 33 | 55.7568 | 33 | 50000 | 0.017067 | 0.5632 | 0.88 |  | 11.4284 |  |  |  | 1.376 |  |  | 0.005632 |  |  |  | 0.010496 |  | 0.016128 | 50000 | 8.567 |  |  | 1.376 |  |  | 2016 | 2016 | Office-BLDG-LO
2019 | Office-BLDG-LO0 |  | 27 | Match? | 0 | 0 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  |  |  | 0 |  |  | 0 |  |  |  | 0 |  | 0 | 0 | 0 |  |  | 0 |  |  | 2016 | 2016 | Office-BLDG-LO
2019 | Office-BLDG-LO0 |  | 27 | Yes | 0 | 0 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  |  |  | 0 |  |  | 0 |  |  |  | 0 |  | 0 | 0 | 0 |  |  | 0 |  |  | 2016 | 2016 | Office-BLDG-LO
2019 | Office-BLDG-LOWW714 |  | 27 |  | WW714 | LED | Linear WW Open | 1 | 58 | 6.2899 | 58 | 50000 | 0.0013241 | 0.0768 | 0.12 |  | 1.019 |  |  |  | 0.1303 |  |  | 0.000768 |  |  |  | 0.00081434 |  | 0.0015823 | 50000 | 0.7637 |  |  | 0.1303 |  |  | 2016 | 2016 | Office-BLDG-LO
2019 |  | Office-Enclosed |  | 0.74 | [5 empty] | 76.59 | [6 empty] | 3.1987 | [20 empty] | x | 2016 | Office-Enclosed
2019 | Office-EnclosedTR701 |  | 25 | 0.74 | TR701 | LED | Linear Rec Hi Perf Lensed | 1 | 32 | 76.59 | 32 | 50000 | 0.023125 | 0.74 | 1 | 0.74 | 3.1987 |  |  |  | 1.4222 |  |  | 0.0074 |  |  |  | 0.014222 |  | 0.021622 | 50000 | 2.3934 |  |  | 1.4222 |  |  | 2016 | 2016 | Office-Enclosed
2019 | Office-Enclosed0 |  | 25 | Match? | 0 | 0 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  | 0 |  |  | 0 |  |  |  | 0 |  | 0 | 0 | 0 |  |  | 0 |  |  | 2016 | 2016 | Office-Enclosed
2019 | Office-Enclosed0 |  | 25 | Yes | 0 | 0 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  | 0 |  |  | 0 |  |  |  | 0 |  | 0 | 0 | 0 |  |  | 0 |  |  | 2016 | 2016 | Office-Enclosed
2019 | Office-Enclosed0 |  | 25 |  | 0 | 0 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  | 0 |  |  | 0 |  |  |  | 0 |  | 0 | 0 | 0 |  |  | 0 |  |  | 2016 | 2016 | Office-Enclosed
2019 |  | Office - Open Plan (Including Other) |  | 0.61 | [5 empty] | 59.535 | [6 empty] | 0 | [20 empty] | x | 2016 | Office - Open Plan (Including Other)
2019 | Office - Open Plan (Including Other)ID701 |  | 27 | 0.61 | ID701 | LED | Linear Dir/Indir | 1 | 33 | 55.44 | 33 | 50000 | 0.01697 | 0.56 | 0.92 | 0.5612 | 11.3634 |  |  |  | 1.3682 |  |  | 0.0056 |  |  |  | 0.010436 |  | 0.016036 | 50000 | 8.5184 |  |  | 1.3682 |  |  | 2016 | 2016 | Office - Open Plan (Including Other)
2019 | Office - Open Plan (Including Other)TL702 |  | 27 | Match? | TL702 | LED | Task | 1 | 10 | 0 | 10 | 50000 | 0 | 0 | 0 | 0 | 0 |  |  |  | 0 |  |  | 0 |  |  |  | 0 |  | 0 | 50000 | 0 |  |  | 0 |  |  | 2016 | 2016 | Office - Open Plan (Including Other)
2019 | Office - Open Plan (Including Other)0 |  | 27 | Yes | 0 | 0 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  | 0 |  |  | 0 |  |  |  | 0 |  | 0 | 0 | 0 |  |  | 0 |  |  | 2016 | 2016 | Office - Open Plan (Including Other)
2019 | Office - Open Plan (Including Other)WW714 |  | 27 |  | WW714 | LED | Linear WW Open | 1 | 58 | 4.095 | 58 | 50000 | 0.00086207 | 0.05 | 0.08 | 0.0488 | 0.66343 |  |  |  | 0.084828 |  |  | 0.0005 |  |  |  | 0.00053017 |  | 0.0010302 | 50000 | 0.4972 |  |  | 0.084828 |  |  | 2016 | 2016 | Office - Open Plan (Including Other)
Input |  | Office-Enclosed-whole |  | 0.74 | [5 empty] | 76.59 | [6 empty] | #N/A | [20 empty] | x | 2016 | Office-Enclosed-whole
2019 | Office-Enclosed731-whole-Small |  | 25 | 0.74 | TR701 | LED | Linear Rec Hi Perf Lensed | 1 | 32 | 76.59 | 32 | 50000 | 0.023125 | 0.74 | 0.92 | 0.6808 | 3.1987 |  |  |  | 1.4222 |  |  | 0.0074 |  |  |  | 0.014222 |  | 0.021622 | 50000 | 2.3934 |  |  | 1.4222 |  |  | 2016 | 2016 | Office-Enclosed-whole
2019 | Office-Enclosed0-whole-Small |  | 25 | Match? | 0 | 0 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  | 0 |  |  | 0 |  |  |  | 0 |  | 0 | 0 | 0 |  |  | 0 |  |  | 2016 | 2016 | Office-Enclosed-whole
2019 | Office-Enclosed0-whole-Small |  | 25 | Yes | 0 | 0 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  | 0 |  |  | 0 |  |  |  | 0 |  | 0 | 0 | 0 |  |  | 0 |  |  | 2016 | 2016 | Office-Enclosed-whole
2019 | Office-Enclosed0-whole-Small |  | 25 |  | 0 | 0 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  | 0 |  |  | 0 |  |  |  | 0 |  | 0 | 0 | 0 |  |  | 0 |  |  | 2016 | 2016 | Office-Enclosed-whole
Input |  | Office - Open Plan (Including Other)-whole |  | 0.61 | [5 empty] | 59.535 | [6 empty] | #N/A | [20 empty] | x | 2016 | Office - Open Plan (Including Other)-whole
2019 | Office - Open Plan (Including Other)ID701-whole-small |  | 27 | 0.61 | ID701 | LED | Linear Dir/Indir | 1 | 33 | 55.44 | 33 | 50000 | 0.01697 | 0.56 | 0.92 | 0.5612 | 11.3634 |  |  |  | 1.3682 |  |  | 0.0056 |  |  |  | 0.010436 |  | 0.016036 | 50000 | 8.5184 |  |  | 1.3682 |  |  | 2016 | 2016 | Office - Open Plan (Including Other)-whole
2019 | Office - Open Plan (Including Other)0-whole-small |  | 27 | Match? | 0 | 0 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  | 0 |  |  | 0 |  |  |  | 0 |  | 0 | 0 | 0 |  |  | 0 |  |  | 2016 | 2016 | Office - Open Plan (Including Other)-whole
2019 | Office - Open Plan (Including Other)0-whole-small |  | 27 | Yes | 0 | 0 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  | 0 |  |  | 0 |  |  |  | 0 |  | 0 | 0 | 0 |  |  | 0 |  |  | 2016 | 2016 | Office - Open Plan (Including Other)-whole
2019 | Office - Open Plan (Including Other)WW714-whole-small |  | 27 |  | WW714 | LED | Linear WW Open | 1 | 58 | 4.095 | 58 | 50000 | 0.00086207 | 0.05 | 0.08 | 0.0488 | 0.66343 |  |  |  | 0.084828 |  |  | 0.0005 |  |  |  | 0.00053017 |  | 0.0010302 | 50000 | 0.4972 |  |  | 0.084828 |  |  | 2016 | 2016 | Office - Open Plan (Including Other)-whole
Input |  | Office-Enclosed-whole-large |  | 0.74 | [5 empty] | 76.59 | [6 empty] | #N/A | [20 empty] | x | 2016 | Office-Enclosed-whole-large
2019 | Office-EnclosedTR701-whole-large |  | 25 | 0.74 | TR701 | LED | Linear Rec Hi Perf Lensed | 1 | 32 | 76.59 | 32 | 50000 | 0.023125 | 0.74 | 1 | 0.74 | 3.1987 |  |  |  | 1.4222 |  |  | 0.0074 |  |  |  | 0.014222 |  | 0.021622 | 50000 | 2.3934 |  |  | 1.4222 |  |  | 2016 | 2016 | Office-Enclosed-whole-large
2019 | Office-Enclosed0-whole-large |  | 25 | Match? | 0 | 0 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  | 0 |  |  | 0 |  |  |  | 0 |  | 0 | 0 | 0 |  |  | 0 |  |  | 2016 | 2016 | Office-Enclosed-whole-large
2019 | Office-Enclosed0-whole-large |  | 25 | Yes | 0 | 0 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  | 0 |  |  | 0 |  |  |  | 0 |  | 0 | 0 | 0 |  |  | 0 |  |  | 2016 | 2016 | Office-Enclosed-whole-large
2019 | Office-Enclosed0-whole-large |  | 25 |  | 0 | 0 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  | 0 |  |  | 0 |  |  |  | 0 |  | 0 | 0 | 0 |  |  | 0 |  |  | 2016 | 2016 | Office-Enclosed-whole-large
Input |  | Office - Open Plan (Including Other)-whole-large |  | 0.61 | [5 empty] | 59.535 | [6 empty] | #N/A | [20 empty] | x | 2016 | Office - Open Plan (Including Other)-whole-large
2019 | Office - Open Plan (Including Other)ID701-whole-large |  | 27 | 0.61 | ID701 | LED | Linear Dir/Indir | 1 | 33 | 55.44 | 33 | 50000 | 0.01697 | 0.56 | 0.92 | 0.5612 | 11.3634 |  |  |  | 1.3682 |  |  | 0.0056 |  |  |  | 0.010436 |  | 0.016036 | 50000 | 8.5184 |  |  | 1.3682 |  |  | 2016 | 2016 | Office - Open Plan (Including Other)-whole-large
2019 | Office - Open Plan (Including Other)TL702-whole-large |  | 27 | Match? | TL702 | LED | Task | 1 | 10 | 0 | 10 | 50000 | 0 | 0 | 0 | 0 | 0 |  |  |  | 0 |  |  | 0 |  |  |  | 0 |  | 0 | 50000 | 0 |  |  | 0 |  |  | 2016 | 2016 | Office - Open Plan (Including Other)-whole-large
2019 | Office - Open Plan (Including Other)0-whole-large |  | 27 | Yes | 0 | 0 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  | 0 |  |  | 0 |  |  |  | 0 |  | 0 | 0 | 0 |  |  | 0 |  |  | 2016 | 2016 | Office - Open Plan (Including Other)-whole-large
2019 | Office - Open Plan (Including Other)WW714-whole-large |  | 27 |  | WW714 | LED | Linear WW Open | 1 | 58 | 4.095 | 58 | 50000 | 0.00086207 | 0.05 | 0.08 | 0.0488 | 0.66343 |  |  |  | 0.084828 |  |  | 0.0005 |  |  |  | 0.00053017 |  | 0.0010302 | 50000 | 0.4972 |  |  | 0.084828 |  |  | 2016 | 2016 | Office - Open Plan (Including Other)-whole-large
2019 |  | Restrooms |  | 0.63 | [5 empty] | 52.8716 | [6 empty] | #N/A | [20 empty] | x | 2016 | Restrooms
2019 | RestroomsDL709 |  | 12 | 0.63 | DL709 | LED | Downlight open | 1 | 21 | 28.7696 | 21 | 50000 | 0.0177 | 0.3717 | 0.59 | 0.3717 | 3.5159 |  |  |  | 1.0885 |  |  | 0.003717 |  |  |  | 0.010885 |  | 0.014602 | 50000 | 2.6341 |  |  | 1.0885 |  |  | 2016 | 2016 | Restrooms
2019 | Restrooms0 |  | 12 | Match? | 0 | 0 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  | 0 |  |  | 0 |  |  |  | 0 |  | 0 | 0 | 0 |  |  | 0 |  |  | 2016 | 2016 | Restrooms
2019 | Restrooms0 |  | 12 | Yes | 0 | 0 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  | 0 |  |  | 0 |  |  |  | 0 |  | 0 | 0 | 0 |  |  | 0 |  |  | 2016 | 2016 | Restrooms
2019 | RestroomsWG701 |  | 12 |  | WG701 | LED | Wallgrazing direct distribution | 1 | 18 | 24.102 | 18 | 50000 | 0.014444 | 0.26 | 0.41 | 0.2583 | 2.6025 |  |  |  | 0.88833 |  |  | 0.0026 |  |  |  | 0.0088833 |  | 0.011483 | 50000 | 1.9499 |  |  | 0.88833 |  |  | 2016 | 2016 | Restrooms
2019 |  | Retail - Sales Area |  | 1.05 | [5 empty] | 104.139 | [6 empty] | 6.9277 | [20 empty] | x | 2016 | Retail - Sales Area
2019 | Retail - Sales AreaTR701 |  | 97 | 1.05 | TR701 | LED | Linear Rec Hi Perf Lensed | 1 | 32 | 65.205 | 32 | 50000 | 0.019688 | 0.63 | 0.6 | 0.63 | 2.7232 |  |  |  | 1.2108 |  |  | 0.0063 |  |  |  | 0.012108 |  | 0.018408 | 50000 | 2.0377 |  |  | 1.2108 |  |  | 2016 | 2016 | Retail - Sales Area |  | 3312
2019 | Retail - Sales AreaDL703 |  | 97 | Match? | DL703 | LED | Downlight open or lensed | 1 | 23 | 19.467 | 23 | 50000 | 0.0091304 | 0.21 | 0.2 | 0.21 | 2.1026 |  |  |  | 0.56152 |  |  | 0.0021 |  |  |  | 0.0056152 |  | 0.0077152 | 50000 | 1.5753 |  |  | 0.56152 |  |  | 2016 | 2016 | Retail - Sales Area
2019 | Retail - Sales Area0 |  | 97 | Yes | 0 | 0 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  | 0 |  |  | 0 |  |  |  | 0 |  | 0 | 0 | 0 |  |  | 0 |  |  | 2016 | 2016 | Retail - Sales Area
2019 | Retail - Sales AreaWG701 |  | 97 |  | WG701 | LED | Wallgrazing direct distribution | 1 | 18 | 19.467 | 18 | 50000 | 0.011667 | 0.21 | 0.2 | 0.21 | 2.102 |  |  |  | 0.7175 |  |  | 0.0021 |  |  |  | 0.007175 |  | 0.009275 | 50000 | 1.5749 |  |  | 0.7175 |  |  | 2016 | 2016 | Retail - Sales Area
2019 |  | Stairway |  | 0.49 | [5 empty] | 43.7355 | [6 empty] | #N/A | [20 empty] | x | 2016 | Stairway
2019 | StairwayTR703 |  | 11 | 0.484 | TR703 | LED | Linear Rec Hi Perf Lensed | 1 | 35 | 26.0739 | 35 | 50000 | 0.0074571 | 0.261 | 0.53719 | 0.26 | 1.0317 |  |  |  | 0.45861 |  |  | 0.00261 |  |  |  | 0.0045861 |  | 0.0071961 | 50000 | 0.77181 |  |  | 0.45861 |  |  | 2016 | 2016 | Stairway
2019 | StairwayWG703 |  | 11 | Match? | WG703 | LED | Wallgrazing direct distribution | 1 | 18 | 17.6616 | 18 | 50000 | 0.012389 | 0.223 | 0.59917 | 0.29 | 2.2321 |  |  |  | 0.76192 |  |  | 0.00223 |  |  |  | 0.0076192 |  | 0.0098492 | 50000 | 1.6724 |  |  | 0.76192 |  |  | 2016 | 2016 | Stairway
2019 | Stairway0 |  | 11 | Yes | 0 | 0 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  | 0 |  |  | 0 |  |  |  | 0 |  | 0 | 0 | 0 |  |  | 0 |  |  | 2016 | 2016 | Stairway
2019 | Stairway0 |  | 11 |  | 0 | 0 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.0646e-07 | 9.9928e-08 | 0 |  |  |  | 0 |  |  | 0 |  |  |  | 0 |  | 0 | 0 | 0 |  |  | 0 |  |  | 2016 | 2016 | Stairway
2019 | Storage Total | Storage |  | 0.38 |  |  | 20 |  |  | 35.226 | [6 empty] | 1.76 |  |  |  | 0.59436 |  |  | 0.0038 | [13 empty] | x | 2016 | Storage
2019 | StorageLB702 |  | 41 | 0.38 | LB702 | LED | Lowbay linear wrap | 1 | 37 | 35.226 | 37 | 50000 | 0.01027 | 0.38 | 1 | 0.38 | 1.76 |  |  |  | 0.59436 |  |  | 0.0038 |  |  |  | 0.0063162 |  | 0.010116 | 50000 | 1.3172 |  |  | 0.59436 |  |  | 2016 | 2016 | Storage
2019 | Storage0 |  | 41 | Match? | 0 | 0 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  | 0 |  |  | 0 |  |  |  | 0 |  | 0 | 0 | 0 |  |  | 0 |  |  | 2016 | 2016 | Storage
2019 | Storage0 |  | 41 | Yes | 0 | 0 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  | 0 |  |  | 0 |  |  |  | 0 |  | 0 | 0 | 0 |  |  | 0 |  |  | 2016 | 2016 | Storage
2019 | Storage0 |  | 41 |  | 0 | 0 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 9.9297e-08 | 0 | 0 | 0 |  |  |  | 0 |  |  | 0 |  |  |  | 0 |  | 0 | 0 | 0 |  |  | 0 |  |  | 2016 | 2016 | Storage
1 FL linear fluorescent, CF compact fluorescent, MH metal halide
Where LSC design variations between 2016 and 2019 resulted in large cost anomolies, one of the designs was selected and LPD was adjusted to match requirements.

## Int Lighting Comp (hidden)
90.1 Cost Effectiveness - Cost Estimate - Interior Lighting | [40 empty] | Lighting output factors
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | [12 empty] | 1 | 2 | 3 | 6 | 7
[30 empty] | Note: ballast replacement hours from Means | [10 empty] | Type | lm/W | Lum/Lamp | L L Depr | Depr w/ dirt | 0.95
[30 empty] | are for retrofit conditions, since balasts are included | [10 empty] | INC | 12.6 |  | 0.83 | 0.7885
Labor cost/hour, electrical - general, RS Means 2020 |  |  | 61.5 | [26 empty] | with the fixture and adding a replacement multiplier | [10 empty] | PAR | 15 |  | 0.83 | 0.7885
[30 empty] | would be redundant. | [10 empty] | MR |  |  | 0.83 | 0.7885
Interior Lighting Fixture Costs - Used for both Target & Base Code | [29 empty] | So hours are divided by the multiplier that will be added | [10 empty] | CF | 65 |  | 0.9 | 0.855
[30 empty] | as a cost adjustment in the final prototype estimate. | [10 empty] | LED | 0 |  | 0.92 | 0.874
Description | [9 empty] | New Construction Costs | [8 empty] | Replacement Costs | [9 empty] | 1.65 | [11 empty] | FL | 90 | 2900 | 0.9 | 0.855
Fixture Type Code | Type of Lamp | Fixture Description Distribution Type | Lamp Description | Fixture Watts | Lamp Watts | Number of Lamps | Lamp Life hours | Ballast Description (ballast cost under replacement costs, for first cost, ballast included with fixture) | Ballast Life hours | Fixture Cost (ballast if any included) | Fixture Source | Fixture Label in Source | Lamp Cost (per lamp) | Lamp Source (Grainger 2018) | Lamp ID in Source (Grainger 2018) | Installation Labor RS Means 2020 Reference Number | Installation Labor Hours | Installation Labor Cost | Replace Labor RS Means Reference Number (section 26 61 23.10 if not shown) | Relamp Labor Hours | Relamp Labor Cost | Ballast / Driver Replacement Ballast Cost |  | Ballast ID in Source | Ballast Replace Labor RS Means Reference Number | Replace Ballast Labor Hours | Replace Ballast Labor Cost | Fixt Lumens Used | (Means) Replace Ballast Labor Hours | # Times Used in Cost Effectiveness Analysis | Raw Lum/Lamp | Ballast Factor | Luminaire Efficiency | 90.1 Efficacy | Eff icacy Based Source Lumens | Catalog Lumens | override Fixture lum | Lumen Depr | Fixt Lumens Used |  | MH | 80 |  | 0.7 | 0.665
[41 empty] | TH | 19.2 |  | 0.9 | 0.855
[41 empty] | CMH | 90 |  | 0.7 | 0.665
0 | NA | NA |  | 0 | 0 | 0 | 0 | NA | 0 | 0 |  |  | 0
301 | INC | Inc residential screw in lamp | A19 | 60 | 60 | 1 | 1000 | NA | 0 | 0 | NA |  | 0.89 | www.1000bulbs.com |  | repl by resident | 0 | 0 | repl by resident | 0 | 0 | 0 |  |  |  |  | 0 | 540 |  | 2 | 750 | 1 | 0.8 |  | 0 |  |  | 0.9 | 540
302 | CF | CFL residential screw in lamp | A19 | 14 | 14 | 1 | 10000 | NA | 0 | 0 | NA |  | 1.92 | www.1000bulbs.com | FC14 | repl by resident | 0 | 0 | repl by resident | 0 | 0 | 0 | 0 |  | 0 |  | 0 | 648 |  | 2 | 900 | 1 | 0.8 |  | 0 |  |  | 0.9 | 648
303 | LED | LEC residential screw in lamp | A19 | 9 | 9 | 1 | 15000 | NA | 0 | 0 | NA |  | 1.62 | www.1000bulbs.com | #N/A | repl by resident | 0 | 0 | repl by resident | 0 | 0 | 0 |  |  |  |  | 0 | 576 |  | 2 | 800 | 1 | 0.8 |  | 0 |  |  | 0.9 | 576
511 | PAR | Downlight open - flood | PAR30L | 60 | 60 | 1 | 4200 | NA | 0 | 37.08 | grainger.com | H7ICAT+4XA90 | 21.38 | grainger.com | 4HCK8 | 26 51 13.50-4470 | 1 | 61.5 | 1780 | 0.05 | 2.91 | 0 | #N/A | #N/A | #N/A | 0 | 0 | 336.15 |  | 1 | 900 | 0.83 | 0.5 |  | 0 |  |  | 0.9 | 336.15
522 | LED | Downlight open | LED | 18 | 1 | 1 | 50000 | NA | 0 | 155 | grainger.com | 45AY05 | 0.01 | #N/A | #N/A | 26 51 13.55-0100 | 1 | 61.5 | #N/A | 0.01 | 0.615 | 116.25 | Assumes 75% initial fixture cost | #N/A | Assumes same labor time | 1 | 61.5 | 850.5 |  | 3 | 0 | 1 | 0.874 | 52.5 | 945 |  |  | 0.9 | 850.5
524 | CF | indirect Wall Scounce | Double Biax - 4 Pin | 39 | 18 | 2 | 10000 | Programmed-Rapid Start Ballast | 50000 | 89.67 | goodmart.com | P7083-09EBWB | 15.7 | see above | 1PGX2 | 5600 | 1 | 61.5 | 0570 | 0.1 | 5.8 | 0 | 0 | 0 | 0 | 0 | 0 | 810.2835 |  | 1 | 585 | 0.9 | 0.855 |  | 0 |  |  | 0.9 | 810.2835
534-2 | FL | Linear Wall Cove | F32T8 - Bi-Pin Base | 29 | 32 | 1 | 36000 | Electronic Ballast - Program-Start 1 Lamp | 50000 | 380 | goodmart.com | 74IW-1T5HO-3I-UEB-SI | 3.35 | grainger.com | 4PL15 | 2200 | 0.941 | 57.8715 | 26 61 23.10-0180 | 0.08889 | 5.4667 | 30 | grainger.com | 6WXE9 | 26 51 13.50-7630 | 1 | 61.5 | 2349 | 1 | 2 | 2900 | 0.88 | 0.5 | 90 | 2610 |  |  | 0.9 | 2349
537-1 | FL | Linear WW Open | F32T8 - Bi-Pin Base | 29 | 32 | 1 | 36000 | Electronic Ballast - Program Start 1 Lamp | 50000 | 103.57 | Build.com | Elco ETC424W | 3.35 | grainger.com | 4PL15 | 3540 | 1 | 61.5 | 26 61 23.10-0180 | 0.08889 | 5.4667 | 30 | grainger.com | 6WXE9 | 26 51 13.50-7630 | 1 | 61.5 | 2008.395 | 1 | 1 | 2900 | 0.9 | 0.855 |  | 0 |  |  | 0.9 | 2008.395
537-1_LED | LED | Wallgrazing direct distribution | LED | 23 | 1 | 1 | 50000 | #N/A | 50000 | 179.99 | Elocity LED | WW-LG-RGBW-2 | 0.01 | #N/A | #N/A | 26 51 13.55-1000 | 1.509 | 92.8035 | #N/A | 1e-06 | 6.15e-05 | 89.995 | Assumes 75% initial fixture cost | #N/A | Assumes same labor time | 1.509 | 92.8035 | 2132.1 |  | 1 | 0 | 0.92 | 0.874 | 103 | 2369 |  |  | 0.9 | 2132.1
572 | TH | Downlight open | PAR30 | 75 | 75 | 1 | 850 | NA | 0 | 27.9 | grainger.com | 5TP94 | 21.38 | grainger.com | 4HCK8 | 26 51 13.50-4470 | 1 | 61.5 | 1700 | 0.4 | 23.5 | 0 | #N/A | #N/A | #N/A | 0 | 0 | 1282.5 |  | 1 | 1440 | 0.9 | 0.5 | 19 | 1425 |  |  | 0.9 | 1282.5
600 | FL | High Perf Lensed | F32T8 - Bi-Pin Base | 58 | 32 | 2 | 36000 | Electronic Ballast - Program-Start 2 Lamp | 50000 | 172 | grainger.com | 6HHG0 | 3.35 | grainger.com | 4PL15 | 26 51 13.50-3530 | 1.6 | 98.4 |  |  | 0.1 | 36.56 | grainger.com | 2DCX1 | 26 51 13.50-7630 | 1 | 61.5 | 4134.24 |  | 0 | 2900 | 0.9 | 0.88 |  | 0 |  |  | 0.9 | 4134.24
600_LED | LED | High Perf Lensed | LED | 40 | 1 | 1 | 50000 | #N/A | 50000 | 172 | grainger.com | 6HHG0 | 0.01 | #N/A | #N/A | 26 51 13.55-1000 | 1.509 | 92.8035 | #N/A | 0.01 | 0.615 | 129 | Assumes 75% initial fixture cost | #N/A | Assumes same labor time | 1.509 | 92.8035 | 3600 |  | 1 | 0 | 0.92 | 0.88 | 100 | 4000 |  |  | 0.9 | 3600
604 | FL | Wall Mounted Linear Direct/Indirect | F32T8 - Bi-Pin Base | 29 | 32 | 1 | 36000 | Electronic Ballast - Program-Start 1 Lamp | 50000 | 349 | goodmart.com | DUW-4-1T8-GEB10RS-120-LD | 3.35 | grainger.com | 4PL15 | 3540 | 0.49 | 30.135 | 26 61 23.10-0180 | 0.08889 | 5.4667 | 30 | grainger.com | 6WXE9 | 26 51 13.50-7630 | 1 | 61.5 | 2008.395 | 1 | 1 | 2900 | 0.9 | 0.855 |  |  |  |  | 0.9 | 2008.395
700 | LED | Linear Rec Hi Perf Lensed | LED | 36 | 1 | 1 | 50000 | #N/A | 50000 | 138 | RS-Means | 26.51-13.55-1000 | 0.01 | #N/A | #N/A | 26 51 13.55-1000 | 1.509 | 92.8035 | #N/A | 0.01 | 0.615 | 103.5 | Assumes 75% initial fixture cost | #N/A | Assumes same labor time | 1.509 | 92.8035 | 3337.2 |  | 4 | 0 | 1 | 1 | 103 | 3708 |  |  | 0.9 | 3337.2
701 | LED | Downlight open | LED | 12 | 1 | 1 | 50000 | #N/A | 50000 | 164.9468 | Grainger + efficacy & CRI function | --- | 0.01 | #N/A | #N/A | 26 51 13.55-0100 | 1 | 61.5 | #N/A | 0.01 | 0.615 | 123.7101 | Assumes 75% initial fixture cost | #N/A | Assumes same labor time | 1 | 61.5 | 734.4 |  | 2 | 0 | 1 | 1 | 68 | 816 |  |  | 0.9 | 734.4 | 164.9468
702 | LED | Linear Wall Cove | LED | 19 | 1 | 1 | 50000 | #N/A | 50000 | 170 | goodmart.com | NanoLume-6W-2700K-120-120V-W-S-24inch | 0.01 | #N/A | #N/A | 26 51 13.55-3565 | 1.6 | 98.4 | #N/A | 0.01 | 0.615 | 127.5 | Assumes 75% initial fixture cost | #N/A | Assumes same labor time | 1.6 | 98.4 | 1436.4 |  | 1 | 0 | 1 | 1 | 84 | 1596 |  |  | 0.9 | 1436.4
703 | LED | Linear WW Open | LED | 75 | 1 | 1 | 50000 | #N/A | 50000 | 769 | goodmart.com | C2X21LEDWWWH | 0.01 | #N/A | #N/A | 26 51 13.55-3565 | 1.6 | 98.4 | #N/A | 0.01 | 0.615 | 576.75 | Assumes 75% initial fixture cost | #N/A | Assumes same labor time | 1.6 | 98.4 | 4725 |  | 7 | 0 | 1 | 1 | 70 | 5250 |  |  | 0.9 | 4725
720 | LED | Downlight Lensed | LED | 22 | 1 | 1 | 50000 | #N/A | 50000 | 168.667 | Grainger + efficacy & CRI function | --- | 0.01 | #N/A | #N/A | 26 51 13.55-0100 | 1 | 61.5 | #N/A | 0.01 | 0.615 | 126.5002 | Assumes 75% initial fixture cost | #N/A | Assumes same labor time | 1 | 61.5 | 1386 |  | 3 | 0 | 1 | 1 | 70 | 1540 |  |  | 0.9 | 1386 | 168.667
723 | LED | Indirect Pendant | LED | 46 | 1 | 1 | 50000 | #N/A | 50000 | 636 | LBC Lighting | Contech CPL3 12" | 0.01 | #N/A | #N/A | 26 51 13.55-3010 | 1.311 | 80.6265 | #N/A | 0.01 | 0.615 | 477 | Assumes 75% initial fixture cost | #N/A | Assumes same labor time | 1.311 | 80.6265 | 2898 |  | 1 | 0 | 1 | 1 | 70 | 3220 |  |  | 0.9 | 2898
727-1 | LED | WW Open | LED | 20 | 1 | 1 | 50000 | #N/A | 50000 | 270 | goodmart.com | C4X420LEDWW30KCCLW | 0.01 | #N/A | #N/A | 26 51 13.55-3540 | 1 | 61.5 | #N/A | 0.01 | 0.615 | 202.5 | Assumes 75% initial fixture cost | #N/A | Assumes same labor time | 1 | 61.5 | 1800 |  | 2 | 0 | 1 | 1 | 100 | 2000 |  |  | 0.9 | 1800
727-2 | LED | WW Open | LED | 25 | 1 | 1 | 50000 | #N/A | 50000 | 670 | goodmart.com | 0.08.3KVHO.W33.1.18.1 | 0.01 | #N/A | #N/A | 26 51 13.55-3540 | 1 | 61.5 | #N/A | 0.01 | 0.615 | 502.5 | Assumes 75% initial fixture cost | #N/A | Assumes same labor time | 1 | 61.5 | 2250 |  | 1 | 0 | 1 | 1 | 100 | 2500 |  |  | 0.9 | 2250
730 | LED | Linear Direct Lensed | LED | 40.3 | 1 | 1 | 50000 | #N/A | 50000 | 191 | grainer.com | 45AZ95 | 0.01 | #N/A | #N/A | 26 51 13.55-0100 | 1 | 61.5 | #N/A | 0.01 | 0.615 | 143.25 | Assumes 75% initial fixture cost | #N/A | Assumes same labor time | 1 | 61.5 | 3518.19 |  | 2 | 0 | 1 | 1 | 97 | 3909.1 |  |  | 0.9 | 3518.19
731 | LED | Narrow Linear | LED | 40 | 1 | 1 | 50000 | #N/A | 50000 | 382 | Esimate - twice 730 |  | 0.01 | #N/A | #N/A | 26 51 13.55-3010 | 1.311 | 80.6265 | #N/A | 0.01 | 0.615 | 286.5 | Assumes 75% initial fixture cost | #N/A | Assumes same labor time | 1.311 | 80.6265 | 3168 |  | 4 | 0 | 1 | 1 | 88 | 3520 |  |  | 0.9 | 3168
735 | LED | Linear Dir/Ind | LED | 38 | 1 | 1 | 50000 | #N/A | 50000 | 669.3 | goodmart.com | CS14-38L-35K-10V | 0.01 | #N/A | #N/A | 26 51 13.55-3010 | 1.311 | 80.6265 | #N/A | 0.01 | 0.615 | 501.975 | Assumes 75% initial fixture cost | #N/A | Assumes same labor time | 1.311 | 80.6265 | 3420 |  | 7 | 0 | 1 | 1 | 100 | 3800 |  |  | 0.9 | 3420
738 | LED | Linear Industrial | LED | 38 | 1 | 1 | 50000 | #N/A | 50000 | 250 | grainer.com | 53CT75 | 0.01 | #N/A | #N/A | 26 51 13.55-2000 | 0.941 | 57.8715 | #N/A | 0.01 | 0.615 | 187.5 | Assumes 75% initial fixture cost | #N/A | Assumes same labor time | 0.941 | 57.8715 | 3933 |  | 2 | 0 | 1 | 1 | 115 | 4370 |  |  | 0.9 | 3933
739 | LED | Task | LED | 10 | 1 | 1 | 50000 | #N/A | 50000 | 128 | grainer.com | 39F141 | 0.01 | #N/A | #N/A |  | 0.49 | 30.135 | #N/A | 0.01 | 0.615 | 96 | Assumes 75% initial fixture cost | #N/A | Assumes same labor time | 0.49 | 30.135 | 612 |  | 9 | 0 | 1 | 1 | 68 | 680 |  |  | 0.9 | 612
741 | LED | Downlight open | LED | 24 | 1 | 1 | 50000 | #N/A | 50000 | 164.9468 | Grainger + efficacy & CRI function | --- | 0.01 | #N/A | #N/A | 26 51 13.55-0100 | 1 | 61.5 | #N/A | 0.01 | 0.615 | 123.7101 | Assumes 75% initial fixture cost | #N/A | Assumes same labor time | 1 | 61.5 | 1468.8 |  | 1 | 0 | 1 | 1 | 68 | 1632 |  |  | 0.9 | 1468.8 | 164.9468
DL701 | LED | Downlight small 90 CRI | LED | 38 | 1 | 1 | 50000 | #N/A | 50000 | 180.0792 | Grainger + efficacy & CRI function | --- | 0.01 | #N/A | #N/A | 26 51 13.55-0100 | 1 | 61.5 | #N/A | 0.01 | 0.615 | 135.0594 | Assumes 75% initial fixture cost | #N/A | Assumes same labor time | 1 | 61.5 | 2052 |  | 1 | 0 | 1 | 1 | 60 | 2280 |  |  | 0.9 | 2052 | 180.0792
DL702 | LED | Downlight small 90 CRI | LED | 24 | 1 | 1 | 50000 | #N/A | 50000 | 180.0792 | Grainger + efficacy & CRI function | --- | 0.01 | #N/A | #N/A | 26 51 13.55-0100 | 1 | 61.5 | #N/A | 0.01 | 0.615 | 135.0594 | Assumes 75% initial fixture cost | #N/A | Assumes same labor time | 1 | 61.5 | 1296 |  | 2 | 0 | 1 | 1 | 60 | 1440 |  |  | 0.9 | 1296 | 180.0792
DL703 | LED | Downlight open or lensed | LED | 23 | 1 | 1 | 50000 | #N/A | 50000 | 230.0503 | Grainger + efficacy & CRI function | --- | 0.01 | #N/A | #N/A | 26 51 13.55-0100 | 1 | 61.5 | #N/A | 0.01 | 0.615 | 172.5377 | Assumes 75% initial fixture cost | #N/A | Assumes same labor time | 1 | 61.5 | 2132.1 |  | 2 | 0 | 1 | 1 | 103 | 2369 |  |  | 0.9 | 2132.1 | 230.0503 | 20 | 1400 | 70 | 179 | 3000 K | 6" | 45AX90
DL706 | LED | Downlight open | LED | 12 | 1 | 1 | 50000 | #N/A | 50000 | 164.9468 | Grainger + efficacy & CRI function | --- | 0.01 | #N/A | #N/A | 26 51 13.55-0100 | 1 | 61.5 | #N/A | 0.01 | 0.615 | 123.7101 | Assumes 75% initial fixture cost | #N/A | Assumes same labor time | 1 | 61.5 | 734.4 |  | 2 | 0 | 1 | 1 | 68 | 816 |  |  | 0.9 | 734.4 | 164.9468 | 12 | 600 | 50 | 133 | 3000 K | 6" | 45AY26
DL707 | LED | Downlight open | LED | 8 | 1 | 1 | 50000 | #N/A | 50000 | 204.0089 | Grainger + efficacy & CRI function | --- | 0.01 | #N/A | #N/A | 26 51 13.55-0100 | 1 | 61.5 | #N/A | 0.01 | 0.615 | 153.0067 | Assumes 75% initial fixture cost | #N/A | Assumes same labor time | 1 | 61.5 | 640.8 |  | 2 | 0 | 1 | 1 | 89 | 712 |  |  | 0.9 | 640.8 | 204.0089 | 8.9 | 600 | 67.4157 | 152 | 3000 K | 6" | 45AY90
DL709 | LED | Downlight open | LED | 21 | 1 | 1 | 50000 | #N/A | 50000 | 198.4286 | Grainger + efficacy & CRI function | --- | 0.01 | #N/A | #N/A | 26 51 13.55-0100 | 1 | 61.5 | #N/A | 0.01 | 0.615 | 148.8214 | Assumes 75% initial fixture cost | #N/A | Assumes same labor time | 1 | 61.5 | 1625.4 |  | 2 | 0 | 1 | 1 | 86 | 1806 |  |  | 0.9 | 1625.4 | 198.4286
ID701 | LED | Linear Dir/Indir | LED | 33 | 1 | 1 | 50000 | #N/A | 50000 | 669.3 | goodmart.com | CS14-38L HE-35K-10V | 0.01 | #N/A | #N/A | 26 51 13.55-3010 | 1.311 | 80.6265 | #N/A | 0.01 | 0.615 | 501.975 | Assumes 75% initial fixture cost | #N/A | Assumes same labor time | 1.311 | 80.6265 | 3267 | 1 | 7 | 0 | 1 | 1 | 110 | 3630 |  |  | 0.9 | 3267
IP701 | LED | indirect Pendant | LED | 38 | 1 | 1 | 50000 | #N/A | 50000 | 636 | LBC Lighting | Contech CPL3 12" | 0.01 | #N/A | #N/A | 26 51 13.55-3010 | 1.311 | 80.6265 | #N/A | 0.01 | 0.615 | 477 | Assumes 75% initial fixture cost | #N/A | Assumes same labor time | 1.311 | 80.6265 | 2907 |  | 1 | 0 | 1 | 1 | 85 | 3230 |  |  | 0.9 | 2907
LB702 | LED | Lowbay linear wrap | LED | 37 | 1 | 1 | 50000 | #N/A | 50000 | 171 | RS-Means | 2651-13.55-3000 | 0.01 | #N/A | #N/A | 26 51 13.55-2000 | 0.941 | 57.8715 | #N/A | 0.01 | 0.615 | 128.25 | Assumes 75% initial fixture cost | #N/A | Assumes same labor time | 0.941 | 57.8715 | 3429.9 |  | 2 | 0 | 1 | 1 | 103 | 3811 |  |  | 0.9 | 3429.9
TL702 | LED | Task | LED | 10 | 1 | 1 | 50000 | #N/A | 50000 | 128 | grainer.com | 39F141 | 0.01 | #N/A | #N/A |  | 0.49 | 30.135 | #N/A | 0.01 | 0.615 | 96 | Assumes 75% initial fixture cost | #N/A | Assumes same labor time | 0.49 | 30.135 | 612 |  | 3 | 0 | 1 | 1 | 68 | 680 |  |  | 0.9 | 612
TR701 | LED | Linear Rec Hi Perf Lensed | LED | 32 | 1 | 1 | 50000 | #N/A | 50000 | 138 | RS-Means | 26.51-13.55-1000 | 0.01 | #N/A | #N/A | 26 51 13.55-0100 | 1 | 61.5 | #N/A | 0.01 | 0.615 | 103.5 | Assumes 75% initial fixture cost | #N/A | Assumes same labor time | 1 | 61.5 | 3312 |  | 5 | 0 | 1 | 1 | 115 | 3680 |  |  | 0.9 | 3312
TR703 | LED | Linear Rec Hi Perf Lensed | LED | 35 | 1 | 1 | 50000 | #N/A | 50000 | 138 | RS-Means | 26.51-13.55-1000 | 0.01 | #N/A | #N/A | 26 51 13.55-0100 | 1 | 61.5 | #N/A | 0.01 | 0.615 | 103.5 | Assumes 75% initial fixture cost | #N/A | Assumes same labor time | 1 | 61.5 | 3496.5 |  | 3 | 0 | 1 | 1 | 111 | 3885 |  |  | 0.9 | 3496.5
TR704 | LED | Linear Rec Hi Perf Lensed | LED | 32 | 1 | 1 | 50000 | #N/A | 50000 | 138 | RS-Means | 26.51-13.55-1000 | 0.01 | #N/A | #N/A | 26 51 13.55-0100 | 1 | 61.5 | #N/A | 0.01 | 0.615 | 103.5 | Assumes 75% initial fixture cost | #N/A | Assumes same labor time | 1 | 61.5 | 3196.8 |  | 3 | 0 | 1 | 1 | 111 | 3552 |  |  | 0.9 | 3196.8
WG701 | LED | Wallgrazing direct distribution | LED | 18 | 1 | 1 | 50000 | #N/A | 50000 | 179.99 | Elocity LED | WW-LG-RGBW-2 | 0.01 | #N/A | #N/A | 26 51 13.55-3540 | 1 | 61.5 | #N/A | 0.01 | 0.615 | 134.9925 | Assumes 75% initial fixture cost | #N/A | Assumes same labor time | 1 | 61.5 | 1668.6 |  | 3 | 0 | 1 | 1 | 103 | 1854 |  |  | 0.9 | 1668.6
WG702 | LED | Wallgrazing direct distribution | LED | 18 | 1 | 1 | 50000 | #N/A | 50000 | 179.99 | Elocity LED | WW-LG-RGBW-2 | 0.01 | #N/A | #N/A | 26 51 13.55-3540 | 1 | 61.5 | #N/A | 0.01 | 0.615 | 134.9925 | Assumes 75% initial fixture cost | #N/A | Assumes same labor time | 1 | 61.5 | 1425.6 |  | 1 | 0 | 1 | 1 | 88 | 1584 |  |  | 0.9 | 1425.6
WG703 | LED | Wallgrazing direct distribution | LED | 18 | 1 | 1 | 50000 | #N/A | 50000 | 179.99 | Elocity LED | WW-LG-RGBW-2 | 0.01 | #N/A | #N/A | 26 51 13.55-3540 | 1 | 61.5 | #N/A | 0.01 | 0.615 | 134.9925 | Assumes 75% initial fixture cost | #N/A | Assumes same labor time | 1 | 61.5 | 1425.6 |  | 1 | 0 | 1 | 1 | 88 | 1584 |  |  | 0.9 | 1425.6
WW703 | LED | Linear WW Open | LED | 53 | 1 | 1 | 50000 | #N/A | 50000 | 769 | goodmart.com | C2X21LEDWWWH | 0.01 | #N/A | #N/A | 26 51 13.55-3570 | 1.6 | 98.4 | #N/A | 0.01 | 0.615 | 576.75 | Assumes 75% initial fixture cost | #N/A | Assumes same labor time | 1.6 | 98.4 | 4722.3 |  | 1 | 0 | 1 | 1 | 99 | 5247 |  |  | 0.9 | 4722.3
WW704 | LED | Linear WW Open | LED | 60 | 1 | 1 | 50000 | #N/A | 50000 | 769 | goodmart.com | C2X21LEDWWWH | 0.01 | #N/A | #N/A | 26 51 13.55-3570 | 1.6 | 98.4 | #N/A | 0.01 | 0.615 | 576.75 | Assumes 75% initial fixture cost | #N/A | Assumes same labor time | 1.6 | 98.4 | 2538 |  | 1 | 0 | 1 | 1 | 47 | 2820 |  |  | 0.9 | 2538
WW708 | LED | Linear WW Open | LED | 53 | 1 | 1 | 50000 | #N/A | 50000 | 769 | goodmart.com | C2X21LEDWWWH | 0.01 | #N/A | #N/A | 26 51 13.55-3570 | 1.6 | 98.4 | #N/A | 0.01 | 0.615 | 576.75 | Assumes 75% initial fixture cost | #N/A | Assumes same labor time | 1.6 | 98.4 | 4722.3 |  | 1 | 0 | 1 | 1 | 99 | 5247 |  |  | 0.9 | 4722.3
WW714 | LED | Linear WW Open | LED | 58 | 1 | 1 | 50000 | #N/A | 50000 | 769 | goodmart.com | C2X21LEDWWWH | 0.01 | #N/A | #N/A | 26 51 13.55-3570 | 1.6 | 98.4 | #N/A | 0.01 | 0.615 | 576.75 | Assumes 75% initial fixture cost | #N/A | Assumes same labor time | 1.6 | 98.4 | 4750.2 |  | 8 | 0 | 1 | 1 | 91 | 5278 |  |  | 0.9 | 4750.2
759-1 | LED | Lowbay Lensed (Lin Ind - repl MH) | LED | 1 | 1 | 1 | 10 |  |  | 0.01 |  |  | 0.01 |  |  | 4010 | 2.959 | 181.9785 |  |  |  | 0.01 | [5 empty] | 0 |  | 0 | 0 | 0.92 | 0.874 |  | 0 |  |  | 0.9 | 0
599 | CF | Direct/Indirect | Triple Lamp - 4 Pin | 186 | 42 | 4 | 12000 | NA |  | 121 | RS Means 2014 | 2651-13.50-5520 | 34.3 | see above | 1PHA8 | 5510 | 1 | 53.5 | 1800 | 0.2 | 10.68 | 0 | [5 empty] | 1890.6615 |  | 0 | 682.5 | 0.9 | 0.855 |  |  |  |  | 0.9 | 1890.6615
[31 empty] | NA | 1
Note: to add more fixture types, insert rows above dark grey line
Each fixture must have a unique fixture type code or fixture ID in the first column.
Note: ballast replacement hours from Means
are for retrofit conditions, since balasts are included
with the fixture and adding a replacement multiplier
would be redundant.
So hours are divided by the multiplier that will be added
as a cost adjustment in the final prototype estimate.
Note on AM10: Reid Hart: If override entry exists, it has priority, then Efficacy, then if neither, lumen per lamp & ballast factor based
These costs are for the selected fixtures from 90.1 Lighting Subcommittee that are included in the lighting space types in the selected building prototype models analyzed for the cost-effectiveness project. These costs include lamps, ballasts, installation, and lamp replacements. 90.1 does not require specific lighting equipment; selections are based on information from Lighting Subcommittee experts.

## Int Ltg LPD Space Types SO (hidden)
| IECC Cost Effectiveness - Interior Lighting Power Density - Fixture Costs per Square Foot for Each Space Type - Small Office | [18 empty] | SMALL OFFICE
Adjustment Factors for LPD
| Interior lighting costs by space type and fixture type IECC 2009, North Carolina Base Code, and IECC 2012 tables. | [18 empty] | 2009 | 1
| 90.1-07 and 2010 in Int Ltg LPD Space Types 90_1 (same for all prototypes). Values come from "Int Ltg Comp" worksheet in this workbook. | [18 empty] | N. Carolina | 0.89
[20 empty] | 2012 | 0.975
Interior Lighting Costs by Space Type, 2009
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33 | 34 | 35
| Space Type Lighting Descriptions and Cost Parameters | [14 empty] | New Construction Cost | [6 empty] | Lamp Replacement Cost | [6 empty] | Ballast Replacement Cost
IECC 2009 Lookup Values | 2009 Space Types | 90.1 Lighting Subcommittee Model Number | Space Type Lighting Power Allowance W/ft2 | Fixture ID Number | Fixture Type | Lamp Type1 | Lamp Wattage | Number of Lamps | Not Used | Fixture Watts | Lamp Life Hours | Quantity of Fixtures/ft2 | Fixture Watts/ft2 | not used | not used | Fixture Cost/ft2 | not used | not used | not used | Labor Cost $/ft2 | Not Used | Not Used | Lamp Cost $/ft2 | Not Used | Not Used | Not Used | Labor Cost/ft2 | Overhead and Profit, $/ft2 | Total $/ft2 | Ballast Life Hours | Ballast Cost, $/ft2 | Not Used | Not Used | Labor Cost/ft2 | Not Used | Not Used
Classroom/Lecture/Training | Classroom/Lecture/Training |  | 1.4
Classroom/Lecture/Training535 |  | 3.1 |  | 535 | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A | #N/A | 1.1518 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A |  |  | #N/A | #N/A |  |  | #N/A
Classroom/Lecture/Training537-2 |  | 3.1 |  | 537-2 | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A | #N/A | 0.24817 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A |  |  | #N/A | #N/A |  |  | #N/A
Classroom/Lecture/Training0 |  | 3.1 |  | 0 | NA | NA | 0 | 0 |  | 0 | 0 | 0 | 0 |  |  | 0 |  |  |  | 0 |  |  | 0 |  |  |  | 0 |  |  | 0 | 0 |  |  | 0
| Conference/Meeting/Multipurpose |  | 1.3
Conference/Meeting/Multipurpose535 |  | 31 |  | 535 | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A | #N/A | 0.66403 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A |  |  | #N/A | #N/A |  |  | #N/A
Conference/Meeting/Multipurpose537-1 |  | 31 |  | 537-1 | Linear WW Open | FL | 32 | 1 |  | 29 | 36000 | 0.013036 | 0.37804 |  |  | 1.3501 |  |  |  | 0.80171 |  |  | 0.04367 |  |  |  | 0.071264 |  |  | 50000 | 0.39108 |  |  | 0.80171
Conference/Meeting/Multipurpose511 |  | 31 |  | 511 | Downlight open - flood | PAR | 60 | 1 |  | 60 | 4200 | 0.0042988 | 0.25793 |  |  | 0.1594 |  |  |  | 0.26438 |  |  | 0.091909 |  |  |  | 0.01251 |  |  | 0 | 0 |  |  | 0
| Corridor/Transition |  | 0.5
Corridor/Transition530 |  | 2 |  | 530 | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A | #N/A | 0.28757 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A |  |  | #N/A | #N/A |  |  | #N/A
Corridor/Transition537-2 |  | 2 |  | 537-2 | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A | #N/A | 0.21243 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A |  |  | #N/A | #N/A |  |  | #N/A
Corridor/Transition0 |  | 2 |  | 0 | NA | NA | 0 | 0 |  | 0 | 0 | 0 | 0 |  |  | 0 |  |  |  | 0 |  |  | 0 |  |  |  | 0 |  |  | 0 | 0 |  |  | 0
| Dining Area |  | 0.9
Dining Area531 |  | 6 |  | 531 | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A | #N/A | 0.6903 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A |  |  | #N/A | #N/A |  |  | #N/A
Dining Area524 |  | 6 |  | 524 | indirect Wall Scounce | CF | 18 | 2 |  | 39 | 10000 | 0.0053769 | 0.2097 |  |  | 0.48215 |  |  |  | 0.33068 |  |  | 0.16884 |  |  |  | 0.031186 |  |  | 50000 | 0 |  |  | 0
Dining Area0 |  | 6
| Electrical/Mechanical |  | 1.5
Electrical/Mechanical538 |  | 4 |  | 538 | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A | #N/A | 1.5 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A |  |  | #N/A | #N/A |  |  | #N/A
Electrical/Mechanical0 |  | 4 |  | 0 | NA | NA | 0 | 0 |  | 0 | 0 | 0 | 0 |  |  | 0 |  |  |  | 0 |  |  | 0 |  |  |  | 0 |  |  | 0 | 0 |  |  | 0
Electrical/Mechanical0 |  | 4 |  | 0 | NA | NA | 0 | 0 |  | 0 | 0 | 0 | 0 |  |  | 0 |  |  |  | 0 |  |  | 0 |  |  |  | 0 |  |  | 0 | 0 |  |  | 0
| Food Preparation |  | 1.2
Food Preparation530 |  | 8 |  | 530 | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A | #N/A | 1.2 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A |  |  | #N/A | #N/A |  |  | #N/A
Food Preparation0 |  | 8 |  | 0 | NA | NA | 0 | 0 |  | 0 | 0 | 0 | 0 |  |  | 0 |  |  |  | 0 |  |  | 0 |  |  |  | 0 |  |  | 0 | 0 |  |  | 0
Food Preparation0 |  | 8 |  | 0 | NA | NA | 0 | 0 |  | 0 | 0 | 0 | 0 |  |  | 0 |  |  |  | 0 |  |  | 0 |  |  |  | 0 |  |  | 0 | 0 |  |  | 0
| Gymnasium/Fitness-Fitness Area |  | 0.9
Gymnasium/Fitness-Fitness Area535 |  | 126 |  | 535 | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A | #N/A | 0.9 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A |  |  | #N/A | #N/A |  |  | #N/A
Gymnasium/Fitness-Fitness Area0 |  | 126 |  | 0 | NA | NA | 0 | 0 |  | 0 | 0 | 0 | 0 |  |  | 0 |  |  |  | 0 |  |  | 0 |  |  |  | 0 |  |  | 0 | 0 |  |  | 0
Gymnasium/Fitness-Fitness Area0 |  | 126 |  | 0 | NA | NA | 0 | 0 |  | 0 | 0 | 0 | 0 |  |  | 0 |  |  |  | 0 |  |  | 0 |  |  |  | 0 |  |  | 0 | 0 |  |  | 0
| Highway Lodging Guest Rooms |  | 1.1
Highway Lodging Guest Rooms524 |  | 75.01 |  | 524 | indirect Wall Scounce | CF | 18 | 2 |  | 39 | 10000 | 0.0042947 | 0.16749 |  |  | 0.3851 |  |  |  | 0.26412 |  |  | 0.13485 |  |  |  | 0.024909 |  |  | 50000 | 0 |  |  | 0
Highway Lodging Guest Rooms520 |  | 75.01 |  | 520 | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A | #N/A | 0.93251 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A |  |  | #N/A | #N/A |  |  | #N/A
Highway Lodging Guest Rooms0 |  | 75.01 |  | 0 | NA | NA | 0 | 0 |  | 0 | 0 | 0 | 0 |  |  | 0 |  |  |  | 0 |  |  | 0 |  |  |  | 0 |  |  | 0 | 0 |  |  | 0
| Hospital - Laundry/Washing |  | 0.6
Hospital - Laundry-washing530 |  | 82 |  | 530 | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A | #N/A | 0.6 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A |  |  | #N/A | #N/A |  |  | #N/A
Hospital - Laundry-washing0 |  | 82 |  | 0 | NA | NA | 0 | 0 |  | 0 | 0 | 0 | 0 |  |  | 0 |  |  |  | 0 |  |  | 0 |  |  |  | 0 |  |  | 0 | 0 |  |  | 0
Hospital - Laundry-washing0 |  | 82 |  | 0 | NA | NA | 0 | 0 |  | 0 | 0 | 0 | 0 |  |  | 0 |  |  |  | 0 |  |  | 0 |  |  |  | 0 |  |  | 0 | 0 |  |  | 0
| Library |  | 1.2
Library535 |  | 19 |  | 535 | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A | #N/A | 0.61 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A |  |  | #N/A | #N/A |  |  | #N/A
Library520 |  | 19 |  | 520 | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A | #N/A | 0.26 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A |  |  | #N/A | #N/A |  |  | #N/A
Library529 |  | 19 |  | 529 | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A | #N/A | 0.32 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A |  |  | #N/A | #N/A |  |  | #N/A
| Lobby |  | 1.3
Lobby534-2 |  | 20.1 |  | 534-2 | Linear Wall Cove | FL | 32 | 1 |  | 29 | 36000 | 0.0089923 | 0.26078 |  |  | 3.4171 |  |  |  | 0.5204 |  |  | 0.030124 |  |  |  | 0.049158 |  |  | 50000 | 0.26977 |  |  | 0.55303
Lobby523 |  | 20.1 |  | 523 | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A | #N/A | 0.9503 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A |  |  | #N/A | #N/A |  |  | #N/A
Lobby521 |  | 20.1 |  | 521 | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A | #N/A | 0.088925 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A |  |  | #N/A | #N/A |  |  | #N/A
| Lobby - Hotel |  | 1.1 | [27 empty] | #N/A
Lobby - Hotel535 |  | 79 |  | 535 | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A | #N/A | 0.027528 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A |  |  | #N/A | #N/A |  |  | #N/A
Lobby - Hotel572 |  | 79 |  | 572 | Downlight open | TH | 75 | 1 |  | 75 | 850 | 0.012798 | 0.95987 |  |  | 0.35707 |  |  |  | 0.78709 |  |  | 0.27363 |  |  |  | 0.30076 |  |  | 0 | 0 |  |  | 0
Lobby - Hotel524 |  | 79 |  | 524 | indirect Wall Scounce | CF | 18 | 2 |  | 39 | 10000 | 0.0028873 | 0.1126 |  |  | 0.2589 |  |  |  | 0.17757 |  |  | 0.09066 |  |  |  | 0.016746 |  |  | 50000 | 0 |  |  | 0
| Lounge/Recreation - Break room |  | 1.2
Lounge/Recreation - Breakroom537-1 |  | 9 |  | 537-1 | Linear WW Open | FL | 32 | 1 |  | 29 | 36000 | 0.013041 | 0.37818 |  |  | 1.3506 |  |  |  | 0.802 |  |  | 0.043686 |  |  |  | 0.07129 |  |  | 50000 | 0.39122 |  |  | 0.802
Lounge/Recreation - Breakroom572 |  | 9 |  | 0 | NA | NA | 0 | 0 |  | 0 | 0 | 0 | 0 |  |  | 0 |  |  |  | 0 |  |  | 0 |  |  |  | 0 |  |  | 0 | 0 |  |  | 0
Lounge/Recreation - Breakroom521 |  | 9 |  | 521 | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A | #N/A | 0.82182 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A |  |  | #N/A | #N/A |  |  | #N/A
| Office-Enclosed |  | 1.1
Office-Enclosed535 |  | 25 |  | 535 | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A | #N/A | 0.77644 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A |  |  | #N/A | #N/A |  |  | #N/A
Office-Enclosed539 |  | 25 |  | 539 | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A | #N/A | 0.1228 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A |  |  | #N/A | #N/A |  |  | #N/A
Office-Enclosed537-2 |  | 25 |  | 537-2 | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A | #N/A | 0.20075 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A |  |  | #N/A | #N/A |  |  | #N/A
| Office - Open Plan (Including Other) |  | 1.1
Office - Open Plan (Including Other)535 |  | 27 |  | 535 | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A | #N/A | 0.88036 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A |  |  | #N/A | #N/A |  |  | #N/A
Office - Open Plan (Including Other)539 |  | 27 |  | 539 | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A | #N/A | 0.15664 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A |  |  | #N/A | #N/A |  |  | #N/A
Office - Open Plan (Including Other)524 |  | 27 |  | 524 | indirect Wall Scounce | CF | 18 | 2 |  | 39 | 10000 | 0.0016152 | 0.062993 |  |  | 0.14484 |  |  |  | 0.099336 |  |  | 0.050718 |  |  |  | 0.0093682 |  |  | 50000 | 0 |  |  | 0
| Restrooms |  | 0.9
Restrooms521 |  | 12 |  | 521 | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A | #N/A | 0.42464 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A |  |  | #N/A | #N/A |  |  | #N/A
Restrooms537-1 |  | 12 |  | 537-1 | Linear WW Open | FL | 32 | 1 |  | 29 | 36000 | 0.011753 | 0.34083 |  |  | 1.2172 |  |  |  | 0.7228 |  |  | 0.039372 |  |  |  | 0.06425 |  |  | 50000 | 0.35259 |  |  | 0.7228
Restrooms524 |  | 12 |  | 524 | indirect Wall Scounce | CF | 18 | 2 |  | 39 | 10000 | 0.0034493 | 0.13452 |  |  | 0.3093 |  |  |  | 0.21213 |  |  | 0.10831 |  |  |  | 0.020006 |  |  | 50000 | 0 |  |  | 0
| Retail - Sales Area |  | 1.7
Retail - Sales Area535 |  | 97 |  | 535 | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A | #N/A | 0.95948 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A |  |  | #N/A | #N/A |  |  | #N/A
Retail - Sales Area541 |  | 97 |  | 541 | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A | #N/A | 0.74052 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A |  |  | #N/A | #N/A |  |  | #N/A
Retail - Sales Area572 |  | 97 |  | 0 | NA | NA | 0 | 0 |  | 0 | 0 | 0 | 0 |  |  | 0 |  |  |  | 0 |  |  | 0 |  |  |  | 0 |  |  | 0 | 0 |  |  | 0
| Stairway |  | 0.6
Stairway530 |  | 11 |  | 530 | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A | #N/A | 0.6 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A |  |  | #N/A | #N/A |  |  | #N/A
Stairway0 |  | 11 |  | 0 | NA | NA | 0 | 0 |  | 0 | 0 | 0 | 0 |  |  | 0 |  |  |  | 0 |  |  | 0 |  |  |  | 0 |  |  | 0 | 0 |  |  | 0
Stairway0 |  | 11 |  | 0 | NA | NA | 0 | 0 |  | 0 | 0 | 0 | 0 |  |  | 0 |  |  |  | 0 |  |  | 0 |  |  |  | 0 |  |  | 0 | 0 |  |  | 0
| Storage |  | 0.8
Storage530 |  | 41 |  | 530 | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A | #N/A | 0.8 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A |  |  | #N/A | #N/A |  |  | #N/A
Storage553 |  | 41 |  | 0 | NA | NA | 0 | 0 |  | 0 | 0 | 0 | 0 |  |  | 0 |  |  |  | 0 |  |  | 0 |  |  |  | 0 |  |  | 0 | 0 |  |  | 0
Storage0 |  | 41 |  | 0 | NA | NA | 0 | 0 |  | 0 | 0 | 0 | 0 |  |  | 0 |  |  |  | 0 |  |  | 0 |  |  |  | 0 |  |  | 0 | 0 |  |  | 0
1 FL linear fluorescent, CF compact fluorescent, MH metal halide
Interior Lighting Costs by Space Type, North Carolina Base Code
| Space Type Lighting Descriptions and Cost Parameters | [14 empty] | New Construction Cost | [6 empty] | Lamp Replacement Cost | [6 empty] | Ballast Replacement Cost
North Carolina Base Code Lookup Values | 2009 Space Types | 90.1 Lighting Subcommittee Model Number | Space Type Lighting Power Allowance W/ft2 | Fixture ID Number | Fixture Type | Lamp Type1 | Lamp Wattage | Number of Lamps | Not Used | Fixture Watts | Lamp Life Hours | Quantity of Fixtures/ft2 | Fixture Watts/ft2 | not used | not used | Fixture Cost/ft2 | not used | not used | not used | Labor Cost $/ft2 | Not Used | Not Used | Lamp Cost $/ft2 | Not Used | Not Used | Not Used | Labor Cost/ft2 |  |  | Ballast Life Hours | Ballast Cost, $/ft2 | Not Used | Not Used | Labor Cost/ft2 | Not Used | Not Used
Classroom/Lecture/Training | Classroom/Lecture/Training |  | 1.246
Classroom/Lecture/Training535 |  | 3.1 |  | 535 | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A | #N/A | 1.0251 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A |  |  | #N/A | #N/A |  |  | #N/A
Classroom/Lecture/Training537-2 |  | 3.1 |  | 537-2 | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A | #N/A | 0.22088 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A |  |  | #N/A | #N/A |  |  | #N/A
Classroom/Lecture/Training0 |  | 3.1 |  | 0 | NA | NA | 0 | 0 |  | 0 | 0 | 0 | 0 |  |  | 0 |  |  |  | 0 |  |  | 0 |  |  |  | 0 |  |  | 0 | 0 |  |  | 0
| Conference/Meeting/Multipurpose |  | 1.157
Conference/Meeting/Multipurpose535 |  | 31 |  | 535 | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A | #N/A | 0.59099 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A |  |  | #N/A | #N/A |  |  | #N/A
Conference/Meeting/Multipurpose537-1 |  | 31 |  | 537-1 | Linear WW Open | FL | 32 | 1 |  | 29 | 36000 | 0.011602 | 0.33646 |  |  | 1.2016 |  |  |  | 0.71352 |  |  | 0.038866 |  |  |  | 0.063425 |  |  | 50000 | 0.34806 |  |  | 0.71352
Conference/Meeting/Multipurpose511 |  | 31 |  | 511 | Downlight open - flood | PAR | 60 | 1 |  | 60 | 4200 | 0.003826 | 0.22956 |  |  | 0.14187 |  |  |  | 0.2353 |  |  | 0.081799 |  |  |  | 0.011134 |  |  | 0 | 0 |  |  | 0
| Corridor/Transition |  | 0.445
Corridor/Transition530 |  | 2 |  | 530 | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A | #N/A | 0.25594 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A |  |  | #N/A | #N/A |  |  | #N/A
Corridor/Transition537-2 |  | 2 |  | 537-2 | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A | #N/A | 0.18906 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A |  |  | #N/A | #N/A |  |  | #N/A
Corridor/Transition0 |  | 2 |  | 0 | NA | NA | 0 | 0 |  | 0 | 0 | 0 | 0 |  |  | 0 |  |  |  | 0 |  |  | 0 |  |  |  | 0 |  |  | 0 | 0 |  |  | 0
| Dining Area |  | 0.801
Dining Area531 |  | 6 |  | 531 | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A | #N/A | 0.61437 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A |  |  | #N/A | #N/A |  |  | #N/A
Dining Area524 |  | 6 |  | 524 | indirect Wall Scounce | CF | 18 | 2 |  | 39 | 10000 | 0.0047855 | 0.18663 |  |  | 0.42911 |  |  |  | 0.29431 |  |  | 0.15026 |  |  |  | 0.027756 |  |  | 50000 | 0 |  |  | 0
Dining Area0 |  | 6
| Electrical/Mechanical |  | 1.335
Electrical/Mechanical538 |  | 4 |  | 538 | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A | #N/A | 1.335 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A |  |  | #N/A | #N/A |  |  | #N/A
Electrical/Mechanical0 |  | 4 |  | 0 | NA | NA | 0 | 0 |  | 0 | 0 | 0 | 0 |  |  | 0 |  |  |  | 0 |  |  | 0 |  |  |  | 0 |  |  | 0 | 0 |  |  | 0
Electrical/Mechanical0 |  | 4 |  | 0 | NA | NA | 0 | 0 |  | 0 | 0 | 0 | 0 |  |  | 0 |  |  |  | 0 |  |  | 0 |  |  |  | 0 |  |  | 0 | 0 |  |  | 0
| Food Preparation |  | 1.068
Food Preparation530 |  | 8 |  | 530 | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A | #N/A | 1.068 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A |  |  | #N/A | #N/A |  |  | #N/A
Food Preparation0 |  | 8 |  | 0 | NA | NA | 0 | 0 |  | 0 | 0 | 0 | 0 |  |  | 0 |  |  |  | 0 |  |  | 0 |  |  |  | 0 |  |  | 0 | 0 |  |  | 0
Food Preparation0 |  | 8 |  | 0 | NA | NA | 0 | 0 |  | 0 | 0 | 0 | 0 |  |  | 0 |  |  |  | 0 |  |  | 0 |  |  |  | 0 |  |  | 0 | 0 |  |  | 0
| Gymnasium/Fitness-Fitness Area |  | 0.801
Gymnasium/Fitness-Fitness Area535 |  | 126 |  | 535 | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A | #N/A | 0.801 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A |  |  | #N/A | #N/A |  |  | #N/A
Gymnasium/Fitness-Fitness Area0 |  | 126 |  | 0 | NA | NA | 0 | 0 |  | 0 | 0 | 0 | 0 |  |  | 0 |  |  |  | 0 |  |  | 0 |  |  |  | 0 |  |  | 0 | 0 |  |  | 0
Gymnasium/Fitness-Fitness Area0 |  | 126 |  | 0 | NA | NA | 0 | 0 |  | 0 | 0 | 0 | 0 |  |  | 0 |  |  |  | 0 |  |  | 0 |  |  |  | 0 |  |  | 0 | 0 |  |  | 0
| Highway Lodging Guest Rooms |  | 0.979
Highway Lodging Guest Rooms524 |  | 75.01 |  | 524 | indirect Wall Scounce | CF | 18 | 2 |  | 39 | 10000 | 0.0038222 | 0.14907 |  |  | 0.34274 |  |  |  | 0.23507 |  |  | 0.12002 |  |  |  | 0.022169 |  |  | 50000 | 0 |  |  | 0
Highway Lodging Guest Rooms520 |  | 75.01 |  | 520 | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A | #N/A | 0.82993 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A |  |  | #N/A | #N/A |  |  | #N/A
Highway Lodging Guest Rooms0 |  | 75.01 |  | 0 | NA | NA | 0 | 0 |  | 0 | 0 | 0 | 0 |  |  | 0 |  |  |  | 0 |  |  | 0 |  |  |  | 0 |  |  | 0 | 0 |  |  | 0
| Hospital - Laundry/Washing |  | 0.534
Hospital - Laundry-washing530 |  | 82 |  | 530 | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A | #N/A | 0.534 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A |  |  | #N/A | #N/A |  |  | #N/A
Hospital - Laundry-washing0 |  | 82 |  | 0 | NA | NA | 0 | 0 |  | 0 | 0 | 0 | 0 |  |  | 0 |  |  |  | 0 |  |  | 0 |  |  |  | 0 |  |  | 0 | 0 |  |  | 0
Hospital - Laundry-washing0 |  | 82 |  | 0 | NA | NA | 0 | 0 |  | 0 | 0 | 0 | 0 |  |  | 0 |  |  |  | 0 |  |  | 0 |  |  |  | 0 |  |  | 0 | 0 |  |  | 0
| Library |  | 1.068
Library535 |  | 19 |  | 535 | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A | #N/A | 0.5429 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A |  |  | #N/A | #N/A |  |  | #N/A
Library520 |  | 19 |  | 520 | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A | #N/A | 0.2314 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A |  |  | #N/A | #N/A |  |  | #N/A
Library529 |  | 19 |  | 529 | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A | #N/A | 0.2848 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A |  |  | #N/A | #N/A |  |  | #N/A
| Lobby |  | 1.157
Lobby534-2 |  | 20.1 |  | 534-2 | Linear Wall Cove | FL | 32 | 1 |  | 29 | 36000 | 0.0080031 | 0.23209 |  |  | 3.0412 |  |  |  | 0.46315 |  |  | 0.026811 |  |  |  | 0.043751 |  |  | 50000 | 0.24009 |  |  | 0.49219
Lobby523 |  | 20.1 |  | 523 | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A | #N/A | 0.84577 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A |  |  | #N/A | #N/A |  |  | #N/A
Lobby521 |  | 20.1 |  | 521 | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A | #N/A | 0.079143 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A |  |  | #N/A | #N/A |  |  | #N/A
| Lobby - Hotel |  | 0.979 | [27 empty] | #N/A
Lobby - Hotel535 |  | 79 |  | 535 | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A | #N/A | 0.0245 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A |  |  | #N/A | #N/A |  |  | #N/A
Lobby - Hotel572 |  | 79 |  | 572 | Downlight open | TH | 75 | 1 |  | 75 | 850 | 0.01139 | 0.85428 |  |  | 0.31779 |  |  |  | 0.70051 |  |  | 0.24353 |  |  |  | 0.26768 |  |  | 0 | 0 |  |  | 0
Lobby - Hotel524 |  | 79 |  | 524 | indirect Wall Scounce | CF | 18 | 2 |  | 39 | 10000 | 0.0025697 | 0.10022 |  |  | 0.23042 |  |  |  | 0.15804 |  |  | 0.080688 |  |  |  | 0.014904 |  |  | 50000 | 0 |  |  | 0
| Lounge/Recreation - Break room |  | 1.068
Lounge/Recreation - Breakroom537-1 |  | 9 |  | 537-1 | Linear WW Open | FL | 32 | 1 |  | 29 | 36000 | 0.011606 | 0.33658 |  |  | 1.202 |  |  |  | 0.71378 |  |  | 0.038881 |  |  |  | 0.063448 |  |  | 50000 | 0.34818 |  |  | 0.71378
Lounge/Recreation - Breakroom572 |  | 9 |  | 0 | NA | NA | 0 | 0 |  | 0 | 0 | 0 | 0 |  |  | 0 |  |  |  | 0 |  |  | 0 |  |  |  | 0 |  |  | 0 | 0 |  |  | 0
Lounge/Recreation - Breakroom521 |  | 9 |  | 521 | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A | #N/A | 0.73142 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A |  |  | #N/A | #N/A |  |  | #N/A
| Office-Enclosed |  | 0.979
Office-Enclosed535 |  | 25 |  | 535 | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A | #N/A | 0.69103 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A |  |  | #N/A | #N/A |  |  | #N/A
Office-Enclosed539 |  | 25 |  | 539 | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A | #N/A | 0.1093 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A |  |  | #N/A | #N/A |  |  | #N/A
Office-Enclosed537-2 |  | 25 |  | 537-2 | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A | #N/A | 0.17867 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A |  |  | #N/A | #N/A |  |  | #N/A
| Office - Open Plan (Including Other) |  | 0.979
Office - Open Plan (Including Other)535 |  | 27 |  | 535 | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A | #N/A | 0.78352 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A |  |  | #N/A | #N/A |  |  | #N/A
Office - Open Plan (Including Other)539 |  | 27 |  | 539 | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A | #N/A | 0.13941 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A |  |  | #N/A | #N/A |  |  | #N/A
Office - Open Plan (Including Other)524 |  | 27 |  | 524 | indirect Wall Scounce | CF | 18 | 2 |  | 39 | 10000 | 0.0014375 | 0.056064 |  |  | 0.1289 |  |  |  | 0.088409 |  |  | 0.045139 |  |  |  | 0.0083377 |  |  | 50000 | 0 |  |  | 0
| Restrooms |  | 0.801
Restrooms521 |  | 12 |  | 521 | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A | #N/A | 0.37793 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A |  |  | #N/A | #N/A |  |  | #N/A
Restrooms537-1 |  | 12 |  | 537-1 | Linear WW Open | FL | 32 | 1 |  | 29 | 36000 | 0.01046 | 0.30334 |  |  | 1.0833 |  |  |  | 0.64329 |  |  | 0.035041 |  |  |  | 0.057182 |  |  | 50000 | 0.3138 |  |  | 0.64329
Restrooms524 |  | 12 |  | 524 | indirect Wall Scounce | CF | 18 | 2 |  | 39 | 10000 | 0.0030699 | 0.11973 |  |  | 0.27528 |  |  |  | 0.1888 |  |  | 0.096395 |  |  |  | 0.017805 |  |  | 50000 | 0 |  |  | 0
| Retail - Sales Area |  | 1.513
Retail - Sales Area535 |  | 97 |  | 535 | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A | #N/A | 0.85394 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A |  |  | #N/A | #N/A |  |  | #N/A
Retail - Sales Area541 |  | 97 |  | 541 | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A | #N/A | 0.65906 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A |  |  | #N/A | #N/A |  |  | #N/A
Retail - Sales Area572 |  | 97 |  | 0 | NA | NA | 0 | 0 |  | 0 | 0 | 0 | 0 |  |  | 0 |  |  |  | 0 |  |  | 0 |  |  |  | 0 |  |  | 0 | 0 |  |  | 0
| Stairway |  | 0.534
Stairway530 |  | 11 |  | 530 | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A | #N/A | 0.534 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A |  |  | #N/A | #N/A |  |  | #N/A
Stairway0 |  | 11 |  | 0 | NA | NA | 0 | 0 |  | 0 | 0 | 0 | 0 |  |  | 0 |  |  |  | 0 |  |  | 0 |  |  |  | 0 |  |  | 0 | 0 |  |  | 0
Stairway0 |  | 11 |  | 0 | NA | NA | 0 | 0 |  | 0 | 0 | 0 | 0 |  |  | 0 |  |  |  | 0 |  |  | 0 |  |  |  | 0 |  |  | 0 | 0 |  |  | 0
| Storage |  | 0.712
Storage530 |  | 41 |  | 530 | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A | #N/A | 0.712 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A |  |  | #N/A | #N/A |  |  | #N/A
Storage553 |  | 41 |  | 0 | NA | NA | 0 | 0 |  | 0 | 0 | 0 | 0 |  |  | 0 |  |  |  | 0 |  |  | 0 |  |  |  | 0 |  |  | 0 | 0 |  |  | 0
Storage0 |  | 41 |  | 0 | NA | NA | 0 | 0 |  | 0 | 0 | 0 | 0 |  |  | 0 |  |  |  | 0 |  |  | 0 |  |  |  | 0 |  |  | 0 | 0 |  |  | 0
1 FL linear fluorescent, CF compact fluorescent, MH metal halide
Interior Lighting Costs by Space Type, 2012
| Space Type Lighting Descriptions and Cost Parameters | [18 empty] | New Construction Cost |  |  | Lamp Replacement Cost | [6 empty] | Ballast Replacement Cost
IECC 2012 Lookup Values | 2012 Space Types | Model Number | Lighting Power Allowance, LPD, W/ft2 | Fixtures - ID Number | Fixture type | Lamp Type | Lamp Wattage | Number of Lamps |  | Fixture Watts | Lamp Life, Hours | Quantity of Fixtures/ft2 | Fixture Watts/ft2 |  |  | Fixture Cost only, $/ft2 | not used | not used | not used | Labor Cost $/ft2 |  |  | Lamp Cost, $/ft2 | Labor Crew Type |  |  | Labor Cost/ft2 |  |  | Ballast Life Hours | Ballast Cost, $/ft2 | Not Used | Not Used | Labor Cost/ft2
Classroom/Lecture/Training | Classroom/Lecture/Training |  | 1.209 | [26 empty] | 0 | #N/A |  |  | 0
Classroom/Lecture/Training535 |  | 3.1 |  | 535 | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A | #N/A | 0.90115 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A |  |  | #N/A | #N/A |  |  | #N/A
Classroom/Lecture/Training521 |  | 3.1 |  | 521 | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A | #N/A | 0.1502 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A |  |  | #N/A | #N/A |  |  | #N/A
Classroom/Lecture/Training0 |  | 3.1 |  | 0 | NA | NA | 0 | 0 |  | 0 | 0 | 0 | 0 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A |  |  | #N/A | 0 |  |  | 0
Classroom/Lecture/Training537-1 |  | 3.1 |  | 537-1 | Linear WW Open | FL | 32 | #N/A |  | #N/A | #N/A | #N/A | 0.15766 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A |  |  | #N/A | #N/A |  |  | #N/A
| Conference/Meeting/Multipurpose |  | 1.1992
Conference/Meeting/Multipurpose535 |  | 31 |  | 535 | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A | #N/A | 0.5892 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A |  |  | #N/A | #N/A |  |  | #N/A
Conference/Meeting/Multipurpose511 |  | 31 |  | 511 | Downlight open - flood | PAR | 60 | #N/A |  | #N/A | #N/A | #N/A | 0.4262 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A |  |  | #N/A | #N/A |  |  | #N/A
Conference/Meeting/Multipurpose0 |  | 31 |  | 0 | NA | NA | 0 | 0 |  | 0 | 0 | 0 | 0 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A |  |  | #N/A | 0 |  |  | 0
Conference/Meeting/Multipurpose527-1 |  | 31 |  | 527-1 | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A | #N/A | 0.18385 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A |  |  | #N/A | #N/A |  |  | #N/A
| Corridor/Transition |  | 0.6435
Corridor/Transition521 |  | 2 |  | 521 | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A | #N/A | 0.6435 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A |  |  | #N/A | #N/A |  |  | #N/A
Corridor/Transition0 |  | 2 |  | 0 | NA | NA | 0 | 0 |  | 0 | 0 | 0 | 0 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A |  |  | #N/A | 0 |  |  | 0
Corridor/Transition0 |  | 2 |  | 0 | NA | NA | 0 | 0 |  | 0 | 0 | 0 | 0 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A |  |  | #N/A | 0 |  |  | 0
Corridor/Transition527-2 |  | 2 |  | 0 | NA | NA | 0 | 0 |  | 0 | 0 | 0 | 9.818e-08 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A |  |  | #N/A | 0 |  |  | 0
| Dining Area |  | 0.63375
Dining Area535 |  | 6 |  | 535 | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A | #N/A | 0.23392 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A |  |  | #N/A | #N/A |  |  | #N/A
Dining Area521 |  | 6 |  | 521 | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A | #N/A | 0.11471 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A |  |  | #N/A | #N/A |  |  | #N/A
Dining Area0 |  | 6 |  | 0 | NA | NA | 0 | 0 |  | 0 | 0 | 0 | 0 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A |  |  | #N/A | 0 |  |  | 0
Dining Area537-1 |  | 6 |  | 537-1 | Linear WW Open | FL | 32 | #N/A |  | #N/A | #N/A | #N/A | 0.28512 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A |  |  | #N/A | #N/A |  |  | #N/A
| Electrical/Mechanical |  | 0.92625
Electrical/Mechanical538 |  | 4 |  | 538 | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A | #N/A | 0.92625 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A |  |  | #N/A | #N/A |  |  | #N/A
Electrical/Mechanical0 |  | 4 |  | 0 | NA | NA | 0 | 0 |  | 0 | 0 | 0 | 0 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A |  |  | #N/A | 0 |  |  | 0
Electrical/Mechanical0 |  | 4 |  | 0 | NA | NA | 0 | 0 |  | 0 | 0 | 0 | 0 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A |  |  | #N/A | 0 |  |  | 0
Electrical/Mechanical0 |  | 4 |  | 0 | NA | NA | 0 | 0 |  | 0 | 0 | 0 | 9.7327e-08 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A |  |  | #N/A | 0 |  |  | 0
| Food Preparation |  | 0.96525
Food Preparation530 |  | 8 |  | 530 | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A | #N/A | 0.96525 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A |  |  | #N/A | #N/A |  |  | #N/A
Food Preparation0 |  | 8 |  | 0 | NA | NA | 0 | 0 |  | 0 | 0 | 0 | 0 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A |  |  | #N/A | 0 |  |  | 0
Food Preparation0 |  | 8 |  | 0 | NA | NA | 0 | 0 |  | 0 | 0 | 0 | 0 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A |  |  | #N/A | 0 |  |  | 0
Food Preparation0 |  | 8 |  | 0 | NA | NA | 0 | 0 |  | 0 | 0 | 0 | 9.744e-08 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A |  |  | #N/A | 0 |  |  | 0
| Gymnasium/Fitness-Fitness Area |  | 0.702
Gymnasium/Fitness-Fitness Area535 |  | 126 |  | 535 | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A | #N/A | 0.702 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A |  |  | #N/A | #N/A |  |  | #N/A
Gymnasium/Fitness-Fitness Area0 |  | 126 |  | 0 | NA | NA | 0 | 0 |  | 0 | 0 | 0 | 0 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A |  |  | #N/A | 0 |  |  | 0
Gymnasium/Fitness-Fitness Area0 |  | 126 |  | 0 | NA | NA | 0 | 0 |  | 0 | 0 | 0 | 0 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A |  |  | #N/A | 0 |  |  | 0
Gymnasium/Fitness-Fitness Area0 |  | 126 |  | 0 | NA | NA | 0 | 0 |  | 0 | 0 | 0 | 9.708e-08 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A |  |  | #N/A | 0 |  |  | 0
| Highway Lodging Guest Rooms |  | 0.73125
Highway Lodging Guest Rooms529 |  | 75.01 |  | 529 | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A | #N/A | 0.41332 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A |  |  | #N/A | #N/A |  |  | #N/A
Highway Lodging Guest Rooms520 |  | 75.01 |  | 520 | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A | #N/A | 0.31792 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A |  |  | #N/A | #N/A |  |  | #N/A
Highway Lodging Guest Rooms0 |  | 75.01 |  | 0 | NA | NA | 0 | 0 |  | 0 | 0 | 0 | 0 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A |  |  | #N/A | 0 |  |  | 0
Highway Lodging Guest Rooms0 |  | 75.01 |  | 0 | NA | NA | 0 | 0 |  | 0 | 0 | 0 | 9.7184e-08 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A |  |  | #N/A | 0 |  |  | 0
| Hospital - Laundry/Washing |  | 0.585
Hospital - Laundry-washing530 |  | 82 |  | 530 | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A | #N/A | 0.585 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A |  |  | #N/A | #N/A |  |  | #N/A
Hospital - Laundry-washing0 |  | 82 |  | 0 | NA | NA | 0 | 0 |  | 0 | 0 | 0 | 0 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A |  |  | #N/A | 0 |  |  | 0
Hospital - Laundry-washing0 |  | 82 |  | 0 | NA | NA | 0 | 0 |  | 0 | 0 | 0 | 0 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A |  |  | #N/A | 0 |  |  | 0
Hospital - Laundry-washing0 |  | 82 |  | 0 | NA | NA | 0 | 0 |  | 0 | 0 | 0 | 9.8248e-08 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A |  |  | #N/A | 0 |  |  | 0
| Library |  | 0.90675
Library535 |  | 19 |  | 535 | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A | #N/A | 0.38295 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A |  |  | #N/A | #N/A |  |  | #N/A
Library520 |  | 19 |  | 520 | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A | #N/A | 0.5238 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A |  |  | #N/A | #N/A |  |  | #N/A
Library0 |  | 19 |  | 0 | NA | NA | 0 | 0 |  | 0 | 0 | 0 | 0 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A |  |  | #N/A | 0 |  |  | 0
Library0 |  | 19 |  | 0 | NA | NA | 0 | 0 |  | 0 | 0 | 0 | 9.7376e-08 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A |  |  | #N/A | 0 |  |  | 0
| Lounge/Recreation - Break room |  | 0.71175
Lounge/Recreation - Breakroom521 |  | 9 |  | 521 | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A | #N/A | 0.4242 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A |  |  | #N/A | #N/A |  |  | #N/A
Lounge/Recreation - Breakroom0 |  | 9 |  | 0 | NA | NA | 0 | 0 |  | 0 | 0 | 0 | 0 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A |  |  | #N/A | 0 |  |  | 0
Lounge/Recreation - Breakroom0 |  | 9 |  | 0 | NA | NA | 0 | 0 |  | 0 | 0 | 0 | 0 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A |  |  | #N/A | 0 |  |  | 0
Lounge/Recreation - Breakroom527-2 |  | 9 |  | 527-2 | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A | #N/A | 0.28755 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A |  |  | #N/A | #N/A |  |  | #N/A
| Lobby |  | 0.8775
Lobby523 |  | 20.1 |  | 523 | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A | #N/A | 0.48944 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A |  |  | #N/A | #N/A |  |  | #N/A
Lobby521 |  | 20.1 |  | 521 | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A | #N/A | 0.23067 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A |  |  | #N/A | #N/A |  |  | #N/A
Lobby0 |  | 20.1 |  | 0 | NA | NA | 0 | 0 |  | 0 | 0 | 0 | 0 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A |  |  | #N/A | 0 |  |  | 0
Lobby534-2 |  | 20.1 |  | 534-2 | Linear Wall Cove | FL | 32 | #N/A |  | #N/A | #N/A | #N/A | 0.15739 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A |  |  | #N/A | #N/A |  |  | #N/A
| Office-Enclosed |  | 1.0822
Office-Enclosed531 |  | 25 |  | 531 | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A | #N/A | 0.65817 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A |  |  | #N/A | #N/A |  |  | #N/A
Office-Enclosed539 |  | 25 |  | 539 | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A | #N/A | 0.18158 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A |  |  | #N/A | #N/A |  |  | #N/A
Office-Enclosed0 |  | 25 |  | 0 | NA | NA | 0 | 0 |  | 0 | 0 | 0 | 0 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A |  |  | #N/A | 0 |  |  | 0
Office-Enclosed537-1 |  | 25 |  | 537-1 | Linear WW Open | FL | 32 | #N/A |  | #N/A | #N/A | #N/A | 0.2425 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A |  |  | #N/A | #N/A |  |  | #N/A
| Office - Open Plan (Including Other) |  | 0.9555
Office - Open Plan (Including Other)535 |  | 27 |  | 535 | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A | #N/A | 0.70389 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A |  |  | #N/A | #N/A |  |  | #N/A
Office - Open Plan (Including Other)539 |  | 27 |  | 539 | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A | #N/A | 0.094598 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A |  |  | #N/A | #N/A |  |  | #N/A
Office - Open Plan (Including Other)0 |  | 27 |  | 0 | NA | NA | 0 | 0 |  | 0 | 0 | 0 | 0 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A |  |  | #N/A | 0 |  |  | 0
Office - Open Plan (Including Other)537-1 |  | 27 |  | 537-1 | Linear WW Open | FL | 32 | #N/A |  | #N/A | #N/A | #N/A | 0.15701 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A |  |  | #N/A | #N/A |  |  | #N/A
| Restrooms |  | 0.9555
Restrooms604 |  | 12 |  | 604 | Wall Mounted Linear Direct/Indirect | FL | 32 | #N/A |  | #N/A | #N/A | #N/A | 0.28117 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A |  |  | #N/A | #N/A |  |  | #N/A
Restrooms520 |  | 12 |  | 520 | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A | #N/A | 0.43368 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A |  |  | #N/A | #N/A |  |  | #N/A
Restrooms0 |  | 12 |  | 0 | NA | NA | 0 | 0 |  | 0 | 0 | 0 | 0 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A |  |  | #N/A | 0 |  |  | 0
Restrooms534-2 |  | 12 |  | 534-2 | Linear Wall Cove | FL | 32 | #N/A |  | #N/A | #N/A | #N/A | 0.24065 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A |  |  | #N/A | #N/A |  |  | #N/A
| Retail - Sales Area |  | 1.638
Retail - Sales Area535 |  | 97 |  | 535 | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A | #N/A | 0.99219 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A |  |  | #N/A | #N/A |  |  | #N/A
Retail - Sales Area541 |  | 97 |  | 541 | #N/A |  | #N/A | #N/A |  | #N/A | #N/A | #N/A | 0.4914 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A |  |  | #N/A | #N/A |  |  | #N/A
Retail - Sales Area0 |  | 97 |  | 0 | NA | NA | 0 | 0 |  | 0 | 0 | 0 | 0 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A |  |  | #N/A | 0 |  |  | 0
Retail - Sales Area537-1 |  | 97 |  | 537-1 | Linear WW Open | FL | 32 | #N/A |  | #N/A | #N/A | #N/A | 0.15441 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A |  |  | #N/A | #N/A |  |  | #N/A
| Stairway |  | 0.67275
Stairway530 |  | 11 |  | 530 | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A | #N/A | 0.36296 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A |  |  | #N/A | #N/A |  |  | #N/A
Stairway602 |  | 11 |  | 602 | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A | #N/A | 0.30979 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A |  |  | #N/A | #N/A |  |  | #N/A
Stairway0 |  | 11 |  | 0 | NA | NA | 0 | 0 |  | 0 | 0 | 0 | 0 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A |  |  | #N/A | 0 |  |  | 0
Stairway0 |  | 11 |  | 0 | NA | NA | 0 | 0 |  | 0 | 0 | 0 | 9.743e-08 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A |  |  | #N/A | 0 |  |  | 0
| Storage |  | 0.61425
Storage538 |  | 41 |  | 538 | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A | #N/A | 0.61425 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A |  |  | #N/A | #N/A |  |  | #N/A
Storage0 |  | 41 |  | 0 | NA | NA | 0 | 0 |  | 0 | 0 | 0 | 0 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A |  |  | #N/A | 0 |  |  | 0
Storage0 |  | 41 |  | 0 | NA | NA | 0 | 0 |  | 0 | 0 | 0 | 0 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A |  |  | #N/A | 0 |  |  | 0
Storage0 |  | 41 |  | 0 | NA | NA | 0 | 0 |  | 0 | 0 | 0 | 9.6815e-08 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A |  |  | #N/A | 0 |  |  | 0
| Lobby - Hotel |  | 1.0335
Lobby - Hotel572 |  | 79 |  | 572 | Downlight open | TH | 75 | #N/A |  | #N/A | #N/A | #N/A | 0.87642 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A |  |  | #N/A | #N/A |  |  | #N/A
Lobby - Hotel0 |  | 79 |  | 0 | NA | NA | 0 | 0 |  | 0 | 0 | 0 | 0 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A |  |  | #N/A | 0 |  |  | 0
Lobby - Hotel0 |  | 79 |  | 0 | NA | NA | 0 | 0 |  | 0 | 0 | 0 | 0 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A |  |  | #N/A | 0 |  |  | 0
Lobby - Hotel527-1 |  | 79 |  | 527-1 | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A | #N/A | 0.15708 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A |  |  | #N/A | #N/A |  |  | #N/A
1 FL linear fluorescent, CF compact fluorescent, MH metal halide

## Int Ltg LPD Space Types LO (hidden)
| IECC Cost Effectiveness - Interior Lighting Power Density - Fixture Costs per Square Foot for Each Space Type - Large Office | [18 empty] | LARGE OFFICE
Adjustment Factors for LPD
| Interior lighting costs by space type and fixture type IECC 2009, North Carolina Base Code, and IECC 2012 tables. | [18 empty] | 2009 | 1
| 90.1-07 and 2010 in Int Ltg LPD Space Types 90_1 (same for all prototypes). Values come from "Int Ltg Comp" worksheet in this workbook. | [18 empty] | N. Carolina | 0.89
[20 empty] | 2012 | 0.992
Interior Lighting Costs by Space Type, 2009
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33 | 34 | 35
| Space Type Lighting Descriptions and Cost Parameters | [14 empty] | New Construction Cost | [6 empty] | Lamp Replacement Cost | [6 empty] | Ballast Replacement Cost
IECC 2009 Lookup Values | 2009 Space Types | 90.1 Lighting Subcommittee Model Number | Space Type Lighting Power Allowance W/ft2 | Fixture ID Number | Fixture Type | Lamp Type1 | Lamp Wattage | Number of Lamps | Not Used | Fixture Watts | Lamp Life Hours | Quantity of Fixtures/ft2 | Fixture Watts/ft2 | not used | not used | Fixture Cost/ft2 | not used | not used | not used | Labor Cost $/ft2 | Not Used | Not Used | Lamp Cost $/ft2 | Not Used | Not Used | Not Used | Labor Cost/ft2 | Not Used, $/ft2 | Total $/ft2 | Ballast Life Hours | Ballast Cost, $/ft2 | Not Used | Not Used | Labor Cost/ft2 | Not Used | Not Used
Classroom/Lecture/Training | Classroom/Lecture/Training |  | 1.4
Classroom/Lecture/Training535 |  | 3.1 |  | 535 | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A | #N/A | 1.1518 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A |  | #N/A | #N/A | #N/A |  |  | #N/A
Classroom/Lecture/Training537-2 |  | 3.1 |  | 537-2 | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A | #N/A | 0.24817 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A |  | #N/A | #N/A | #N/A |  |  | #N/A
Classroom/Lecture/Training0 |  | 3.1 |  | 0 | NA | NA | 0 | 0 |  | 0 | 0 | 0 | 0 |  |  | 0 |  |  |  | 0 |  |  | 0 |  |  |  | 0 |  | 0 | 0 | 0 |  |  | 0
| Conference/Meeting/Multipurpose |  | 1.3
Conference/Meeting/Multipurpose535 |  | 31 |  | 535 | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A | #N/A | 0.66403 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A |  | #N/A | #N/A | #N/A |  |  | #N/A
Conference/Meeting/Multipurpose537-1 |  | 31 |  | 537-1 | Linear WW Open | FL | 32 | 1 |  | 29 | 36000 | 0.013036 | 0.37804 |  |  | 1.3501 |  |  |  | 0.80171 |  |  | 0.04367 |  |  |  | 0.071264 |  | 0.11493 | 50000 | 0.39108 |  |  | 0.80171
Conference/Meeting/Multipurpose511 |  | 31 |  | 511 | Downlight open - flood | PAR | 60 | 1 |  | 60 | 4200 | 0.0042988 | 0.25793 |  |  | 0.1594 |  |  |  | 0.26438 |  |  | 0.091909 |  |  |  | 0.01251 |  | 0.10442 | 0 | 0 |  |  | 0
| Corridor/Transition |  | 0.5
Corridor/Transition530 |  | 2 |  | 530 | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A | #N/A | 0.28757 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A |  | #N/A | #N/A | #N/A |  |  | #N/A
Corridor/Transition537-2 |  | 2 |  | 537-2 | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A | #N/A | 0.21243 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A |  | #N/A | #N/A | #N/A |  |  | #N/A
Corridor/Transition0 |  | 2 |  | 0 | NA | NA | 0 | 0 |  | 0 | 0 | 0 | 0 |  |  | 0 |  |  |  | 0 |  |  | 0 |  |  |  | 0 |  | 0 | 0 | 0 |  |  | 0
| Dining Area |  | 0.9
Dining Area531 |  | 6 |  | 531 | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A | #N/A | 0.6903 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A |  | #N/A | #N/A | #N/A |  |  | #N/A
Dining Area524 |  | 6 |  | 524 | indirect Wall Scounce | CF | 18 | 2 |  | 39 | 10000 | 0.0053769 | 0.2097 |  |  | 0.48215 |  |  |  | 0.33068 |  |  | 0.16884 |  |  |  | 0.031186 |  | 0.20002 | 50000 | 0 |  |  | 0
Dining Area0 |  | 6
| Electrical/Mechanical |  | 1.5
Electrical/Mechanical538 |  | 4 |  | 538 | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A | #N/A | 1.5 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A |  | #N/A | #N/A | #N/A |  |  | #N/A
Electrical/Mechanical0 |  | 4 |  | 0 | NA | NA | 0 | 0 |  | 0 | 0 | 0 | 0 |  |  | 0 |  |  |  | 0 |  |  | 0 |  |  |  | 0 |  | 0 | 0 | 0 |  |  | 0
Electrical/Mechanical0 |  | 4 |  | 0 | NA | NA | 0 | 0 |  | 0 | 0 | 0 | 0 |  |  | 0 |  |  |  | 0 |  |  | 0 |  |  |  | 0 |  | 0 | 0 | 0 |  |  | 0
| Food Preparation |  | 1.2
Food Preparation530 |  | 8 |  | 530 | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A | #N/A | 1.2 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A |  | #N/A | #N/A | #N/A |  |  | #N/A
Food Preparation0 |  | 8 |  | 0 | NA | NA | 0 | 0 |  | 0 | 0 | 0 | 0 |  |  | 0 |  |  |  | 0 |  |  | 0 |  |  |  | 0 |  | 0 | 0 | 0 |  |  | 0
Food Preparation0 |  | 8 |  | 0 | NA | NA | 0 | 0 |  | 0 | 0 | 0 | 0 |  |  | 0 |  |  |  | 0 |  |  | 0 |  |  |  | 0 |  | 0 | 0 | 0 |  |  | 0
| Gymnasium/Fitness-Fitness Area |  | 0.9
Gymnasium/Fitness-Fitness Area535 |  | 126 |  | 535 | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A | #N/A | 0.9 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A |  | #N/A | #N/A | #N/A |  |  | #N/A
Gymnasium/Fitness-Fitness Area0 |  | 126 |  | 0 | NA | NA | 0 | 0 |  | 0 | 0 | 0 | 0 |  |  | 0 |  |  |  | 0 |  |  | 0 |  |  |  | 0 |  | 0 | 0 | 0 |  |  | 0
Gymnasium/Fitness-Fitness Area0 |  | 126 |  | 0 | NA | NA | 0 | 0 |  | 0 | 0 | 0 | 0 |  |  | 0 |  |  |  | 0 |  |  | 0 |  |  |  | 0 |  | 0 | 0 | 0 |  |  | 0
| Highway Lodging Guest Rooms |  | 1.1
Highway Lodging Guest Rooms524 |  | 75.01 |  | 524 | indirect Wall Scounce | CF | 18 | 2 |  | 39 | 10000 | 0.0042947 | 0.16749 |  |  | 0.3851 |  |  |  | 0.26412 |  |  | 0.13485 |  |  |  | 0.024909 |  | 0.15976 | 50000 | 0 |  |  | 0
Highway Lodging Guest Rooms520 |  | 75.01 |  | 520 | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A | #N/A | 0.93251 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A |  | #N/A | #N/A | #N/A |  |  | #N/A
Highway Lodging Guest Rooms0 |  | 75.01 |  | 0 | NA | NA | 0 | 0 |  | 0 | 0 | 0 | 0 |  |  | 0 |  |  |  | 0 |  |  | 0 |  |  |  | 0 |  | 0 | 0 | 0 |  |  | 0
| Hospital - Laundry/Washing |  | 0.6
Hospital - Laundry-washing530 |  | 82 |  | 530 | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A | #N/A | 0.6 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A |  | #N/A | #N/A | #N/A |  |  | #N/A
Hospital - Laundry-washing0 |  | 82 |  | 0 | NA | NA | 0 | 0 |  | 0 | 0 | 0 | 0 |  |  | 0 |  |  |  | 0 |  |  | 0 |  |  |  | 0 |  | 0 | 0 | 0 |  |  | 0
Hospital - Laundry-washing0 |  | 82 |  | 0 | NA | NA | 0 | 0 |  | 0 | 0 | 0 | 0 |  |  | 0 |  |  |  | 0 |  |  | 0 |  |  |  | 0 |  | 0 | 0 | 0 |  |  | 0
| Library |  | 1.2
Library535 |  | 19 |  | 535 | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A | #N/A | 0.61 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A |  | #N/A | #N/A | #N/A |  |  | #N/A
Library520 |  | 19 |  | 520 | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A | #N/A | 0.26 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A |  | #N/A | #N/A | #N/A |  |  | #N/A
Library529 |  | 19 |  | 529 | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A | #N/A | 0.32 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A |  | #N/A | #N/A | #N/A |  |  | #N/A
| Lobby |  | 1.3
Lobby534-2 |  | 20.1 |  | 534-2 | Linear Wall Cove | FL | 32 | 1 |  | 29 | 36000 | 0.0089923 | 0.26078 |  |  | 3.4171 |  |  |  | 0.5204 |  |  | 0.030124 |  |  |  | 0.049158 |  | 0.079283 | 50000 | 0.26977 |  |  | 0.55303
Lobby523 |  | 20.1 |  | 523 | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A | #N/A | 0.9503 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A |  | #N/A | #N/A | #N/A |  |  | #N/A
Lobby521 |  | 20.1 |  | 521 | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A | #N/A | 0.088925 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A |  | #N/A | #N/A | #N/A |  |  | #N/A
| Lobby - Hotel |  | 1.1 | [27 empty] | #N/A
Lobby - Hotel535 |  | 79 |  | 535 | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A | #N/A | 0.027528 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A |  | #N/A | #N/A | #N/A |  |  | #N/A
Lobby - Hotel572 |  | 79 |  | 572 | Downlight open | TH | 75 | 1 |  | 75 | 850 | 0.012798 | 0.95987 |  |  | 0.35707 |  |  |  | 0.78709 |  |  | 0.27363 |  |  |  | 0.30076 |  | 0.57439 | 0 | 0 |  |  | 0
Lobby - Hotel524 |  | 79 |  | 524 | indirect Wall Scounce | CF | 18 | 2 |  | 39 | 10000 | 0.0028873 | 0.1126 |  |  | 0.2589 |  |  |  | 0.17757 |  |  | 0.09066 |  |  |  | 0.016746 |  | 0.10741 | 50000 | 0 |  |  | 0
| Lounge/Recreation - Break room |  | 1.2
Lounge/Recreation - Breakroom537-1 |  | 9 |  | 537-1 | Linear WW Open | FL | 32 | 1 |  | 29 | 36000 | 0.013041 | 0.37818 |  |  | 1.3506 |  |  |  | 0.802 |  |  | 0.043686 |  |  |  | 0.07129 |  | 0.11498 | 50000 | 0.39122 |  |  | 0.802
Lounge/Recreation - Breakroom572 |  | 9 |  | 0 | NA | NA | 0 | 0 |  | 0 | 0 | 0 | 0 |  |  | 0 |  |  |  | 0 |  |  | 0 |  |  |  | 0 |  | 0 | 0 | 0 |  |  | 0
Lounge/Recreation - Breakroom521 |  | 9 |  | 521 | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A | #N/A | 0.82182 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A |  | #N/A | #N/A | #N/A |  |  | #N/A
| Office-Enclosed |  | 1.1
Office-Enclosed535 |  | 25 |  | 535 | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A | #N/A | 0.77644 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A |  | #N/A | #N/A | #N/A |  |  | #N/A
Office-Enclosed539 |  | 25 |  | 539 | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A | #N/A | 0.1228 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A |  | #N/A | #N/A | #N/A |  |  | #N/A
Office-Enclosed537-2 |  | 25 |  | 537-2 | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A | #N/A | 0.20075 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A |  | #N/A | #N/A | #N/A |  |  | #N/A
| Office - Open Plan (Including Other) |  | 1.1
Office - Open Plan (Including Other)535 |  | 27 |  | 535 | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A | #N/A | 0.88036 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A |  | #N/A | #N/A | #N/A |  |  | #N/A
Office - Open Plan (Including Other)539 |  | 27 |  | 539 | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A | #N/A | 0.15664 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A |  | #N/A | #N/A | #N/A |  |  | #N/A
Office - Open Plan (Including Other)524 |  | 27 |  | 524 | indirect Wall Scounce | CF | 18 | 2 |  | 39 | 10000 | 0.0016152 | 0.062993 |  |  | 0.14484 |  |  |  | 0.099336 |  |  | 0.050718 |  |  |  | 0.0093682 |  | 0.060086 | 50000 | 0 |  |  | 0
| Restrooms |  | 0.9
Restrooms521 |  | 12 |  | 521 | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A | #N/A | 0.42464 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A |  | #N/A | #N/A | #N/A |  |  | #N/A
Restrooms537-1 |  | 12 |  | 537-1 | Linear WW Open | FL | 32 | 1 |  | 29 | 36000 | 0.011753 | 0.34083 |  |  | 1.2172 |  |  |  | 0.7228 |  |  | 0.039372 |  |  |  | 0.06425 |  | 0.10362 | 50000 | 0.35259 |  |  | 0.7228
Restrooms524 |  | 12 |  | 524 | indirect Wall Scounce | CF | 18 | 2 |  | 39 | 10000 | 0.0034493 | 0.13452 |  |  | 0.3093 |  |  |  | 0.21213 |  |  | 0.10831 |  |  |  | 0.020006 |  | 0.12832 | 50000 | 0 |  |  | 0
| Retail - Sales Area |  | 1.7
Retail - Sales Area535 |  | 97 |  | 535 | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A | #N/A | 0.95948 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A |  | #N/A | #N/A | #N/A |  |  | #N/A
Retail - Sales Area541 |  | 97 |  | 541 | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A | #N/A | 0.74052 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A |  | #N/A | #N/A | #N/A |  |  | #N/A
Retail - Sales Area572 |  | 97 |  | 0 | NA | NA | 0 | 0 |  | 0 | 0 | 0 | 0 |  |  | 0 |  |  |  | 0 |  |  | 0 |  |  |  | 0 |  | 0 | 0 | 0 |  |  | 0
| Stairway |  | 0.6
Stairway530 |  | 11 |  | 530 | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A | #N/A | 0.6 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A |  | #N/A | #N/A | #N/A |  |  | #N/A
Stairway0 |  | 11 |  | 0 | NA | NA | 0 | 0 |  | 0 | 0 | 0 | 0 |  |  | 0 |  |  |  | 0 |  |  | 0 |  |  |  | 0 |  | 0 | 0 | 0 |  |  | 0
Stairway0 |  | 11 |  | 0 | NA | NA | 0 | 0 |  | 0 | 0 | 0 | 0 |  |  | 0 |  |  |  | 0 |  |  | 0 |  |  |  | 0 |  | 0 | 0 | 0 |  |  | 0
| Storage |  | 0.8
Storage530 |  | 41 |  | 530 | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A | #N/A | 0.8 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A |  | #N/A | #N/A | #N/A |  |  | #N/A
Storage553 |  | 41 |  | 0 | NA | NA | 0 | 0 |  | 0 | 0 | 0 | 0 |  |  | 0 |  |  |  | 0 |  |  | 0 |  |  |  | 0 |  | 0 | 0 | 0 |  |  | 0
Storage0 |  | 41 |  | 0 | NA | NA | 0 | 0 |  | 0 | 0 | 0 | 0 |  |  | 0 |  |  |  | 0 |  |  | 0 |  |  |  | 0 |  | 0 | 0 | 0 |  |  | 0
1 FL linear fluorescent, CF compact fluorescent, MH metal halide
Interior Lighting Costs by Space Type, North Carolina Base Code
| Space Type Lighting Descriptions and Cost Parameters | [14 empty] | New Construction Cost | [6 empty] | Lamp Replacement Cost | [6 empty] | Ballast Replacement Cost
North Carolina Base Code Lookup Values | 2009 Space Types | 90.1 Lighting Subcommittee Model Number | Space Type Lighting Power Allowance W/ft2 | Fixture ID Number | Fixture Type | Lamp Type1 | Lamp Wattage | Number of Lamps | Not Used | Fixture Watts | Lamp Life Hours | Quantity of Fixtures/ft2 | Fixture Watts/ft2 | not used | not used | Fixture Cost/ft2 | not used | not used | not used | Labor Cost $/ft2 | Not Used | Not Used | Lamp Cost $/ft2 | Not Used | Not Used | Not Used | Labor Cost/ft2 | Overhead and Profit, $/ft2 | Total $/ft2 | Ballast Life Hours | Ballast Cost, $/ft2 | Not Used | Not Used | Labor Cost/ft2 | Not Used | Not Used
Classroom/Lecture/Training | Classroom/Lecture/Training |  | 1.246
Classroom/Lecture/Training535 |  | 3.1 |  | 535 | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A | #N/A | 1.0251 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A |  | #N/A | #N/A | #N/A |  |  | #N/A
Classroom/Lecture/Training537-2 |  | 3.1 |  | 537-2 | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A | #N/A | 0.22088 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A |  | #N/A | #N/A | #N/A |  |  | #N/A
Classroom/Lecture/Training0 |  | 3.1 |  | 0 | NA | NA | 0 | 0 |  | 0 | 0 | 0 | 0 |  |  | 0 |  |  |  | 0 |  |  | 0 |  |  |  | 0 |  | 0 | 0 | 0 |  |  | 0
| Conference/Meeting/Multipurpose |  | 1.157
Conference/Meeting/Multipurpose535 |  | 31 |  | 535 | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A | #N/A | 0.59099 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A |  | #N/A | #N/A | #N/A |  |  | #N/A
Conference/Meeting/Multipurpose537-1 |  | 31 |  | 537-1 | Linear WW Open | FL | 32 | 1 |  | 29 | 36000 | 0.011602 | 0.33646 |  |  | 1.2016 |  |  |  | 0.71352 |  |  | 0.038866 |  |  |  | 0.063425 |  | 0.10229 | 50000 | 0.34806 |  |  | 0.71352
Conference/Meeting/Multipurpose511 |  | 31 |  | 511 | Downlight open - flood | PAR | 60 | 1 |  | 60 | 4200 | 0.003826 | 0.22956 |  |  | 0.14187 |  |  |  | 0.2353 |  |  | 0.081799 |  |  |  | 0.011134 |  | 0.092933 | 0 | 0 |  |  | 0
| Corridor/Transition |  | 0.445
Corridor/Transition530 |  | 2 |  | 530 | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A | #N/A | 0.25594 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A |  | #N/A | #N/A | #N/A |  |  | #N/A
Corridor/Transition537-2 |  | 2 |  | 537-2 | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A | #N/A | 0.18906 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A |  | #N/A | #N/A | #N/A |  |  | #N/A
Corridor/Transition0 |  | 2 |  | 0 | NA | NA | 0 | 0 |  | 0 | 0 | 0 | 0 |  |  | 0 |  |  |  | 0 |  |  | 0 |  |  |  | 0 |  | 0 | 0 | 0 |  |  | 0
| Dining Area |  | 0.801
Dining Area531 |  | 6 |  | 531 | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A | #N/A | 0.61437 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A |  | #N/A | #N/A | #N/A |  |  | #N/A
Dining Area524 |  | 6 |  | 524 | indirect Wall Scounce | CF | 18 | 2 |  | 39 | 10000 | 0.0047855 | 0.18663 |  |  | 0.42911 |  |  |  | 0.29431 |  |  | 0.15026 |  |  |  | 0.027756 |  | 0.17802 | 50000 | 0 |  |  | 0
Dining Area0 |  | 6
| Electrical/Mechanical |  | 1.335
Electrical/Mechanical538 |  | 4 |  | 538 | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A | #N/A | 1.335 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A |  | #N/A | #N/A | #N/A |  |  | #N/A
Electrical/Mechanical0 |  | 4 |  | 0 | NA | NA | 0 | 0 |  | 0 | 0 | 0 | 0 |  |  | 0 |  |  |  | 0 |  |  | 0 |  |  |  | 0 |  | 0 | 0 | 0 |  |  | 0
Electrical/Mechanical0 |  | 4 |  | 0 | NA | NA | 0 | 0 |  | 0 | 0 | 0 | 0 |  |  | 0 |  |  |  | 0 |  |  | 0 |  |  |  | 0 |  | 0 | 0 | 0 |  |  | 0
| Food Preparation |  | 1.068
Food Preparation530 |  | 8 |  | 530 | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A | #N/A | 1.068 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A |  | #N/A | #N/A | #N/A |  |  | #N/A
Food Preparation0 |  | 8 |  | 0 | NA | NA | 0 | 0 |  | 0 | 0 | 0 | 0 |  |  | 0 |  |  |  | 0 |  |  | 0 |  |  |  | 0 |  | 0 | 0 | 0 |  |  | 0
Food Preparation0 |  | 8 |  | 0 | NA | NA | 0 | 0 |  | 0 | 0 | 0 | 0 |  |  | 0 |  |  |  | 0 |  |  | 0 |  |  |  | 0 |  | 0 | 0 | 0 |  |  | 0
| Gymnasium/Fitness-Fitness Area |  | 0.801
Gymnasium/Fitness-Fitness Area535 |  | 126 |  | 535 | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A | #N/A | 0.801 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A |  | #N/A | #N/A | #N/A |  |  | #N/A
Gymnasium/Fitness-Fitness Area0 |  | 126 |  | 0 | NA | NA | 0 | 0 |  | 0 | 0 | 0 | 0 |  |  | 0 |  |  |  | 0 |  |  | 0 |  |  |  | 0 |  | 0 | 0 | 0 |  |  | 0
Gymnasium/Fitness-Fitness Area0 |  | 126 |  | 0 | NA | NA | 0 | 0 |  | 0 | 0 | 0 | 0 |  |  | 0 |  |  |  | 0 |  |  | 0 |  |  |  | 0 |  | 0 | 0 | 0 |  |  | 0
| Highway Lodging Guest Rooms |  | 0.979
Highway Lodging Guest Rooms524 |  | 75.01 |  | 524 | indirect Wall Scounce | CF | 18 | 2 |  | 39 | 10000 | 0.0038222 | 0.14907 |  |  | 0.34274 |  |  |  | 0.23507 |  |  | 0.12002 |  |  |  | 0.022169 |  | 0.14219 | 50000 | 0 |  |  | 0
Highway Lodging Guest Rooms520 |  | 75.01 |  | 520 | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A | #N/A | 0.82993 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A |  | #N/A | #N/A | #N/A |  |  | #N/A
Highway Lodging Guest Rooms0 |  | 75.01 |  | 0 | NA | NA | 0 | 0 |  | 0 | 0 | 0 | 0 |  |  | 0 |  |  |  | 0 |  |  | 0 |  |  |  | 0 |  | 0 | 0 | 0 |  |  | 0
| Hospital - Laundry/Washing |  | 0.534
Hospital - Laundry-washing530 |  | 82 |  | 530 | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A | #N/A | 0.534 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A |  | #N/A | #N/A | #N/A |  |  | #N/A
Hospital - Laundry-washing0 |  | 82 |  | 0 | NA | NA | 0 | 0 |  | 0 | 0 | 0 | 0 |  |  | 0 |  |  |  | 0 |  |  | 0 |  |  |  | 0 |  | 0 | 0 | 0 |  |  | 0
Hospital - Laundry-washing0 |  | 82 |  | 0 | NA | NA | 0 | 0 |  | 0 | 0 | 0 | 0 |  |  | 0 |  |  |  | 0 |  |  | 0 |  |  |  | 0 |  | 0 | 0 | 0 |  |  | 0
| Library |  | 1.068
Library535 |  | 19 |  | 535 | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A | #N/A | 0.5429 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A |  | #N/A | #N/A | #N/A |  |  | #N/A
Library520 |  | 19 |  | 520 | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A | #N/A | 0.2314 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A |  | #N/A | #N/A | #N/A |  |  | #N/A
Library529 |  | 19 |  | 529 | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A | #N/A | 0.2848 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A |  | #N/A | #N/A | #N/A |  |  | #N/A
| Lobby |  | 1.157
Lobby534-2 |  | 20.1 |  | 534-2 | Linear Wall Cove | FL | 32 | 1 |  | 29 | 36000 | 0.0080031 | 0.23209 |  |  | 3.0412 |  |  |  | 0.46315 |  |  | 0.026811 |  |  |  | 0.043751 |  | 0.070562 | 50000 | 0.24009 |  |  | 0.49219
Lobby523 |  | 20.1 |  | 523 | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A | #N/A | 0.84577 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A |  | #N/A | #N/A | #N/A |  |  | #N/A
Lobby521 |  | 20.1 |  | 521 | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A | #N/A | 0.079143 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A |  | #N/A | #N/A | #N/A |  |  | #N/A
| Lobby - Hotel |  | 0.979 | [27 empty] | #N/A
Lobby - Hotel535 |  | 79 |  | 535 | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A | #N/A | 0.0245 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A |  | #N/A | #N/A | #N/A |  |  | #N/A
Lobby - Hotel572 |  | 79 |  | 572 | Downlight open | TH | 75 | 1 |  | 75 | 850 | 0.01139 | 0.85428 |  |  | 0.31779 |  |  |  | 0.70051 |  |  | 0.24353 |  |  |  | 0.26768 |  | 0.5112 | 0 | 0 |  |  | 0
Lobby - Hotel524 |  | 79 |  | 524 | indirect Wall Scounce | CF | 18 | 2 |  | 39 | 10000 | 0.0025697 | 0.10022 |  |  | 0.23042 |  |  |  | 0.15804 |  |  | 0.080688 |  |  |  | 0.014904 |  | 0.095592 | 50000 | 0 |  |  | 0
| Lounge/Recreation - Break room |  | 1.068
Lounge/Recreation - Breakroom537-1 |  | 9 |  | 537-1 | Linear WW Open | FL | 32 | 1 |  | 29 | 36000 | 0.011606 | 0.33658 |  |  | 1.202 |  |  |  | 0.71378 |  |  | 0.038881 |  |  |  | 0.063448 |  | 0.10233 | 50000 | 0.34818 |  |  | 0.71378
Lounge/Recreation - Breakroom572 |  | 9 |  | 0 | NA | NA | 0 | 0 |  | 0 | 0 | 0 | 0 |  |  | 0 |  |  |  | 0 |  |  | 0 |  |  |  | 0 |  | 0 | 0 | 0 |  |  | 0
Lounge/Recreation - Breakroom521 |  | 9 |  | 521 | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A | #N/A | 0.73142 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A |  | #N/A | #N/A | #N/A |  |  | #N/A
| Office-Enclosed |  | 0.979
Office-Enclosed535 |  | 25 |  | 535 | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A | #N/A | 0.69103 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A |  | #N/A | #N/A | #N/A |  |  | #N/A
Office-Enclosed539 |  | 25 |  | 539 | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A | #N/A | 0.1093 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A |  | #N/A | #N/A | #N/A |  |  | #N/A
Office-Enclosed537-2 |  | 25 |  | 537-2 | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A | #N/A | 0.17867 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A |  | #N/A | #N/A | #N/A |  |  | #N/A
| Office - Open Plan (Including Other) |  | 0.979
Office - Open Plan (Including Other)535 |  | 27 |  | 535 | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A | #N/A | 0.78352 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A |  | #N/A | #N/A | #N/A |  |  | #N/A
Office - Open Plan (Including Other)539 |  | 27 |  | 539 | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A | #N/A | 0.13941 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A |  | #N/A | #N/A | #N/A |  |  | #N/A
Office - Open Plan (Including Other)524 |  | 27 |  | 524 | indirect Wall Scounce | CF | 18 | 2 |  | 39 | 10000 | 0.0014375 | 0.056064 |  |  | 0.1289 |  |  |  | 0.088409 |  |  | 0.045139 |  |  |  | 0.0083377 |  | 0.053476 | 50000 | 0 |  |  | 0
| Restrooms |  | 0.801
Restrooms521 |  | 12 |  | 521 | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A | #N/A | 0.37793 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A |  | #N/A | #N/A | #N/A |  |  | #N/A
Restrooms537-1 |  | 12 |  | 537-1 | Linear WW Open | FL | 32 | 1 |  | 29 | 36000 | 0.01046 | 0.30334 |  |  | 1.0833 |  |  |  | 0.64329 |  |  | 0.035041 |  |  |  | 0.057182 |  | 0.092223 | 50000 | 0.3138 |  |  | 0.64329
Restrooms524 |  | 12 |  | 524 | indirect Wall Scounce | CF | 18 | 2 |  | 39 | 10000 | 0.0030699 | 0.11973 |  |  | 0.27528 |  |  |  | 0.1888 |  |  | 0.096395 |  |  |  | 0.017805 |  | 0.1142 | 50000 | 0 |  |  | 0
| Retail - Sales Area |  | 1.513
Retail - Sales Area535 |  | 97 |  | 535 | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A | #N/A | 0.85394 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A |  | #N/A | #N/A | #N/A |  |  | #N/A
Retail - Sales Area541 |  | 97 |  | 541 | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A | #N/A | 0.65906 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A |  | #N/A | #N/A | #N/A |  |  | #N/A
Retail - Sales Area572 |  | 97 |  | 0 | NA | NA | 0 | 0 |  | 0 | 0 | 0 | 0 |  |  | 0 |  |  |  | 0 |  |  | 0 |  |  |  | 0 |  | 0 | 0 | 0 |  |  | 0
| Stairway |  | 0.534
Stairway530 |  | 11 |  | 530 | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A | #N/A | 0.534 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A |  | #N/A | #N/A | #N/A |  |  | #N/A
Stairway0 |  | 11 |  | 0 | NA | NA | 0 | 0 |  | 0 | 0 | 0 | 0 |  |  | 0 |  |  |  | 0 |  |  | 0 |  |  |  | 0 |  | 0 | 0 | 0 |  |  | 0
Stairway0 |  | 11 |  | 0 | NA | NA | 0 | 0 |  | 0 | 0 | 0 | 0 |  |  | 0 |  |  |  | 0 |  |  | 0 |  |  |  | 0 |  | 0 | 0 | 0 |  |  | 0
| Storage |  | 0.712
Storage530 |  | 41 |  | 530 | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A | #N/A | 0.712 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A |  | #N/A | #N/A | #N/A |  |  | #N/A
Storage553 |  | 41 |  | 0 | NA | NA | 0 | 0 |  | 0 | 0 | 0 | 0 |  |  | 0 |  |  |  | 0 |  |  | 0 |  |  |  | 0 |  | 0 | 0 | 0 |  |  | 0
Storage0 |  | 41 |  | 0 | NA | NA | 0 | 0 |  | 0 | 0 | 0 | 0 |  |  | 0 |  |  |  | 0 |  |  | 0 |  |  |  | 0 |  | 0 | 0 | 0 |  |  | 0
1 FL linear fluorescent, CF compact fluorescent, MH metal halide
Interior Lighting Costs by Space Type, 2012
| Space Type Lighting Descriptions and Cost Parameters | [18 empty] | New Construction Cost |  |  | Lamp Replacement Cost | [6 empty] | Ballast Replacement Cost
IECC 2012 Lookup Values | 2012 Space Types | Model Number | Lighting Power Allowance, LPD, W/ft2 | Fixtures - ID Number | Fixture type | Lamp Type | Lamp Wattage | Number of Lamps |  | Fixture Watts | Lamp Life, Hours | Quantity of Fixtures/ft2 | Fixture Watts/ft2 |  |  | Fixture Cost only, $/ft2 | not used | not used | not used | Labor Cost $/ft2 |  |  | Lamp Cost, $/ft2 | Labor Crew Type |  |  | Labor Cost/ft2 | Overhead and Profit, $/ft2 | Total $/ft2 | Ballast Life Hours | Ballast Cost, $/ft2 | Not Used | Not Used | Labor Cost/ft2
Classroom/Lecture/Training | Classroom/Lecture/Training |  | 1.2301 | [26 empty] | 0 | #N/A |  |  | 0
Classroom/Lecture/Training535 |  | 3.1 |  | 535 | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A | #N/A | 0.91686 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A | #NAME? | #N/A | #N/A | #N/A |  |  | #N/A
Classroom/Lecture/Training521 |  | 3.1 |  | 521 | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A | #N/A | 0.15281 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A | #NAME? | #N/A | #N/A | #N/A |  |  | #N/A
Classroom/Lecture/Training0 |  | 3.1 |  | 0 | NA | NA | 0 | 0 |  | 0 | 0 | 0 | 0 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A | #NAME? | #N/A | #N/A | 0 |  |  | 0
Classroom/Lecture/Training537-1 |  | 3.1 |  | 537-1 | Linear WW Open | FL | 32 | #N/A |  | #N/A | #N/A | #N/A | 0.16041 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A | #NAME? | #N/A | #N/A | #N/A |  |  | #N/A
| Conference/Meeting/Multipurpose |  | 1.2202
Conference/Meeting/Multipurpose535 |  | 31 |  | 535 | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A | #N/A | 0.59947 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A | #NAME? | #N/A | #N/A | #N/A |  |  | #N/A
Conference/Meeting/Multipurpose511 |  | 31 |  | 511 | Downlight open - flood | PAR | 60 | #N/A |  | #N/A | #N/A | #N/A | 0.43363 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A | #NAME? | #N/A | #N/A | #N/A |  |  | #N/A
Conference/Meeting/Multipurpose0 |  | 31 |  | 0 | NA | NA | 0 | 0 |  | 0 | 0 | 0 | 0 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A | #NAME? | #N/A | #N/A | 0 |  |  | 0
Conference/Meeting/Multipurpose527-1 |  | 31 |  | 527-1 | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A | #N/A | 0.18706 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A | #NAME? | #N/A | #N/A | #N/A |  |  | #N/A
| Corridor/Transition |  | 0.65472
Corridor/Transition521 |  | 2 |  | 521 | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A | #N/A | 0.65472 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A | #NAME? | #N/A | #N/A | #N/A |  |  | #N/A
Corridor/Transition0 |  | 2 |  | 0 | NA | NA | 0 | 0 |  | 0 | 0 | 0 | 0 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A | #NAME? | #N/A | #N/A | 0 |  |  | 0
Corridor/Transition0 |  | 2 |  | 0 | NA | NA | 0 | 0 |  | 0 | 0 | 0 | 0 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A | #NAME? | #N/A | #N/A | 0 |  |  | 0
Corridor/Transition527-2 |  | 2 |  | 0 | NA | NA | 0 | 0 |  | 0 | 0 | 0 | 9.9891e-08 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A | #NAME? | #N/A | #N/A | 0 |  |  | 0
| Dining Area |  | 0.6448
Dining Area535 |  | 6 |  | 535 | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A | #N/A | 0.238 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A | #NAME? | #N/A | #N/A | #N/A |  |  | #N/A
Dining Area521 |  | 6 |  | 521 | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A | #N/A | 0.11671 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A | #NAME? | #N/A | #N/A | #N/A |  |  | #N/A
Dining Area0 |  | 6 |  | 0 | NA | NA | 0 | 0 |  | 0 | 0 | 0 | 0 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A | #NAME? | #N/A | #N/A | 0 |  |  | 0
Dining Area537-1 |  | 6 |  | 537-1 | Linear WW Open | FL | 32 | #N/A |  | #N/A | #N/A | #N/A | 0.29009 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A | #NAME? | #N/A | #N/A | #N/A |  |  | #N/A
| Electrical/Mechanical |  | 0.9424
Electrical/Mechanical538 |  | 4 |  | 538 | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A | #N/A | 0.9424 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A | #NAME? | #N/A | #N/A | #N/A |  |  | #N/A
Electrical/Mechanical0 |  | 4 |  | 0 | NA | NA | 0 | 0 |  | 0 | 0 | 0 | 0 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A | #NAME? | #N/A | #N/A | 0 |  |  | 0
Electrical/Mechanical0 |  | 4 |  | 0 | NA | NA | 0 | 0 |  | 0 | 0 | 0 | 0 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A | #NAME? | #N/A | #N/A | 0 |  |  | 0
Electrical/Mechanical0 |  | 4 |  | 0 | NA | NA | 0 | 0 |  | 0 | 0 | 0 | 9.9024e-08 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A | #NAME? | #N/A | #N/A | 0 |  |  | 0
| Food Preparation |  | 0.98208
Food Preparation530 |  | 8 |  | 530 | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A | #N/A | 0.98208 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A | #NAME? | #N/A | #N/A | #N/A |  |  | #N/A
Food Preparation0 |  | 8 |  | 0 | NA | NA | 0 | 0 |  | 0 | 0 | 0 | 0 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A | #NAME? | #N/A | #N/A | 0 |  |  | 0
Food Preparation0 |  | 8 |  | 0 | NA | NA | 0 | 0 |  | 0 | 0 | 0 | 0 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A | #NAME? | #N/A | #N/A | 0 |  |  | 0
Food Preparation0 |  | 8 |  | 0 | NA | NA | 0 | 0 |  | 0 | 0 | 0 | 9.9139e-08 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A | #NAME? | #N/A | #N/A | 0 |  |  | 0
| Gymnasium/Fitness-Fitness Area |  | 0.71424
Gymnasium/Fitness-Fitness Area535 |  | 126 |  | 535 | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A | #N/A | 0.71424 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A | #NAME? | #N/A | #N/A | #N/A |  |  | #N/A
Gymnasium/Fitness-Fitness Area0 |  | 126 |  | 0 | NA | NA | 0 | 0 |  | 0 | 0 | 0 | 0 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A | #NAME? | #N/A | #N/A | 0 |  |  | 0
Gymnasium/Fitness-Fitness Area0 |  | 126 |  | 0 | NA | NA | 0 | 0 |  | 0 | 0 | 0 | 0 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A | #NAME? | #N/A | #N/A | 0 |  |  | 0
Gymnasium/Fitness-Fitness Area0 |  | 126 |  | 0 | NA | NA | 0 | 0 |  | 0 | 0 | 0 | 9.8773e-08 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A | #NAME? | #N/A | #N/A | 0 |  |  | 0
| Highway Lodging Guest Rooms |  | 0.744
Highway Lodging Guest Rooms529 |  | 75.01 |  | 529 | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A | #N/A | 0.42053 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A | #NAME? | #N/A | #N/A | #N/A |  |  | #N/A
Highway Lodging Guest Rooms520 |  | 75.01 |  | 520 | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A | #N/A | 0.32347 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A | #NAME? | #N/A | #N/A | #N/A |  |  | #N/A
Highway Lodging Guest Rooms0 |  | 75.01 |  | 0 | NA | NA | 0 | 0 |  | 0 | 0 | 0 | 0 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A | #NAME? | #N/A | #N/A | 0 |  |  | 0
Highway Lodging Guest Rooms0 |  | 75.01 |  | 0 | NA | NA | 0 | 0 |  | 0 | 0 | 0 | 9.8878e-08 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A | #NAME? | #N/A | #N/A | 0 |  |  | 0
| Hospital - Laundry/Washing |  | 0.5952
Hospital - Laundry-washing530 |  | 82 |  | 530 | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A | #N/A | 0.5952 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A | #NAME? | #N/A | #N/A | #N/A |  |  | #N/A
Hospital - Laundry-washing0 |  | 82 |  | 0 | NA | NA | 0 | 0 |  | 0 | 0 | 0 | 0 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A | #NAME? | #N/A | #N/A | 0 |  |  | 0
Hospital - Laundry-washing0 |  | 82 |  | 0 | NA | NA | 0 | 0 |  | 0 | 0 | 0 | 0 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A | #NAME? | #N/A | #N/A | 0 |  |  | 0
Hospital - Laundry-washing0 |  | 82 |  | 0 | NA | NA | 0 | 0 |  | 0 | 0 | 0 | 9.9961e-08 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A | #NAME? | #N/A | #N/A | 0 |  |  | 0
| Library |  | 0.92256
Library535 |  | 19 |  | 535 | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A | #N/A | 0.38963 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A | #NAME? | #N/A | #N/A | #N/A |  |  | #N/A
Library520 |  | 19 |  | 520 | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A | #N/A | 0.53293 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A | #NAME? | #N/A | #N/A | #N/A |  |  | #N/A
Library0 |  | 19 |  | 0 | NA | NA | 0 | 0 |  | 0 | 0 | 0 | 0 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A | #NAME? | #N/A | #N/A | 0 |  |  | 0
Library0 |  | 19 |  | 0 | NA | NA | 0 | 0 |  | 0 | 0 | 0 | 9.9073e-08 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A | #NAME? | #N/A | #N/A | 0 |  |  | 0
| Lounge/Recreation - Break room |  | 0.72416
Lounge/Recreation - Breakroom521 |  | 9 |  | 521 | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A | #N/A | 0.4316 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A | #NAME? | #N/A | #N/A | #N/A |  |  | #N/A
Lounge/Recreation - Breakroom0 |  | 9 |  | 0 | NA | NA | 0 | 0 |  | 0 | 0 | 0 | 0 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A | #NAME? | #N/A | #N/A | 0 |  |  | 0
Lounge/Recreation - Breakroom0 |  | 9 |  | 0 | NA | NA | 0 | 0 |  | 0 | 0 | 0 | 0 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A | #NAME? | #N/A | #N/A | 0 |  |  | 0
Lounge/Recreation - Breakroom527-2 |  | 9 |  | 527-2 | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A | #N/A | 0.29256 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A | #NAME? | #N/A | #N/A | #N/A |  |  | #N/A
| Lobby |  | 0.8928
Lobby523 |  | 20.1 |  | 523 | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A | #N/A | 0.49797 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A | #NAME? | #N/A | #N/A | #N/A |  |  | #N/A
Lobby521 |  | 20.1 |  | 521 | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A | #N/A | 0.2347 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A | #NAME? | #N/A | #N/A | #N/A |  |  | #N/A
Lobby0 |  | 20.1 |  | 0 | NA | NA | 0 | 0 |  | 0 | 0 | 0 | 0 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A | #NAME? | #N/A | #N/A | 0 |  |  | 0
Lobby534-2 |  | 20.1 |  | 534-2 | Linear Wall Cove | FL | 32 | #N/A |  | #N/A | #N/A | #N/A | 0.16013 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A | #NAME? | #N/A | #N/A | #N/A |  |  | #N/A
| Office-Enclosed |  | 1.1011
Office-Enclosed531 |  | 25 |  | 531 | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A | #N/A | 0.66965 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A | #NAME? | #N/A | #N/A | #N/A |  |  | #N/A
Office-Enclosed539 |  | 25 |  | 539 | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A | #N/A | 0.18474 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A | #NAME? | #N/A | #N/A | #N/A |  |  | #N/A
Office-Enclosed0 |  | 25 |  | 0 | NA | NA | 0 | 0 |  | 0 | 0 | 0 | 0 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A | #NAME? | #N/A | #N/A | 0 |  |  | 0
Office-Enclosed537-1 |  | 25 |  | 537-1 | Linear WW Open | FL | 32 | #N/A |  | #N/A | #N/A | #N/A | 0.24673 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A | #NAME? | #N/A | #N/A | #N/A |  |  | #N/A
| Office - Open Plan (Including Other) |  | 0.97216
Office - Open Plan (Including Other)535 |  | 27 |  | 535 | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A | #N/A | 0.71616 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A | #NAME? | #N/A | #N/A | #N/A |  |  | #N/A
Office - Open Plan (Including Other)539 |  | 27 |  | 539 | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A | #N/A | 0.096248 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A | #NAME? | #N/A | #N/A | #N/A |  |  | #N/A
Office - Open Plan (Including Other)0 |  | 27 |  | 0 | NA | NA | 0 | 0 |  | 0 | 0 | 0 | 0 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A | #NAME? | #N/A | #N/A | 0 |  |  | 0
Office - Open Plan (Including Other)537-1 |  | 27 |  | 537-1 | Linear WW Open | FL | 32 | #N/A |  | #N/A | #N/A | #N/A | 0.15975 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A | #NAME? | #N/A | #N/A | #N/A |  |  | #N/A
| Restrooms |  | 0.97216
Restrooms604 |  | 12 |  | 604 | Wall Mounted Linear Direct/Indirect | FL | 32 | #N/A |  | #N/A | #N/A | #N/A | 0.28607 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A | #NAME? | #N/A | #N/A | #N/A |  |  | #N/A
Restrooms520 |  | 12 |  | 520 | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A | #N/A | 0.44124 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A | #NAME? | #N/A | #N/A | #N/A |  |  | #N/A
Restrooms0 |  | 12 |  | 0 | NA | NA | 0 | 0 |  | 0 | 0 | 0 | 0 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A | #NAME? | #N/A | #N/A | 0 |  |  | 0
Restrooms534-2 |  | 12 |  | 534-2 | Linear Wall Cove | FL | 32 | #N/A |  | #N/A | #N/A | #N/A | 0.24485 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A | #NAME? | #N/A | #N/A | #N/A |  |  | #N/A
| Retail - Sales Area |  | 1.6666
Retail - Sales Area535 |  | 97 |  | 535 | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A | #N/A | 1.0095 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A | #NAME? | #N/A | #N/A | #N/A |  |  | #N/A
Retail - Sales Area541 |  | 97 |  | 541 | #N/A |  | #N/A | #N/A |  | #N/A | #N/A | #N/A | 0.49997 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A | #NAME? | #N/A | #N/A | #N/A |  |  | #N/A
Retail - Sales Area0 |  | 97 |  | 0 | NA | NA | 0 | 0 |  | 0 | 0 | 0 | 0 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A | #NAME? | #N/A | #N/A | 0 |  |  | 0
Retail - Sales Area537-1 |  | 97 |  | 537-1 | Linear WW Open | FL | 32 | #N/A |  | #N/A | #N/A | #N/A | 0.1571 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A | #NAME? | #N/A | #N/A | #N/A |  |  | #N/A
| Stairway |  | 0.68448
Stairway530 |  | 11 |  | 530 | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A | #N/A | 0.36928 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A | #NAME? | #N/A | #N/A | #N/A |  |  | #N/A
Stairway602 |  | 11 |  | 602 | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A | #N/A | 0.3152 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A | #NAME? | #N/A | #N/A | #N/A |  |  | #N/A
Stairway0 |  | 11 |  | 0 | NA | NA | 0 | 0 |  | 0 | 0 | 0 | 0 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A | #NAME? | #N/A | #N/A | 0 |  |  | 0
Stairway0 |  | 11 |  | 0 | NA | NA | 0 | 0 |  | 0 | 0 | 0 | 9.9128e-08 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A | #NAME? | #N/A | #N/A | 0 |  |  | 0
| Storage |  | 0.62496
Storage538 |  | 41 |  | 538 | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A | #N/A | 0.62496 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A | #NAME? | #N/A | #N/A | #N/A |  |  | #N/A
Storage0 |  | 41 |  | 0 | NA | NA | 0 | 0 |  | 0 | 0 | 0 | 0 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A | #NAME? | #N/A | #N/A | 0 |  |  | 0
Storage0 |  | 41 |  | 0 | NA | NA | 0 | 0 |  | 0 | 0 | 0 | 0 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A | #NAME? | #N/A | #N/A | 0 |  |  | 0
Storage0 |  | 41 |  | 0 | NA | NA | 0 | 0 |  | 0 | 0 | 0 | 9.8503e-08 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A | #NAME? | #N/A | #N/A | 0 |  |  | 0
| Lobby - Hotel |  | 1.0515
Lobby - Hotel572 |  | 79 |  | 572 | Downlight open | TH | 75 | #N/A |  | #N/A | #N/A | #N/A | 0.8917 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A | #NAME? | #N/A | #N/A | #N/A |  |  | #N/A
Lobby - Hotel0 |  | 79 |  | 0 | NA | NA | 0 | 0 |  | 0 | 0 | 0 | 0 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A | #NAME? | #N/A | #N/A | 0 |  |  | 0
Lobby - Hotel0 |  | 79 |  | 0 | NA | NA | 0 | 0 |  | 0 | 0 | 0 | 0 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A | #NAME? | #N/A | #N/A | 0 |  |  | 0
Lobby - Hotel527-1 |  | 79 |  | 527-1 | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A | #N/A | 0.15982 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A | #NAME? | #N/A | #N/A | #N/A |  |  | #N/A
1 FL linear fluorescent, CF compact fluorescent, MH metal halide

## Int Ltg LPD IECC Space Types SR (hidden)
| IECC Cost Effectiveness - Interior Lighting Power Density - Fixture Costs per Square Foot for Each Space Type - Standalone Retail | [18 empty] | RETAIL STANDALONE
Adjustment Factors for LPD
| Interior lighting costs by space type and fixture type IECC 2009, North Carolina Base Code, and IECC 2012 tables. | [18 empty] | 2009 | 0.969
| 90.1-07 and 2010 in Int Ltg LPD Space Types 90_1 (same for all prototypes). Values come from "Int Ltg Comp" worksheet in this workbook. | [18 empty] | N. Carolina | 0.911
[20 empty] | 2012 | 0.932
Interior Lighting Costs by Space Type, 2009
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33 | 34 | 35
| Space Type Lighting Descriptions and Cost Parameters | [14 empty] | New Construction Cost | [6 empty] | Lamp Replacement Cost | [6 empty] | Ballast Replacement Cost
IECC 2009 Lookup Values | 2009 Space Types | 90.1 Lighting Subcommittee Model Number | Space Type Lighting Power Allowance W/ft2 | Fixture ID Number | Fixture Type | Lamp Type1 | Lamp Wattage | Number of Lamps | Not Used | Fixture Watts | Lamp Life Hours | Quantity of Fixtures/ft2 | Fixture Watts/ft2 | not used | not used | Fixture Cost/ft2 | not used | not used | not used | Labor Cost $/ft2 | Not Used | Not Used | Lamp Cost $/ft2 | Not Used | Not Used | Not Used | Labor Cost/ft2 | Overhead and Profit, $/ft2 | Total $/ft2 | Ballast Life Hours | Ballast Cost, $/ft2 | Not Used | Not Used | Labor Cost/ft2 | Not Used | Not Used
Classroom/Lecture/Training | Classroom/Lecture/Training |  | 1.3566
Classroom/Lecture/Training535 |  | 3.1 |  | 535 | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A | #N/A | 1.1161 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A |  | #N/A | #N/A | #N/A |  |  | #N/A
Classroom/Lecture/Training537-2 |  | 3.1 |  | 537-2 | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A | #N/A | 0.24048 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A |  | #N/A | #N/A | #N/A |  |  | #N/A
Classroom/Lecture/Training0 |  | 3.1 |  | 0 | NA | NA | 0 | 0 |  | 0 | 0 | 0 | 0 |  |  | 0 |  |  |  | 0 |  |  | 0 |  |  |  | 0 |  | 0 | 0 | 0 |  |  | 0
| Conference/Meeting/Multipurpose |  | 1.2597
Conference/Meeting/Multipurpose535 |  | 31 |  | 535 | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A | #N/A | 0.64344 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A |  | #N/A | #N/A | #N/A |  |  | #N/A
Conference/Meeting/Multipurpose537-1 |  | 31 |  | 537-1 | Linear WW Open | FL | 32 | 1 |  | 29 | 36000 | 0.012632 | 0.36632 |  |  | 1.3083 |  |  |  | 0.77685 |  |  | 0.042316 |  |  |  | 0.069055 |  | 0.11137 | 50000 | 0.37895 |  |  | 0.77685
Conference/Meeting/Multipurpose511 |  | 31 |  | 511 | Downlight open - flood | PAR | 60 | 1 |  | 60 | 4200 | 0.0041656 | 0.24993 |  |  | 0.15446 |  |  |  | 0.25618 |  |  | 0.08906 |  |  |  | 0.012122 |  | 0.10118 | 0 | 0 |  |  | 0
| Corridor/Transition |  | 0.4845
Corridor/Transition530 |  | 2 |  | 530 | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A | #N/A | 0.27866 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A |  | #N/A | #N/A | #N/A |  |  | #N/A
Corridor/Transition537-2 |  | 2 |  | 537-2 | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A | #N/A | 0.20584 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A |  | #N/A | #N/A | #N/A |  |  | #N/A
Corridor/Transition0 |  | 2 |  | 0 | NA | NA | 0 | 0 |  | 0 | 0 | 0 | 0 |  |  | 0 |  |  |  | 0 |  |  | 0 |  |  |  | 0 |  | 0 | 0 | 0 |  |  | 0
| Dining Area |  | 0.8721
Dining Area531 |  | 6 |  | 531 | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A | #N/A | 0.6689 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A |  | #N/A | #N/A | #N/A |  |  | #N/A
Dining Area524 |  | 6 |  | 524 | indirect Wall Scounce | CF | 18 | 2 |  | 39 | 10000 | 0.0052102 | 0.2032 |  |  | 0.4672 |  |  |  | 0.32043 |  |  | 0.1636 |  |  |  | 0.030219 |  | 0.19382 | 50000 | 0 |  |  | 0
Dining Area0 |  | 6
| Electrical/Mechanical |  | 1.4535
Electrical/Mechanical538 |  | 4 |  | 538 | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A | #N/A | 1.4535 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A |  | #N/A | #N/A | #N/A |  |  | #N/A
Electrical/Mechanical0 |  | 4 |  | 0 | NA | NA | 0 | 0 |  | 0 | 0 | 0 | 0 |  |  | 0 |  |  |  | 0 |  |  | 0 |  |  |  | 0 |  | 0 | 0 | 0 |  |  | 0
Electrical/Mechanical0 |  | 4 |  | 0 | NA | NA | 0 | 0 |  | 0 | 0 | 0 | 0 |  |  | 0 |  |  |  | 0 |  |  | 0 |  |  |  | 0 |  | 0 | 0 | 0 |  |  | 0
| Food Preparation |  | 1.1628
Food Preparation530 |  | 8 |  | 530 | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A | #N/A | 1.1628 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A |  | #N/A | #N/A | #N/A |  |  | #N/A
Food Preparation0 |  | 8 |  | 0 | NA | NA | 0 | 0 |  | 0 | 0 | 0 | 0 |  |  | 0 |  |  |  | 0 |  |  | 0 |  |  |  | 0 |  | 0 | 0 | 0 |  |  | 0
Food Preparation0 |  | 8 |  | 0 | NA | NA | 0 | 0 |  | 0 | 0 | 0 | 0 |  |  | 0 |  |  |  | 0 |  |  | 0 |  |  |  | 0 |  | 0 | 0 | 0 |  |  | 0
| Gymnasium/Fitness-Fitness Area |  | 0.8721
Gymnasium/Fitness-Fitness Area535 |  | 126 |  | 535 | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A | #N/A | 0.8721 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A |  | #N/A | #N/A | #N/A |  |  | #N/A
Gymnasium/Fitness-Fitness Area0 |  | 126 |  | 0 | NA | NA | 0 | 0 |  | 0 | 0 | 0 | 0 |  |  | 0 |  |  |  | 0 |  |  | 0 |  |  |  | 0 |  | 0 | 0 | 0 |  |  | 0
Gymnasium/Fitness-Fitness Area0 |  | 126 |  | 0 | NA | NA | 0 | 0 |  | 0 | 0 | 0 | 0 |  |  | 0 |  |  |  | 0 |  |  | 0 |  |  |  | 0 |  | 0 | 0 | 0 |  |  | 0
| Highway Lodging Guest Rooms |  | 1.0659
Highway Lodging Guest Rooms524 |  | 75.01 |  | 524 | indirect Wall Scounce | CF | 18 | 2 |  | 39 | 10000 | 0.0041615 | 0.1623 |  |  | 0.37316 |  |  |  | 0.25593 |  |  | 0.13067 |  |  |  | 0.024137 |  | 0.15481 | 50000 | 0 |  |  | 0
Highway Lodging Guest Rooms520 |  | 75.01 |  | 520 | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A | #N/A | 0.9036 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A |  | #N/A | #N/A | #N/A |  |  | #N/A
Highway Lodging Guest Rooms0 |  | 75.01 |  | 0 | NA | NA | 0 | 0 |  | 0 | 0 | 0 | 0 |  |  | 0 |  |  |  | 0 |  |  | 0 |  |  |  | 0 |  | 0 | 0 | 0 |  |  | 0
| Hospital - Laundry/Washing |  | 0.5814
Hospital - Laundry-washing530 |  | 82 |  | 530 | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A | #N/A | 0.5814 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A |  | #N/A | #N/A | #N/A |  |  | #N/A
Hospital - Laundry-washing0 |  | 82 |  | 0 | NA | NA | 0 | 0 |  | 0 | 0 | 0 | 0 |  |  | 0 |  |  |  | 0 |  |  | 0 |  |  |  | 0 |  | 0 | 0 | 0 |  |  | 0
Hospital - Laundry-washing0 |  | 82 |  | 0 | NA | NA | 0 | 0 |  | 0 | 0 | 0 | 0 |  |  | 0 |  |  |  | 0 |  |  | 0 |  |  |  | 0 |  | 0 | 0 | 0 |  |  | 0
| Library |  | 1.1628
Library535 |  | 19 |  | 535 | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A | #N/A | 0.59109 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A |  | #N/A | #N/A | #N/A |  |  | #N/A
Library520 |  | 19 |  | 520 | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A | #N/A | 0.25194 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A |  | #N/A | #N/A | #N/A |  |  | #N/A
Library529 |  | 19 |  | 529 | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A | #N/A | 0.31008 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A |  | #N/A | #N/A | #N/A |  |  | #N/A
| Lobby |  | 1.2597
Lobby534-2 |  | 20.1 |  | 534-2 | Linear Wall Cove | FL | 32 | 1 |  | 29 | 36000 | 0.0087135 | 0.25269 |  |  | 3.3111 |  |  |  | 0.50427 |  |  | 0.02919 |  |  |  | 0.047635 |  | 0.076825 | 50000 | 0.26141 |  |  | 0.53588
Lobby523 |  | 20.1 |  | 523 | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A | #N/A | 0.92084 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A |  | #N/A | #N/A | #N/A |  |  | #N/A
Lobby521 |  | 20.1 |  | 521 | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A | #N/A | 0.086168 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A |  | #N/A | #N/A | #N/A |  |  | #N/A
| Lobby - Hotel |  | 1.0659 | [27 empty] | #N/A
Lobby - Hotel535 |  | 79 |  | 535 | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A | #N/A | 0.026674 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A |  | #N/A | #N/A | #N/A |  |  | #N/A
Lobby - Hotel572 |  | 79 |  | 572 | Downlight open | TH | 75 | 1 |  | 75 | 850 | 0.012402 | 0.93011 |  |  | 0.346 |  |  |  | 0.76269 |  |  | 0.26514 |  |  |  | 0.29144 |  | 0.55658 | 0 | 0 |  |  | 0
Lobby - Hotel524 |  | 79 |  | 524 | indirect Wall Scounce | CF | 18 | 2 |  | 39 | 10000 | 0.0027978 | 0.10911 |  |  | 0.25088 |  |  |  | 0.17206 |  |  | 0.08785 |  |  |  | 0.016227 |  | 0.10408 | 50000 | 0 |  |  | 0
| Lounge/Recreation - Break room |  | 1.1628
Lounge/Recreation - Breakroom537-1 |  | 9 |  | 537-1 | Linear WW Open | FL | 32 | 1 |  | 29 | 36000 | 0.012636 | 0.36645 |  |  | 1.3087 |  |  |  | 0.77714 |  |  | 0.042332 |  |  |  | 0.06908 |  | 0.11141 | 50000 | 0.37909 |  |  | 0.77714
Lounge/Recreation - Breakroom572 |  | 9 |  | 0 | NA | NA | 0 | 0 |  | 0 | 0 | 0 | 0 |  |  | 0 |  |  |  | 0 |  |  | 0 |  |  |  | 0 |  | 0 | 0 | 0 |  |  | 0
Lounge/Recreation - Breakroom521 |  | 9 |  | 521 | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A | #N/A | 0.79635 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A |  | #N/A | #N/A | #N/A |  |  | #N/A
| Office-Enclosed |  | 1.0659
Office-Enclosed535 |  | 25 |  | 535 | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A | #N/A | 0.75237 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A |  | #N/A | #N/A | #N/A |  |  | #N/A
Office-Enclosed539 |  | 25 |  | 539 | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A | #N/A | 0.119 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A |  | #N/A | #N/A | #N/A |  |  | #N/A
Office-Enclosed537-2 |  | 25 |  | 537-2 | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A | #N/A | 0.19453 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A |  | #N/A | #N/A | #N/A |  |  | #N/A
| Office - Open Plan (Including Other) |  | 1.0659
Office - Open Plan (Including Other)535 |  | 27 |  | 535 | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A | #N/A | 0.85307 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A |  | #N/A | #N/A | #N/A |  |  | #N/A
Office - Open Plan (Including Other)539 |  | 27 |  | 539 | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A | #N/A | 0.15179 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A |  | #N/A | #N/A | #N/A |  |  | #N/A
Office - Open Plan (Including Other)524 |  | 27 |  | 524 | indirect Wall Scounce | CF | 18 | 2 |  | 39 | 10000 | 0.0015651 | 0.06104 |  |  | 0.14035 |  |  |  | 0.096256 |  |  | 0.049145 |  |  |  | 0.0090778 |  | 0.058223 | 50000 | 0 |  |  | 0
| Restrooms |  | 0.8721
Restrooms521 |  | 12 |  | 521 | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A | #N/A | 0.41148 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A |  | #N/A | #N/A | #N/A |  |  | #N/A
Restrooms537-1 |  | 12 |  | 537-1 | Linear WW Open | FL | 32 | 1 |  | 29 | 36000 | 0.011389 | 0.33027 |  |  | 1.1795 |  |  |  | 0.70039 |  |  | 0.038152 |  |  |  | 0.062258 |  | 0.10041 | 50000 | 0.34166 |  |  | 0.70039
Restrooms524 |  | 12 |  | 524 | indirect Wall Scounce | CF | 18 | 2 |  | 39 | 10000 | 0.0033424 | 0.13035 |  |  | 0.29971 |  |  |  | 0.20556 |  |  | 0.10495 |  |  |  | 0.019386 |  | 0.12434 | 50000 | 0 |  |  | 0
| Retail - Sales Area |  | 1.6473
Retail - Sales Area535 |  | 97 |  | 535 | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A | #N/A | 0.92974 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A |  | #N/A | #N/A | #N/A |  |  | #N/A
Retail - Sales Area541 |  | 97 |  | 541 | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A | #N/A | 0.71756 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A |  | #N/A | #N/A | #N/A |  |  | #N/A
Retail - Sales Area572 |  | 97 |  | 0 | NA | NA | 0 | 0 |  | 0 | 0 | 0 | 0 |  |  | 0 |  |  |  | 0 |  |  | 0 |  |  |  | 0 |  | 0 | 0 | 0 |  |  | 0
| Stairway |  | 0.5814
Stairway530 |  | 11 |  | 530 | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A | #N/A | 0.5814 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A |  | #N/A | #N/A | #N/A |  |  | #N/A
Stairway0 |  | 11 |  | 0 | NA | NA | 0 | 0 |  | 0 | 0 | 0 | 0 |  |  | 0 |  |  |  | 0 |  |  | 0 |  |  |  | 0 |  | 0 | 0 | 0 |  |  | 0
Stairway0 |  | 11 |  | 0 | NA | NA | 0 | 0 |  | 0 | 0 | 0 | 0 |  |  | 0 |  |  |  | 0 |  |  | 0 |  |  |  | 0 |  | 0 | 0 | 0 |  |  | 0
| Storage |  | 0.7752
Storage530 |  | 41 |  | 530 | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A | #N/A | 0.7752 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A |  | #N/A | #N/A | #N/A |  |  | #N/A
Storage553 |  | 41 |  | 0 | NA | NA | 0 | 0 |  | 0 | 0 | 0 | 0 |  |  | 0 |  |  |  | 0 |  |  | 0 |  |  |  | 0 |  | 0 | 0 | 0 |  |  | 0
Storage0 |  | 41 |  | 0 | NA | NA | 0 | 0 |  | 0 | 0 | 0 | 0 |  |  | 0 |  |  |  | 0 |  |  | 0 |  |  |  | 0 |  | 0 | 0 | 0 |  |  | 0
1 FL linear fluorescent, CF compact fluorescent, MH metal halide
Interior Lighting Costs by Space Type, North Carolina Base Code
| Space Type Lighting Descriptions and Cost Parameters | [14 empty] | New Construction Cost | [6 empty] | Lamp Replacement Cost | [6 empty] | Ballast Replacement Cost
North Carolina Base Code Lookup Values | 2009 Space Types | 90.1 Lighting Subcommittee Model Number | Space Type Lighting Power Allowance W/ft2 | Fixture ID Number | Fixture Type | Lamp Type1 | Lamp Wattage | Number of Lamps | Not Used | Fixture Watts | Lamp Life Hours | Quantity of Fixtures/ft2 | Fixture Watts/ft2 | not used | not used | Fixture Cost/ft2 | not used | not used | not used | Labor Cost $/ft2 | Not Used | Not Used | Lamp Cost $/ft2 | Not Used | Not Used | Not Used | Labor Cost/ft2 |  | Total $/ft2 | Ballast Life Hours | Ballast Cost, $/ft2 | Not Used | Not Used | Labor Cost/ft2 | Not Used | Not Used
Classroom/Lecture/Training | Classroom/Lecture/Training |  | 1.2754
Classroom/Lecture/Training535 |  | 3.1 |  | 535 | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A | #N/A | 1.0493 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A |  | #N/A | #N/A | #N/A |  |  | #N/A
Classroom/Lecture/Training537-2 |  | 3.1 |  | 537-2 | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A | #N/A | 0.22609 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A |  | #N/A | #N/A | #N/A |  |  | #N/A
Classroom/Lecture/Training0 |  | 3.1 |  | 0 | NA | NA | 0 | 0 |  | 0 | 0 | 0 | 0 |  |  | 0 |  |  |  | 0 |  |  | 0 |  |  |  | 0 |  | 0 | 0 | 0 |  |  | 0
| Conference/Meeting/Multipurpose |  | 1.1843
Conference/Meeting/Multipurpose535 |  | 31 |  | 535 | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A | #N/A | 0.60493 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A |  | #N/A | #N/A | #N/A |  |  | #N/A
Conference/Meeting/Multipurpose537-1 |  | 31 |  | 537-1 | Linear WW Open | FL | 32 | 1 |  | 29 | 36000 | 0.011876 | 0.34439 |  |  | 1.23 |  |  |  | 0.73035 |  |  | 0.039784 |  |  |  | 0.064921 |  | 0.1047 | 50000 | 0.35627 |  |  | 0.73035
Conference/Meeting/Multipurpose511 |  | 31 |  | 511 | Downlight open - flood | PAR | 60 | 1 |  | 60 | 4200 | 0.0039162 | 0.23497 |  |  | 0.14521 |  |  |  | 0.24085 |  |  | 0.083729 |  |  |  | 0.011396 |  | 0.095126 | 0 | 0 |  |  | 0
| Corridor/Transition |  | 0.4555
Corridor/Transition530 |  | 2 |  | 530 | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A | #N/A | 0.26198 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A |  | #N/A | #N/A | #N/A |  |  | #N/A
Corridor/Transition537-2 |  | 2 |  | 537-2 | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A | #N/A | 0.19352 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A |  | #N/A | #N/A | #N/A |  |  | #N/A
Corridor/Transition0 |  | 2 |  | 0 | NA | NA | 0 | 0 |  | 0 | 0 | 0 | 0 |  |  | 0 |  |  |  | 0 |  |  | 0 |  |  |  | 0 |  | 0 | 0 | 0 |  |  | 0
| Dining Area |  | 0.8199
Dining Area531 |  | 6 |  | 531 | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A | #N/A | 0.62886 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A |  | #N/A | #N/A | #N/A |  |  | #N/A
Dining Area524 |  | 6 |  | 524 | indirect Wall Scounce | CF | 18 | 2 |  | 39 | 10000 | 0.0048984 | 0.19104 |  |  | 0.43924 |  |  |  | 0.30125 |  |  | 0.15381 |  |  |  | 0.028411 |  | 0.18222 | 50000 | 0 |  |  | 0
Dining Area0 |  | 6
| Electrical/Mechanical |  | 1.3665
Electrical/Mechanical538 |  | 4 |  | 538 | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A | #N/A | 1.3665 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A |  | #N/A | #N/A | #N/A |  |  | #N/A
Electrical/Mechanical0 |  | 4 |  | 0 | NA | NA | 0 | 0 |  | 0 | 0 | 0 | 0 |  |  | 0 |  |  |  | 0 |  |  | 0 |  |  |  | 0 |  | 0 | 0 | 0 |  |  | 0
Electrical/Mechanical0 |  | 4 |  | 0 | NA | NA | 0 | 0 |  | 0 | 0 | 0 | 0 |  |  | 0 |  |  |  | 0 |  |  | 0 |  |  |  | 0 |  | 0 | 0 | 0 |  |  | 0
| Food Preparation |  | 1.0932
Food Preparation530 |  | 8 |  | 530 | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A | #N/A | 1.0932 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A |  | #N/A | #N/A | #N/A |  |  | #N/A
Food Preparation0 |  | 8 |  | 0 | NA | NA | 0 | 0 |  | 0 | 0 | 0 | 0 |  |  | 0 |  |  |  | 0 |  |  | 0 |  |  |  | 0 |  | 0 | 0 | 0 |  |  | 0
Food Preparation0 |  | 8 |  | 0 | NA | NA | 0 | 0 |  | 0 | 0 | 0 | 0 |  |  | 0 |  |  |  | 0 |  |  | 0 |  |  |  | 0 |  | 0 | 0 | 0 |  |  | 0
| Gymnasium/Fitness-Fitness Area |  | 0.8199
Gymnasium/Fitness-Fitness Area535 |  | 126 |  | 535 | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A | #N/A | 0.8199 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A |  | #N/A | #N/A | #N/A |  |  | #N/A
Gymnasium/Fitness-Fitness Area0 |  | 126 |  | 0 | NA | NA | 0 | 0 |  | 0 | 0 | 0 | 0 |  |  | 0 |  |  |  | 0 |  |  | 0 |  |  |  | 0 |  | 0 | 0 | 0 |  |  | 0
Gymnasium/Fitness-Fitness Area0 |  | 126 |  | 0 | NA | NA | 0 | 0 |  | 0 | 0 | 0 | 0 |  |  | 0 |  |  |  | 0 |  |  | 0 |  |  |  | 0 |  | 0 | 0 | 0 |  |  | 0
| Highway Lodging Guest Rooms |  | 1.0021
Highway Lodging Guest Rooms524 |  | 75.01 |  | 524 | indirect Wall Scounce | CF | 18 | 2 |  | 39 | 10000 | 0.0039124 | 0.15258 |  |  | 0.35083 |  |  |  | 0.24061 |  |  | 0.12285 |  |  |  | 0.022692 |  | 0.14554 | 50000 | 0 |  |  | 0
Highway Lodging Guest Rooms520 |  | 75.01 |  | 520 | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A | #N/A | 0.84952 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A |  | #N/A | #N/A | #N/A |  |  | #N/A
Highway Lodging Guest Rooms0 |  | 75.01 |  | 0 | NA | NA | 0 | 0 |  | 0 | 0 | 0 | 0 |  |  | 0 |  |  |  | 0 |  |  | 0 |  |  |  | 0 |  | 0 | 0 | 0 |  |  | 0
| Hospital - Laundry/Washing |  | 0.5466
Hospital - Laundry-washing530 |  | 82 |  | 530 | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A | #N/A | 0.5466 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A |  | #N/A | #N/A | #N/A |  |  | #N/A
Hospital - Laundry-washing0 |  | 82 |  | 0 | NA | NA | 0 | 0 |  | 0 | 0 | 0 | 0 |  |  | 0 |  |  |  | 0 |  |  | 0 |  |  |  | 0 |  | 0 | 0 | 0 |  |  | 0
Hospital - Laundry-washing0 |  | 82 |  | 0 | NA | NA | 0 | 0 |  | 0 | 0 | 0 | 0 |  |  | 0 |  |  |  | 0 |  |  | 0 |  |  |  | 0 |  | 0 | 0 | 0 |  |  | 0
| Library |  | 1.0932
Library535 |  | 19 |  | 535 | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A | #N/A | 0.55571 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A |  | #N/A | #N/A | #N/A |  |  | #N/A
Library520 |  | 19 |  | 520 | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A | #N/A | 0.23686 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A |  | #N/A | #N/A | #N/A |  |  | #N/A
Library529 |  | 19 |  | 529 | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A | #N/A | 0.29152 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A |  | #N/A | #N/A | #N/A |  |  | #N/A
| Lobby |  | 1.1843
Lobby534-2 |  | 20.1 |  | 534-2 | Linear Wall Cove | FL | 32 | 1 |  | 29 | 36000 | 0.008192 | 0.23757 |  |  | 3.113 |  |  |  | 0.47408 |  |  | 0.027443 |  |  |  | 0.044783 |  | 0.072226 | 50000 | 0.24576 |  |  | 0.50381
Lobby523 |  | 20.1 |  | 523 | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A | #N/A | 0.86572 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A |  | #N/A | #N/A | #N/A |  |  | #N/A
Lobby521 |  | 20.1 |  | 521 | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A | #N/A | 0.08101 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A |  | #N/A | #N/A | #N/A |  |  | #N/A
| Lobby - Hotel |  | 1.0021 | [27 empty] | #N/A
Lobby - Hotel535 |  | 79 |  | 535 | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A | #N/A | 0.025078 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A |  | #N/A | #N/A | #N/A |  |  | #N/A
Lobby - Hotel572 |  | 79 |  | 572 | Downlight open | TH | 75 | 1 |  | 75 | 850 | 0.011659 | 0.87444 |  |  | 0.32529 |  |  |  | 0.71704 |  |  | 0.24927 |  |  |  | 0.27399 |  | 0.52327 | 0 | 0 |  |  | 0
Lobby - Hotel524 |  | 79 |  | 524 | indirect Wall Scounce | CF | 18 | 2 |  | 39 | 10000 | 0.0026303 | 0.10258 |  |  | 0.23586 |  |  |  | 0.16176 |  |  | 0.082592 |  |  |  | 0.015256 |  | 0.097847 | 50000 | 0 |  |  | 0
| Lounge/Recreation - Break room |  | 1.0932
Lounge/Recreation - Breakroom537-1 |  | 9 |  | 537-1 | Linear WW Open | FL | 32 | 1 |  | 29 | 36000 | 0.01188 | 0.34452 |  |  | 1.2304 |  |  |  | 0.73062 |  |  | 0.039798 |  |  |  | 0.064945 |  | 0.10474 | 50000 | 0.3564 |  |  | 0.73062
Lounge/Recreation - Breakroom572 |  | 9 |  | 0 | NA | NA | 0 | 0 |  | 0 | 0 | 0 | 0 |  |  | 0 |  |  |  | 0 |  |  | 0 |  |  |  | 0 |  | 0 | 0 | 0 |  |  | 0
Lounge/Recreation - Breakroom521 |  | 9 |  | 521 | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A | #N/A | 0.74868 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A |  | #N/A | #N/A | #N/A |  |  | #N/A
| Office-Enclosed |  | 1.0021
Office-Enclosed535 |  | 25 |  | 535 | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A | #N/A | 0.70734 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A |  | #N/A | #N/A | #N/A |  |  | #N/A
Office-Enclosed539 |  | 25 |  | 539 | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A | #N/A | 0.11187 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A |  | #N/A | #N/A | #N/A |  |  | #N/A
Office-Enclosed537-2 |  | 25 |  | 537-2 | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A | #N/A | 0.18289 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A |  | #N/A | #N/A | #N/A |  |  | #N/A
| Office - Open Plan (Including Other) |  | 1.0021
Office - Open Plan (Including Other)535 |  | 27 |  | 535 | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A | #N/A | 0.80201 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A |  | #N/A | #N/A | #N/A |  |  | #N/A
Office - Open Plan (Including Other)539 |  | 27 |  | 539 | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A | #N/A | 0.1427 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A |  | #N/A | #N/A | #N/A |  |  | #N/A
Office - Open Plan (Including Other)524 |  | 27 |  | 524 | indirect Wall Scounce | CF | 18 | 2 |  | 39 | 10000 | 0.0014715 | 0.057387 |  |  | 0.13195 |  |  |  | 0.090495 |  |  | 0.046204 |  |  |  | 0.0085345 |  | 0.054738 | 50000 | 0 |  |  | 0
| Restrooms |  | 0.8199
Restrooms521 |  | 12 |  | 521 | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A | #N/A | 0.38685 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A |  | #N/A | #N/A | #N/A |  |  | #N/A
Restrooms537-1 |  | 12 |  | 537-1 | Linear WW Open | FL | 32 | 1 |  | 29 | 36000 | 0.010707 | 0.3105 |  |  | 1.1089 |  |  |  | 0.65847 |  |  | 0.035868 |  |  |  | 0.058532 |  | 0.094399 | 50000 | 0.32121 |  |  | 0.65847
Restrooms524 |  | 12 |  | 524 | indirect Wall Scounce | CF | 18 | 2 |  | 39 | 10000 | 0.0031423 | 0.12255 |  |  | 0.28177 |  |  |  | 0.19325 |  |  | 0.09867 |  |  |  | 0.018226 |  | 0.1169 | 50000 | 0 |  |  | 0
| Retail - Sales Area |  | 1.5487
Retail - Sales Area535 |  | 97 |  | 535 | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A | #N/A | 0.87409 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A |  | #N/A | #N/A | #N/A |  |  | #N/A
Retail - Sales Area541 |  | 97 |  | 541 | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A | #N/A | 0.67461 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A |  | #N/A | #N/A | #N/A |  |  | #N/A
Retail - Sales Area572 |  | 97 |  | 0 | NA | NA | 0 | 0 |  | 0 | 0 | 0 | 0 |  |  | 0 |  |  |  | 0 |  |  | 0 |  |  |  | 0 |  | 0 | 0 | 0 |  |  | 0
| Stairway |  | 0.5466
Stairway530 |  | 11 |  | 530 | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A | #N/A | 0.5466 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A |  | #N/A | #N/A | #N/A |  |  | #N/A
Stairway0 |  | 11 |  | 0 | NA | NA | 0 | 0 |  | 0 | 0 | 0 | 0 |  |  | 0 |  |  |  | 0 |  |  | 0 |  |  |  | 0 |  | 0 | 0 | 0 |  |  | 0
Stairway0 |  | 11 |  | 0 | NA | NA | 0 | 0 |  | 0 | 0 | 0 | 0 |  |  | 0 |  |  |  | 0 |  |  | 0 |  |  |  | 0 |  | 0 | 0 | 0 |  |  | 0
| Storage |  | 0.7288
Storage530 |  | 41 |  | 530 | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A | #N/A | 0.7288 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A |  | #N/A | #N/A | #N/A |  |  | #N/A
Storage553 |  | 41 |  | 0 | NA | NA | 0 | 0 |  | 0 | 0 | 0 | 0 |  |  | 0 |  |  |  | 0 |  |  | 0 |  |  |  | 0 |  | 0 | 0 | 0 |  |  | 0
Storage0 |  | 41 |  | 0 | NA | NA | 0 | 0 |  | 0 | 0 | 0 | 0 |  |  | 0 |  |  |  | 0 |  |  | 0 |  |  |  | 0 |  | 0 | 0 | 0 |  |  | 0
1 FL linear fluorescent, CF compact fluorescent, MH metal halide
Interior Lighting Costs by Space Type, 2012
| Space Type Lighting Descriptions and Cost Parameters | [18 empty] | New Construction Cost |  |  | Lamp Replacement Cost | [6 empty] | Ballast Replacement Cost
IECC 2012 Lookup Values | 2012 Space Types | Model Number | Lighting Power Allowance, LPD, W/ft2 | Fixtures - ID Number | Fixture type | Lamp Type | Lamp Wattage | Number of Lamps |  | Fixture Watts | Lamp Life, Hours | Quantity of Fixtures/ft2 | Fixture Watts/ft2 |  |  | Fixture Cost only, $/ft2 | not used | not used | not used | Labor Cost $/ft2 |  |  | Lamp Cost, $/ft2 | Labor Crew Type |  |  | Labor Cost/ft2 |  | Total $/ft2 | Ballast Life Hours | Ballast Cost, $/ft2 | Not Used | Not Used | Labor Cost/ft2
Classroom/Lecture/Training | Classroom/Lecture/Training |  | 1.1557 | [26 empty] | 0 | #N/A |  |  | 0
Classroom/Lecture/Training535 |  | 3.1 |  | 535 | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A | #N/A | 0.8614 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A |  | #N/A | #N/A | #N/A |  |  | #N/A
Classroom/Lecture/Training521 |  | 3.1 |  | 521 | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A | #N/A | 0.14357 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A |  | #N/A | #N/A | #N/A |  |  | #N/A
Classroom/Lecture/Training0 |  | 3.1 |  | 0 | NA | NA | 0 | 0 |  | 0 | 0 | 0 | 0 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A |  | #N/A | #N/A | 0 |  |  | 0
Classroom/Lecture/Training537-1 |  | 3.1 |  | 537-1 | Linear WW Open | FL | 32 | #N/A |  | #N/A | #N/A | #N/A | 0.1507 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A |  | #N/A | #N/A | #N/A |  |  | #N/A
| Conference/Meeting/Multipurpose |  | 1.1464
Conference/Meeting/Multipurpose535 |  | 31 |  | 535 | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A | #N/A | 0.56321 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A |  | #N/A | #N/A | #N/A |  |  | #N/A
Conference/Meeting/Multipurpose511 |  | 31 |  | 511 | Downlight open - flood | PAR | 60 | #N/A |  | #N/A | #N/A | #N/A | 0.40741 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A |  | #N/A | #N/A | #N/A |  |  | #N/A
Conference/Meeting/Multipurpose0 |  | 31 |  | 0 | NA | NA | 0 | 0 |  | 0 | 0 | 0 | 0 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A |  | #N/A | #N/A | 0 |  |  | 0
Conference/Meeting/Multipurpose527-1 |  | 31 |  | 527-1 | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A | #N/A | 0.17574 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A |  | #N/A | #N/A | #N/A |  |  | #N/A
| Corridor/Transition |  | 0.61512
Corridor/Transition521 |  | 2 |  | 521 | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A | #N/A | 0.61512 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A |  | #N/A | #N/A | #N/A |  |  | #N/A
Corridor/Transition0 |  | 2 |  | 0 | NA | NA | 0 | 0 |  | 0 | 0 | 0 | 0 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A |  | #N/A | #N/A | 0 |  |  | 0
Corridor/Transition0 |  | 2 |  | 0 | NA | NA | 0 | 0 |  | 0 | 0 | 0 | 0 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A |  | #N/A | #N/A | 0 |  |  | 0
Corridor/Transition527-2 |  | 2 |  | 0 | NA | NA | 0 | 0 |  | 0 | 0 | 0 | 9.385e-08 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A |  | #N/A | #N/A | 0 |  |  | 0
| Dining Area |  | 0.6058
Dining Area535 |  | 6 |  | 535 | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A | #N/A | 0.2236 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A |  | #N/A | #N/A | #N/A |  |  | #N/A
Dining Area521 |  | 6 |  | 521 | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A | #N/A | 0.10965 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A |  | #N/A | #N/A | #N/A |  |  | #N/A
Dining Area0 |  | 6 |  | 0 | NA | NA | 0 | 0 |  | 0 | 0 | 0 | 0 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A |  | #N/A | #N/A | 0 |  |  | 0
Dining Area537-1 |  | 6 |  | 537-1 | Linear WW Open | FL | 32 | #N/A |  | #N/A | #N/A | #N/A | 0.27255 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A |  | #N/A | #N/A | #N/A |  |  | #N/A
| Electrical/Mechanical |  | 0.8854
Electrical/Mechanical538 |  | 4 |  | 538 | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A | #N/A | 0.8854 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A |  | #N/A | #N/A | #N/A |  |  | #N/A
Electrical/Mechanical0 |  | 4 |  | 0 | NA | NA | 0 | 0 |  | 0 | 0 | 0 | 0 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A |  | #N/A | #N/A | 0 |  |  | 0
Electrical/Mechanical0 |  | 4 |  | 0 | NA | NA | 0 | 0 |  | 0 | 0 | 0 | 0 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A |  | #N/A | #N/A | 0 |  |  | 0
Electrical/Mechanical0 |  | 4 |  | 0 | NA | NA | 0 | 0 |  | 0 | 0 | 0 | 9.3035e-08 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A |  | #N/A | #N/A | 0 |  |  | 0
| Food Preparation |  | 0.92268
Food Preparation530 |  | 8 |  | 530 | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A | #N/A | 0.92268 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A |  | #N/A | #N/A | #N/A |  |  | #N/A
Food Preparation0 |  | 8 |  | 0 | NA | NA | 0 | 0 |  | 0 | 0 | 0 | 0 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A |  | #N/A | #N/A | 0 |  |  | 0
Food Preparation0 |  | 8 |  | 0 | NA | NA | 0 | 0 |  | 0 | 0 | 0 | 0 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A |  | #N/A | #N/A | 0 |  |  | 0
Food Preparation0 |  | 8 |  | 0 | NA | NA | 0 | 0 |  | 0 | 0 | 0 | 9.3143e-08 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A |  | #N/A | #N/A | 0 |  |  | 0
| Gymnasium/Fitness-Fitness Area |  | 0.67104
Gymnasium/Fitness-Fitness Area535 |  | 126 |  | 535 | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A | #N/A | 0.67104 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A |  | #N/A | #N/A | #N/A |  |  | #N/A
Gymnasium/Fitness-Fitness Area0 |  | 126 |  | 0 | NA | NA | 0 | 0 |  | 0 | 0 | 0 | 0 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A |  | #N/A | #N/A | 0 |  |  | 0
Gymnasium/Fitness-Fitness Area0 |  | 126 |  | 0 | NA | NA | 0 | 0 |  | 0 | 0 | 0 | 0 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A |  | #N/A | #N/A | 0 |  |  | 0
Gymnasium/Fitness-Fitness Area0 |  | 126 |  | 0 | NA | NA | 0 | 0 |  | 0 | 0 | 0 | 9.2799e-08 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A |  | #N/A | #N/A | 0 |  |  | 0
| Highway Lodging Guest Rooms |  | 0.699
Highway Lodging Guest Rooms529 |  | 75.01 |  | 529 | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A | #N/A | 0.3951 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A |  | #N/A | #N/A | #N/A |  |  | #N/A
Highway Lodging Guest Rooms520 |  | 75.01 |  | 520 | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A | #N/A | 0.3039 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A |  | #N/A | #N/A | #N/A |  |  | #N/A
Highway Lodging Guest Rooms0 |  | 75.01 |  | 0 | NA | NA | 0 | 0 |  | 0 | 0 | 0 | 0 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A |  | #N/A | #N/A | 0 |  |  | 0
Highway Lodging Guest Rooms0 |  | 75.01 |  | 0 | NA | NA | 0 | 0 |  | 0 | 0 | 0 | 9.2898e-08 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A |  | #N/A | #N/A | 0 |  |  | 0
| Hospital - Laundry/Washing |  | 0.5592
Hospital - Laundry-washing530 |  | 82 |  | 530 | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A | #N/A | 0.5592 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A |  | #N/A | #N/A | #N/A |  |  | #N/A
Hospital - Laundry-washing0 |  | 82 |  | 0 | NA | NA | 0 | 0 |  | 0 | 0 | 0 | 0 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A |  | #N/A | #N/A | 0 |  |  | 0
Hospital - Laundry-washing0 |  | 82 |  | 0 | NA | NA | 0 | 0 |  | 0 | 0 | 0 | 0 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A |  | #N/A | #N/A | 0 |  |  | 0
Hospital - Laundry-washing0 |  | 82 |  | 0 | NA | NA | 0 | 0 |  | 0 | 0 | 0 | 9.3915e-08 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A |  | #N/A | #N/A | 0 |  |  | 0
| Library |  | 0.86676
Library535 |  | 19 |  | 535 | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A | #N/A | 0.36606 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A |  | #N/A | #N/A | #N/A |  |  | #N/A
Library520 |  | 19 |  | 520 | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A | #N/A | 0.5007 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A |  | #N/A | #N/A | #N/A |  |  | #N/A
Library0 |  | 19 |  | 0 | NA | NA | 0 | 0 |  | 0 | 0 | 0 | 0 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A |  | #N/A | #N/A | 0 |  |  | 0
Library0 |  | 19 |  | 0 | NA | NA | 0 | 0 |  | 0 | 0 | 0 | 9.3081e-08 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A |  | #N/A | #N/A | 0 |  |  | 0
| Lounge/Recreation - Break room |  | 0.68036
Lounge/Recreation - Breakroom521 |  | 9 |  | 521 | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A | #N/A | 0.40549 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A |  | #N/A | #N/A | #N/A |  |  | #N/A
Lounge/Recreation - Breakroom0 |  | 9 |  | 0 | NA | NA | 0 | 0 |  | 0 | 0 | 0 | 0 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A |  | #N/A | #N/A | 0 |  |  | 0
Lounge/Recreation - Breakroom0 |  | 9 |  | 0 | NA | NA | 0 | 0 |  | 0 | 0 | 0 | 0 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A |  | #N/A | #N/A | 0 |  |  | 0
Lounge/Recreation - Breakroom527-2 |  | 9 |  | 527-2 | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A | #N/A | 0.27487 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A |  | #N/A | #N/A | #N/A |  |  | #N/A
| Lobby |  | 0.8388
Lobby523 |  | 20.1 |  | 523 | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A | #N/A | 0.46786 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A |  | #N/A | #N/A | #N/A |  |  | #N/A
Lobby521 |  | 20.1 |  | 521 | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A | #N/A | 0.2205 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A |  | #N/A | #N/A | #N/A |  |  | #N/A
Lobby0 |  | 20.1 |  | 0 | NA | NA | 0 | 0 |  | 0 | 0 | 0 | 0 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A |  | #N/A | #N/A | 0 |  |  | 0
Lobby534-2 |  | 20.1 |  | 534-2 | Linear Wall Cove | FL | 32 | #N/A |  | #N/A | #N/A | #N/A | 0.15044 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A |  | #N/A | #N/A | #N/A |  |  | #N/A
| Office-Enclosed |  | 1.0345
Office-Enclosed531 |  | 25 |  | 531 | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A | #N/A | 0.62914 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A |  | #N/A | #N/A | #N/A |  |  | #N/A
Office-Enclosed539 |  | 25 |  | 539 | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A | #N/A | 0.17357 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A |  | #N/A | #N/A | #N/A |  |  | #N/A
Office-Enclosed0 |  | 25 |  | 0 | NA | NA | 0 | 0 |  | 0 | 0 | 0 | 0 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A |  | #N/A | #N/A | 0 |  |  | 0
Office-Enclosed537-1 |  | 25 |  | 537-1 | Linear WW Open | FL | 32 | #N/A |  | #N/A | #N/A | #N/A | 0.23181 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A |  | #N/A | #N/A | #N/A |  |  | #N/A
| Office - Open Plan (Including Other) |  | 0.91336
Office - Open Plan (Including Other)535 |  | 27 |  | 535 | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A | #N/A | 0.67285 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A |  | #N/A | #N/A | #N/A |  |  | #N/A
Office - Open Plan (Including Other)539 |  | 27 |  | 539 | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A | #N/A | 0.090426 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A |  | #N/A | #N/A | #N/A |  |  | #N/A
Office - Open Plan (Including Other)0 |  | 27 |  | 0 | NA | NA | 0 | 0 |  | 0 | 0 | 0 | 0 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A |  | #N/A | #N/A | 0 |  |  | 0
Office - Open Plan (Including Other)537-1 |  | 27 |  | 537-1 | Linear WW Open | FL | 32 | #N/A |  | #N/A | #N/A | #N/A | 0.15009 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A |  | #N/A | #N/A | #N/A |  |  | #N/A
| Restrooms |  | 0.91336
Restrooms604 |  | 12 |  | 604 | Wall Mounted Linear Direct/Indirect | FL | 32 | #N/A |  | #N/A | #N/A | #N/A | 0.26877 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A |  | #N/A | #N/A | #N/A |  |  | #N/A
Restrooms520 |  | 12 |  | 520 | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A | #N/A | 0.41455 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A |  | #N/A | #N/A | #N/A |  |  | #N/A
Restrooms0 |  | 12 |  | 0 | NA | NA | 0 | 0 |  | 0 | 0 | 0 | 0 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A |  | #N/A | #N/A | 0 |  |  | 0
Restrooms534-2 |  | 12 |  | 534-2 | Linear Wall Cove | FL | 32 | #N/A |  | #N/A | #N/A | #N/A | 0.23004 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A |  | #N/A | #N/A | #N/A |  |  | #N/A
| Retail - Sales Area |  | 1.5658
Retail - Sales Area535 |  | 97 |  | 535 | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A | #N/A | 0.94843 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A |  | #N/A | #N/A | #N/A |  |  | #N/A
Retail - Sales Area541 |  | 97 |  | 541 | #N/A |  | #N/A | #N/A |  | #N/A | #N/A | #N/A | 0.46973 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A |  | #N/A | #N/A | #N/A |  |  | #N/A
Retail - Sales Area0 |  | 97 |  | 0 | NA | NA | 0 | 0 |  | 0 | 0 | 0 | 0 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A |  | #N/A | #N/A | 0 |  |  | 0
Retail - Sales Area537-1 |  | 97 |  | 537-1 | Linear WW Open | FL | 32 | #N/A |  | #N/A | #N/A | #N/A | 0.1476 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A |  | #N/A | #N/A | #N/A |  |  | #N/A
| Stairway |  | 0.64308
Stairway530 |  | 11 |  | 530 | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A | #N/A | 0.34695 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A |  | #N/A | #N/A | #N/A |  |  | #N/A
Stairway602 |  | 11 |  | 602 | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A | #N/A | 0.29613 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A |  | #N/A | #N/A | #N/A |  |  | #N/A
Stairway0 |  | 11 |  | 0 | NA | NA | 0 | 0 |  | 0 | 0 | 0 | 0 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A |  | #N/A | #N/A | 0 |  |  | 0
Stairway0 |  | 11 |  | 0 | NA | NA | 0 | 0 |  | 0 | 0 | 0 | 9.3133e-08 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A |  | #N/A | #N/A | 0 |  |  | 0
| Storage |  | 0.58716
Storage538 |  | 41 |  | 538 | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A | #N/A | 0.58716 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A |  | #N/A | #N/A | #N/A |  |  | #N/A
Storage0 |  | 41 |  | 0 | NA | NA | 0 | 0 |  | 0 | 0 | 0 | 0 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A |  | #N/A | #N/A | 0 |  |  | 0
Storage0 |  | 41 |  | 0 | NA | NA | 0 | 0 |  | 0 | 0 | 0 | 0 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A |  | #N/A | #N/A | 0 |  |  | 0
Storage0 |  | 41 |  | 0 | NA | NA | 0 | 0 |  | 0 | 0 | 0 | 9.2545e-08 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A |  | #N/A | #N/A | 0 |  |  | 0
| Lobby - Hotel |  | 0.98792
Lobby - Hotel572 |  | 79 |  | 572 | Downlight open | TH | 75 | #N/A |  | #N/A | #N/A | #N/A | 0.83777 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A |  | #N/A | #N/A | #N/A |  |  | #N/A
Lobby - Hotel0 |  | 79 |  | 0 | NA | NA | 0 | 0 |  | 0 | 0 | 0 | 0 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A |  | #N/A | #N/A | 0 |  |  | 0
Lobby - Hotel0 |  | 79 |  | 0 | NA | NA | 0 | 0 |  | 0 | 0 | 0 | 0 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A |  | #N/A | #N/A | 0 |  |  | 0
Lobby - Hotel527-1 |  | 79 |  | 527-1 | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A | #N/A | 0.15015 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A |  | #N/A | #N/A | #N/A |  |  | #N/A
1 FL linear fluorescent, CF compact fluorescent, MH metal halide

## Int Ltg LPD Space Types PS (hidden)
| IECC Cost Effectiveness - Interior Lighting Power Density - Fixture Costs per Square Foot for Each Space Type - Primary School | [18 empty] | PRIMARY SCHOOL
Adjustment Factors for LPD
| Interior lighting costs by space type and fixture type IECC 2009, North Carolina Base Code, and IECC 2012 tables. | [18 empty] | 2009 | 1.011
| 90.1-07 and 2010 in Int Ltg LPD Space Types 90_1 (same for all prototypes). Values come from "Int Ltg Comp" worksheet in this workbook. | [18 empty] | N. Carolina | 0.825
[20 empty] | 2012 | 0.94
Interior Lighting Costs by Space Type, 2009
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 30 | 31 | 32 | 33 | 34 | 35
| Space Type Lighting Descriptions and Cost Parameters | [14 empty] | New Construction Cost | [6 empty] | Lamp Replacement Cost | [5 empty] | Ballast Replacement Cost
IECC 2009 Lookup Values | 2009 Space Types | 90.1 Lighting Subcommittee Model Number | Space Type Lighting Power Allowance W/ft2 | Fixture ID Number | Fixture Type | Lamp Type1 | Lamp Wattage | Number of Lamps | Not Used | Fixture Watts | Lamp Life Hours | Quantity of Fixtures/ft2 | Fixture Watts/ft2 | not used | not used | Fixture Cost/ft2 | not used | not used | not used | Labor Cost $/ft2 | Not Used | Not Used | Lamp Cost $/ft2 | Not Used | Not Used | Not Used | Labor Cost/ft2 | Total $/ft2 | Ballast Life Hours | Ballast Cost, $/ft2 | Not Used | Not Used | Labor Cost/ft2 | Not Used | Not Used
Classroom/Lecture/Training | Classroom/Lecture/Training |  | 1.4154
Classroom/Lecture/Training535 |  | 3.1 |  | 535 | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A | #N/A | 1.1645 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A | #N/A | #N/A | #N/A |  |  | #N/A
Classroom/Lecture/Training537-2 |  | 3.1 |  | 537-2 | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A | #N/A | 0.2509 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A | #N/A | #N/A | #N/A |  |  | #N/A
Classroom/Lecture/Training0 |  | 3.1 |  | 0 | NA | NA | 0 | 0 |  | 0 | 0 | 0 | 0 |  |  | 0 |  |  |  | 0 |  |  | 0 |  |  |  | 0 | 0 | 0 | 0 |  |  | 0
| Conference/Meeting/Multipurpose |  | 1.3143
Conference/Meeting/Multipurpose535 |  | 31 |  | 535 | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A | #N/A | 0.67133 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A | #N/A | #N/A | #N/A |  |  | #N/A
Conference/Meeting/Multipurpose537-1 |  | 31 |  | 537-1 | Linear WW Open | FL | 32 | 1 |  | 29 | 36000 | 0.013179 | 0.3822 |  |  | 1.365 |  |  |  | 0.81053 |  |  | 0.044151 |  |  |  | 0.072048 | 0.1162 | 50000 | 0.39538 |  |  | 0.81053
Conference/Meeting/Multipurpose511 |  | 31 |  | 511 | Downlight open - flood | PAR | 60 | 1 |  | 60 | 4200 | 0.0043461 | 0.26077 |  |  | 0.16115 |  |  |  | 0.26729 |  |  | 0.09292 |  |  |  | 0.012647 | 0.10557 | 0 | 0 |  |  | 0
| Corridor/Transition |  | 0.5055
Corridor/Transition530 |  | 2 |  | 530 | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A | #N/A | 0.29073 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A | #N/A | #N/A | #N/A |  |  | #N/A
Corridor/Transition537-2 |  | 2 |  | 537-2 | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A | #N/A | 0.21477 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A | #N/A | #N/A | #N/A |  |  | #N/A
Corridor/Transition0 |  | 2 |  | 0 | NA | NA | 0 | 0 |  | 0 | 0 | 0 | 0 |  |  | 0 |  |  |  | 0 |  |  | 0 |  |  |  | 0 | 0 | 0 | 0 |  |  | 0
| Dining Area |  | 0.9099
Dining Area531 |  | 6 |  | 531 | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A | #N/A | 0.69789 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A | #N/A | #N/A | #N/A |  |  | #N/A
Dining Area524 |  | 6 |  | 524 | indirect Wall Scounce | CF | 18 | 2 |  | 39 | 10000 | 0.0054361 | 0.21201 |  |  | 0.48745 |  |  |  | 0.33432 |  |  | 0.17069 |  |  |  | 0.031529 | 0.20222 | 50000 | 0 |  |  | 0
Dining Area0 |  | 6
| Electrical/Mechanical |  | 1.5165
Electrical/Mechanical538 |  | 4 |  | 538 | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A | #N/A | 1.5165 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A | #N/A | #N/A | #N/A |  |  | #N/A
Electrical/Mechanical0 |  | 4 |  | 0 | NA | NA | 0 | 0 |  | 0 | 0 | 0 | 0 |  |  | 0 |  |  |  | 0 |  |  | 0 |  |  |  | 0 | 0 | 0 | 0 |  |  | 0
Electrical/Mechanical0 |  | 4 |  | 0 | NA | NA | 0 | 0 |  | 0 | 0 | 0 | 0 |  |  | 0 |  |  |  | 0 |  |  | 0 |  |  |  | 0 | 0 | 0 | 0 |  |  | 0
| Food Preparation |  | 1.2132
Food Preparation530 |  | 8 |  | 530 | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A | #N/A | 1.2132 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A | #N/A | #N/A | #N/A |  |  | #N/A
Food Preparation0 |  | 8 |  | 0 | NA | NA | 0 | 0 |  | 0 | 0 | 0 | 0 |  |  | 0 |  |  |  | 0 |  |  | 0 |  |  |  | 0 | 0 | 0 | 0 |  |  | 0
Food Preparation0 |  | 8 |  | 0 | NA | NA | 0 | 0 |  | 0 | 0 | 0 | 0 |  |  | 0 |  |  |  | 0 |  |  | 0 |  |  |  | 0 | 0 | 0 | 0 |  |  | 0
| Gymnasium/Fitness-Fitness Area |  | 0.9099
Gymnasium/Fitness-Fitness Area535 |  | 126 |  | 535 | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A | #N/A | 0.9099 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A | #N/A | #N/A | #N/A |  |  | #N/A
Gymnasium/Fitness-Fitness Area0 |  | 126 |  | 0 | NA | NA | 0 | 0 |  | 0 | 0 | 0 | 0 |  |  | 0 |  |  |  | 0 |  |  | 0 |  |  |  | 0 | 0 | 0 | 0 |  |  | 0
Gymnasium/Fitness-Fitness Area0 |  | 126 |  | 0 | NA | NA | 0 | 0 |  | 0 | 0 | 0 | 0 |  |  | 0 |  |  |  | 0 |  |  | 0 |  |  |  | 0 | 0 | 0 | 0 |  |  | 0
| Highway Lodging Guest Rooms |  | 1.1121
Highway Lodging Guest Rooms524 |  | 75.01 |  | 524 | indirect Wall Scounce | CF | 18 | 2 |  | 39 | 10000 | 0.0043419 | 0.16933 |  |  | 0.38934 |  |  |  | 0.26703 |  |  | 0.13634 |  |  |  | 0.025183 | 0.16152 | 50000 | 0 |  |  | 0
Highway Lodging Guest Rooms520 |  | 75.01 |  | 520 | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A | #N/A | 0.94277 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A | #N/A | #N/A | #N/A |  |  | #N/A
Highway Lodging Guest Rooms0 |  | 75.01 |  | 0 | NA | NA | 0 | 0 |  | 0 | 0 | 0 | 0 |  |  | 0 |  |  |  | 0 |  |  | 0 |  |  |  | 0 | 0 | 0 | 0 |  |  | 0
| Hospital - Laundry/Washing |  | 0.6066
Hospital - Laundry-washing530 |  | 82 |  | 530 | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A | #N/A | 0.6066 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A | #N/A | #N/A | #N/A |  |  | #N/A
Hospital - Laundry-washing0 |  | 82 |  | 0 | NA | NA | 0 | 0 |  | 0 | 0 | 0 | 0 |  |  | 0 |  |  |  | 0 |  |  | 0 |  |  |  | 0 | 0 | 0 | 0 |  |  | 0
Hospital - Laundry-washing0 |  | 82 |  | 0 | NA | NA | 0 | 0 |  | 0 | 0 | 0 | 0 |  |  | 0 |  |  |  | 0 |  |  | 0 |  |  |  | 0 | 0 | 0 | 0 |  |  | 0
| Library |  | 1.2132
Library535 |  | 19 |  | 535 | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A | #N/A | 0.61671 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A | #N/A | #N/A | #N/A |  |  | #N/A
Library520 |  | 19 |  | 520 | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A | #N/A | 0.26286 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A | #N/A | #N/A | #N/A |  |  | #N/A
Library529 |  | 19 |  | 529 | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A | #N/A | 0.32352 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A | #N/A | #N/A | #N/A |  |  | #N/A
| Lobby |  | 1.3143
Lobby534-2 |  | 20.1 |  | 534-2 | Linear Wall Cove | FL | 32 | 1 |  | 29 | 36000 | 0.0090912 | 0.26364 |  |  | 3.4547 |  |  |  | 0.52612 |  |  | 0.030456 |  |  |  | 0.049699 | 0.080155 | 50000 | 0.27274 |  |  | 0.55911
Lobby523 |  | 20.1 |  | 523 | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A | #N/A | 0.96075 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A | #N/A | #N/A | #N/A |  |  | #N/A
Lobby521 |  | 20.1 |  | 521 | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A | #N/A | 0.089903 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A | #N/A | #N/A | #N/A |  |  | #N/A
| Lobby - Hotel |  | 1.1121 | [26 empty] | #N/A
Lobby - Hotel535 |  | 79 |  | 535 | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A | #N/A | 0.027831 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A | #N/A | #N/A | #N/A |  |  | #N/A
Lobby - Hotel572 |  | 79 |  | 572 | Downlight open | TH | 75 | 1 |  | 75 | 850 | 0.012939 | 0.97043 |  |  | 0.361 |  |  |  | 0.79575 |  |  | 0.27664 |  |  |  | 0.30407 | 0.5807 | 0 | 0 |  |  | 0
Lobby - Hotel524 |  | 79 |  | 524 | indirect Wall Scounce | CF | 18 | 2 |  | 39 | 10000 | 0.002919 | 0.11384 |  |  | 0.26175 |  |  |  | 0.17952 |  |  | 0.091658 |  |  |  | 0.01693 | 0.10859 | 50000 | 0 |  |  | 0
| Lounge/Recreation - Break room |  | 1.2132
Lounge/Recreation - Breakroom537-1 |  | 9 |  | 537-1 | Linear WW Open | FL | 32 | 1 |  | 29 | 36000 | 0.013184 | 0.38234 |  |  | 1.3655 |  |  |  | 0.81082 |  |  | 0.044167 |  |  |  | 0.072074 | 0.11624 | 50000 | 0.39552 |  |  | 0.81082
Lounge/Recreation - Breakroom572 |  | 9 |  | 0 | NA | NA | 0 | 0 |  | 0 | 0 | 0 | 0 |  |  | 0 |  |  |  | 0 |  |  | 0 |  |  |  | 0 | 0 | 0 | 0 |  |  | 0
Lounge/Recreation - Breakroom521 |  | 9 |  | 521 | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A | #N/A | 0.83086 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A | #N/A | #N/A | #N/A |  |  | #N/A
| Office-Enclosed |  | 1.1121
Office-Enclosed535 |  | 25 |  | 535 | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A | #N/A | 0.78498 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A | #N/A | #N/A | #N/A |  |  | #N/A
Office-Enclosed539 |  | 25 |  | 539 | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A | #N/A | 0.12415 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A | #N/A | #N/A | #N/A |  |  | #N/A
Office-Enclosed537-2 |  | 25 |  | 537-2 | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A | #N/A | 0.20296 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A | #N/A | #N/A | #N/A |  |  | #N/A
| Office - Open Plan (Including Other) |  | 1.1121
Office - Open Plan (Including Other)535 |  | 27 |  | 535 | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A | #N/A | 0.89005 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A | #N/A | #N/A | #N/A |  |  | #N/A
Office - Open Plan (Including Other)539 |  | 27 |  | 539 | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A | #N/A | 0.15837 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A | #N/A | #N/A | #N/A |  |  | #N/A
Office - Open Plan (Including Other)524 |  | 27 |  | 524 | indirect Wall Scounce | CF | 18 | 2 |  | 39 | 10000 | 0.001633 | 0.063686 |  |  | 0.14643 |  |  |  | 0.10043 |  |  | 0.051276 |  |  |  | 0.0094713 | 0.060747 | 50000 | 0 |  |  | 0
| Restrooms |  | 0.9099
Restrooms521 |  | 12 |  | 521 | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A | #N/A | 0.42931 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A | #N/A | #N/A | #N/A |  |  | #N/A
Restrooms537-1 |  | 12 |  | 537-1 | Linear WW Open | FL | 32 | 1 |  | 29 | 36000 | 0.011882 | 0.34458 |  |  | 1.2306 |  |  |  | 0.73075 |  |  | 0.039805 |  |  |  | 0.064957 | 0.10476 | 50000 | 0.35646 |  |  | 0.73075
Restrooms524 |  | 12 |  | 524 | indirect Wall Scounce | CF | 18 | 2 |  | 39 | 10000 | 0.0034873 | 0.136 |  |  | 0.3127 |  |  |  | 0.21447 |  |  | 0.1095 |  |  |  | 0.020226 | 0.12973 | 50000 | 0 |  |  | 0
| Retail - Sales Area |  | 1.7187
Retail - Sales Area535 |  | 97 |  | 535 | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A | #N/A | 0.97004 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A | #N/A | #N/A | #N/A |  |  | #N/A
Retail - Sales Area541 |  | 97 |  | 541 | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A | #N/A | 0.74866 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A | #N/A | #N/A | #N/A |  |  | #N/A
Retail - Sales Area572 |  | 97 |  | 0 | NA | NA | 0 | 0 |  | 0 | 0 | 0 | 0 |  |  | 0 |  |  |  | 0 |  |  | 0 |  |  |  | 0 | 0 | 0 | 0 |  |  | 0
| Stairway |  | 0.6066
Stairway530 |  | 11 |  | 530 | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A | #N/A | 0.6066 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A | #N/A | #N/A | #N/A |  |  | #N/A
Stairway0 |  | 11 |  | 0 | NA | NA | 0 | 0 |  | 0 | 0 | 0 | 0 |  |  | 0 |  |  |  | 0 |  |  | 0 |  |  |  | 0 | 0 | 0 | 0 |  |  | 0
Stairway0 |  | 11 |  | 0 | NA | NA | 0 | 0 |  | 0 | 0 | 0 | 0 |  |  | 0 |  |  |  | 0 |  |  | 0 |  |  |  | 0 | 0 | 0 | 0 |  |  | 0
| Storage |  | 0.8088
Storage530 |  | 41 |  | 530 | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A | #N/A | 0.8088 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A | #N/A | #N/A | #N/A |  |  | #N/A
Storage553 |  | 41 |  | 0 | NA | NA | 0 | 0 |  | 0 | 0 | 0 | 0 |  |  | 0 |  |  |  | 0 |  |  | 0 |  |  |  | 0 | 0 | 0 | 0 |  |  | 0
Storage0 |  | 41 |  | 0 | NA | NA | 0 | 0 |  | 0 | 0 | 0 | 0 |  |  | 0 |  |  |  | 0 |  |  | 0 |  |  |  | 0 | 0 | 0 | 0 |  |  | 0
1 FL linear fluorescent, CF compact fluorescent, MH metal halide
Interior Lighting Costs by Space Type, North Carolina Base Code
| Space Type Lighting Descriptions and Cost Parameters | [14 empty] | New Construction Cost | [6 empty] | Lamp Replacement Cost | [5 empty] | Ballast Replacement Cost
North Carolina Base Code Lookup Values | 2009 Space Types | 90.1 Lighting Subcommittee Model Number | Space Type Lighting Power Allowance W/ft2 | Fixture ID Number | Fixture Type | Lamp Type1 | Lamp Wattage | Number of Lamps | Not Used | Fixture Watts | Lamp Life Hours | Quantity of Fixtures/ft2 | Fixture Watts/ft2 | not used | not used | Fixture Cost/ft2 | not used | not used | not used | Labor Cost $/ft2 | Not Used | Not Used | Lamp Cost $/ft2 | Not Used | Not Used | Not Used | Labor Cost/ft2 | Total $/ft2 | Ballast Life Hours | Ballast Cost, $/ft2 | Not Used | Not Used | Labor Cost/ft2 | Not Used | Not Used
Classroom/Lecture/Training | Classroom/Lecture/Training |  | 1.155
Classroom/Lecture/Training535 |  | 3.1 |  | 535 | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A | #N/A | 0.95026 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A | #N/A | #N/A | #N/A |  |  | #N/A
Classroom/Lecture/Training537-2 |  | 3.1 |  | 537-2 | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A | #N/A | 0.20474 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A | #N/A | #N/A | #N/A |  |  | #N/A
Classroom/Lecture/Training0 |  | 3.1 |  | 0 | NA | NA | 0 | 0 |  | 0 | 0 | 0 | 0 |  |  | 0 |  |  |  | 0 |  |  | 0 |  |  |  | 0 | 0 | 0 | 0 |  |  | 0
| Conference/Meeting/Multipurpose |  | 1.0725
Conference/Meeting/Multipurpose535 |  | 31 |  | 535 | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A | #N/A | 0.54782 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A | #N/A | #N/A | #N/A |  |  | #N/A
Conference/Meeting/Multipurpose537-1 |  | 31 |  | 537-1 | Linear WW Open | FL | 32 | 1 |  | 29 | 36000 | 0.010755 | 0.31188 |  |  | 1.1139 |  |  |  | 0.66141 |  |  | 0.036028 |  |  |  | 0.058793 | 0.09482 | 50000 | 0.32264 |  |  | 0.66141
Conference/Meeting/Multipurpose511 |  | 31 |  | 511 | Downlight open - flood | PAR | 60 | 1 |  | 60 | 4200 | 0.0035465 | 0.21279 |  |  | 0.13151 |  |  |  | 0.21811 |  |  | 0.075825 |  |  |  | 0.01032 | 0.086146 | 0 | 0 |  |  | 0
| Corridor/Transition |  | 0.4125
Corridor/Transition530 |  | 2 |  | 530 | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A | #N/A | 0.23725 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A | #N/A | #N/A | #N/A |  |  | #N/A
Corridor/Transition537-2 |  | 2 |  | 537-2 | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A | #N/A | 0.17525 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A | #N/A | #N/A | #N/A |  |  | #N/A
Corridor/Transition0 |  | 2 |  | 0 | NA | NA | 0 | 0 |  | 0 | 0 | 0 | 0 |  |  | 0 |  |  |  | 0 |  |  | 0 |  |  |  | 0 | 0 | 0 | 0 |  |  | 0
| Dining Area |  | 0.7425
Dining Area531 |  | 6 |  | 531 | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A | #N/A | 0.5695 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A | #N/A | #N/A | #N/A |  |  | #N/A
Dining Area524 |  | 6 |  | 524 | indirect Wall Scounce | CF | 18 | 2 |  | 39 | 10000 | 0.004436 | 0.173 |  |  | 0.39777 |  |  |  | 0.27281 |  |  | 0.13929 |  |  |  | 0.025729 | 0.16502 | 50000 | 0 |  |  | 0
Dining Area0 |  | 6
| Electrical/Mechanical |  | 1.2375
Electrical/Mechanical538 |  | 4 |  | 538 | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A | #N/A | 1.2375 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A | #N/A | #N/A | #N/A |  |  | #N/A
Electrical/Mechanical0 |  | 4 |  | 0 | NA | NA | 0 | 0 |  | 0 | 0 | 0 | 0 |  |  | 0 |  |  |  | 0 |  |  | 0 |  |  |  | 0 | 0 | 0 | 0 |  |  | 0
Electrical/Mechanical0 |  | 4 |  | 0 | NA | NA | 0 | 0 |  | 0 | 0 | 0 | 0 |  |  | 0 |  |  |  | 0 |  |  | 0 |  |  |  | 0 | 0 | 0 | 0 |  |  | 0
| Food Preparation |  | 0.99
Food Preparation530 |  | 8 |  | 530 | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A | #N/A | 0.99 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A | #N/A | #N/A | #N/A |  |  | #N/A
Food Preparation0 |  | 8 |  | 0 | NA | NA | 0 | 0 |  | 0 | 0 | 0 | 0 |  |  | 0 |  |  |  | 0 |  |  | 0 |  |  |  | 0 | 0 | 0 | 0 |  |  | 0
Food Preparation0 |  | 8 |  | 0 | NA | NA | 0 | 0 |  | 0 | 0 | 0 | 0 |  |  | 0 |  |  |  | 0 |  |  | 0 |  |  |  | 0 | 0 | 0 | 0 |  |  | 0
| Gymnasium/Fitness-Fitness Area |  | 0.7425
Gymnasium/Fitness-Fitness Area535 |  | 126 |  | 535 | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A | #N/A | 0.7425 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A | #N/A | #N/A | #N/A |  |  | #N/A
Gymnasium/Fitness-Fitness Area0 |  | 126 |  | 0 | NA | NA | 0 | 0 |  | 0 | 0 | 0 | 0 |  |  | 0 |  |  |  | 0 |  |  | 0 |  |  |  | 0 | 0 | 0 | 0 |  |  | 0
Gymnasium/Fitness-Fitness Area0 |  | 126 |  | 0 | NA | NA | 0 | 0 |  | 0 | 0 | 0 | 0 |  |  | 0 |  |  |  | 0 |  |  | 0 |  |  |  | 0 | 0 | 0 | 0 |  |  | 0
| Highway Lodging Guest Rooms |  | 0.9075
Highway Lodging Guest Rooms524 |  | 75.01 |  | 524 | indirect Wall Scounce | CF | 18 | 2 |  | 39 | 10000 | 0.0035431 | 0.13818 |  |  | 0.31771 |  |  |  | 0.2179 |  |  | 0.11125 |  |  |  | 0.02055 | 0.1318 | 50000 | 0 |  |  | 0
Highway Lodging Guest Rooms520 |  | 75.01 |  | 520 | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A | #N/A | 0.76932 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A | #N/A | #N/A | #N/A |  |  | #N/A
Highway Lodging Guest Rooms0 |  | 75.01 |  | 0 | NA | NA | 0 | 0 |  | 0 | 0 | 0 | 0 |  |  | 0 |  |  |  | 0 |  |  | 0 |  |  |  | 0 | 0 | 0 | 0 |  |  | 0
| Hospital - Laundry/Washing |  | 0.495
Hospital - Laundry-washing530 |  | 82 |  | 530 | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A | #N/A | 0.495 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A | #N/A | #N/A | #N/A |  |  | #N/A
Hospital - Laundry-washing0 |  | 82 |  | 0 | NA | NA | 0 | 0 |  | 0 | 0 | 0 | 0 |  |  | 0 |  |  |  | 0 |  |  | 0 |  |  |  | 0 | 0 | 0 | 0 |  |  | 0
Hospital - Laundry-washing0 |  | 82 |  | 0 | NA | NA | 0 | 0 |  | 0 | 0 | 0 | 0 |  |  | 0 |  |  |  | 0 |  |  | 0 |  |  |  | 0 | 0 | 0 | 0 |  |  | 0
| Library |  | 0.99
Library535 |  | 19 |  | 535 | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A | #N/A | 0.50325 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A | #N/A | #N/A | #N/A |  |  | #N/A
Library520 |  | 19 |  | 520 | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A | #N/A | 0.2145 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A | #N/A | #N/A | #N/A |  |  | #N/A
Library529 |  | 19 |  | 529 | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A | #N/A | 0.264 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A | #N/A | #N/A | #N/A |  |  | #N/A
| Lobby |  | 1.0725
Lobby534-2 |  | 20.1 |  | 534-2 | Linear Wall Cove | FL | 32 | 1 |  | 29 | 36000 | 0.0074186 | 0.21514 |  |  | 2.8191 |  |  |  | 0.42933 |  |  | 0.024852 |  |  |  | 0.040556 | 0.065408 | 50000 | 0.22256 |  |  | 0.45625
Lobby523 |  | 20.1 |  | 523 | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A | #N/A | 0.784 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A | #N/A | #N/A | #N/A |  |  | #N/A
Lobby521 |  | 20.1 |  | 521 | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A | #N/A | 0.073363 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A | #N/A | #N/A | #N/A |  |  | #N/A
| Lobby - Hotel |  | 0.9075 | [26 empty] | #N/A
Lobby - Hotel535 |  | 79 |  | 535 | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A | #N/A | 0.02271 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A | #N/A | #N/A | #N/A |  |  | #N/A
Lobby - Hotel572 |  | 79 |  | 572 | Downlight open | TH | 75 | 1 |  | 75 | 850 | 0.010559 | 0.79189 |  |  | 0.29458 |  |  |  | 0.64935 |  |  | 0.22574 |  |  |  | 0.24813 | 0.47387 | 0 | 0 |  |  | 0
Lobby - Hotel524 |  | 79 |  | 524 | indirect Wall Scounce | CF | 18 | 2 |  | 39 | 10000 | 0.002382 | 0.092898 |  |  | 0.21359 |  |  |  | 0.14649 |  |  | 0.074795 |  |  |  | 0.013816 | 0.088611 | 50000 | 0 |  |  | 0
| Lounge/Recreation - Break room |  | 0.99
Lounge/Recreation - Breakroom537-1 |  | 9 |  | 537-1 | Linear WW Open | FL | 32 | 1 |  | 29 | 36000 | 0.010759 | 0.312 |  |  | 1.1143 |  |  |  | 0.66165 |  |  | 0.036041 |  |  |  | 0.058814 | 0.094855 | 50000 | 0.32276 |  |  | 0.66165
Lounge/Recreation - Breakroom572 |  | 9 |  | 0 | NA | NA | 0 | 0 |  | 0 | 0 | 0 | 0 |  |  | 0 |  |  |  | 0 |  |  | 0 |  |  |  | 0 | 0 | 0 | 0 |  |  | 0
Lounge/Recreation - Breakroom521 |  | 9 |  | 521 | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A | #N/A | 0.678 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A | #N/A | #N/A | #N/A |  |  | #N/A
| Office-Enclosed |  | 0.9075
Office-Enclosed535 |  | 25 |  | 535 | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A | #N/A | 0.64057 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A | #N/A | #N/A | #N/A |  |  | #N/A
Office-Enclosed539 |  | 25 |  | 539 | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A | #N/A | 0.10131 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A | #N/A | #N/A | #N/A |  |  | #N/A
Office-Enclosed537-2 |  | 25 |  | 537-2 | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A | #N/A | 0.16562 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A | #N/A | #N/A | #N/A |  |  | #N/A
| Office - Open Plan (Including Other) |  | 0.9075
Office - Open Plan (Including Other)535 |  | 27 |  | 535 | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A | #N/A | 0.7263 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A | #N/A | #N/A | #N/A |  |  | #N/A
Office - Open Plan (Including Other)539 |  | 27 |  | 539 | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A | #N/A | 0.12923 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A | #N/A | #N/A | #N/A |  |  | #N/A
Office - Open Plan (Including Other)524 |  | 27 |  | 524 | indirect Wall Scounce | CF | 18 | 2 |  | 39 | 10000 | 0.0013326 | 0.051969 |  |  | 0.11949 |  |  |  | 0.081952 |  |  | 0.041842 |  |  |  | 0.0077288 | 0.049571 | 50000 | 0 |  |  | 0
| Restrooms |  | 0.7425
Restrooms521 |  | 12 |  | 521 | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A | #N/A | 0.35033 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A | #N/A | #N/A | #N/A |  |  | #N/A
Restrooms537-1 |  | 12 |  | 537-1 | Linear WW Open | FL | 32 | 1 |  | 29 | 36000 | 0.0096961 | 0.28119 |  |  | 1.0042 |  |  |  | 0.59631 |  |  | 0.032482 |  |  |  | 0.053006 | 0.085488 | 50000 | 0.29088 |  |  | 0.59631
Restrooms524 |  | 12 |  | 524 | indirect Wall Scounce | CF | 18 | 2 |  | 39 | 10000 | 0.0028457 | 0.11098 |  |  | 0.25517 |  |  |  | 0.17501 |  |  | 0.089355 |  |  |  | 0.016505 | 0.10586 | 50000 | 0 |  |  | 0
| Retail - Sales Area |  | 1.4025
Retail - Sales Area535 |  | 97 |  | 535 | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A | #N/A | 0.79157 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A | #N/A | #N/A | #N/A |  |  | #N/A
Retail - Sales Area541 |  | 97 |  | 541 | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A | #N/A | 0.61093 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A | #N/A | #N/A | #N/A |  |  | #N/A
Retail - Sales Area572 |  | 97 |  | 0 | NA | NA | 0 | 0 |  | 0 | 0 | 0 | 0 |  |  | 0 |  |  |  | 0 |  |  | 0 |  |  |  | 0 | 0 | 0 | 0 |  |  | 0
| Stairway |  | 0.495
Stairway530 |  | 11 |  | 530 | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A | #N/A | 0.495 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A | #N/A | #N/A | #N/A |  |  | #N/A
Stairway0 |  | 11 |  | 0 | NA | NA | 0 | 0 |  | 0 | 0 | 0 | 0 |  |  | 0 |  |  |  | 0 |  |  | 0 |  |  |  | 0 | 0 | 0 | 0 |  |  | 0
Stairway0 |  | 11 |  | 0 | NA | NA | 0 | 0 |  | 0 | 0 | 0 | 0 |  |  | 0 |  |  |  | 0 |  |  | 0 |  |  |  | 0 | 0 | 0 | 0 |  |  | 0
| Storage |  | 0.66
Storage530 |  | 41 |  | 530 | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A | #N/A | 0.66 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A | #N/A | #N/A | #N/A |  |  | #N/A
Storage553 |  | 41 |  | 0 | NA | NA | 0 | 0 |  | 0 | 0 | 0 | 0 |  |  | 0 |  |  |  | 0 |  |  | 0 |  |  |  | 0 | 0 | 0 | 0 |  |  | 0
Storage0 |  | 41 |  | 0 | NA | NA | 0 | 0 |  | 0 | 0 | 0 | 0 |  |  | 0 |  |  |  | 0 |  |  | 0 |  |  |  | 0 | 0 | 0 | 0 |  |  | 0
1 FL linear fluorescent, CF compact fluorescent, MH metal halide
Interior Lighting Costs by Space Type, 2012
| Space Type Lighting Descriptions and Cost Parameters | [18 empty] | New Construction Cost |  |  | Lamp Replacement Cost | [5 empty] | Ballast Replacement Cost
IECC 2012 Lookup Values | 2012 Space Types | Model Number | Lighting Power Allowance, LPD, W/ft2 | Fixtures - ID Number | Fixture type | Lamp Type | Lamp Wattage | Number of Lamps |  | Fixture Watts | Lamp Life, Hours | Quantity of Fixtures/ft2 | Fixture Watts/ft2 |  |  | Fixture Cost only, $/ft2 | not used | not used | not used | Labor Cost $/ft2 |  |  | Lamp Cost, $/ft2 | Labor Crew Type |  |  | Labor Cost/ft2 | Total $/ft2 | Ballast Life Hours | Ballast Cost, $/ft2 | Not Used | Not Used | Labor Cost/ft2
Classroom/Lecture/Training | Classroom/Lecture/Training |  | 1.1656 | [25 empty] | 0 | #N/A |  |  | 0
Classroom/Lecture/Training535 |  | 3.1 |  | 535 | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A | #N/A | 0.8688 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A | #N/A | #N/A | #N/A |  |  | #N/A
Classroom/Lecture/Training521 |  | 3.1 |  | 521 | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A | #N/A | 0.1448 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A | #N/A | #N/A | #N/A |  |  | #N/A
Classroom/Lecture/Training0 |  | 3.1 |  | 0 | NA | NA | 0 | 0 |  | 0 | 0 | 0 | 0 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A | #N/A | #N/A | 0 |  |  | 0
Classroom/Lecture/Training537-1 |  | 3.1 |  | 537-1 | Linear WW Open | FL | 32 | #N/A |  | #N/A | #N/A | #N/A | 0.152 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A | #N/A | #N/A | #N/A |  |  | #N/A
| Conference/Meeting/Multipurpose |  | 1.1562
Conference/Meeting/Multipurpose535 |  | 31 |  | 535 | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A | #N/A | 0.56805 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A | #N/A | #N/A | #N/A |  |  | #N/A
Conference/Meeting/Multipurpose511 |  | 31 |  | 511 | Downlight open - flood | PAR | 60 | #N/A |  | #N/A | #N/A | #N/A | 0.4109 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A | #N/A | #N/A | #N/A |  |  | #N/A
Conference/Meeting/Multipurpose0 |  | 31 |  | 0 | NA | NA | 0 | 0 |  | 0 | 0 | 0 | 0 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A | #N/A | #N/A | 0 |  |  | 0
Conference/Meeting/Multipurpose527-1 |  | 31 |  | 527-1 | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A | #N/A | 0.17725 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A | #N/A | #N/A | #N/A |  |  | #N/A
| Corridor/Transition |  | 0.6204
Corridor/Transition521 |  | 2 |  | 521 | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A | #N/A | 0.6204 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A | #N/A | #N/A | #N/A |  |  | #N/A
Corridor/Transition0 |  | 2 |  | 0 | NA | NA | 0 | 0 |  | 0 | 0 | 0 | 0 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A | #N/A | #N/A | 0 |  |  | 0
Corridor/Transition0 |  | 2 |  | 0 | NA | NA | 0 | 0 |  | 0 | 0 | 0 | 0 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A | #N/A | #N/A | 0 |  |  | 0
Corridor/Transition527-2 |  | 2 |  | 0 | NA | NA | 0 | 0 |  | 0 | 0 | 0 | 9.4655e-08 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A | #N/A | #N/A | 0 |  |  | 0
| Dining Area |  | 0.611
Dining Area535 |  | 6 |  | 535 | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A | #N/A | 0.22552 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A | #N/A | #N/A | #N/A |  |  | #N/A
Dining Area521 |  | 6 |  | 521 | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A | #N/A | 0.11059 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A | #N/A | #N/A | #N/A |  |  | #N/A
Dining Area0 |  | 6 |  | 0 | NA | NA | 0 | 0 |  | 0 | 0 | 0 | 0 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A | #N/A | #N/A | 0 |  |  | 0
Dining Area537-1 |  | 6 |  | 537-1 | Linear WW Open | FL | 32 | #N/A |  | #N/A | #N/A | #N/A | 0.27489 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A | #N/A | #N/A | #N/A |  |  | #N/A
| Electrical/Mechanical |  | 0.893
Electrical/Mechanical538 |  | 4 |  | 538 | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A | #N/A | 0.893 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A | #N/A | #N/A | #N/A |  |  | #N/A
Electrical/Mechanical0 |  | 4 |  | 0 | NA | NA | 0 | 0 |  | 0 | 0 | 0 | 0 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A | #N/A | #N/A | 0 |  |  | 0
Electrical/Mechanical0 |  | 4 |  | 0 | NA | NA | 0 | 0 |  | 0 | 0 | 0 | 0 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A | #N/A | #N/A | 0 |  |  | 0
Electrical/Mechanical0 |  | 4 |  | 0 | NA | NA | 0 | 0 |  | 0 | 0 | 0 | 9.3833e-08 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A | #N/A | #N/A | 0 |  |  | 0
| Food Preparation |  | 0.9306
Food Preparation530 |  | 8 |  | 530 | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A | #N/A | 0.9306 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A | #N/A | #N/A | #N/A |  |  | #N/A
Food Preparation0 |  | 8 |  | 0 | NA | NA | 0 | 0 |  | 0 | 0 | 0 | 0 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A | #N/A | #N/A | 0 |  |  | 0
Food Preparation0 |  | 8 |  | 0 | NA | NA | 0 | 0 |  | 0 | 0 | 0 | 0 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A | #N/A | #N/A | 0 |  |  | 0
Food Preparation0 |  | 8 |  | 0 | NA | NA | 0 | 0 |  | 0 | 0 | 0 | 9.3942e-08 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A | #N/A | #N/A | 0 |  |  | 0
| Gymnasium/Fitness-Fitness Area |  | 0.6768
Gymnasium/Fitness-Fitness Area535 |  | 126 |  | 535 | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A | #N/A | 0.6768 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A | #N/A | #N/A | #N/A |  |  | #N/A
Gymnasium/Fitness-Fitness Area0 |  | 126 |  | 0 | NA | NA | 0 | 0 |  | 0 | 0 | 0 | 0 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A | #N/A | #N/A | 0 |  |  | 0
Gymnasium/Fitness-Fitness Area0 |  | 126 |  | 0 | NA | NA | 0 | 0 |  | 0 | 0 | 0 | 0 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A | #N/A | #N/A | 0 |  |  | 0
Gymnasium/Fitness-Fitness Area0 |  | 126 |  | 0 | NA | NA | 0 | 0 |  | 0 | 0 | 0 | 9.3595e-08 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A | #N/A | #N/A | 0 |  |  | 0
| Highway Lodging Guest Rooms |  | 0.705
Highway Lodging Guest Rooms529 |  | 75.01 |  | 529 | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A | #N/A | 0.39849 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A | #N/A | #N/A | #N/A |  |  | #N/A
Highway Lodging Guest Rooms520 |  | 75.01 |  | 520 | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A | #N/A | 0.30651 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A | #N/A | #N/A | #N/A |  |  | #N/A
Highway Lodging Guest Rooms0 |  | 75.01 |  | 0 | NA | NA | 0 | 0 |  | 0 | 0 | 0 | 0 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A | #N/A | #N/A | 0 |  |  | 0
Highway Lodging Guest Rooms0 |  | 75.01 |  | 0 | NA | NA | 0 | 0 |  | 0 | 0 | 0 | 9.3695e-08 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A | #N/A | #N/A | 0 |  |  | 0
| Hospital - Laundry/Washing |  | 0.564
Hospital - Laundry-washing530 |  | 82 |  | 530 | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A | #N/A | 0.564 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A | #N/A | #N/A | #N/A |  |  | #N/A
Hospital - Laundry-washing0 |  | 82 |  | 0 | NA | NA | 0 | 0 |  | 0 | 0 | 0 | 0 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A | #N/A | #N/A | 0 |  |  | 0
Hospital - Laundry-washing0 |  | 82 |  | 0 | NA | NA | 0 | 0 |  | 0 | 0 | 0 | 0 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A | #N/A | #N/A | 0 |  |  | 0
Hospital - Laundry-washing0 |  | 82 |  | 0 | NA | NA | 0 | 0 |  | 0 | 0 | 0 | 9.4721e-08 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A | #N/A | #N/A | 0 |  |  | 0
| Library |  | 0.8742
Library535 |  | 19 |  | 535 | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A | #N/A | 0.3692 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A | #N/A | #N/A | #N/A |  |  | #N/A
Library520 |  | 19 |  | 520 | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A | #N/A | 0.505 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A | #N/A | #N/A | #N/A |  |  | #N/A
Library0 |  | 19 |  | 0 | NA | NA | 0 | 0 |  | 0 | 0 | 0 | 0 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A | #N/A | #N/A | 0 |  |  | 0
Library0 |  | 19 |  | 0 | NA | NA | 0 | 0 |  | 0 | 0 | 0 | 9.388e-08 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A | #N/A | #N/A | 0 |  |  | 0
| Lounge/Recreation - Break room |  | 0.6862
Lounge/Recreation - Breakroom521 |  | 9 |  | 521 | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A | #N/A | 0.40897 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A | #N/A | #N/A | #N/A |  |  | #N/A
Lounge/Recreation - Breakroom0 |  | 9 |  | 0 | NA | NA | 0 | 0 |  | 0 | 0 | 0 | 0 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A | #N/A | #N/A | 0 |  |  | 0
Lounge/Recreation - Breakroom0 |  | 9 |  | 0 | NA | NA | 0 | 0 |  | 0 | 0 | 0 | 0 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A | #N/A | #N/A | 0 |  |  | 0
Lounge/Recreation - Breakroom527-2 |  | 9 |  | 527-2 | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A | #N/A | 0.27723 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A | #N/A | #N/A | #N/A |  |  | #N/A
| Lobby |  | 0.846
Lobby523 |  | 20.1 |  | 523 | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A | #N/A | 0.47187 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A | #N/A | #N/A | #N/A |  |  | #N/A
Lobby521 |  | 20.1 |  | 521 | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A | #N/A | 0.22239 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A | #N/A | #N/A | #N/A |  |  | #N/A
Lobby0 |  | 20.1 |  | 0 | NA | NA | 0 | 0 |  | 0 | 0 | 0 | 0 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A | #N/A | #N/A | 0 |  |  | 0
Lobby534-2 |  | 20.1 |  | 534-2 | Linear Wall Cove | FL | 32 | #N/A |  | #N/A | #N/A | #N/A | 0.15174 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A | #N/A | #N/A | #N/A |  |  | #N/A
| Office-Enclosed |  | 1.0434
Office-Enclosed531 |  | 25 |  | 531 | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A | #N/A | 0.63454 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A | #N/A | #N/A | #N/A |  |  | #N/A
Office-Enclosed539 |  | 25 |  | 539 | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A | #N/A | 0.17506 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A | #N/A | #N/A | #N/A |  |  | #N/A
Office-Enclosed0 |  | 25 |  | 0 | NA | NA | 0 | 0 |  | 0 | 0 | 0 | 0 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A | #N/A | #N/A | 0 |  |  | 0
Office-Enclosed537-1 |  | 25 |  | 537-1 | Linear WW Open | FL | 32 | #N/A |  | #N/A | #N/A | #N/A | 0.2338 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A | #N/A | #N/A | #N/A |  |  | #N/A
| Office - Open Plan (Including Other) |  | 0.9212
Office - Open Plan (Including Other)535 |  | 27 |  | 535 | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A | #N/A | 0.67862 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A | #N/A | #N/A | #N/A |  |  | #N/A
Office - Open Plan (Including Other)539 |  | 27 |  | 539 | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A | #N/A | 0.091203 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A | #N/A | #N/A | #N/A |  |  | #N/A
Office - Open Plan (Including Other)0 |  | 27 |  | 0 | NA | NA | 0 | 0 |  | 0 | 0 | 0 | 0 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A | #N/A | #N/A | 0 |  |  | 0
Office - Open Plan (Including Other)537-1 |  | 27 |  | 537-1 | Linear WW Open | FL | 32 | #N/A |  | #N/A | #N/A | #N/A | 0.15138 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A | #N/A | #N/A | #N/A |  |  | #N/A
| Restrooms |  | 0.9212
Restrooms604 |  | 12 |  | 604 | Wall Mounted Linear Direct/Indirect | FL | 32 | #N/A |  | #N/A | #N/A | #N/A | 0.27108 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A | #N/A | #N/A | #N/A |  |  | #N/A
Restrooms520 |  | 12 |  | 520 | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A | #N/A | 0.41811 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A | #N/A | #N/A | #N/A |  |  | #N/A
Restrooms0 |  | 12 |  | 0 | NA | NA | 0 | 0 |  | 0 | 0 | 0 | 0 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A | #N/A | #N/A | 0 |  |  | 0
Restrooms534-2 |  | 12 |  | 534-2 | Linear Wall Cove | FL | 32 | #N/A |  | #N/A | #N/A | #N/A | 0.23201 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A | #N/A | #N/A | #N/A |  |  | #N/A
| Retail - Sales Area |  | 1.5792
Retail - Sales Area535 |  | 97 |  | 535 | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A | #N/A | 0.95657 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A | #N/A | #N/A | #N/A |  |  | #N/A
Retail - Sales Area541 |  | 97 |  | 541 | #N/A |  | #N/A | #N/A |  | #N/A | #N/A | #N/A | 0.47376 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A | #N/A | #N/A | #N/A |  |  | #N/A
Retail - Sales Area0 |  | 97 |  | 0 | NA | NA | 0 | 0 |  | 0 | 0 | 0 | 0 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A | #N/A | #N/A | 0 |  |  | 0
Retail - Sales Area537-1 |  | 97 |  | 537-1 | Linear WW Open | FL | 32 | #N/A |  | #N/A | #N/A | #N/A | 0.14887 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A | #N/A | #N/A | #N/A |  |  | #N/A
| Stairway |  | 0.6486
Stairway530 |  | 11 |  | 530 | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A | #N/A | 0.34993 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A | #N/A | #N/A | #N/A |  |  | #N/A
Stairway602 |  | 11 |  | 602 | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A | #N/A | 0.29867 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A | #N/A | #N/A | #N/A |  |  | #N/A
Stairway0 |  | 11 |  | 0 | NA | NA | 0 | 0 |  | 0 | 0 | 0 | 0 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A | #N/A | #N/A | 0 |  |  | 0
Stairway0 |  | 11 |  | 0 | NA | NA | 0 | 0 |  | 0 | 0 | 0 | 9.3932e-08 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A | #N/A | #N/A | 0 |  |  | 0
| Storage |  | 0.5922
Storage538 |  | 41 |  | 538 | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A | #N/A | 0.5922 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A | #N/A | #N/A | #N/A |  |  | #N/A
Storage0 |  | 41 |  | 0 | NA | NA | 0 | 0 |  | 0 | 0 | 0 | 0 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A | #N/A | #N/A | 0 |  |  | 0
Storage0 |  | 41 |  | 0 | NA | NA | 0 | 0 |  | 0 | 0 | 0 | 0 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A | #N/A | #N/A | 0 |  |  | 0
Storage0 |  | 41 |  | 0 | NA | NA | 0 | 0 |  | 0 | 0 | 0 | 9.3339e-08 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A | #N/A | #N/A | 0 |  |  | 0
| Lobby - Hotel |  | 0.9964
Lobby - Hotel572 |  | 79 |  | 572 | Downlight open | TH | 75 | #N/A |  | #N/A | #N/A | #N/A | 0.84496 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A | #N/A | #N/A | #N/A |  |  | #N/A
Lobby - Hotel0 |  | 79 |  | 0 | NA | NA | 0 | 0 |  | 0 | 0 | 0 | 0 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A | #N/A | #N/A | 0 |  |  | 0
Lobby - Hotel0 |  | 79 |  | 0 | NA | NA | 0 | 0 |  | 0 | 0 | 0 | 0 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A | #N/A | #N/A | 0 |  |  | 0
Lobby - Hotel527-1 |  | 79 |  | 527-1 | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A | #N/A | 0.15144 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A | #N/A | #N/A | #N/A |  |  | #N/A
1 FL linear fluorescent, CF compact fluorescent, MH metal halide

## Int Ltg LPD Space Types SH (hidden)
| IECC Cost Effectiveness - Interior Lighting Power Density - Fixture Costs per Square Foot for Each Space Type - Small Hotel | [18 empty] | SMALL HOTEL
Adjustment Factors for LPD
| Interior lighting costs by space type and fixture type IECC 2009, North Carolina Base Code, and IECC 2012 tables. | [18 empty] | 2009 | 1.295
| 90.1-07 and 2010 in Int Ltg LPD Space Types 90_1 (same for all prototypes). Values come from "Int Ltg Comp" worksheet in this workbook. | [18 empty] | N. Carolina | 1.359
[20 empty] | 2012 | 1.129
Interior Lighting Costs by Space Type, 2009
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 31 | 32 | 33 | 34 | 35
| Space Type Lighting Descriptions and Cost Parameters | [14 empty] | New Construction Cost | [6 empty] | Lamp Replacement Cost |  |  |  |  | Ballast Replacement Cost
IECC 2009 Lookup Values | 2009 Space Types | 90.1 Lighting Subcommittee Model Number | Space Type Lighting Power Allowance W/ft2 | Fixture ID Number | Fixture Type | Lamp Type1 | Lamp Wattage | Number of Lamps | Not Used | Fixture Watts | Lamp Life Hours | Quantity of Fixtures/ft2 | Fixture Watts/ft2 | not used | not used | Fixture Cost/ft2 | not used | not used | not used | Labor Cost $/ft2 | Not Used | Not Used | Lamp Cost $/ft2 | Not Used | Not Used | Not Used | Labor Cost/ft2 | Ballast Life Hours | Ballast Cost, $/ft2 | Not Used | Not Used | Labor Cost/ft2 | Not Used | Not Used
Classroom/Lecture/Training | Classroom/Lecture/Training |  | 1.813
Classroom/Lecture/Training535 |  | 3.1 |  | 535 | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A | #N/A | 1.4916 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A | #N/A | #N/A |  |  | #N/A
Classroom/Lecture/Training537-2 |  | 3.1 |  | 537-2 | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A | #N/A | 0.32139 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A | #N/A | #N/A |  |  | #N/A
Classroom/Lecture/Training0 |  | 3.1 |  | 0 | NA | NA | 0 | 0 |  | 0 | 0 | 0 | 0 |  |  | 0 |  |  |  | 0 |  |  | 0 |  |  |  | 0 | 0 | 0 |  |  | 0
| Conference/Meeting/Multipurpose |  | 1.6835
Conference/Meeting/Multipurpose535 |  | 31 |  | 535 | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A | #N/A | 0.85992 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A | #N/A | #N/A |  |  | #N/A
Conference/Meeting/Multipurpose537-1 |  | 31 |  | 537-1 | Linear WW Open | FL | 32 | 1 |  | 29 | 36000 | 0.016881 | 0.48956 |  |  | 1.7484 |  |  |  | 1.0382 |  |  | 0.056553 |  |  |  | 0.092286 | 50000 | 0.50644 |  |  | 1.0382
Conference/Meeting/Multipurpose511 |  | 31 |  | 511 | Downlight open - flood | PAR | 60 | 1 |  | 60 | 4200 | 0.005567 | 0.33402 |  |  | 0.20642 |  |  |  | 0.34237 |  |  | 0.11902 |  |  |  | 0.0162 | 0 | 0 |  |  | 0
| Corridor/Transition |  | 0.6475
Corridor/Transition530 |  | 2 |  | 530 | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A | #N/A | 0.3724 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A | #N/A | #N/A |  |  | #N/A
Corridor/Transition537-2 |  | 2 |  | 537-2 | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A | #N/A | 0.2751 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A | #N/A | #N/A |  |  | #N/A
Corridor/Transition0 |  | 2 |  | 0 | NA | NA | 0 | 0 |  | 0 | 0 | 0 | 0 |  |  | 0 |  |  |  | 0 |  |  | 0 |  |  |  | 0 | 0 | 0 |  |  | 0
| Dining Area |  | 1.1655
Dining Area531 |  | 6 |  | 531 | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A | #N/A | 0.89394 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A | #N/A | #N/A |  |  | #N/A
Dining Area524 |  | 6 |  | 524 | indirect Wall Scounce | CF | 18 | 2 |  | 39 | 10000 | 0.0069631 | 0.27156 |  |  | 0.62438 |  |  |  | 0.42823 |  |  | 0.21864 |  |  |  | 0.040386 | 50000 | 0 |  |  | 0
Dining Area0 |  | 6
| Electrical/Mechanical |  | 1.9425
Electrical/Mechanical538 |  | 4 |  | 538 | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A | #N/A | 1.9425 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A | #N/A | #N/A |  |  | #N/A
Electrical/Mechanical0 |  | 4 |  | 0 | NA | NA | 0 | 0 |  | 0 | 0 | 0 | 0 |  |  | 0 |  |  |  | 0 |  |  | 0 |  |  |  | 0 | 0 | 0 |  |  | 0
Electrical/Mechanical0 |  | 4 |  | 0 | NA | NA | 0 | 0 |  | 0 | 0 | 0 | 0 |  |  | 0 |  |  |  | 0 |  |  | 0 |  |  |  | 0 | 0 | 0 |  |  | 0
| Food Preparation |  | 1.554
Food Preparation530 |  | 8 |  | 530 | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A | #N/A | 1.554 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A | #N/A | #N/A |  |  | #N/A
Food Preparation0 |  | 8 |  | 0 | NA | NA | 0 | 0 |  | 0 | 0 | 0 | 0 |  |  | 0 |  |  |  | 0 |  |  | 0 |  |  |  | 0 | 0 | 0 |  |  | 0
Food Preparation0 |  | 8 |  | 0 | NA | NA | 0 | 0 |  | 0 | 0 | 0 | 0 |  |  | 0 |  |  |  | 0 |  |  | 0 |  |  |  | 0 | 0 | 0 |  |  | 0
| Gymnasium/Fitness-Fitness Area |  | 1.1655
Gymnasium/Fitness-Fitness Area535 |  | 126 |  | 535 | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A | #N/A | 1.1655 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A | #N/A | #N/A |  |  | #N/A
Gymnasium/Fitness-Fitness Area0 |  | 126 |  | 0 | NA | NA | 0 | 0 |  | 0 | 0 | 0 | 0 |  |  | 0 |  |  |  | 0 |  |  | 0 |  |  |  | 0 | 0 | 0 |  |  | 0
Gymnasium/Fitness-Fitness Area0 |  | 126 |  | 0 | NA | NA | 0 | 0 |  | 0 | 0 | 0 | 0 |  |  | 0 |  |  |  | 0 |  |  | 0 |  |  |  | 0 | 0 | 0 |  |  | 0
| Highway Lodging Guest Rooms |  | 1.1
Highway Lodging Guest Rooms524 |  | 75.01 |  | 524 | indirect Wall Scounce | CF | 18 | 2 |  | 39 | 10000 | 0.0042947 | 0.16749 |  |  | 0.3851 |  |  |  | 0.26412 |  |  | 0.13485 |  |  |  | 0.024909 | 50000 | 0 |  |  | 0
Highway Lodging Guest Rooms520 |  | 75.01 |  | 520 | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A | #N/A | 0.93251 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A | #N/A | #N/A |  |  | #N/A
Highway Lodging Guest Rooms0 |  | 75.01 |  | 0 | NA | NA | 0 | 0 |  | 0 | 0 | 0 | 0 |  |  | 0 |  |  |  | 0 |  |  | 0 |  |  |  | 0 | 0 | 0 |  |  | 0
| Hospital - Laundry/Washing |  | 0.777
Hospital - Laundry-washing530 |  | 82 |  | 530 | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A | #N/A | 0.777 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A | #N/A | #N/A |  |  | #N/A
Hospital - Laundry-washing0 |  | 82 |  | 0 | NA | NA | 0 | 0 |  | 0 | 0 | 0 | 0 |  |  | 0 |  |  |  | 0 |  |  | 0 |  |  |  | 0 | 0 | 0 |  |  | 0
Hospital - Laundry-washing0 |  | 82 |  | 0 | NA | NA | 0 | 0 |  | 0 | 0 | 0 | 0 |  |  | 0 |  |  |  | 0 |  |  | 0 |  |  |  | 0 | 0 | 0 |  |  | 0
| Library |  | 1.554
Library535 |  | 19 |  | 535 | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A | #N/A | 0.78995 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A | #N/A | #N/A |  |  | #N/A
Library520 |  | 19 |  | 520 | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A | #N/A | 0.3367 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A | #N/A | #N/A |  |  | #N/A
Library529 |  | 19 |  | 529 | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A | #N/A | 0.4144 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A | #N/A | #N/A |  |  | #N/A
| Lobby |  | 1.6835
Lobby534-2 |  | 20.1 |  | 534-2 | Linear Wall Cove | FL | 32 | 1 |  | 29 | 36000 | 0.011645 | 0.33771 |  |  | 4.4251 |  |  |  | 0.67391 |  |  | 0.039011 |  |  |  | 0.06366 | 50000 | 0.34935 |  |  | 0.71617
Lobby523 |  | 20.1 |  | 523 | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A | #N/A | 1.2306 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A | #N/A | #N/A |  |  | #N/A
Lobby521 |  | 20.1 |  | 521 | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A | #N/A | 0.11516 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A | #N/A | #N/A |  |  | #N/A
| Lobby - Hotel |  | 1.4245 | [25 empty] | #N/A
Lobby - Hotel535 |  | 79 |  | 535 | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A | #N/A | 0.035648 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A | #N/A | #N/A |  |  | #N/A
Lobby - Hotel572 |  | 79 |  | 572 | Downlight open | TH | 75 | 1 |  | 75 | 850 | 0.016574 | 1.243 |  |  | 0.46241 |  |  |  | 1.0193 |  |  | 0.35435 |  |  |  | 0.38948 | 0 | 0 |  |  | 0
Lobby - Hotel524 |  | 79 |  | 524 | indirect Wall Scounce | CF | 18 | 2 |  | 39 | 10000 | 0.003739 | 0.14582 |  |  | 0.33528 |  |  |  | 0.22995 |  |  | 0.11741 |  |  |  | 0.021686 | 50000 | 0 |  |  | 0
| Lounge/Recreation - Break room |  | 1.554
Lounge/Recreation - Breakroom537-1 |  | 9 |  | 537-1 | Linear WW Open | FL | 32 | 1 |  | 29 | 36000 | 0.016888 | 0.48974 |  |  | 1.749 |  |  |  | 1.0386 |  |  | 0.056573 |  |  |  | 0.09232 | 50000 | 0.50663 |  |  | 1.0386
Lounge/Recreation - Breakroom572 |  | 9 |  | 0 | NA | NA | 0 | 0 |  | 0 | 0 | 0 | 0 |  |  | 0 |  |  |  | 0 |  |  | 0 |  |  |  | 0 | 0 | 0 |  |  | 0
Lounge/Recreation - Breakroom521 |  | 9 |  | 521 | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A | #N/A | 1.0643 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A | #N/A | #N/A |  |  | #N/A
| Office-Enclosed |  | 1.4245
Office-Enclosed535 |  | 25 |  | 535 | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A | #N/A | 1.0055 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A | #N/A | #N/A |  |  | #N/A
Office-Enclosed539 |  | 25 |  | 539 | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A | #N/A | 0.15903 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A | #N/A | #N/A |  |  | #N/A
Office-Enclosed537-2 |  | 25 |  | 537-2 | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A | #N/A | 0.25997 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A | #N/A | #N/A |  |  | #N/A
| Office - Open Plan (Including Other) |  | 1.4245
Office - Open Plan (Including Other)535 |  | 27 |  | 535 | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A | #N/A | 1.1401 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A | #N/A | #N/A |  |  | #N/A
Office - Open Plan (Including Other)539 |  | 27 |  | 539 | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A | #N/A | 0.20286 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A | #N/A | #N/A |  |  | #N/A
Office - Open Plan (Including Other)524 |  | 27 |  | 524 | indirect Wall Scounce | CF | 18 | 2 |  | 39 | 10000 | 0.0020917 | 0.081576 |  |  | 0.18756 |  |  |  | 0.12864 |  |  | 0.065679 |  |  |  | 0.012132 | 50000 | 0 |  |  | 0
| Restrooms |  | 1.1655
Restrooms521 |  | 12 |  | 521 | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A | #N/A | 0.54991 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A | #N/A | #N/A |  |  | #N/A
Restrooms537-1 |  | 12 |  | 537-1 | Linear WW Open | FL | 32 | 1 |  | 29 | 36000 | 0.01522 | 0.44138 |  |  | 1.5763 |  |  |  | 0.93603 |  |  | 0.050987 |  |  |  | 0.083203 | 50000 | 0.4566 |  |  | 0.93603
Restrooms524 |  | 12 |  | 524 | indirect Wall Scounce | CF | 18 | 2 |  | 39 | 10000 | 0.0044669 | 0.17421 |  |  | 0.40055 |  |  |  | 0.27471 |  |  | 0.14026 |  |  |  | 0.025908 | 50000 | 0 |  |  | 0
| Retail - Sales Area |  | 2.2015
Retail - Sales Area535 |  | 97 |  | 535 | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A | #N/A | 1.2425 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A | #N/A | #N/A |  |  | #N/A
Retail - Sales Area541 |  | 97 |  | 541 | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A | #N/A | 0.95897 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A | #N/A | #N/A |  |  | #N/A
Retail - Sales Area572 |  | 97 |  | 0 | NA | NA | 0 | 0 |  | 0 | 0 | 0 | 0 |  |  | 0 |  |  |  | 0 |  |  | 0 |  |  |  | 0 | 0 | 0 |  |  | 0
| Stairway |  | 0.777
Stairway530 |  | 11 |  | 530 | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A | #N/A | 0.777 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A | #N/A | #N/A |  |  | #N/A
Stairway0 |  | 11 |  | 0 | NA | NA | 0 | 0 |  | 0 | 0 | 0 | 0 |  |  | 0 |  |  |  | 0 |  |  | 0 |  |  |  | 0 | 0 | 0 |  |  | 0
Stairway0 |  | 11 |  | 0 | NA | NA | 0 | 0 |  | 0 | 0 | 0 | 0 |  |  | 0 |  |  |  | 0 |  |  | 0 |  |  |  | 0 | 0 | 0 |  |  | 0
| Storage |  | 1.036
Storage530 |  | 41 |  | 530 | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A | #N/A | 1.036 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A | #N/A | #N/A |  |  | #N/A
Storage553 |  | 41 |  | 0 | NA | NA | 0 | 0 |  | 0 | 0 | 0 | 0 |  |  | 0 |  |  |  | 0 |  |  | 0 |  |  |  | 0 | 0 | 0 |  |  | 0
Storage0 |  | 41 |  | 0 | NA | NA | 0 | 0 |  | 0 | 0 | 0 | 0 |  |  | 0 |  |  |  | 0 |  |  | 0 |  |  |  | 0 | 0 | 0 |  |  | 0
1 FL linear fluorescent, CF compact fluorescent, MH metal halide
Interior Lighting Costs by Space Type, North Carolina Base Code
| Space Type Lighting Descriptions and Cost Parameters | [14 empty] | New Construction Cost | [6 empty] | Lamp Replacement Cost |  |  |  |  | Ballast Replacement Cost
| 2009 Space Types | 90.1 Lighting Subcommittee Model Number | Space Type Lighting Power Allowance W/ft2 | Fixture ID Number | Fixture Type | Lamp Type1 | Lamp Wattage | Number of Lamps | Not Used | Fixture Watts | Lamp Life Hours | Quantity of Fixtures/ft2 | Fixture Watts/ft2 | not used | not used | Fixture Cost/ft2 | not used | not used | not used | Labor Cost $/ft2 | Not Used | Not Used | Lamp Cost $/ft2 | Not Used | Not Used | Not Used | Labor Cost/ft2 | Ballast Life Hours | Ballast Cost, $/ft2 | Not Used | Not Used | Labor Cost/ft2 | Not Used | Not Used
Classroom/Lecture/Training | Classroom/Lecture/Training |  | 1.9026
Classroom/Lecture/Training535 |  | 3.1 |  | 535 | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A | #N/A | 1.5653 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A | #N/A | #N/A |  |  | #N/A
Classroom/Lecture/Training537-2 |  | 3.1 |  | 537-2 | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A | #N/A | 0.33727 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A | #N/A | #N/A |  |  | #N/A
Classroom/Lecture/Training0 |  | 3.1 |  | 0 | NA | NA | 0 | 0 |  | 0 | 0 | 0 | 0 |  |  | 0 |  |  |  | 0 |  |  | 0 |  |  |  | 0 | 0 | 0 |  |  | 0
| Conference/Meeting/Multipurpose |  | 1.7667
Conference/Meeting/Multipurpose535 |  | 31 |  | 535 | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A | #N/A | 0.90242 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A | #N/A | #N/A |  |  | #N/A
Conference/Meeting/Multipurpose537-1 |  | 31 |  | 537-1 | Linear WW Open | FL | 32 | 1 |  | 29 | 36000 | 0.017716 | 0.51376 |  |  | 1.8348 |  |  |  | 1.0895 |  |  | 0.059348 |  |  |  | 0.096847 | 50000 | 0.53147 |  |  | 1.0895
Conference/Meeting/Multipurpose511 |  | 31 |  | 511 | Downlight open - flood | PAR | 60 | 1 |  | 60 | 4200 | 0.0058421 | 0.35053 |  |  | 0.21663 |  |  |  | 0.35929 |  |  | 0.1249 |  |  |  | 0.017001 | 0 | 0 |  |  | 0
| Corridor/Transition |  | 0.6795
Corridor/Transition530 |  | 2 |  | 530 | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A | #N/A | 0.39081 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A | #N/A | #N/A |  |  | #N/A
Corridor/Transition537-2 |  | 2 |  | 537-2 | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A | #N/A | 0.28869 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A | #N/A | #N/A |  |  | #N/A
Corridor/Transition0 |  | 2 |  | 0 | NA | NA | 0 | 0 |  | 0 | 0 | 0 | 0 |  |  | 0 |  |  |  | 0 |  |  | 0 |  |  |  | 0 | 0 | 0 |  |  | 0
| Dining Area |  | 1.2231
Dining Area531 |  | 6 |  | 531 | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A | #N/A | 0.93812 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A | #N/A | #N/A |  |  | #N/A
Dining Area524 |  | 6 |  | 524 | indirect Wall Scounce | CF | 18 | 2 |  | 39 | 10000 | 0.0073072 | 0.28498 |  |  | 0.65524 |  |  |  | 0.44939 |  |  | 0.22945 |  |  |  | 0.042382 | 50000 | 0 |  |  | 0
Dining Area0 |  | 6
| Electrical/Mechanical |  | 2.0385
Electrical/Mechanical538 |  | 4 |  | 538 | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A | #N/A | 2.0385 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A | #N/A | #N/A |  |  | #N/A
Electrical/Mechanical0 |  | 4 |  | 0 | NA | NA | 0 | 0 |  | 0 | 0 | 0 | 0 |  |  | 0 |  |  |  | 0 |  |  | 0 |  |  |  | 0 | 0 | 0 |  |  | 0
Electrical/Mechanical0 |  | 4 |  | 0 | NA | NA | 0 | 0 |  | 0 | 0 | 0 | 0 |  |  | 0 |  |  |  | 0 |  |  | 0 |  |  |  | 0 | 0 | 0 |  |  | 0
| Food Preparation |  | 1.6308
Food Preparation530 |  | 8 |  | 530 | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A | #N/A | 1.6308 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A | #N/A | #N/A |  |  | #N/A
Food Preparation0 |  | 8 |  | 0 | NA | NA | 0 | 0 |  | 0 | 0 | 0 | 0 |  |  | 0 |  |  |  | 0 |  |  | 0 |  |  |  | 0 | 0 | 0 |  |  | 0
Food Preparation0 |  | 8 |  | 0 | NA | NA | 0 | 0 |  | 0 | 0 | 0 | 0 |  |  | 0 |  |  |  | 0 |  |  | 0 |  |  |  | 0 | 0 | 0 |  |  | 0
| Gymnasium/Fitness-Fitness Area |  | 1.2231
Gymnasium/Fitness-Fitness Area535 |  | 126 |  | 535 | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A | #N/A | 1.2231 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A | #N/A | #N/A |  |  | #N/A
Gymnasium/Fitness-Fitness Area0 |  | 126 |  | 0 | NA | NA | 0 | 0 |  | 0 | 0 | 0 | 0 |  |  | 0 |  |  |  | 0 |  |  | 0 |  |  |  | 0 | 0 | 0 |  |  | 0
Gymnasium/Fitness-Fitness Area0 |  | 126 |  | 0 | NA | NA | 0 | 0 |  | 0 | 0 | 0 | 0 |  |  | 0 |  |  |  | 0 |  |  | 0 |  |  |  | 0 | 0 | 0 |  |  | 0
| Highway Lodging Guest Rooms |  | 1.1
Highway Lodging Guest Rooms524 |  | 75.01 |  | 524 | indirect Wall Scounce | CF | 18 | 2 |  | 39 | 10000 | 0.0042947 | 0.16749 |  |  | 0.3851 |  |  |  | 0.26412 |  |  | 0.13485 |  |  |  | 0.024909 | 50000 | 0 |  |  | 0
Highway Lodging Guest Rooms520 |  | 75.01 |  | 520 | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A | #N/A | 0.93251 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A | #N/A | #N/A |  |  | #N/A
Highway Lodging Guest Rooms0 |  | 75.01 |  | 0 | NA | NA | 0 | 0 |  | 0 | 0 | 0 | 0 |  |  | 0 |  |  |  | 0 |  |  | 0 |  |  |  | 0 | 0 | 0 |  |  | 0
| Hospital - Laundry/Washing |  | 0.8154
Hospital - Laundry-washing530 |  | 82 |  | 530 | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A | #N/A | 0.8154 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A | #N/A | #N/A |  |  | #N/A
Hospital - Laundry-washing0 |  | 82 |  | 0 | NA | NA | 0 | 0 |  | 0 | 0 | 0 | 0 |  |  | 0 |  |  |  | 0 |  |  | 0 |  |  |  | 0 | 0 | 0 |  |  | 0
Hospital - Laundry-washing0 |  | 82 |  | 0 | NA | NA | 0 | 0 |  | 0 | 0 | 0 | 0 |  |  | 0 |  |  |  | 0 |  |  | 0 |  |  |  | 0 | 0 | 0 |  |  | 0
| Library |  | 1.6308
Library535 |  | 19 |  | 535 | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A | #N/A | 0.82899 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A | #N/A | #N/A |  |  | #N/A
Library520 |  | 19 |  | 520 | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A | #N/A | 0.35334 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A | #N/A | #N/A |  |  | #N/A
Library529 |  | 19 |  | 529 | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A | #N/A | 0.43488 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A | #N/A | #N/A |  |  | #N/A
| Lobby |  | 1.7667
Lobby534-2 |  | 20.1 |  | 534-2 | Linear Wall Cove | FL | 32 | 1 |  | 29 | 36000 | 0.012221 | 0.3544 |  |  | 4.6438 |  |  |  | 0.70722 |  |  | 0.040939 |  |  |  | 0.066806 | 50000 | 0.36662 |  |  | 0.75156
Lobby523 |  | 20.1 |  | 523 | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A | #N/A | 1.2915 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A | #N/A | #N/A |  |  | #N/A
Lobby521 |  | 20.1 |  | 521 | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A | #N/A | 0.12085 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A | #N/A | #N/A |  |  | #N/A
| Lobby - Hotel |  | 1.4949 | [25 empty] | #N/A
Lobby - Hotel535 |  | 79 |  | 535 | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A | #N/A | 0.03741 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A | #N/A | #N/A |  |  | #N/A
Lobby - Hotel572 |  | 79 |  | 572 | Downlight open | TH | 75 | 1 |  | 75 | 850 | 0.017393 | 1.3045 |  |  | 0.48526 |  |  |  | 1.0697 |  |  | 0.37186 |  |  |  | 0.40873 | 0 | 0 |  |  | 0
Lobby - Hotel524 |  | 79 |  | 524 | indirect Wall Scounce | CF | 18 | 2 |  | 39 | 10000 | 0.0039238 | 0.15303 |  |  | 0.35185 |  |  |  | 0.24131 |  |  | 0.12321 |  |  |  | 0.022758 | 50000 | 0 |  |  | 0
| Lounge/Recreation - Break room |  | 1.6308
Lounge/Recreation - Breakroom537-1 |  | 9 |  | 537-1 | Linear WW Open | FL | 32 | 1 |  | 29 | 36000 | 0.017722 | 0.51394 |  |  | 1.8355 |  |  |  | 1.0899 |  |  | 0.059369 |  |  |  | 0.096883 | 50000 | 0.53167 |  |  | 1.0899
Lounge/Recreation - Breakroom572 |  | 9 |  | 0 | NA | NA | 0 | 0 |  | 0 | 0 | 0 | 0 |  |  | 0 |  |  |  | 0 |  |  | 0 |  |  |  | 0 | 0 | 0 |  |  | 0
Lounge/Recreation - Breakroom521 |  | 9 |  | 521 | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A | #N/A | 1.1169 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A | #N/A | #N/A |  |  | #N/A
| Office-Enclosed |  | 1.4949
Office-Enclosed535 |  | 25 |  | 535 | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A | #N/A | 1.0552 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A | #N/A | #N/A |  |  | #N/A
Office-Enclosed539 |  | 25 |  | 539 | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A | #N/A | 0.16689 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A | #N/A | #N/A |  |  | #N/A
Office-Enclosed537-2 |  | 25 |  | 537-2 | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A | #N/A | 0.27282 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A | #N/A | #N/A |  |  | #N/A
| Office - Open Plan (Including Other) |  | 1.4949
Office - Open Plan (Including Other)535 |  | 27 |  | 535 | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A | #N/A | 1.1964 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A | #N/A | #N/A |  |  | #N/A
Office - Open Plan (Including Other)539 |  | 27 |  | 539 | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A | #N/A | 0.21288 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A | #N/A | #N/A |  |  | #N/A
Office - Open Plan (Including Other)524 |  | 27 |  | 524 | indirect Wall Scounce | CF | 18 | 2 |  | 39 | 10000 | 0.0021951 | 0.085608 |  |  | 0.19683 |  |  |  | 0.135 |  |  | 0.068925 |  |  |  | 0.012731 | 50000 | 0 |  |  | 0
| Restrooms |  | 1.2231
Restrooms521 |  | 12 |  | 521 | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A | #N/A | 0.57709 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A | #N/A | #N/A |  |  | #N/A
Restrooms537-1 |  | 12 |  | 537-1 | Linear WW Open | FL | 32 | 1 |  | 29 | 36000 | 0.015972 | 0.46319 |  |  | 1.6542 |  |  |  | 0.98229 |  |  | 0.053507 |  |  |  | 0.087315 | 50000 | 0.47916 |  |  | 0.98229
Restrooms524 |  | 12 |  | 524 | indirect Wall Scounce | CF | 18 | 2 |  | 39 | 10000 | 0.0046877 | 0.18282 |  |  | 0.42034 |  |  |  | 0.28829 |  |  | 0.14719 |  |  |  | 0.027188 | 50000 | 0 |  |  | 0
| Retail - Sales Area |  | 2.3103
Retail - Sales Area535 |  | 97 |  | 535 | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A | #N/A | 1.3039 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A | #N/A | #N/A |  |  | #N/A
Retail - Sales Area541 |  | 97 |  | 541 | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A | #N/A | 1.0064 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A | #N/A | #N/A |  |  | #N/A
Retail - Sales Area572 |  | 97 |  | 0 | NA | NA | 0 | 0 |  | 0 | 0 | 0 | 0 |  |  | 0 |  |  |  | 0 |  |  | 0 |  |  |  | 0 | 0 | 0 |  |  | 0
| Stairway |  | 0.8154
Stairway530 |  | 11 |  | 530 | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A | #N/A | 0.8154 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A | #N/A | #N/A |  |  | #N/A
Stairway0 |  | 11 |  | 0 | NA | NA | 0 | 0 |  | 0 | 0 | 0 | 0 |  |  | 0 |  |  |  | 0 |  |  | 0 |  |  |  | 0 | 0 | 0 |  |  | 0
Stairway0 |  | 11 |  | 0 | NA | NA | 0 | 0 |  | 0 | 0 | 0 | 0 |  |  | 0 |  |  |  | 0 |  |  | 0 |  |  |  | 0 | 0 | 0 |  |  | 0
| Storage |  | 1.0872
Storage530 |  | 41 |  | 530 | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A | #N/A | 1.0872 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A | #N/A | #N/A |  |  | #N/A
Storage553 |  | 41 |  | 0 | NA | NA | 0 | 0 |  | 0 | 0 | 0 | 0 |  |  | 0 |  |  |  | 0 |  |  | 0 |  |  |  | 0 | 0 | 0 |  |  | 0
Storage0 |  | 41 |  | 0 | NA | NA | 0 | 0 |  | 0 | 0 | 0 | 0 |  |  | 0 |  |  |  | 0 |  |  | 0 |  |  |  | 0 | 0 | 0 |  |  | 0
1 FL linear fluorescent, CF compact fluorescent, MH metal halide
Interior Lighting Costs by Space Type, 2012
| Space Type Lighting Descriptions and Cost Parameters | [18 empty] | New Construction Cost |  |  | Lamp Replacement Cost |  |  |  |  | Ballast Replacement Cost
IECC 2012 Lookup Values | 2012 Space Types | Model Number | Lighting Power Allowance, LPD, W/ft2 | Fixtures - ID Number | Fixture type | Lamp Type | Lamp Wattage | Number of Lamps |  | Fixture Watts | Lamp Life, Hours | Quantity of Fixtures/ft2 | Fixture Watts/ft2 |  |  | Fixture Cost only, $/ft2 | not used | not used | not used | Labor Cost $/ft2 |  |  | Lamp Cost, $/ft2 | Labor Crew Type |  |  | Labor Cost/ft2 | Ballast Life Hours | Ballast Cost, $/ft2 | Not Used | Not Used | Labor Cost/ft2
Classroom/Lecture/Training | Classroom/Lecture/Training |  | 1.4 | [24 empty] | 0 | #N/A |  |  | 0
Classroom/Lecture/Training535 |  | 3.1 |  | 535 | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A | #N/A | 1.0435 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A | #N/A | #N/A |  |  | #N/A
Classroom/Lecture/Training521 |  | 3.1 |  | 521 | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A | #N/A | 0.17392 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A | #N/A | #N/A |  |  | #N/A
Classroom/Lecture/Training0 |  | 3.1 |  | 0 | NA | NA | 0 | 0 |  | 0 | 0 | 0 | 0 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A | #N/A | 0 |  |  | 0
Classroom/Lecture/Training537-1 |  | 3.1 |  | 537-1 | Linear WW Open | FL | 32 | #N/A |  | #N/A | #N/A | #N/A | 0.18256 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A | #N/A | #N/A |  |  | #N/A
| Conference/Meeting/Multipurpose |  | 1.3887
Conference/Meeting/Multipurpose535 |  | 31 |  | 535 | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A | #N/A | 0.68226 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A | #N/A | #N/A |  |  | #N/A
Conference/Meeting/Multipurpose511 |  | 31 |  | 511 | Downlight open - flood | PAR | 60 | #N/A |  | #N/A | #N/A | #N/A | 0.49352 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A | #N/A | #N/A |  |  | #N/A
Conference/Meeting/Multipurpose0 |  | 31 |  | 0 | NA | NA | 0 | 0 |  | 0 | 0 | 0 | 0 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A | #N/A | 0 |  |  | 0
Conference/Meeting/Multipurpose527-1 |  | 31 |  | 527-1 | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A | #N/A | 0.21289 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A | #N/A | #N/A |  |  | #N/A
| Corridor/Transition |  | 0.74514
Corridor/Transition521 |  | 2 |  | 521 | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A | #N/A | 0.74514 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A | #N/A | #N/A |  |  | #N/A
Corridor/Transition0 |  | 2 |  | 0 | NA | NA | 0 | 0 |  | 0 | 0 | 0 | 0 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A | #N/A | 0 |  |  | 0
Corridor/Transition0 |  | 2 |  | 0 | NA | NA | 0 | 0 |  | 0 | 0 | 0 | 0 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A | #N/A | 0 |  |  | 0
Corridor/Transition527-2 |  | 2 |  | 0 | NA | NA | 0 | 0 |  | 0 | 0 | 0 | 1.1369e-07 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A | #N/A | 0 |  |  | 0
| Dining Area |  | 0.73385
Dining Area535 |  | 6 |  | 535 | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A | #N/A | 0.27086 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A | #N/A | #N/A |  |  | #N/A
Dining Area521 |  | 6 |  | 521 | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A | #N/A | 0.13283 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A | #N/A | #N/A |  |  | #N/A
Dining Area0 |  | 6 |  | 0 | NA | NA | 0 | 0 |  | 0 | 0 | 0 | 0 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A | #N/A | 0 |  |  | 0
Dining Area537-1 |  | 6 |  | 537-1 | Linear WW Open | FL | 32 | #N/A |  | #N/A | #N/A | #N/A | 0.33015 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A | #N/A | #N/A |  |  | #N/A
| Electrical/Mechanical |  | 1.0725
Electrical/Mechanical538 |  | 4 |  | 538 | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A | #N/A | 1.0725 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A | #N/A | #N/A |  |  | #N/A
Electrical/Mechanical0 |  | 4 |  | 0 | NA | NA | 0 | 0 |  | 0 | 0 | 0 | 0 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A | #N/A | 0 |  |  | 0
Electrical/Mechanical0 |  | 4 |  | 0 | NA | NA | 0 | 0 |  | 0 | 0 | 0 | 0 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A | #N/A | 0 |  |  | 0
Electrical/Mechanical0 |  | 4 |  | 0 | NA | NA | 0 | 0 |  | 0 | 0 | 0 | 1.127e-07 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A | #N/A | 0 |  |  | 0
| Food Preparation |  | 1.1177
Food Preparation530 |  | 8 |  | 530 | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A | #N/A | 1.1177 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A | #N/A | #N/A |  |  | #N/A
Food Preparation0 |  | 8 |  | 0 | NA | NA | 0 | 0 |  | 0 | 0 | 0 | 0 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A | #N/A | 0 |  |  | 0
Food Preparation0 |  | 8 |  | 0 | NA | NA | 0 | 0 |  | 0 | 0 | 0 | 0 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A | #N/A | 0 |  |  | 0
Food Preparation0 |  | 8 |  | 0 | NA | NA | 0 | 0 |  | 0 | 0 | 0 | 1.1283e-07 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A | #N/A | 0 |  |  | 0
| Gymnasium/Fitness-Fitness Area |  | 0.81288
Gymnasium/Fitness-Fitness Area535 |  | 126 |  | 535 | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A | #N/A | 0.81288 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A | #N/A | #N/A |  |  | #N/A
Gymnasium/Fitness-Fitness Area0 |  | 126 |  | 0 | NA | NA | 0 | 0 |  | 0 | 0 | 0 | 0 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A | #N/A | 0 |  |  | 0
Gymnasium/Fitness-Fitness Area0 |  | 126 |  | 0 | NA | NA | 0 | 0 |  | 0 | 0 | 0 | 0 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A | #N/A | 0 |  |  | 0
Gymnasium/Fitness-Fitness Area0 |  | 126 |  | 0 | NA | NA | 0 | 0 |  | 0 | 0 | 0 | 1.1241e-07 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A | #N/A | 0 |  |  | 0
| Highway Lodging Guest Rooms |  | 0.75
Highway Lodging Guest Rooms529 |  | 75.01 |  | 529 | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A | #N/A | 0.42392 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A | #N/A | #N/A |  |  | #N/A
Highway Lodging Guest Rooms520 |  | 75.01 |  | 520 | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A | #N/A | 0.32608 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A | #N/A | #N/A |  |  | #N/A
Highway Lodging Guest Rooms0 |  | 75.01 |  | 0 | NA | NA | 0 | 0 |  | 0 | 0 | 0 | 0 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A | #N/A | 0 |  |  | 0
Highway Lodging Guest Rooms0 |  | 75.01 |  | 0 | NA | NA | 0 | 0 |  | 0 | 0 | 0 | 9.9676e-08 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A | #N/A | 0 |  |  | 0
| Hospital - Laundry/Washing |  | 0.6774
Hospital - Laundry-washing530 |  | 82 |  | 530 | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A | #N/A | 0.6774 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A | #N/A | #N/A |  |  | #N/A
Hospital - Laundry-washing0 |  | 82 |  | 0 | NA | NA | 0 | 0 |  | 0 | 0 | 0 | 0 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A | #N/A | 0 |  |  | 0
Hospital - Laundry-washing0 |  | 82 |  | 0 | NA | NA | 0 | 0 |  | 0 | 0 | 0 | 0 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A | #N/A | 0 |  |  | 0
Hospital - Laundry-washing0 |  | 82 |  | 0 | NA | NA | 0 | 0 |  | 0 | 0 | 0 | 1.1377e-07 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A | #N/A | 0 |  |  | 0
| Library |  | 1.05
Library535 |  | 19 |  | 535 | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A | #N/A | 0.44344 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A | #N/A | #N/A |  |  | #N/A
Library520 |  | 19 |  | 520 | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A | #N/A | 0.60653 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A | #N/A | #N/A |  |  | #N/A
Library0 |  | 19 |  | 0 | NA | NA | 0 | 0 |  | 0 | 0 | 0 | 0 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A | #N/A | 0 |  |  | 0
Library0 |  | 19 |  | 0 | NA | NA | 0 | 0 |  | 0 | 0 | 0 | 1.1276e-07 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A | #N/A | 0 |  |  | 0
| Lounge/Recreation - Break room |  | 0.82417
Lounge/Recreation - Breakroom521 |  | 9 |  | 521 | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A | #N/A | 0.4912 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A | #N/A | #N/A |  |  | #N/A
Lounge/Recreation - Breakroom0 |  | 9 |  | 0 | NA | NA | 0 | 0 |  | 0 | 0 | 0 | 0 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A | #N/A | 0 |  |  | 0
Lounge/Recreation - Breakroom0 |  | 9 |  | 0 | NA | NA | 0 | 0 |  | 0 | 0 | 0 | 0 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A | #N/A | 0 |  |  | 0
Lounge/Recreation - Breakroom527-2 |  | 9 |  | 527-2 | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A | #N/A | 0.33297 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A | #N/A | #N/A |  |  | #N/A
| Lobby |  | 1.0161
Lobby523 |  | 20.1 |  | 523 | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A | #N/A | 0.56675 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A | #N/A | #N/A |  |  | #N/A
Lobby521 |  | 20.1 |  | 521 | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A | #N/A | 0.26711 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A | #N/A | #N/A |  |  | #N/A
Lobby0 |  | 20.1 |  | 0 | NA | NA | 0 | 0 |  | 0 | 0 | 0 | 0 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A | #N/A | 0 |  |  | 0
Lobby534-2 |  | 20.1 |  | 534-2 | Linear Wall Cove | FL | 32 | #N/A |  | #N/A | #N/A | #N/A | 0.18224 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A | #N/A | #N/A |  |  | #N/A
| Office-Enclosed |  | 1.2532
Office-Enclosed531 |  | 25 |  | 531 | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A | #N/A | 0.76213 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A | #N/A | #N/A |  |  | #N/A
Office-Enclosed539 |  | 25 |  | 539 | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A | #N/A | 0.21026 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A | #N/A | #N/A |  |  | #N/A
Office-Enclosed0 |  | 25 |  | 0 | NA | NA | 0 | 0 |  | 0 | 0 | 0 | 0 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A | #N/A | 0 |  |  | 0
Office-Enclosed537-1 |  | 25 |  | 537-1 | Linear WW Open | FL | 32 | #N/A |  | #N/A | #N/A | #N/A | 0.2808 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A | #N/A | #N/A |  |  | #N/A
| Office - Open Plan (Including Other) |  | 1.1064
Office - Open Plan (Including Other)535 |  | 27 |  | 535 | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A | #N/A | 0.81507 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A | #N/A | #N/A |  |  | #N/A
Office - Open Plan (Including Other)539 |  | 27 |  | 539 | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A | #N/A | 0.10954 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A | #N/A | #N/A |  |  | #N/A
Office - Open Plan (Including Other)0 |  | 27 |  | 0 | NA | NA | 0 | 0 |  | 0 | 0 | 0 | 0 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A | #N/A | 0 |  |  | 0
Office - Open Plan (Including Other)537-1 |  | 27 |  | 537-1 | Linear WW Open | FL | 32 | #N/A |  | #N/A | #N/A | #N/A | 0.18181 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A | #N/A | #N/A |  |  | #N/A
| Restrooms |  | 1.1064
Restrooms604 |  | 12 |  | 604 | Wall Mounted Linear Direct/Indirect | FL | 32 | #N/A |  | #N/A | #N/A | #N/A | 0.32558 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A | #N/A | #N/A |  |  | #N/A
Restrooms520 |  | 12 |  | 520 | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A | #N/A | 0.50218 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A | #N/A | #N/A |  |  | #N/A
Restrooms0 |  | 12 |  | 0 | NA | NA | 0 | 0 |  | 0 | 0 | 0 | 0 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A | #N/A | 0 |  |  | 0
Restrooms534-2 |  | 12 |  | 534-2 | Linear Wall Cove | FL | 32 | #N/A |  | #N/A | #N/A | #N/A | 0.27866 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A | #N/A | #N/A |  |  | #N/A
| Retail - Sales Area |  | 1.8967
Retail - Sales Area535 |  | 97 |  | 535 | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A | #N/A | 1.1489 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A | #N/A | #N/A |  |  | #N/A
Retail - Sales Area541 |  | 97 |  | 541 | #N/A |  | #N/A | #N/A |  | #N/A | #N/A | #N/A | 0.56902 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A | #N/A | #N/A |  |  | #N/A
Retail - Sales Area0 |  | 97 |  | 0 | NA | NA | 0 | 0 |  | 0 | 0 | 0 | 0 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A | #N/A | 0 |  |  | 0
Retail - Sales Area537-1 |  | 97 |  | 537-1 | Linear WW Open | FL | 32 | #N/A |  | #N/A | #N/A | #N/A | 0.1788 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A | #N/A | #N/A |  |  | #N/A
| Stairway |  | 0.77901
Stairway530 |  | 11 |  | 530 | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A | #N/A | 0.42028 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A | #N/A | #N/A |  |  | #N/A
Stairway602 |  | 11 |  | 602 | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A | #N/A | 0.35873 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A | #N/A | #N/A |  |  | #N/A
Stairway0 |  | 11 |  | 0 | NA | NA | 0 | 0 |  | 0 | 0 | 0 | 0 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A | #N/A | 0 |  |  | 0
Stairway0 |  | 11 |  | 0 | NA | NA | 0 | 0 |  | 0 | 0 | 0 | 1.1282e-07 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A | #N/A | 0 |  |  | 0
| Storage |  | 0.71127
Storage538 |  | 41 |  | 538 | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A | #N/A | 0.71127 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A | #N/A | #N/A |  |  | #N/A
Storage0 |  | 41 |  | 0 | NA | NA | 0 | 0 |  | 0 | 0 | 0 | 0 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A | #N/A | 0 |  |  | 0
Storage0 |  | 41 |  | 0 | NA | NA | 0 | 0 |  | 0 | 0 | 0 | 0 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A | #N/A | 0 |  |  | 0
Storage0 |  | 41 |  | 0 | NA | NA | 0 | 0 |  | 0 | 0 | 0 | 1.1211e-07 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A | #N/A | 0 |  |  | 0
| Lobby - Hotel |  | 1.1967
Lobby - Hotel572 |  | 79 |  | 572 | Downlight open | TH | 75 | #N/A |  | #N/A | #N/A | #N/A | 1.0148 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A | #N/A | #N/A |  |  | #N/A
Lobby - Hotel0 |  | 79 |  | 0 | NA | NA | 0 | 0 |  | 0 | 0 | 0 | 0 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A | #N/A | 0 |  |  | 0
Lobby - Hotel0 |  | 79 |  | 0 | NA | NA | 0 | 0 |  | 0 | 0 | 0 | 0 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A | #N/A | 0 |  |  | 0
Lobby - Hotel527-1 |  | 79 |  | 527-1 | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A | #N/A | 0.18189 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A | #N/A | #N/A |  |  | #N/A
1 FL linear fluorescent, CF compact fluorescent, MH metal halide

## Int Ltg LPD Space Types MA (hidden)
| IECC Cost Effectiveness - Interior Lighting Power Density - Fixture Costs per Square Foot for Each Space Type - Mid-rise Apartment | [18 empty] | MID-RISE APT.
Adjustment Factors for LPD
| Interior lighting costs by space type and fixture type IECC 2009, North Carolina Base Code, and IECC 2012 tables. | [18 empty] | 2009 | 1.106
| 90.1-07 and 2010 in Int Ltg LPD Space Types 90_1 (same for all prototypes). Values come from "Int Ltg Comp" worksheet in this workbook. | [18 empty] | N. Carolina | 0.838
[20 empty] | 2012 | 0.782
Interior Lighting Costs by Space Type, 2009
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 31 | 32 | 33 | 34 | 35
| Space Type Lighting Descriptions and Cost Parameters | [14 empty] | New Construction Cost | [6 empty] | Lamp Replacement Cost |  |  |  |  | Ballast Replacement Cost
IECC 2009 Lookup Values | 2009 Space Types | 90.1 Lighting Subcommittee Model Number | Space Type Lighting Power Allowance W/ft2 | Fixture ID Number | Fixture Type | Lamp Type1 | Lamp Wattage | Number of Lamps | Not Used | Fixture Watts | Lamp Life Hours | Quantity of Fixtures/ft2 | Fixture Watts/ft2 | not used | not used | Fixture Cost/ft2 | not used | not used | not used | Labor Cost $/ft2 | Not Used | Not Used | Lamp Cost $/ft2 | Not Used | Not Used | Not Used | Labor Cost/ft2 | Ballast Life Hours | Ballast Cost, $/ft2 | Not Used | Not Used | Labor Cost/ft2 | Not Used | Not Used
Classroom/Lecture/Training | Classroom/Lecture/Training |  | 1.5484
Classroom/Lecture/Training535 |  | 3.1 |  | 535 | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A | #N/A | 1.2739 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A | #N/A | #N/A |  |  | #N/A
Classroom/Lecture/Training537-2 |  | 3.1 |  | 537-2 | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A | #N/A | 0.27448 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A | #N/A | #N/A |  |  | #N/A
Classroom/Lecture/Training0 |  | 3.1 |  | 0 | NA | NA | 0 | 0 |  | 0 | 0 | 0 | 0 |  |  | 0 |  |  |  | 0 |  |  | 0 |  |  |  | 0 | 0 | 0 |  |  | 0
| Conference/Meeting/Multipurpose |  | 1.4378
Conference/Meeting/Multipurpose535 |  | 31 |  | 535 | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A | #N/A | 0.73442 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A | #N/A | #N/A |  |  | #N/A
Conference/Meeting/Multipurpose537-1 |  | 31 |  | 537-1 | Linear WW Open | FL | 32 | 1 |  | 29 | 36000 | 0.014418 | 0.41811 |  |  | 1.4932 |  |  |  | 0.88669 |  |  | 0.048299 |  |  |  | 0.078818 | 50000 | 0.43253 |  |  | 0.88669
Conference/Meeting/Multipurpose511 |  | 31 |  | 511 | Downlight open - flood | PAR | 60 | 1 |  | 60 | 4200 | 0.0047545 | 0.28527 |  |  | 0.1763 |  |  |  | 0.2924 |  |  | 0.10165 |  |  |  | 0.013836 | 0 | 0 |  |  | 0
| Corridor/Transition |  | 0.553
Corridor/Transition530 |  | 2 |  | 530 | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A | #N/A | 0.31805 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A | #N/A | #N/A |  |  | #N/A
Corridor/Transition537-2 |  | 2 |  | 537-2 | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A | #N/A | 0.23495 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A | #N/A | #N/A |  |  | #N/A
Corridor/Transition0 |  | 2 |  | 0 | NA | NA | 0 | 0 |  | 0 | 0 | 0 | 0 |  |  | 0 |  |  |  | 0 |  |  | 0 |  |  |  | 0 | 0 | 0 |  |  | 0
| Dining Area |  | 0.9954
Dining Area531 |  | 6 |  | 531 | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A | #N/A | 0.76347 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A | #N/A | #N/A |  |  | #N/A
Dining Area524 |  | 6 |  | 524 | indirect Wall Scounce | CF | 18 | 2 |  | 39 | 10000 | 0.0059469 | 0.23193 |  |  | 0.53326 |  |  |  | 0.36573 |  |  | 0.18673 |  |  |  | 0.034492 | 50000 | 0 |  |  | 0
Dining Area0 |  | 6
| Electrical/Mechanical |  | 1.659
Electrical/Mechanical538 |  | 4 |  | 538 | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A | #N/A | 1.659 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A | #N/A | #N/A |  |  | #N/A
Electrical/Mechanical0 |  | 4 |  | 0 | NA | NA | 0 | 0 |  | 0 | 0 | 0 | 0 |  |  | 0 |  |  |  | 0 |  |  | 0 |  |  |  | 0 | 0 | 0 |  |  | 0
Electrical/Mechanical0 |  | 4 |  | 0 | NA | NA | 0 | 0 |  | 0 | 0 | 0 | 0 |  |  | 0 |  |  |  | 0 |  |  | 0 |  |  |  | 0 | 0 | 0 |  |  | 0
| Food Preparation |  | 1.3272
Food Preparation530 |  | 8 |  | 530 | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A | #N/A | 1.3272 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A | #N/A | #N/A |  |  | #N/A
Food Preparation0 |  | 8 |  | 0 | NA | NA | 0 | 0 |  | 0 | 0 | 0 | 0 |  |  | 0 |  |  |  | 0 |  |  | 0 |  |  |  | 0 | 0 | 0 |  |  | 0
Food Preparation0 |  | 8 |  | 0 | NA | NA | 0 | 0 |  | 0 | 0 | 0 | 0 |  |  | 0 |  |  |  | 0 |  |  | 0 |  |  |  | 0 | 0 | 0 |  |  | 0
| Gymnasium/Fitness-Fitness Area |  | 0.9954
Gymnasium/Fitness-Fitness Area535 |  | 126 |  | 535 | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A | #N/A | 0.9954 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A | #N/A | #N/A |  |  | #N/A
Gymnasium/Fitness-Fitness Area0 |  | 126 |  | 0 | NA | NA | 0 | 0 |  | 0 | 0 | 0 | 0 |  |  | 0 |  |  |  | 0 |  |  | 0 |  |  |  | 0 | 0 | 0 |  |  | 0
Gymnasium/Fitness-Fitness Area0 |  | 126 |  | 0 | NA | NA | 0 | 0 |  | 0 | 0 | 0 | 0 |  |  | 0 |  |  |  | 0 |  |  | 0 |  |  |  | 0 | 0 | 0 |  |  | 0
| Highway Lodging Guest Rooms |  | 1.2166
Highway Lodging Guest Rooms524 |  | 75.01 |  | 524 | indirect Wall Scounce | CF | 18 | 2 |  | 39 | 10000 | 0.0047499 | 0.18525 |  |  | 0.42592 |  |  |  | 0.29212 |  |  | 0.14915 |  |  |  | 0.027549 | 50000 | 0 |  |  | 0
Highway Lodging Guest Rooms520 |  | 75.01 |  | 520 | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A | #N/A | 1.0314 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A | #N/A | #N/A |  |  | #N/A
Highway Lodging Guest Rooms0 |  | 75.01 |  | 0 | NA | NA | 0 | 0 |  | 0 | 0 | 0 | 0 |  |  | 0 |  |  |  | 0 |  |  | 0 |  |  |  | 0 | 0 | 0 |  |  | 0
| Hospital - Laundry/Washing |  | 0.6636
Hospital - Laundry-washing530 |  | 82 |  | 530 | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A | #N/A | 0.6636 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A | #N/A | #N/A |  |  | #N/A
Hospital - Laundry-washing0 |  | 82 |  | 0 | NA | NA | 0 | 0 |  | 0 | 0 | 0 | 0 |  |  | 0 |  |  |  | 0 |  |  | 0 |  |  |  | 0 | 0 | 0 |  |  | 0
Hospital - Laundry-washing0 |  | 82 |  | 0 | NA | NA | 0 | 0 |  | 0 | 0 | 0 | 0 |  |  | 0 |  |  |  | 0 |  |  | 0 |  |  |  | 0 | 0 | 0 |  |  | 0
| Library |  | 1.3272
Library535 |  | 19 |  | 535 | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A | #N/A | 0.67466 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A | #N/A | #N/A |  |  | #N/A
Library520 |  | 19 |  | 520 | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A | #N/A | 0.28756 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A | #N/A | #N/A |  |  | #N/A
Library529 |  | 19 |  | 529 | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A | #N/A | 0.35392 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A | #N/A | #N/A |  |  | #N/A
| Lobby |  | 1.4378
Lobby534-2 |  | 20.1 |  | 534-2 | Linear Wall Cove | FL | 32 | 1 |  | 29 | 36000 | 0.0099455 | 0.28842 |  |  | 3.7793 |  |  |  | 0.57556 |  |  | 0.033317 |  |  |  | 0.054369 | 50000 | 0.29836 |  |  | 0.61165
Lobby523 |  | 20.1 |  | 523 | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A | #N/A | 1.051 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A | #N/A | #N/A |  |  | #N/A
Lobby521 |  | 20.1 |  | 521 | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A | #N/A | 0.098351 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A | #N/A | #N/A |  |  | #N/A
| Lobby - Hotel |  | 1.2166 | [25 empty] | #N/A
Lobby - Hotel535 |  | 79 |  | 535 | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A | #N/A | 0.030446 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A | #N/A | #N/A |  |  | #N/A
Lobby - Hotel572 |  | 79 |  | 572 | Downlight open | TH | 75 | 1 |  | 75 | 850 | 0.014155 | 1.0616 |  |  | 0.39492 |  |  |  | 0.87052 |  |  | 0.30263 |  |  |  | 0.33264 | 0 | 0 |  |  | 0
Lobby - Hotel524 |  | 79 |  | 524 | indirect Wall Scounce | CF | 18 | 2 |  | 39 | 10000 | 0.0031933 | 0.12454 |  |  | 0.28635 |  |  |  | 0.19639 |  |  | 0.10027 |  |  |  | 0.018521 | 50000 | 0 |  |  | 0
| Lounge/Recreation - Break room |  | 1.3272
Lounge/Recreation - Breakroom537-1 |  | 9 |  | 537-1 | Linear WW Open | FL | 32 | 1 |  | 29 | 36000 | 0.014423 | 0.41826 |  |  | 1.4938 |  |  |  | 0.88701 |  |  | 0.048317 |  |  |  | 0.078846 | 50000 | 0.43269 |  |  | 0.88701
Lounge/Recreation - Breakroom572 |  | 9 |  | 0 | NA | NA | 0 | 0 |  | 0 | 0 | 0 | 0 |  |  | 0 |  |  |  | 0 |  |  | 0 |  |  |  | 0 | 0 | 0 |  |  | 0
Lounge/Recreation - Breakroom521 |  | 9 |  | 521 | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A | #N/A | 0.90894 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A | #N/A | #N/A |  |  | #N/A
| Office-Enclosed |  | 1.2166
Office-Enclosed535 |  | 25 |  | 535 | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A | #N/A | 0.85875 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A | #N/A | #N/A |  |  | #N/A
Office-Enclosed539 |  | 25 |  | 539 | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A | #N/A | 0.13582 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A | #N/A | #N/A |  |  | #N/A
Office-Enclosed537-2 |  | 25 |  | 537-2 | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A | #N/A | 0.22203 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A | #N/A | #N/A |  |  | #N/A
| Office - Open Plan (Including Other) |  | 1.2166
Office - Open Plan (Including Other)535 |  | 27 |  | 535 | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A | #N/A | 0.97368 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A | #N/A | #N/A |  |  | #N/A
Office - Open Plan (Including Other)539 |  | 27 |  | 539 | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A | #N/A | 0.17325 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A | #N/A | #N/A |  |  | #N/A
Office - Open Plan (Including Other)524 |  | 27 |  | 524 | indirect Wall Scounce | CF | 18 | 2 |  | 39 | 10000 | 0.0017864 | 0.069671 |  |  | 0.16019 |  |  |  | 0.10987 |  |  | 0.056094 |  |  |  | 0.010361 | 50000 | 0 |  |  | 0
| Restrooms |  | 0.9954
Restrooms521 |  | 12 |  | 521 | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A | #N/A | 0.46965 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A | #N/A | #N/A |  |  | #N/A
Restrooms537-1 |  | 12 |  | 537-1 | Linear WW Open | FL | 32 | 1 |  | 29 | 36000 | 0.012999 | 0.37696 |  |  | 1.3463 |  |  |  | 0.79942 |  |  | 0.043546 |  |  |  | 0.07106 | 50000 | 0.38996 |  |  | 0.79942
Restrooms524 |  | 12 |  | 524 | indirect Wall Scounce | CF | 18 | 2 |  | 39 | 10000 | 0.003815 | 0.14878 |  |  | 0.34209 |  |  |  | 0.23462 |  |  | 0.11979 |  |  |  | 0.022127 | 50000 | 0 |  |  | 0
| Retail - Sales Area |  | 1.8802
Retail - Sales Area535 |  | 97 |  | 535 | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A | #N/A | 1.0612 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A | #N/A | #N/A |  |  | #N/A
Retail - Sales Area541 |  | 97 |  | 541 | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A | #N/A | 0.81901 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A | #N/A | #N/A |  |  | #N/A
Retail - Sales Area572 |  | 97 |  | 0 | NA | NA | 0 | 0 |  | 0 | 0 | 0 | 0 |  |  | 0 |  |  |  | 0 |  |  | 0 |  |  |  | 0 | 0 | 0 |  |  | 0
| Stairway |  | 0.6636
Stairway530 |  | 11 |  | 530 | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A | #N/A | 0.6636 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A | #N/A | #N/A |  |  | #N/A
Stairway0 |  | 11 |  | 0 | NA | NA | 0 | 0 |  | 0 | 0 | 0 | 0 |  |  | 0 |  |  |  | 0 |  |  | 0 |  |  |  | 0 | 0 | 0 |  |  | 0
Stairway0 |  | 11 |  | 0 | NA | NA | 0 | 0 |  | 0 | 0 | 0 | 0 |  |  | 0 |  |  |  | 0 |  |  | 0 |  |  |  | 0 | 0 | 0 |  |  | 0
| Storage |  | 0.8848
Storage530 |  | 41 |  | 530 | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A | #N/A | 0.8848 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A | #N/A | #N/A |  |  | #N/A
Storage553 |  | 41 |  | 0 | NA | NA | 0 | 0 |  | 0 | 0 | 0 | 0 |  |  | 0 |  |  |  | 0 |  |  | 0 |  |  |  | 0 | 0 | 0 |  |  | 0
Storage0 |  | 41 |  | 0 | NA | NA | 0 | 0 |  | 0 | 0 | 0 | 0 |  |  | 0 |  |  |  | 0 |  |  | 0 |  |  |  | 0 | 0 | 0 |  |  | 0
| Dwelling Units Low End |  | 0.39
DwellingUnits530_Low |  |  |  | 530 | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A | #N/A | 0.07 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A | #N/A | #N/A |  |  | #N/A
DwellingUnits501_Low |  |  |  | 501 | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A | #N/A | 0.27 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A | #N/A | #N/A |  |  | #N/A
DwellingUnits700_Low |  |  |  | 700 | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A | #N/A | 0.05 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A | #N/A | #N/A |  |  | #N/A
| Dwelling Units High End |  | 0.78
DwellingUnits505_High |  |  |  | 505 | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A | #N/A | 0.23 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A | #N/A | #N/A |  |  | #N/A
DwellingUnits501_High |  |  |  | 501 | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A | #N/A | 0.1 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A | #N/A | #N/A |  |  | #N/A
DwellingUnits500_High |  |  |  | 500 | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A | #N/A | 0.22 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A | #N/A | #N/A |  |  | #N/A
DwellingUnits700_High |  |  |  | 700 | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A | #N/A | 0.14 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A | #N/A | #N/A |  |  | #N/A
DwellingUnits530_High |  |  |  | 530 | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A | #N/A | 0.09 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A | #N/A | #N/A |  |  | #N/A
1 FL linear fluorescent, CF compact fluorescent, MH metal halide
Interior Lighting Costs by Space Type, North Carolina Base Code
| Space Type Lighting Descriptions and Cost Parameters | [14 empty] | New Construction Cost | [6 empty] | Lamp Replacement Cost |  |  |  |  | Ballast Replacement Cost
North Carolina Base Code Lookup Values | NC Space Types | 90.1 Lighting Subcommittee Model Number | Space Type Lighting Power Allowance W/ft2 | Fixture ID Number | Fixture Type | Lamp Type1 | Lamp Wattage | Number of Lamps | Not Used | Fixture Watts | Lamp Life Hours | Quantity of Fixtures/ft2 | Fixture Watts/ft2 | not used | not used | Fixture Cost/ft2 | not used | not used | not used | Labor Cost $/ft2 | Not Used | Not Used | Lamp Cost $/ft2 | Not Used | Not Used | Not Used | Labor Cost/ft2 | Ballast Life Hours | Ballast Cost, $/ft2 | Not Used | Not Used | Labor Cost/ft2 | Not Used | Not Used
Classroom/Lecture/Training | Classroom/Lecture/Training |  | 1.1732
Classroom/Lecture/Training535 |  | 3.1 |  | 535 | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A | #N/A | 0.96523 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A | #N/A | #N/A |  |  | #N/A
Classroom/Lecture/Training537-2 |  | 3.1 |  | 537-2 | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A | #N/A | 0.20797 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A | #N/A | #N/A |  |  | #N/A
Classroom/Lecture/Training0 |  | 3.1 |  | 0 | NA | NA | 0 | 0 |  | 0 | 0 | 0 | 0 |  |  | 0 |  |  |  | 0 |  |  | 0 |  |  |  | 0 | 0 | 0 |  |  | 0
| Conference/Meeting/Multipurpose |  | 1.0894
Conference/Meeting/Multipurpose535 |  | 31 |  | 535 | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A | #N/A | 0.55646 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A | #N/A | #N/A |  |  | #N/A
Conference/Meeting/Multipurpose537-1 |  | 31 |  | 537-1 | Linear WW Open | FL | 32 | 1 |  | 29 | 36000 | 0.010924 | 0.3168 |  |  | 1.1314 |  |  |  | 0.67183 |  |  | 0.036596 |  |  |  | 0.059719 | 50000 | 0.32772 |  |  | 0.67183
Conference/Meeting/Multipurpose511 |  | 31 |  | 511 | Downlight open - flood | PAR | 60 | 1 |  | 60 | 4200 | 0.0036024 | 0.21615 |  |  | 0.13358 |  |  |  | 0.22155 |  |  | 0.07702 |  |  |  | 0.010483 | 0 | 0 |  |  | 0
| Corridor/Transition |  | 0.419
Corridor/Transition530 |  | 2 |  | 530 | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A | #N/A | 0.24098 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A | #N/A | #N/A |  |  | #N/A
Corridor/Transition537-2 |  | 2 |  | 537-2 | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A | #N/A | 0.17802 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A | #N/A | #N/A |  |  | #N/A
Corridor/Transition0 |  | 2 |  | 0 | NA | NA | 0 | 0 |  | 0 | 0 | 0 | 0 |  |  | 0 |  |  |  | 0 |  |  | 0 |  |  |  | 0 | 0 | 0 |  |  | 0
| Dining Area |  | 0.7542
Dining Area531 |  | 6 |  | 531 | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A | #N/A | 0.57847 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A | #N/A | #N/A |  |  | #N/A
Dining Area524 |  | 6 |  | 524 | indirect Wall Scounce | CF | 18 | 2 |  | 39 | 10000 | 0.0045059 | 0.17573 |  |  | 0.40404 |  |  |  | 0.27711 |  |  | 0.14148 |  |  |  | 0.026134 | 50000 | 0 |  |  | 0
Dining Area0 |  | 6
| Electrical/Mechanical |  | 1.257
Electrical/Mechanical538 |  | 4 |  | 538 | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A | #N/A | 1.257 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A | #N/A | #N/A |  |  | #N/A
Electrical/Mechanical0 |  | 4 |  | 0 | NA | NA | 0 | 0 |  | 0 | 0 | 0 | 0 |  |  | 0 |  |  |  | 0 |  |  | 0 |  |  |  | 0 | 0 | 0 |  |  | 0
Electrical/Mechanical0 |  | 4 |  | 0 | NA | NA | 0 | 0 |  | 0 | 0 | 0 | 0 |  |  | 0 |  |  |  | 0 |  |  | 0 |  |  |  | 0 | 0 | 0 |  |  | 0
| Food Preparation |  | 1.0056
Food Preparation530 |  | 8 |  | 530 | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A | #N/A | 1.0056 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A | #N/A | #N/A |  |  | #N/A
Food Preparation0 |  | 8 |  | 0 | NA | NA | 0 | 0 |  | 0 | 0 | 0 | 0 |  |  | 0 |  |  |  | 0 |  |  | 0 |  |  |  | 0 | 0 | 0 |  |  | 0
Food Preparation0 |  | 8 |  | 0 | NA | NA | 0 | 0 |  | 0 | 0 | 0 | 0 |  |  | 0 |  |  |  | 0 |  |  | 0 |  |  |  | 0 | 0 | 0 |  |  | 0
| Gymnasium/Fitness-Fitness Area |  | 0.7542
Gymnasium/Fitness-Fitness Area535 |  | 126 |  | 535 | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A | #N/A | 0.7542 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A | #N/A | #N/A |  |  | #N/A
Gymnasium/Fitness-Fitness Area0 |  | 126 |  | 0 | NA | NA | 0 | 0 |  | 0 | 0 | 0 | 0 |  |  | 0 |  |  |  | 0 |  |  | 0 |  |  |  | 0 | 0 | 0 |  |  | 0
Gymnasium/Fitness-Fitness Area0 |  | 126 |  | 0 | NA | NA | 0 | 0 |  | 0 | 0 | 0 | 0 |  |  | 0 |  |  |  | 0 |  |  | 0 |  |  |  | 0 | 0 | 0 |  |  | 0
| Highway Lodging Guest Rooms |  | 0.9218
Highway Lodging Guest Rooms524 |  | 75.01 |  | 524 | indirect Wall Scounce | CF | 18 | 2 |  | 39 | 10000 | 0.0035989 | 0.14036 |  |  | 0.32272 |  |  |  | 0.22133 |  |  | 0.11301 |  |  |  | 0.020874 | 50000 | 0 |  |  | 0
Highway Lodging Guest Rooms520 |  | 75.01 |  | 520 | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A | #N/A | 0.78144 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A | #N/A | #N/A |  |  | #N/A
Highway Lodging Guest Rooms0 |  | 75.01 |  | 0 | NA | NA | 0 | 0 |  | 0 | 0 | 0 | 0 |  |  | 0 |  |  |  | 0 |  |  | 0 |  |  |  | 0 | 0 | 0 |  |  | 0
| Hospital - Laundry/Washing |  | 0.5028
Hospital - Laundry-washing530 |  | 82 |  | 530 | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A | #N/A | 0.5028 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A | #N/A | #N/A |  |  | #N/A
Hospital - Laundry-washing0 |  | 82 |  | 0 | NA | NA | 0 | 0 |  | 0 | 0 | 0 | 0 |  |  | 0 |  |  |  | 0 |  |  | 0 |  |  |  | 0 | 0 | 0 |  |  | 0
Hospital - Laundry-washing0 |  | 82 |  | 0 | NA | NA | 0 | 0 |  | 0 | 0 | 0 | 0 |  |  | 0 |  |  |  | 0 |  |  | 0 |  |  |  | 0 | 0 | 0 |  |  | 0
| Library |  | 1.0056
Library535 |  | 19 |  | 535 | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A | #N/A | 0.51118 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A | #N/A | #N/A |  |  | #N/A
Library520 |  | 19 |  | 520 | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A | #N/A | 0.21788 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A | #N/A | #N/A |  |  | #N/A
Library529 |  | 19 |  | 529 | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A | #N/A | 0.26816 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A | #N/A | #N/A |  |  | #N/A
| Lobby |  | 1.0894
Lobby534-2 |  | 20.1 |  | 534-2 | Linear Wall Cove | FL | 32 | 1 |  | 29 | 36000 | 0.0075355 | 0.21853 |  |  | 2.8635 |  |  |  | 0.43609 |  |  | 0.025244 |  |  |  | 0.041195 | 50000 | 0.22607 |  |  | 0.46344
Lobby523 |  | 20.1 |  | 523 | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A | #N/A | 0.79635 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A | #N/A | #N/A |  |  | #N/A
Lobby521 |  | 20.1 |  | 521 | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A | #N/A | 0.074519 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A | #N/A | #N/A |  |  | #N/A
| Lobby - Hotel |  | 0.9218 | [25 empty] | #N/A
Lobby - Hotel535 |  | 79 |  | 535 | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A | #N/A | 0.023068 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A | #N/A | #N/A |  |  | #N/A
Lobby - Hotel572 |  | 79 |  | 572 | Downlight open | TH | 75 | 1 |  | 75 | 850 | 0.010725 | 0.80437 |  |  | 0.29923 |  |  |  | 0.65958 |  |  | 0.2293 |  |  |  | 0.25204 | 0 | 0 |  |  | 0
Lobby - Hotel524 |  | 79 |  | 524 | indirect Wall Scounce | CF | 18 | 2 |  | 39 | 10000 | 0.0024195 | 0.094362 |  |  | 0.21696 |  |  |  | 0.1488 |  |  | 0.075973 |  |  |  | 0.014033 | 50000 | 0 |  |  | 0
| Lounge/Recreation - Break room |  | 1.0056
Lounge/Recreation - Breakroom537-1 |  | 9 |  | 537-1 | Linear WW Open | FL | 32 | 1 |  | 29 | 36000 | 0.010928 | 0.31691 |  |  | 1.1318 |  |  |  | 0.67207 |  |  | 0.036609 |  |  |  | 0.059741 | 50000 | 0.32784 |  |  | 0.67207
Lounge/Recreation - Breakroom572 |  | 9 |  | 0 | NA | NA | 0 | 0 |  | 0 | 0 | 0 | 0 |  |  | 0 |  |  |  | 0 |  |  | 0 |  |  |  | 0 | 0 | 0 |  |  | 0
Lounge/Recreation - Breakroom521 |  | 9 |  | 521 | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A | #N/A | 0.68869 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A | #N/A | #N/A |  |  | #N/A
| Office-Enclosed |  | 0.9218
Office-Enclosed535 |  | 25 |  | 535 | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A | #N/A | 0.65066 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A | #N/A | #N/A |  |  | #N/A
Office-Enclosed539 |  | 25 |  | 539 | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A | #N/A | 0.10291 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A | #N/A | #N/A |  |  | #N/A
Office-Enclosed537-2 |  | 25 |  | 537-2 | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A | #N/A | 0.16823 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A | #N/A | #N/A |  |  | #N/A
| Office - Open Plan (Including Other) |  | 0.9218
Office - Open Plan (Including Other)535 |  | 27 |  | 535 | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A | #N/A | 0.73774 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A | #N/A | #N/A |  |  | #N/A
Office - Open Plan (Including Other)539 |  | 27 |  | 539 | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A | #N/A | 0.13127 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A | #N/A | #N/A |  |  | #N/A
Office - Open Plan (Including Other)524 |  | 27 |  | 524 | indirect Wall Scounce | CF | 18 | 2 |  | 39 | 10000 | 0.0013535 | 0.052788 |  |  | 0.12137 |  |  |  | 0.083243 |  |  | 0.042501 |  |  |  | 0.0078506 | 50000 | 0 |  |  | 0
| Restrooms |  | 0.7542
Restrooms521 |  | 12 |  | 521 | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A | #N/A | 0.35585 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A | #N/A | #N/A |  |  | #N/A
Restrooms537-1 |  | 12 |  | 537-1 | Linear WW Open | FL | 32 | 1 |  | 29 | 36000 | 0.0098489 | 0.28562 |  |  | 1.0201 |  |  |  | 0.60571 |  |  | 0.032994 |  |  |  | 0.053841 | 50000 | 0.29547 |  |  | 0.60571
Restrooms524 |  | 12 |  | 524 | indirect Wall Scounce | CF | 18 | 2 |  | 39 | 10000 | 0.0028905 | 0.11273 |  |  | 0.2592 |  |  |  | 0.17777 |  |  | 0.090763 |  |  |  | 0.016765 | 50000 | 0 |  |  | 0
| Retail - Sales Area |  | 1.4246
Retail - Sales Area535 |  | 97 |  | 535 | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A | #N/A | 0.80405 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A | #N/A | #N/A |  |  | #N/A
Retail - Sales Area541 |  | 97 |  | 541 | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A | #N/A | 0.62055 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A | #N/A | #N/A |  |  | #N/A
Retail - Sales Area572 |  | 97 |  | 0 | NA | NA | 0 | 0 |  | 0 | 0 | 0 | 0 |  |  | 0 |  |  |  | 0 |  |  | 0 |  |  |  | 0 | 0 | 0 |  |  | 0
| Stairway |  | 0.5028
Stairway530 |  | 11 |  | 530 | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A | #N/A | 0.5028 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A | #N/A | #N/A |  |  | #N/A
Stairway0 |  | 11 |  | 0 | NA | NA | 0 | 0 |  | 0 | 0 | 0 | 0 |  |  | 0 |  |  |  | 0 |  |  | 0 |  |  |  | 0 | 0 | 0 |  |  | 0
Stairway0 |  | 11 |  | 0 | NA | NA | 0 | 0 |  | 0 | 0 | 0 | 0 |  |  | 0 |  |  |  | 0 |  |  | 0 |  |  |  | 0 | 0 | 0 |  |  | 0
| Storage |  | 0.6704
Storage530 |  | 41 |  | 530 | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A | #N/A | 0.6704 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A | #N/A | #N/A |  |  | #N/A
Storage553 |  | 41 |  | 0 | NA | NA | 0 | 0 |  | 0 | 0 | 0 | 0 |  |  | 0 |  |  |  | 0 |  |  | 0 |  |  |  | 0 | 0 | 0 |  |  | 0
Storage0 |  | 41 |  | 0 | NA | NA | 0 | 0 |  | 0 | 0 | 0 | 0 |  |  | 0 |  |  |  | 0 |  |  | 0 |  |  |  | 0 | 0 | 0 |  |  | 0
| Dwelling Units Low End |  | 0.39
DwellingUnits530_Low |  |  |  | 530 | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A | #N/A | 0.07 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A | #N/A | #N/A |  |  | #N/A
DwellingUnits501_Low |  |  |  | 501 | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A | #N/A | 0.27 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A | #N/A | #N/A |  |  | #N/A
DwellingUnits700_Low |  |  |  | 700 | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A | #N/A | 0.05 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A | #N/A | #N/A |  |  | #N/A
| Dwelling Units High End |  | 0.78
DwellingUnits505_High |  |  |  | 505 | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A | #N/A | 0.23 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A | #N/A | #N/A |  |  | #N/A
DwellingUnits501_High |  |  |  | 501 | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A | #N/A | 0.1 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A | #N/A | #N/A |  |  | #N/A
DwellingUnits500_High |  |  |  | 500 | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A | #N/A | 0.22 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A | #N/A | #N/A |  |  | #N/A
DwellingUnits700_High |  |  |  | 700 | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A | #N/A | 0.14 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A | #N/A | #N/A |  |  | #N/A
DwellingUnits530_High |  |  |  | 530 | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A | #N/A | 0.09 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A | #N/A | #N/A |  |  | #N/A
1 FL linear fluorescent, CF compact fluorescent, MH metal halide
Interior Lighting Costs by Space Type, 2012
| Space Type Lighting Descriptions and Cost Parameters | [18 empty] | New Construction Cost |  |  | Lamp Replacement Cost |  |  |  |  | Ballast Replacement Cost
IECC 2012 Lookup Values | 2012 Space Types | Model Number | Lighting Power Allowance, LPD, W/ft2 | Fixtures - ID Number | Fixture type | Lamp Type | Lamp Wattage | Number of Lamps |  | Fixture Watts | Lamp Life, Hours | Quantity of Fixtures/ft2 | Fixture Watts/ft2 |  |  | Fixture Cost only, $/ft2 | not used | not used | not used | Labor Cost $/ft2 |  |  | Lamp Cost, $/ft2 | Labor Crew Type |  |  | Labor Cost/ft2 | Ballast Life Hours | Ballast Cost, $/ft2 | Not Used | Not Used | Labor Cost/ft2
Classroom/Lecture/Training | Classroom/Lecture/Training |  | 0.96968 | [24 empty] | 0 | #N/A |  |  | 0
Classroom/Lecture/Training535 |  | 3.1 |  | 535 | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A | #N/A | 0.72277 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A | #N/A | #N/A |  |  | #N/A
Classroom/Lecture/Training521 |  | 3.1 |  | 521 | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A | #N/A | 0.12046 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A | #N/A | #N/A |  |  | #N/A
Classroom/Lecture/Training0 |  | 3.1 |  | 0 | NA | NA | 0 | 0 |  | 0 | 0 | 0 | 0 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A | #N/A | 0 |  |  | 0
Classroom/Lecture/Training537-1 |  | 3.1 |  | 537-1 | Linear WW Open | FL | 32 | #N/A |  | #N/A | #N/A | #N/A | 0.12645 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A | #N/A | #N/A |  |  | #N/A
| Conference/Meeting/Multipurpose |  | 0.96186
Conference/Meeting/Multipurpose535 |  | 31 |  | 535 | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A | #N/A | 0.47257 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A | #N/A | #N/A |  |  | #N/A
Conference/Meeting/Multipurpose511 |  | 31 |  | 511 | Downlight open - flood | PAR | 60 | #N/A |  | #N/A | #N/A | #N/A | 0.34184 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A | #N/A | #N/A |  |  | #N/A
Conference/Meeting/Multipurpose0 |  | 31 |  | 0 | NA | NA | 0 | 0 |  | 0 | 0 | 0 | 0 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A | #N/A | 0 |  |  | 0
Conference/Meeting/Multipurpose527-1 |  | 31 |  | 527-1 | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A | #N/A | 0.14746 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A | #N/A | #N/A |  |  | #N/A
| Corridor/Transition |  | 0.51612
Corridor/Transition521 |  | 2 |  | 521 | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A | #N/A | 0.51612 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A | #N/A | #N/A |  |  | #N/A
Corridor/Transition0 |  | 2 |  | 0 | NA | NA | 0 | 0 |  | 0 | 0 | 0 | 0 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A | #N/A | 0 |  |  | 0
Corridor/Transition0 |  | 2 |  | 0 | NA | NA | 0 | 0 |  | 0 | 0 | 0 | 0 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A | #N/A | 0 |  |  | 0
Corridor/Transition527-2 |  | 2 |  | 0 | NA | NA | 0 | 0 |  | 0 | 0 | 0 | 7.8745e-08 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A | #N/A | 0 |  |  | 0
| Dining Area |  | 0.5083
Dining Area535 |  | 6 |  | 535 | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A | #N/A | 0.18761 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A | #N/A | #N/A |  |  | #N/A
Dining Area521 |  | 6 |  | 521 | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A | #N/A | 0.092006 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A | #N/A | #N/A |  |  | #N/A
Dining Area0 |  | 6 |  | 0 | NA | NA | 0 | 0 |  | 0 | 0 | 0 | 0 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A | #N/A | 0 |  |  | 0
Dining Area537-1 |  | 6 |  | 537-1 | Linear WW Open | FL | 32 | #N/A |  | #N/A | #N/A | #N/A | 0.22868 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A | #N/A | #N/A |  |  | #N/A
| Electrical/Mechanical |  | 0.7429
Electrical/Mechanical538 |  | 4 |  | 538 | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A | #N/A | 0.7429 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A | #N/A | #N/A |  |  | #N/A
Electrical/Mechanical0 |  | 4 |  | 0 | NA | NA | 0 | 0 |  | 0 | 0 | 0 | 0 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A | #N/A | 0 |  |  | 0
Electrical/Mechanical0 |  | 4 |  | 0 | NA | NA | 0 | 0 |  | 0 | 0 | 0 | 0 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A | #N/A | 0 |  |  | 0
Electrical/Mechanical0 |  | 4 |  | 0 | NA | NA | 0 | 0 |  | 0 | 0 | 0 | 7.8061e-08 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A | #N/A | 0 |  |  | 0
| Food Preparation |  | 0.77418
Food Preparation530 |  | 8 |  | 530 | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A | #N/A | 0.77418 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A | #N/A | #N/A |  |  | #N/A
Food Preparation0 |  | 8 |  | 0 | NA | NA | 0 | 0 |  | 0 | 0 | 0 | 0 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A | #N/A | 0 |  |  | 0
Food Preparation0 |  | 8 |  | 0 | NA | NA | 0 | 0 |  | 0 | 0 | 0 | 0 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A | #N/A | 0 |  |  | 0
Food Preparation0 |  | 8 |  | 0 | NA | NA | 0 | 0 |  | 0 | 0 | 0 | 7.8152e-08 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A | #N/A | 0 |  |  | 0
| Gymnasium/Fitness-Fitness Area |  | 0.56304
Gymnasium/Fitness-Fitness Area535 |  | 126 |  | 535 | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A | #N/A | 0.56304 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A | #N/A | #N/A |  |  | #N/A
Gymnasium/Fitness-Fitness Area0 |  | 126 |  | 0 | NA | NA | 0 | 0 |  | 0 | 0 | 0 | 0 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A | #N/A | 0 |  |  | 0
Gymnasium/Fitness-Fitness Area0 |  | 126 |  | 0 | NA | NA | 0 | 0 |  | 0 | 0 | 0 | 0 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A | #N/A | 0 |  |  | 0
Gymnasium/Fitness-Fitness Area0 |  | 126 |  | 0 | NA | NA | 0 | 0 |  | 0 | 0 | 0 | 7.7863e-08 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A | #N/A | 0 |  |  | 0
| Highway Lodging Guest Rooms |  | 0.5865
Highway Lodging Guest Rooms529 |  | 75.01 |  | 529 | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A | #N/A | 0.33151 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A | #N/A | #N/A |  |  | #N/A
Highway Lodging Guest Rooms520 |  | 75.01 |  | 520 | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A | #N/A | 0.25499 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A | #N/A | #N/A |  |  | #N/A
Highway Lodging Guest Rooms0 |  | 75.01 |  | 0 | NA | NA | 0 | 0 |  | 0 | 0 | 0 | 0 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A | #N/A | 0 |  |  | 0
Highway Lodging Guest Rooms0 |  | 75.01 |  | 0 | NA | NA | 0 | 0 |  | 0 | 0 | 0 | 7.7946e-08 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A | #N/A | 0 |  |  | 0
| Hospital - Laundry/Washing |  | 0.4692
Hospital - Laundry-washing530 |  | 82 |  | 530 | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A | #N/A | 0.4692 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A | #N/A | #N/A |  |  | #N/A
Hospital - Laundry-washing0 |  | 82 |  | 0 | NA | NA | 0 | 0 |  | 0 | 0 | 0 | 0 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A | #N/A | 0 |  |  | 0
Hospital - Laundry-washing0 |  | 82 |  | 0 | NA | NA | 0 | 0 |  | 0 | 0 | 0 | 0 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A | #N/A | 0 |  |  | 0
Hospital - Laundry-washing0 |  | 82 |  | 0 | NA | NA | 0 | 0 |  | 0 | 0 | 0 | 7.88e-08 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A | #N/A | 0 |  |  | 0
| Library |  | 0.72726
Library535 |  | 19 |  | 535 | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A | #N/A | 0.30715 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A | #N/A | #N/A |  |  | #N/A
Library520 |  | 19 |  | 520 | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A | #N/A | 0.42011 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A | #N/A | #N/A |  |  | #N/A
Library0 |  | 19 |  | 0 | NA | NA | 0 | 0 |  | 0 | 0 | 0 | 0 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A | #N/A | 0 |  |  | 0
Library0 |  | 19 |  | 0 | NA | NA | 0 | 0 |  | 0 | 0 | 0 | 7.81e-08 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A | #N/A | 0 |  |  | 0
| Lounge/Recreation - Break room |  | 0.57086
Lounge/Recreation - Breakroom521 |  | 9 |  | 521 | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A | #N/A | 0.34023 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A | #N/A | #N/A |  |  | #N/A
Lounge/Recreation - Breakroom0 |  | 9 |  | 0 | NA | NA | 0 | 0 |  | 0 | 0 | 0 | 0 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A | #N/A | 0 |  |  | 0
Lounge/Recreation - Breakroom0 |  | 9 |  | 0 | NA | NA | 0 | 0 |  | 0 | 0 | 0 | 0 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A | #N/A | 0 |  |  | 0
Lounge/Recreation - Breakroom527-2 |  | 9 |  | 527-2 | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A | #N/A | 0.23063 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A | #N/A | #N/A |  |  | #N/A
| Lobby |  | 0.7038
Lobby523 |  | 20.1 |  | 523 | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A | #N/A | 0.39256 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A | #N/A | #N/A |  |  | #N/A
Lobby521 |  | 20.1 |  | 521 | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A | #N/A | 0.18501 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A | #N/A | #N/A |  |  | #N/A
Lobby0 |  | 20.1 |  | 0 | NA | NA | 0 | 0 |  | 0 | 0 | 0 | 0 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A | #N/A | 0 |  |  | 0
Lobby534-2 |  | 20.1 |  | 534-2 | Linear Wall Cove | FL | 32 | #N/A |  | #N/A | #N/A | #N/A | 0.12623 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A | #N/A | #N/A |  |  | #N/A
| Office-Enclosed |  | 0.86802
Office-Enclosed531 |  | 25 |  | 531 | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A | #N/A | 0.52789 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A | #N/A | #N/A |  |  | #N/A
Office-Enclosed539 |  | 25 |  | 539 | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A | #N/A | 0.14563 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A | #N/A | #N/A |  |  | #N/A
Office-Enclosed0 |  | 25 |  | 0 | NA | NA | 0 | 0 |  | 0 | 0 | 0 | 0 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A | #N/A | 0 |  |  | 0
Office-Enclosed537-1 |  | 25 |  | 537-1 | Linear WW Open | FL | 32 | #N/A |  | #N/A | #N/A | #N/A | 0.1945 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A | #N/A | #N/A |  |  | #N/A
| Office - Open Plan (Including Other) |  | 0.76636
Office - Open Plan (Including Other)535 |  | 27 |  | 535 | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A | #N/A | 0.56456 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A | #N/A | #N/A |  |  | #N/A
Office - Open Plan (Including Other)539 |  | 27 |  | 539 | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A | #N/A | 0.075873 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A | #N/A | #N/A |  |  | #N/A
Office - Open Plan (Including Other)0 |  | 27 |  | 0 | NA | NA | 0 | 0 |  | 0 | 0 | 0 | 0 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A | #N/A | 0 |  |  | 0
Office - Open Plan (Including Other)537-1 |  | 27 |  | 537-1 | Linear WW Open | FL | 32 | #N/A |  | #N/A | #N/A | #N/A | 0.12593 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A | #N/A | #N/A |  |  | #N/A
| Restrooms |  | 0.76636
Restrooms604 |  | 12 |  | 604 | Wall Mounted Linear Direct/Indirect | FL | 32 | #N/A |  | #N/A | #N/A | #N/A | 0.22551 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A | #N/A | #N/A |  |  | #N/A
Restrooms520 |  | 12 |  | 520 | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A | #N/A | 0.34783 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A | #N/A | #N/A |  |  | #N/A
Restrooms0 |  | 12 |  | 0 | NA | NA | 0 | 0 |  | 0 | 0 | 0 | 0 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A | #N/A | 0 |  |  | 0
Restrooms534-2 |  | 12 |  | 534-2 | Linear Wall Cove | FL | 32 | #N/A |  | #N/A | #N/A | #N/A | 0.19301 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A | #N/A | #N/A |  |  | #N/A
| Retail - Sales Area |  | 1.3138
Retail - Sales Area535 |  | 97 |  | 535 | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A | #N/A | 0.79579 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A | #N/A | #N/A |  |  | #N/A
Retail - Sales Area541 |  | 97 |  | 541 | #N/A |  | #N/A | #N/A |  | #N/A | #N/A | #N/A | 0.39413 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A | #N/A | #N/A |  |  | #N/A
Retail - Sales Area0 |  | 97 |  | 0 | NA | NA | 0 | 0 |  | 0 | 0 | 0 | 0 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A | #N/A | 0 |  |  | 0
Retail - Sales Area537-1 |  | 97 |  | 537-1 | Linear WW Open | FL | 32 | #N/A |  | #N/A | #N/A | #N/A | 0.12384 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A | #N/A | #N/A |  |  | #N/A
| Stairway |  | 0.53958
Stairway530 |  | 11 |  | 530 | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A | #N/A | 0.29111 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A | #N/A | #N/A |  |  | #N/A
Stairway602 |  | 11 |  | 602 | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A | #N/A | 0.24847 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A | #N/A | #N/A |  |  | #N/A
Stairway0 |  | 11 |  | 0 | NA | NA | 0 | 0 |  | 0 | 0 | 0 | 0 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A | #N/A | 0 |  |  | 0
Stairway0 |  | 11 |  | 0 | NA | NA | 0 | 0 |  | 0 | 0 | 0 | 7.8143e-08 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A | #N/A | 0 |  |  | 0
| Storage |  | 0.49266
Storage538 |  | 41 |  | 538 | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A | #N/A | 0.49266 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A | #N/A | #N/A |  |  | #N/A
Storage0 |  | 41 |  | 0 | NA | NA | 0 | 0 |  | 0 | 0 | 0 | 0 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A | #N/A | 0 |  |  | 0
Storage0 |  | 41 |  | 0 | NA | NA | 0 | 0 |  | 0 | 0 | 0 | 0 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A | #N/A | 0 |  |  | 0
Storage0 |  | 41 |  | 0 | NA | NA | 0 | 0 |  | 0 | 0 | 0 | 7.765e-08 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A | #N/A | 0 |  |  | 0
| Lobby - Hotel |  | 0.82892
Lobby - Hotel572 |  | 79 |  | 572 | Downlight open | TH | 75 | #N/A |  | #N/A | #N/A | #N/A | 0.70293 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A | #N/A | #N/A |  |  | #N/A
Lobby - Hotel0 |  | 79 |  | 0 | NA | NA | 0 | 0 |  | 0 | 0 | 0 | 0 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A | #N/A | 0 |  |  | 0
Lobby - Hotel0 |  | 79 |  | 0 | NA | NA | 0 | 0 |  | 0 | 0 | 0 | 0 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A | #N/A | 0 |  |  | 0
Lobby - Hotel527-1 |  | 79 |  | 527-1 | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A | #N/A | 0.12599 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A | #N/A | #N/A |  |  | #N/A
| Dwelling Units Low End |  | 0.3
DwellingUnits501_Low |  |  |  | 501 | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A | #N/A | 0.13 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A | #N/A | #N/A |  |  | #N/A
DwellingUnits700_Low |  |  |  | 700 | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A | #N/A | 0.1 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A | #N/A | #N/A |  |  | #N/A
DwellingUnits530_Low |  |  |  | 530 | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A | #N/A | 0.07 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A | #N/A | #N/A |  |  | #N/A
| Dwelling Units High End |  | 0.62
DwellingUnits505_High |  |  |  | 505 | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A | #N/A | 0.23 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A | #N/A | #N/A |  |  | #N/A
DwellingUnits500_High |  |  |  | 500 | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A | #N/A | 0.08 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A | #N/A | #N/A |  |  | #N/A
DwellingUnits700_High |  |  |  | 700 | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A | #N/A | 0.18 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A | #N/A | #N/A |  |  | #N/A
DwellingUnits701_High |  |  |  | 701 | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A | #N/A | 0.04 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A | #N/A | #N/A |  |  | #N/A
DwellingUnits530_High |  |  |  | 530 | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A | #N/A | 0.09 |  |  | #N/A |  |  |  | #N/A |  |  | #N/A |  |  |  | #N/A | #N/A | #N/A |  |  | #N/A
1 FL linear fluorescent, CF compact fluorescent, MH metal halide
Note on D87: Susan Loper: Refer to workbook Dwelling Units 4/22/13
Note on D290: Susan Loper: Refer to workbook - Dwelling Units 4/22/13
Dwelling Units - Dwelling units were added to IECC 2009, 2012 and NC. For 2009 and NC - 50% of lamps were INC and 50% were HE. For 2012 - 25% of lamps were INC and 75% were HE. INC lamps were replaced with CF to convert to HE.

## IntLtgCostCheck (hidden)
Note: Pivot Tables to right query spaces
"Refresh" (right click) both pivot tables to right after changes to update table below
Note: where LPA increases;
[9 empty] | space design/cost remains the same | [37 empty] | This pivot only captures the space totals
|  | Green indicates cost is low relative to LPD change, Red high | [9 empty] | Should match +/- 1% |  | Should match +/- 5%-10% | [18 empty] | Check of totals on the Int Ltg LPD Space Type 90_1 All tab
| Checking 2018oct24 | [32 empty] | Data | Case | [12 empty] | Data | Case
| Space | New cost/sf |  |  | Fixture LPD w/sf |  |  |  | Space LPA w/sf |  |  | Fixt LPD/Space LPA |  | Space net Lum/sf |  |  |  | Sp/Fx LPD |  |  | Space Type LPA W/ft2 |  | Fixture LPD W/ft2 |  |  | Cost $/ft2 |  |  | Lumen Compare |  |  |  |  | Sum of Space Type Lighting Power Allowance W/ft24 |  |  | Sum of Fixture Watts/ft214 |  |  | Sum of New_Fixture + Lamp Cost, $/ft2_17 |  |  | Count of 90.1-2013 Space Types2 |  |  |  |  | Sum of Space Type Lighting Power Allowance W/ft24 |  |  | Count of 90.1-2013 Space Types2
|  | 2016 | 2019 | dCost | 2016 | 2019 | dLPD | d$/dLPD | 2016 | 2019 | dLPA | 2016 | 2019 | 2016 | 2019 | dLum |  | 2010 | 2013 |  | 2013 | 2016 | 2013 | 2016 | dLPD | 2013 | 2016 | d$/dLPD | 2013 | 2016 |  |  | space | 2016 | 2013 | 2019 | 2016 | 2013 | 2019 | 2016 | 2013 | 2019 | 2016 | 2013 | 2019 |  | 90.1-2019 Space Types2 | 2013 | 2016 | 2019 | 2013 | 2016 | 2019
| Classroom/Lecture/Training | 17.4638 | 17.4236 | 0.9977 | 0.92 | 1.24 | 1.3478 | 0.74023 | 1.24 | 0.92 | 0.74194 | 0.74194 | 1.3478 | 1 | 1 | 1 |  | 1 | 10.8235 | Classroom/Lecture/Training | 0.92 | 0.71 | 0.71 | 0.17 | 4.5962 | 0.92 | 0.55 | 0.11966 | 1 | 1 |  |  | Classroom/Lecture/Training | 0.71 | 1.84 | 0.71 | 0.17 | 0.92 | 0.55 | 6.9764 | 10.9792 | 2.3774 | 1 | 1 |  |  | Classroom/Lecture/Training | 0.92 | 0.71 |  | 1 | 1
| Conference/Meeting/Multipurpose | 1.08 | 0 | 0 | 0 | 0.96 |  | #VALUE! | 1.07 | 0.97 | 0.90654 | 0 | 0.98969 | 0 | 1 | #DIV/0! |  | #DIV/0! | 2.2396 | Conference/Meeting/Multipurpose | 1.07 | 0.97 | 0 | 0.96 | 7.2976 | 1.08 | 0 | 0 | 0 | 1 |  |  | Conference/Meeting/Multipurpose | 1.93 | 2.15 |  | 0.96 | 1.08 |  | 14.5928 | 14.5952 |  | 1 | 1 |  |  | Conference/Meeting/Multipurpose | 1.07 | 0.97 |  | 1 | 1
| Corridor/Transition | 0.66 | 0 | 0 | 0 | 0.41 |  | #VALUE! | 0.66 | 0.41 | 0.62121 | 0 | 1 | 0 | 1 | #DIV/0! |  | #DIV/0! | 3.2195 | Corridor/Transition | 0.66 | 0.41 | 0 | 0.41 | 6.8675 | 0.66 | 0 | 0 | 0 | 1 |  |  | Corridor/Transition | 0.82 | 1.32 |  | 0.41 | 0.66 |  | #VALUE! | 16.2017 |  | 1 | 1 |  |  | Corridor/Transition | 0.66 | 0.41 |  | 1 | 1
| Dining Area | 0.63 | 0 | 0 | 0 | 0.43 |  | #VALUE! | 0.63 | 0.43 | 0.68254 | 0 | 1 | 0 | 1 | #DIV/0! |  | #DIV/0! | 2.9302 | Dining Area | 0.63 | 0.43 | 0 | 0.43 | 6.3549 | 0.63 | 0 | 0 | 0 | 1 |  |  | Dining Area | 0.86 | 1.26 |  | 0.43 | 0.63 |  | #VALUE! | 8.3012 |  | 1 | 1 |  |  | Dining Area | 0.63 | 0.43 |  | 1 | 1
| Electrical/Mechanical | 0.43 | 0 | 0 | 0 | 0.43 |  | #VALUE! | 0.43 | 0.43 | 1 | 0 | 1 | 0 | 1 | #DIV/0! |  | #DIV/0! | 2 | Electrical/Mechanical | 0.43 | 0.43 | 0 | 0.43 | 4.0775 | 0.43 | 0 | 0 | 0 | 1 |  |  | Electrical/Mechanical | 0.86 | 0.86 |  | 0.43 | 0.43 |  | #VALUE! | 8.1549 |  | 1 | 1 |  |  | Dwelling-Unit | 0.5805 |  |  | 2
| Food Preparation | 1.06 | 4.1599 | 3.9244 | 0 | 1.09 |  | #VALUE! | 1.06 | 1.09 | 1.0283 | 0 | 1 | 0 | 1 | #DIV/0! |  | #DIV/0! | 1.945 | Food Preparation | 1.06 | 1.09 | 0 | 1.09 | 9.3639 | 1.06 | 4.1599 | 0.44425 | 0 | 1 |  |  | Food Preparation | 2.18 | 2.12 |  | 1.09 | 1.06 |  | 9.29 | 18.7278 |  | 1 | 1 |  |  | Electrical/Mechanical | 0.43 | 0.43 |  | 1 | 1
| Gymnasium/Fitness-Fitness Area | 0.5 | 0 | 0 | 0 | 0.7 |  | #VALUE! | 0.5 | 0.7 | 1.4 | 0 | 1 | 0 | 1 | #DIV/0! |  | #DIV/0! | 1.4286 | Gymnasium/Fitness-Fitness Area | 0.5 | 0.7 | 0 | 0.7 | 4.6103 | 0.5 | 0 | 0 | 0 | 1 |  |  | Gymnasium/Fitness-Fitness Area | 1.4 | 1 |  | 0.7 | 0.5 |  | #VALUE! | 17.6232 |  | 1 | 1 |  |  | Food Preparation | 1.06 | 1.09 |  | 1 | 1
| Highway Lodging Guest Rooms | 0.77 | 0 | 0 | 0 | 0.41 |  | #VALUE! | 0.77 | 0.41 | 0.53247 | 0 | 1 | 0 | 1 | #DIV/0! |  | #DIV/0! | 3.7561 | Highway Lodging Guest Rooms | 0.77 | 0.41 | 0 | 0.41 | 2.409 | 0.77 | 0 | 0 | 0 | 1 |  |  | Highway Lodging Guest Rooms | 0.82 | 1.54 |  | 0.41 | 0.77 |  | 10.2941 | 5.5123 |  | 1 | 1 |  |  | Gymnasium/Fitness-Fitness Area | 0.5 | 0.7 |  | 1 | 1
| Library | 0.82 | 0 | 0 | 0 | 0.95 |  | #VALUE! | 0.82 | 0.96 | 1.1707 | 0 | 0.98958 | 0 | 1 | #DIV/0! |  | #DIV/0! | 1.7263 | Library | 0.82 | 0.96 | 0 | 0.95 | 5.9143 | 0.82 | 0 | 0 | 0 | 1 |  |  | Library | 1.91 | 1.64 |  | 0.95 | 0.82 |  | 31.5131 | 22.5362 |  | 1 | 1 |  |  | Highway Lodging Guest Rooms | 0.77 | 0.41 |  | 1 | 1
| Lobby | 1 | 0 | 0 | 0 | 0.84 |  | #VALUE! | 1 | 0.84 | 0.84 | 0 | 1 | 0 | 1 | #DIV/0! |  | #DIV/0! | 2.381 | Lobby | 1 | 0.84 | 0 | 0.84 | 10.6199 | 1 | 0 | 0 | 0 | 1 |  |  | Lobby | 1.68 | 2 |  | 0.84 | 1 |  | 23.3687 | 26.2231 |  | 1 | 1 |  |  | Laundry-Washing | 0.43 | 0.53 |  | 1 | 1
| Lobby - Hotel | 1.06 | 0 | 0 | 0 | 0.5 |  | #VALUE! | 1.06 | 0.51 | 0.48113 | 0 | 0.98039 | 0 | 1 | #DIV/0! |  | #DIV/0! | 4.24 | Lobby - Hotel | 1.06 | 0.51 | 0 | 0.5 | 2.753 | 1.06 | 0 | 0 | 0 | 1 |  |  | Lobby - Hotel | 1.01 | 2.12 |  | 0.5 | 1.06 |  | 8.9145 | 5.5059 |  | 1 | 1 |  |  | Library | 0.82 | 0.96 |  | 1 | 1
| Lounge/Recreation - Break room | #N/A | #N/A |  | #N/A | #N/A |  | #VALUE! | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A |  | #DIV/0! | 2.6557 | Lounge/Recreation - Break room | #N/A | #N/A | #N/A | #N/A | 5.4144 | #N/A | #N/A | #N/A | #N/A | #N/A |  |  | Office - Open Plan (Including Other) | 1.22 | 1.62 |  | 0.61 | 0.81 |  | 12.0268 | 24.7504 |  | 1 | 1 |  |  | Lobby | 1 | 0.84 |  | 1 | 1
Flu-LED | Office - Open Plan (Including Other) | 0.81 | 0 | 0 | 0 | 0.61 |  | #VALUE! | 0.81 | 0.61 | 0.75309 | 0 | 1 | 0 | 1 | #DIV/0! |  | #DIV/0! | 2.5135 | Office - Open Plan (Including Other) | 0.81 | 0.61 | 0 | 0.61 | 8.1739 | 0.81 | 0 | 0 | 0 | 1 |  |  | Office-Enclosed | 1.48 | 1.86 |  | 0.74 | 0.93 |  | 6.3973 | 11.8113 |  | 1 | 1 |  |  | Lobby - Hotel | 1.06 | 0.51 |  | 1 | 1
Flu-LED | Office-Enclosed | 0.93 | 0 | 0 | 0 | 0.74 |  | #VALUE! | 0.93 | 0.74 | 0.7957 | 0 | 1 | 0 | 1 | #DIV/0! |  | #DIV/0! | 2.6912 | Office-Enclosed | 0.93 | 0.74 | 0 | 0.74 | 6.1849 | 0.93 | 0 | 0 | 0 | 1 |  |  | Restrooms | 1.26 | 1.7 |  | 0.6317 | 0.85 |  | #VALUE! | 19.5071 |  | 1 | 1 |  |  | Lounge/Recreation - Breakroom | 0.62 | 0.59 |  | 1 | 1
| Restrooms | 0.85 | 0 | 0 | 0 | 0.6317 |  | #VALUE! | 0.85 | 0.63 | 0.74118 | 0 | 1.0027 | 0 | 1 | #DIV/0! |  | #DIV/0! | 2.3143 | Restrooms | 0.85 | 0.63 | 0 | 0.6317 | 7.4616 | 0.85 | 0 | 0 | 0 | 1 |  |  | Retail - Sales Area | 2.1 | 2.43 |  | 1.05 | 1.21 |  | 13.8554 | 12.6761 |  | 1 | 1 |  |  | Office - Open Plan (Including Other) | 0.81 | 0.61 |  | 1 | 1
| Retail - Sales Area | 1.21 | 0 | 0 | 0 | 1.05 |  | #VALUE! | 1.22 | 1.05 | 0.86066 | 0 | 1 | 0 | 1 | #DIV/0! |  | #DIV/0! | 2.3967 | Retail - Sales Area | 1.22 | 1.05 | 0 | 1.05 | 6.9238 | 1.21 | 0 | 0 | 0 | 1 |  |  | Stairway | 0.974 | 1.16 |  | 0.484 | 0.58 |  | #VALUE! | 10.7401 |  | 1 | 1 |  |  | Office - Open Plan (Including Other)-whole | 0.81 | 0.61 |  | 1 | 1
| Stairway | 0.58 | 0 | 0 | 0 | 0.484 |  | #VALUE! | 0.58 | 0.49 | 0.84483 | 0 | 0.98776 | 0 | 1 | #DIV/0! |  | #DIV/0! | 2.4211 | Stairway | 0.58 | 0.49 | 0 | 0.484 | 5.3461 | 0.58 | 0 | 0 | 0 | 1 |  |  | Storage | 0.76 | 0.92 |  | 0.38 | 0.46 |  | 3.52 | 6.0618 |  | 1 | 1 |  |  | Office - Open Plan (Including Other)-whole-large |  | 0.61 |  |  | 1
| Storage | 0.46 | 2.0573 | 4.4723 | 0 | 0.38 |  | #VALUE! | 0.46 | 0.38 | 0.82609 | 0 | 1 | 0 | 1 | #DIV/0! |  | #DIV/0! | 2.6557 | Storage | 0.46 | 0.38 | 0 | 0.38 | 3.0309 | 0.46 | 2.0573 | 0.67876 | 0 | 1 |  |  | Office - Open Plan (Including Other)-whole | 1.22 | 1.62 |  | 0.61 | 0.81 |  | #VALUE! | 24.7504 |  | 1 | 1 |  |  | Office - Open Plan (Including Other)-whole-small | 0.81 |  |  | 1
| Office - Open Plan (Including Other)-whole | 0.81 | 0 | 0 | 0 | 0.61 |  | #VALUE! | 0.81 | 0.61 | 0.75309 | 0 | 1 | 0 | 1 | #DIV/0! |  | #DIV/0! | 1.6226 | Office - Open Plan (Including Other)-whole | 0.81 | 0.61 | 0 | 0.61 | 8.7794 | 0.81 | 0 | 0 | 0 | 1 |  |  | Laundry-Washing | 1.06 | 0.86 |  | 0.53 | 0.43 |  | #VALUE! | 4.0845 |  | 1 | 1 |  |  | Office-BLDG-LO | 0.79 | 0.64 |  | 1 | 1
| Laundry-Washing | 0.43 | 0 | 0 | 0 | 0.53 |  | #VALUE! | 0.43 | 0.53 | 1.2326 | 0 | 1 | 0 | 1 | #DIV/0! |  |  |  | Laundry-Washing | 0.43 | 0.53 | 0 | 0.53 | 2.0422 | 0.43 | 0 |  | 0 | 1 |  |  | Office-BLDG-SO | 1.28 | 1.5832 |  | 0.64 | 0.7932 |  | 24.8948 | 27.0271 |  | 1 | 1 |  |  | Office-BLDG-SO | 0.79 | 0.64 |  | 1 | 1
Flu-Flu | Office-BLDG-SO | 0.7932 | 0 | 0 | 0 | 0.64 |  | #VALUE! | 0.79 | 0.64 | 0.81013 | 0 | 1 | 0 | 1 | #DIV/0! |  |  |  | Office-BLDG-SO | 0.79 | 0.64 | 0 | 0.64 | 5.912 | 0.7932 | 0 |  | 0 | 1 |  |  | Office-BLDG-LO | 1.28 | 1.5832 |  | 0.64 | 0.7932 |  | #VALUE! | 27.0271 |  | 1 | 1 |  |  | Office-Enclosed | 0.93 | 0.74 |  | 1 | 1
Flu-Flu | Office-BLDG-LO | 0.7932 | 0 | 0 | 0 | 0.64 |  | #VALUE! | 0.79 | 0.64 | 0.81013 | 0 | 1 | 0 | 1 | #DIV/0! |  |  |  | Office-BLDG-LO | 0.79 | 0.64 | 0 | 0.64 | 5.912 | 0.7932 | 0 |  | 0 | 1 |  |  | Office-Enclosed-whole-small |  | 1.758 |  |  | 0.88 |  |  | 11.0683 |  |  | 1 |  |  | Office-Enclosed-whole |  | 0.74 |  |  | 1
| Office-Enclosed-whole-small | 0.88 | 0 | 0 | 0 | 0 |  | #VALUE! | 0.878 | 0 |  | 0 | #DIV/0! | 0 | 1 |  |  |  |  | Office-Enclosed-whole-small | 0.878 | 0 | 0 | 0 |  | 0.88 | 0 |  | 0 | 1 |  |  | Office - Open Plan (Including Other)-whole-small |  | 1.62 |  |  | 0.81 |  |  | 24.7504 |  |  | 1 |  |  | Office-Enclosed-whole-large | 0.826 | 0.74 |  | 1 | 1
| Office - Open Plan (Including Other)-whole-small | 0.81 | 0 | 0 | 0 | 0 |  | #VALUE! | 0.81 | 0 |  | 0 | #DIV/0! | 0 | 1 |  |  |  |  | Office - Open Plan (Including Other)-whole-small | 0.81 | 0 | 0 | 0 |  | 0.81 | 0 |  | 0 | 1 |  |  | Office-Enclosed-whole-large | 1.48 | 1.656 |  | 0.74 | 0.83 |  | #VALUE! | 10.5046 |  | 1 | 1 |  |  | Office-Enclosed-whole-small | 0.878 |  |  | 1
| Office-Enclosed-whole-large | 0.83 | 0 | 0 | 0 | 0.74 |  | #VALUE! | 0.826 | 0.74 |  | 0 | 1 | 0 | 1 |  |  |  |  | Office-Enclosed-whole-large | 0.826 | 0.74 | 0 | 0.74 | 5.4348 | 0.83 | 0 |  | 0 | 1 |  |  | Office - Open Plan (Including Other)-whole-large | 1.22 |  |  | 0.61 |  |  | #VALUE! |  |  | 1 |  |  |  | Restrooms | 0.85 | 0.63 |  | 1 | 1
| Office - Open Plan (Including Other)-whole-large | 0 | 0 |  | 0 | 0.61 |  | #VALUE! | 0 | 0.61 |  | #DIV/0! | 1 | 0 | 0 |  |  |  |  | Office - Open Plan (Including Other)-whole-large | 0 | 0.61 | 0 | 0.61 | 8.3555 | 0 | 0 |  | 0 | 0 |  |  | Lounge/Recreation - Breakroom | 1.15 | 1.249 |  | 0.56 | 0.629 |  | #VALUE! | 21.3949 |  | 1 | 1 |  |  | Retail - Sales Area | 1.22 | 1.05 |  | 1 | 1
| Grand Total | #N/A | #N/A |  | #N/A | #N/A |  | #VALUE! | #N/A | #N/A |  | #N/A | #N/A | #N/A | #N/A |  |  |  |  | Grand Total | #N/A | #N/A | #N/A | #N/A | 8.3555 | #N/A | #N/A |  | #N/A | #N/A |  |  | Total Result | 30.664 | 39.4694 | 0.71 | 15.1157 | 19.7454 | 0.55 | #VALUE! | 390.5148 | 2.3774 | 24 | 25 |  |  | Stairway | 0.58 | 0.49 |  | 1 | 1
| 0 | #N/A | #N/A |  | #N/A | #N/A |  | #VALUE! | #N/A | #N/A |  | #N/A | #N/A | #N/A | #N/A |  |  |  |  | 0 | #N/A | #N/A | #N/A | #N/A | 8.3555 | #N/A | #N/A |  | #N/A | #N/A | [12 empty] | #DIV/0! | #DIV/0! |  |  | Storage | 0.46 | 0.38 |  | 1 | 1
| 0 | 0 | 0 |  | 0 | 0 |  | #VALUE! | 0 | 0 |  | #DIV/0! | #DIV/0! | 0 | 0 | [27 empty] | #DIV/0! | #DIV/0! |  |  | (empty) | 20.3259 | 15.684 | 0.71
| 0 | 0 | 0 |  | 0 | 0 |  | #VALUE! | 0 | 0 |  | #DIV/0! | #DIV/0! | 0 | 0 | [31 empty] | Total Result | 40.6304 | 32.144 | 0.71 | 27 | 25
| Checking version 2014jul14n5SL3 | Round 1 | 41876
|  | New cost/sf |  |  | LPD w/sf
| Space | 2010 | 2013 | dCost | 2010 | 2013 | dLPD | d$/dLPD
| Highway Lodging Guest Rooms | 4.1071 | 4.1071 | 1 | 0.75 | 0.91 | 1.2133 | 0.82418
| Retail - Sales Area | 6.4741 | 4.9244 | 0.76063 | 1.68 | 1.42 | 0.84524 | 0.8999
| Food Preparation | 3.4769 | 4.2496 | 1.2222 | 0.99 | 1.21 | 1.2222 | 1
| Library | 4.0293 | 4.9392 | 1.2258 | 0.93 | 1.06 | 1.1398 | 1.0755
| Electrical/Mechanical | 1.9165 | 0.99295 | 0.51811 | 0.95 | 0.42 | 0.44211 | 1.1719
|  | New cost/sf |  |  | LPD w/sf
| Space | 2010 | 2013 | dCost | 2010 | 2013 | dLPD | d$/dLPD
| Classroom/Lecture/Training | 6.4506 | 6.1622 | 0.95529 | 1.24 | 1.24 | 1 | 0.95529 | Why Delta?
| Corridor/Transition | 2.0588 | 2.1596 | 1.049 | 0.66 | 0.66 | 1 | 1.049 | Why Delta?
| Lobby - Hotel | 0.74687 | 1.4267 | 1.9102 | 1.06 | 1.06 | 1 | 1.9102 | Why Delta?
| Lounge/Recreation - Break room | 3.2317 | 1.9192 | 0.59387 | 0.73 | 0.73 | 1 | 0.59387 | Why Delta?
| Office - Open Plan (Including Other) | 4.9776 | 4.5956 | 0.92325 | 0.98 | 0.98 | 1 | 0.92325 | Why Delta?
| Office-Enclosed | 5.123 | 5.1309 | 1.0015 | 1.11 | 1.11 | 1 | 1.0015 | Why Delta?
| Stairway | 2.4233 | 3.3134 | 1.3673 | 0.69 | 0.69 | 1 | 1.3673 | Why Delta?
|  | New cost/sf |  |  | LPD w/sf
| Space | 2010 | 2013 | dCost | 2010 | 2013 | dLPD | d$/dLPD
| Conference/Meeting/Multipurpose | 5.4214 | 5.4214 | 1 | 1.23 | 1.23 | 1 | 1
| Dining Area | 3.3865 | 3.3865 | 1 | 0.65 | 0.65 | 1 | 1
| Gymnasium/Fitness-Fitness Area | 3.6489 | 3.6489 | 1 | 0.72 | 0.72 | 1 | 1
| Hospital - Laundry/Washing | 2.1072 | 2.1072 | 1 | 0.6 | 0.6 | 1 | 1
| Lobby | 3.455 | 3.455 | 1 | 0.9 | 0.9 | 1 | 1
| Restrooms | 3.6893 | 3.6893 | 1 | 0.98 | 0.98 | 1 | 1
| Storage | 1.2709 | 1.2709 | 1 | 0.63 | 0.63 | 1 | 1
Check of fixture detail on the Int Ltg LPD Space Type 90_1 All tab
[31 empty] | 2010 |  |  | 2013
[31 empty] | case_data | Data
[31 empty] | 2013 |  | 2016 |  | 2019
[30 empty] | space | Sum of Number of Lamps9 | Sum of Fixture Watts/ft214 | Sum of Number of Lamps9 | Sum of Fixture Watts/ft214 | Sum of Number of Lamps9 | Sum of Fixture Watts/ft214 |  |  | Data
[30 empty] | Classroom/Lecture/Training | 127 | 0.92 | 70 | 0.17 | 32 | 0.55 | Proto | Space | Average of area2010 | Average of area2013 | Sum of LPD2010 | Sum of LPD2013 | Sum of Tot2010 | Sum of Tot2013
[30 empty] | Conference/Meeting/Multipurpose | 61 | 1.08 | 116 | 0.96 |  |  | LgOfc |  | 498600 | 498600 | 0.79 | 0.64 | 11714643.2162 | 10793603.292
[30 empty] | Corridor/Transition | 87 | 0.66 | 65 | 0.41 |  |  |  | Office-BLDG-LO | 498600 | 498600 | 0.79 | 0.64 | 11714643.2162 | 10793603.292
[30 empty] | Dining Area | 59 | 0.63 | 98 | 0.43 |  |  | MrApt |  | 11248.3333 | 11248.3333 | 1.88 | 1.4405 | 69812.6818 | 47622.0429
[30 empty] | Electrical/Mechanical | 48 | 0.43 | 47 | 0.43 |  |  |  | Corridor/Transition | 3345 | 3345 | 0.66 | 0.41 | 55900.2195 | 39135.9026
[30 empty] | Food Preparation | 80 | 1.06 | 67 | 1.09 |  |  |  | Office-Enclosed | 950 | 950 | 0.93 | 0.74 | 13110.7681 | 7217.5325
[30 empty] | Gymnasium/Fitness-Fitness Area | 38 | 0.5 | 33 | 0.7 |  |  |  | Dwelling-Unit | 29450 | 29450 | 0.29 | 0.2905 | 801.6943 | 1268.6077
[30 empty] | Highway Lodging Guest Rooms | 24 | 0.77 | 81 | 0.41 |  |  | PriSch |  | 8478.875 | 8478.875 | 5.92 | 4.89 | 924822.8814 | 778120.4685
[30 empty] | Library | 60 | 0.82 | 54 | 0.95 |  |  |  | Classroom/Lecture/Training | 37187 | 37187 | 0.92 | 0.71 | 466155.3389 | 381994.9966
[30 empty] | Lobby | 65 | 1 | 94 | 0.84 |  |  |  | Corridor/Transition | 12073 | 12073 | 0.66 | 0.41 | 201758.8489 | 141251.9438
[30 empty] | Lobby - Hotel | 21 | 1.06 | 77 | 0.5 |  |  |  | Dining Area | 3389 | 3389 | 0.63 | 0.43 | 31459.0629 | 38228.7343
[30 empty] | Office - Open Plan (Including Other) | 123 | 0.81 | 101 | 0.61 |  |  |  | Electrical/Mechanical | 2712 | 2712 | 0.43 | 0.43 | 21681.1351 | 19898.6668
[30 empty] | Office-Enclosed | 46 | 0.93 | 32 | 0.74 |  |  |  | Gymnasium/Fitness-Fitness Area | 3841 | 3841 | 0.5 | 0.7 | 58820.6788 | 94819.9481
[30 empty] | Restrooms | 24 | 0.85 | 39 | 0.6317 |  |  |  | Lobby | 1840 | 1840 | 1 | 0.84 | 43420.4959 | 39159.4028
[30 empty] | Retail - Sales Area | 83 | 1.21 | 73 | 1.05 |  |  |  | Office-Enclosed | 4745 | 4745 | 0.93 | 0.74 | 65484.8363 | 36049.6757
[30 empty] | Stairway | 59 | 0.58 | 53 | 0.484 |  |  |  | Restrooms | 2044 | 2044 | 0.85 | 0.63 | 36042.4846 | 26717.1004
[30 empty] | Storage | 38 | 0.46 | 37 | 0.38 |  |  | SmHtl |  | 3601.0833 | 3601.0833 | 8.36 | 6.79 | 381178.8247 | 410803.5574
[30 empty] | Office-Enclosed-whole |  |  | 32 | 0.74 |  |  |  | Conference/Meeting/Multipurpose | 864 | 864 | 1.07 | 0.97 | 12764.2245 | 12623.1293
[30 empty] | Office - Open Plan (Including Other)-whole | 123 | 0.81 | 91 | 0.61 |  |  |  | Corridor/Transition | 5668 | 5668 | 0.66 | 0.41 | 94721.209 | 66314.5877
[30 empty] | Laundry-Washing | 40 | 0.43 | 35 | 0.53 |  |  |  | Electrical/Mechanical | 351 | 351 | 0.43 | 0.43 | 2806.0761 | 2575.3805
[30 empty] | Office-BLDG-SO | 123 | 0.7932 | 91 | 0.64 |  |  |  | Gymnasium/Fitness-Fitness Area | 351 | 351 | 0.5 | 0.7 | 5375.1779 | 8664.8794
[30 empty] | Office-BLDG-LO | 123 | 0.7932 | 91 | 0.64 |  |  |  | Highway Lodging Guest Rooms | 27933 | 27933 | 0.77 | 0.41 | 187596.1627 | 258863.2926
[30 empty] | Office-Enclosed-whole-small | 46 | 0.88 | [5 empty] | Lobby - Hotel | 1755 | 1755 | 1.06 | 0.51 | 11496.214 | 15919.9488
[30 empty] | Office - Open Plan (Including Other)-whole-small | 123 | 0.81 | [5 empty] | Office-Enclosed | 1404 | 1404 | 0.93 | 0.74 | 19376.3351 | 10666.7534
[30 empty] | Office-Enclosed-whole-large | 46 | 0.83 | 32 | 0.74 |  |  |  | Restrooms | 351 | 351 | 0.85 | 0.63 | 6189.2916 | 4587.9169
[30 empty] | Office - Open Plan (Including Other)-whole-large |  |  | 101 | 0.61 |  |  |  | Stairway | 1728 | 1728 | 0.58 | 0.49 | 21017.4294 | 12612.432
[30 empty] | Dwelling-Unit | 6 | 0.5805 | [5 empty] | Storage | 1404 | 1404 | 0.46 | 0.38 | 8321.8087 | 5349.9408
[30 empty] | Lounge/Recreation - Breakroom | 43 | 0.629 | 26 | 0.56 |  |  |  | Laundry-washing | 1053 | 1053 | 0.43 | 0.53 | 4586.6049 | 5239.3708
[30 empty] | Total Result | 1716 | 20.3259 | 1636 | 15.8557 | 32 | 0.55 |  | Lounge/Recreation - Breakroom | 351 | 351 | 0.62 | 0.59 | 6928.2908 | 7385.9251
[37 empty] | SmOfc |  | 5500 | 5500 | 0.79 | 0.64 | 129222.8711 | 119063.0126
[38 empty] | Office-BLDG-SO | 5500 | 5500 | 0.79 | 0.64 | 129222.8711 | 119063.0126
[37 empty] | SoRtl |  | 8228 | 8228 | 2.68 | 2.27 | 361422.0139 | 331349.3403
[38 empty] | Lobby | 129 | 129 | 1 | 0.84 | 3044.1543 | 2745.4147
[38 empty] | Retail - Sales Area | 20467 | 20467 | 1.22 | 1.05 | 334147.4081 | 313026.6051
[38 empty] | Storage | 4088 | 4088 | 0.46 | 0.38 | 24230.4515 | 15577.3205
[37 empty] | (empty) |  | 23192.7273 | 23192.7273 | #VALUE! | #VALUE! | 9310412.0934 | 8294830.1326
[38 empty] | Conference/Meeting/Multipurpose | 5034 | 5034 | 2.14 | 1.94 | 148738.6718 | 147094.521
[38 empty] | Corridor/Transition | 10982 | 10982 | 1.32 | 0.82 | 367053.0405 | 256974.8773
[38 empty] | Electrical/Mechanical | 15566.5 | 15566.5 | 0.86 | 0.86 | 248893.3553 | 228431.1186
[38 empty] | Food Preparation | 1808 | 1808 | 1.06 | 1.09 | 32731.041 | 19946.939
[38 empty] | Library | 4293 | 4293 | 0.82 | 0.96 | 89123.1031 | 122467.5268
[38 empty] | Lobby | 7061 | 7061 | 2 | 1.68 | 333252.3057 | 300548.4167
[38 empty] | Restrooms | 7862.5 | 7862.5 | 1.7 | 1.26 | 277283.7921 | 205541.2933
[38 empty] | Stairway | 4324.5 | 4324.5 | 1.16 | 0.98 | 105196.613 | 63127.8498
[38 empty] | Storage | 6318 | 6318 | 0.92 | 0.76 | 74896.278 | 48149.4673
[38 empty] | #N/A | 4820 | 4820 | #VALUE! | #VALUE! | 190281.2636 | 202849.9079
(empty)
[38 empty] | Office - Open Plan (Including Other)-whole | 285144 | 285144 | 0.81 | 0.61 | 6263190.2884 | 5962858.5347
[38 empty] | Office - Open Plan (Including Other)-whole-small | 1100 | 1100 | 0.81 | 0.61 | 24161.499 | 23002.9192
[38 empty] | Office-Enclosed-whole-small | 1595 | 1595 | 0.878 | 0.74 | 20691.3206 | 12117.8573
[38 empty] | Office-Enclosed-whole-large | 92363 | 92363 | 0.826 | 0.74 | 1134919.5213 | 701718.9037
[37 empty] | Total Result |  | 23676.26 | 23676.26 | #VALUE! | #VALUE! | 22891514.5826 | 20775391.8463
Below references pivot above that must be refreshed
Check of totals on the Int Ltg LPD Proto 90_1 tab
[37 empty] | Prototype/Space | Floor area 2010 | Floor area 2013 | LPD2010 | LPD2013 | Tot $ 2010 | Tot $ 2013 | Delta $ | Delta LPD
[37 empty] | LgOfc | 606347.5333 | 606347.5333 | 0.96749 | 0.87382 | 7612177.0796 | 7678975.5258 | 66798.4462 | -0.093661 | 0.0087752
[37 empty] | Office-BLDG-LO | 0 | 498600 | 498600 | 0.79 | 0.64 | 11714643.2162 | 11714642.5762 | -498599.21
[37 empty] | MrApt | Office-BLDG-LO | 498600 | 498600 | 0.79 | 0.64 | 11714643.2162 | 11714642.5762 | -498599.21 | 0.060444
[37 empty] | Corridor/Transition | 0 | 11248.3333 | 11248.3333 | 1.88 | 1.4405 | 69812.6818 | 69811.2413 | -11246.4533
[37 empty] | Office-Enclosed | Corridor/Transition | 3345 | 3345 | 0.66 | 0.41 | 55900.2195 | 55899.8095 | -3344.34
[37 empty] | Dwelling-Unit | Office-Enclosed | 950 | 950 | 0.93 | 0.74 | 13110.7681 | 13110.0281 | -949.07
[37 empty] | PriSch | Dwelling-Unit | 29450 | 29450 | 0.29 | 0.2905 | 801.6943 | 801.4038 | -29449.71 | -0.081724
[37 empty] | Classroom/Lecture/Training | 0 | 8478.875 | 8478.875 | 5.92 | 4.89 | 924822.8814 | 924817.9914 | -8472.955
[37 empty] | Corridor/Transition | Classroom/Lecture/Training | 37187 | 37187 | 0.92 | 0.71 | 466155.3389 | 466154.6289 | -37186.08
[37 empty] | Dining Area | Corridor/Transition | 12073 | 12073 | 0.66 | 0.41 | 201758.8489 | 201758.4389 | -12072.34
[37 empty] | Electrical/Mechanical | Dining Area | 3389 | 3389 | 0.63 | 0.43 | 31459.0629 | 31458.6329 | -3388.37
[37 empty] | Food Preparation | Electrical/Mechanical | 2712 | 2712 | 0.43 | 0.43 | 21681.1351 | 21680.7051 | -2711.57
[37 empty] | Gymnasium/Fitness-Fitness Area | Gymnasium/Fitness-Fitness Area | 3841 | 3841 | 0.5 | 0.7 | 58820.6788 | 58819.9788 | -3840.5
[37 empty] | Library | Lobby | 1840 | 1840 | 1 | 0.84 | 43420.4959 | 43419.6559 | -1839
[37 empty] | Lobby | Office-Enclosed | 4745 | 4745 | 0.93 | 0.74 | 65484.8363 | 65484.0963 | -4744.07
[37 empty] | Office-Enclosed | Restrooms | 2044 | 2044 | 0.85 | 0.63 | 36042.4846 | 36041.8546 | -2043.15
[37 empty] | Restrooms | 0 | 3601.0833 | 3601.0833 | 8.36 | 6.79 | 381178.8247 | 381172.0347 | -3592.7233
[37 empty] | SmHtl | Conference/Meeting/Multipurpose | 864 | 864 | 1.07 | 0.97 | 12764.2245 | 12763.2545 | -862.93 | -0.29163
[37 empty] | Conference/Meeting/Multipurpose | Corridor/Transition | 5668 | 5668 | 0.66 | 0.41 | 94721.209 | 94720.799 | -5667.34
[37 empty] | Corridor/Transition | Electrical/Mechanical | 351 | 351 | 0.43 | 0.43 | 2806.0761 | 2805.6461 | -350.57
[37 empty] | Electrical/Mechanical | Gymnasium/Fitness-Fitness Area | 351 | 351 | 0.5 | 0.7 | 5375.1779 | 5374.4779 | -350.5
[37 empty] | Gymnasium/Fitness-Fitness Area | Highway Lodging Guest Rooms | 27933 | 27933 | 0.77 | 0.41 | 187596.1627 | 187595.7527 | -27932.23
[37 empty] | Highway Lodging Guest Rooms | Lobby - Hotel | 1755 | 1755 | 1.06 | 0.51 | 11496.214 | 11495.704 | -1753.94 | -0.46165
[37 empty] | Lobby - Hotel | Office-Enclosed | 1404 | 1404 | 0.93 | 0.74 | 19376.3351 | 19375.5951 | -1403.07
[37 empty] | Lounge/Recreation - Break room | Restrooms | 351 | 351 | 0.85 | 0.63 | 6189.2916 | 6188.6616 | -350.15
[37 empty] | Office-Enclosed | Stairway | 1728 | 1728 | 0.58 | 0.49 | 21017.4294 | 21016.9394 | -1727.42
[37 empty] | Restrooms | Storage | 1404 | 1404 | 0.46 | 0.38 | 8321.8087 | 8321.4287 | -1403.54
[37 empty] | Stairway | Laundry-washing | 1053 | 1053 | 0.43 | 0.53 | 4586.6049 | 4586.0749 | -1052.57
[37 empty] | Storage | Lounge/Recreation - Breakroom | 351 | 351 | 0.62 | 0.59 | 6928.2908 | 6927.7008 | -350.38
[37 empty] | Laundry-washing | 0 | 5500 | 5500 | 0.79 | 0.64 | 129222.8711 | 129222.2311 | -5499.21
[37 empty] | SmOfc | Office-BLDG-SO | 5500 | 5500 | 0.79 | 0.64 | 129222.8711 | 129222.2311 | -5499.21 | 0.043726
[37 empty] | Office-BLDG-SO | 0 | 8228 | 8228 | 2.68 | 2.27 | 361422.0139 | 361419.7439 | -8225.32
[37 empty] | SoRtl | Lobby | 129 | 129 | 1 | 0.84 | 3044.1543 | 3043.3143 | -128 | 0.15992
[37 empty] | Lobby | Retail - Sales Area | 20467 | 20467 | 1.22 | 1.05 | 334147.4081 | 334146.3581 | -20465.78
[37 empty] | Retail - Sales Area | Storage | 4088 | 4088 | 0.46 | 0.38 | 24230.4515 | 24230.0715 | -4087.54
[37 empty] | Storage | 0 | 23192.7273 | 23192.7273 | #VALUE! | #VALUE! | 9310412.0934 | #VALUE! | #VALUE!
[37 empty] | Grand Total | Conference/Meeting/Multipurpose | 5034 | 5034 | 2.14 | 1.94 | 148738.6718 | 148736.7318 | -5031.86 | 0.011039
[37 empty] | 0 | Corridor/Transition | 10982 | 10982 | 1.32 | 0.82 | 367053.0405 | 367052.2205 | -10980.68
[37 empty] | 0 | Electrical/Mechanical | 15566.5 | 15566.5 | 0.86 | 0.86 | 248893.3553 | 248892.4953 | -15565.64
[37 empty] | 0 | Food Preparation | 1808 | 1808 | 1.06 | 1.09 | 32731.041 | 32729.951 | -1806.94
[37 empty] | 0 | Library | 4293 | 4293 | 0.82 | 0.96 | 89123.1031 | 89122.1431 | -4292.18
[37 empty] | 0 | Lobby | 7061 | 7061 | 2 | 1.68 | 333252.3057 | 333250.6257 | -7059
[37 empty] | 0 | Restrooms | 7862.5 | 7862.5 | 1.7 | 1.26 | 277283.7921 | 277282.5321 | -7860.8
[37 empty] | 0 | Stairway | 4324.5 | 4324.5 | 1.16 | 0.98 | 105196.613 | 105195.633 | -4323.34
[37 empty] | 0 | Storage | 6318 | 6318 | 0.92 | 0.76 | 74896.278 | 74895.518 | -6317.08
[37 empty] | 0 | #N/A | 4820 | 4820 | #VALUE! | #VALUE! | 190281.2636 | #VALUE! | #VALUE!
[37 empty] | 0 | (empty) | 0 | 0 | 0 | 0 | 0 | 0 | 0
[37 empty] | 0 | Office - Open Plan (Including Other)-whole | 285144 | 285144 | 0.81 | 0.61 | 6263190.2884 | 6263189.6784 | -285143.19
[37 empty] | 0 | Office - Open Plan (Including Other)-whole-small | 1100 | 1100 | 0.81 | 0.61 | 24161.499 | 24160.889 | -1099.19
[37 empty] | 0 | Office-Enclosed-whole-small | 1595 | 1595 | 0.878 | 0.74 | 20691.3206 | 20690.5806 | -1594.122
[37 empty] | 0 | Office-Enclosed-whole-large | 92363 | 92363 | 0.826 | 0.74 | 1134919.5213 | 1134918.7813 | -92362.174
[37 empty] | Total Result | 0 | 23676.26 | 23676.26 | #VALUE! | #VALUE! | 22891514.5826 | #VALUE! | #VALUE!
[37 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Lobby - Hotel572 | 1 | 0.89889 | 1 | 0.89889
| Lounge/Recreation - Break room | 2 | 0.73 | 2 | 0.73 | [31 empty] | Total |  |  |  |  | 7662298.868 | 7746627.6774 | 84328.8094
| Lounge/Recreation - Breakroom0 | 0 | 0 | 0 | 0
| Lounge/Recreation - Breakroom521 | 1 | 0.43508 | 1 | 0.43508
| Lounge/Recreation - Breakroom527-2 | 1 | 0.29492 | 1 | 0.29492
| Office - Open Plan (Including Other) | 4 | 0.98104 | 4 | 0.98104
| Office - Open Plan (Including Other)0 | 0 | 0 | 0 | 0
| Office - Open Plan (Including Other)535 | 2 | 0.48 | 2 | 0.48
| Office - Open Plan (Including Other)537-1 | 1 | 0.16104 | 1 | 0.16104
| Office - Open Plan (Including Other)539 | 1 | 0.34 | 1 | 0.34
| Office-Enclosed | 4 | 1.1113 | 4 | 1.1113
| Office-Enclosed0 | 0 | 0 | 0 | 0
| Office-Enclosed531 | 2 | 0.67505 | 2 | 0.67505 | [11 empty] | 8/26/2014 missing
| Office-Enclosed537-1 | 1 | 0.25 | 1 | 0.25 | [11 empty] | Office-Enclosed537-2 | [15 empty] | Check of totals on the Int Ltg LPD Space Type 90_1 All tab
| Office-Enclosed539 | 1 | 0.18623 | 1 | 0.18623 | [11 empty] | Corridor/Transition530 | [16 empty] | Case | Data
| Restrooms | 3 | 0.98 | 3 | 0.98 | [11 empty] | Corridor/Transition537-2 | [16 empty] | 2013 |  | 2016 |  | 2019
| Restrooms0 | 0 | 0 | 0 | 0 | [11 empty] | Corridor/Transition527-2 | [15 empty] | space | Sum of Rep_Lmp_Total $/ft230 | Sum of RepBal_Ballast Cost, $/ft232 | Sum of Rep_Lmp_Total $/ft230 | Sum of RepBal_Ballast Cost, $/ft232 | Sum of Rep_Lmp_Total $/ft230 | Sum of RepBal_Ballast Cost, $/ft232 | Lamp repl 2016/2013 |  | Ballast repl 2016/2013
| Restrooms520 | 1 | 0.4448 | 1 | 0.4448 | [11 empty] | Lounge/Recreation - Breakroom537-1 | [15 empty] | Classroom/Lecture/Training | 0.024816 | 4.1103 | 0.0071608 | 1.7233 | 0.01607 | 1.7789 | 4.941% |  | 509.2%
| Restrooms534-2 | 1 | 0.24682 | 1 | 0.24682 | [11 empty] | Lobby - Hotel524 | [15 empty] | Conference/Meeting/Multipurpose | 0.19729 | 5.1469 | 0.026295 | 5.4651 |  |  | 13.33% |  | 106.2%
| Restrooms604 | 1 | 0.28838 | 1 | 0.28838 | [11 empty] | Lobby - Hotel537-1 | [15 empty] | Corridor/Transition | 0.028371 | 6.0707 | 0.018373 | 4.3242 |  |  | 64.76% |  | 71.23%
| Retail - Sales Area | 4 | 1.68 | 4 | 1.42 | [27 empty] | Dining Area | 0.10018 | 2.6085 | 0.018363 | 4.17 |  |  | 18.33% |  | 159.9%
| Retail - Sales Area0 | 0 | 0 | 0 | 0 | [27 empty] | Electrical/Mechanical | 0.020322 | 3.0549 | 0.020423 | 2.7172 |  |  | 100.5% |  | 88.95%
| Retail - Sales Area535 | 2 | 0.96 | 2 | 0.4 | [27 empty] | Food Preparation | 0.026867 | 7.015 | 0.031552 | 3.4756 |  |  | 117.4% |  | 49.54%
| Retail - Sales Area537-1 | 1 | 0 | 1 | 0.16 | [27 empty] | Gymnasium/Fitness-Fitness Area | 0.013092 | 6.6049 | 0.020045 | 10.648 |  |  | 153.1% |  | 161.2%
| Retail - Sales Area541 | 1 | 0.72 | 1 | 0.86 | [27 empty] | Highway Lodging Guest Rooms | 0.66119 | 0.46 | 0.0098996 | 3.8572 |  |  | 1.497% |  | 838.5%
| Stairway | 3 | 0.69 | 3 | 0.69 | [27 empty] | Library | 0.025238 | 8.4449 | 0.030666 | 11.8103 |  |  | 121.5% |  | 139.9%
| Stairway0 | 0 | 9.9928e-08 | 0 | 9.9928e-08 | [27 empty] | Lobby | 0.07077 | #VALUE! | 0.024512 | 8.757 |  |  | 34.64% |  | #VALUE!
| Stairway530 | 2 | 0.37 | 2 | 0.37 | [27 empty] | Lobby - Hotel | 0.54508 | 1.62 | 0.01641 | 3.3392 |  |  | 3.011% |  | 206.1%
| Stairway602 | 1 | 0.32 | 1 | 0.32 | [27 empty] | Office - Open Plan (Including Other) | 0.026729 | 9.2753 | 0.017067 | 9.0156 |  |  | 63.85% |  | 97.2%
| Storage | 2 | 0.63 | 2 | 0.63 | [27 empty] | Office-Enclosed | 0.036736 | 4.4223 | 0.021622 | 2.3934 |  |  | 58.86% |  | 54.12%
| Storage0 | 0 | 9.9297e-08 | 0 | 9.9297e-08 | [27 empty] | Restrooms | 0.20521 | 1.8224 | 0.026086 | 4.584 |  |  | 12.71% |  | 251.5%
| Storage538 | 2 | 0.63 | 2 | 0.63 | [27 empty] | Retail - Sales Area | 0.030721 | 4.2749 | 0.035398 | 5.1879 |  |  | 115.2% |  | 121.4%
[33 empty] | Stairway | 0.019646 | 4.0232 | 0.017045 | 2.4442 |  |  | 86.76% |  | 60.75%
[33 empty] | Storage | 0.012045 | 2.2697 | 0.010116 | 1.3172 |  |  | 83.99% |  | 58.03%
[33 empty] | Office - Open Plan (Including Other)-whole | 0.026729 | 9.2753 | 0.017067 | 9.0156 |  |  | 63.85% |  | 97.2%
[15 empty] | A match below indicates that the lookup can be found in the reference table. | [17 empty] | Laundry-Washing | 0.01083 | 1.5285 | 0.014613 | 1.5673 |  |  | 134.9% |  | 102.5%
[15 empty] | It does not guarantee that all relevant items are present. | [17 empty] | Office-BLDG-SO | 0.020265 | 10.1292 | 0.01771 | 9.3307 |  |  | 87.39% |  | 92.12%
[15 empty] | 62 | 62 | Office - Open Plan (Including Other) | Office - Open Plan (Including Other) | [14 empty] | Office-BLDG-LO | 0.020265 | 10.1292 | 0.01771 | 9.3307 |  |  | 87.39% |  | 0.92117
| 41877 | [7 empty] | Problem? | [5 empty] | 64 | 64 | Office - Open Plan (Including Other)535 | Office - Open Plan (Including Other)535 | [14 empty] | Office-Enclosed-whole-small | 0.034493 | 4.144 |  |  |  |  | 0% |  | 0
|  | 2010 |  | 2013 | [10 empty] | 66 | 66 | Office - Open Plan (Including Other)539 | Office - Open Plan (Including Other)539 | [14 empty] | Office - Open Plan (Including Other)-whole-small | 0.026729 | 9.2753 |  |  |  |  | 0% |  | 0%
| Row Labels | Sum of Number of Lamps9 | Sum of Fixture Watts/ft214 | Sum of Number of Lamps9 | Sum of Fixture Watts/ft214 |  | #N/A | #N/A | FALSE | FALSE |  |  |  |  | 63 | 63 | Office - Open Plan (Including Other)0 | Office - Open Plan (Including Other)0 | [14 empty] | Office-Enclosed-whole-large | 0.032695 | 3.933 | 0.021622 | 2.3934 |  |  | 66.13% |  | 60.86%
| Classroom/Lecture/Training | 4 | 1.2369 | 4 | 1.2369 |  | 241 | 241 | FALSE | FALSE |  |  |  |  | 65 | 65 | Office - Open Plan (Including Other)537-1 | Office - Open Plan (Including Other)537-1 | [14 empty] | Office - Open Plan (Including Other)-whole-large |  |  | 0.017067 | 9.0156 |  |  | #DIV/0! |  | #DIV/0!
| Classroom/Lecture/Training0 | 0 | 0 | 0 | 0 |  | 244 | 244 | FALSE | FALSE |  |  |  |  | 64 | 64 | Office - Open Plan (Including Other)535 | Office - Open Plan (Including Other)535 | [14 empty] | Lounge/Recreation - Breakroom | 0.025007 | 8.0184 | 0.036692 | 7.4551
| Classroom/Lecture/Training521 | 1 | 0.15367 | 1 | 0.15367 |  | 243 | 243 | FALSE | FALSE |  |  |  |  | 66 | 66 | Office - Open Plan (Including Other)539 | Office - Open Plan (Including Other)539 | [14 empty] | Total Result | 2.2413 | #VALUE! | 0.49351 | 133.3378 | 0.01607 | 1.7789
| Classroom/Lecture/Training535 | 2 | 0.92197 | 2 | 0.92197 |  | 242 | 242 | FALSE | FALSE |  |  |  |  | 63 | 63 | Office - Open Plan (Including Other)0 | Office - Open Plan (Including Other)0
| Classroom/Lecture/Training537-1 | 1 | 0.1613 | 1 | 0.1613 |  | 245 | 245 | FALSE | FALSE |  |  |  |  | 65 | 65 | Office - Open Plan (Including Other)537-1 | Office - Open Plan (Including Other)537-1
| Conference/Meeting/Multipurpose | 4 | 1.23 | 4 | 1.23 |  | 19 | 19 | FALSE | FALSE |  |  |  |  | 67 | 67 | Office-Enclosed | Office-Enclosed
| Conference/Meeting/Multipurpose0 | 0 | 0 | 0 | 0 |  | 22 | 22 | FALSE | FALSE |  |  |  |  | 69 | 69 | Office-Enclosed531 | Office-Enclosed531
| Conference/Meeting/Multipurpose511 | 1 | 0.43713 | 1 | 0.43713 |  | 21 | 21 | FALSE | FALSE |  |  |  |  | 71 | 71 | Office-Enclosed539 | Office-Enclosed539
| Conference/Meeting/Multipurpose527-1 | 1 | 0.18856 | 1 | 0.18856 |  | 23 | 23 | FALSE | FALSE |  |  |  |  | 70 | 68 | Office-Enclosed537-1 | Office-Enclosed0
| Conference/Meeting/Multipurpose535 | 2 | 0.6043 | 2 | 0.6043 |  | 20 | 20 | FALSE | FALSE |  |  |  |  | 68 | 70 | Office-Enclosed0 | Office-Enclosed537-1
| Corridor/Transition | 5 | 0.65543 | 1 | 0.65543 |  | 28 | 28 | FALSE | FALSE |  |  |  |  | 69 | 69 | Office-Enclosed531 | Office-Enclosed531
| Corridor/Transition0 | 4 | 0 | 0 | 0 |  | 30 | 30 | FALSE | FALSE |  |  |  |  | 71 | 71 | Office-Enclosed539 | Office-Enclosed539
| Corridor/Transition521 | 1 | 0.65543 | 1 | 0.65543 |  | 29 | 29 | FALSE | FALSE |  |  |  |  | 70 | 68 | Office-Enclosed537-1 | Office-Enclosed0
| Dining Area | 4 | 0.65 | 4 | 0.65 |  | 232 | 232 | FALSE | FALSE |  |  |  |  | 68 | 70 | Office-Enclosed0 | Office-Enclosed537-1
| Dining Area0 | 0 | 0 | 0 | 0 |  | 235 | 235 | FALSE | FALSE |  |  |  |  | 15 | 15 | Conference/Meeting/Multipurpose | Conference/Meeting/Multipurpose
| Dining Area521 | 1 | 0.11765 | 1 | 0.11765 |  | 234 | 234 | FALSE | FALSE |  |  |  |  | 19 | 19 | Conference/Meeting/Multipurpose535 | Conference/Meeting/Multipurpose535
| Dining Area535 | 2 | 0.23991 | 2 | 0.23991 |  | 233 | 233 | FALSE | FALSE |  |  |  |  | 17 | 17 | Conference/Meeting/Multipurpose511 | Conference/Meeting/Multipurpose511
| Dining Area537-1 | 1 | 0.29243 | 1 | 0.29243 |  | 236 | 236 | FALSE | FALSE |  |  |  |  | 16 | 16 | Conference/Meeting/Multipurpose0 | Conference/Meeting/Multipurpose0
| Electrical/Mechanical | 2 | 0.95 | 3 | 0.42 |  | 73 | 73 | FALSE | FALSE |  |  |  |  | 18 | 18 | Conference/Meeting/Multipurpose527-1 | Conference/Meeting/Multipurpose527-1
| Electrical/Mechanical0 | 0 | 0 | 0 | 0 |  | 75 | 76 | FALSE | FALSE |  |  |  |  | 19 | 19 | Conference/Meeting/Multipurpose535 | Conference/Meeting/Multipurpose535
| Electrical/Mechanical538 | 2 | 0.95 | 2 | 0.32 |  | 74 | 74 | FALSE | FALSE |  |  |  |  | 17 | 17 | Conference/Meeting/Multipurpose511 | Conference/Meeting/Multipurpose511
| Electrical/Mechanical539 |  |  | 1 | 0.1 |  | #N/A | 75 | FALSE | FALSE |  |  |  |  | 16 | 16 | Conference/Meeting/Multipurpose0 | Conference/Meeting/Multipurpose0
| Food Preparation | 2 | 0.99 | 4 | 1.21 |  | 268 | 268 | FALSE | FALSE |  |  |  |  | 18 | 18 | Conference/Meeting/Multipurpose527-1 | Conference/Meeting/Multipurpose527-1
| Food Preparation0 | 0 | 0 | 0 | 0 |  | 270 | 271 | FALSE | FALSE |  |  |  |  | 20 | 20 | Corridor/Transition | Corridor/Transition
| Food Preparation530 | 2 | 0.99 | 4 | 1.21 |  | 269 | 269 | FALSE | FALSE |  |  |  |  | 22 | 22 | Corridor/Transition521 | Corridor/Transition521
| Gymnasium/Fitness-Fitness Area | 2 | 0.72 | 2 | 0.72 |  | 259 | 259 | FALSE | FALSE |  |  |  |  | 21 | 21 | Corridor/Transition0 | Corridor/Transition0
| Gymnasium/Fitness-Fitness Area0 | 0 | 0 | 0 | 0 |  | 261 | 261 | FALSE | FALSE |  |  |  |  | 21 | 21 | Corridor/Transition0 | Corridor/Transition0
| Gymnasium/Fitness-Fitness Area535 | 2 | 0.72 | 2 | 0.72 |  | 260 | 260 | FALSE | FALSE |  |  |  |  | 21 | 21 | Corridor/Transition0 | Corridor/Transition0
| Highway Lodging Guest Rooms | 2 | 0.75 | 2 | 0.91 |  | 315 | 315 | FALSE | FALSE |  |  |  |  | 22 | 22 | Corridor/Transition521 | Corridor/Transition521
| Highway Lodging Guest Rooms0 | 0 | 0 | 0 | 0 |  | 318 | 318 | FALSE | FALSE |  |  |  |  | 21 | 21 | Corridor/Transition0 | Corridor/Transition0
| Highway Lodging Guest Rooms520 | 1 | 0.32608 | 1 | 0.38 |  | 317 | 317 | FALSE | FALSE |  |  |  |  | 21 | 21 | Corridor/Transition0 | Corridor/Transition0
| Highway Lodging Guest Rooms529 | 1 | 0.42392 | 1 | 0.53 |  | 316 | 316 | FALSE | FALSE |  |  |  |  | 21 | 21 | Corridor/Transition0 | Corridor/Transition0
| Hospital - Laundry/Washing | 2 | 0.6 | 2 | 0.6 |  | #N/A | #N/A | TRUE | TRUE |  |  |  |  | 15 | 15 | Conference/Meeting/Multipurpose | Conference/Meeting/Multipurpose
| Hospital - Laundry-washing0 | 0 | 1.0077e-07 | 0 | 1.0077e-07 |  | 371 | 371 | FALSE | FALSE |  |  |  |  | 19 | 19 | Conference/Meeting/Multipurpose535 | Conference/Meeting/Multipurpose535
| Hospital - Laundry-washing530 | 2 | 0.6 | 2 | 0.6 |  | 370 | 370 | FALSE | FALSE |  |  |  |  | 17 | 17 | Conference/Meeting/Multipurpose511 | Conference/Meeting/Multipurpose511
| Library | 3 | 0.93 | 3 | 1.06 |  | 277 | 277 | FALSE | FALSE |  |  |  |  | 16 | 16 | Conference/Meeting/Multipurpose0 | Conference/Meeting/Multipurpose0
| Library0 | 0 | 0 | 0 | 0 |  | 280 | 280 | FALSE | FALSE |  |  |  |  | 18 | 18 | Conference/Meeting/Multipurpose527-1 | Conference/Meeting/Multipurpose527-1
| Library520 | 1 | 0.53723 | 1 | 0.34 |  | 279 | 279 | FALSE | FALSE |  |  |  |  | 19 | 19 | Conference/Meeting/Multipurpose535 | Conference/Meeting/Multipurpose535
| Library535 | 2 | 0.39277 | 2 | 0.72 |  | 278 | 278 | FALSE | FALSE |  |  |  |  | 17 | 17 | Conference/Meeting/Multipurpose511 | Conference/Meeting/Multipurpose511
| Lobby | 3 | 0.9 | 3 | 0.9 |  | 91 | 91 | FALSE | FALSE |  |  |  |  | 16 | 16 | Conference/Meeting/Multipurpose0 | Conference/Meeting/Multipurpose0
| Lobby0 | 0 | 0 | 0 | 0 |  | 94 | 94 | FALSE | FALSE |  |  |  |  | 18 | 18 | Conference/Meeting/Multipurpose527-1 | Conference/Meeting/Multipurpose527-1
| Lobby521 | 1 | 0.23659 | 1 | 0.23659 |  | 93 | 93 | FALSE | FALSE |  |  |  |  | 86 | 86 | Storage | Storage
| Lobby523 | 1 | 0.50199 | 1 | 0.50199 |  | 92 | 92 | FALSE | FALSE |  |  |  |  | 88 | 88 | Storage538 | Storage538
| Lobby534-2 | 1 | 0.16142 | 1 | 0.16142 |  | 95 | 95 | FALSE | FALSE |  |  |  |  | 87 | 87 | Storage0 | Storage0
| Lobby - Hotel | 5 | 1.0589 | 2 | 1.0589 |  | 342 | 342 | FALSE | FALSE |  |  |  |  | 87 | 87 | Storage0 | Storage0
| Lobby - Hotel0 | 3 | 0 | 0 | 0 |  | 344 | 344 | FALSE | FALSE |  |  |  |  | 87 | 87 | Storage0 | Storage0
| Lobby - Hotel527-1 | 1 | 0.16 | 1 | 0.16 |  | 346 | 346 | FALSE | FALSE |  |  |  |  | 88 | 88 | Storage538 | Storage538
| Lobby - Hotel572 | 1 | 0.89889 | 1 | 0.89889 |  | 343 | 343 | FALSE | FALSE |  |  |  |  | 87 | 87 | Storage0 | Storage0
| Lounge/Recreation - Break room | 2 | 0.73 | 2 | 0.73 |  | 64 | 64 | FALSE | FALSE |  |  |  |  | 87 | 87 | Storage0 | Storage0
| Lounge/Recreation - Breakroom0 | 0 | 0 | 0 | 0 |  | 66 | 66 | FALSE | FALSE |  |  |  |  | 87 | 87 | Storage0 | Storage0
| Lounge/Recreation - Breakroom521 | 1 | 0.43508 | 1 | 0.43508 |  | 65 | 65 | FALSE | FALSE |  |  |  |  | 72 | 72 | Restrooms | Restrooms
| Lounge/Recreation - Breakroom527-2 | 1 | 0.29492 | 1 | 0.29492 |  | #N/A | 68 | TRUE | FALSE |  |  |  |  | 76 | 76 | Restrooms604 | Restrooms604
| Office - Open Plan (Including Other) | 4 | 0.98104 | 4 | 0.98104 |  | 1 | 1 | FALSE | FALSE |  |  |  |  | 74 | 74 | Restrooms520 | Restrooms520
| Office - Open Plan (Including Other)0 | 0 | 0 | 0 | 0 |  | 4 | 4 | FALSE | FALSE |  |  |  |  | 73 | 73 | Restrooms0 | Restrooms0
| Office - Open Plan (Including Other)535 | 2 | 0.48 | 2 | 0.48 |  | 2 | 2 | FALSE | FALSE |  |  |  |  | 75 | 75 | Restrooms534-2 | Restrooms534-2
| Office - Open Plan (Including Other)537-1 | 1 | 0.16104 | 1 | 0.16104 |  | 5 | 5 | FALSE | FALSE |  |  |  |  | 76 | 76 | Restrooms604 | Restrooms604
| Office - Open Plan (Including Other)539 | 1 | 0.34 | 1 | 0.34 |  | 3 | 3 | FALSE | FALSE |  |  |  |  | 74 | 74 | Restrooms520 | Restrooms520
| Office-Enclosed | 4 | 1.1113 | 4 | 1.1113 |  | 10 | 10 | FALSE | FALSE |  |  |  |  | 73 | 73 | Restrooms0 | Restrooms0
| Office-Enclosed0 | 0 | 0 | 0 | 0 |  | 14 | 13 | FALSE | FALSE |  |  |  |  | 75 | 75 | Restrooms534-2 | Restrooms534-2
| Office-Enclosed531 | 2 | 0.67505 | 2 | 0.67505 |  | 11 | 11 | FALSE | FALSE |  |  |  |  | 58 | 58 | Lounge/Recreation - Break room | Lounge/Recreation - Break room
| Office-Enclosed537-1 | 1 | 0.25 | 1 | 0.25 |  | 13 | 14 | FALSE | FALSE |  |  |  |  | 60 | 60 | Lounge/Recreation - Breakroom521 | Lounge/Recreation - Breakroom521
| Office-Enclosed539 | 1 | 0.18623 | 1 | 0.18623 |  | 12 | 12 | FALSE | FALSE |  |  |  |  | 59 | 59 | Lounge/Recreation - Breakroom0 | Lounge/Recreation - Breakroom0
| Restrooms | 3 | 0.98 | 3 | 0.98 |  | 55 | 55 | FALSE | FALSE |  |  |  |  | 59 | 59 | Lounge/Recreation - Breakroom0 | Lounge/Recreation - Breakroom0
| Restrooms0 | 0 | 0 | 0 | 0 |  | 58 | 58 | FALSE | FALSE |  |  |  |  | 59 | 61 | Lounge/Recreation - Breakroom0 | Lounge/Recreation - Breakroom527-2
| Restrooms520 | 1 | 0.4448 | 1 | 0.4448 |  | 57 | 57 | FALSE | FALSE |  |  |  |  | 60 | 60 | Lounge/Recreation - Breakroom521 | Lounge/Recreation - Breakroom521
| Restrooms534-2 | 1 | 0.24682 | 1 | 0.24682 |  | 59 | 59 | FALSE | FALSE |  |  |  |  | 59 | 59 | Lounge/Recreation - Breakroom0 | Lounge/Recreation - Breakroom0
| Restrooms604 | 1 | 0.28838 | 1 | 0.28838 |  | 56 | 56 | FALSE | FALSE |  |  |  |  | 59 | 59 | Lounge/Recreation - Breakroom0 | Lounge/Recreation - Breakroom0
| Retail - Sales Area | 4 | 1.68 | 4 | 1.42 |  | 203 | 203 | FALSE | FALSE |  |  |  |  | 59 | 61 | Lounge/Recreation - Breakroom0 | Lounge/Recreation - Breakroom527-2
| Retail - Sales Area0 | 0 | 0 | 0 | 0 |  | 206 | 206 | FALSE | FALSE |  |  |  |  | 28 | 28 | Electrical/Mechanical | Electrical/Mechanical
| Retail - Sales Area535 | 2 | 0.96 | 2 | 0.4 |  | 204 | 204 | FALSE | FALSE |  |  |  |  | 30 | 30 | Electrical/Mechanical538 | Electrical/Mechanical538
| Retail - Sales Area537-1 | 1 | 0 | 1 | 0.16 |  | 207 | 207 | FALSE | FALSE |  |  |  |  | 29 | 31 | Electrical/Mechanical0 | Electrical/Mechanical539
| Retail - Sales Area541 | 1 | 0.72 | 1 | 0.86 |  | 205 | 205 | FALSE | FALSE |  |  |  |  | 29 | 29 | Electrical/Mechanical0 | Electrical/Mechanical0
| Stairway | 3 | 0.69 | 3 | 0.69 |  | 82 | 82 | FALSE | FALSE |  |  |  |  | 29 | 29 | Electrical/Mechanical0 | Electrical/Mechanical0
| Stairway0 | 0 | 9.9928e-08 | 0 | 9.9928e-08 |  | 85 | 85 | FALSE | FALSE |  |  |  |  | 30 | 30 | Electrical/Mechanical538 | Electrical/Mechanical538
| Stairway530 | 2 | 0.37 | 2 | 0.37 |  | 83 | 83 | FALSE | FALSE |  |  |  |  | 29 | 31 | Electrical/Mechanical0 | Electrical/Mechanical539
| Stairway602 | 1 | 0.32 | 1 | 0.32 |  | 84 | 84 | FALSE | FALSE |  |  |  |  | 29 | 29 | Electrical/Mechanical0 | Electrical/Mechanical0
| Storage | 2 | 0.63 | 2 | 0.63 |  | 46 | 46 | FALSE | FALSE |  |  |  |  | 29 | 29 | Electrical/Mechanical0 | Electrical/Mechanical0
| Storage0 | 0 | 9.9297e-08 | 0 | 9.9297e-08 |  | 48 | 48 | FALSE | FALSE |  |  |  |  | 82 | 82 | Stairway | Stairway
| Storage538 | 2 | 0.63 | 2 | 0.63 |  | 47 | 47 | FALSE | FALSE |  |  |  |  | 84 | 84 | Stairway530 | Stairway530
| Storage538 | 2 | 0.63 | 2 | 0.63 |  | 47 | 47 | FALSE | FALSE |  |  |  |  | 85 | 85 | Stairway602 | Stairway602
[7 empty] | #N/A | #N/A | FALSE | FALSE |  |  |  |  | 83 | 83 | Stairway0 | Stairway0
[7 empty] | #N/A | #N/A | FALSE | FALSE |  |  |  |  | 83 | 83 | Stairway0 | Stairway0
[7 empty] | #N/A | #N/A | FALSE | FALSE |  |  |  |  | 84 | 84 | Stairway530 | Stairway530
[7 empty] | #N/A | #N/A | FALSE | FALSE |  |  |  |  | 85 | 85 | Stairway602 | Stairway602
[7 empty] | #N/A | #N/A | FALSE | FALSE |  |  |  |  | 83 | 83 | Stairway0 | Stairway0
[7 empty] | #N/A | #N/A | FALSE | FALSE |  |  |  |  | 83 | 83 | Stairway0 | Stairway0
[7 empty] | #N/A | #N/A | FALSE | FALSE |  |  |  |  | 49 | 49 | Lobby | Lobby
[7 empty] | #N/A | #N/A | FALSE | FALSE |  |  |  |  | 52 | 52 | Lobby523 | Lobby523
[7 empty] | #N/A | #N/A | FALSE | FALSE |  |  |  |  | 51 | 51 | Lobby521 | Lobby521
[7 empty] | #N/A | #N/A | FALSE | FALSE |  |  |  |  | 50 | 50 | Lobby0 | Lobby0
[7 empty] | #N/A | #N/A | FALSE | FALSE |  |  |  |  | 53 | 53 | Lobby534-2 | Lobby534-2
[7 empty] | #N/A | #N/A | FALSE | FALSE |  |  |  |  | 52 | 52 | Lobby523 | Lobby523
[7 empty] | #N/A | #N/A | FALSE | FALSE |  |  |  |  | 51 | 51 | Lobby521 | Lobby521
[7 empty] | #N/A | #N/A | FALSE | FALSE |  |  |  |  | 50 | 50 | Lobby0 | Lobby0
[15 empty] | 53 | 53 | Lobby534-2 | Lobby534-2
[15 empty] | 62 | 62 | Office - Open Plan (Including Other) | Office - Open Plan (Including Other)
[15 empty] | 64 | 64 | Office - Open Plan (Including Other)535 | Office - Open Plan (Including Other)535
[15 empty] | 66 | 66 | Office - Open Plan (Including Other)539 | Office - Open Plan (Including Other)539
[15 empty] | 63 | 63 | Office - Open Plan (Including Other)0 | Office - Open Plan (Including Other)0
[15 empty] | 65 | 65 | Office - Open Plan (Including Other)537-1 | Office - Open Plan (Including Other)537-1
[15 empty] | 64 | 64 | Office - Open Plan (Including Other)535 | Office - Open Plan (Including Other)535
[15 empty] | 66 | 66 | Office - Open Plan (Including Other)539 | Office - Open Plan (Including Other)539
[15 empty] | 63 | 63 | Office - Open Plan (Including Other)0 | Office - Open Plan (Including Other)0
[15 empty] | 65 | 65 | Office - Open Plan (Including Other)537-1 | Office - Open Plan (Including Other)537-1
[15 empty] | 67 | 67 | Office-Enclosed | Office-Enclosed
[15 empty] | 69 | 69 | Office-Enclosed531 | Office-Enclosed531
[15 empty] | 71 | 71 | Office-Enclosed539 | Office-Enclosed539
[15 empty] | 70 | 68 | Office-Enclosed537-1 | Office-Enclosed0
[15 empty] | 68 | 70 | Office-Enclosed0 | Office-Enclosed537-1
[15 empty] | 69 | 69 | Office-Enclosed531 | Office-Enclosed531
[15 empty] | 71 | 71 | Office-Enclosed539 | Office-Enclosed539
[15 empty] | 70 | 68 | Office-Enclosed537-1 | Office-Enclosed0
[15 empty] | 68 | 70 | Office-Enclosed0 | Office-Enclosed537-1
[15 empty] | 15 | 15 | Conference/Meeting/Multipurpose | Conference/Meeting/Multipurpose
[15 empty] | 19 | 19 | Conference/Meeting/Multipurpose535 | Conference/Meeting/Multipurpose535
[15 empty] | 17 | 17 | Conference/Meeting/Multipurpose511 | Conference/Meeting/Multipurpose511
[15 empty] | 16 | 16 | Conference/Meeting/Multipurpose0 | Conference/Meeting/Multipurpose0
[15 empty] | 18 | 18 | Conference/Meeting/Multipurpose527-1 | Conference/Meeting/Multipurpose527-1
[15 empty] | 19 | 19 | Conference/Meeting/Multipurpose535 | Conference/Meeting/Multipurpose535
[15 empty] | 17 | 17 | Conference/Meeting/Multipurpose511 | Conference/Meeting/Multipurpose511
[15 empty] | 16 | 16 | Conference/Meeting/Multipurpose0 | Conference/Meeting/Multipurpose0
[15 empty] | 18 | 18 | Conference/Meeting/Multipurpose527-1 | Conference/Meeting/Multipurpose527-1
[15 empty] | 20 | 20 | Corridor/Transition | Corridor/Transition
[15 empty] | 22 | 22 | Corridor/Transition521 | Corridor/Transition521
[15 empty] | 21 | 21 | Corridor/Transition0 | Corridor/Transition0
[15 empty] | 21 | 21 | Corridor/Transition0 | Corridor/Transition0
[15 empty] | 21 | 21 | Corridor/Transition0 | Corridor/Transition0
[15 empty] | 22 | 22 | Corridor/Transition521 | Corridor/Transition521
[15 empty] | 21 | 21 | Corridor/Transition0 | Corridor/Transition0
[15 empty] | 21 | 21 | Corridor/Transition0 | Corridor/Transition0
[15 empty] | 21 | 21 | Corridor/Transition0 | Corridor/Transition0
[15 empty] | 86 | 86 | Storage | Storage
[15 empty] | 88 | 88 | Storage538 | Storage538
[15 empty] | 87 | 87 | Storage0 | Storage0
[15 empty] | 87 | 87 | Storage0 | Storage0
[15 empty] | 87 | 87 | Storage0 | Storage0
[15 empty] | 88 | 88 | Storage538 | Storage538
[15 empty] | 87 | 87 | Storage0 | Storage0
[15 empty] | 87 | 87 | Storage0 | Storage0
[15 empty] | 87 | 87 | Storage0 | Storage0
[15 empty] | 72 | 72 | Restrooms | Restrooms
[15 empty] | 76 | 76 | Restrooms604 | Restrooms604
[15 empty] | 74 | 74 | Restrooms520 | Restrooms520
[15 empty] | 73 | 73 | Restrooms0 | Restrooms0
[15 empty] | 75 | 75 | Restrooms534-2 | Restrooms534-2
[15 empty] | 76 | 76 | Restrooms604 | Restrooms604
[15 empty] | 74 | 74 | Restrooms520 | Restrooms520
[15 empty] | 73 | 73 | Restrooms0 | Restrooms0
[15 empty] | 75 | 75 | Restrooms534-2 | Restrooms534-2
[15 empty] | 58 | 58 | Lounge/Recreation - Break room | Lounge/Recreation - Break room
[15 empty] | 60 | 60 | Lounge/Recreation - Breakroom521 | Lounge/Recreation - Breakroom521
[15 empty] | 59 | 59 | Lounge/Recreation - Breakroom0 | Lounge/Recreation - Breakroom0
[15 empty] | 59 | 59 | Lounge/Recreation - Breakroom0 | Lounge/Recreation - Breakroom0
[15 empty] | 59 | 61 | Lounge/Recreation - Breakroom0 | Lounge/Recreation - Breakroom527-2
[15 empty] | 60 | 60 | Lounge/Recreation - Breakroom521 | Lounge/Recreation - Breakroom521
[15 empty] | 59 | 59 | Lounge/Recreation - Breakroom0 | Lounge/Recreation - Breakroom0
[15 empty] | 59 | 59 | Lounge/Recreation - Breakroom0 | Lounge/Recreation - Breakroom0
[15 empty] | 59 | 61 | Lounge/Recreation - Breakroom0 | Lounge/Recreation - Breakroom527-2
[15 empty] | 28 | 28 | Electrical/Mechanical | Electrical/Mechanical
[15 empty] | 30 | 30 | Electrical/Mechanical538 | Electrical/Mechanical538
[15 empty] | 29 | 31 | Electrical/Mechanical0 | Electrical/Mechanical539
[15 empty] | 29 | 29 | Electrical/Mechanical0 | Electrical/Mechanical0
[15 empty] | 29 | 29 | Electrical/Mechanical0 | Electrical/Mechanical0
[15 empty] | 30 | 30 | Electrical/Mechanical538 | Electrical/Mechanical538
[15 empty] | 29 | 31 | Electrical/Mechanical0 | Electrical/Mechanical539
[15 empty] | 29 | 29 | Electrical/Mechanical0 | Electrical/Mechanical0
[15 empty] | 29 | 29 | Electrical/Mechanical0 | Electrical/Mechanical0
[15 empty] | 82 | 82 | Stairway | Stairway
[15 empty] | 84 | 84 | Stairway530 | Stairway530
[15 empty] | 85 | 85 | Stairway602 | Stairway602
[15 empty] | 83 | 83 | Stairway0 | Stairway0
[15 empty] | 83 | 83 | Stairway0 | Stairway0
[15 empty] | 84 | 84 | Stairway530 | Stairway530
[15 empty] | 85 | 85 | Stairway602 | Stairway602
[15 empty] | 83 | 83 | Stairway0 | Stairway0
[15 empty] | 83 | 83 | Stairway0 | Stairway0
[15 empty] | 49 | 49 | Lobby | Lobby
[15 empty] | 52 | 52 | Lobby523 | Lobby523
[15 empty] | 51 | 51 | Lobby521 | Lobby521
[15 empty] | 50 | 50 | Lobby0 | Lobby0
[15 empty] | 53 | 53 | Lobby534-2 | Lobby534-2
[15 empty] | 52 | 52 | Lobby523 | Lobby523
[15 empty] | 51 | 51 | Lobby521 | Lobby521
[15 empty] | 50 | 50 | Lobby0 | Lobby0
[15 empty] | 53 | 53 | Lobby534-2 | Lobby534-2
[15 empty] | 86 | 86 | Storage | Storage
[15 empty] | 88 | 88 | Storage538 | Storage538
[15 empty] | 87 | 87 | Storage0 | Storage0
[15 empty] | 87 | 87 | Storage0 | Storage0
[15 empty] | 87 | 87 | Storage0 | Storage0
[15 empty] | 88 | 88 | Storage538 | Storage538
[15 empty] | 87 | 87 | Storage0 | Storage0
[15 empty] | 87 | 87 | Storage0 | Storage0
[15 empty] | 87 | 87 | Storage0 | Storage0
[15 empty] | 77 | 77 | Retail - Sales Area | Retail - Sales Area
[15 empty] | 79 | 79 | Retail - Sales Area535 | Retail - Sales Area535
[15 empty] | 81 | 81 | Retail - Sales Area541 | Retail - Sales Area541
[15 empty] | 78 | 78 | Retail - Sales Area0 | Retail - Sales Area0
[15 empty] | 80 | 80 | Retail - Sales Area537-1 | Retail - Sales Area537-1
[15 empty] | 79 | 79 | Retail - Sales Area535 | Retail - Sales Area535
[15 empty] | 81 | 81 | Retail - Sales Area541 | Retail - Sales Area541
[15 empty] | 78 | 78 | Retail - Sales Area0 | Retail - Sales Area0
[15 empty] | 80 | 80 | Retail - Sales Area537-1 | Retail - Sales Area537-1
[15 empty] | 49 | 49 | Lobby | Lobby
[15 empty] | 52 | 52 | Lobby523 | Lobby523
[15 empty] | 51 | 51 | Lobby521 | Lobby521
[15 empty] | 50 | 50 | Lobby0 | Lobby0
[15 empty] | 53 | 53 | Lobby534-2 | Lobby534-2
[15 empty] | 52 | 52 | Lobby523 | Lobby523
[15 empty] | 51 | 51 | Lobby521 | Lobby521
[15 empty] | 50 | 50 | Lobby0 | Lobby0
[15 empty] | 53 | 53 | Lobby534-2 | Lobby534-2
[15 empty] | 72 | 72 | Restrooms | Restrooms
[15 empty] | 76 | 76 | Restrooms604 | Restrooms604
[15 empty] | 74 | 74 | Restrooms520 | Restrooms520
[15 empty] | 73 | 73 | Restrooms0 | Restrooms0
[15 empty] | 75 | 75 | Restrooms534-2 | Restrooms534-2
[15 empty] | 76 | 76 | Restrooms604 | Restrooms604
[15 empty] | 74 | 74 | Restrooms520 | Restrooms520
[15 empty] | 73 | 73 | Restrooms0 | Restrooms0
[15 empty] | 75 | 75 | Restrooms534-2 | Restrooms534-2
[15 empty] | 23 | 23 | Dining Area | Dining Area
[15 empty] | 26 | 26 | Dining Area535 | Dining Area535
[15 empty] | 25 | 25 | Dining Area521 | Dining Area521
[15 empty] | 24 | 24 | Dining Area0 | Dining Area0
[15 empty] | 27 | 27 | Dining Area537-1 | Dining Area537-1
[15 empty] | 26 | 26 | Dining Area535 | Dining Area535
[15 empty] | 25 | 25 | Dining Area521 | Dining Area521
[15 empty] | 24 | 24 | Dining Area0 | Dining Area0
[15 empty] | 27 | 27 | Dining Area537-1 | Dining Area537-1
[15 empty] | 10 | 10 | Classroom/Lecture/Training | Classroom/Lecture/Training
[15 empty] | 13 | 13 | Classroom/Lecture/Training535 | Classroom/Lecture/Training535
[15 empty] | 12 | 12 | Classroom/Lecture/Training521 | Classroom/Lecture/Training521
[15 empty] | 11 | 11 | Classroom/Lecture/Training0 | Classroom/Lecture/Training0
[15 empty] | 14 | 14 | Classroom/Lecture/Training537-1 | Classroom/Lecture/Training537-1
[15 empty] | 13 | 13 | Classroom/Lecture/Training535 | Classroom/Lecture/Training535
[15 empty] | 12 | 12 | Classroom/Lecture/Training521 | Classroom/Lecture/Training521
[15 empty] | 11 | 11 | Classroom/Lecture/Training0 | Classroom/Lecture/Training0
[15 empty] | 14 | 14 | Classroom/Lecture/Training537-1 | Classroom/Lecture/Training537-1
[15 empty] | 20 | 20 | Corridor/Transition | Corridor/Transition
[15 empty] | 22 | 22 | Corridor/Transition521 | Corridor/Transition521
[15 empty] | 21 | 21 | Corridor/Transition0 | Corridor/Transition0
[15 empty] | 21 | 21 | Corridor/Transition0 | Corridor/Transition0
[15 empty] | 21 | 21 | Corridor/Transition0 | Corridor/Transition0
[15 empty] | 22 | 22 | Corridor/Transition521 | Corridor/Transition521
[15 empty] | 21 | 21 | Corridor/Transition0 | Corridor/Transition0
[15 empty] | 21 | 21 | Corridor/Transition0 | Corridor/Transition0
[15 empty] | 21 | 21 | Corridor/Transition0 | Corridor/Transition0
[15 empty] | 35 | 35 | Gymnasium/Fitness-Fitness Area | Gymnasium/Fitness-Fitness Area
[15 empty] | 37 | 37 | Gymnasium/Fitness-Fitness Area535 | Gymnasium/Fitness-Fitness Area535
[15 empty] | 36 | 36 | Gymnasium/Fitness-Fitness Area0 | Gymnasium/Fitness-Fitness Area0
[15 empty] | 36 | 36 | Gymnasium/Fitness-Fitness Area0 | Gymnasium/Fitness-Fitness Area0
[15 empty] | 36 | 36 | Gymnasium/Fitness-Fitness Area0 | Gymnasium/Fitness-Fitness Area0
[15 empty] | 37 | 37 | Gymnasium/Fitness-Fitness Area535 | Gymnasium/Fitness-Fitness Area535
[15 empty] | 36 | 36 | Gymnasium/Fitness-Fitness Area0 | Gymnasium/Fitness-Fitness Area0
[15 empty] | 36 | 36 | Gymnasium/Fitness-Fitness Area0 | Gymnasium/Fitness-Fitness Area0
[15 empty] | 36 | 36 | Gymnasium/Fitness-Fitness Area0 | Gymnasium/Fitness-Fitness Area0
[15 empty] | 32 | 32 | Food Preparation | Food Preparation
[15 empty] | 34 | 34 | Food Preparation530 | Food Preparation530
[15 empty] | 33 | 34 | Food Preparation0 | Food Preparation530
[15 empty] | 33 | 33 | Food Preparation0 | Food Preparation0
[15 empty] | 33 | 33 | Food Preparation0 | Food Preparation0
[15 empty] | 34 | 34 | Food Preparation530 | Food Preparation530
[15 empty] | 33 | 34 | Food Preparation0 | Food Preparation530
[15 empty] | 33 | 33 | Food Preparation0 | Food Preparation0
[15 empty] | 33 | 33 | Food Preparation0 | Food Preparation0
[15 empty] | 45 | 45 | Library | Library
[15 empty] | 48 | 48 | Library535 | Library535
[15 empty] | 47 | 47 | Library520 | Library520
[15 empty] | 46 | 46 | Library0 | Library0
[15 empty] | 46 | 46 | Library0 | Library0
[15 empty] | 48 | 48 | Library535 | Library535
[15 empty] | 47 | 47 | Library520 | Library520
[15 empty] | 46 | 46 | Library0 | Library0
[15 empty] | 46 | 46 | Library0 | Library0
[15 empty] | 49 | 49 | Lobby | Lobby
[15 empty] | 52 | 52 | Lobby523 | Lobby523
[15 empty] | 51 | 51 | Lobby521 | Lobby521
[15 empty] | 50 | 50 | Lobby0 | Lobby0
[15 empty] | 53 | 53 | Lobby534-2 | Lobby534-2
[15 empty] | 52 | 52 | Lobby523 | Lobby523
[15 empty] | 51 | 51 | Lobby521 | Lobby521
[15 empty] | 50 | 50 | Lobby0 | Lobby0
[15 empty] | 53 | 53 | Lobby534-2 | Lobby534-2
[15 empty] | 28 | 28 | Electrical/Mechanical | Electrical/Mechanical
[15 empty] | 30 | 30 | Electrical/Mechanical538 | Electrical/Mechanical538
[15 empty] | 29 | 31 | Electrical/Mechanical0 | Electrical/Mechanical539
[15 empty] | 29 | 29 | Electrical/Mechanical0 | Electrical/Mechanical0
[15 empty] | 29 | 29 | Electrical/Mechanical0 | Electrical/Mechanical0
[15 empty] | 30 | 30 | Electrical/Mechanical538 | Electrical/Mechanical538
[15 empty] | 29 | 31 | Electrical/Mechanical0 | Electrical/Mechanical539
[15 empty] | 29 | 29 | Electrical/Mechanical0 | Electrical/Mechanical0
[15 empty] | 29 | 29 | Electrical/Mechanical0 | Electrical/Mechanical0
[15 empty] | 67 | 67 | Office-Enclosed | Office-Enclosed
[15 empty] | 69 | 69 | Office-Enclosed531 | Office-Enclosed531
[15 empty] | 71 | 71 | Office-Enclosed539 | Office-Enclosed539
[15 empty] | 70 | 68 | Office-Enclosed537-1 | Office-Enclosed0
[15 empty] | 68 | 70 | Office-Enclosed0 | Office-Enclosed537-1
[15 empty] | 69 | 69 | Office-Enclosed531 | Office-Enclosed531
[15 empty] | 71 | 71 | Office-Enclosed539 | Office-Enclosed539
[15 empty] | 70 | 68 | Office-Enclosed537-1 | Office-Enclosed0
[15 empty] | 68 | 70 | Office-Enclosed0 | Office-Enclosed537-1
[15 empty] | 38 | 38 | Highway Lodging Guest Rooms | Highway Lodging Guest Rooms
[15 empty] | 41 | 41 | Highway Lodging Guest Rooms529 | Highway Lodging Guest Rooms529
[15 empty] | 40 | 40 | Highway Lodging Guest Rooms520 | Highway Lodging Guest Rooms520
[15 empty] | 39 | 39 | Highway Lodging Guest Rooms0 | Highway Lodging Guest Rooms0
[15 empty] | 39 | 39 | Highway Lodging Guest Rooms0 | Highway Lodging Guest Rooms0
[15 empty] | 41 | 41 | Highway Lodging Guest Rooms529 | Highway Lodging Guest Rooms529
[15 empty] | 40 | 40 | Highway Lodging Guest Rooms520 | Highway Lodging Guest Rooms520
[15 empty] | 39 | 39 | Highway Lodging Guest Rooms0 | Highway Lodging Guest Rooms0
[15 empty] | 39 | 39 | Highway Lodging Guest Rooms0 | Highway Lodging Guest Rooms0
[15 empty] | 20 | 20 | Corridor/Transition | Corridor/Transition
[15 empty] | 22 | 22 | Corridor/Transition521 | Corridor/Transition521
[15 empty] | 21 | 21 | Corridor/Transition0 | Corridor/Transition0
[15 empty] | 21 | 21 | Corridor/Transition0 | Corridor/Transition0
[15 empty] | 21 | 21 | Corridor/Transition0 | Corridor/Transition0
[15 empty] | 22 | 22 | Corridor/Transition521 | Corridor/Transition521
[15 empty] | 21 | 21 | Corridor/Transition0 | Corridor/Transition0
[15 empty] | 21 | 21 | Corridor/Transition0 | Corridor/Transition0
[15 empty] | 21 | 21 | Corridor/Transition0 | Corridor/Transition0
[15 empty] | 82 | 82 | Stairway | Stairway
[15 empty] | 84 | 84 | Stairway530 | Stairway530
[15 empty] | 85 | 85 | Stairway602 | Stairway602
[15 empty] | 83 | 83 | Stairway0 | Stairway0
[15 empty] | 83 | 83 | Stairway0 | Stairway0
[15 empty] | 84 | 84 | Stairway530 | Stairway530
[15 empty] | 85 | 85 | Stairway602 | Stairway602
[15 empty] | 83 | 83 | Stairway0 | Stairway0
[15 empty] | 83 | 83 | Stairway0 | Stairway0
[15 empty] | 54 | 54 | Lobby - Hotel | Lobby - Hotel
[15 empty] | 57 | 57 | Lobby - Hotel572 | Lobby - Hotel572
[15 empty] | 55 | 55 | Lobby - Hotel0 | Lobby - Hotel0
[15 empty] | 55 | 55 | Lobby - Hotel0 | Lobby - Hotel0
[15 empty] | 56 | 56 | Lobby - Hotel527-1 | Lobby - Hotel527-1
[15 empty] | 57 | 57 | Lobby - Hotel572 | Lobby - Hotel572
[15 empty] | 55 | 55 | Lobby - Hotel0 | Lobby - Hotel0
[15 empty] | 55 | 55 | Lobby - Hotel0 | Lobby - Hotel0
[15 empty] | 56 | 56 | Lobby - Hotel527-1 | Lobby - Hotel527-1
[15 empty] | 86 | 86 | Storage | Storage
[15 empty] | 88 | 88 | Storage538 | Storage538
[15 empty] | 87 | 87 | Storage0 | Storage0
[15 empty] | 87 | 87 | Storage0 | Storage0
[15 empty] | 87 | 87 | Storage0 | Storage0
[15 empty] | 88 | 88 | Storage538 | Storage538
[15 empty] | 87 | 87 | Storage0 | Storage0
[15 empty] | 87 | 87 | Storage0 | Storage0
[15 empty] | 87 | 87 | Storage0 | Storage0
[15 empty] | 67 | 67 | Office-Enclosed | Office-Enclosed
[15 empty] | 69 | 69 | Office-Enclosed531 | Office-Enclosed531
[15 empty] | 71 | 71 | Office-Enclosed539 | Office-Enclosed539
[15 empty] | 70 | 68 | Office-Enclosed537-1 | Office-Enclosed0
[15 empty] | 68 | 70 | Office-Enclosed0 | Office-Enclosed537-1
[15 empty] | 69 | 69 | Office-Enclosed531 | Office-Enclosed531
[15 empty] | 71 | 71 | Office-Enclosed539 | Office-Enclosed539
[15 empty] | 70 | 68 | Office-Enclosed537-1 | Office-Enclosed0
[15 empty] | 68 | 70 | Office-Enclosed0 | Office-Enclosed537-1
[15 empty] | #N/A | #N/A | Hospital - Laundry-washing | Hospital - Laundry-washing
[15 empty] | 44 | 44 | Hospital - Laundry-washing530 | Hospital - Laundry-washing530
[15 empty] | 43 | 43 | Hospital - Laundry-washing0 | Hospital - Laundry-washing0
[15 empty] | 43 | 43 | Hospital - Laundry-washing0 | Hospital - Laundry-washing0
[15 empty] | 43 | 43 | Hospital - Laundry-washing0 | Hospital - Laundry-washing0
[15 empty] | 44 | 44 | Hospital - Laundry-washing530 | Hospital - Laundry-washing530
[15 empty] | 43 | 43 | Hospital - Laundry-washing0 | Hospital - Laundry-washing0
[15 empty] | 43 | 43 | Hospital - Laundry-washing0 | Hospital - Laundry-washing0
[15 empty] | 43 | 43 | Hospital - Laundry-washing0 | Hospital - Laundry-washing0
[15 empty] | 15 | 15 | Conference/Meeting/Multipurpose | Conference/Meeting/Multipurpose
[15 empty] | 19 | 19 | Conference/Meeting/Multipurpose535 | Conference/Meeting/Multipurpose535
[15 empty] | 17 | 17 | Conference/Meeting/Multipurpose511 | Conference/Meeting/Multipurpose511
[15 empty] | 16 | 16 | Conference/Meeting/Multipurpose0 | Conference/Meeting/Multipurpose0
[15 empty] | 18 | 18 | Conference/Meeting/Multipurpose527-1 | Conference/Meeting/Multipurpose527-1
[15 empty] | 19 | 19 | Conference/Meeting/Multipurpose535 | Conference/Meeting/Multipurpose535
[15 empty] | 17 | 17 | Conference/Meeting/Multipurpose511 | Conference/Meeting/Multipurpose511
[15 empty] | 16 | 16 | Conference/Meeting/Multipurpose0 | Conference/Meeting/Multipurpose0
[15 empty] | 18 | 18 | Conference/Meeting/Multipurpose527-1 | Conference/Meeting/Multipurpose527-1
[15 empty] | 72 | 72 | Restrooms | Restrooms
[15 empty] | 76 | 76 | Restrooms604 | Restrooms604
[15 empty] | 74 | 74 | Restrooms520 | Restrooms520
[15 empty] | 73 | 73 | Restrooms0 | Restrooms0
[15 empty] | 75 | 75 | Restrooms534-2 | Restrooms534-2
[15 empty] | 76 | 76 | Restrooms604 | Restrooms604
[15 empty] | 74 | 74 | Restrooms520 | Restrooms520
[15 empty] | 73 | 73 | Restrooms0 | Restrooms0
[15 empty] | 75 | 75 | Restrooms534-2 | Restrooms534-2
[15 empty] | 35 | 35 | Gymnasium/Fitness-Fitness Area | Gymnasium/Fitness-Fitness Area
[15 empty] | 37 | 37 | Gymnasium/Fitness-Fitness Area535 | Gymnasium/Fitness-Fitness Area535
[15 empty] | 36 | 36 | Gymnasium/Fitness-Fitness Area0 | Gymnasium/Fitness-Fitness Area0
[15 empty] | 36 | 36 | Gymnasium/Fitness-Fitness Area0 | Gymnasium/Fitness-Fitness Area0
[15 empty] | 36 | 36 | Gymnasium/Fitness-Fitness Area0 | Gymnasium/Fitness-Fitness Area0
[15 empty] | 37 | 37 | Gymnasium/Fitness-Fitness Area535 | Gymnasium/Fitness-Fitness Area535
[15 empty] | 36 | 36 | Gymnasium/Fitness-Fitness Area0 | Gymnasium/Fitness-Fitness Area0
[15 empty] | 36 | 36 | Gymnasium/Fitness-Fitness Area0 | Gymnasium/Fitness-Fitness Area0
[15 empty] | 36 | 36 | Gymnasium/Fitness-Fitness Area0 | Gymnasium/Fitness-Fitness Area0
[15 empty] | 58 | 58 | Lounge/Recreation - Break room | Lounge/Recreation - Break room
[15 empty] | 60 | 60 | Lounge/Recreation - Breakroom521 | Lounge/Recreation - Breakroom521
[15 empty] | 59 | 59 | Lounge/Recreation - Breakroom0 | Lounge/Recreation - Breakroom0
[15 empty] | 59 | 59 | Lounge/Recreation - Breakroom0 | Lounge/Recreation - Breakroom0
[15 empty] | 59 | 61 | Lounge/Recreation - Breakroom0 | Lounge/Recreation - Breakroom527-2
[15 empty] | 60 | 60 | Lounge/Recreation - Breakroom521 | Lounge/Recreation - Breakroom521
[15 empty] | 59 | 59 | Lounge/Recreation - Breakroom0 | Lounge/Recreation - Breakroom0
[15 empty] | 59 | 59 | Lounge/Recreation - Breakroom0 | Lounge/Recreation - Breakroom0
[15 empty] | 59 | 61 | Lounge/Recreation - Breakroom0 | Lounge/Recreation - Breakroom527-2
[15 empty] | 28 | 28 | Electrical/Mechanical | Electrical/Mechanical
[15 empty] | 30 | 30 | Electrical/Mechanical538 | Electrical/Mechanical538
[15 empty] | 29 | 31 | Electrical/Mechanical0 | Electrical/Mechanical539
[15 empty] | 29 | 29 | Electrical/Mechanical0 | Electrical/Mechanical0
[15 empty] | 29 | 29 | Electrical/Mechanical0 | Electrical/Mechanical0
[15 empty] | 30 | 30 | Electrical/Mechanical538 | Electrical/Mechanical538
[15 empty] | 29 | 29 | Electrical/Mechanical0 | Electrical/Mechanical0
[15 empty] | 29 | 29 | Electrical/Mechanical0 | Electrical/Mechanical0
[15 empty] | 29 | 29 | Electrical/Mechanical0 | Electrical/Mechanical0
[15 empty] | #N/A | #N/A
[15 empty] | #N/A | #N/A
[15 empty] | 67 | 67 | Office-Enclosed | Office-Enclosed
[15 empty] | 69 | 69 | Office-Enclosed531 | Office-Enclosed531
[15 empty] | 71 | 71 | Office-Enclosed539 | Office-Enclosed539
[15 empty] | 70 | 68 | Office-Enclosed537-1 | Office-Enclosed0
[15 empty] | 68 | 70 | Office-Enclosed0 | Office-Enclosed537-1
[15 empty] | 69 | 69 | Office-Enclosed531 | Office-Enclosed531
[15 empty] | 71 | 71 | Office-Enclosed539 | Office-Enclosed539
[15 empty] | 70 | 68 | Office-Enclosed537-1 | Office-Enclosed0
[15 empty] | 68 | 70 | Office-Enclosed0 | Office-Enclosed537-1
[15 empty] | 20 | 20 | Corridor/Transition | Corridor/Transition
[15 empty] | 22 | 22 | Corridor/Transition521 | Corridor/Transition521
[16 empty] | 21 | Corridor/Transition0 | Corridor/Transition0
[15 empty] | 21 | 21 | Corridor/Transition0 | Corridor/Transition0
[15 empty] | 21 | 21 | Corridor/Transition0 | Corridor/Transition0
[15 empty] | 22 | 22 | Corridor/Transition521 | Corridor/Transition521
[15 empty] | 21 | 21 | Corridor/Transition0 | Corridor/Transition0
[15 empty] | 21 | 21 | Corridor/Transition0 | Corridor/Transition0
[15 empty] | 21 | 21 | Corridor/Transition0 | Corridor/Transition0
Where LSC design variations between 2010 and 2013 resulted in large cost anomolies, one of the designs was selected and LPD was adjusted to match requirements. Adjustments from LSC noted in green on Space and Proto sheets.

## Int Ltg Occ Sens Methodology (hidden)
90.1 Cost Effectiveness - Interior Lighting Occupancy Sensor Cost Methodology
Both 90.1-2010 and 90.1-2013 include requirements for occupancy sensor controls for some space types. 90.1-2013 adds space types required to use occupancy sensors, and also requires a newer type of sensor, manual on/auto off (only turns off automatically must be switched on) for some space types, rather than conventional automatic on/off control.
For the cost estimate, several steps are taken.
The first step involved determining which space types require which sensors, and how many and what type of sensors. This is shown in the "In Ltg Occ Sensor Details" worksheet. Because spaces in the models vary in size and there are many spaces, developing a specific design for each modeled space was not practical. Instead, representative spaces and occupancy control types (such as for small bathrooms) were developed. These spaces were based on the range of spaces in the models, NC3 data (Richman et al. 2008, Thornton et al. 2011). For each representative space, the number and type of sensor were determined. These are determined based on the recommendations of the 90.1 lighting subcommittee lead.
Cost estimates for each type of occupancy sensor including equipment costs from Grainger catalog online, and labor costs from RS Means 2014 are determined. These are applied to the typical controlled spaces according to the number of sensors.
These costs are applied to the prototypes according to the space type areas in the prototypes. For each space type, the area is divided by the appropriate representative controlled space from the occupancy sensors detail sheet. This results in the number of controlled spaces. Costs per controlled space types are multiplied by the number of controlled spaces.
Commissioning Costs for Occupancy Sensors
Three documents were reviewed to determine incremental commissioning costs for occupancy/vacancy sensors. Energy Efficiency Factsheet (WSU 2005) states that building commissioning is between two to four percent of the construction cost of the system. Fimek (2011) states that lighting control start-up and commissioning is 6-7% but it does not specify what the percentage is against. This is assumed to be 7% of the cost of lighting controls including labor.
Peterson (1994) states a variety of estimates:
Northeast utility uses $0.20-0.67/ft2
Northwest utility uses 6% of total measured cost
Commissioning agents use 1-4% of total measured cost or $0.01-0.10/ft2
Based on these documents, the range of commissioning costs on lighting controls including labor is 1% to 7% with an average of 4%. The noted cost/ft2 range of $0.01 to $0.10 was applied to the prototypes used in theses analysis which resulted in a match of 4% with the $0.01/ft2 . This was considered confirmation that the average 4% value is reasonable for comparison purposes and 4% of the total costs was used for incremental commissioning cost of the controls.
Fimek, L. 2011. "Don’t Question Commissioning When It comes to Lighting Controls." http://www.controleng.com/single-article/dont-question-commissioning-when-it-comes-to-lighting-controls/049f2095d0.html. Accessed May 31, 2012.
Peterson, JC, and T Haasl. 1994. A Commissioning Cost-Effectiveness Case Study. http://eec.ucdavis.edu/ACEEE/1994-96/1994/VOL05/201.PDF. Accessed May 31, 2012.
Washington State University Extension Energy Program. 2005. Energy Efficiency Factsheet. SUEEEP98_018, revised October 2005.

## Int Ltg Occ Sens Results (hidden)
Commercial Energy Code Cost Effectiveness - Interior Lighting Occupancy Sensor Controls - Cost Estimate Summary
US National
Summary of Total New Construction, Maintenance, and Replacement Costs By Replacement Year by Prototype
Small Office | [7 empty] | Large Office | [7 empty] | Standalone Retail | [7 empty] | Primary School | [7 empty] | Small Hotel | [7 empty] | Mid-rise Apartment
Base Code | 2019 |  | Target Code | 2022 |  | Incremental Cost |  | Base Code | 2019 |  | Target Code | 2022 |  | Incremental Cost |  | Base Code | 2019 |  | Target Code | 2022 |  | Incremental Cost |  | Base Code | 2019 |  | Target Code | 2022 |  | Incremental Cost |  | Base Code | 2019 |  | Target Code | 2022 |  | Incremental Cost |  | Base Code | 2019 |  | Target Code | 2022 |  | Incremental Cost
Category | All Costs, First Replacement Only | With Repeated Replacements | Category | Replacement First Year | With Repeated Replacements | 30 Year | 40 Year | Category | All Costs, First Replacement Only | With Repeated Replacements | Category | Replacement First Year | With Repeated Replacements | 30 Year | 40 Year | Category | All Costs, First Replacement Only | With Repeated Replacements | Category | Replacement First Year | With Repeated Replacements | 30 Year | 40 Year | Category | All Costs, First Replacement Only | With Repeated Replacements | Category | Replacement First Year | With Repeated Replacements | 30 Year | 40 Year | Category | All Costs, First Replacement Only | With Repeated Replacements | Category | Replacement First Year | With Repeated Replacements | 30 Year | 40 Year | Category | All Costs, First Replacement Only | With Repeated Replacements | Category | Replacement First Year | With Repeated Replacements | 30 Year | 40 Year
New Construction | 0 | 0 | New Construction | 0 | 0 | 0 | 0 | New Construction | 0 | 0 | New Construction | 0 | 0 | 0 | 0 | New Construction | 0 | 0 | New Construction | 0 | 0 | 0 | 0 | New Construction | 0 | 0 | New Construction | 0 | 0 | 0 | 0 | New Construction | 0 | 0 | New Construction | 0 | 0 | 0 | 0 | New Construction | 0 | 0 | New Construction | 0 | 0 | 0 | 0
Maintenance | 0 | 0 | Maintenance | 0 | 0 | 0 | 0 | Maintenance | 0 | 0 | Maintenance | 0 | 0 | 0 | 0 | Maintenance | 0 | 0 | Maintenance | 0 | 0 | 0 | 0 | Maintenance | 0 | 0 | Maintenance | 0 | 0 | 0 | 0 | Maintenance | 0 | 0 | Maintenance | 0 | 0 | 0 | 0 | Maintenance | 0 | 0 | Maintenance | 0 | 0 | 0 | 0
Replacement - Year | 0 | 0 | Replacement - Year | 0 | 0 | 0 | 0 | Replacement - Year | 0 | 0 | Replacement - Year | 0 | 0 | 0 | 0 | Replacement - Year | 0 | 0 | Replacement - Year | 0 | 0 | 0 | 0 | Replacement - Year | 0 | 0 | Replacement - Year | 0 | 0 | 0 | 0 | Replacement - Year | 0 | 0 | Replacement - Year | 0 | 0 | 0 | 0 | Replacement - Year | 0 | 0 | Replacement - Year | 0 | 0 | 0 | 0
1 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 0
2 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 0 | 0
3 | 0 | 0 | 3 | 0 | 0 | 0 | 0 | 3 | 0 | 0 | 3 | 0 | 0 | 0 | 0 | 3 | 0 | 0 | 3 | 0 | 0 | 0 | 0 | 3 | 0 | 0 | 3 | 0 | 0 | 0 | 0 | 3 | 0 | 0 | 3 | 0 | 0 | 0 | 0 | 3 | 0 | 0 | 3 | 0 | 0 | 0 | 0
4 | 0 | 0 | 4 | 0 | 0 | 0 | 0 | 4 | 0 | 0 | 4 | 0 | 0 | 0 | 0 | 4 | 0 | 0 | 4 | 0 | 0 | 0 | 0 | 4 | 0 | 0 | 4 | 0 | 0 | 0 | 0 | 4 | 0 | 0 | 4 | 0 | 0 | 0 | 0 | 4 | 0 | 0 | 4 | 0 | 0 | 0 | 0
5 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 5 | 0 | 0 | 0 | 0
6 | 0 | 0 | 6 | 0 | 0 | 0 | 0 | 6 | 0 | 0 | 6 | 0 | 0 | 0 | 0 | 6 | 0 | 0 | 6 | 0 | 0 | 0 | 0 | 6 | 0 | 0 | 6 | 0 | 0 | 0 | 0 | 6 | 0 | 0 | 6 | 0 | 0 | 0 | 0 | 6 | 0 | 0 | 6 | 0 | 0 | 0 | 0
7 | 0 | 0 | 7 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 7 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 7 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 7 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 7 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 7 | 0 | 0 | 0 | 0
8 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 8 | 0 | 0 | 0 | 0
9 | 0 | 0 | 9 | 0 | 0 | 0 | 0 | 9 | 0 | 0 | 9 | 0 | 0 | 0 | 0 | 9 | 0 | 0 | 9 | 0 | 0 | 0 | 0 | 9 | 0 | 0 | 9 | 0 | 0 | 0 | 0 | 9 | 0 | 0 | 9 | 0 | 0 | 0 | 0 | 9 | 0 | 0 | 9 | 0 | 0 | 0 | 0
10 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 10 | 0 | 0 | 0 | 0
11 | 0 | 0 | 11 | 0 | 0 | 0 | 0 | 11 | 0 | 0 | 11 | 0 | 0 | 0 | 0 | 11 | 0 | 0 | 11 | 0 | 0 | 0 | 0 | 11 | 0 | 0 | 11 | 0 | 0 | 0 | 0 | 11 | 0 | 0 | 11 | 0 | 0 | 0 | 0 | 11 | 0 | 0 | 11 | 0 | 0 | 0 | 0
12 | 0 | 0 | 12 | 0 | 0 | 0 | 0 | 12 | 0 | 0 | 12 | 0 | 0 | 0 | 0 | 12 | 0 | 0 | 12 | 0 | 0 | 0 | 0 | 12 | 0 | 0 | 12 | 0 | 0 | 0 | 0 | 12 | 0 | 0 | 12 | 0 | 0 | 0 | 0 | 12 | 0 | 0 | 12 | 0 | 0 | 0 | 0
13 | 0 | 0 | 13 | 0 | 0 | 0 | 0 | 13 | 0 | 0 | 13 | 0 | 0 | 0 | 0 | 13 | 0 | 0 | 13 | 0 | 0 | 0 | 0 | 13 | 0 | 0 | 13 | 0 | 0 | 0 | 0 | 13 | 0 | 0 | 13 | 0 | 0 | 0 | 0 | 13 | 0 | 0 | 13 | 0 | 0 | 0 | 0
14 | 0 | 0 | 14 | 0 | 0 | 0 | 0 | 14 | 0 | 0 | 14 | 0 | 0 | 0 | 0 | 14 | 0 | 0 | 14 | 0 | 0 | 0 | 0 | 14 | 0 | 0 | 14 | 0 | 0 | 0 | 0 | 14 | 0 | 0 | 14 | 0 | 0 | 0 | 0 | 14 | 0 | 0 | 14 | 0 | 0 | 0 | 0
15 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 15 | 0 | 0 | 0 | 0
16 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 16 | 0 | 0 | 0 | 0
17 | 0 | 0 | 17 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 17 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 17 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 17 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 17 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 17 | 0 | 0 | 0 | 0
18 | 0 | 0 | 18 | 0 | 0 | 0 | 0 | 18 | 0 | 0 | 18 | 0 | 0 | 0 | 0 | 18 | 0 | 0 | 18 | 0 | 0 | 0 | 0 | 18 | 0 | 0 | 18 | 0 | 0 | 0 | 0 | 18 | 0 | 0 | 18 | 0 | 0 | 0 | 0 | 18 | 0 | 0 | 18 | 0 | 0 | 0 | 0
19 | 0 | 0 | 19 | 0 | 0 | 0 | 0 | 19 | 0 | 0 | 19 | 0 | 0 | 0 | 0 | 19 | 0 | 0 | 19 | 0 | 0 | 0 | 0 | 19 | 0 | 0 | 19 | 0 | 0 | 0 | 0 | 19 | 0 | 0 | 19 | 0 | 0 | 0 | 0 | 19 | 0 | 0 | 19 | 0 | 0 | 0 | 0
20 | 0 | 0 | 20 | 0 | 0 | 0 | 0 | 20 | 0 | 0 | 20 | 0 | 0 | 0 | 0 | 20 | 0 | 0 | 20 | 0 | 0 | 0 | 0 | 20 | 0 | 0 | 20 | 0 | 0 | 0 | 0 | 20 | 0 | 0 | 20 | 0 | 0 | 0 | 0 | 20 | 0 | 0 | 20 | 0 | 0 | 0 | 0
21 | 0 | 0 | 21 | 0 | 0 | 0 | 0 | 21 | 0 | 0 | 21 | 0 | 0 | 0 | 0 | 21 | 0 | 0 | 21 | 0 | 0 | 0 | 0 | 21 | 0 | 0 | 21 | 0 | 0 | 0 | 0 | 21 | 0 | 0 | 21 | 0 | 0 | 0 | 0 | 21 | 0 | 0 | 21 | 0 | 0 | 0 | 0
22 | 0 | 0 | 22 | 0 | 0 | 0 | 0 | 22 | 0 | 0 | 22 | 0 | 0 | 0 | 0 | 22 | 0 | 0 | 22 | 0 | 0 | 0 | 0 | 22 | 0 | 0 | 22 | 0 | 0 | 0 | 0 | 22 | 0 | 0 | 22 | 0 | 0 | 0 | 0 | 22 | 0 | 0 | 22 | 0 | 0 | 0 | 0
23 | 0 | 0 | 23 | 0 | 0 | 0 | 0 | 23 | 0 | 0 | 23 | 0 | 0 | 0 | 0 | 23 | 0 | 0 | 23 | 0 | 0 | 0 | 0 | 23 | 0 | 0 | 23 | 0 | 0 | 0 | 0 | 23 | 0 | 0 | 23 | 0 | 0 | 0 | 0 | 23 | 0 | 0 | 23 | 0 | 0 | 0 | 0
24 | 0 | 0 | 24 | 0 | 0 | 0 | 0 | 24 | 0 | 0 | 24 | 0 | 0 | 0 | 0 | 24 | 0 | 0 | 24 | 0 | 0 | 0 | 0 | 24 | 0 | 0 | 24 | 0 | 0 | 0 | 0 | 24 | 0 | 0 | 24 | 0 | 0 | 0 | 0 | 24 | 0 | 0 | 24 | 0 | 0 | 0 | 0
25 | 0 | 0 | 25 | 0 | 0 | 0 | 0 | 25 | 0 | 0 | 25 | 0 | 0 | 0 | 0 | 25 | 0 | 0 | 25 | 0 | 0 | 0 | 0 | 25 | 0 | 0 | 25 | 0 | 0 | 0 | 0 | 25 | 0 | 0 | 25 | 0 | 0 | 0 | 0 | 25 | 0 | 0 | 25 | 0 | 0 | 0 | 0
26 | 0 | 0 | 26 | 0 | 0 | 0 | 0 | 26 | 0 | 0 | 26 | 0 | 0 | 0 | 0 | 26 | 0 | 0 | 26 | 0 | 0 | 0 | 0 | 26 | 0 | 0 | 26 | 0 | 0 | 0 | 0 | 26 | 0 | 0 | 26 | 0 | 0 | 0 | 0 | 26 | 0 | 0 | 26 | 0 | 0 | 0 | 0
27 | 0 | 0 | 27 | 0 | 0 | 0 | 0 | 27 | 0 | 0 | 27 | 0 | 0 | 0 | 0 | 27 | 0 | 0 | 27 | 0 | 0 | 0 | 0 | 27 | 0 | 0 | 27 | 0 | 0 | 0 | 0 | 27 | 0 | 0 | 27 | 0 | 0 | 0 | 0 | 27 | 0 | 0 | 27 | 0 | 0 | 0 | 0
28 | 0 | 0 | 28 | 0 | 0 | 0 | 0 | 28 | 0 | 0 | 28 | 0 | 0 | 0 | 0 | 28 | 0 | 0 | 28 | 0 | 0 | 0 | 0 | 28 | 0 | 0 | 28 | 0 | 0 | 0 | 0 | 28 | 0 | 0 | 28 | 0 | 0 | 0 | 0 | 28 | 0 | 0 | 28 | 0 | 0 | 0 | 0
29 | 0 | 0 | 29 | 0 | 0 | 0 | 0 | 29 | 0 | 0 | 29 | 0 | 0 | 0 | 0 | 29 | 0 | 0 | 29 | 0 | 0 | 0 | 0 | 29 | 0 | 0 | 29 | 0 | 0 | 0 | 0 | 29 | 0 | 0 | 29 | 0 | 0 | 0 | 0 | 29 | 0 | 0 | 29 | 0 | 0 | 0 | 0
30 | 0 | 0 | 30 | 0 | 0 | 0 | 0 | 30 | 0 | 0 | 30 | 0 | 0 | 0 | 0 | 30 | 0 | 0 | 30 | 0 | 0 | 0 | 0 | 30 | 0 | 0 | 30 | 0 | 0 | 0 | 0 | 30 | 0 | 0 | 30 | 0 | 0 | 0 | 0 | 30 | 0 | 0 | 30 | 0 | 0 | 0 | 0
31 | 0 | 0 | 31 | 0 | 0 | 0 | 0 | 31 | 0 | 0 | 31 | 0 | 0 | 0 | 0 | 31 | 0 | 0 | 31 | 0 | 0 | 0 | 0 | 31 | 0 | 0 | 31 | 0 | 0 | 0 | 0 | 31 | 0 | 0 | 31 | 0 | 0 | 0 | 0 | 31 | 0 | 0 | 31 | 0 | 0 | 0 | 0
32 | 0 | 0 | 32 | 0 | 0 | 0 | 0 | 32 | 0 | 0 | 32 | 0 | 0 | 0 | 0 | 32 | 0 | 0 | 32 | 0 | 0 | 0 | 0 | 32 | 0 | 0 | 32 | 0 | 0 | 0 | 0 | 32 | 0 | 0 | 32 | 0 | 0 | 0 | 0 | 32 | 0 | 0 | 32 | 0 | 0 | 0 | 0
33 | 0 | 0 | 33 | 0 | 0 | 0 | 0 | 33 | 0 | 0 | 33 | 0 | 0 | 0 | 0 | 33 | 0 | 0 | 33 | 0 | 0 | 0 | 0 | 33 | 0 | 0 | 33 | 0 | 0 | 0 | 0 | 33 | 0 | 0 | 33 | 0 | 0 | 0 | 0 | 33 | 0 | 0 | 33 | 0 | 0 | 0 | 0
34 | 0 | 0 | 34 | 0 | 0 | 0 | 0 | 34 | 0 | 0 | 34 | 0 | 0 | 0 | 0 | 34 | 0 | 0 | 34 | 0 | 0 | 0 | 0 | 34 | 0 | 0 | 34 | 0 | 0 | 0 | 0 | 34 | 0 | 0 | 34 | 0 | 0 | 0 | 0 | 34 | 0 | 0 | 34 | 0 | 0 | 0 | 0
35 | 0 | 0 | 35 | 0 | 0 | 0 | 0 | 35 | 0 | 0 | 35 | 0 | 0 | 0 | 0 | 35 | 0 | 0 | 35 | 0 | 0 | 0 | 0 | 35 | 0 | 0 | 35 | 0 | 0 | 0 | 0 | 35 | 0 | 0 | 35 | 0 | 0 | 0 | 0 | 35 | 0 | 0 | 35 | 0 | 0 | 0 | 0
36 | 0 | 0 | 36 | 0 | 0 | 0 | 0 | 36 | 0 | 0 | 36 | 0 | 0 | 0 | 0 | 36 | 0 | 0 | 36 | 0 | 0 | 0 | 0 | 36 | 0 | 0 | 36 | 0 | 0 | 0 | 0 | 36 | 0 | 0 | 36 | 0 | 0 | 0 | 0 | 36 | 0 | 0 | 36 | 0 | 0 | 0 | 0
37 | 0 | 0 | 37 | 0 | 0 | 0 | 0 | 37 | 0 | 0 | 37 | 0 | 0 | 0 | 0 | 37 | 0 | 0 | 37 | 0 | 0 | 0 | 0 | 37 | 0 | 0 | 37 | 0 | 0 | 0 | 0 | 37 | 0 | 0 | 37 | 0 | 0 | 0 | 0 | 37 | 0 | 0 | 37 | 0 | 0 | 0 | 0
38 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 38 | 0 | 0 | 0 | 0
39 | 0 | 0 | 39 | 0 | 0 | 0 | 0 | 39 | 0 | 0 | 39 | 0 | 0 | 0 | 0 | 39 | 0 | 0 | 39 | 0 | 0 | 0 | 0 | 39 | 0 | 0 | 39 | 0 | 0 | 0 | 0 | 39 | 0 | 0 | 39 | 0 | 0 | 0 | 0 | 39 | 0 | 0 | 39 | 0 | 0 | 0 | 0
40 | 0 | 0 | 40 | 0 | 0 | 0 | 0 | 40 | 0 | 0 | 40 | 0 | 0 | 0 | 0 | 40 | 0 | 0 | 40 | 0 | 0 | 0 | 0 | 40 | 0 | 0 | 40 | 0 | 0 | 0 | 0 | 40 | 0 | 0 | 40 | 0 | 0 | 0 | 0 | 40 | 0 | 0 | 40 | 0 | 0 | 0 | 0
Residual Year 30 |  | 0 | Residual Year 30 |  | 0 |  | 0 | Residual Year 30 |  | 0 | Residual Year 30 |  | 0 |  | 0 | Residual Year 30 |  | 0 | Residual Year 30 |  | 0 |  | 0 | Residual Year 30 |  | 0 | Residual Year 30 |  | 0 |  | 0 | Residual Year 30 |  | 0 | Residual Year 30 |  | 0 |  | 0 | Residual Year 30 |  | 0 | Residual Year 30 |  | 0 |  | 0
Residual Year 40 |  | 0 | Residual Year 40 |  | 0 |  | 0 | Residual Year 40 |  | 0 | Residual Year 40 |  | 0 |  | 0 | Residual Year 40 |  | 0 | Residual Year 40 |  | 0 |  | 0 | Residual Year 40 |  | 0 | Residual Year 40 |  | 0 |  | 0 | Residual Year 40 |  | 0 | Residual Year 40 |  | 0 |  | 0 | Residual Year 40 |  | 0 | Residual Year 40 |  | 0 |  | 0

## Int Ltg Occ Sens Proto 90.1 (hidden)
[6 empty] | Commercial Energy Code Cost Effectiveness - Cost Estimate - Interior Lighting - Occupancy Control Addenda Cost Estimates 90.1-2010 and 90.1-2013 | [12 empty] | 90.1-2019 | [33 empty] | 90.1 Cost Effectiveness - Occupancy Sensor Controls - Prototype
[6 empty] | Multiple addenda to 90.1-2010 modify requirements for occupancy based controls. Costs are provided for added or changed occupancy controls, so there are no baseline costs shown. Occupancy sensors are used for the cost estimate to meet the occupancy controls requirements although other options are possible. The sensors are assumed to have a 15 year life as supported by members of the 90.1 lighting subcommittee. Commissioning costs are included and described in the methodology. | [46 empty] | Summary
[53 empty] | Named range | L2_Sm_Off_901 | [7 empty] | Named range | L2_Lg_Off_901 | [6 empty] | Named range | L2_St_Ret_901 | [6 empty] | Named range | L2_Pr_Sch_901 | [6 empty] | Named range | L2_Sm_Hot_901 | [6 empty] | Named range | L2_Mid_Apt_901
Interior Lighting - Summary of Total New Construction, Maintenance, and Replacement Costs By Replacement Year by Prototype
[6 empty] | Item and Addenda / Affected Prototype and Space Type |  | 90.1-2010 Description |  |  |  |  | 90.1-2013 Description | [7 empty] | 90.1-2019 | Baseline costs | [6 empty] | 90.1-2019 | [7 empty] | 90.1-2022 | [14 empty] | Incremental Costs | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9
Prototypes Affected | [17 empty] | Other Cost Parameters |  | New Construction Costs | New Construction Costs | [6 empty] | Maintenance Cost | Replacement Costs | [6 empty] | New Construction Costs | New Construction Costs | [5 empty] | Maintenance Costs (none) | Replacement Costs (none) | [8 empty] | Interior Lighting - Summary of Total New Construction, Maintenance, and Replacement Costs By Replacement Year by Prototype 1: Small Office | Large Office | [7 empty] | Standalone Retail | [7 empty] | Primary School | [7 empty] | Small Hotel | [7 empty] | Mid-rise Apartment
Small Office | Large Office | Standalone Retail | Primary School | Small Hotel | Mid-rise Apartment |  |  | Description of cost items | Not Used | Not Used | Space Type Area, ft2 | Number of controlled spaces of the space type | Description of Cost Items | Lookup Value | Not Used | Space Type Area, ft2 | Number of controlled spaces of the space type | Not Used | Not Used | Not Used | Material Subtotal | Not Used | Not Used | Labor Subtotal | Construction Equipment Subtotal | Cost Adjustments | Total | Annual Maintenance (none) | Replacement Life years | Material ($/UoM) | Material Subtotal | Labor Subtotal | Construction Equipment Subtotal | Cost Adjustments | Total | Not Used | Material Subtotal | Labor | Construction Equipment Subtotal | Cost Adjustments | Incremental Added Commis- sioning | Total Cost | Annual Maintenance Cost | Replacement Life (years) | Not Used | Material Subtotal | Labor Subtotal with replacement hours adjustment | Construction Equipment Subtotal | Cost Adjustments | Incremental Added Commis- sioning with OH&P | Total | New Construction Costs Target minus Base | Interior Lighting - Summary of Total New Construction, Maintenance, and Replacement Costs By Replacement Year by Prototype 1: 90.1-2019; Interior Lighting - Summary of Total New Construction, Maintenance, and Replacement Costs By Replacement Year by Prototype 5: 90.1-2022; Interior Lighting - Summary of Total New Construction, Maintenance, and Replacement Costs By Replacement Year by Prototype 8: Incremental Cost | 90.1-2019 |  |  | 90.1-2022 |  |  | Incremental Cost |  | 90.1-2019 |  |  | 90.1-2022 |  |  | Incremental Cost |  | 90.1-2019 |  |  | 90.1-2022 |  |  | Incremental Cost |  | 90.1-2019 |  |  | 90.1-2022 |  |  | Incremental Cost |  | 90.1-2019 |  |  | 90.1-2022 |  |  | Incremental Cost
[6 empty] | Automatic Lighting Shutoff Addenda 90.1-10by 90.1-2013 Section 9.4.1 | [46 empty] | Category | All Costs, First Replacement Only | With Repeated Replacements |  | Category | Replacement First Year | With Repeated Replacements | 30 Year | 40 Year | Category | All Costs, First Replacement Only | With Repeated Replacements | Category | Replacement First Year | With Repeated Replacements | 30 Year | 40 Year | Category | All Costs, First Replacement Only | With Repeated Replacements | Category | Replacement First Year | With Repeated Replacements | 30 Year | 40 Year | Category | All Costs, First Replacement Only | With Repeated Replacements | Category | Replacement First Year | With Repeated Replacements | 30 Year | 40 Year | Category | All Costs, First Replacement Only | With Repeated Replacements | Category | Replacement First Year | With Repeated Replacements | 30 Year | 40 Year | Category | All Costs, First Replacement Only | With Repeated Replacements | Category | Replacement First Year | With Repeated Replacements | 30 Year | 40 Year
[6 empty] | Small Office | [46 empty] | New Construction | 0 | 0 |  | New Construction | 0 | 0 | 0 | 0 | New Construction | 0 | 0 | New Construction | 0 | 0 | 0 | 0 | New Construction | 0 | 0 | New Construction | 0 | 0 | 0 | 0 | New Construction | 0 | 0 | New Construction | 0 | 0 | 0 | 0 | New Construction | 0 | 0 | New Construction | 0 | 0 | 0 | 0 | New Construction | 0 | 0 | New Construction | 0 | 0 | 0 | 0
0 | [5 empty] | Corridor - Other than hospital corridors | Corridor | [5 empty] | auto on/off |  |  | 660 | 2 | [19 empty] | 254.5 | 153.9621 |  | 276.2276 | 16.3385 | 701.0282 |  | 15 |  | 254.5 | 254.0375 |  | 442.7955 | 16.3385 | 967.6714 | 701.0282 | Maintenance | 0 | 0 |  | Maintenance | 0 | 0 | 0 | 0 | Maintenance | 0 | 0 | Maintenance | 0 | 0 | 0 | 0 | Maintenance | 0 | 0 | Maintenance | 0 | 0 | 0 | 0 | Maintenance | 0 | 0 | Maintenance | 0 | 0 | 0 | 0 | Maintenance | 0 | 0 | Maintenance | 0 | 0 | 0 | 0 | Maintenance | 0 | 0 | Maintenance | 0 | 0 | 0 | 0
0 | [5 empty] | Lobby - Other than in hotels and elevator lobbies | Lobby | [5 empty] | auto on/off |  |  | 330 | 1 | [19 empty] | 217.9 | 82.9078 |  | 189.2782 | 12.0323 | 502.1184 |  | 15 |  | 217.9 | 136.798 |  | 291.1126 | 12.0323 | 657.8429 | 502.1184 | Interior Lighting - Summary of Total New Construction, Maintenance, and Replacement Costs By Replacement Year by Prototype 1: Replacement - Year; Interior Lighting - Summary of Total New Construction, Maintenance, and Replacement Costs By Replacement Year by Prototype 5: Replacement - Year; Interior Lighting - Summary of Total New Construction, Maintenance, and Replacement Costs By Replacement Year by Prototype 8: 0; Interior Lighting - Summary of Total New Construction, Maintenance, and Replacement Costs By Replacement Year by Prototype 9: 0 | Replacement - Year |  |  | Replacement - Year |  |  | 0 | 0 | Replacement - Year |  |  | Replacement - Year |  |  | 0 | 0 | Replacement - Year |  |  | Replacement - Year |  |  | 0 | 0 | Replacement - Year |  |  | Replacement - Year |  |  | 0 | 0 | Replacement - Year |  |  | Replacement - Year |  |  | 0 | 0
[53 empty] | 1 | 0 | 0 |  | 1 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 0
[6 empty] | Large Office | [46 empty] | 2 | 0 | 0 |  | 2 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 0 | 0
| 0 |  |  |  |  | Corridor - Other than hospital corridors | Corridor | [5 empty] | auto on/off |  |  | 21304 | 36 | [19 empty] | 4581 | 2771.3178 |  | 4972.0964 | 294.0927 | 12618.5069 |  | 15 |  | 4581 | 4572.6744 |  | 7970.3184 | 294.0927 | 17418.0855 | 12618.5069 | 3 | 0 | 0 |  | 3 | 0 | 0 | 0 | 0 | 3 | 0 | 0 | 3 | 0 | 0 | 0 | 0 | 3 | 0 | 0 | 3 | 0 | 0 | 0 | 0 | 3 | 0 | 0 | 3 | 0 | 0 | 0 | 0 | 3 | 0 | 0 | 3 | 0 | 0 | 0 | 0 | 3 | 0 | 0 | 3 | 0 | 0 | 0 | 0
| 0 |  |  |  |  | Lobby - Other than in hotels and elevator lobbies | Lobby | [5 empty] | auto on/off |  |  | 11669 | 15 | [19 empty] | 3268.5 | 1243.6177 |  | 2839.1735 | 180.4847 | 7531.776 |  | 15 |  | 3268.5 | 2051.9693 |  | 4366.6896 | 180.4847 | 9867.6436 | 7531.776 | 4 | 0 | 0 |  | 4 | 0 | 0 | 0 | 0 | 4 | 0 | 0 | 4 | 0 | 0 | 0 | 0 | 4 | 0 | 0 | 4 | 0 | 0 | 0 | 0 | 4 | 0 | 0 | 4 | 0 | 0 | 0 | 0 | 4 | 0 | 0 | 4 | 0 | 0 | 0 | 0 | 4 | 0 | 0 | 4 | 0 | 0 | 0 | 0
| 0 |  |  |  |  | Storage - Larger than 1000 ft2 | Storage | [5 empty] | manual on/off |  |  | 7380 | 6 | [19 empty] | 1231.5 | 497.4471 |  | 1097.6213 | 69.1579 | 2895.7263 |  | 15 |  | 1231.5 | 820.7877 |  | 1697.2329 | 69.1579 | 3818.6785 | 2895.7263 | 5 | 0 | 0 |  | 5 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 5 | 0 | 0 | 0 | 0
[53 empty] | 6 | 0 | 0 |  | 6 | 0 | 0 | 0 | 0 | 6 | 0 | 0 | 6 | 0 | 0 | 0 | 0 | 6 | 0 | 0 | 6 | 0 | 0 | 0 | 0 | 6 | 0 | 0 | 6 | 0 | 0 | 0 | 0 | 6 | 0 | 0 | 6 | 0 | 0 | 0 | 0 | 6 | 0 | 0 | 6 | 0 | 0 | 0 | 0
[6 empty] | Standalone Retail | [46 empty] | 7 | 0 | 0 |  | 7 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 7 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 7 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 7 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 7 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 7 | 0 | 0 | 0 | 0
|  | 0 |  |  |  | Corridor - Other than hospital corridors | Corridor | [5 empty] | auto on/off |  |  | 249 | 1 | [19 empty] | 127.25 | 76.981 |  | 138.1138 | 8.1692 | 350.5141 |  | 15 |  | 127.25 | 127.0187 |  | 221.3977 | 8.1692 | 483.8357 | 350.5141 | 8 | 0 | 0 |  | 8 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 8 | 0 | 0 | 0 | 0
|  | 0 |  |  |  | Lobby - Other than in hotels and elevator lobbies | Lobby | [5 empty] | auto on/off |  |  | 1033 | 2 | [19 empty] | 435.8 | 165.8157 |  | 378.5565 | 24.0646 | 1004.2368 |  | 15 |  | 435.8 | 273.5959 |  | 582.2253 | 24.0646 | 1315.6858 | 1004.2368 | 9 | 0 | 0 |  | 9 | 0 | 0 | 0 | 0 | 9 | 0 | 0 | 9 | 0 | 0 | 0 | 0 | 9 | 0 | 0 | 9 | 0 | 0 | 0 | 0 | 9 | 0 | 0 | 9 | 0 | 0 | 0 | 0 | 9 | 0 | 0 | 9 | 0 | 0 | 0 | 0 | 9 | 0 | 0 | 9 | 0 | 0 | 0 | 0
|  | 0 |  |  |  | Storage - Larger than 1000 ft2 | Storage | [5 empty] | manual on/off |  |  | 1972 | 2 | [19 empty] | 410.5 | 165.8157 |  | 365.8738 | 23.0526 | 965.2421 |  | 15 |  | 410.5 | 273.5959 |  | 565.7443 | 23.0526 | 1272.8928 | 965.2421 | 10 | 0 | 0 |  | 10 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 10 | 0 | 0 | 0 | 0
[53 empty] | 11 | 0 | 0 |  | 11 | 0 | 0 | 0 | 0 | 11 | 0 | 0 | 11 | 0 | 0 | 0 | 0 | 11 | 0 | 0 | 11 | 0 | 0 | 0 | 0 | 11 | 0 | 0 | 11 | 0 | 0 | 0 | 0 | 11 | 0 | 0 | 11 | 0 | 0 | 0 | 0 | 11 | 0 | 0 | 11 | 0 | 0 | 0 | 0
[6 empty] | Primary School | [46 empty] | 12 | 0 | 0 |  | 12 | 0 | 0 | 0 | 0 | 12 | 0 | 0 | 12 | 0 | 0 | 0 | 0 | 12 | 0 | 0 | 12 | 0 | 0 | 0 | 0 | 12 | 0 | 0 | 12 | 0 | 0 | 0 | 0 | 12 | 0 | 0 | 12 | 0 | 0 | 0 | 0 | 12 | 0 | 0 | 12 | 0 | 0 | 0 | 0
|  |  | 0 |  |  | Corridor - Other than hospital corridors | Corridor | [5 empty] | auto on/off |  |  | 12648 | 22 | [19 empty] | 2799.5 | 1693.5831 |  | 3038.5034 | 179.7233 | 7711.3098 |  | 15 |  | 2799.5 | 2794.4121 |  | 4870.7501 | 179.7233 | 10644.3856 | 7711.3098 | 13 | 0 | 0 |  | 13 | 0 | 0 | 0 | 0 | 13 | 0 | 0 | 13 | 0 | 0 | 0 | 0 | 13 | 0 | 0 | 13 | 0 | 0 | 0 | 0 | 13 | 0 | 0 | 13 | 0 | 0 | 0 | 0 | 13 | 0 | 0 | 13 | 0 | 0 | 0 | 0 | 13 | 0 | 0 | 13 | 0 | 0 | 0 | 0
|  |  | 0 |  |  | Lab Classroom | Classroom/Lecture/Training | [5 empty] | Manual On/ Auto Off |  |  | 5400 | 6 | [19 empty] | 1231.5 | 497.4471 |  | 1097.6213 | 69.1579 | 2895.7263 |  | 15 |  | 1231.5 | 820.7877 |  | 1697.2329 | 69.1579 | 3818.6785 | 2895.7263 | 14 | 0 | 0 |  | 14 | 0 | 0 | 0 | 0 | 14 | 0 | 0 | 14 | 0 | 0 | 0 | 0 | 14 | 0 | 0 | 14 | 0 | 0 | 0 | 0 | 14 | 0 | 0 | 14 | 0 | 0 | 0 | 0 | 14 | 0 | 0 | 14 | 0 | 0 | 0 | 0 | 14 | 0 | 0 | 14 | 0 | 0 | 0 | 0
|  |  | 0 |  |  | Lobby - Other than in hotels and elevator lobbies | Lobby | [5 empty] | auto on/off |  |  | 1841 | 3 | [19 empty] | 653.7 | 248.7235 |  | 567.8347 | 36.0969 | 1506.3552 |  | 15 |  | 653.7 | 410.3939 |  | 873.3379 | 36.0969 | 1973.5287 | 1506.3552 | 15 | 0 | 0 |  | 15 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 15 | 0 | 0 | 0 | 0
|  |  | 0 |  |  | Library Stacks Area | Library Stacks | [8 empty] | 2148 | 3 | [35 empty] | 16 | 0 | 0 |  | 16 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 16 | 0 | 0 | 0 | 0
[53 empty] | 17 | 0 | 0 |  | 17 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 17 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 17 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 17 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 17 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 17 | 0 | 0 | 0 | 0
[6 empty] | Small Hotel | [46 empty] | 18 | 0 | 0 |  | 18 | 0 | 0 | 0 | 0 | 18 | 0 | 0 | 18 | 0 | 0 | 0 | 0 | 18 | 0 | 0 | 18 | 0 | 0 | 0 | 0 | 18 | 0 | 0 | 18 | 0 | 0 | 0 | 0 | 18 | 0 | 0 | 18 | 0 | 0 | 0 | 0 | 18 | 0 | 0 | 18 | 0 | 0 | 0 | 0
|  |  |  | 0 |  | Corridor - Other than hospital corridors | Corridor | [5 empty] | auto on/off |  |  | 5671 | 10 | [19 empty] | 1272.5 | 769.8105 |  | 1381.1379 | 81.6924 | 3505.1408 |  | 15 |  | 1272.5 | 1270.1873 |  | 2213.9773 | 81.6924 | 4838.3571 | 3505.1408 | 19 | 0 | 0 |  | 19 | 0 | 0 | 0 | 0 | 19 | 0 | 0 | 19 | 0 | 0 | 0 | 0 | 19 | 0 | 0 | 19 | 0 | 0 | 0 | 0 | 19 | 0 | 0 | 19 | 0 | 0 | 0 | 0 | 19 | 0 | 0 | 19 | 0 | 0 | 0 | 0 | 19 | 0 | 0 | 19 | 0 | 0 | 0 | 0
[45 empty] | 0 | [7 empty] | 20 | 0 | 0 |  | 20 | 0 | 0 | 0 | 0 | 20 | 0 | 0 | 20 | 0 | 0 | 0 | 0 | 20 | 0 | 0 | 20 | 0 | 0 | 0 | 0 | 20 | 0 | 0 | 20 | 0 | 0 | 0 | 0 | 20 | 0 | 0 | 20 | 0 | 0 | 0 | 0 | 20 | 0 | 0 | 20 | 0 | 0 | 0 | 0
[6 empty] | Mid-rise Apartment | [46 empty] | 21 | 0 | 0 |  | 21 | 0 | 0 | 0 | 0 | 21 | 0 | 0 | 21 | 0 | 0 | 0 | 0 | 21 | 0 | 0 | 21 | 0 | 0 | 0 | 0 | 21 | 0 | 0 | 21 | 0 | 0 | 0 | 0 | 21 | 0 | 0 | 21 | 0 | 0 | 0 | 0 | 21 | 0 | 0 | 21 | 0 | 0 | 0 | 0
[5 empty] | 0 | Corridor - Other than hospital corridors | Corridor | [5 empty] | auto on/off |  |  | 2508 | 5 | [19 empty] | 636.25 | 384.9053 |  | 690.5689 | 40.8462 | 1752.5704 |  | 15 |  | 636.25 | 635.0937 |  | 1106.9887 | 40.8462 | 2419.1785 | 1752.5704 | 22 | 0 | 0 |  | 22 | 0 | 0 | 0 | 0 | 22 | 0 | 0 | 22 | 0 | 0 | 0 | 0 | 22 | 0 | 0 | 22 | 0 | 0 | 0 | 0 | 22 | 0 | 0 | 22 | 0 | 0 | 0 | 0 | 22 | 0 | 0 | 22 | 0 | 0 | 0 | 0 | 22 | 0 | 0 | 22 | 0 | 0 | 0 | 0
[53 empty] | 23 | 0 | 0 |  | 23 | 0 | 0 | 0 | 0 | 23 | 0 | 0 | 23 | 0 | 0 | 0 | 0 | 23 | 0 | 0 | 23 | 0 | 0 | 0 | 0 | 23 | 0 | 0 | 23 | 0 | 0 | 0 | 0 | 23 | 0 | 0 | 23 | 0 | 0 | 0 | 0 | 23 | 0 | 0 | 23 | 0 | 0 | 0 | 0
[6 empty] | Hotel Guestroom Automatic Lighting Shutoff 90.1-2013 section 9.4.1.3 Addenda 90.1-10bc |  | Guestroom automatic lighting shut off not required |  |  |  |  | Guestroom lighting needs to be controlled automatically |  |  |  | No,. Of Guestrooms | [35 empty] | 24 | 0 | 0 |  | 24 | 0 | 0 | 0 | 0 | 24 | 0 | 0 | 24 | 0 | 0 | 0 | 0 | 24 | 0 | 0 | 24 | 0 | 0 | 0 | 0 | 24 | 0 | 0 | 24 | 0 | 0 | 0 | 0 | 24 | 0 | 0 | 24 | 0 | 0 | 0 | 0 | 24 | 0 | 0 | 24 | 0 | 0 | 0 | 0
|  |  |  | 0 |  | Small Hotel | Hotel Guestroom | [5 empty] | number of guestrooms |  |  |  | 78 | [19 empty] | 5906.55 | 5610.3489 |  | 8377.6355 | 460.676 | 20355.2104 |  | 15 |  | 5906.55 | 9257.0757 |  | 13941.7946 | 460.676 | 29566.0962 | 20355.2104 | 25 | 0 | 0 |  | 25 | 0 | 0 | 0 | 0 | 25 | 0 | 0 | 25 | 0 | 0 | 0 | 0 | 25 | 0 | 0 | 25 | 0 | 0 | 0 | 0 | 25 | 0 | 0 | 25 | 0 | 0 | 0 | 0 | 25 | 0 | 0 | 25 | 0 | 0 | 0 | 0 | 25 | 0 | 0 | 25 | 0 | 0 | 0 | 0
[53 empty] | 26 | 0 | 0 |  | 26 | 0 | 0 | 0 | 0 | 26 | 0 | 0 | 26 | 0 | 0 | 0 | 0 | 26 | 0 | 0 | 26 | 0 | 0 | 0 | 0 | 26 | 0 | 0 | 26 | 0 | 0 | 0 | 0 | 26 | 0 | 0 | 26 | 0 | 0 | 0 | 0 | 26 | 0 | 0 | 26 | 0 | 0 | 0 | 0
[53 empty] | 27 | 0 | 0 |  | 27 | 0 | 0 | 0 | 0 | 27 | 0 | 0 | 27 | 0 | 0 | 0 | 0 | 27 | 0 | 0 | 27 | 0 | 0 | 0 | 0 | 27 | 0 | 0 | 27 | 0 | 0 | 0 | 0 | 27 | 0 | 0 | 27 | 0 | 0 | 0 | 0 | 27 | 0 | 0 | 27 | 0 | 0 | 0 | 0
[53 empty] | 28 | 0 | 0 |  | 28 | 0 | 0 | 0 | 0 | 28 | 0 | 0 | 28 | 0 | 0 | 0 | 0 | 28 | 0 | 0 | 28 | 0 | 0 | 0 | 0 | 28 | 0 | 0 | 28 | 0 | 0 | 0 | 0 | 28 | 0 | 0 | 28 | 0 | 0 | 0 | 0 | 28 | 0 | 0 | 28 | 0 | 0 | 0 | 0
[53 empty] | 29 | 0 | 0 |  | 29 | 0 | 0 | 0 | 0 | 29 | 0 | 0 | 29 | 0 | 0 | 0 | 0 | 29 | 0 | 0 | 29 | 0 | 0 | 0 | 0 | 29 | 0 | 0 | 29 | 0 | 0 | 0 | 0 | 29 | 0 | 0 | 29 | 0 | 0 | 0 | 0 | 29 | 0 | 0 | 29 | 0 | 0 | 0 | 0
[53 empty] | 30 | 0 | 0 |  | 30 | 0 | 0 | 0 | 0 | 30 | 0 | 0 | 30 | 0 | 0 | 0 | 0 | 30 | 0 | 0 | 30 | 0 | 0 | 0 | 0 | 30 | 0 | 0 | 30 | 0 | 0 | 0 | 0 | 30 | 0 | 0 | 30 | 0 | 0 | 0 | 0 | 30 | 0 | 0 | 30 | 0 | 0 | 0 | 0
[53 empty] | 31 | 0 | 0 |  | 31 | 0 | 0 |  | 0 | 31 | 0 | 0 | 31 | 0 | 0 |  | 0 | 31 | 0 | 0 | 31 | 0 | 0 |  | 0 | 31 | 0 | 0 | 31 | 0 | 0 |  | 0 | 31 | 0 | 0 | 31 | 0 | 0 |  | 0 | 31 | 0 | 0 | 31 | 0 | 0 |  | 0
[53 empty] | 32 | 0 | 0 |  | 32 | 0 | 0 |  | 0 | 32 | 0 | 0 | 32 | 0 | 0 |  | 0 | 32 | 0 | 0 | 32 | 0 | 0 |  | 0 | 32 | 0 | 0 | 32 | 0 | 0 |  | 0 | 32 | 0 | 0 | 32 | 0 | 0 |  | 0 | 32 | 0 | 0 | 32 | 0 | 0 |  | 0
[53 empty] | 33 | 0 | 0 |  | 33 | 0 | 0 |  | 0 | 33 | 0 | 0 | 33 | 0 | 0 |  | 0 | 33 | 0 | 0 | 33 | 0 | 0 |  | 0 | 33 | 0 | 0 | 33 | 0 | 0 |  | 0 | 33 | 0 | 0 | 33 | 0 | 0 |  | 0 | 33 | 0 | 0 | 33 | 0 | 0 |  | 0
[53 empty] | 34 | 0 | 0 |  | 34 | 0 | 0 |  | 0 | 34 | 0 | 0 | 34 | 0 | 0 |  | 0 | 34 | 0 | 0 | 34 | 0 | 0 |  | 0 | 34 | 0 | 0 | 34 | 0 | 0 |  | 0 | 34 | 0 | 0 | 34 | 0 | 0 |  | 0 | 34 | 0 | 0 | 34 | 0 | 0 |  | 0
[53 empty] | 35 | 0 | 0 |  | 35 | 0 | 0 |  | 0 | 35 | 0 | 0 | 35 | 0 | 0 |  | 0 | 35 | 0 | 0 | 35 | 0 | 0 |  | 0 | 35 | 0 | 0 | 35 | 0 | 0 |  | 0 | 35 | 0 | 0 | 35 | 0 | 0 |  | 0 | 35 | 0 | 0 | 35 | 0 | 0 |  | 0
[53 empty] | 36 | 0 | 0 |  | 36 | 0 | 0 |  | 0 | 36 | 0 | 0 | 36 | 0 | 0 |  | 0 | 36 | 0 | 0 | 36 | 0 | 0 |  | 0 | 36 | 0 | 0 | 36 | 0 | 0 |  | 0 | 36 | 0 | 0 | 36 | 0 | 0 |  | 0 | 36 | 0 | 0 | 36 | 0 | 0 |  | 0
[53 empty] | 37 | 0 | 0 |  | 37 | 0 | 0 |  | 0 | 37 | 0 | 0 | 37 | 0 | 0 |  | 0 | 37 | 0 | 0 | 37 | 0 | 0 |  | 0 | 37 | 0 | 0 | 37 | 0 | 0 |  | 0 | 37 | 0 | 0 | 37 | 0 | 0 |  | 0 | 37 | 0 | 0 | 37 | 0 | 0 |  | 0
[53 empty] | 38 | 0 | 0 |  | 38 | 0 | 0 |  | 0 | 38 | 0 | 0 | 38 | 0 | 0 |  | 0 | 38 | 0 | 0 | 38 | 0 | 0 |  | 0 | 38 | 0 | 0 | 38 | 0 | 0 |  | 0 | 38 | 0 | 0 | 38 | 0 | 0 |  | 0 | 38 | 0 | 0 | 38 | 0 | 0 |  | 0
[53 empty] | 39 | 0 | 0 |  | 39 | 0 | 0 |  | 0 | 39 | 0 | 0 | 39 | 0 | 0 |  | 0 | 39 | 0 | 0 | 39 | 0 | 0 |  | 0 | 39 | 0 | 0 | 39 | 0 | 0 |  | 0 | 39 | 0 | 0 | 39 | 0 | 0 |  | 0 | 39 | 0 | 0 | 39 | 0 | 0 |  | 0
[53 empty] | 40 | 0 | 0 |  | 40 | 0 | 0 |  | 0 | 40 | 0 | 0 | 40 | 0 | 0 |  | 0 | 40 | 0 | 0 | 40 | 0 | 0 |  | 0 | 40 | 0 | 0 | 40 | 0 | 0 |  | 0 | 40 | 0 | 0 | 40 | 0 | 0 |  | 0 | 40 | 0 | 0 | 40 | 0 | 0 |  | 0
[53 empty] | Interior Lighting - Summary of Total New Construction, Maintenance, and Replacement Costs By Replacement Year by Prototype 1: Residual Year 30; Interior Lighting - Summary of Total New Construction, Maintenance, and Replacement Costs By Replacement Year by Prototype 3: 0; Interior Lighting - Summary of Total New Construction, Maintenance, and Replacement Costs By Replacement Year by Prototype 5: Residual Year 30; Interior Lighting - Summary of Total New Construction, Maintenance, and Replacement Costs By Replacement Year by Prototype 7: 0; Interior Lighting - Summary of Total New Construction, Maintenance, and Replacement Costs By Replacement Year by Prototype 9: 0 | Residual Year 30 |  | 0 | Residual Year 30 |  | 0 |  | 0 | Residual Year 30 |  | 0 | Residual Year 30 |  | 0 |  | 0 | Residual Year 30 |  | 0 | Residual Year 30 |  | 0 |  | 0 | Residual Year 30 |  | 0 | Residual Year 30 |  | 0 |  | 0 | Residual Year 30 |  | 0 | Residual Year 30 |  | 0 |  | 0
[53 empty] | Interior Lighting - Summary of Total New Construction, Maintenance, and Replacement Costs By Replacement Year by Prototype 1: Residual Year 40; Interior Lighting - Summary of Total New Construction, Maintenance, and Replacement Costs By Replacement Year by Prototype 3: 0; Interior Lighting - Summary of Total New Construction, Maintenance, and Replacement Costs By Replacement Year by Prototype 5: Residual Year 40; Interior Lighting - Summary of Total New Construction, Maintenance, and Replacement Costs By Replacement Year by Prototype 7: 0; Interior Lighting - Summary of Total New Construction, Maintenance, and Replacement Costs By Replacement Year by Prototype 9: 0 | Residual Year 40 |  | 0 | Residual Year 40 |  | 0 |  | 0 | Residual Year 40 |  | 0 | Residual Year 40 |  | 0 |  | 0 | Residual Year 40 |  | 0 | Residual Year 40 |  | 0 |  | 0 | Residual Year 40 |  | 0 | Residual Year 40 |  | 0 |  | 0 | Residual Year 40 |  | 0 | Residual Year 40 |  | 0 |  | 0

## Int Ltg Occ Sens Proto NC IECC (hidden)
[6 empty] | State Commercial Energy Code Cost Effectiveness - Cost Estimate - Interior Lighting - Occupancy Control Addenda Cost Estimates IECC 2009 (no costs), North Carolina Base Code, IECC 2012 | [12 empty] | 2007 | [35 empty] | 90.1 Cost Effectiveness - Interior Lighting Power Density 90.1-07by and 90.1-07de Costs - Prototype
Summary
[6 empty] | Occupancy sensors are used for the cost estimate to meet the occupancy controls requirements although other options are possible. The sensors are assumed to have a 30 year life as supported by members of the 90.1 lighting subcommittee, and no replacement costs are shown. Commissioning costs are included and described in the methodology. | [48 empty] | Named range | L2_Sm_Off_NC_IECC | [6 empty] | Named range | L2_Lg_Off_NC_IECC | [6 empty] | Named range | L2_St_Ret_NC_IECC | [6 empty] | Named range | L2_Pr_Sch_NC_IECC | [6 empty] | Named range | L2_Sm_Hot_NC_IECC | [6 empty] | Named range | L2_Mid_Apt_NC_IECC
Interior Lighting - Summary of Total New Construction, Maintenance, and Replacement Costs By Replacement Year by Prototype
[6 empty] | Item and Addenda / Affected Prototype and Space Type |  | NC Description |  |  |  |  | 2012 Description | [6 empty] | 90.1-2007 Baseline Costs | NC Costs | [16 empty] | 90.1-2010 - costs with addendum | 2012 - costs | [14 empty] | Incremental Costs
Prototypes Affected | [17 empty] | Other Cost Parameters |  | New Construction Costs | New Construction Costs | [7 empty] | Maintenance Cost | Replacement Costs | [7 empty] | New Construction Costs | New Construction Costs | [5 empty] | Maintenance Costs (none) | Replacement Costs | [8 empty] | Small Office | [7 empty] | Large Office | [7 empty] | Standalone Retail | [7 empty] | Primary School | [7 empty] | Small Hotel | [7 empty] | Mid-rise Apartment
Small Office | Large Office | Standalone Retail | Primary School | Small Hotel | Mid-rise Apartment |  |  | Description of cost items | Not Used | Not Used | Space Type Area, ft2 | Number of controlled spaces of the space type | Description of Cost Items | Lookup Value | Not Used | Space Type Area, ft2 | Number of controlled spaces of the space type | Not Used | Not Used | Not Used | Material Subtotal | Not Used | Not Used | Labor Subtotal | Construction Equipment Subtotal | Cost Adjustments | Commis- sioning with OH&P | Total | Annual Maintenance (none) | Replacement Life years | Material ($/UoM) | Material Subtotal | Labor Subtotal | Construction Equipment Subtotal | Cost Adjustments | Commis- sioning with OH&P | Total | Not Used | Material Subtotal | Labor | Construction Equipment Subtotal | Cost Adjustments | Commis- sioning with OH&P | Total Cost | Annual Maintenance Cost | Replacement Life (years) | Not Used | Material Subtotal | Labor Subtotal | Construction Equipment Subtotal | Cost Adjustments | Commis- sioning with OH&P | Total | New Construction Costs 2012 minus NC | North Carolina |  |  | 2012 |  |  | Incremental Cost |  | North Carolina |  |  | 2012 |  |  | Incremental Cost |  | North Carolina |  |  | 2012 |  |  | Incremental Cost |  | North Carolina |  |  | 2012 |  |  | Incremental Cost |  | North Carolina |  |  | 2012 |  |  | Incremental Cost |  | North Carolina |  |  | 2012 |  |  | Incremental Cost
[6 empty] | Automatic Lighting Shutoff | [48 empty] | Category | All Costs, First Replacement Only | With Repeated Replacements | Category | Replacement First Year | With Repeated Replacements | 30 Year | 40 Year | Category | All Costs, First Replacement Only | With Repeated Replacements | Category | Replacement First Year | With Repeated Replacements | 30 Year | 40 Year | Category | All Costs, First Replacement Only | With Repeated Replacements | Category | Replacement First Year | With Repeated Replacements | 30 Year | 40 Year | Category | All Costs, First Replacement Only | With Repeated Replacements | Category | Replacement First Year | With Repeated Replacements | 30 Year | 40 Year | Category | All Costs, First Replacement Only | With Repeated Replacements | Category | Replacement First Year | With Repeated Replacements | 30 Year | 40 Year | Category | All Costs, First Replacement Only | With Repeated Replacements | Category | Replacement First Year | With Repeated Replacements | 30 Year | 40 Year
[6 empty] | Small Office | [48 empty] | New Construction | 0 | 0 | New Construction | 0 | 0 | 0 | 0 | New Construction | 0 | 0 | New Construction | 0 | 0 | 0 | 0 | New Construction | 0 | 0 | New Construction | 0 | 0 | 0 | 0 | New Construction | 0 | 0 | New Construction | 0 | 0 | 0 | 0 | New Construction | 0 | 0 | New Construction | 0 | 0 | 0 | 0 | New Construction | 0 | 0 | New Construction | 0 | 0 | 0 | 0
n | [5 empty] | Office, Enclosed | Office, Enclosed | Manual On/Auto Off |  |  | 1595 | #N/A | Manual On/Auto Off |  |  | 1595 | #N/A |  |  |  | #N/A |  |  | #N/A |  | #N/A | #N/A | #N/A |  | 15 |  | #N/A | #N/A |  | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A | #N/A | #N/A |  | 15 |  | #N/A | #N/A |  | #N/A | #N/A | #N/A | #N/A | Maintenance | 0 | 0 | Maintenance | 0 | 0 | 0 | 0 | Maintenance | 0 | 0 | Maintenance | 0 | 0 | 0 | 0 | Maintenance | 0 | 0 | Maintenance | 0 | 0 | 0 | 0 | Maintenance | 0 | 0 | Maintenance | 0 | 0 | 0 | 0 | Maintenance | 0 | 0 | Maintenance | 0 | 0 | 0 | 0 | Maintenance | 0 | 0 | Maintenance | 0 | 0 | 0 | 0
n | [5 empty] | Storage | Storage | Manual On/Auto Off |  |  | 770 | 1 | Manual On/Auto Off |  |  | 770 | 1 |  |  |  | 205.25 |  |  | 82.9078 |  | 224.1091 | 11.5263 | 523.7933 |  | 15 |  | 205.25 | 136.798 |  | 282.8722 | 11.5263 | 636.4464 |  | 205.25 | 82.9078 |  | 182.9369 | 11.5263 | 482.621 |  | 15 |  | 205.25 | 136.798 |  | 282.8722 | 11.5263 | 636.4464 | -41.1722 | Replacement - Year |  |  | Replacement - Year |  |  | 0 | 0 | Replacement - Year |  |  | Replacement - Year |  |  | 0 | 0 | Replacement - Year |  |  | Replacement - Year |  |  | 0 | 0 | Replacement - Year |  |  | Replacement - Year |  |  | 0 | 0 | Replacement - Year |  |  | Replacement - Year |  |  | 0 | 0 | Replacement - Year |  |  | Replacement - Year |  |  | 0 | 0
n | [5 empty] | Restrooms | Restrooms | [5 empty] | Auto On/Off |  |  | 220.0033 | #N/A | [21 empty] | #N/A | #N/A |  | #N/A | #N/A | #N/A |  | 15 |  | #N/A | #N/A |  | #N/A | #N/A | #N/A | #N/A | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 0
[55 empty] | 2 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 0 | 0
[6 empty] | Large Office | [48 empty] | 3 | 0 | 0 | 3 | 0 | 0 | 0 | 0 | 3 | 0 | 0 | 3 | 0 | 0 | 0 | 0 | 3 | 0 | 0 | 3 | 0 | 0 | 0 | 0 | 3 | 0 | 0 | 3 | 0 | 0 | 0 | 0 | 3 | 0 | 0 | 3 | 0 | 0 | 0 | 0 | 3 | 0 | 0 | 3 | 0 | 0 | 0 | 0
| n |  |  |  |  | Office, Enclosed | Office, Enclosed | Manual On/Auto Off |  |  | 92363 | #N/A | Manual On/Auto Off |  |  | 92363 | #N/A |  |  |  | #N/A |  |  | #N/A |  | #N/A | #N/A | #N/A |  | 15 |  | #N/A | #N/A |  | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A | #N/A | #N/A |  | 15 |  | #N/A | #N/A |  | #N/A | #N/A | #N/A | #N/A | 4 | 0 | 0 | 4 | 0 | 0 | 0 | 0 | 4 | 0 | 0 | 4 | 0 | 0 | 0 | 0 | 4 | 0 | 0 | 4 | 0 | 0 | 0 | 0 | 4 | 0 | 0 | 4 | 0 | 0 | 0 | 0 | 4 | 0 | 0 | 4 | 0 | 0 | 0 | 0 | 4 | 0 | 0 | 4 | 0 | 0 | 0 | 0
| n |  |  |  |  | Storage | Storage | Manual On/Auto Off |  |  | 4508 | 4 | Manual On/Auto Off |  |  | 4508 | 4 |  |  |  | 821 |  |  | 331.6314 |  | 896.4364 | 46.1053 | 2095.173 |  | 15 |  | 821 | 547.1918 |  | 1131.4886 | 46.1053 | 2545.7857 |  | 821 | 331.6314 |  | 731.7475 | 46.1053 | 1930.4842 |  | 15 |  | 821 | 547.1918 |  | 1131.4886 | 46.1053 | 2545.7857 | -164.6888 | 5 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 5 | 0 | 0 | 0 | 0
| n |  |  |  |  | Restrooms | Restrooms | [5 empty] | Manual On/Auto Off |  |  | 15505 | #N/A | [21 empty] | #N/A | #N/A |  | #N/A | #N/A | #N/A |  | 15 |  | #N/A | #N/A |  | #N/A | #N/A | #N/A | #N/A | 6 | 0 | 0 | 6 | 0 | 0 | 0 | 0 | 6 | 0 | 0 | 6 | 0 | 0 | 0 | 0 | 6 | 0 | 0 | 6 | 0 | 0 | 0 | 0 | 6 | 0 | 0 | 6 | 0 | 0 | 0 | 0 | 6 | 0 | 0 | 6 | 0 | 0 | 0 | 0 | 6 | 0 | 0 | 6 | 0 | 0 | 0 | 0
[55 empty] | 7 | 0 | 0 | 7 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 7 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 7 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 7 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 7 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 7 | 0 | 0 | 0 | 0
[6 empty] | Standalone Retail | [48 empty] | 8 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 8 | 0 | 0 | 0 | 0
|  | n |  |  |  | Storage | Storage | Manual On/Auto Off |  |  | 420 | 1 | Manual On/Auto Off |  |  | 420 | 1 |  |  |  | 205.25 |  |  | 82.9078 |  | 224.1091 | 11.5263 | 523.7933 |  | 15 |  | 205.25 | 136.798 |  | 282.8722 | 11.5263 | 636.4464 |  | 205.25 | 82.9078 |  | 182.9369 | 11.5263 | 482.621 |  | 15 |  | 205.25 | 136.798 |  | 282.8722 | 11.5263 | 636.4464 | -41.1722 | 9 | 0 | 0 | 9 | 0 | 0 | 0 | 0 | 9 | 0 | 0 | 9 | 0 | 0 | 0 | 0 | 9 | 0 | 0 | 9 | 0 | 0 | 0 | 0 | 9 | 0 | 0 | 9 | 0 | 0 | 0 | 0 | 9 | 0 | 0 | 9 | 0 | 0 | 0 | 0 | 9 | 0 | 0 | 9 | 0 | 0 | 0 | 0
|  | n |  |  |  | Office, Enclosed | Storage | Manual On/Auto Off |  |  | 444 | 1 | Manual On/Auto Off |  |  | 444 | 1 |  |  |  | 205.25 |  |  | 82.9078 |  | 224.1091 | 11.5263 | 523.7933 |  | 15 |  | 205.25 | 136.798 |  | 282.8722 | 11.5263 | 636.4464 |  | 205.25 | 82.9078 |  | 182.9369 | 11.5263 | 482.621 |  | 15 |  | 205.25 | 136.798 |  | 282.8722 | 11.5263 | 636.4464 | -41.1722 | 10 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 10 | 0 | 0 | 0 | 0
|  | n |  |  |  | Restrooms | Storage | Manual On/Auto Off |  |  | 247 | 1 | Manual On/Auto Off |  |  | 247 | 1 |  |  |  | 205.25 |  |  | 82.9078 |  | 224.1091 | 11.5263 | 523.7933 |  | 15 |  | 205.25 | 136.798 |  | 282.8722 | 11.5263 | 636.4464 |  | 205.25 | 82.9078 |  | 182.9369 | 11.5263 | 482.621 |  | 15 |  | 205.25 | 136.798 |  | 282.8722 | 11.5263 | 636.4464 | -41.1722 | 11 | 0 | 0 | 11 | 0 | 0 | 0 | 0 | 11 | 0 | 0 | 11 | 0 | 0 | 0 | 0 | 11 | 0 | 0 | 11 | 0 | 0 | 0 | 0 | 11 | 0 | 0 | 11 | 0 | 0 | 0 | 0 | 11 | 0 | 0 | 11 | 0 | 0 | 0 | 0 | 11 | 0 | 0 | 11 | 0 | 0 | 0 | 0
[55 empty] | 12 | 0 | 0 | 12 | 0 | 0 | 0 | 0 | 12 | 0 | 0 | 12 | 0 | 0 | 0 | 0 | 12 | 0 | 0 | 12 | 0 | 0 | 0 | 0 | 12 | 0 | 0 | 12 | 0 | 0 | 0 | 0 | 12 | 0 | 0 | 12 | 0 | 0 | 0 | 0 | 12 | 0 | 0 | 12 | 0 | 0 | 0 | 0
[6 empty] | Primary School | [48 empty] | 13 | 0 | 0 | 13 | 0 | 0 | 0 | 0 | 13 | 0 | 0 | 13 | 0 | 0 | 0 | 0 | 13 | 0 | 0 | 13 | 0 | 0 | 0 | 0 | 13 | 0 | 0 | 13 | 0 | 0 | 0 | 0 | 13 | 0 | 0 | 13 | 0 | 0 | 0 | 0 | 13 | 0 | 0 | 13 | 0 | 0 | 0 | 0
|  |  | n |  |  | Restrooms | Restrooms | [5 empty] | Manual On/Auto Off |  |  | 2044 | #N/A | [21 empty] | #N/A | #N/A |  | #N/A | #N/A | #N/A |  | 15 |  | #N/A | #N/A |  | #N/A | #N/A | #N/A | #N/A | 14 | 0 | 0 | 14 | 0 | 0 | 0 | 0 | 14 | 0 | 0 | 14 | 0 | 0 | 0 | 0 | 14 | 0 | 0 | 14 | 0 | 0 | 0 | 0 | 14 | 0 | 0 | 14 | 0 | 0 | 0 | 0 | 14 | 0 | 0 | 14 | 0 | 0 | 0 | 0 | 14 | 0 | 0 | 14 | 0 | 0 | 0 | 0
|  |  | n |  |  | Classroom/Lecture/Training - K-12 | Classroom/Lecture/Training | Manual On/Auto Off |  |  | 37187 | 35 | Manual On/Auto Off |  |  | 37187 | 35 |  |  |  | 7183.75 |  |  | 2901.7748 |  | 7843.8182 | 403.421 | 18332.7639 |  | 15 |  | 7183.75 | 4787.9283 |  | 9900.5253 | 403.421 | 22275.6247 |  | 7183.75 | 2901.7748 |  | 6402.7909 | 403.421 | 16891.7366 |  | 15 |  | 7183.75 | 4787.9283 |  | 9900.5253 | 403.421 | 22275.6247 | -1441.0273 | 15 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 15 | 0 | 0 | 0 | 0
|  |  | n |  |  | Office, Enclosed | Office, Enclosed | Manual On/Auto Off |  |  | 4745 | #N/A | Manual On/Auto Off |  |  | 4745 | #N/A |  |  |  | #N/A |  |  | #N/A |  | #N/A | #N/A | #N/A |  | 15 |  | #N/A | #N/A |  | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A | #N/A | #N/A |  | 15 |  | #N/A | #N/A |  | #N/A | #N/A | #N/A | #N/A | 16 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 16 | 0 | 0 | 0 | 0
[55 empty] | 17 | 0 | 0 | 17 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 17 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 17 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 17 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 17 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 17 | 0 | 0 | 0 | 0
[6 empty] | Small Hotel | [48 empty] | 18 | 0 | 0 | 18 | 0 | 0 | 0 | 0 | 18 | 0 | 0 | 18 | 0 | 0 | 0 | 0 | 18 | 0 | 0 | 18 | 0 | 0 | 0 | 0 | 18 | 0 | 0 | 18 | 0 | 0 | 0 | 0 | 18 | 0 | 0 | 18 | 0 | 0 | 0 | 0 | 18 | 0 | 0 | 18 | 0 | 0 | 0 | 0
|  |  |  | n |  | Storage | Storage | Manual On/Auto Off |  |  | 1404 | 2 | Manual On/Auto Off |  |  | 1404 | 2 |  |  |  | 410.5 |  |  | 165.8157 |  | 448.2182 | 23.0526 | 1047.5865 |  | 15 |  | 410.5 | 273.5959 |  | 565.7443 | 23.0526 | 1272.8928 |  | 410.5 | 165.8157 |  | 365.8738 | 23.0526 | 965.2421 |  | 15 |  | 410.5 | 273.5959 |  | 565.7443 | 23.0526 | 1272.8928 | -82.3444 | 19 | 0 | 0 | 19 | 0 | 0 | 0 | 0 | 19 | 0 | 0 | 19 | 0 | 0 | 0 | 0 | 19 | 0 | 0 | 19 | 0 | 0 | 0 | 0 | 19 | 0 | 0 | 19 | 0 | 0 | 0 | 0 | 19 | 0 | 0 | 19 | 0 | 0 | 0 | 0 | 19 | 0 | 0 | 19 | 0 | 0 | 0 | 0
|  |  |  | n |  | Office, Enclosed | Office, Enclosed | Manual On/Auto Off |  |  | 1404 | #N/A | Manual On/Auto Off |  |  | 1404 | #N/A |  |  |  | #N/A |  |  | #N/A |  | #N/A | #N/A | #N/A |  | 15 |  | #N/A | #N/A |  | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A | #N/A | #N/A |  | 15 |  | #N/A | #N/A |  | #N/A | #N/A | #N/A | #N/A | 20 | 0 | 0 | 20 | 0 | 0 | 0 | 0 | 20 | 0 | 0 | 20 | 0 | 0 | 0 | 0 | 20 | 0 | 0 | 20 | 0 | 0 | 0 | 0 | 20 | 0 | 0 | 20 | 0 | 0 | 0 | 0 | 20 | 0 | 0 | 20 | 0 | 0 | 0 | 0 | 20 | 0 | 0 | 20 | 0 | 0 | 0 | 0
|  |  |  | n |  | Restrooms | Restrooms | [5 empty] | Manual On/Auto Off |  |  | 351 | #N/A | [8 empty] | 0 | [12 empty] | #N/A | #N/A |  | #N/A | #N/A | #N/A |  | 15 |  | #N/A | #N/A |  | #N/A | #N/A | #N/A | #N/A | 21 | 0 | 0 | 21 | 0 | 0 | 0 | 0 | 21 | 0 | 0 | 21 | 0 | 0 | 0 | 0 | 21 | 0 | 0 | 21 | 0 | 0 | 0 | 0 | 21 | 0 | 0 | 21 | 0 | 0 | 0 | 0 | 21 | 0 | 0 | 21 | 0 | 0 | 0 | 0 | 21 | 0 | 0 | 21 | 0 | 0 | 0 | 0
[31 empty] | 0 | [15 empty] | 0 | [7 empty] | 22 | 0 | 0 | 22 | 0 | 0 | 0 | 0 | 22 | 0 | 0 | 22 | 0 | 0 | 0 | 0 | 22 | 0 | 0 | 22 | 0 | 0 | 0 | 0 | 22 | 0 | 0 | 22 | 0 | 0 | 0 | 0 | 22 | 0 | 0 | 22 | 0 | 0 | 0 | 0 | 22 | 0 | 0 | 22 | 0 | 0 | 0 | 0
[6 empty] | Mid-rise Apartment | [48 empty] | 23 | 0 | 0 | 23 | 0 | 0 | 0 | 0 | 23 | 0 | 0 | 23 | 0 | 0 | 0 | 0 | 23 | 0 | 0 | 23 | 0 | 0 | 0 | 0 | 23 | 0 | 0 | 23 | 0 | 0 | 0 | 0 | 23 | 0 | 0 | 23 | 0 | 0 | 0 | 0 | 23 | 0 | 0 | 23 | 0 | 0 | 0 | 0
[5 empty] | n | Office, Enclosed | Office, Enclosed | Manual On/Auto Off |  |  | 950 | #N/A | Manual On/Auto Off |  |  | 950 | #N/A |  |  |  | #N/A |  |  | #N/A |  | #N/A | #N/A | #N/A |  | 15 |  | #N/A | #N/A |  | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A | #N/A | #N/A |  | 15 |  | #N/A | #N/A |  | #N/A | #N/A | #N/A | #N/A | 24 | 0 | 0 | 24 | 0 | 0 | 0 | 0 | 24 | 0 | 0 | 24 | 0 | 0 | 0 | 0 | 24 | 0 | 0 | 24 | 0 | 0 | 0 | 0 | 24 | 0 | 0 | 24 | 0 | 0 | 0 | 0 | 24 | 0 | 0 | 24 | 0 | 0 | 0 | 0 | 24 | 0 | 0 | 24 | 0 | 0 | 0 | 0
[55 empty] | 25 | 0 | 0 | 25 | 0 | 0 | 0 | 0 | 25 | 0 | 0 | 25 | 0 | 0 | 0 | 0 | 25 | 0 | 0 | 25 | 0 | 0 | 0 | 0 | 25 | 0 | 0 | 25 | 0 | 0 | 0 | 0 | 25 | 0 | 0 | 25 | 0 | 0 | 0 | 0 | 25 | 0 | 0 | 25 | 0 | 0 | 0 | 0
[6 empty] | Occupancy Sensor Control Type Part of addenda 90.1-07aa 90.1-2010 section 9.4.1 |  | Type of automatic shut-off controls allows automatic on and off occupancy sensors. This section only includes those space types that have occupancy sensor controls in both the 90.1-2007 case and the 90.1-2010 case. |  |  |  |  | Type of automatic shut-off controls requires manual on/auto off occupancy sensors for these space types. This section only includes those space types that have occupancy sensor controls in both the 90.1-2007 case and the 90.1-2010 case. | [41 empty] | 26 | 0 | 0 | 26 | 0 | 0 | 0 | 0 | 26 | 0 | 0 | 26 | 0 | 0 | 0 | 0 | 26 | 0 | 0 | 26 | 0 | 0 | 0 | 0 | 26 | 0 | 0 | 26 | 0 | 0 | 0 | 0 | 26 | 0 | 0 | 26 | 0 | 0 | 0 | 0 | 26 | 0 | 0 | 26 | 0 | 0 | 0 | 0
n | [5 empty] | Small Office 2007 Conference/Meeting/ Multipurpose | 2007 Conference/Meeting/ Multipurpose | Auto on/off occupancy sensor control | 2007 Conference/Meeting/ Multipurpose |  | 440 | 1 | Manual On/Auto Off | 2010 Conference/Meeting/ Multipurpose |  | 440 | 1 |  |  |  | #N/A |  |  | #N/A |  | #N/A | #N/A | #N/A |  | 15 |  | #N/A | #N/A |  | #N/A |  | #N/A |  | #N/A | #N/A |  | #N/A | #N/A | #N/A |  | 15 |  | #N/A | #N/A |  | #N/A | #N/A | #N/A | #N/A | 27 | 0 | 0 | 27 | 0 | 0 | 0 | 0 | 27 | 0 | 0 | 27 | 0 | 0 | 0 | 0 | 27 | 0 | 0 | 27 | 0 | 0 | 0 | 0 | 27 | 0 | 0 | 27 | 0 | 0 | 0 | 0 | 27 | 0 | 0 | 27 | 0 | 0 | 0 | 0 | 27 | 0 | 0 | 27 | 0 | 0 | 0 | 0
[54 empty] | 0 | 28 | 0 | 0 | 28 | 0 | 0 | 0 | 0 | 28 | 0 | 0 | 28 | 0 | 0 | 0 | 0 | 28 | 0 | 0 | 28 | 0 | 0 | 0 | 0 | 28 | 0 | 0 | 28 | 0 | 0 | 0 | 0 | 28 | 0 | 0 | 28 | 0 | 0 | 0 | 0 | 28 | 0 | 0 | 28 | 0 | 0 | 0 | 0
| n |  |  |  |  | Large Office 2007 Conference/Meeting/ Multipurpose and employee lunch and break room | 2007 Conference/Meeting/ Multipurpose | Auto on/off occupancy sensor control | 2007 Conference/Meeting/ Multipurpose |  | 7726 | 24 | Manual On/Auto Off | 2010 Conference/Meeting/ Multipurpose |  | 7726 | 24 |  |  |  | #N/A |  |  | #N/A |  | #N/A | #N/A | #N/A |  | 15 |  | #N/A | #N/A |  | #N/A |  | #N/A |  | #N/A | #N/A |  | #N/A | #N/A | #N/A |  | 15 |  | #N/A | #N/A |  | #N/A | #N/A | #N/A | #N/A | 29 | 0 | 0 | 29 | 0 | 0 | 0 | 0 | 29 | 0 | 0 | 29 | 0 | 0 | 0 | 0 | 29 | 0 | 0 | 29 | 0 | 0 | 0 | 0 | 29 | 0 | 0 | 29 | 0 | 0 | 0 | 0 | 29 | 0 | 0 | 29 | 0 | 0 | 0 | 0 | 29 | 0 | 0 | 29 | 0 | 0 | 0 | 0
[54 empty] | 0 | 30 | 0 | 0 | 30 | 0 | 0 | 0 | 0 | 30 | 0 | 0 | 30 | 0 | 0 | 0 | 0 | 30 | 0 | 0 | 30 | 0 | 0 | 0 | 0 | 30 | 0 | 0 | 30 | 0 | 0 | 0 | 0 | 30 | 0 | 0 | 30 | 0 | 0 | 0 | 0 | 30 | 0 | 0 | 30 | 0 | 0 | 0 | 0
[6 empty] | Stairwell Automatic Lighting Shutoff 90.1-2010 section 9.4.1.4 Addenda 90.1-07cf |  | No automatic lighting controls required |  |  |  |  | Auto on/off occupancy sensors lighting controls required in stairwells |  |  |  | number of stair landings | [36 empty] | 0 | 31 | 0 | 0 | 31 | 0 | 0 |  | 0 | 31 | 0 | 0 | 31 | 0 | 0 |  | 0 | 31 | 0 | 0 | 31 | 0 | 0 |  | 0 | 31 | 0 | 0 | 31 | 0 | 0 |  | 0 | 31 | 0 | 0 | 31 | 0 | 0 |  | 0 | 31 | 0 | 0 | 31 | 0 | 0 |  | 0
n | [5 empty] | Small Office Stairs - Active | Stairs - Active |  |  |  |  | 1.5 | Prototype itself only has one floor. But savings included because NC3 data showed small office buildings with stairs. |  |  |  | 1.5 | [37 empty] | 32 | 0 | 0 | 32 | 0 | 0 |  | 0 | 32 | 0 | 0 | 32 | 0 | 0 |  | 0 | 32 | 0 | 0 | 32 | 0 | 0 |  | 0 | 32 | 0 | 0 | 32 | 0 | 0 |  | 0 | 32 | 0 | 0 | 32 | 0 | 0 |  | 0 | 32 | 0 | 0 | 32 | 0 | 0 |  | 0
| n |  |  |  |  | Large Office Stairs - Active | Stairs - Active |  |  |  |  | 26 | Stairwells not explicitly modeled but savings were included. Use two stairwells for costs, times 13 floors. |  |  |  | 26 | [37 empty] | 33 | 0 | 0 | 33 | 0 | 0 |  | 0 | 33 | 0 | 0 | 33 | 0 | 0 |  | 0 | 33 | 0 | 0 | 33 | 0 | 0 |  | 0 | 33 | 0 | 0 | 33 | 0 | 0 |  | 0 | 33 | 0 | 0 | 33 | 0 | 0 |  | 0 | 33 | 0 | 0 | 33 | 0 | 0 |  | 0
|  | n |  |  |  | Standalone Retail Stair - Active | Stairs - Active |  |  |  |  | 1.5 | Prototype itself only has one floor. But savings included because NC3 data showed small office buildings with stairs. |  |  |  | 1.5 | [37 empty] | 34 | 0 | 0 | 34 | 0 | 0 |  | 0 | 34 | 0 | 0 | 34 | 0 | 0 |  | 0 | 34 | 0 | 0 | 34 | 0 | 0 |  | 0 | 34 | 0 | 0 | 34 | 0 | 0 |  | 0 | 34 | 0 | 0 | 34 | 0 | 0 |  | 0 | 34 | 0 | 0 | 34 | 0 | 0 |  | 0
|  |  | n |  |  | Primary School Stairs - Active | Stairs - Active |  |  |  |  | 1.5 | Prototype itself only has one floor. But savings included because NC3 data showed small office buildings with stairs. |  |  |  | 1.5 | [37 empty] | 35 | 0 | 0 | 35 | 0 | 0 |  | 0 | 35 | 0 | 0 | 35 | 0 | 0 |  | 0 | 35 | 0 | 0 | 35 | 0 | 0 |  | 0 | 35 | 0 | 0 | 35 | 0 | 0 |  | 0 | 35 | 0 | 0 | 35 | 0 | 0 |  | 0 | 35 | 0 | 0 | 35 | 0 | 0 |  | 0
|  |  |  | n |  | Small Hotel Stairs - Active | Stairs - Active |  |  |  |  | 8 | Two stairwells, four floors |  |  |  | 8 | [37 empty] | 36 | 0 | 0 | 36 | 0 | 0 |  | 0 | 36 | 0 | 0 | 36 | 0 | 0 |  | 0 | 36 | 0 | 0 | 36 | 0 | 0 |  | 0 | 36 | 0 | 0 | 36 | 0 | 0 |  | 0 | 36 | 0 | 0 | 36 | 0 | 0 |  | 0 | 36 | 0 | 0 | 36 | 0 | 0 |  | 0
[5 empty] | n | Mid-rise Apartment Stairs - Active | Stairs - Active |  |  |  |  | 8 | Stairwells not explicitly modeled but savings were included. Use two stairwells for costs, times four floors. |  |  |  | 8 | [37 empty] | 37 | 0 | 0 | 37 | 0 | 0 |  | 0 | 37 | 0 | 0 | 37 | 0 | 0 |  | 0 | 37 | 0 | 0 | 37 | 0 | 0 |  | 0 | 37 | 0 | 0 | 37 | 0 | 0 |  | 0 | 37 | 0 | 0 | 37 | 0 | 0 |  | 0 | 37 | 0 | 0 | 37 | 0 | 0 |  | 0
[6 empty] | Hotel Guestroom Bathroom Automatic Lighting Shutoff 90.1-2010 section 9.4.1.4 Addenda 90.1-07cf |  | No automatic lighting controls required |  |  |  |  | Automatic lighting controls required in hotel guest rooms |  |  |  | No,. Of Bathrooms | [37 empty] | 38 | 0 | 0 | 38 | 0 | 0 |  | 0 | 38 | 0 | 0 | 38 | 0 | 0 |  | 0 | 38 | 0 | 0 | 38 | 0 | 0 |  | 0 | 38 | 0 | 0 | 38 | 0 | 0 |  | 0 | 38 | 0 | 0 | 38 | 0 | 0 |  | 0 | 38 | 0 | 0 | 38 | 0 | 0 |  | 0
|  |  |  | n |  | Small Hotel Hotel Guestroom, Bathroom | Hotel Guestroom, bathrooms | [5 empty] | number of bathrooms |  |  |  | 78 | [37 empty] | 39 | 0 | 0 | 39 | 0 | 0 |  | 0 | 39 | 0 | 0 | 39 | 0 | 0 |  | 0 | 39 | 0 | 0 | 39 | 0 | 0 |  | 0 | 39 | 0 | 0 | 39 | 0 | 0 |  | 0 | 39 | 0 | 0 | 39 | 0 | 0 |  | 0 | 39 | 0 | 0 | 39 | 0 | 0 |  | 0
[55 empty] | 40 | 0 | 0 | 40 | 0 | 0 |  | 0 | 40 | 0 | 0 | 40 | 0 | 0 |  | 0 | 40 | 0 | 0 | 40 | 0 | 0 |  | 0 | 40 | 0 | 0 | 40 | 0 | 0 |  | 0 | 40 | 0 | 0 | 40 | 0 | 0 |  | 0 | 40 | 0 | 0 | 40 | 0 | 0 |  | 0
[55 empty] | Residual Year 30 |  | 0 | Residual Year 30 |  | 0 |  | 0 | Residual Year 30 |  | 0 | Residual Year 30 |  | 0 |  | 0 | Residual Year 30 |  | 0 | Residual Year 30 |  | 0 |  | 0 | Residual Year 30 |  | 0 | Residual Year 30 |  | 0 |  | 0 | Residual Year 30 |  | 0 | Residual Year 30 |  | 0 |  | 0 | Residual Year 30 |  | 0 | Residual Year 30 |  | 0 |  | 0
[55 empty] | Residual Year 40 |  | 0 | Residual Year 40 |  | 0 |  | 0 | Residual Year 40 |  | 0 | Residual Year 40 |  | 0 |  | 0 | Residual Year 40 |  | 0 | Residual Year 40 |  | 0 |  | 0 | Residual Year 40 |  | 0 | Residual Year 40 |  | 0 |  | 0 | Residual Year 40 |  | 0 | Residual Year 40 |  | 0 |  | 0 | Residual Year 40 |  | 0 | Residual Year 40 |  | 0 |  | 0

## Int Ltg Occ Sensors Comp (hidden)
90.1-2013 Cost Effectiveness - Cost Estimate - Interior Lighting - Occupancy Control Addenda Cost Detail
Occupancy Sensor Cost Items by Addendum and 90.1 Lighting Space Type
90.1-10by | Adds spaces required to have occupancy sensors | [7 empty] | 2010 and 2013 Costs
90.1 Lighting Space Type | Qualifier | Not Used | Space Area for Design and Cost, ft2 | Assumed Dimensions | Occupancy Sensor Control Type | Sensor Equipment Type | Sensor Area Coverage ft2 | Qty of Sensors | Material | Not Used | Total Material Cost/ft2 | Labor Cost | Labor Cost/ft2 | Incremen- tal Commis-sioning Cost | Cost/ft2 | Notes
Classroom/Lecture/Training | Laboratory classroom |  | 1065 | 30 ft. by 35.5 ft. | Manual On/ Auto Off | ceiling mount - infrared | 1250 | 1 | 205.25 |  | 0.19272 | 82.9078 | 0.077848 | 11.5263 | 0.28139 | 30 students, industry standard 30 s.f. per student
Corridor | Other than hospital corridors |  | 600 | 6 ft. by 100 ft. | auto on/off | ceiling mount infrared | 678 | 1 | 127.25 |  | 0.21208 | 76.981 | 0.1283 | 8.1692 | 0.354 | web information
Storage | Larger than 1000 ft2 |  | 1250 | 25 ft. by 50 ft. | manual on/off | ceiling mount infrared | 1250 | 1 | 205.25 |  | 0.1642 | 82.9078 | 0.066326 | 11.5263 | 0.23975
Lobby | Other than in hotels and elevator lobbies |  | 800 | 25 ft. by 40 ft. | auto on/off | ceiling mount infrared and ultrasonic | 800 | 1 | 217.9 |  | 0.27237 | 82.9078 | 0.10363 | 12.0323 | 0.39105
Library Stacks | Stacks area only |  | 800 | 20 ft. by 40 ft. | auto on/off | ceiling mount infrared and ultrasonic | 800 | 1 | 217.9 |  | 0.27237 | 82.9078 | 0.10363 | 12.0323 | 0.39105
90.1-10bc | separate occupancy control for hotel guestroom
Hotel Guestroom | Adder for receptacle control - wiring for 2 switched receptacles per guestroom, 3 x 25 feet per receptacle (Means 2014, 26 05 19.90 0920) |  | 351 |  | Manual On/ Auto Off | wall mount - infrared | 600 | 1 | 75.725 |  | 0.21574 | 71.9275 | 0.20492 | 5.9061 | 0.43749
1. Richman, E.E., E. Rauch, J. Knappek, J. Phillips, K. Petty, and P. Lopez-Rangel. 2008 National Commercial Construction Characteristics and Compliance with Building Energy Codes: 1999-2007. 2008 ACEEE Summer Study on Energy Efficiency in Buildings. ACEEE Publications, Washington D.C.
Occupancy Sensor Costs by Type | [8 empty] | 11 |  | 13 | 14
Sensor Control Type | Sensor Equipment Type |  | Sensor Coverage, ft2 | Material Cost | Source | Label in Source |  | Labor Hours | Labor Cost RS Means 2012 | Not Used | Label in Source
auto on/off | wall mount infrared |  | 900 | 47.3 | Grainger 2014 | 25L182 |  | 0.333 | 22.4276 |  | 2661-13.10-0150
auto on/off | wall mount ultrasonic |  | 400 | 150.5 | Grainger 2014 | 11X349 |  | 0.333 | 22.4276 |  | 2661-13.10-0150
auto on/off | wall mount infrared and ultrasonic |  | 400 | 148.75 | Grainger 2014 | 6FAA1 |  | 0.333 | 22.4276 |  | 2661-13.10-0150
auto on/off | ceiling mount infrared |  | 678 | 127.25 | Grainger 2014 | 12H987, 6LFG0 (sensor + control) |  | 1.143 | 76.981 |  | 2661-13.10-0100
auto on/off | ceiling mount ultrasonic |  | 500 | 201.2 | Grainger 2014 | 4TXU1, 6FJA2 |  | 1.143 | 76.981 |  | 2661-13.10-0110
auto on/off | ceiling mount infrared and ultrasonic |  | 452 | 145.9 | Grainger 2014 | 6DXE6 |  | 1.231 | 82.9078 |  | 2661-13.10-0120
auto on/off | ceiling mount infrared and ultrasonic |  | 800 | 217.9 | Grainger 2014 | 16T959, 4AVK9 (sensor + power pack) |  | 1.231 | 82.9078 |  | 2661-13.10-0120
manual on/off | wall mount infrared |  | 600 | 62.3 | Grainger 2014 | 11X308 |  | 0.333 | 22.4276 |  | 2661-13.10-0150
manual on/off | wall mount infrared |  | 900 | 87.6 | Grainger 2014 | 36N342 |  | 0.333 | 22.4276 |  | 2661-13.10-0150
manual on/off | wall mount ultrasonic |  | 600 | 93.94 | www.westsidewholesale.com | WattStopper CU-250-I |  | 0.333 | 22.4276 |  | 2661-13.10-0150
manual on/off | wall mount infrared and ultrasonic |  | 400 | 190.5 | Grainger 2014 | 6FAA6 |  | 0.333 | 22.4276 |  | 2661-13.10-0150
manual on/off | ceiling mount infrared |  | 1250 | 205.25 | Grainger 2014 | 5PWR5, 6FLG0 (VAC Sensor + Control) |  | 1.231 | 82.9078 |  | 2661-13.10-0100
manual on/off | ceiling mount infrared |  | 678 | 127.25 | Grainger 2014 | 12H988, 6FLG0 |  | 1.231 | 82.9078 |  | 2661-13.10-0100

## Lighting Control Method (hidden)
90.1 Cost Effectiveness Analysis - Lighting Controls Addenda Cost Methodology
Addendum 90.1-10ay expanded the daylighting control requirements introduced in 90.1-2010 by requiring independent control of lights in the secondary sidelighted area, as well as requiring controls to turn general lighting completely off when sufficient daylight is available. The threshold for requiring controls was changed from an area threshold of 250 ft2 to a controlled power threshold of 150 W. This change results in some smaller private offices being included for daylight control in the 2013 models. These changes appear in Section 9.4.1.1 and Table 9.6.1 in 90.1-2013. There are no changes to controls in toplighted areas between 90.1-2010 and 90.1-2013.
Costs for material, labor and commissioning were developed by PNNL from data produced by a daylighting consultant. The cost estimate was based on a switchable wired photocontrol system.
In the Small Office and Large Office prototypes, one photosensor was included per perimeter zone (or per orientation) and per floor. In the Primary School and Small Hotel prototypes, one photosensor is included per space. The same photosensor is used to control both the primary and sidelighted areas, using a controller that can switch the two areas independently. One power pack is required per primary sidelighted area and one per secondary sidelighted area. The primary school multi-classroom pods are divided into separate classrooms based on the corner classroom area.
Labor is calculated based on the number of sensors and the number of fixtures to be wired to the controller. Five minutes installation per fixture was estimated. The number of fixtures in the daylighted areas was determined by using the fixtures per ft2 values developed for the 90.1 analysis as described in "Int Ltg LPD Space Type 90_1 All" worksheet in this workbook. The daylighted areas were multiplied by the quantity of fixtures per ft2 as determined for the interior lighting power allowance cost calculations.
Replacement and commissioning costs are included for both 90.1-2010 and 90.1-2013. Functional testing costs were estimated based on information provided by the daylighting consultant. Replacement costs involve only the cost of the photosensor and power pack; the lighting fixture types were based on fixture selection without daylighting. For new construction, ten minutes of commissioning were estimated for each fixture. The control wiring was not replaced during the study period of the 90.1 cost-effectiveness study. Functional testing, including calibration of photosensors, is a small cost that is included with two hours of installation per photosensor.

## Lighting Controls Proto (hidden)
[12 empty] | 90.1 Cost Effectiveness Analysis - Interior Lighting Egress Controls Cost Estimate | [46 empty] | Daylighting - Summary of Total New Construction, Maintenance, and Replacement Costs By Replacement Year by Prototype
For egress area occupancy sensor control, costs are provided per circuit for equipment and installation, as well as commissioning.
[12 empty] | Item and Addenda / Affected Prototype and Space Type | 90.1-2013 Description |  |  |  |  | 90.1-2016 Description | [5 empty] | 90.1-2019 Costs | [17 empty] | 90.1-2022 Costs | [15 empty] | Incremental Costs | Small Office | [7 empty] | Large Office | [7 empty] | Standalone Retail | [7 empty] | Primary School | [7 empty] | Small Hotel | [7 empty] | Mid-rise Apartment
Prototypes Affected | [5 empty] | Climate Location | [17 empty] | New Construction Costs | [9 empty] | Replacement Costs | [7 empty] | New Construction Costs | [8 empty] | Replacement Costs | [7 empty] | 90.1-2010 |  |  | 90.1-2013 |  |  | Incremental Cost |  | 90.1-2010 |  |  | 90.1-2013 |  |  | Incremental Cost |  | 90.1-2010 |  |  | 90.1-2013 |  |  | Incremental Cost |  | 90.1-2010 |  |  | 90.1-2013 |  |  | Incremental Cost |  | 90.1-2010 |  |  | 90.1-2013 |  |  | Incremental Cost |  | 90.1-2010 |  |  | 90.1-2013 |  |  | Incremental Cost
Small Office | Large Office | Standalone Retail | Primary School | Small Hotel | Mid-rise Apartment | 2A Houston | 3A Memphis | 3B El Paso | 4A Baltimore | 5A Chicago | Details under separate sheet |  | Description |  |  |  |  | Description |  | 4 | 0.5 |  |  | Material | Bare material per unit | Labor hours per unit | Labor | Construc-tion Equipment | Cost Adjustments |  | Incremental Added Commis- sioning | Total Cost | Main- tenance None | Measure Life years | Material | Labor Cost with replacement hour adjustment | Construc- tion Equipment | Cost Adjustments | Incremental Added Commis- sioning Including OH&P | Total Cost |  | Material | Bare material per unit | Labor hours per unit | Labor | Construc-tion Equipment | Cost Adjustments | Incremental Added Commis- sioning | Total Cost | Main- tenance None | Measure Life years | Material | Labor Cost with replacement hour adjustment | Construc- tion Equipment | Cost Adjustments | Incremental Added Commis- sioning Including OH&P | Total Cost | New Construc-tion Costs 2010 minus 2007 | Category | All Costs, First Replacement Only | With Repeated Replacements | Category | Replacement First Year | With Repeated Replacements | 30 Year | 40 Year | Category | All Costs, First Replacement Only | With Repeated Replacements | Category | Replacement First Year | With Repeated Replacements | 30 Year | 40 Year | Category | All Costs, First Replacement Only | With Repeated Replacements | Category | Replacement First Year | With Repeated Replacements | 30 Year | 40 Year | Category | All Costs, First Replacement Only | With Repeated Replacements | Category | Replacement First Year | With Repeated Replacements | 30 Year | 40 Year | Category | All Costs, First Replacement Only | With Repeated Replacements | Category | Replacement First Year | With Repeated Replacements | 30 Year | 40 Year | Category | All Costs, First Replacement Only | With Repeated Replacements | Category | Replacement First Year | With Repeated Replacements | 30 Year | 40 Year
[12 empty] | Daylighting Controls - Base Costs per Fixture and Sensor | Cost description same as 2013 (see to the right) |  |  |  |  | Cost items include sensors and powerpacks, wiring and commissioning. Switchable wired photocontrol systems are assumed. Wiring is CAT5. Cost of the wire is identified to be minimal according to source. | Toplit area ft2 | Quantity of fixtures | Quantity of sensors and controlled banks of lights | [23 empty] | 2 hours per sensor for installation. 5 min/fixture to run CAT5 wires. |  |  | 10 minutes per fixture for commissioning for each ballast |  |  |  |  | 2 hours per sensor for installation. The fixture wiring is assumed to be in place. |  |  | Test control of sensor, 30 minutes per sensor. Ballasts remain in place and don't need additional commissioning. |  |  | Scroll down for summary results! | [7 empty] | Scroll down for summary results! | [7 empty] | Scroll down for summary results! | [7 empty] | Scroll down for summary results! | [7 empty] | Scroll down for summary results!
[18 empty] | Costs per sensor including the cost of the daylight sensor, a powerpack per sensor, and wiring of the sensor. | 1 | 1 | 1 |  |  | 129.8925 | 129.8925 |  | 134.7 |  | 195.1654 |  |  | 589.6504 |  | 15 | 129.8925 | 222.255 |  | 326.967 | 50 | 729.1145 |  | 129.8925 | 129.8925 |  | 134.7 |  | 195.1654 |  | 589.6504 |  | 15 | 129.8925 | 222.255 |  | 326.967 | 50 | 729.1145
[18 empty] | Costs per light fixture include wiring ballasts to sensor control. | 1 | 1 | 1 |  |  | 30 | 30 |  | 5.6125 |  | 20.4576 |  | 16.6667 | 102.7368 | [9 empty] | 30 | 30 |  | 5.6125 |  | 20.4576 | 16.6667 | 102.7368
[12 empty] | Daylighting Controls, Sidelit Areas Addenda 90.1-10ay 90.1-2013 section 9.4.1 | General interior lighting must be separately controlled when the combined primary sidelighted area in an enclosed space equals or exceeds 250 ft2. Additionally, the multi-level photocontrol must be capable of lowering the design lighting power to at least 35%, with one intermediate step between 50% and 70%. Costs include photo sensors, controllers, and wiring to selectively activate and de-activate a subset of lamps to achieve the multi-level control. Costs are shown in this row on a cost/ft2 basis and below are applied to the affected areas. | Sidelit area ft2 | Quantity of fixtures | Quantity of sensors | Quantity of power packs required for secondary sidelighted area | - Addendum 90.1-10ay does not add daylighting control to new spaces in the prototypes below. - Addendum 90.1-10ay does add controls for the secondary sidelighted area. It is assumed that the same sensor can be used with extra commissioning for the fixtures in the secondary sidelighted area. A second power pack is needed for the secondary sidelighted area. - Addendum 90.1-10ay also requires lights to be turned all the way off, but it is assumed that controllers installed in the spaces for the 2010 requirement include the ability to turn the lights off completely. | Sidelit area ft2 | Quantity of fixtures | Quantity of sensors | Quantity of power packs required for secondary sidelighted area
0 | [5 empty] | 0 | 0 | 0 | 0 | 0 |  | Small_Office_Sidelighting_Control | Small office - number of fixtures calculated using table below (based on fixtures/ft2 from LPD calculations) - 1 sensor and controlled bank per orientation | 608 | 17 | 4 | 0 | Small office - number of fixtures calculated using table below (based on fixtures/ft2 from LPD calculations) - 1 sensor and controlled bank per orientation | 1053.89 | 25.4415 | 4 | 4 |  | 519.57 |  |  | 634.2125 |  | 872.7813 |  | 283.9 | 2310.4638 | 0 | 15 | 519.57 | 889.02 |  | 1307.8681 | 200 | 2916.4581 |  | 639.57 |  |  | 681.5904 |  | 978.6792 | 424.873 | 2724.7126 | 0 | 15 | 639.57 | 889.02 |  | 1386.0388 | 200 | 3114.6288 | 414.2488
| 0 |  |  |  |  | 0 | 0 | 0 | 0 | 0 |  | Large_Office_Sidelighting_Control | Large office - number of fixtures calculated using table below (based on fixtures/ft2 from LPD calculations) - 1 sensor per façade (primary) per floor = 1 x 4 x 10 = 40 | 62932 | 1668 | 40 | 0 | Large office - number of fixtures calculated using table below (based on fixtures/ft2 from LPD calculations) - 1 sensor per façade per floor = 1 x 4 x 10 = 40 | 69793 | 1684.8422 | 40 | 40 |  | 5195.7 |  |  | 14749.65 |  | 16845.1771 |  | 27855.6 | 64646.1271 | 0 | 15 | 5195.7 | 8890.2 |  | 13078.6811 | 2000 | 29164.5811 |  | 6395.7 |  |  | 14844.1769 |  | 17537.993 | 28136.865 | 66914.7349 | 0 | 15 | 6395.7 | 8890.2 |  | 13860.3876 | 2000 | 31146.2876 | 2268.6078
|  |  | 0 |  |  | 0 | 0 | 0 | 0 | 0 |  | Primary_School_Sidelighting_Control | Primary School - control applied to selected classrooms, offices, lobby, cafeteria and library - number of fixtures calculated using table below (based on fixtures/ft2 from LPD calculations) - 1 sensor per classroom, lobby, office, café and library | 14952.66 | 379 | 73 | 0 | Primary School - control applied to selected classrooms, offices, lobby, cafeteria and library - number of fixtures calculated using table below (based on fixtures/ft2 from LPD calculations) - 1 sensor per classroom, lobby, office, café and library | 28678.81 | 722 | 73 | 73 |  | 9482.1525 |  |  | 11960.2375 |  | 16300.8006 |  | 6329.3 | 44072.4906 | 0 | 15 | 9482.1525 | 16224.615 |  | 23868.5931 | 3650 | 53225.3606 |  | 11672.1525 |  |  | 13885.325 |  | 19257.2807 | 12057.4 | 56872.1582 | 0 | 15 | 11672.1525 | 16224.615 |  | 25295.2074 | 3650 | 56841.9749 | 12799.6676
|  |  |  | 0 |  | 0 | 0 | 0 | 0 | 0 |  | Small_Hotel_Sidelighting_Control | Small Hotel - control applied to ground floor front lounge only. - number of fixtures calculated using table below (based on fixtures/ft2 from LPD calculations) | 423 | 9 | 1 | 0 | Small Hotel - Four spaces controlled (lounge, meeting room, office, laundry) - number of fixtures calculated using table below (based on fixtures/ft2 from LPD calculations) | 5076 | 65 | 4 | 4 |  | 129.8925 |  |  | 185.2125 |  | 243.9346 |  | 150.3 | 709.3396 | 0 | 15 | 129.8925 | 222.255 |  | 326.967 | 50 | 729.1145 |  | 639.57 |  |  | 903.6125 |  | 1193.0389 | 1085.5 | 3821.7214 | 0 | 15 | 639.57 | 889.02 |  | 1386.0388 | 200 | 3114.6288 | 3112.3817
[12 empty] | Egress Occupancy Sensor Controls - Base Costs per Circuit with 4 Sensors per general egress area | Cost description same as 2013 (see to the right) |  |  |  |  | Cost items include sensors and powerpacks, wiring and commissioning. Switchable wired photocontrol systems are assumed. Wiring is CAT5. Cost of the wire is identified to be minimal according to source. | Egress number of circuits | Quantity of sensors per circuit | LV Wiring per circuit (3-wire), CLF | [26 empty] | 10 minutes per sensor for commissioning |  |  |  |  | 2 hours per sensor for installation. The fixture wiring is assumed to be in place. |  |  | 10 minutes per sensor for commissioning |  |  | Scroll down for summary results! | [7 empty] | Scroll down for summary results! | [7 empty] | Scroll down for summary results! | [7 empty] | Scroll down for summary results! | [7 empty] | Scroll down for summary results!
[18 empty] | Costs per ultrasonic occupancy sensor. |  | 4 |  |  | Sensor | 129.8925 | 129.8925 | 1.143 | 76.981 |  |  |  | 5.75 |  |  | 15 | 129.8925 | [5 empty] | Sensor | 129.8925 | 129.8925 | 1.143 | 76.981 |  |  | 16.6667 | 354.5757 |  | 15 | 129.8925 | 222.255 |  | 326.967 | 50 | 729.1145
[18 empty] | Costs per powerpack and line voltage wiring per circuit. | 1 |  |  |  | Power Pack | 48 | 48 | 0.8 | 53.88 | [6 empty] | 15 | 48 | [5 empty] | Power Pack | 48 | 48 | 0.8 | 53.88 |  |  |  | 150.68 |  | 15 | 48 | 222.255 |  | 273.6204 | 50 | 593.8754
[18 empty] | Costs per low voltage wiring from sensors. |  |  | 2 |  | LV - 3- Wiring | 79 | 39.5 | 1.6 | 107.76 | [13 empty] | LV - 3- Wiring | 39.5 | 39.5 | 1.6 | 107.76 |  |  |  | 188.36
[12 empty] | Added Occupancy Sensor Controls for Egress Areas Addenda 90.1-13 ah 90.1-2016 section 9.4.1.1 | In 90.1-2013, egress controls are explictly exempt, so there are no special occupancy controls required for energy efficiency. Any base controls, fire alarm interconnection, or emergency power sources would be required in both 90.1-2013 and 90.1-2016, so their costs are not included here. | Egress areas | Quantity of sensors | Low voltage sensor wiring | Quantity of power packs required for egress circuits | 90.1-2016 ah requires egress areas to be controlled off when the building is unoccupied. Additional occupancy sensors will be required for the circuits that may have emergency backup power. Costs include occupancy sensors, controllers with relays, and wiring to turn off these lights when spaces are unoccupied. Costs are shown in this row on a cost/circut basis and below are applied to the estimated number of circuited egress areas in each prototype. | Egress areas | Quantity of sensors | Low voltage sensor wiring, CLF | Quantity of power packs required for egress circuits | [33 empty] | Cx per sensor; 10 minutes
0 | [5 empty] | X | X | X | X | X |  | Small_Office_Egress_Control | Small office | 2 | 0 | 0 | 0 | Small office | 2 | 8 | 4 | 2 |  | 0 |  |  | 0 |  | 0 |  | 0 | 0 | 0 | 15 | 0 | 0 |  | 0 | 0 | 0 |  | 1293.14 |  |  | 1154.6484 |  | 1763.0409 | 133.6 | 4344.4293 | 0 | 15 | 1293.14 | 1905.1699 |  | 2919.8229 | 133.6 | 6251.7327 | 4344.4293
| 0 |  |  |  |  | X | X | X | X | X |  | Large_Office_Egress_Control | Large office | 66 | 0 | 0 | 0 | Large office | 66 | 264 | 132 | 66 |  | 0 |  |  | 0 |  | 0 |  | 0 | 0 | 0 | 15 | 0 | 0 |  | 0 | 0 | 0 |  | 42673.62 |  |  | 38103.3972 |  | 58180.3512 | 4408.8 | 143366.1684 | 0 | 15 | 42673.62 | 62870.6054 |  | 96354.1553 | 4408.8 | 206307.1807 | 143366.1684
|  |  | 0 |  |  | X | X | X | X | X |  | Primary_School_Egress_Control | Primary School | 7 | 0 | 0 | 0 | Primary School | 7 | 28 | 14 | 7 |  | 0 |  |  | 0 |  | 0 |  | 0 | 0 | 0 | 15 | 0 | 0 |  | 0 | 0 | 0 |  | 4525.99 |  |  | 4041.2694 |  | 6170.6433 | 467.6 | 15205.5027 | 0 | 15 | 4525.99 | 6668.0945 |  | 10219.3801 | 467.6 | 21881.0646 | 15205.5027
| 0 |  |  |  |  | X | X | X | X | X |  | StandAlone_Retail_Egress_Control | Stand Alone Retail | 6 | 0 | 0 | 0 | Stand Alone Retail | 5 | 20 | 10 | 5 |  | 0 |  |  | 0 |  | 0 |  | 0 | 0 | 0 | 15 | 0 | 0 |  | 0 | 0 | 0 |  | 3232.85 |  |  | 2886.621 |  | 4407.6024 | 334 | 10861.0734 | 0 | 15 | 3232.85 | 4762.9246 |  | 7299.5572 | 334 | 15629.3319 | 10861.0734
Matl
[18 empty] | Lighting controls inflation factor = 1 as prices are from Means 2018 | 1
[19 empty] | 2010 |  |  |  |  | 2013 | [34 empty] | Small Office | [7 empty] | Large Office | [7 empty] | Standalone Retail | [7 empty] | Primary School | [7 empty] | Small Hotel | [7 empty] | Mid-rise Apartment
[19 empty] | Quantity of fixtures/ft2 |  |  |  | Total | Quantity of fixtures/ft2 |  |  |  | Total | 2010 |  | 2013 | [27 empty] | 90.1-2010 |  |  | 90.1-2013 |  |  | Incremental Cost |  | 90.1-2010 |  |  | 90.1-2013 |  |  | Incremental Cost |  | 90.1-2010 |  |  | 90.1-2013 |  |  | Incremental Cost |  | 90.1-2010 |  |  | 90.1-2013 |  |  | Incremental Cost |  | 90.1-2010 |  |  | 90.1-2013 |  |  | Incremental Cost |  | 90.1-2010 |  |  | 90.1-2013 |  |  | Incremental Cost
[18 empty] | Prototype and Space | 1 | 2 | 3 | 4 | Fixtures/ft2 | 1 | 2 | 3 | 4 | Fixtures/ft2 | Area | Number of Fixtures | Area | Number of Fixtures | [26 empty] | Category | All Costs, First Replacement Only | With Repeated Replacements | Category | Replacement First Year | With Repeated Replacements | 30 Year | 40 Year | Category | All Costs, First Replacement Only | With Repeated Replacements | Category | Replacement First Year | With Repeated Replacements | 30 Year | 40 Year | Category | All Costs, First Replacement Only | With Repeated Replacements | Category | Replacement First Year | With Repeated Replacements | 30 Year | 40 Year | Category | All Costs, First Replacement Only | With Repeated Replacements | Category | Replacement First Year | With Repeated Replacements | 30 Year | 40 Year | Category | All Costs, First Replacement Only | With Repeated Replacements | Category | Replacement First Year | With Repeated Replacements | 30 Year | 40 Year | Category | All Costs, First Replacement Only | With Repeated Replacements | Category | Replacement First Year | With Repeated Replacements | 30 Year | 40 Year
[18 empty] | Small Office |  |  |  |  | 0.026496 |  |  |  |  | 0.024141 | [30 empty] | New Construction | 0 | 0 | New Construction | 0 | 0 | 0 | 0 | New Construction | 0 | 0 | New Construction | 0 | 0 | 0 | 0 | New Construction | 0 | 0 | New Construction | 0 | 0 | 0 | 0 | New Construction | 0 | 0 | New Construction | 0 | 0 | 0 | 0 | New Construction | 0 | 0 | New Construction | 0 | 0 | 0 | 0 | New Construction | 0 | 0 | New Construction | 0 | 0 | 0 | 0
[18 empty] | Conference | 0.0070186 | 0.0053309 | 0 | 0.0068987 | 0.019248 | 0.0063947 | 0.004857 | 0 | 0.0062855 | 0.017537 | [30 empty] | Maintenance | 0 | 0 | Maintenance | 0 | 0 | 0 | 0 | Maintenance | 0 | 0 | Maintenance | 0 | 0 | 0 | 0 | Maintenance | 0 | 0 | Maintenance | 0 | 0 | 0 | 0 | Maintenance | 0 | 0 | Maintenance | 0 | 0 | 0 | 0 | Maintenance | 0 | 0 | Maintenance | 0 | 0 | 0 | 0 | Maintenance | 0 | 0 | Maintenance | 0 | 0 | 0 | 0
[18 empty] | Office - enclosed | 0.011403 | 0.010067 | 0 | 0.0063345 | 0.027804 | 0.010389 | 0.0091719 | 0 | 0.0057714 | 0.025333 | [30 empty] | Replacement - Year |  |  | Replacement - Year |  |  | 0 | 0 | Replacement - Year |  |  | Replacement - Year |  |  | 0 | 0 | Replacement - Year |  |  | Replacement - Year |  |  | 0 | 0 | Replacement - Year |  |  | Replacement - Year |  |  | 0 | 0 | Replacement - Year |  |  | Replacement - Year |  |  | 0 | 0 | Replacement - Year |  |  | Replacement - Year |  |  | 0 | 0
[18 empty] | Office - open plan | 0.0069971 | 0.020816 | 0 | 0.0046216 | 0.032435 | 0.0063751 | 0.018966 | 0 | 0.0042108 | 0.029552 | [30 empty] | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 0
[59 empty] | 2 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 0 | 0
[18 empty] | Large Office |  |  |  |  | 0.026496 |  |  |  |  | 0.024141 | [30 empty] | 3 | 0 | 0 | 3 | 0 | 0 | 0 | 0 | 3 | 0 | 0 | 3 | 0 | 0 | 0 | 0 | 3 | 0 | 0 | 3 | 0 | 0 | 0 | 0 | 3 | 0 | 0 | 3 | 0 | 0 | 0 | 0 | 3 | 0 | 0 | 3 | 0 | 0 | 0 | 0 | 3 | 0 | 0 | 3 | 0 | 0 | 0 | 0
[18 empty] | Conference | 0.0070186 | 0.0053309 | 0 | 0.0068987 | 0.019248 | 0.0063947 | 0.004857 | 0 | 0.0062855 | 0.017537 | [30 empty] | 4 | 0 | 0 | 4 | 0 | 0 | 0 | 0 | 4 | 0 | 0 | 4 | 0 | 0 | 0 | 0 | 4 | 0 | 0 | 4 | 0 | 0 | 0 | 0 | 4 | 0 | 0 | 4 | 0 | 0 | 0 | 0 | 4 | 0 | 0 | 4 | 0 | 0 | 0 | 0 | 4 | 0 | 0 | 4 | 0 | 0 | 0 | 0
[18 empty] | Office - enclosed | 0.011403 | 0.010067 | 0 | 0.0063345 | 0.027804 | 0.010389 | 0.0091719 | 0 | 0.0057714 | 0.025333 | [30 empty] | 5 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 5 | 0 | 0 | 0 | 0
[18 empty] | Office - open plan | 0.0069971 | 0.020816 | 0 | 0.0046216 | 0.032435 | 0.0063751 | 0.018966 | 0 | 0.0042108 | 0.029552 | [30 empty] | 6 | 0 | 0 | 6 | 0 | 0 | 0 | 0 | 6 | 0 | 0 | 6 | 0 | 0 | 0 | 0 | 6 | 0 | 0 | 6 | 0 | 0 | 0 | 0 | 6 | 0 | 0 | 6 | 0 | 0 | 0 | 0 | 6 | 0 | 0 | 6 | 0 | 0 | 0 | 0 | 6 | 0 | 0 | 6 | 0 | 0 | 0 | 0
[59 empty] | 7 | 0 | 0 | 7 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 7 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 7 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 7 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 7 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 7 | 0 | 0 | 0 | 0
[18 empty] | Small Hotel | [40 empty] | 8 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 8 | 0 | 0 | 0 | 0
[18 empty] | Lounge | 0.014503 | 0 | 0 | 0.0049154 | 0.019418 | 0.014503 | 0 | 0 | 0.0049154 | 0.019418 | 423 | 9 | 1023.75 | 20 | [26 empty] | 9 | 0 | 0 | 9 | 0 | 0 | 0 | 0 | 9 | 0 | 0 | 9 | 0 | 0 | 0 | 0 | 9 | 0 | 0 | 9 | 0 | 0 | 0 | 0 | 9 | 0 | 0 | 9 | 0 | 0 | 0 | 0 | 9 | 0 | 0 | 9 | 0 | 0 | 0 | 0 | 9 | 0 | 0 | 9 | 0 | 0 | 0 | 0
[18 empty] | Office enclosed | 0.014063 | 0.012416 | 0 | 0.0078125 | 0.034292 | 0.014063 | 0.012416 | 0 | 0.0078125 | 0.034292 | 0 | 0 | 732.375 | 26 | [26 empty] | 10 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 10 | 0 | 0 | 0 | 0
[18 empty] | Laundry | 0.010345 | 0 | 0 | 0 | 0.010345 | 0.010345 | 0 | 0 | 0 | 0.010345 | 0 | 0 | 549.2812 | 6 | [26 empty] | 11 | 0 | 0 | 11 | 0 | 0 | 0 | 0 | 11 | 0 | 0 | 11 | 0 | 0 | 0 | 0 | 11 | 0 | 0 | 11 | 0 | 0 | 0 | 0 | 11 | 0 | 0 | 11 | 0 | 0 | 0 | 0 | 11 | 0 | 0 | 11 | 0 | 0 | 0 | 0 | 11 | 0 | 0 | 11 | 0 | 0 | 0 | 0
[18 empty] | Conference | 0.0095921 | 0.0072855 | 0 | 0.0094282 | 0.026306 | 0.0095921 | 0.0072855 | 0 | 0.0094282 | 0.026306 | 0 | 0 | 484.3125 | 13 | [26 empty] | 12 | 0 | 0 | 12 | 0 | 0 | 0 | 0 | 12 | 0 | 0 | 12 | 0 | 0 | 0 | 0 | 12 | 0 | 0 | 12 | 0 | 0 | 0 | 0 | 12 | 0 | 0 | 12 | 0 | 0 | 0 | 0 | 12 | 0 | 0 | 12 | 0 | 0 | 0 | 0 | 12 | 0 | 0 | 12 | 0 | 0 | 0 | 0
[59 empty] | 13 | 0 | 0 | 13 | 0 | 0 | 0 | 0 | 13 | 0 | 0 | 13 | 0 | 0 | 0 | 0 | 13 | 0 | 0 | 13 | 0 | 0 | 0 | 0 | 13 | 0 | 0 | 13 | 0 | 0 | 0 | 0 | 13 | 0 | 0 | 13 | 0 | 0 | 0 | 0 | 13 | 0 | 0 | 13 | 0 | 0 | 0 | 0
[18 empty] | Primary School | [40 empty] | 14 | 0 | 0 | 14 | 0 | 0 | 0 | 0 | 14 | 0 | 0 | 14 | 0 | 0 | 0 | 0 | 14 | 0 | 0 | 14 | 0 | 0 | 0 | 0 | 14 | 0 | 0 | 14 | 0 | 0 | 0 | 0 | 14 | 0 | 0 | 14 | 0 | 0 | 0 | 0 | 14 | 0 | 0 | 14 | 0 | 0 | 0 | 0
[18 empty] | Classroom | 0.014634 | 0.0051222 | 0 | 0.0050406 | 0.024797 | 0.014634 | 0.0051222 | 0 | 0.0050406 | 0.024797 | 10961.66 | 272 | 21105.81 | 524 | [26 empty] | 15 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 15 | 0 | 0 | 0 | 0
[18 empty] | Computer Classroom | 0.014634 | 0.0051222 | 0 | 0.0050406 | 0.024797 | 0.014634 | 0.0051222 | 0 | 0.0050406 | 0.024797 | 487 | 13 | 973 | 25 | [26 empty] | 16 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 16 | 0 | 0 | 0 | 0
[18 empty] | Lobby | 0.016733 | 0.0078863 | 0 | 0.0053807 | 0.03 | 0.016733 | 0.0078863 | 0 | 0.0053807 | 0.03 | 514 | 16 | 1028 | 31 | [26 empty] | 17 | 0 | 0 | 17 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 17 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 17 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 17 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 17 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 17 | 0 | 0 | 0 | 0
[18 empty] | Offices | 0.014063 | 0.012416 | 0 | 0.0078125 | 0.034292 | 0.014063 | 0.012416 | 0 | 0.0078125 | 0.034292 | 1069 | 37 | 2002 | 69 | [26 empty] | 18 | 0 | 0 | 18 | 0 | 0 | 0 | 0 | 18 | 0 | 0 | 18 | 0 | 0 | 0 | 0 | 18 | 0 | 0 | 18 | 0 | 0 | 0 | 0 | 18 | 0 | 0 | 18 | 0 | 0 | 0 | 0 | 18 | 0 | 0 | 18 | 0 | 0 | 0 | 0 | 18 | 0 | 0 | 18 | 0 | 0 | 0 | 0
[18 empty] | Café | 0.0038082 | 0.0039218 | 0 | 0.0091385 | 0.016868 | 0.0038082 | 0.0039218 | 0 | 0.0091385 | 0.016868 | 906 | 16 | 1677 | 29 | [26 empty] | 19 | 0 | 0 | 19 | 0 | 0 | 0 | 0 | 19 | 0 | 0 | 19 | 0 | 0 | 0 | 0 | 19 | 0 | 0 | 19 | 0 | 0 | 0 | 0 | 19 | 0 | 0 | 19 | 0 | 0 | 0 | 0 | 19 | 0 | 0 | 19 | 0 | 0 | 0 | 0 | 19 | 0 | 0 | 19 | 0 | 0 | 0 | 0
[18 empty] | Library | 0.0062345 | 0.017908 | 0 | 0 | 0.024142 | 0.011429 | 0.011333 | 0 | 0 | 0.022762 | 1015 | 25 | 1893 | 44 | [26 empty] | 20 | 0 | 0 | 20 | 0 | 0 | 0 | 0 | 20 | 0 | 0 | 20 | 0 | 0 | 0 | 0 | 20 | 0 | 0 | 20 | 0 | 0 | 0 | 0 | 20 | 0 | 0 | 20 | 0 | 0 | 0 | 0 | 20 | 0 | 0 | 20 | 0 | 0 | 0 | 0 | 20 | 0 | 0 | 20 | 0 | 0 | 0 | 0
[59 empty] | 21 | 0 | 0 | 21 | 0 | 0 | 0 | 0 | 21 | 0 | 0 | 21 | 0 | 0 | 0 | 0 | 21 | 0 | 0 | 21 | 0 | 0 | 0 | 0 | 21 | 0 | 0 | 21 | 0 | 0 | 0 | 0 | 21 | 0 | 0 | 21 | 0 | 0 | 0 | 0 | 21 | 0 | 0 | 21 | 0 | 0 | 0 | 0
[59 empty] | 22 | 0 | 0 | 22 | 0 | 0 | 0 | 0 | 22 | 0 | 0 | 22 | 0 | 0 | 0 | 0 | 22 | 0 | 0 | 22 | 0 | 0 | 0 | 0 | 22 | 0 | 0 | 22 | 0 | 0 | 0 | 0 | 22 | 0 | 0 | 22 | 0 | 0 | 0 | 0 | 22 | 0 | 0 | 22 | 0 | 0 | 0 | 0
[59 empty] | 23 | 0 | 0 | 23 | 0 | 0 | 0 | 0 | 23 | 0 | 0 | 23 | 0 | 0 | 0 | 0 | 23 | 0 | 0 | 23 | 0 | 0 | 0 | 0 | 23 | 0 | 0 | 23 | 0 | 0 | 0 | 0 | 23 | 0 | 0 | 23 | 0 | 0 | 0 | 0 | 23 | 0 | 0 | 23 | 0 | 0 | 0 | 0
[59 empty] | 24 | 0 | 0 | 24 | 0 | 0 | 0 | 0 | 24 | 0 | 0 | 24 | 0 | 0 | 0 | 0 | 24 | 0 | 0 | 24 | 0 | 0 | 0 | 0 | 24 | 0 | 0 | 24 | 0 | 0 | 0 | 0 | 24 | 0 | 0 | 24 | 0 | 0 | 0 | 0 | 24 | 0 | 0 | 24 | 0 | 0 | 0 | 0
[59 empty] | 25 | 0 | 0 | 25 | 0 | 0 | 0 | 0 | 25 | 0 | 0 | 25 | 0 | 0 | 0 | 0 | 25 | 0 | 0 | 25 | 0 | 0 | 0 | 0 | 25 | 0 | 0 | 25 | 0 | 0 | 0 | 0 | 25 | 0 | 0 | 25 | 0 | 0 | 0 | 0 | 25 | 0 | 0 | 25 | 0 | 0 | 0 | 0
[59 empty] | 26 | 0 | 0 | 26 | 0 | 0 | 0 | 0 | 26 | 0 | 0 | 26 | 0 | 0 | 0 | 0 | 26 | 0 | 0 | 26 | 0 | 0 | 0 | 0 | 26 | 0 | 0 | 26 | 0 | 0 | 0 | 0 | 26 | 0 | 0 | 26 | 0 | 0 | 0 | 0 | 26 | 0 | 0 | 26 | 0 | 0 | 0 | 0
[59 empty] | 27 | 0 | 0 | 27 | 0 | 0 | 0 | 0 | 27 | 0 | 0 | 27 | 0 | 0 | 0 | 0 | 27 | 0 | 0 | 27 | 0 | 0 | 0 | 0 | 27 | 0 | 0 | 27 | 0 | 0 | 0 | 0 | 27 | 0 | 0 | 27 | 0 | 0 | 0 | 0 | 27 | 0 | 0 | 27 | 0 | 0 | 0 | 0
[59 empty] | 28 | 0 | 0 | 28 | 0 | 0 | 0 | 0 | 28 | 0 | 0 | 28 | 0 | 0 | 0 | 0 | 28 | 0 | 0 | 28 | 0 | 0 | 0 | 0 | 28 | 0 | 0 | 28 | 0 | 0 | 0 | 0 | 28 | 0 | 0 | 28 | 0 | 0 | 0 | 0 | 28 | 0 | 0 | 28 | 0 | 0 | 0 | 0
[59 empty] | 29 | 0 | 0 | 29 | 0 | 0 | 0 | 0 | 29 | 0 | 0 | 29 | 0 | 0 | 0 | 0 | 29 | 0 | 0 | 29 | 0 | 0 | 0 | 0 | 29 | 0 | 0 | 29 | 0 | 0 | 0 | 0 | 29 | 0 | 0 | 29 | 0 | 0 | 0 | 0 | 29 | 0 | 0 | 29 | 0 | 0 | 0 | 0
[59 empty] | 30 | 0 | 0 | 30 | 0 | 0 | 0 | 0 | 30 | 0 | 0 | 30 | 0 | 0 | 0 | 0 | 30 | 0 | 0 | 30 | 0 | 0 | 0 | 0 | 30 | 0 | 0 | 30 | 0 | 0 | 0 | 0 | 30 | 0 | 0 | 30 | 0 | 0 | 0 | 0 | 30 | 0 | 0 | 30 | 0 | 0 | 0 | 0
[59 empty] | 31 | 0 | 0 | 31 | 0 | 0 |  | 0 | 31 | 0 | 0 | 31 | 0 | 0 |  | 0 | 31 | 0 | 0 | 31 | 0 | 0 |  | 0 | 31 | 0 | 0 | 31 | 0 | 0 |  | 0 | 31 | 0 | 0 | 31 | 0 | 0 |  | 0 | 31 | 0 | 0 | 31 | 0 | 0 |  | 0
[59 empty] | 32 | 0 | 0 | 32 | 0 | 0 |  | 0 | 32 | 0 | 0 | 32 | 0 | 0 |  | 0 | 32 | 0 | 0 | 32 | 0 | 0 |  | 0 | 32 | 0 | 0 | 32 | 0 | 0 |  | 0 | 32 | 0 | 0 | 32 | 0 | 0 |  | 0 | 32 | 0 | 0 | 32 | 0 | 0 |  | 0
[59 empty] | 33 | 0 | 0 | 33 | 0 | 0 |  | 0 | 33 | 0 | 0 | 33 | 0 | 0 |  | 0 | 33 | 0 | 0 | 33 | 0 | 0 |  | 0 | 33 | 0 | 0 | 33 | 0 | 0 |  | 0 | 33 | 0 | 0 | 33 | 0 | 0 |  | 0 | 33 | 0 | 0 | 33 | 0 | 0 |  | 0
[59 empty] | 34 | 0 | 0 | 34 | 0 | 0 |  | 0 | 34 | 0 | 0 | 34 | 0 | 0 |  | 0 | 34 | 0 | 0 | 34 | 0 | 0 |  | 0 | 34 | 0 | 0 | 34 | 0 | 0 |  | 0 | 34 | 0 | 0 | 34 | 0 | 0 |  | 0 | 34 | 0 | 0 | 34 | 0 | 0 |  | 0
[59 empty] | 35 | 0 | 0 | 35 | 0 | 0 |  | 0 | 35 | 0 | 0 | 35 | 0 | 0 |  | 0 | 35 | 0 | 0 | 35 | 0 | 0 |  | 0 | 35 | 0 | 0 | 35 | 0 | 0 |  | 0 | 35 | 0 | 0 | 35 | 0 | 0 |  | 0 | 35 | 0 | 0 | 35 | 0 | 0 |  | 0
[59 empty] | 36 | 0 | 0 | 36 | 0 | 0 |  | 0 | 36 | 0 | 0 | 36 | 0 | 0 |  | 0 | 36 | 0 | 0 | 36 | 0 | 0 |  | 0 | 36 | 0 | 0 | 36 | 0 | 0 |  | 0 | 36 | 0 | 0 | 36 | 0 | 0 |  | 0 | 36 | 0 | 0 | 36 | 0 | 0 |  | 0
[59 empty] | 37 | 0 | 0 | 37 | 0 | 0 |  | 0 | 37 | 0 | 0 | 37 | 0 | 0 |  | 0 | 37 | 0 | 0 | 37 | 0 | 0 |  | 0 | 37 | 0 | 0 | 37 | 0 | 0 |  | 0 | 37 | 0 | 0 | 37 | 0 | 0 |  | 0 | 37 | 0 | 0 | 37 | 0 | 0 |  | 0
[59 empty] | 38 | 0 | 0 | 38 | 0 | 0 |  | 0 | 38 | 0 | 0 | 38 | 0 | 0 |  | 0 | 38 | 0 | 0 | 38 | 0 | 0 |  | 0 | 38 | 0 | 0 | 38 | 0 | 0 |  | 0 | 38 | 0 | 0 | 38 | 0 | 0 |  | 0 | 38 | 0 | 0 | 38 | 0 | 0 |  | 0
[59 empty] | 39 | 0 | 0 | 39 | 0 | 0 |  | 0 | 39 | 0 | 0 | 39 | 0 | 0 |  | 0 | 39 | 0 | 0 | 39 | 0 | 0 |  | 0 | 39 | 0 | 0 | 39 | 0 | 0 |  | 0 | 39 | 0 | 0 | 39 | 0 | 0 |  | 0 | 39 | 0 | 0 | 39 | 0 | 0 |  | 0
[59 empty] | 40 | 0 | 0 | 40 | 0 | 0 |  | 0 | 40 | 0 | 0 | 40 | 0 | 0 |  | 0 | 40 | 0 | 0 | 40 | 0 | 0 |  | 0 | 40 | 0 | 0 | 40 | 0 | 0 |  | 0 | 40 | 0 | 0 | 40 | 0 | 0 |  | 0 | 40 | 0 | 0 | 40 | 0 | 0 |  | 0
[59 empty] | Residual Year 30 |  | 0 | Residual Year 30 |  | 0 |  | 0 | Residual Year 30 |  | 0 | Residual Year 30 |  | 0 |  | 0 | Residual Year 30 |  | 0 | Residual Year 30 |  | 0 |  | 0 | Residual Year 30 |  | 0 | Residual Year 30 |  | 0 |  | 0 | Residual Year 30 |  | 0 | Residual Year 30 |  | 0 |  | 0 | Residual Year 30 |  | 0 | Residual Year 30 |  | 0 |  | 0
[59 empty] | Residual Year 40 |  | 0 | Residual Year 40 |  | 0 |  | 0 | Residual Year 40 |  | 0 | Residual Year 40 |  | 0 |  | 0 | Residual Year 40 |  | 0 | Residual Year 40 |  | 0 |  | 0 | Residual Year 40 |  | 0 | Residual Year 40 |  | 0 |  | 0 | Residual Year 40 |  | 0 | Residual Year 40 |  | 0 |  | 0 | Residual Year 40 |  | 0 | Residual Year 40 |  | 0 |  | 0

## Ext Ltg Methodology (hidden)
90.1 Cost Effectiveness - Exterior Lighting Cost Estimate Methodology
90.1-2007 section 9.4.3 and Table 9.4.5 require exterior lighting power to fall below a maximum power allowance which is the sum of various allowances by space area plus 5% additional power. 90.1-2010 provides similar exterior lighting requirements in section 9.4.3 and renumbered Table 9.4.3B. However, the allowances are defined for five exterior lighting zones related to the level of development of the surrounding areas of the building. The power allowance values vary in some cases between the zone types.
90.1-2007 section 9.4.1.3 requires controls to turn lights off when sufficient daylight is present or when the lighting is not required during nighttime hours. 90.1-2010 requires the same type of lighting controls as 90.1-2007 but also adds additional lighting control requirements. Exterior facade and landscape lighting is to be automatically turned off between business closing or midnight, whichever is later, and until 6:00 am or business opening, whichever is earlier. Exterior lighting not specified as facade or landscape lighting, including advertising signage, is to be automatically reduced to 30% of its peak power between midnight or within 1 hour of business closing, whichever is later, and until 6:00 am or business opening, whichever is earlier, and during any period activity is not detected for a time longer than 15 minutes.
The exterior lighting power allowances were calculated for the simulation work for each prototype for 90.1-2007 and 90.1-2010. For 90.1-2010 Each prototype was identified with one or two of these lighting zones. Those with two lighting zones were weighted 50% for each zone type. Most of the exterior lighting power for the prototype buildings come from parking, entrances, and facades. The area and quantities of these was defined to calculate the lighting power allowances. This portion of exterior lighting is included in the cost estimate.
Comprehensive lighting models used to develop the exterior lighting power allowances were not available for 90.1-2010 in a form compatible with defining the specific prototype exterior lighting for the cost estimate. Instead, a PNNL lighting expert utilized to lighting power allowance and the parking area, quantity of entrances and façade areas described above to developed sufficient equipment and installation detail for the cost estimate. The quantity of equipment as adjusted from standard lighting equipment developed to just match the maximum power allowance values from the two versions of Standard 90.1.
Costs for fixtures, lamps, ballasts and occupancy sensors were developed by PNNL from the current Grainger catalog and other online sources. Costs for parking lighting poles and electrical conduit in poured concrete were extracted from the RS Means Electrical Cost Data (RS Means 2012b). Replacement costs are estimated for lamps and ballasts and replacement lives are calculated from useful life of the products divided by the exterior lighting hours of operation extracted from the prototype model output reports. Costs for individual components were determined and total costs per prototype were calculated by multiplying the quantity of the components.
Parking
For each site, a lighting power density (LPD) value is provided per code for parking lots in watts per square foot (W/sq. ft). The allowed power density value was multiplied by the area of the site to determine the total allowed power for that application at the site.
Example (Small Office): 0.06 W/sq. ft (Zone 2 90.1-2010) × 8,100 sq. = 486 W
A typical fixture type was selected for the parking lot, with an appropriate type of lamp and ballast. The input power to the ballast was used to calculate the number of fixtures that could be installed within the allowed power values.
Example (Small Office): 100W pulse-start metal halide lamp with input power of 125 W. 3.89 fixtures with this lamp-ballast combination can be installed within the 486 W as calculated in step 1.
The average initial illuminance of the lighting system was calculated by taking the initial lumens of the lamp, multiplying by the fixture efficiency (the amount of light that actually leaves the fixture compared to that generated by the lamp) divided by the area of the parking. This was done to verify the reasonableness of the schematic design, although this is constrained to meet the maximum power allowance.
Example (Small Office): 8,500 lumens × 4 fixtures × 75% efficiency = 25,500 lumens. 25,500 lumens / 8,100 sq. ft = 3.1 footcandles [(fc) lumens / sq. ft]
A mounting height was selected for the fixtures. The mounting height affects the spacing of the fixtures. Because the cost of the pole is usually more expensive than the fixture, the goal in lighting design is to limit the number of poles on a site.
90.1-2010 includes a requirement to turn off lights after 15 minutes of inactivity (in addition to the time of day restriction). One occupancy sensor per pole is included in the costs.
Final costs were determined to circuit (provide power) to the poles and fixtures. Std. 90.1-2007 designs assume that all fixtures turn on and off at the same time. Std. 90.1-2010 designs assume a lighting curfew therefore have two circuits some lights can be extinguished at the designated curve. Sample layouts were created in MS Excel to approximate the amount of conduit needed in the parking lot. RS Means Electrical Cost Data 2012 costs for conduit in slab were used.
Entrances
The number of doors and the lighting power allowances were developed for the prototypes in earlier work as described above.
Door lighting cannot be generalized the same way that parking lot lighting can be. The metrics are different (W / lf and W/ sf, respectively). The height of the door also plays a role. Short doors (3 ft) are going to have a lower header than wide doors (e.g., 12 ft). As the door header height increases, larger light sources are needed. As light source increases (e.g., going from CFL to metal halide) increases the cost of both the fixture and the lamp.
Compact fluorescent lamps (CFLs) were selected as the light source over the doors. It was assumed that the fixtures over the doors were wallpacks/over door lights (a standard fixture for lighting over doors). It was assume one fixture per door and two lamps per fixture. The total power of the light fixture was calculated and then compared to the code allowed power.
The light source for the roll-up doors was assumed to be a metal halide (probe-start for Std. 90.1-2007 and pulse-start for Std. 90.1-2010). These are common lamps used in lighting loading areas.
Example (Small Office): 1 fixture with a 32 W CFL (36 W input power) x 2 lamps = 72 W input power. 72 W (fixture input power) / 90 W (code allowed) = 20% below code. The quantity of fixtures was increased to a fractional amount to account for the maximum allowed power.
All fixtures were assumed to be mounted in roughly the same place and controlled with an astronomical time clock. Therefore, there is no difference in wiring between the Std. 90.1-2007 and Std. 90.1-2010 designs in terms of wiring labor. Astronomical time clocks typically allow manual settings as well and are assumed to be adequate to meet the 90.1-2010 added controls requirements.
Facades
Façade lighting could be lighting an architectural feature, signage, or other elements. The light source, type of light fixture, and controls are going to be affected on the elements being lighted. The costs were developed based a generic façade area and maximum allowed lighting power as determined for the prototypes as described above.
Example (Small Office): A low ballast factor 1-lamp fluorescent fixtures (22.5 / fixture) × 2 fixtures = 45 W. 45 W (designed power value ) / 36 W (allowed power) = 24% over code, yet, the actual power differential is 9 W. The quantity of fixtures was increased to a fractional amount to account for the maximum allowed power.
Costs were determined similarly to the parking from the same sources.

## Ext Lighting Proto (hidden)
State Commercial Energy Code Cost Effectiveness - Exterior Lighting Power Allowance and Controls
[34 empty] | Exterior Lighting Operating Hours | [66 empty] | Exterior Lighting Summary by Prototype of Total New Construction, Maintenance, and Replacement Costs By Replacement Year
[19 empty] | Addendum 90.1-07i changes the exterior lighting power allowances in Tables 9.4.3B (9.4.3 in 90.1-2007). The addendum also introduces exterior lighting zone type in Table 9.4.3A, described in the methodology. One or more of zone types 2, 3 and 4 apply to the prototypes. Addendum 90.1-07cd adds exterior lighting control requirements in section 9.4.1.3. Exterior Façade and landscape lighting are turned off between business closing or midnight, whichever is later, and until 6 am or business opening, whichever is earlier. Other exterior lighting is reduced to 30% in the same time period or when no activity for more than 15 minutes. Exterior lighting operating hours per year are shown to the right and reflect addition of controls. | [14 empty] | 2013, all lights | 4365 | 4365
[34 empty] | 2016, façade lights | 2175 | 2175
[34 empty] | 2016, other lights | 2832 | 2832
[19 empty] | Base Code Description |  | 2019 | [16 empty] | Target Code Description | 2022 | [16 empty] | Base Code Costs | [20 empty] | 90.1-2016 - costs with addendum | Target Code costs | [22 empty] | Small Office | [7 empty] | Large Office | [7 empty] | Standalone Retail | [7 empty] | Primary School | [7 empty] | Small Hotel | [7 empty] | Mid-rise Apartment
| Related 90.1-13 Addenda and 90.1-2016 Sections |  |  |  | Prototypes Affected | [5 empty] | Climate Location | [5 empty] | Name of Item | [38 empty] | New Construction Costs | [8 empty] | Maintenance Cost | Replacement Costs (Lamps above; ballasts or drivers on line below) | [10 empty] | New Construction Costs | New Construction Costs | [8 empty] | Maintenance | Replacement Costs (Lamps above; ballasts or drivers on line below) | [10 empty] | Incremental Costs 2016 minus 2013 |  | 90.1-2019 |  |  | 90.1-2022 |  |  | Incremental Cost |  | 90.1-2019 |  |  | 90.1-2022 |  |  | Incremental Cost |  | 90.1-2019 |  |  | 90.1-2022 |  |  | Incremental Cost |  | 90.1-2019 |  |  | 90.1-2022 |  |  | Incremental Cost |  | 90.1-2019 |  |  | 90.1-2022 |  |  | Incremental Cost |  | 90.1-2019 |  |  | 90.1-2022 |  |  | Incremental Cost
| 90.1 Addenda | 90.1-2013 Chapter(s) Affected | 90.1-2016 Section(s) affected | Affected Items | Small Office | Large Office | Standalone Retail | Primary School | Small Hotel | Mid-rise Apartment | 2A Houston | 3A Memphis | 3B El Paso | 4A Baltimore | 5A Chicago | Not Used | Interior Lighting Power Density | Not Used | Costs to provide exterior lighting fixtures, lamps and ballasts, and parking poles and conduit and slab to meet the exterior lighting maximum power allowed under 90.1-2007 Table 9.4.3. Costs by prototype and area of the building. Parking doors and Façade lighting only are included in the prototypes. Only exterior with different power allowance between 2007 and 2010 are included. In some exterior lighting zones (in 2010) the allowances are the same as for 2007. For IECC, 2009 and 2012 costs are the same, so for this comparison, costs are set to zero. | Exterior Lighting Zone | Code Unit and Value for Power Allowance, e.g. area, ft2 | Base Site Allowance | Allocation of Base Site Allowance | Base Watts | Allowed W/ft2 or W/lf | Allowed Power W | Fixture Type | Input Power per Fixture W | Fixture Quantity | Lamps Per Fixture | Lamp Or Ballast Life | Pole Quantity | Length of Poles | Conduit in Slab ft |  | Cost Weighting Factor for Zones | Not Used | Costs to provide exterior lighting fixtures, lamps and ballasts, and parking poles and conduit and slab to meet the exterior lighting maximum power allowed under 90.1-2010 Table 9.4.3B. Costs by an area of the building. Parking doors and Façade lighting only are included in the prototypes. Only exterior lighting with different power allowance between 2007 and 2010 are included. In some exterior lighting zones (in 2010) the allowances are the same as for 2007. Control requirement costs for parking are reflected in additional in slab conduit for circuiting of lights and use of the same type of timeclock as in the 90.1-2007 case. Controls for façade is assumed to be provided by same time clock as in the 90.1-2007 case. | Exterior Lighting Zone | Code Unit and Value for Power Allowance, e.g. area, ft2 | Base Site Allowance | Allocation of Base Site Allowance | Base Watts | Allowed Power W/ft2 | Allowed Power W | Fixture Type | Input Power per Fixture W | Fixture Quantity | Lamps Per Fixture | Lamp or Ballast Life | Pole Quantity | Length of Poles | Conduit in Slab, ft | Cost Weighting Factor for Zones | Material Cost/ft2 | Material Subtotal | Labor Crew Type Not Used | Labor Hours/ft2 | Labor Subtotal | Construction Equipment Subtotal | Cost Adjustments | Not Used | Not Used | Total | Annual Main-tenance None | Replacement Life (years) | Material Cost/ft2 | Material Subtotal | Labor Crew Type Not Used | Labor Hours/ft2 | Labor Subtotal | Construction Equipment Subtotal | Cost Adjustments | Not Used | Not Used | Total | Material Cost/ft2 | Material Subtotal | Labor Crew Type Not Used | Labor Hours/ft2 | Labor Subtotal | Construction Equipment Subtotal | Cost Adjustments | Incremental Added Design with OH&P | Incremental Added Commis- sioning with OH&P | Total | Annual Maintenance Cost None | Replacement Life (years) | Material Cost/ft2 | Material Subtotal | Labor Crew Type Not Used | Labor Hours/ft2 | Labor Subtotal | Construction Equipment Subtotal | Cost Adjustments | Incremental Added Design with OH&P | Incremental Added Commis- sioning with OH&P | Total | New Construction Costs | Replacement Costs (may have different frequency) | Category | All Costs, First Replacement Only | With Repeated Replacements | Category | Replacement First Year | With Repeated Replacements | 30 Year | 40 Year | Category | All Costs, First Replacement Only | With Repeated Replacements | Category | Replacement First Year | With Repeated Replacements | 30 Year | 40 Year | Category | All Costs, First Replacement Only | With Repeated Replacements | Category | Replacement First Year | With Repeated Replacements | 30 Year | 40 Year | Category | All Costs, First Replacement Only | With Repeated Replacements | Category | Replacement First Year | With Repeated Replacements | 30 Year | 40 Year | Category | All Costs, First Replacement Only | With Repeated Replacements | Category | Replacement First Year | With Repeated Replacements | 30 Year | 40 Year | Category | All Costs, First Replacement Only | With Repeated Replacements | Category | Replacement First Year | With Repeated Replacements | 30 Year | 40 Year
[101 empty] | New Construction | 0 | 0 | New Construction | 0 | 0 | 0 | 0 | New Construction | 0 | 0 | New Construction | 0 | 0 | 0 | 0 | New Construction | 0 | 0 | New Construction | 0 | 0 | 0 | 0 | New Construction | 0 | 0 | New Construction | 0 | 0 | 0 | 0 | New Construction | 0 | 0 | New Construction | 0 | 0 | 0 | 0 | New Construction | 0 | 0 | New Construction | 0 | 0 | 0 | 0
[101 empty] | Maintenance | 0 | 0 | Maintenance | 0 | 0 | 0 | 0 | Maintenance | 0 | 0 | Maintenance | 0 | 0 | 0 | 0 | Maintenance | 0 | 0 | Maintenance | 0 | 0 | 0 | 0 | Maintenance | 0 | 0 | Maintenance | 0 | 0 | 0 | 0 | Maintenance | 0 | 0 | Maintenance | 0 | 0 | 0 | 0 | Maintenance | 0 | 0 | Maintenance | 0 | 0 | 0 | 0
[5 empty] | Scroll down to row 65 for space by space analysis; scroll right for 40 year cost tabulations by building type | [15 empty] | Scroll down to row 65 for space by space analysis; scroll right for 40 year cost tabulations by building type | [16 empty] | Scroll down to row 65 for space by space analysis; scroll right for 40 year cost tabulations by building type | [17 empty] | Scroll down to row 65 for space by space analysis; scroll right for 40 year cost tabulations by building type | [12 empty] | Scroll down to row 65 for space by space analysis; scroll right for 40 year cost tabulations by building type | [15 empty] | Scroll down to row 65 for space by space analysis; scroll right for 40 year cost tabulations by building type | [6 empty] | Scroll down to row 65 for space by space analysis; scroll right for 40 year cost tabulations by building type
[101 empty] | Replacement - Year |  |  | Replacement - Year |  |  | 0 | 0 | Replacement - Year |  |  | Replacement - Year |  |  | 0 | 0 | Replacement - Year |  |  | Replacement - Year |  |  | 0 | 0 | Replacement - Year |  |  | Replacement - Year |  |  | 0 | 0 | Replacement - Year |  |  | Replacement - Year |  |  | 0 | 0 | Replacement - Year |  |  | Replacement - Year |  |  | 0 | 0
[101 empty] | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 0
[101 empty] | 2 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 0 | 0
[101 empty] | 3 | 0 | 0 | 3 | 0 | 0 | 0 | 0 | 3 | 0 | 0 | 3 | 0 | 0 | 0 | 0 | 3 | 0 | 0 | 3 | 0 | 0 | 0 | 0 | 3 | 0 | 0 | 3 | 0 | 0 | 0 | 0 | 3 | 0 | 0 | 3 | 0 | 0 | 0 | 0 | 3 | 0 | 0 | 3 | 0 | 0 | 0 | 0
[101 empty] | 4 | 0 | 0 | 4 | 0 | 0 | 0 | 0 | 4 | 0 | 0 | 4 | 0 | 0 | 0 | 0 | 4 | 0 | 0 | 4 | 0 | 0 | 0 | 0 | 4 | 0 | 0 | 4 | 0 | 0 | 0 | 0 | 4 | 0 | 0 | 4 | 0 | 0 | 0 | 0 | 4 | 0 | 0 | 4 | 0 | 0 | 0 | 0
[101 empty] | 5 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 5 | 0 | 0 | 0 | 0
[101 empty] | 6 | 0 | 0 | 6 | 0 | 0 | 0 | 0 | 6 | 0 | 0 | 6 | 0 | 0 | 0 | 0 | 6 | 0 | 0 | 6 | 0 | 0 | 0 | 0 | 6 | 0 | 0 | 6 | 0 | 0 | 0 | 0 | 6 | 0 | 0 | 6 | 0 | 0 | 0 | 0 | 6 | 0 | 0 | 6 | 0 | 0 | 0 | 0
[101 empty] | 7 | 0 | 0 | 7 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 7 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 7 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 7 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 7 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 7 | 0 | 0 | 0 | 0
[101 empty] | 8 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 8 | 0 | 0 | 0 | 0
[101 empty] | 9 | 0 | 0 | 9 | 0 | 0 | 0 | 0 | 9 | 0 | 0 | 9 | 0 | 0 | 0 | 0 | 9 | 0 | 0 | 9 | 0 | 0 | 0 | 0 | 9 | 0 | 0 | 9 | 0 | 0 | 0 | 0 | 9 | 0 | 0 | 9 | 0 | 0 | 0 | 0 | 9 | 0 | 0 | 9 | 0 | 0 | 0 | 0
[101 empty] | 10 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 10 | 0 | 0 | 0 | 0
[101 empty] | 11 | 0 | 0 | 11 | 0 | 0 | 0 | 0 | 11 | 0 | 0 | 11 | 0 | 0 | 0 | 0 | 11 | 0 | 0 | 11 | 0 | 0 | 0 | 0 | 11 | 0 | 0 | 11 | 0 | 0 | 0 | 0 | 11 | 0 | 0 | 11 | 0 | 0 | 0 | 0 | 11 | 0 | 0 | 11 | 0 | 0 | 0 | 0
[101 empty] | 12 | 0 | 0 | 12 | 0 | 0 | 0 | 0 | 12 | 0 | 0 | 12 | 0 | 0 | 0 | 0 | 12 | 0 | 0 | 12 | 0 | 0 | 0 | 0 | 12 | 0 | 0 | 12 | 0 | 0 | 0 | 0 | 12 | 0 | 0 | 12 | 0 | 0 | 0 | 0 | 12 | 0 | 0 | 12 | 0 | 0 | 0 | 0
[101 empty] | 13 | 0 | 0 | 13 | 0 | 0 | 0 | 0 | 13 | 0 | 0 | 13 | 0 | 0 | 0 | 0 | 13 | 0 | 0 | 13 | 0 | 0 | 0 | 0 | 13 | 0 | 0 | 13 | 0 | 0 | 0 | 0 | 13 | 0 | 0 | 13 | 0 | 0 | 0 | 0 | 13 | 0 | 0 | 13 | 0 | 0 | 0 | 0
[101 empty] | 14 | 0 | 0 | 14 | 0 | 0 | 0 | 0 | 14 | 0 | 0 | 14 | 0 | 0 | 0 | 0 | 14 | 0 | 0 | 14 | 0 | 0 | 0 | 0 | 14 | 0 | 0 | 14 | 0 | 0 | 0 | 0 | 14 | 0 | 0 | 14 | 0 | 0 | 0 | 0 | 14 | 0 | 0 | 14 | 0 | 0 | 0 | 0
[5 empty] | Scroll down to row 65 for space by space analysis; scroll right for 40 year cost tabulations by building type | [15 empty] | Scroll down to row 65 for space by space analysis; scroll right for 40 year cost tabulations by building type | [16 empty] | Scroll down to row 65 for space by space analysis; scroll right for 40 year cost tabulations by building type | [17 empty] | Scroll down to row 65 for space by space analysis; scroll right for 40 year cost tabulations by building type | [12 empty] | Scroll down to row 65 for space by space analysis; scroll right for 40 year cost tabulations by building type | [15 empty] | Scroll down to row 65 for space by space analysis; scroll right for 40 year cost tabulations by building type | [6 empty] | Scroll down to row 65 for space by space analysis; scroll right for 40 year cost tabulations by building type | [8 empty] | 15 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 15 | 0 | 0 | 0 | 0
[101 empty] | 16 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 16 | 0 | 0 | 0 | 0
[101 empty] | 17 | 0 | 0 | 17 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 17 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 17 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 17 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 17 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 17 | 0 | 0 | 0 | 0
[101 empty] | 18 | 0 | 0 | 18 | 0 | 0 | 0 | 0 | 18 | 0 | 0 | 18 | 0 | 0 | 0 | 0 | 18 | 0 | 0 | 18 | 0 | 0 | 0 | 0 | 18 | 0 | 0 | 18 | 0 | 0 | 0 | 0 | 18 | 0 | 0 | 18 | 0 | 0 | 0 | 0 | 18 | 0 | 0 | 18 | 0 | 0 | 0 | 0
[101 empty] | 19 | 0 | 0 | 19 | 0 | 0 | 0 | 0 | 19 | 0 | 0 | 19 | 0 | 0 | 0 | 0 | 19 | 0 | 0 | 19 | 0 | 0 | 0 | 0 | 19 | 0 | 0 | 19 | 0 | 0 | 0 | 0 | 19 | 0 | 0 | 19 | 0 | 0 | 0 | 0 | 19 | 0 | 0 | 19 | 0 | 0 | 0 | 0
[101 empty] | 20 | 0 | 0 | 20 | 0 | 0 | 0 | 0 | 20 | 0 | 0 | 20 | 0 | 0 | 0 | 0 | 20 | 0 | 0 | 20 | 0 | 0 | 0 | 0 | 20 | 0 | 0 | 20 | 0 | 0 | 0 | 0 | 20 | 0 | 0 | 20 | 0 | 0 | 0 | 0 | 20 | 0 | 0 | 20 | 0 | 0 | 0 | 0
[101 empty] | 21 | 0 | 0 | 21 | 0 | 0 | 0 | 0 | 21 | 0 | 0 | 21 | 0 | 0 | 0 | 0 | 21 | 0 | 0 | 21 | 0 | 0 | 0 | 0 | 21 | 0 | 0 | 21 | 0 | 0 | 0 | 0 | 21 | 0 | 0 | 21 | 0 | 0 | 0 | 0 | 21 | 0 | 0 | 21 | 0 | 0 | 0 | 0
[101 empty] | 22 | 0 | 0 | 22 | 0 | 0 | 0 | 0 | 22 | 0 | 0 | 22 | 0 | 0 | 0 | 0 | 22 | 0 | 0 | 22 | 0 | 0 | 0 | 0 | 22 | 0 | 0 | 22 | 0 | 0 | 0 | 0 | 22 | 0 | 0 | 22 | 0 | 0 | 0 | 0 | 22 | 0 | 0 | 22 | 0 | 0 | 0 | 0
[101 empty] | 23 | 0 | 0 | 23 | 0 | 0 | 0 | 0 | 23 | 0 | 0 | 23 | 0 | 0 | 0 | 0 | 23 | 0 | 0 | 23 | 0 | 0 | 0 | 0 | 23 | 0 | 0 | 23 | 0 | 0 | 0 | 0 | 23 | 0 | 0 | 23 | 0 | 0 | 0 | 0 | 23 | 0 | 0 | 23 | 0 | 0 | 0 | 0
[101 empty] | 24 | 0 | 0 | 24 | 0 | 0 | 0 | 0 | 24 | 0 | 0 | 24 | 0 | 0 | 0 | 0 | 24 | 0 | 0 | 24 | 0 | 0 | 0 | 0 | 24 | 0 | 0 | 24 | 0 | 0 | 0 | 0 | 24 | 0 | 0 | 24 | 0 | 0 | 0 | 0 | 24 | 0 | 0 | 24 | 0 | 0 | 0 | 0
[101 empty] | 25 | 0 | 0 | 25 | 0 | 0 | 0 | 0 | 25 | 0 | 0 | 25 | 0 | 0 | 0 | 0 | 25 | 0 | 0 | 25 | 0 | 0 | 0 | 0 | 25 | 0 | 0 | 25 | 0 | 0 | 0 | 0 | 25 | 0 | 0 | 25 | 0 | 0 | 0 | 0 | 25 | 0 | 0 | 25 | 0 | 0 | 0 | 0
[101 empty] | 26 | 0 | 0 | 26 | 0 | 0 | 0 | 0 | 26 | 0 | 0 | 26 | 0 | 0 | 0 | 0 | 26 | 0 | 0 | 26 | 0 | 0 | 0 | 0 | 26 | 0 | 0 | 26 | 0 | 0 | 0 | 0 | 26 | 0 | 0 | 26 | 0 | 0 | 0 | 0 | 26 | 0 | 0 | 26 | 0 | 0 | 0 | 0
[101 empty] | 27 | 0 | 0 | 27 | 0 | 0 | 0 | 0 | 27 | 0 | 0 | 27 | 0 | 0 | 0 | 0 | 27 | 0 | 0 | 27 | 0 | 0 | 0 | 0 | 27 | 0 | 0 | 27 | 0 | 0 | 0 | 0 | 27 | 0 | 0 | 27 | 0 | 0 | 0 | 0 | 27 | 0 | 0 | 27 | 0 | 0 | 0 | 0
[101 empty] | 28 | 0 | 0 | 28 | 0 | 0 | 0 | 0 | 28 | 0 | 0 | 28 | 0 | 0 | 0 | 0 | 28 | 0 | 0 | 28 | 0 | 0 | 0 | 0 | 28 | 0 | 0 | 28 | 0 | 0 | 0 | 0 | 28 | 0 | 0 | 28 | 0 | 0 | 0 | 0 | 28 | 0 | 0 | 28 | 0 | 0 | 0 | 0
[101 empty] | 29 | 0 | 0 | 29 | 0 | 0 | 0 | 0 | 29 | 0 | 0 | 29 | 0 | 0 | 0 | 0 | 29 | 0 | 0 | 29 | 0 | 0 | 0 | 0 | 29 | 0 | 0 | 29 | 0 | 0 | 0 | 0 | 29 | 0 | 0 | 29 | 0 | 0 | 0 | 0 | 29 | 0 | 0 | 29 | 0 | 0 | 0 | 0
[101 empty] | 30 | 0 | 0 | 30 | 0 | 0 | 0 | 0 | 30 | 0 | 0 | 30 | 0 | 0 | 0 | 0 | 30 | 0 | 0 | 30 | 0 | 0 | 0 | 0 | 30 | 0 | 0 | 30 | 0 | 0 | 0 | 0 | 30 | 0 | 0 | 30 | 0 | 0 | 0 | 0 | 30 | 0 | 0 | 30 | 0 | 0 | 0 | 0
[101 empty] | 31 | 0 | 0 | 31 | 0 | 0 |  | 0 | 31 | 0 | 0 | 31 | 0 | 0 |  | 0 | 31 | 0 | 0 | 31 | 0 | 0 |  | 0 | 31 | 0 | 0 | 31 | 0 | 0 |  | 0 | 31 | 0 | 0 | 31 | 0 | 0 |  | 0 | 31 | 0 | 0 | 31 | 0 | 0 |  | 0
[101 empty] | 32 | 0 | 0 | 32 | 0 | 0 |  | 0 | 32 | 0 | 0 | 32 | 0 | 0 |  | 0 | 32 | 0 | 0 | 32 | 0 | 0 |  | 0 | 32 | 0 | 0 | 32 | 0 | 0 |  | 0 | 32 | 0 | 0 | 32 | 0 | 0 |  | 0 | 32 | 0 | 0 | 32 | 0 | 0 |  | 0
[5 empty] | Scroll down to row 65 for space by space analysis; scroll right for 40 year cost tabulations by building type | [15 empty] | Scroll down to row 65 for space by space analysis; scroll right for 40 year cost tabulations by building type | [16 empty] | Scroll down to row 65 for space by space analysis; scroll right for 40 year cost tabulations by building type | [17 empty] | Scroll down to row 65 for space by space analysis; scroll right for 40 year cost tabulations by building type | [12 empty] | Scroll down to row 65 for space by space analysis; scroll right for 40 year cost tabulations by building type | [15 empty] | Scroll down to row 65 for space by space analysis; scroll right for 40 year cost tabulations by building type | [6 empty] | Scroll down to row 65 for space by space analysis; scroll right for 40 year cost tabulations by building type | [8 empty] | 33 | 0 | 0 | 33 | 0 | 0 |  | 0 | 33 | 0 | 0 | 33 | 0 | 0 |  | 0 | 33 | 0 | 0 | 33 | 0 | 0 |  | 0 | 33 | 0 | 0 | 33 | 0 | 0 |  | 0 | 33 | 0 | 0 | 33 | 0 | 0 |  | 0 | 33 | 0 | 0 | 33 | 0 | 0 |  | 0
[101 empty] | 34 | 0 | 0 | 34 | 0 | 0 |  | 0 | 34 | 0 | 0 | 34 | 0 | 0 |  | 0 | 34 | 0 | 0 | 34 | 0 | 0 |  | 0 | 34 | 0 | 0 | 34 | 0 | 0 |  | 0 | 34 | 0 | 0 | 34 | 0 | 0 |  | 0 | 34 | 0 | 0 | 34 | 0 | 0 |  | 0
[101 empty] | 35 | 0 | 0 | 35 | 0 | 0 |  | 0 | 35 | 0 | 0 | 35 | 0 | 0 |  | 0 | 35 | 0 | 0 | 35 | 0 | 0 |  | 0 | 35 | 0 | 0 | 35 | 0 | 0 |  | 0 | 35 | 0 | 0 | 35 | 0 | 0 |  | 0 | 35 | 0 | 0 | 35 | 0 | 0 |  | 0
[101 empty] | 36 | 0 | 0 | 36 | 0 | 0 |  | 0 | 36 | 0 | 0 | 36 | 0 | 0 |  | 0 | 36 | 0 | 0 | 36 | 0 | 0 |  | 0 | 36 | 0 | 0 | 36 | 0 | 0 |  | 0 | 36 | 0 | 0 | 36 | 0 | 0 |  | 0 | 36 | 0 | 0 | 36 | 0 | 0 |  | 0
[101 empty] | 37 | 0 | 0 | 37 | 0 | 0 |  | 0 | 37 | 0 | 0 | 37 | 0 | 0 |  | 0 | 37 | 0 | 0 | 37 | 0 | 0 |  | 0 | 37 | 0 | 0 | 37 | 0 | 0 |  | 0 | 37 | 0 | 0 | 37 | 0 | 0 |  | 0 | 37 | 0 | 0 | 37 | 0 | 0 |  | 0
[101 empty] | 38 | 0 | 0 | 38 | 0 | 0 |  | 0 | 38 | 0 | 0 | 38 | 0 | 0 |  | 0 | 38 | 0 | 0 | 38 | 0 | 0 |  | 0 | 38 | 0 | 0 | 38 | 0 | 0 |  | 0 | 38 | 0 | 0 | 38 | 0 | 0 |  | 0 | 38 | 0 | 0 | 38 | 0 | 0 |  | 0
[101 empty] | 39 | 0 | 0 | 39 | 0 | 0 |  | 0 | 39 | 0 | 0 | 39 | 0 | 0 |  | 0 | 39 | 0 | 0 | 39 | 0 | 0 |  | 0 | 39 | 0 | 0 | 39 | 0 | 0 |  | 0 | 39 | 0 | 0 | 39 | 0 | 0 |  | 0 | 39 | 0 | 0 | 39 | 0 | 0 |  | 0
[101 empty] | 40 | 0 | 0 | 40 | 0 | 0 |  | 0 | 40 | 0 | 0 | 40 | 0 | 0 |  | 0 | 40 | 0 | 0 | 40 | 0 | 0 |  | 0 | 40 | 0 | 0 | 40 | 0 | 0 |  | 0 | 40 | 0 | 0 | 40 | 0 | 0 |  | 0 | 40 | 0 | 0 | 40 | 0 | 0 |  | 0
[101 empty] | Residual Year 30 |  | 0 | Residual Year 30 |  | 0 |  | 0 | Residual Year 30 |  | 0 | Residual Year 30 |  | 0 |  | 0 | Residual Year 30 |  | 0 | Residual Year 30 |  | 0 |  | 0 | Residual Year 30 |  | 0 | Residual Year 30 |  | 0 |  | 0 | Residual Year 30 |  | 0 | Residual Year 30 |  | 0 |  | 0 | Residual Year 30 |  | 0 | Residual Year 30 |  | 0 |  | 0
[101 empty] | Residual Year 40 |  | 0 | Residual Year 40 |  | 0 |  | 0 | Residual Year 40 |  | 0 | Residual Year 40 |  | 0 |  | 0 | Residual Year 40 |  | 0 | Residual Year 40 |  | 0 |  | 0 | Residual Year 40 |  | 0 | Residual Year 40 |  | 0 |  | 0 | Residual Year 40 |  | 0 | Residual Year 40 |  | 0 |  | 0 | Residual Year 40 |  | 0 | Residual Year 40 |  | 0 |  | 0
[19 empty] | Base Code Description |  | 2019 | [16 empty] | Target Code Description | 2022 | [16 empty] | Base Code Costs | [20 empty] | 90.1-2016 - costs with addendum | Target Code costs
| Related 90.1-13 Addenda and 90.1-2016 Sections |  |  |  | Prototypes Affected | [5 empty] | Climate Location | [5 empty] | Name of Item | [38 empty] | New Construction Costs | [8 empty] | Maintenance Cost | Replacement Costs | [10 empty] | New Construction Costs | New Construction Costs | [8 empty] | Maintenance | Replacement Costs | [10 empty] | Incremental Costs 2016 minus 2013
| 90.1 Addenda | 90.1-2013 Chapter(s) Affected | 90.1-2016 Section(s) affected | Affected Items | Small Office | Large Office | Standalone Retail | Primary School | Small Hotel | Mid-rise Apartment | 2A Houston | 3A Memphis | 3B El Paso | 4A Baltimore | 5A Chicago | Not Used | Interior Lighting Power Density | Not Used | Costs to provide exterior lighting fixtures, lamps and ballasts, and parking poles and conduit and slab to meet the exterior lighting maximum power allowed under 90.1-2007 Table 9.4.3. Costs by prototype and area of the building. Parking doors and Façade lighting only are included in the prototypes. Only exterior with different power allowance between 2007 and 2010 are included. In some exterior lighting zones (in 2010) the allowances are the same as for 2007. For IECC, 2009 and 2012 costs are the same, so for this comparison, costs are set to zero. | Exterior Lighting Zone | Code Unit and Value for Power Allowance, e.g. area, ft2 | Base Site Allowance | Allocation of Base Site Allowance | Base Watts | Allowed W/ft2 or W/lf | Allowed Power W | Fixture Type | Input Power per Fixture W | Fixture Quantity | Lamps Per Fixture | Lamp Or Ballast Life | Pole Quantity | Length of Poles | Conduit in Slab ft |  | Cost Weighting Factor for Zones | Not Used | Costs to provide exterior lighting fixtures, lamps and ballasts, and parking poles and conduit and slab to meet the exterior lighting maximum power allowed under 90.1-2010 Table 9.4.3B. Costs by an area of the building. Parking doors and Façade lighting only are included in the prototypes. Only exterior lighting with different power allowance between 2007 and 2010 are included. In some exterior lighting zones (in 2010) the allowances are the same as for 2007. Control requirement costs for parking are reflected in additional in slab conduit for circuiting of lights and use of the same type of timeclock as in the 90.1-2007 case. Controls for façade is assumed to be provided by same time clock as in the 90.1-2007 case. | Exterior Lighting Zone | Code Unit and Value for Power Allowance, e.g. area, ft2 | Base Site Allowance | Allocation of Base Site Allowance | Base Watts | Allowed Power W/ft2 | Allowed Power W | Fixture Type | Input Power per Fixture W | Fixture Quantity | Lamps Per Fixture | Lamp or Ballast Life | Pole Quantity | Length of Poles | Conduit in Slab, ft | Cost Weighting Factor for Zones | Material Cost/ft2 | Material Subtotal | Labor Crew Type Not Used | Labor Hours/ft2 | Labor Subtotal | Construction Equipment Subtotal | Cost Adjustments | Not Used | Not Used | Total | Annual Main-tenance None | Replacement Life (years) | Material Cost/ft2 | Material Subtotal | Labor Crew Type Not Used | Labor Hours/ft2 | Labor Subtotal | Construction Equipment Subtotal | Cost Adjustments | Not Used | Not Used | Total | Material Cost/ft2 | Material Subtotal | Labor Crew Type Not Used | Labor Hours/ft2 | Labor Subtotal | Construction Equipment Subtotal | Cost Adjustments | Incremental Added Design with OH&P | Incremental Added Commis- sioning with OH&P | Total | Annual Maintenance Cost None | Replacement Life (years) | Material Cost/ft2 | Material Subtotal | Labor Crew Type Not Used | Labor Hours/ft2 | Labor Subtotal | Construction Equipment Subtotal | Cost Adjustments | Incremental Added Design with OH&P | Incremental Added Commis- sioning with OH&P | Total | New Construction Costs | Replacement Costs (may have different frequency)
[5 empty] | 0 | [5 empty] | X | X | X | X | X |  | Small _Office_Interior_Lighting_LPD |  | Small Office | [18 empty] | Small Office | [16 empty] | Small Office | [10 empty] | Small Office | [10 empty] | Small Office | [10 empty] | Small Office | [9 empty] | Small Office | 0 | 0
[5 empty] | 0 | [5 empty] | X | X | X | X | X
[5 empty] | 0 | [5 empty] | X | X | X | X | X |  |  |  | Zone 2 |  |  | 600 | 0 | 0 | [7 empty] | 0 |  |  |  | 1 |  |  |  |  | 400 | 0 | 0 | [8 empty] | 0
[5 empty] | 0 | [5 empty] | X | X | X | X | X |  |  |  | Zone 3 |  |  | 750 | 0 | 0 | [16 empty] | 500 | 0 | 0
[5 empty] | 0 | [5 empty] | X | X | X | X | X |  |  |  | Zone 4 |  |  | 1300 | 0 | 0 | [16 empty] | 900 | 0 | 0
[5 empty] | 0 | [5 empty] | X | X | X | X | X |  |  |  | Area required per space |  | 325 | [16 empty] | Area required per space |  | 325
[5 empty] | 0 | [5 empty] | X | X | X | X | X |  |  |  | # of Parking Spaces |  | 27.4154 | [16 empty] | # of Parking Spaces |  | 27.4154
[5 empty] | 0 | [5 empty] | X | X | X | X | X |  |  |  | # of spaces per fixture |  | 20 | [16 empty] | # of spaces per fixture |  | 20
[5 empty] | 0 | [5 empty] | X | X | X | X | X |  |  |  | # of Fixtures |  | 1.3708 | [16 empty] | # of Fixtures | 0 | 1.3708
[5 empty] | 0 | [5 empty] | X | X | X | X | X |  |  |  | Parking |  | area, ft2 | [16 empty] | Parking |  | area, ft2
[5 empty] | 0 | [5 empty] | X | X | X | X | X |  |  |  | includes lamp replacement | zone 2 | 8910 | 600 | 0 | 0 | 0.06 | 534.6 | LED-PK-85 LPW-6600 lm | 73 | 7.3233 | 1 | 100000 | 4 | 20 | 156.2143 |  | 0.5 |  | includes lamp replacement | zone 2 | 8910 | 400 | 0 | 0 | 0.04 | 356.4 | LED-PK-91 LPW-5600 lm | 59 | 6.0407 | 1 | 100000 | 4 | 20 | 280 | 0.5 |  | 4715.8105 |  |  | 1610.5223 | 96.5 | 3946.7338 | 1.6274 |  | 10369.5666 |  | 23 |  | 0 |  |  | 0 |  | 0 |  |  | 0 |  | 4226.6 |  |  | 725.7436 | 96.5 | 2847.2528 |  |  | 7896.0964 |  | 35 |  | 0 |  |  | 0 |  | 0 |  |  | 0 | EXCLUDED
[5 empty] | 0 | [5 empty] | X | X | X | X | X |  |  |  | ballast replacement | [11 empty] | 100000 | [6 empty] | ballast replacement | [11 empty] | 50000 | [15 empty] | 23 |  | 1076.5233 |  |  | 1205.6723 |  | 2015.9651 |  |  | 4298.1607 | [11 empty] | 18 |  | 469.6627 |  |  | 335.6427 |  | 671.9415 |  |  | 1477.247 |  | EXCLUDED
[5 empty] | 0 | [5 empty] | X | X | X | X | X |  |  |  |  | zone 3 | 8910 | 750 | 0 | 0 | 0.1 | 891 | LED-PK-85 LPW-6600 lm | 73 | 12.2055 | 1 | 100000 | 7 | 20 | 156 |  | 0.5 |  | " " | zone 3 | 8910 | 500 | 0 | 0 | 0.06 | 534.6 | LED-PK-91 LPW-5600 lm | 59 | 9.061 | 1 | 100000 | 7 | 20 | 280 | 0.5 |  | 8016.321 |  |  | 2652.4708 | 168.875 | 6628.0887 | 1.6351 |  | 17465.7555 |  | 23 |  | 0 |  |  | 0 |  | 0 |  |  | 0 |  | 6893.75 |  |  | 1118.4653 | 168.875 | 4584.2881 |  |  | 12765.3784 |  | 35 |  | 0 |  |  | 0 |  | 0 |  |  | 0 | EXCLUDED
[5 empty] | 0 | [5 empty] | X | X | X | X | X | [15 empty] | 100000 | [6 empty] | " " | [11 empty] | 50000 | [15 empty] | 23 |  | 1794.2055 |  |  | 2009.4539 |  | 3359.9418 |  |  | 7163.6012 | [11 empty] | 18 |  | 704.4941 |  |  | 503.4641 |  | 1007.9123 |  |  | 2215.8705 |  | EXCLUDED
[5 empty] | 0 | [5 empty] | X | X | X | X | X |  |  |  |  | zone 4 | 8910 | 1300 | 0 | 0 | 0.13 | 1158.3 | LED-PK-85 LPW-6600 lm | 73 | 15.8671 | 1 | 100000 | 8 | 20 | 156 |  | 0 |  | " " | zone 4 | 8910 | 900 | 0 | 0 | 0.08 | 712.8 | LED-PK-91 LPW-5600 lm | 59 | 12.0814 | 1 | 100000 | 8 | 20 | 280 | 0 |  | 0 |  |  | 0 | 0 | 0 |  |  | 0 |  | 23 |  | 0 |  |  | 0 |  | 0 |  |  | 0 |  | 0 |  |  | 0 | 0 | 0 |  |  | 0 |  | 35 |  | 0 |  |  | 0 |  | 0 |  |  | 0
[5 empty] | 0 | [5 empty] | X | X | X | X | X | [15 empty] | 100000 | [6 empty] | " " | [27 empty] | 23 |  | 0 |  |  | 0 |  | 0 |  |  | 0 | [11 empty] | 0 |  | 0 |  |  | 0 |  | 0 |  |  | 0
[5 empty] | 0 | [5 empty] | X | X | X | X | X
[5 empty] | 0 | [5 empty] | X | X | X | X | X |  |  |  | Doors |  | linear feet, ft | [16 empty] | Doors |  | linear feet, ft
[5 empty] | 0 | [5 empty] | X | X | X | X | X |  |  |  | Main Door includes lamp replacement | zone 2 | 3.3 | 600 | 0 | 0 | 20 | 66 | LED-Wall-97 LPW-2700 lm | 28 | 2.3571 | 1 | 60000 | 0 | 0 |  |  | 0.5 |  | includes lamp replacement | zone 2 | 3.3 | 400 | 0 | 0 | 14 | 46.2 | LED-Wall-103 LPW-2900 lm | 28 | 1.65 | 1 | 100000 | 0 | 0 |  | 0.5 |  | 408.9643 |  |  | 79.3768 | 0 | 281.6482 | 1.7339 |  | 769.9893 |  | 14 |  | 0 |  |  | 0 |  | 0 |  |  | 0 |  | 535.425 |  |  | 27.7819 | 0 | 295.2278 |  |  | 858.4346 |  | 35 |  | 0 |  |  | 0 |  | 0 |  |  | 0 | EXCLUDED
[5 empty] | 0 | [5 empty] | X | X | X | X | X |  |  |  | ballast replacement | [11 empty] | 60000 | [6 empty] | ballast replacement | [11 empty] | 100000 | [15 empty] | 14 |  | 204.4821 |  |  | 130.9717 |  | 276.0189 |  |  | 611.4727 | [11 empty] | 35 |  | 267.7125 |  |  | 91.6802 |  | 274.3641 |  |  | 633.7568 |  | EXCLUDED
[5 empty] | 0 | [5 empty] | X | X | X | X | X |  |  |  | Other Doors - includes lamp replacement | zone 2 | 3.3 | 750 | 0 | 0 | 20 | 66 | LED-Wall-97 LPW-2700 lm | 28 | 2.3571 | 1 | 60000 | 0 | 0 |  |  | 0.5 |  | Other Doors - includes lamp replacement | zone 2 | 3.3 | 500 | 0 | 0 | 14 | 46.2 | LED-Wall-103 LPW-2900 lm | 28 | 1.65 | 1 | 100000 | 0 | 0 |  | 0.5 |  | 408.9643 |  |  | 79.3768 | 0 | 281.6482 | 1.7339 |  | 769.9893 |  | 14 |  | 0 |  |  | 0 |  | 0 |  |  | 0 |  | 535.425 |  |  | 27.7819 | 0 | 295.2278 |  |  | 858.4346 |  | 35 |  | 0 |  |  | 0 |  | 0 |  |  | 0 | EXCLUDED
[5 empty] | 0 | [5 empty] | X | X | X | X | X |  |  |  | ballast replacement | [11 empty] | 60000 | [6 empty] | ballast replacement | [11 empty] | 100000 | [15 empty] | 14 |  | 204.4821 |  |  | 130.9717 |  | 276.0189 |  |  | 611.4727 | [11 empty] | 35 |  | 267.7125 |  |  | 91.6802 |  | 274.3641 |  |  | 633.7568 |  | EXCLUDED
[5 empty] | 0 | [5 empty] | X | X | X | X | X |  |  |  | Rool-up Door includes lamp replacement | zone 2 | 2.563 | 1300 | 0 | 0 | 20 | 51.26 | LED-Wall-97 LPW-2700 lm | 28 | 1.8307 | 1 | 60000 | 0 | 0 |  |  | 0.5 |  | Rool-up Door includes lamp replacement | zone 2 | 2.563 | 900 | 0 | 0 | 14 | 35.882 | LED-Wall-103 LPW-2900 lm | 28 | 1.2815 | 1 | 100000 | 0 | 0 |  | 0.5 |  | 317.6289 |  |  | 61.6493 | 0 | 218.7468 | 1.7339 |  | 598.025 |  | 14 |  | 0 |  |  | 0 |  | 0 |  |  | 0 |  | 415.8467 |  |  | 21.5773 | 0 | 229.2936 |  |  | 666.7176 |  | 35 |  | 0 |  |  | 0 |  | 0 |  |  | 0 | EXCLUDED
[5 empty] | 0 | [5 empty] | X | X | X | X | X |  |  |  | ballast replacement | [11 empty] | 60000 | [6 empty] | ballast replacement | [11 empty] | 100000 | [15 empty] | 14 |  | 158.8145 |  |  | 101.7214 |  | 214.3747 |  |  | 474.9105 | [11 empty] | 35 |  | 207.9234 |  |  | 71.2049 |  | 213.0895 |  |  | 492.2178 |  | EXCLUDED
[5 empty] | 0 | [5 empty] | X | X | X | X | X | [10 empty] | 183.26 | [18 empty] | 128.282
[5 empty] | 0 | [5 empty] | X | X | X | X | X |  |  |  | Main Door includes lamp replacement | zone 3 | 3.3 | 750 | 0 | 0 | 30 | 99 | LED-Wall-97 LPW-2700 lm | 28 | 3.5357 | 1 | 60000 | 0 | 0 |  |  | 0.5 |  | " " | zone 3 | 3.3 | 500 | 0 | 0 | 21 | 69.3 | LED-Wall-103 LPW-2900 lm | 28 | 2.475 | 1 | 100000 | 0 | 0 |  | 0.5 |  | 613.4464 |  |  | 119.0652 | 0 | 422.4723 | 1.7339 |  | 1154.9839 |  | 14 |  | 0 |  |  | 0 |  | 0 |  |  | 0 |  | 803.1375 |  |  | 41.6728 | 0 | 442.8416 |  |  | 1287.652 |  | 35 |  | 0 |  |  | 0 |  | 0 |  |  | 0 | EXCLUDED
[5 empty] | 0 | [5 empty] | X | X | X | X | X |  |  |  | ballast replacement | [11 empty] | 60000 | [6 empty] | " " | [11 empty] | 100000 | [15 empty] | 14 |  | 306.7232 |  |  | 196.4575 |  | 414.0283 |  |  | 917.2091 | [11 empty] | 35 |  | 401.5688 |  |  | 137.5203 |  | 411.5462 |  |  | 950.6352 |  | EXCLUDED
[5 empty] | 0 | [5 empty] | X | X | X | X | X |  |  |  | Other Doors - includes lamp replacement | Zone 3 | 3.3 | 600 | 0 | 0 | 30 | 99 | LED-Wall-97 LPW-2700 lm | 28 | 3.5357 | 1 | 60000 | 0 | 0 |  |  | 0.5 |  | Other Doors - includes lamp replacement | Zone 3 | 3.3 | 400 | 0 | 0 | 21 | 69.3 | LED-Wall-103 LPW-2900 lm | 28 | 2.475 | 1 | 100000 | 0 | 0 |  | 0.5 |  | 613.4464 |  |  | 119.0652 | 0 | 422.4723 | 1.7339 |  | 1154.9839 |  | 14 |  | 0 |  |  | 0 |  | 0 |  |  | 0 |  | 803.1375 |  |  | 41.6728 | 0 | 442.8416 |  |  | 1287.652 |  | 35 |  | 0 |  |  | 0 |  | 0 |  |  | 0 | EXCLUDED
[5 empty] | 0 | [5 empty] | X | X | X | X | X |  |  |  | ballast replacement | [11 empty] | 60000 | [6 empty] | ballast replacement | [11 empty] | 100000 | [15 empty] | 14 |  | 306.7232 |  |  | 196.4575 |  | 414.0283 |  |  | 917.2091 | [11 empty] | 35 |  | 401.5688 |  |  | 137.5203 |  | 411.5462 |  |  | 950.6352 |  | EXCLUDED
[5 empty] | 0 | [5 empty] | X | X | X | X | X |  |  |  | Rool-up Door includes lamp replacement | Zone 3 | 2.563 | 750 | 0 | 0 | 20 | 51.26 | LED-Wall-97 LPW-2700 lm | 28 | 1.8307 | 1 | 60000 | 0 | 0 |  |  | 0.5 |  | Rool-up Door includes lamp replacement | Zone 3 | 2.563 | 500 | 0 | 0 | 21 | 53.823 | LED-Wall-103 LPW-2900 lm | 28 | 1.9223 | 1 | 100000 | 0 | 0 |  | 0.5 |  | 317.6289 |  |  | 61.6493 | 0 | 218.7468 | 1.7339 |  | 598.025 |  | 14 |  | 0 |  |  | 0 |  | 0 |  |  | 0 |  | 623.7701 |  |  | 32.3659 | 0 | 343.9403 |  |  | 1000.0764 |  | 35 |  | 0 |  |  | 0 |  | 0 |  |  | 0 | EXCLUDED
[5 empty] | 0 | [5 empty] | X | X | X | X | X |  |  |  | ballast replacement | [11 empty] | 60000 | [6 empty] | ballast replacement | [11 empty] | 100000 | [15 empty] | 14 |  | 158.8145 |  |  | 101.7214 |  | 214.3747 |  |  | 474.9105 | [11 empty] | 35 |  | 311.8851 |  |  | 106.8074 |  | 319.6342 |  |  | 738.3267 |  | EXCLUDED
[5 empty] | 0 | [5 empty] | X | X | X | X | X | [10 empty] | 249.26 | [18 empty] | 192.423
[5 empty] | 0 | [5 empty] | X | X | X | X | X |  |  |  | Main Door includes lamp replacement | zone 4 | 3.3 | 1300 | 0 | 0 | 30 | 99 | LED-Wall-97 LPW-2700 lm | 28 | 3.5357 | 1 | 60000 | 0 | 0 |  |  | 0 |  | " " | zone 4 | 3.3 | 900 | 0 | 0 | 21 | 69.3 | LED-Wall-103 LPW-2900 lm | 28 | 2.475 | 1 | 100000 | 0 | 0 |  | 0 |  | 0 |  |  | 0 | 0 | 0 |  |  | 0 |  | 14 |  | 0 |  |  | 0 |  | 0 |  |  | 0 |  | 0 |  |  | 0 | 0 | 0 |  |  | 0 |  | 35 |  | 0 |  |  | 0 |  | 0 |  |  | 0
[5 empty] | 0 | [5 empty] | X | X | X | X | X |  |  |  | ballast replacement | [11 empty] | 60000 | [6 empty] | " " | [11 empty] | 100000 | [15 empty] | 14 |  | 0 |  |  | 0 |  | 0 |  |  | 0 | [11 empty] | 35 |  | 0 |  |  | 0 |  | 0 |  |  | 0
[5 empty] | 0 | [5 empty] | X | X | X | X | X |  |  |  | Other Doors - includes lamp replacement | Zone 4 | 3.3 | 750 | 0 | 0 | 30 | 99 | LED-Wall-97 LPW-2700 lm | 28 | 3.5357 | 1 | 60000 | 0 | 0 |  |  | 0 |  | Other Doors - includes lamp replacement | Zone 4 | 3.3 | 500 | 0 | 0 | 21 | 69.3 | LED-Wall-103 LPW-2900 lm | 28 | 2.475 | 1 | 100000 | 0 | 0 |  | 0 |  | 0 |  |  | 0 | 0 | 0 |  |  | 0 |  | 14 |  | 0 |  |  | 0 |  | 0 |  |  | 0 |  | 0 |  |  | 0 | 0 | 0 |  |  | 0 |  | 35 |  | 0 |  |  | 0 |  | 0 |  |  | 0
[5 empty] | 0 | [5 empty] | X | X | X | X | X |  |  |  | ballast replacement | [11 empty] | 60000 | [6 empty] | ballast replacement | [11 empty] | 100000 | [15 empty] | 14 |  | 0 |  |  | 0 |  | 0 |  |  | 0 | [11 empty] | 35 |  | 0 |  |  | 0 |  | 0 |  |  | 0
[5 empty] | 0 | [5 empty] | X | X | X | X | X |  |  |  | Rool-up Door includes lamp replacement | Zone 4 | 2.563 | 600 | 0 | 0 | 20 | 51.26 | LED-Wall-97 LPW-2700 lm | 28 | 1.8307 | 1 | 60000 | 0 | 0 |  |  | 0 |  | Rool-up Door includes lamp replacement | Zone 4 | 2.563 | 400 | 0 | 0 | 21 | 53.823 | LED-Wall-103 LPW-2900 lm | 28 | 1.9223 | 1 | 100000 | 0 | 0 |  | 0 |  | 0 |  |  | 0 | 0 | 0 |  |  | 0 |  | 14 |  | 0 |  |  | 0 |  | 0 |  |  | 0 |  | 0 |  |  | 0 | 0 | 0 |  |  | 0 |  | 35 |  | 0 |  |  | 0 |  | 0 |  |  | 0
[5 empty] | 0 | [5 empty] | X | X | X | X | X |  |  |  | ballast replacement | [11 empty] | 60000 | [6 empty] | ballast replacement | [11 empty] | 100000 | [15 empty] | 14 |  | 0 |  |  | 0 |  | 0 |  |  | 0 | [11 empty] | 35 |  | 0 |  |  | 0 |  | 0 |  |  | 0
[5 empty] | 0 | [5 empty] | X | X | X | X | X | [10 empty] | 249.26 | [18 empty] | 192.423
[5 empty] | 0 | [5 empty] | X | X | X | X | X
[5 empty] | 0 | [5 empty] | X | X | X | X | X
[5 empty] | 0 | [5 empty] | X | X | X | X | X |  |  |  | Façade |  | area, ft2 | [7 empty] | 0.85176 | [8 empty] | Façade |  | area, ft2
[5 empty] | 0 | [5 empty] | X | X | X | X | X |  |  |  | includes lamp replacement | zone 2 | 405 | 600 | 0 | 0 | 0.1 | 40.5 | LED-Flood-104 LPD-2600 lm | 25 | 1.62 | 1 | 100000 | 0 | 0 |  |  | 0.5 |  | includes lamp replacement | zone 2 | 405 | 400 | 0 | 0 | 0.1 | 40.5 | LED-Flood-104 LPD-2600 lm | 25 | 1.62 | 1 | 100000 | 0 | 0 |  | 0.5 |  | 214.65 |  |  | 54.5535 | 0 | 160.2732 | 1.6797 |  | 429.4767 |  | 23 |  | 0 |  |  | 0 |  | 0 |  |  | 0 |  | 214.65 |  |  | 27.2767 | 0 | 133.9379 |  |  | 375.8646 |  | 35 |  | 0 |  |  | 0 |  | 0 |  |  | 0 | EXCLUDED
[5 empty] | 0 | [5 empty] | X | X | X | X | X |  |  |  | ballast replacement | [11 empty] | 100000 | [6 empty] | ballast replacement | [11 empty] | 100000 | [15 empty] | 23 |  | 107.325 |  |  | 90.0133 |  | 168.0665 |  |  | 365.4048 | [11 empty] | 35 |  | 107.325 |  |  | 90.0133 |  | 168.0665 |  |  | 365.4048
[5 empty] | 0 | [5 empty] | X | X | X | X | X |  |  |  |  | zone 3 | 405 | 750 | 0 | 0 | 0.15 | 60.75 | LED-Flood-104 LPD-2600 lm | 25 | 2.43 | 1 | 100000 | 0 | 0 |  |  | 0.5 |  | " " | zone 3 | 405 | 500 | 0 | 0 | 0.15 | 60.75 | LED-Flood-104 LPD-2600 lm | 25 | 2.43 | 1 | 100000 | 0 | 0 |  | 0.5 |  | 321.975 |  |  | 81.8303 | 0 | 240.4099 | 1.6797 |  | 644.2151 |  | 23 |  | 0 |  |  | 0 |  | 0 |  |  | 0 |  | 321.975 |  |  | 40.9151 | 0 | 200.9068 |  |  | 563.7969 |  | 35 |  | 0 |  |  | 0 |  | 0 |  |  | 0 | EXCLUDED
[5 empty] | 0 | [5 empty] | X | X | X | X | X | [15 empty] | 100000 | [6 empty] | " " | [11 empty] | 100000 | [15 empty] | 23 |  | 160.9875 |  |  | 135.0199 |  | 252.0998 |  |  | 548.1072 | [11 empty] | 35 |  | 160.9875 |  |  | 135.0199 |  | 252.0998 |  |  | 548.1072
[5 empty] | 0 | [5 empty] | X | X | X | X | X |  |  |  |  | zone 4 | 405 | 1300 | 0 | 0 | 0.2 | 81 | LED-Flood-104 LPD-2600 lm | 25 | 3.24 | 1 | 100000 | 0 | 0 |  |  | 0 |  | " " | zone 4 | 405 | 900 | 0 | 0 | 0.2 | 81 | LED-Flood-104 LPD-2600 lm | 25 | 3.24 | 1 | 100000 | 0 | 0 |  | 0 |  | 0 |  |  | 0 | 0 | 0 |  |  | 0 |  | 23 |  | 0 |  |  | 0 |  | 0 |  |  | 0 |  | 0 |  |  | 0 | 0 | 0 |  |  | 0 |  | 35 |  | 0 |  |  | 0 |  | 0 |  |  | 0
[5 empty] | 0 | [5 empty] | X | X | X | X | X | [15 empty] | 100000 | [6 empty] | " " | [11 empty] | 100000 | [15 empty] | 23 |  | 0 |  |  | 0 |  | 0 |  |  | 0 | [11 empty] | 35 |  | 0 |  |  | 0 |  | 0 |  |  | 0
[5 empty] | 0 | [5 empty] | X | X | X | X | X
[6 empty] | 0 |  |  |  |  | X | X | X | X | X |  |  |  | Large Office | [18 empty] | Large Office | [16 empty] | Large Office | [10 empty] | Large Office | [10 empty] | Large Office | [10 empty] | Large Office | [9 empty] | Large Office | 0 | 0
[6 empty] | 0 |  |  |  |  | X | X | X | X | X
[6 empty] | 0 |  |  |  |  | X | X | X | X | X |  |  |  | Zone 2 |  |  | 600 | 0 | 0 | [7 empty] | 0 | [5 empty] | Zone 2 |  |  | 400 | 0 | 0
[6 empty] | 0 |  |  |  |  | X | X | X | X | X |  |  |  | Zone 3 |  |  | 750 | 0 | 0 | [13 empty] | Zone 3 |  |  | 500 | 0 | 0
[6 empty] | 0 |  |  |  |  | X | X | X | X | X |  |  |  | Zone 4 |  |  | 1300 | 0 | 0 | [13 empty] | Zone 4 |  |  | 900 | 0 | 0
[6 empty] | 0 |  |  |  |  | X | X | X | X | X |  |  |  | Area required per space |  | 325 | [16 empty] | Area required per space |  | 325
[6 empty] | 0 |  |  |  |  | X | X | X | X | X |  |  |  | # of Parking Spaces |  | 1000.2677 | [16 empty] | # of Parking Spaces |  | 1000.2677
[6 empty] | 0 |  |  |  |  | X | X | X | X | X |  |  |  | # of spaces per fixture |  | 20 | [16 empty] | # of spaces per fixture |  | 20
[6 empty] | 0 |  |  |  |  | X | X | X | X | X |  |  |  | # of Fixtures | 0 | 50.0134 | [16 empty] | # of Fixtures | 0 | 50.0134
[6 empty] | 0 |  |  |  |  | X | X | X | X | X |  |  |  | Parking |  | area, ft2 | [16 empty] | Parking |  | area, ft2
[6 empty] | 0 |  |  |  |  | X | X | X | X | X |  |  |  | includes lamp replacement | zone 2 | 325087 | 600 | 0 | 0 | 0.06 | 19505.22 | LED-PK-102 LPW-28700 lm | 281 | 69.4136 | 1 | 100000 | 18 | 35 | 2534.9504 |  | 0 |  | includes lamp replacement | zone 2 | 325087 | 400 | 0 | 0 | 0.04 | 13003.48 | LED-PK-107 LPW-30200 lm | 281 | 46.2757 | 1 | 100000 | 12 | 35 | 2534.9504 | 0 |  | 0 |  |  | 0 | 0 | 0 |  |  | 0 |  | 23 |  | 0 |  |  | 0 |  | 0 |  |  | 0 |  | 0 |  |  | 0 | 0 | 0 |  |  | 0 |  | 35 |  | 0 |  |  | 0 |  | 0 |  |  | 0
[6 empty] | 0 |  |  |  |  | X | X | X | X | X |  |  |  | ballast replacement | [11 empty] | 50000 | [6 empty] | ballast replacement | [27 empty] | 11 |  | 0 |  |  | 0 |  | 0 |  |  | 0 | [11 empty] | 0 |  | 0 |  |  | 0 |  | 0 |  |  | 0
[6 empty] | 0 |  |  |  |  | X | X | X | X | X |  |  |  |  | zone 3 | 325087 | 750 | 0 | 0 | 0.1 | 32508.7 | LED-PK-102 LPW-28700 lm | 281 | 115.6893 | 1 | 100000 | 29 | 35 | 2534.9504 |  | 0 |  | " " | zone 3 | 325087 | 500 | 0 | 0 | 0.06 | 19505.22 | LED-PK-107 LPW-30200 lm | 281 | 69.4136 | 1 | 100000 | 18 | 35 | 2534.9504 | 0 |  | 0 |  |  | 0 | 0 | 0 |  |  | 0 |  | 23 |  | 0 |  |  | 0 |  | 0 |  |  | 0 |  | 0 |  |  | 0 | 0 | 0 |  |  | 0 |  | 35 |  | 0 |  |  | 0 |  | 0 |  |  | 0
[6 empty] | 0 |  |  |  |  | X | X | X | X | X | [15 empty] | 50000 | [6 empty] | " " | [11 empty] | 50000 | [15 empty] | 11 |  | 0 |  |  | 0 |  | 0 |  |  | 0 | [11 empty] | 18 |  | 0 |  |  | 0 |  | 0 |  |  | 0
[6 empty] | 0 |  |  |  |  | X | X | X | X | X |  |  |  |  | zone 4 | 325087 | 1300 | 0 | 0 | 0.13 | 42261.31 | LED-PK-102 LPW-28700 lm | 281 | 150.3961 | 1 | 100000 | 38 | 35 | 2534.9504 |  | 1 |  | " " | zone 4 | 325087 | 900 | 0 | 0 | 0.08 | 26006.96 | LED-PK-107 LPW-30200 lm | 281 | 92.5515 | 1 | 100000 | 24 | 35 | 2534.9504 | 1 |  | 227301.3414 |  |  | 44777.1821 | 2232.5 | 157819.3179 | 1.7381 |  | 432130.3415 |  | 23 |  | 0 |  |  | 0 |  | 0 |  |  | 0 |  | 141977.9416 |  |  | 29580.4049 | 1410 | 100138.1258 |  |  | 273106.4724 |  | 35 |  | 0 |  |  | 0 |  | 0 |  |  | 0 | EXCLUDED
[6 empty] | 0 |  |  |  |  | X | X | X | X | X | [15 empty] | 50000 | [6 empty] | " " | [11 empty] | 50000 | [15 empty] | 11 |  | 23386.5968 |  |  | 16713.1449 |  | 33458.9599 |  |  | 73558.7016 | [11 empty] | 18 |  | 14391.7519 |  |  | 10285.0123 |  | 20590.1292 |  |  | 45266.8933 |  | EXCLUDED
[6 empty] | 0 |  |  |  |  | X | X | X | X | X
[6 empty] | 0 |  |  |  |  | X | X | X | X | X |  |  |  | Doors |  | linear feet, ft | [16 empty] | Doors |  | linear feet, ft
[6 empty] | 0 |  |  |  |  | X | X | X | X | X |  |  |  | Main Door includes lamp replacement | zone 2 | 10.44 | 600 | 0 | 0 | 20 | 208.8 | LED-Wall-86 LPW-7700 lm | 83 | 2.5157 | 1 | 60000 | 0 | 0 |  |  | 0 |  | Main Door includes lamp replacement | zone 2 | 10.44 | 400 | 0 | 0 | 14 | 146.16 | LED-Wall-101 LPW-8000 lm | 83 | 1.761 | 1 | 60000 | 0 | 0 |  | 0 |  | 0 |  |  | 0 | 0 | 0 |  |  | 0 |  | 14 |  | 0 |  |  | 0 |  | 0 |  |  | 0 |  | 0 |  |  | 0 | 0 | 0 |  |  | 0 |  | 21 |  | 0 |  |  | 0 |  | 0 |  |  | 0
[6 empty] | 0 |  |  |  |  | X | X | X | X | X |  |  |  | ballast replacement | [11 empty] | 60000 | [6 empty] | ballast replacement | [11 empty] | 60000 | [15 empty] | 14 |  | 0 |  |  | 0 |  | 0 |  |  | 0 | [11 empty] | 21 |  | 0 |  |  | 0 |  | 0 |  |  | 0
[6 empty] | 0 |  |  |  |  | X | X | X | X | X |  |  |  | Other Doors - includes lamp replacement | zone 2 | 34.56 | 750 | 0 | 0 | 20 | 691.2 | LED-Wall-86 LPW-7700 lm | 83 | 8.3277 | 1 | 60000 | 0 | 0 |  |  | 0 |  | Other Doors - includes lamp replacement | zone 2 | 34.56 | 500 | 0 | 0 | 14 | 483.84 | LED-Wall-101 LPW-8000 lm | 83 | 5.8294 | 1 | 60000 | 0 | 0 |  | 0 |  | 0 |  |  | 0 | 0 | 0 |  |  | 0 |  | 14 |  | 0 |  |  | 0 |  | 0 |  |  | 0 |  | 0 |  |  | 0 | 0 | 0 |  |  | 0 |  | 21 |  | 0 |  |  | 0 |  | 0 |  |  | 0
[6 empty] | 0 |  |  |  |  | X | X | X | X | X |  |  |  | ballast replacement | [11 empty] | 60000 | [6 empty] | ballast replacement | [11 empty] | 60000 | [15 empty] | 14 |  | 0 |  |  | 0 |  | 0 |  |  | 0 | [11 empty] | 21 |  | 0 |  |  | 0 |  | 0 |  |  | 0
[6 empty] | 0 |  |  |  |  | X | X | X | X | X |  |  |  | Rool-up Door includes lamp replacement | zone 2 | 0.192 | 1300 | 0 | 0 | 20 | 3.84 | LED-Wall-86 LPW-7700 lm | 83 | 0.046265 | 1 | 60000 | 0 | 0 |  |  | 0 |  | Rool-up Door includes lamp replacement | zone 2 | 0.192 | 900 | 0 | 0 | 14 | 2.688 | LED-Wall-101 LPW-8000 lm | 83 | 0.032386 | 1 | 60000 | 0 | 0 |  | 0 |  | 0 |  |  | 0 | 0 | 0 |  |  | 0 |  | 14 |  | 0 |  |  | 0 |  | 0 |  |  | 0 |  | 0 |  |  | 0 | 0 | 0 |  |  | 0 |  | 21 |  | 0 |  |  | 0 |  | 0 |  |  | 0
[6 empty] | 0 |  |  |  |  | X | X | X | X | X |  |  |  | ballast replacement | [11 empty] | 60000 | [6 empty] | ballast replacement | [11 empty] | 60000 | [15 empty] | 14 |  | 0 |  |  | 0 |  | 0 |  |  | 0 | [11 empty] | 21 |  | 0 |  |  | 0 |  | 0 |  |  | 0
[6 empty] | 0 |  |  |  |  | X | X | X | X | X | [10 empty] | 903.84 | [18 empty] | 632.688
[6 empty] | 0 |  |  |  |  | X | X | X | X | X |  |  |  | Main Door includes lamp replacement | Zone 3 | 10.44 | 0 | 0 | 0 | 30 | 313.2 | LED-Wall-86 LPW-7700 lm | 83 | 3.7735 | 1 | 60000 | 0 | 0 |  |  | 0 |  | Main Door includes lamp replacement | Zone 3 | 10.44 | 0 | 0 | 0 | 21 | 219.24 | LED-Wall-101 LPW-8000 lm | 83 | 2.6414 | 1 | 60000 | 0 | 0 |  | 0 |  | 0 |  |  | 0 | 0 | 0 |  |  | 0 |  | 14 |  | 0 |  |  | 0 |  | 0 |  |  | 0 |  | 0 |  |  | 0 | 0 | 0 |  |  | 0 |  | 21 |  | 0 |  |  | 0 |  | 0 |  |  | 0
[6 empty] | 0 |  |  |  |  | X | X | X | X | X |  |  |  | ballast replacement | [11 empty] | 60000 | [6 empty] | ballast replacement | [11 empty] | 60000 | [15 empty] | 14 |  | 0 |  |  | 0 |  | 0 |  |  | 0 | [11 empty] | 21 |  | 0 |  |  | 0 |  | 0 |  |  | 0
[6 empty] | 0 |  |  |  |  | X | X | X | X | X |  |  |  | Other Doors - includes lamp replacement | Zone 3 | 34.56 | 600 | 0 | 0 | 30 | 1036.8 | LED-Wall-86 LPW-7700 lm | 83 | 12.4916 | 1 | 60000 | 0 | 0 |  |  | 0 |  | Other Doors - includes lamp replacement | Zone 3 | 34.56 | 400 | 0 | 0 | 21 | 725.76 | LED-Wall-101 LPW-8000 lm | 83 | 8.7441 | 1 | 60000 | 0 | 0 |  | 0 |  | 0 |  |  | 0 | 0 | 0 |  |  | 0 |  | 14 |  | 0 |  |  | 0 |  | 0 |  |  | 0 |  | 0 |  |  | 0 | 0 | 0 |  |  | 0 |  | 21 |  | 0 |  |  | 0 |  | 0 |  |  | 0
[6 empty] | 0 |  |  |  |  | X | X | X | X | X |  |  |  | ballast replacement | [11 empty] | 60000 | [6 empty] | ballast replacement | [11 empty] | 60000 | [15 empty] | 14 |  | 0 |  |  | 0 |  | 0 |  |  | 0 | [11 empty] | 21 |  | 0 |  |  | 0 |  | 0 |  |  | 0
[6 empty] | 0 |  |  |  |  | X | X | X | X | X |  |  |  | Rool-up Door includes lamp replacement | Zone 3 | 0.192 | 750 | 0 | 0 | 20 | 3.84 | LED-Wall-86 LPW-7700 lm | 83 | 0.046265 | 1 | 60000 | 0 | 0 |  |  | 0 |  | Rool-up Door includes lamp replacement | Zone 3 | 0.192 | 500 | 0 | 0 | 21 | 4.032 | LED-Wall-101 LPW-8000 lm | 83 | 0.048578 | 1 | 60000 | 0 | 0 |  | 0 |  | 0 |  |  | 0 | 0 | 0 |  |  | 0 |  | 14 |  | 0 |  |  | 0 |  | 0 |  |  | 0 |  | 0 |  |  | 0 | 0 | 0 |  |  | 0 |  | 21 |  | 0 |  |  | 0 |  | 0 |  |  | 0
[6 empty] | 0 |  |  |  |  | X | X | X | X | X |  |  |  | ballast replacement | [11 empty] | 60000 | [6 empty] | ballast replacement | [11 empty] | 60000 | [15 empty] | 14 |  | 0 |  |  | 0 |  | 0 |  |  | 0 | [11 empty] | 21 |  | 0 |  |  | 0 |  | 0 |  |  | 0
[6 empty] | 0 |  |  |  |  | X | X | X | X | X | [10 empty] | 1353.84 | [18 empty] | 949.032
[6 empty] | 0 |  |  |  |  | X | X | X | X | X |  |  |  | Main Door includes lamp replacement | Zone 4 | 10.44 | 1300 | 0 | 0 | 30 | 313.2 | LED-Wall-86 LPW-7700 lm | 83 | 3.7735 | 1 | 60000 | 0 | 0 |  |  | 1 |  | Main Door includes lamp replacement | Zone 4 | 10.44 | 900 | 0 | 0 | 21 | 219.24 | LED-Wall-101 LPW-8000 lm | 83 | 2.6414 | 1 | 60000 | 0 | 0 |  | 1 |  | 1973.5373 |  |  | 254.1448 | 0 | 1234.6938 | 1.8042 |  | 3462.376 |  | 14 |  | 0 |  |  | 0 |  | 0 |  |  | 0 |  | 1282.4219 |  |  | 177.9014 | 0 | 814.6305 |  |  | 2274.9538 |  | 21 |  | 0 |  |  | 0 |  | 0 |  |  | 0 | EXCLUDED
[6 empty] | 0 |  |  |  |  | X | X | X | X | X |  |  |  | ballast replacement | [11 empty] | 60000 | [6 empty] | ballast replacement | [11 empty] | 60000 | [15 empty] | 14 |  | 986.7687 |  |  | 419.339 |  | 1100.0602 |  |  | 2506.1678 | [11 empty] | 21 |  | 641.211 |  |  | 293.5373 |  | 737.7791 |  |  | 1672.5273 |  | EXCLUDED
[6 empty] | 0 |  |  |  |  | X | X | X | X | X |  |  |  | Other Doors - includes lamp replacement | Zone 4 | 34.56 | 0 | 0 | 0 | 30 | 1036.8 | LED-Wall-86 LPW-7700 lm | 83 | 12.4916 | 1 | 60000 | 0 | 0 |  |  | 1 |  | Other Doors - includes lamp replacement | Zone 4 | 34.56 | 0 | 0 | 0 | 21 | 725.76 | LED-Wall-101 LPW-8000 lm | 83 | 8.7441 | 1 | 60000 | 0 | 0 |  | 1 |  | 6533.0892 |  |  | 841.307 | 0 | 4087.2624 | 1.8042 |  | 11461.6585 |  | 14 |  | 0 |  |  | 0 |  | 0 |  |  | 0 |  | 4245.2588 |  |  | 588.9149 | 0 | 2696.7079 |  |  | 7530.8816 |  | 21 |  | 0 |  |  | 0 |  | 0 |  |  | 0 | EXCLUDED
[6 empty] | 0 |  |  |  |  | X | X | X | X | X |  |  |  | ballast replacement | [11 empty] | 60000 | [6 empty] | ballast replacement | [11 empty] | 60000 | [15 empty] | 14 |  | 3266.5446 |  |  | 1388.1565 |  | 3641.5785 |  |  | 8296.2796 | [11 empty] | 21 |  | 2122.6294 |  |  | 971.7096 |  | 2442.3031 |  |  | 5536.6421 |  | EXCLUDED
[6 empty] | 0 |  |  |  |  | X | X | X | X | X |  |  |  | Rool-up Door includes lamp replacement | Zone 4 | 0.192 | 600 | 0 | 0 | 20 | 3.84 | LED-Wall-86 LPW-7700 lm | 83 | 0.046265 | 1 | 60000 | 0 | 0 |  |  | 1 |  | Rool-up Door includes lamp replacement | Zone 4 | 0.192 | 400 | 0 | 0 | 21 | 4.032 | LED-Wall-101 LPW-8000 lm | 83 | 0.048578 | 1 | 60000 | 0 | 0 |  | 1 |  | 24.1966 |  |  | 3.116 | 0 | 15.138 | 1.8042 |  | 42.4506 |  | 14 |  | 0 |  |  | 0 |  | 0 |  |  | 0 |  | 23.5848 |  |  | 3.2717 | 0 | 14.9817 |  |  | 41.8382 |  | 21 |  | 0 |  |  | 0 |  | 0 |  |  | 0 | EXCLUDED
[6 empty] | 0 |  |  |  |  | X | X | X | X | X |  |  |  | ballast replacement | [11 empty] | 60000 | [6 empty] | ballast replacement | [11 empty] | 60000 | [15 empty] | 14 |  | 12.0983 |  |  | 5.1413 |  | 13.4873 |  |  | 30.727 | [11 empty] | 21 |  | 11.7924 |  |  | 5.3984 |  | 13.5684 |  |  | 30.7591 |  | EXCLUDED
[6 empty] | 0 |  |  |  |  | X | X | X | X | X | [10 empty] | 1353.84 | [18 empty] | 949.032
[6 empty] | 0 |  |  |  |  | X | X | X | X | X
[6 empty] | 0 |  |  |  |  | X | X | X | X | X |  |  |  | Façade |  | area, ft2 | [16 empty] | Façade |  | area, ft2
[6 empty] | 0 |  |  |  |  | X | X | X | X | X |  |  |  | includes lamp replacement | zone 2 | 14319 | 600 | 0 | 0 | 0.1 | 1431.9 | LED-FLD-134 LPW-5600 lm | 39 | 36.7154 | 1 | 100000 | 0 | 0 |  |  | 0 |  | includes lamp replacement | zone 2 | 14319 | 400 | 0 | 0 | 0.1 | 1431.9 | LED-FLD-134 LPW-5600 lm | 39 | 36.7154 | 1 | 100000 | 0 | 0 |  | 0 |  | 0 |  |  | 0 | 0 | 0 |  |  | 0 |  | 23 |  | 0 |  |  | 0 |  | 0 |  |  | 0 |  | 0 |  |  | 0 | 0 | 0 |  |  | 0 |  | 35 |  | 0 |  |  | 0 |  | 0 |  |  | 0
[6 empty] | 0 |  |  |  |  | X | X | X | X | X |  |  |  | ballast replacement | [11 empty] | 100000 | [6 empty] | ballast replacement | [11 empty] | 100000 | [15 empty] | 23 |  | 0 |  |  | 0 |  | 0 |  |  | 0 | [11 empty] | 35 |  | 0 |  |  | 0 |  | 0 |  |  | 0
[6 empty] | 0 |  |  |  |  | X | X | X | X | X |  |  |  |  | zone 3 | 14319 | 750 | 0 | 0 | 0.15 | 2147.85 | LED-FLD-134 LPW-5600 lm | 39 | 55.0731 | 1 | 100000 | 0 | 0 |  |  | 0 |  | " " | zone 3 | 14319 | 500 | 0 | 0 | 0.15 | 2147.85 | LED-FLD-134 LPW-5600 lm | 39 | 55.0731 | 1 | 100000 | 0 | 0 |  | 0 |  | 0 |  |  | 0 | 0 | 0 |  |  | 0 |  | 23 |  | 0 |  |  | 0 |  | 0 |  |  | 0 |  | 0 |  |  | 0 | 0 | 0 |  |  | 0 |  | 35 |  | 0 |  |  | 0 |  | 0 |  |  | 0
[6 empty] | 0 |  |  |  |  | X | X | X | X | X | [15 empty] | 100000 | [6 empty] | " " | [11 empty] | 100000 | [15 empty] | 23 |  | 0 |  |  | 0 |  | 0 |  |  | 0 | [11 empty] | 35 |  | 0 |  |  | 0 |  | 0 |  |  | 0
[6 empty] | 0 |  |  |  |  | X | X | X | X | X |  |  |  |  | zone 4 | 14319 | 1300 | 0 | 0 | 0.2 | 2863.8 | LED-FLD-134 LPW-5600 lm | 39 | 73.4308 | 1 | 100000 | 0 | 0 |  |  | 1 |  | " " | zone 4 | 14319 | 900 | 0 | 0 | 0.2 | 2863.8 | LED-FLD-134 LPW-5600 lm | 39 | 73.4308 | 1 | 100000 | 0 | 0 |  | 1 |  | 37802.16 |  |  | 9891.1246 | 0 | 28499.7128 | 1.6735 |  | 76192.9974 |  | 23 |  | 0 |  |  | 0 |  | 0 |  |  | 0 |  | 37802.16 |  |  | 9891.1246 | 0 | 28499.7128 |  |  | 76192.9974 |  | 35 |  | 0 |  |  | 0 |  | 0 |  |  | 0
[6 empty] | 0 |  |  |  |  | X | X | X | X | X | [15 empty] | 100000 | [6 empty] | " " | [11 empty] | 100000 | [15 empty] | 23 |  | 18901.08 |  |  | 16320.3556 |  | 30108.6883 |  |  | 65330.1239 | [11 empty] | 35 |  | 18901.08 |  |  | 16320.3556 |  | 30108.6883 |  |  | 65330.1239
[6 empty] | 0 |  |  |  |  | X | X | X | X | X
[7 empty] | 0 |  |  |  | X | X | X | X | X |  |  |  | Standalone Retail | [18 empty] | Standalone Retail | [16 empty] | Standalone Retail | [10 empty] | Standalone Retail | [21 empty] | Standalone Retail | [9 empty] | Standalone Retail | 0 | 0
[7 empty] | 0 |  |  |  | X | X | X | X | X
[7 empty] | 0 |  |  |  | X | X | X | X | X |  |  |  | Zone 2 |  |  | 600 | 0 | 0 | [7 empty] | 0 | [8 empty] | 400 | 0 | 0
[7 empty] | 0 |  |  |  | X | X | X | X | X |  |  |  | Zone 3 |  |  | 750 | 0 | 0 | [16 empty] | 500 | 0 | 0
[7 empty] | 0 |  |  |  | X | X | X | X | X |  |  |  | Zone 4 |  |  | 1300 | 0 | 0 | [16 empty] | 900 | 0 | 0
[7 empty] | 0 |  |  |  | X | X | X | X | X |  |  |  | Area required per space |  | 325 | [16 empty] | Area required per space |  | 325
[7 empty] | 0 |  |  |  | X | X | X | X | X |  |  |  | # of Parking Spaces |  | 107.7446 | [16 empty] | # of Parking Spaces |  | 107.7446
[7 empty] | 0 |  |  |  | X | X | X | X | X |  |  |  | # of spaces per fixture |  | 20 | [16 empty] | # of spaces per fixture |  | 20
[7 empty] | 0 |  |  |  | X | X | X | X | X |  |  |  | # of Fixtures | 0 | 5.3872 | [16 empty] | # of Fixtures | 0 | 5.3872
[7 empty] | 0 |  |  |  | X | X | X | X | X |  |  |  | Parking |  | area, ft2 | [16 empty] | Parking |  | area, ft2
[7 empty] | 0 |  |  |  | X | X | X | X | X |  |  |  | includes lamp replacement | zone 2 | 35017 | 600 | 0 | 0 | 0.06 | 2101.02 | LED-PK-92 LPW-13000 lm | 141 | 14.9009 | 1 | 100000 | 7 | 30 | 193.6452 |  | 0.5 |  | includes lamp replacement | zone 2 | 35017 | 400 | 0 | 0 | 0.04 | 1400.68 | LED-PK-109 LPW-14500 lm | 134 | 10.4528 | 1 | 100000 | 5 | 30 | 374.6338 | 0.5 |  | 12192.0254 |  |  | 2771.4564 | 189.875 | 8842.2664 | 1.7137 |  | 23995.6232 |  | 23 |  | 0 |  |  | 0 |  | 0 |  |  | 0 |  | 10102.0071 |  |  | 1088.2849 | 135.625 | 6153.8495 |  |  | 17479.7665 |  | 35 |  | 0 |  |  | 0 |  | 0 |  |  | 0 | EXCLUDED
[7 empty] | 0 |  |  |  | X | X | X | X | X |  |  |  | ballast replacement | [11 empty] | 50000 | [6 empty] | ballast replacement | [11 empty] | 50000 | [15 empty] | 11 |  | 1158.5412 |  |  | 827.9472 |  | 1657.5128 |  |  | 3644.0011 | [11 empty] | 18 |  | 812.708 |  |  | 580.7988 |  | 1162.7328 |  |  | 2556.2396 |  | EXCLUDED
[7 empty] | 0 |  |  |  | X | X | X | X | X |  |  |  |  | zone 3 | 35017 | 750 | 0 | 0 | 0.1 | 3501.7 | LED-PK-92 LPW-13000 lm | 141 | 24.8348 | 1 | 100000 | 12 | 30 | 193.6452 |  | 0.5 |  |  | zone 3 | 35017 | 500 | 0 | 0 | 0.06 | 2101.02 | LED-PK-109 LPW-14500 lm | 134 | 15.6793 | 1 | 100000 | 8 | 30 | 361.2172 | 0.5 |  | 20535.5137 |  |  | 4573.1357 | 325.5 | 14803.3568 | 1.7181 |  | 40237.5061 |  | 23 |  | 0 |  |  | 0 |  | 0 |  |  | 0 |  | 15472.7799 |  |  | 1594.7867 | 217 | 9358.6365 |  |  | 26643.2031 |  | 35 |  | 0 |  |  | 0 |  | 0 |  |  | 0 | EXCLUDED
[7 empty] | 0 |  |  |  | X | X | X | X | X | [15 empty] | 50000 | [18 empty] | 50000 | [15 empty] | 11 |  | 1930.902 |  |  | 1379.9119 |  | 2762.5213 |  |  | 6073.3351 | [11 empty] | 18 |  | 1219.062 |  |  | 871.1981 |  | 1744.0992 |  |  | 3834.3594 |  | EXCLUDED
[7 empty] | 0 |  |  |  | X | X | X | X | X |  |  |  |  | zone 4 | 35017 | 1300 | 0 | 0 | 0.13 | 4552.21 | LED-PK-92 LPW-13000 lm | 141 | 32.2852 | 1 | 100000 | 16 | 30 | 193.6452 |  | 0 |  |  | zone 4 | 35017 | 900 | 0 | 0 | 0.08 | 2801.36 | LED-PK-109 LPW-14500 lm | 134 | 20.9057 | 1 | 100000 | 10 | 30 | 0 | 0 |  | 0 |  |  | 0 | 0 | 0 |  |  | 0 |  | 23 |  | 0 |  |  | 0 |  | 0 |  |  | 0 |  | 0 |  |  | 0 | 0 | 0 |  |  | 0 |  | 35 |  | 0 |  |  | 0 |  | 0 |  |  | 0
[7 empty] | 0 |  |  |  | X | X | X | X | X | [15 empty] | 50000 | [18 empty] | 50000 | [15 empty] | 11 |  | 0 |  |  | 0 |  | 0 |  |  | 0 | [11 empty] | 18 |  | 0 |  |  | 0 |  | 0 |  |  | 0
[7 empty] | 0 |  |  |  | X | X | X | X | X
[7 empty] | 0 |  |  |  | X | X | X | X | X |  |  |  | Doors |  | linear feet, ft | [16 empty] | Doors |  | linear feet, ft
[7 empty] | 0 |  |  |  | X | X | X | X | X |  |  |  | includes lamp replacement | zone 2 | 7.4085 | 600 | 0 | 0 | 20 | 148.17 | LED-Wall-85 LPW-2300 lm | 26 | 5.6988 | 1 | 100000 | 0 | 0 |  |  | 0.5 |  | includes lamp replacement | zone 2 | 7.4085 | 400 | 0 | 0 | 14 | 103.719 | LED-Wall-101 LPW-2800 lm | 28 | 3.7043 | 1 | 100000 | 0 | 0 |  | 0.5 |  | 1786.5883 |  |  | 191.9086 | 0 | 1080.8893 | 1.8304 |  | 3059.3862 |  | 23 |  | 0 |  |  | 0 |  | 0 |  |  | 0 |  | 1252.0365 |  |  | 62.3703 | 0 | 687.8547 |  |  | 2002.2615 |  | 35 |  | 0 |  |  | 0 |  | 0 |  |  | 0 | EXCLUDED
[7 empty] | 0 |  |  |  | X | X | X | X | X |  |  |  | ballast replacement | [11 empty] | 100000 | [6 empty] | ballast replacement | [11 empty] | 100000 | [15 empty] | 23 |  | 893.2941 |  |  | 316.6493 |  | 927.1935 |  |  | 2137.1369 | [11 empty] | 35 |  | 626.0182 |  |  | 205.822 |  | 632.2354 |  |  | 1464.0757 |  | EXCLUDED
[7 empty] | 0 |  |  |  | X | X | X | X | X |  |  |  | Other Doors - includes lamp replacement | zone 2 | 21.6921 | 750 | 0 | 0 | 20 | 433.8418 | LED-Wall-85 LPW-2300 lm | 26 | 16.6862 | 1 | 100000 | 0 | 0 |  |  | 0.5 |  | Other Doors - includes lamp replacement | zone 2 | 21.6921 | 500 | 0 | 0 | 14 | 303.6892 | LED-Wall-101 LPW-2800 lm | 28 | 10.846 | 1 | 100000 | 0 | 0 |  | 0.5 |  | 5231.1305 |  |  | 561.9085 | 0 | 3164.844 | 1.8304 |  | 8957.8829 |  | 23 |  | 0 |  |  | 0 |  | 0 |  |  | 0 |  | 3665.9629 |  |  | 182.6203 | 0 | 2014.0385 |  |  | 5862.6216 |  | 35 |  | 0 |  |  | 0 |  | 0 |  |  | 0 | EXCLUDED
[7 empty] | 0 |  |  |  | X | X | X | X | X |  |  |  | ballast replacement | [11 empty] | 100000 | [6 empty] | ballast replacement | [11 empty] | 100000 | [15 empty] | 23 |  | 2615.5652 |  |  | 927.149 |  | 2714.8225 |  |  | 6257.5368 | [11 empty] | 35 |  | 1832.9814 |  |  | 602.6469 |  | 1851.1852 |  |  | 4286.8135 |  | EXCLUDED
[7 empty] | 0 |  |  |  | X | X | X | X | X |  |  |  | Rool-up Door includes lamp replacement | zone 2 | 45.4388 | 1300 | 0 | 0 | 20 | 908.776 | LED-Wall-85 LPW-2300 lm | 26 | 34.9529 | 1 | 100000 | 0 | 0 |  |  | 0.5 |  | Rool-up Door includes lamp replacement | zone 2 | 45.4388 | 900 | 0 | 0 | 14 | 636.1432 | LED-Wall-101 LPW-2800 lm | 28 | 22.7194 | 1 | 100000 | 0 | 0 |  | 0.5 |  | 10957.7414 |  |  | 1177.0397 | 0 | 6629.4546 | 1.8304 |  | 18764.2356 |  | 23 |  | 0 |  |  | 0 |  | 0 |  |  | 0 |  | 7679.1572 |  |  | 382.5379 | 0 | 4218.842 |  |  | 12280.5371 |  | 35 |  | 0 |  |  | 0 |  | 0 |  |  | 0 | EXCLUDED
[7 empty] | 0 |  |  |  | X | X | X | X | X |  |  |  | ballast replacement | [11 empty] | 100000 | [6 empty] | ballast replacement | [11 empty] | 100000 | [15 empty] | 23 |  | 5478.8707 |  |  | 1942.1155 |  | 5686.7867 |  |  | 13107.7728 | [11 empty] | 35 |  | 3839.5786 |  |  | 1262.3751 |  | 3877.7103 |  |  | 8979.664 |  | EXCLUDED
[7 empty] | 0 |  |  |  | X | X | X | X | X | [10 empty] | 1490.7878 | [18 empty] | 1043.5514
[7 empty] | 0 |  |  |  | X | X | X | X | X |  |  |  | includes lamp replacement | zone 3 | 7.4085 | 750 | 0 | 0 | 30 | 222.255 | LED-Wall-85 LPW-2300 lm | 26 | 8.5483 | 1 | 100000 | 0 | 0 |  |  | 0.5 |  | " " | zone 3 | 7.4085 | 500 | 0 | 0 | 21 | 155.5785 | LED-Wall-101 LPW-2800 lm | 28 | 5.5564 | 1 | 100000 | 0 | 0 |  | 0.5 |  | 2679.8824 |  |  | 287.863 | 0 | 1621.334 | 1.8304 |  | 4589.0794 |  | 23 |  | 0 |  |  | 0 |  | 0 |  |  | 0 |  | 1878.0548 |  |  | 93.5555 | 0 | 1031.782 |  |  | 3003.3922 |  | 35 |  | 0 |  |  | 0 |  | 0 |  |  | 0 | EXCLUDED
[7 empty] | 0 |  |  |  | X | X | X | X | X |  |  |  | ballast replacement | [11 empty] | 100000 | [6 empty] | " " | [11 empty] | 100000 | [15 empty] | 23 |  | 1339.9412 |  |  | 474.9739 |  | 1390.7902 |  |  | 3205.7053 | [11 empty] | 35 |  | 939.0274 |  |  | 308.733 |  | 948.3531 |  |  | 2196.1135 |  | EXCLUDED
[7 empty] | 0 |  |  |  | X | X | X | X | X |  |  |  | Other Doors - includes lamp replacement | Zone 3 | 21.6921 | 600 | 0 | 0 | 30 | 650.7626 | LED-Wall-85 LPW-2300 lm | 26 | 25.0293 | 1 | 100000 | 0 | 0 |  |  | 0.5 |  | Other Doors - includes lamp replacement | Zone 3 | 21.6921 | 400 | 0 | 0 | 21 | 455.5338 | LED-Wall-101 LPW-2800 lm | 28 | 16.2691 | 1 | 100000 | 0 | 0 |  | 0.5 |  | 7846.6957 |  |  | 842.8628 | 0 | 4747.2659 | 1.8304 |  | 13436.8244 |  | 23 |  | 0 |  |  | 0 |  | 0 |  |  | 0 |  | 5498.9443 |  |  | 273.9304 | 0 | 3021.0577 |  |  | 8793.9324 |  | 35 |  | 0 |  |  | 0 |  | 0 |  |  | 0 | EXCLUDED
[7 empty] | 0 |  |  |  | X | X | X | X | X |  |  |  | ballast replacement | [11 empty] | 100000 | [6 empty] | ballast replacement | [11 empty] | 100000 | [15 empty] | 23 |  | 3923.3478 |  |  | 1390.7236 |  | 4072.2338 |  |  | 9386.3052 | [11 empty] | 35 |  | 2749.4722 |  |  | 903.9703 |  | 2776.7778 |  |  | 6430.2203 |  | EXCLUDED
[7 empty] | 0 |  |  |  | X | X | X | X | X |  |  |  | Rool-up Door includes lamp replacement | Zone 3 | 45.4388 | 750 | 0 | 0 | 20 | 908.776 | LED-Wall-85 LPW-2300 lm | 26 | 34.9529 | 1 | 100000 | 0 | 0 |  |  | 0.5 |  | Rool-up Door includes lamp replacement | Zone 3 | 45.4388 | 500 | 0 | 0 | 21 | 954.2148 | LED-Wall-101 LPW-2800 lm | 28 | 34.0791 | 1 | 100000 | 0 | 0 |  | 0.5 |  | 10957.7414 |  |  | 1177.0397 | 0 | 6629.4546 | 1.8304 |  | 18764.2356 |  | 23 |  | 0 |  |  | 0 |  | 0 |  |  | 0 |  | 11518.7358 |  |  | 573.8068 | 0 | 6328.2629 |  |  | 18420.8056 |  | 35 |  | 0 |  |  | 0 |  | 0 |  |  | 0 | EXCLUDED
[7 empty] | 0 |  |  |  | X | X | X | X | X |  |  |  | ballast replacement | [11 empty] | 100000 | [6 empty] | ballast replacement | [11 empty] | 100000 | [15 empty] | 23 |  | 5478.8707 |  |  | 1942.1155 |  | 5686.7867 |  |  | 13107.7728 | [11 empty] | 35 |  | 5759.3679 |  |  | 1893.5626 |  | 5816.5655 |  |  | 13469.496 |  | EXCLUDED
[7 empty] | 0 |  |  |  | X | X | X | X | X | [10 empty] | 1781.7936 | [18 empty] | 1565.3271
[7 empty] | 0 |  |  |  | X | X | X | X | X |  |  |  | includes lamp replacement | zone 4 | 7.4085 | 1300 | 0 | 0 | 30 | 222.255 | LED-Wall-85 LPW-2300 lm | 26 | 8.5483 | 1 | 100000 | 0 | 0 |  |  | 0 |  | " " | zone 4 | 7.4085 | 900 | 0 | 0 | 21 | 155.5785 | LED-Wall-101 LPW-2800 lm | 28 | 5.5564 | 1 | 100000 | 0 | 0 |  | 0 |  | 0 |  |  | 0 | 0 | 0 |  |  | 0 |  | 23 |  | 0 |  |  | 0 |  | 0 |  |  | 0 |  | 0 |  |  | 0 | 0 | 0 |  |  | 0 |  | 35 |  | 0 |  |  | 0 |  | 0 |  |  | 0
[7 empty] | 0 |  |  |  | X | X | X | X | X |  |  |  | ballast replacement | [11 empty] | 100000 | [6 empty] | " " | [11 empty] | 100000 | [15 empty] | 23 |  | 0 |  |  | 0 |  | 0 |  |  | 0 | [11 empty] | 35 |  | 0 |  |  | 0 |  | 0 |  |  | 0
[7 empty] | 0 |  |  |  | X | X | X | X | X |  |  |  | Other Doors - includes lamp replacement | Zone 4 | 21.6921 | 750 | 0 | 0 | 30 | 650.7626 | LED-Wall-85 LPW-2300 lm | 26 | 25.0293 | 1 | 100000 | 0 | 0 |  |  | 0 |  | Other Doors - includes lamp replacement | Zone 4 | 21.6921 | 500 | 0 | 0 | 21 | 455.5338 | LED-Wall-101 LPW-2800 lm | 28 | 16.2691 | 1 | 100000 | 0 | 0 |  | 0 |  | 0 |  |  | 0 | 0 | 0 |  |  | 0 |  | 23 |  | 0 |  |  | 0 |  | 0 |  |  | 0 |  | 0 |  |  | 0 | 0 | 0 |  |  | 0 |  | 35 |  | 0 |  |  | 0 |  | 0 |  |  | 0
[7 empty] | 0 |  |  |  | X | X | X | X | X |  |  |  | ballast replacement | [11 empty] | 100000 | [6 empty] | ballast replacement | [11 empty] | 100000 | [15 empty] | 23 |  | 0 |  |  | 0 |  | 0 |  |  | 0 | [11 empty] | 35 |  | 0 |  |  | 0 |  | 0 |  |  | 0
[7 empty] | 0 |  |  |  | X | X | X | X | X |  |  |  | Rool-up Door includes lamp replacement | Zone 4 | 45.4388 | 600 | 0 | 0 | 20 | 908.776 | LED-Wall-85 LPW-2300 lm | 26 | 34.9529 | 1 | 100000 | 0 | 0 |  |  | 0 |  | Rool-up Door includes lamp replacement | Zone 4 | 45.4388 | 400 | 0 | 0 | 21 | 954.2148 | LED-Wall-101 LPW-2800 lm | 28 | 34.0791 | 1 | 100000 | 0 | 0 |  | 0 |  | 0 |  |  | 0 | 0 | 0 |  |  | 0 |  | 23 |  | 0 |  |  | 0 |  | 0 |  |  | 0 |  | 0 |  |  | 0 | 0 | 0 |  |  | 0 |  | 35 |  | 0 |  |  | 0 |  | 0 |  |  | 0
[7 empty] | 0 |  |  |  | X | X | X | X | X |  |  |  | ballast replacement | [11 empty] | 100000 | [6 empty] | ballast replacement | [11 empty] | 100000 | [15 empty] | 23 |  | 0 |  |  | 0 |  | 0 |  |  | 0 | [11 empty] | 35 |  | 0 |  |  | 0 |  | 0 |  |  | 0
[7 empty] | 0 |  |  |  | X | X | X | X | X | [10 empty] | 1781.7936 | [18 empty] | 1565.3271
[7 empty] | 0 |  |  |  | X | X | X | X | X
[7 empty] | 0 |  |  |  | X | X | X | X | X |  |  |  | Façade |  | area, ft2 | [16 empty] | Façade |  | area, ft2
[7 empty] | 0 |  |  |  | X | X | X | X | X |  |  |  | includes lamp replacement | zone 2 | 964 | 600 | 0 | 0 | 0.1 | 96.4 | LED-Flood-104 LPD-2600 lm | 25 | 3.856 | 1 | 100000 | 0 | 0 |  |  | 0.5 |  | includes lamp replacement | zone 2 | 964 | 400 | 0 | 0 | 0.1 | 96.4 | LED-Flood-104 LPD-2600 lm | 25 | 3.856 | 1 | 100000 | 0 | 0 |  | 0.5 |  | 510.92 |  |  | 129.8508 | 0 | 381.4899 | 1.6797 |  | 1022.2607 |  | 23 |  | 0 |  |  | 0 |  | 0 |  |  | 0 |  | 510.92 |  |  | 64.9254 | 0 | 318.8052 |  |  | 894.6506 |  | 35 |  | 0 |  |  | 0 |  | 0 |  |  | 0 | EXCLUDED
[7 empty] | 0 |  |  |  | X | X | X | X | X |  |  |  | ballast replacement | [11 empty] | 100000 | [6 empty] | ballast replacement | [11 empty] | 100000 | [15 empty] | 23 |  | 255.46 |  |  | 214.2538 |  | 400.0398 |  |  | 869.7536 | [11 empty] | 35 |  | 255.46 |  |  | 214.2538 |  | 400.0398 |  |  | 869.7536
[7 empty] | 0 |  |  |  | X | X | X | X | X |  |  |  |  | zone 3 | 964 | 750 | 0 | 0 | 0.15 | 144.6 | LED-Flood-104 LPD-2600 lm | 25 | 5.784 | 1 | 100000 | 0 | 0 |  |  | 0.5 |  | " " | zone 3 | 964 | 500 | 0 | 0 | 0.15 | 144.6 | LED-Flood-104 LPD-2600 lm | 25 | 5.784 | 1 | 100000 | 0 | 0 |  | 0.5 |  | 766.38 |  |  | 194.7762 | 0 | 572.2349 | 1.6797 |  | 1533.3911 |  | 23 |  | 0 |  |  | 0 |  | 0 |  |  | 0 |  | 766.38 |  |  | 97.3881 | 0 | 478.2078 |  |  | 1341.9759 |  | 35 |  | 0 |  |  | 0 |  | 0 |  |  | 0 | EXCLUDED
[7 empty] | 0 |  |  |  | X | X | X | X | X | [15 empty] | 100000 | [6 empty] | " " | [11 empty] | 100000 | [15 empty] | 23 |  | 383.19 |  |  | 321.3807 |  | 600.0597 |  |  | 1304.6304 | [11 empty] | 35 |  | 383.19 |  |  | 321.3807 |  | 600.0597 |  |  | 1304.6304
[7 empty] | 0 |  |  |  | X | X | X | X | X |  |  |  |  | zone 4 | 964 | 1300 | 0 | 0 | 0.2 | 192.8 | LED-Flood-104 LPD-2600 lm | 25 | 7.712 | 1 | 100000 | 0 | 0 |  |  | 0 |  | " " | zone 4 | 964 | 900 | 0 | 0 | 0.2 | 192.8 | LED-Flood-104 LPD-2600 lm | 25 | 7.712 | 1 | 100000 | 0 | 0 |  | 0 |  | 0 |  |  | 0 | 0 | 0 |  |  | 0 |  | 23 |  | 0 |  |  | 0 |  | 0 |  |  | 0 |  | 0 |  |  | 0 | 0 | 0 |  |  | 0 |  | 35 |  | 0 |  |  | 0 |  | 0 |  |  | 0
[7 empty] | 0 |  |  |  | X | X | X | X | X | [15 empty] | 100000 | [6 empty] | " " | [11 empty] | 100000 | [15 empty] | 23 |  | 0 |  |  | 0 |  | 0 |  |  | 0 | [11 empty] | 35 |  | 0 |  |  | 0 |  | 0 |  |  | 0
[7 empty] | 0 |  |  |  | X | X | X | X | X
[8 empty] | 0 |  |  | X | X | X | X | X |  |  |  | Primary School | [18 empty] | Primary School | [16 empty] | Primary School | [10 empty] | Primary School | [10 empty] | Primary School | [10 empty] | Primary School | [9 empty] | Primary School | 0 | 0
[8 empty] | 0 |  |  | X | X | X | X | X
[8 empty] | 0 |  |  | X | X | X | X | X | [6 empty] | 600 | 0 | 0 | [7 empty] | 0 |  |  |  | 1 |  |  |  |  | 400 | 0 | 0
[8 empty] | 0 |  |  | X | X | X | X | X | [6 empty] | 750 | 0 | 0 | [16 empty] | 500 | 0 | 0
[8 empty] | 0 |  |  | X | X | X | X | X | [6 empty] | 1300 | 0 | 0 | [16 empty] | 900 | 0 | 0
[8 empty] | 0 |  |  | X | X | X | X | X |  |  |  | Area required per space |  | 325 | [16 empty] | Area required per space |  | 325
[8 empty] | 0 |  |  | X | X | X | X | X |  |  |  | # of Parking Spaces |  | 45.2862 | [16 empty] | # of Parking Spaces |  | 45.2862
[8 empty] | 0 |  |  | X | X | X | X | X |  |  |  | # of spaces per fixture |  | 20 | [16 empty] | # of spaces per fixture |  | 20
[8 empty] | 0 |  |  | X | X | X | X | X |  |  |  | # of Fixtures | 0 | 2.2643 | [16 empty] | # of Fixtures | 0 | 2.2643
[8 empty] | 0 |  |  | X | X | X | X | X |  |  |  | Parking |  | area, ft2 | [16 empty] | Parking |  | area, ft2 | [32 empty] | 0
[8 empty] | 0 |  |  | X | X | X | X | X |  |  |  | includes lamp replacement | zone 2 | 14718 | 600 | 0 | 0 | 0.06 | 883.08 | LED-PK-85 LPW-6600 lm | 73 | 12.097 | 1 | 100000 | 6 | 21 | 168.9465 |  | 1 |  | includes lamp replacement | zone 2 | 14718 | 400 | 0 | 0 | 0.04 | 588.72 | LED-PK-91 LPW-5600 lm | 59 | 9.9783 | 1 | 100000 | 5 | 21 | 277.555 | 1 |  | 14992.9061 |  |  | 4964.9652 | 293.1 | 12393.863 | 1.634 |  | 32644.8343 |  | 23 |  | 0 |  |  | 0 |  | 0 |  |  | 0 |  | 11997.7083 |  |  | 3893.2079 | 244.25 | 9843.5543 |  |  | 25978.7204 |  | 35 |  | 0 |  |  | 0 |  | 0 |  |  | 0 | EXCLUDED
[8 empty] | 0 |  |  | X | X | X | X | X |  |  |  | ballast replacement | [11 empty] | 100000 | [6 empty] | ballast replacement | [11 empty] | 50000 | [15 empty] | 23 |  | 3556.514 |  |  | 3983.1841 |  | 6660.1513 |  |  | 14199.8494 | [11 empty] | 18 |  | 1551.6264 |  |  | 1108.8641 |  | 2219.8957 |  |  | 4880.3863 |  | EXCLUDED
[8 empty] | 0 |  |  | X | X | X | X | X |  |  |  |  | zone 3 | 14718 | 750 | 0 | 0 | 0.1 | 1471.8 | LED-PK-85 LPW-6600 lm | 73 | 20.1616 | 1 | 100000 | 10 | 21 | 168.9465 |  | 0 |  | " " | zone 3 | 14718 | 500 | 0 | 0 | 0.06 | 883.08 | LED-PK-91 LPW-5600 lm | 59 | 14.9675 | 1 | 100000 | 7 | 21 | 0 | 0 |  | 0 |  |  | 0 | 0 | 0 |  |  | 0 |  | 23 |  | 0 |  |  | 0 |  | 0 |  |  | 0 |  | 0 |  |  | 0 | 0 | 0 |  |  | 0 |  | 35 |  | 0 |  |  | 0 |  | 0 |  |  | 0
[8 empty] | 0 |  |  | X | X | X | X | X | [15 empty] | 100000 | [6 empty] | " " | [11 empty] | 50000 | [15 empty] | 23 |  | 0 |  |  | 0 |  | 0 |  |  | 0 | [11 empty] | 18 |  | 0 |  |  | 0 |  | 0 |  |  | 0
[8 empty] | 0 |  |  | X | X | X | X | X |  |  |  |  | zone 4 | 14718 | 1300 | 0 | 0 | 0.13 | 1913.34 | LED-PK-85 LPW-6600 lm | 73 | 26.2101 | 1 | 100000 | 13 | 21 | 168.9465 |  | 0 |  | " " | zone 4 | 14718 | 900 | 0 | 0 | 0.08 | 1177.44 | LED-PK-91 LPW-5600 lm | 59 | 19.9566 | 1 | 100000 | 10 | 21 | 0 | 0 |  | 0 |  |  | 0 | 0 | 0 |  |  | 0 |  | 23 |  | 0 |  |  | 0 |  | 0 |  |  | 0 |  | 0 |  |  | 0 | 0 | 0 |  |  | 0 |  | 35 |  | 0 |  |  | 0 |  | 0 |  |  | 0
[8 empty] | 0 |  |  | X | X | X | X | X | [15 empty] | 100000 | [6 empty] | " " | [11 empty] | 50000 | [15 empty] | 23 |  | 0 |  |  | 0 |  | 0 |  |  | 0 | [11 empty] | 18 |  | 0 |  |  | 0 |  | 0 |  |  | 0
[8 empty] | 0 |  |  | X | X | X | X | X
[8 empty] | 0 |  |  | X | X | X | X | X |  |  |  | Doors |  | linear feet, ft | [16 empty] | Doors |  | linear feet, ft
[8 empty] | 0 |  |  | X | X | X | X | X |  |  |  | Main Door includes lamp replacement | zone 2 | 44.376 | 600 | 0 | 0 | 20 | 887.52 | LED-Wall-85 LPW-2300 lm | 26 | 34.1354 | 1 | 100000 | 0 | 0 |  |  | 1 |  | Main Door includes lamp replacement | zone 2 | 44.376 | 400 | 0 | 0 | 14 | 621.264 | LED-Wall-101 LPW-2800 lm | 28 | 22.188 | 1 | 100000 | 0 | 0 |  | 1 |  | 21402.8862 |  |  | 2299.0182 | 0 | 12948.7872 | 1.8304 |  | 36650.6915 |  | 23 |  | 0 |  |  | 0 |  | 0 |  |  | 0 |  | 14999.088 |  |  | 1494.3618 | 0 | 8961.7232 |  |  | 25455.173 |  | 35 |  | 0 |  |  | 0 |  | 0 |  |  | 0 | EXCLUDED
[8 empty] | 0 |  |  | X | X | X | X | X |  |  |  | ballast replacement | [11 empty] | 100000 | [6 empty] | ballast replacement | [27 empty] | 23 |  | 10701.4431 |  |  | 3793.38 |  | 11107.5489 |  |  | 25602.3719 | [11 empty] | 0 |  | 7499.544 |  |  | 2465.697 |  | 7574.0237 |  |  | 17539.2647 |  | EXCLUDED
[8 empty] | 0 |  |  | X | X | X | X | X |  |  |  | Other Doors - includes lamp replacement | zone 2 | 73.1538 | 750 | 0 | 0 | 20 | 1463.0767 | LED-Wall-85 LPW-2300 lm | 26 | 56.2722 | 1 | 100000 | 0 | 0 |  |  | 0 |  | Other Doors - includes lamp replacement | zone 2 | 73.1538 | 500 | 0 | 0 | 14 | 1024.1537 | LED-Wall-101 LPW-2800 lm | 28 | 36.5769 | 1 | 100000 | 0 | 0 |  | 0 |  | 0 |  |  | 0 | 0 | 0 |  |  | 0 |  | 23 |  | 0 |  |  | 0 |  | 0 |  |  | 0 |  | 0 |  |  | 0 | 0 | 0 |  |  | 0 |  | 35 |  | 0 |  |  | 0 |  | 0 |  |  | 0
[8 empty] | 0 |  |  | X | X | X | X | X |  |  |  | ballast replacement | [11 empty] | 100000 | [6 empty] | ballast replacement | [11 empty] | 100000 | [15 empty] | 23 |  | 0 |  |  | 0 |  | 0 |  |  | 0 | [11 empty] | 35 |  | 0 |  |  | 0 |  | 0 |  |  | 0
[8 empty] | 0 |  |  | X | X | X | X | X |  |  |  | Rool-up Door includes lamp replacement | zone 2 | 5.473 | 1300 | 0 | 0 | 20 | 109.4608 | LED-Wall-85 LPW-2300 lm | 26 | 4.21 | 1 | 100000 | 0 | 0 |  |  | 0 |  | Rool-up Door includes lamp replacement | zone 2 | 5.473 | 900 | 0 | 0 | 14 | 76.6226 | LED-Wall-101 LPW-2800 lm | 28 | 2.7365 | 1 | 100000 | 0 | 0 |  | 0 |  | 0 |  |  | 0 | 0 | 0 |  |  | 0 |  | 23 |  | 0 |  |  | 0 |  | 0 |  |  | 0 |  | 0 |  |  | 0 | 0 | 0 |  |  | 0 |  | 35 |  | 0 |  |  | 0 |  | 0 |  |  | 0
[8 empty] | 0 |  |  | X | X | X | X | X |  |  |  | ballast replacement | [11 empty] | 100000 | [6 empty] | ballast replacement | [11 empty] | 100000 | [15 empty] | 23 |  | 0 |  |  | 0 |  | 0 |  |  | 0 | [11 empty] | 35 |  | 0 |  |  | 0 |  | 0 |  |  | 0
[8 empty] | 0 |  |  | X | X | X | X | X | [10 empty] | 2460.0575 | [18 empty] | 1722.0403
[8 empty] | 0 |  |  | X | X | X | X | X |  |  |  | Main Door includes lamp replacement | zone 3 | 44.376 | 750 | 0 | 0 | 30 | 1331.28 | LED-Wall-85 LPW-2300 lm | 26 | 51.2031 | 1 | 100000 | 0 | 0 |  |  | 0 |  | Main Door includes lamp replacement | zone 3 | 44.376 | 500 | 0 | 0 | 21 | 931.896 | LED-Wall-101 LPW-2800 lm | 28 | 33.282 | 1 | 100000 | 0 | 0 |  | 0 |  | 0 |  |  | 0 | 0 | 0 |  |  | 0 |  | 23 |  | 0 |  |  | 0 |  | 0 |  |  | 0 |  | 0 |  |  | 0 | 0 | 0 |  |  | 0 |  | 35 |  | 0 |  |  | 0 |  | 0 |  |  | 0
[8 empty] | 0 |  |  | X | X | X | X | X |  |  |  | ballast replacement | [18 empty] | ballast replacement | [11 empty] | 100000 | [15 empty] | 0 |  | 0 |  |  | 0 |  | 0 |  |  | 0 | [11 empty] | 35 |  | 0 |  |  | 0 |  | 0 |  |  | 0
[8 empty] | 0 |  |  | X | X | X | X | X |  |  |  | Other Doors - includes lamp replacement | Zone 3 | 73.1538 | 600 | 0 | 0 | 30 | 2194.6151 | LED-Wall-85 LPW-2300 lm | 26 | 84.4083 | 1 | 100000 | 0 | 0 |  |  | 0 |  | Other Doors - includes lamp replacement | Zone 3 | 73.1538 | 400 | 0 | 0 | 21 | 1536.2306 | LED-Wall-101 LPW-2800 lm | 28 | 54.8654 | 1 | 100000 | 0 | 0 |  | 0 |  | 0 |  |  | 0 | 0 | 0 |  |  | 0 |  | 23 |  | 0 |  |  | 0 |  | 0 |  |  | 0 |  | 0 |  |  | 0 | 0 | 0 |  |  | 0 |  | 35 |  | 0 |  |  | 0 |  | 0 |  |  | 0
[8 empty] | 0 |  |  | X | X | X | X | X |  |  |  | ballast replacement | [11 empty] | 100000 | [6 empty] | ballast replacement | [11 empty] | 100000 | [15 empty] | 23 |  | 0 |  |  | 0 |  | 0 |  |  | 0 | [11 empty] | 35 |  | 0 |  |  | 0 |  | 0 |  |  | 0
[8 empty] | 0 |  |  | X | X | X | X | X |  |  |  | Rool-up Door includes lamp replacement | Zone 3 | 5.473 | 750 | 0 | 0 | 20 | 109.4608 | LED-Wall-85 LPW-2300 lm | 26 | 4.21 | 1 | 100000 | 0 | 0 |  |  | 0 |  | Rool-up Door includes lamp replacement | Zone 3 | 5.473 | 500 | 0 | 0 | 21 | 114.9338 | LED-Wall-101 LPW-2800 lm | 28 | 4.1048 | 1 | 100000 | 0 | 0 |  | 0 |  | 0 |  |  | 0 | 0 | 0 |  |  | 0 |  | 23 |  | 0 |  |  | 0 |  | 0 |  |  | 0 |  | 0 |  |  | 0 | 0 | 0 |  |  | 0 |  | 35 |  | 0 |  |  | 0 |  | 0 |  |  | 0
[8 empty] | 0 |  |  | X | X | X | X | X |  |  |  | ballast replacement | [11 empty] | 100000 | [6 empty] | ballast replacement | [11 empty] | 100000 | [15 empty] | 23 |  | 0 |  |  | 0 |  | 0 |  |  | 0 | [11 empty] | 35 |  | 0 |  |  | 0 |  | 0 |  |  | 0
[8 empty] | 0 |  |  | X | X | X | X | X | [10 empty] | 3635.3559 | [18 empty] | 2583.0604
[8 empty] | 0 |  |  | X | X | X | X | X |  |  |  | Main Door includes lamp replacement | zone 4 | 44.376 | 1300 | 0 | 0 | 30 | 1331.28 | LED-Wall-85 LPW-2300 lm | 26 | 51.2031 | 1 | 100000 | 0 | 0 |  |  | 0 |  | Main Door includes lamp replacement | zone 4 | 44.376 | 900 | 0 | 0 | 21 | 931.896 | LED-Wall-101 LPW-2800 lm | 28 | 33.282 | 1 | 100000 | 0 | 0 |  | 0 |  | 0 |  |  | 0 | 0 | 0 |  |  | 0 |  | 23 |  | 0 |  |  | 0 |  | 0 |  |  | 0 |  | 0 |  |  | 0 | 0 | 0 |  |  | 0 |  | 35 |  | 0 |  |  | 0 |  | 0 |  |  | 0
[8 empty] | 0 |  |  | X | X | X | X | X |  |  |  | ballast replacement | [18 empty] | ballast replacement | [11 empty] | 100000 | [15 empty] | 0 |  | 0 |  |  | 0 |  | 0 |  |  | 0 | [11 empty] | 35 |  | 0 |  |  | 0 |  | 0 |  |  | 0
[8 empty] | 0 |  |  | X | X | X | X | X |  |  |  | Other Doors - includes lamp replacement | Zone 4 | 73.1538 | 750 | 0 | 0 | 30 | 2194.6151 | LED-Wall-85 LPW-2300 lm | 26 | 84.4083 | 1 | 100000 | 0 | 0 |  |  | 0 |  | Other Doors - includes lamp replacement | Zone 4 | 73.1538 | 500 | 0 | 0 | 21 | 1536.2306 | LED-Wall-101 LPW-2800 lm | 28 | 54.8654 | 1 | 100000 | 0 | 0 |  | 0 |  | 0 |  |  | 0 | 0 | 0 |  |  | 0 |  | 23 |  | 0 |  |  | 0 |  | 0 |  |  | 0 |  | 0 |  |  | 0 | 0 | 0 |  |  | 0 |  | 35 |  | 0 |  |  | 0 |  | 0 |  |  | 0
[8 empty] | 0 |  |  | X | X | X | X | X |  |  |  | ballast replacement | [11 empty] | 100000 | [6 empty] | ballast replacement | [11 empty] | 100000 | [15 empty] | 23 |  | 0 |  |  | 0 |  | 0 |  |  | 0 | [11 empty] | 35 |  | 0 |  |  | 0 |  | 0 |  |  | 0
[8 empty] | 0 |  |  | X | X | X | X | X |  |  |  | Rool-up Door includes lamp replacement | Zone 4 | 5.473 | 600 | 0 | 0 | 20 | 109.4608 | LED-Wall-85 LPW-2300 lm | 26 | 4.21 | 1 | 100000 | 0 | 0 |  |  | 0 |  | Rool-up Door includes lamp replacement | Zone 4 | 5.473 | 400 | 0 | 0 | 21 | 114.9338 | LED-Wall-101 LPW-2800 lm | 28 | 4.1048 | 1 | 100000 | 0 | 0 |  | 0 |  | 0 |  |  | 0 | 0 | 0 |  |  | 0 |  | 23 |  | 0 |  |  | 0 |  | 0 |  |  | 0 |  | 0 |  |  | 0 | 0 | 0 |  |  | 0 |  | 35 |  | 0 |  |  | 0 |  | 0 |  |  | 0
[8 empty] | 0 |  |  | X | X | X | X | X |  |  |  | ballast replacement | [11 empty] | 100000 | [6 empty] | ballast replacement | [11 empty] | 100000 | [15 empty] | 23 |  | 0 |  |  | 0 |  | 0 |  |  | 0 | [11 empty] | 35 |  | 0 |  |  | 0 |  | 0 |  |  | 0
[8 empty] | 0 |  |  | X | X | X | X | X | [10 empty] | 3635.3559 | [18 empty] | 2583.0604
[8 empty] | 0 |  |  | X | X | X | X | X
[8 empty] | 0 |  |  | X | X | X | X | X |  |  |  | Façade |  | area, ft2 | [16 empty] | Façade |  | area, ft2
[8 empty] | 0 |  |  | X | X | X | X | X |  |  |  | includes lamp replacement | zone 2 | 544 | 600 | 0 | 0 | 0.1 | 54.4 | LED-Flood-104 LPD-2600 lm | 25 | 2.176 | 1 | 100000 | 0 | 0 |  |  | 1 |  | includes lamp replacement | zone 2 | 544 | 400 | 0 | 0 | 0.1 | 54.4 | LED-Flood-104 LPD-2600 lm | 25 | 2.176 | 1 | 100000 | 0 | 0 |  | 1 |  | 576.64 |  |  | 146.5536 | 0 | 430.5612 | 1.6797 |  | 1153.7548 |  | 23 |  | 0 |  |  | 0 |  | 0 |  |  | 0 |  | 576.64 |  |  | 146.5536 | 0 | 430.5612 |  |  | 1153.7548 |  | 35 |  | 0 |  |  | 0 |  | 0 |  |  | 0
[8 empty] | 0 |  |  | X | X | X | X | X |  |  |  | ballast replacement | [11 empty] | 100000 | [6 empty] | ballast replacement | [11 empty] | 100000 | [15 empty] | 23 |  | 288.32 |  |  | 241.8134 |  | 451.4972 |  |  | 981.6306 | [11 empty] | 35 |  | 288.32 |  |  | 241.8134 |  | 451.4972 |  |  | 981.6306
[8 empty] | 0 |  |  | X | X | X | X | X |  |  |  |  | zone 3 | 544 | 750 | 0 | 0 | 0.15 | 81.6 | LED-Flood-104 LPD-2600 lm | 25 | 3.264 | 1 | 100000 | 0 | 0 |  |  | 0 |  | " " | zone 3 | 544 | 500 | 0 | 0 | 0.15 | 81.6 | LED-Flood-104 LPD-2600 lm | 25 | 3.264 | 1 | 100000 | 0 | 0 |  | 0 |  | 0 |  |  | 0 | 0 | 0 |  |  | 0 |  | 23 |  | 0 |  |  | 0 |  | 0 |  |  | 0 |  | 0 |  |  | 0 | 0 | 0 |  |  | 0 |  | 35 |  | 0 |  |  | 0 |  | 0 |  |  | 0
[8 empty] | 0 |  |  | X | X | X | X | X | [15 empty] | 100000 | [6 empty] | " " | [11 empty] | 100000 | [15 empty] | 23 |  | 0 |  |  | 0 |  | 0 |  |  | 0 | [11 empty] | 35 |  | 0 |  |  | 0 |  | 0 |  |  | 0
[8 empty] | 0 |  |  | X | X | X | X | X |  |  |  |  | zone 4 | 544 | 1300 | 0 | 0 | 0.2 | 108.8 | LED-Flood-104 LPD-2600 lm | 25 | 4.352 | 1 | 100000 | 0 | 0 |  |  | 0 |  | " " | zone 4 | 544 | 900 | 0 | 0 | 0.2 | 108.8 | LED-Flood-104 LPD-2600 lm | 25 | 4.352 | 1 | 100000 | 0 | 0 |  | 0 |  | 0 |  |  | 0 | 0 | 0 |  |  | 0 |  | 23 |  | 0 |  |  | 0 |  | 0 |  |  | 0 |  | 0 |  |  | 0 | 0 | 0 |  |  | 0 |  | 35 |  | 0 |  |  | 0 |  | 0 |  |  | 0
[8 empty] | 0 |  |  | X | X | X | X | X | [15 empty] | 100000 | [6 empty] | " " | [11 empty] | 100000 | [15 empty] | 23 |  | 0 |  |  | 0 |  | 0 |  |  | 0 | [11 empty] | 35 |  | 0 |  |  | 0 |  | 0 |  |  | 0
[8 empty] | 0 |  |  | X | X | X | X | X
[9 empty] | 0 |  | X | X | X | X | X |  |  |  | Small Hotel | [18 empty] | Small Hotel | [16 empty] | Small Hotel | [10 empty] | Small Hotel | [10 empty] | Small Hotel | [10 empty] | Small Hotel | [9 empty] | Small Hotel | 0 | 0
[9 empty] | 0 |  | X | X | X | X | X
[9 empty] | 0 |  | X | X | X | X | X | [6 empty] | 600 | 0 | 0 | [11 empty] | 1 |  |  |  |  | 400 | 0 | 0
[9 empty] | 0 |  | X | X | X | X | X | [6 empty] | 750 | 0 | 0 | [16 empty] | 500 | 0 | 0
[9 empty] | 0 |  | X | X | X | X | X | [6 empty] | 1300 | 0 | 0 | [16 empty] | 900 | 0 | 0
[9 empty] | 0 |  | X | X | X | X | X |  |  |  | Area required per space |  | 325 | [16 empty] | Area required per space |  | 325
[9 empty] | 0 |  | X | X | X | X | X |  |  |  | # of Parking Spaces |  | 103.68 | [16 empty] | # of Parking Spaces |  | 103.68
[9 empty] | 0 |  | X | X | X | X | X |  |  |  | # of spaces per fixture |  | 20 | [16 empty] | # of spaces per fixture |  | 20
[9 empty] | 0 |  | X | X | X | X | X |  |  |  | # of Fixtures | 0 | 5.184 | [16 empty] | # of Fixtures | 0 | 5.184
[9 empty] | 0 |  | X | X | X | X | X |  |  |  | Parking |  | area, ft2 | [16 empty] | Parking |  | area, ft2
[9 empty] | 0 |  | X | X | X | X | X |  |  |  | includes lamp replacement | zone 2 | 33696 | 600 | 0 | 0 | 0.06 | 2021.76 | LED-PK-92 LPW-13000 lm | 141 | 14 | 1 | 100000 | 7 | 30 | 885.3616 |  | 0.5 |  | includes lamp replacement | zone 2 | 33696 | 400 | 0 | 0 | 0.04 | 1347.84 | LED-PK-109 LPW-14500 lm | 134 | 10 | 1 | 100000 | 5 | 30 | 918.3803 | 0.5 |  | 12149.1504 |  |  | 3321.8102 | 189.875 | 9352.1335 | 1.6746 |  | 25012.969 |  | 23 |  | 0 |  |  | 0 |  | 0 |  |  | 0 |  | 10116.6644 |  |  | 1314.3364 | 135.625 | 6379.4471 |  |  | 17946.073 |  | 35 |  | 0 |  |  | 0 |  | 0 |  |  | 0 | EXCLUDED
[9 empty] | 0 |  | X | X | X | X | X |  |  |  | ballast replacement | [11 empty] | 50000 | [6 empty] | ballast replacement | [11 empty] | 50000 | [15 empty] | 11 |  | 1088.5 |  |  | 777.8925 |  | 1557.3056 |  |  | 3423.6981 | [11 empty] | 18 |  | 777.5 |  |  | 555.6375 |  | 1112.3611 |  |  | 2445.4986 |  | EXCLUDED
[9 empty] | 0 |  | X | X | X | X | X |  |  |  |  | zone 3 | 33696 | 750 | 0 | 0 | 0.1 | 3369.6 | LED-PK-92 LPW-13000 lm | 141 | 24 | 1 | 100000 | 12 | 30 | 885.3616 |  | 0.5 |  | " " | zone 3 | 33696 | 500 | 0 | 0 | 0.06 | 2021.76 | LED-PK-109 LPW-14500 lm | 134 | 15 | 1 | 100000 | 8 | 30 | 918.3803 | 0.5 |  | 20520.4004 |  |  | 5128.5327 | 325.5 | 15332.0097 | 1.6941 |  | 41306.4428 |  | 23 |  | 0 |  |  | 0 |  | 0 |  |  | 0 |  | 15369.4144 |  |  | 1818.2046 | 217 | 9522.5275 |  |  | 26927.1465 |  | 35 |  | 0 |  |  | 0 |  | 0 |  |  | 0 | EXCLUDED
[9 empty] | 0 |  | X | X | X | X | X | [15 empty] | 50000 | [6 empty] | " " | [11 empty] | 50000 | [15 empty] | 11 |  | 1866 |  |  | 1333.53 |  | 2669.6667 |  |  | 5869.1967 | [11 empty] | 18 |  | 1166.25 |  |  | 833.4562 |  | 1668.5417 |  |  | 3668.2479 |  | EXCLUDED
[9 empty] | 0 |  | X | X | X | X | X |  |  |  |  | zone 4 | 33696 | 1300 | 0 | 0 | 0.13 | 4380.48 | LED-PK-92 LPW-13000 lm | 141 | 31 | 1 | 100000 | 16 | 30 | 885.3616 |  | 0 |  | " " | zone 4 | 33696 | 900 | 0 | 0 | 0.08 | 2695.68 | LED-PK-109 LPW-14500 lm | 134 | 20 | 1 | 100000 | 10 | 30 | 918.3803 | 0 |  | 0 |  |  | 0 | 0 | 0 |  |  | 0 |  | 23 |  | 0 |  |  | 0 |  | 0 |  |  | 0 |  | 0 |  |  | 0 | 0 | 0 |  |  | 0 |  | 35 |  | 0 |  |  | 0 |  | 0 |  |  | 0
[9 empty] | 0 |  | X | X | X | X | X | [15 empty] | 50000 | [6 empty] | " " | [11 empty] | 50000 | [15 empty] | 11 |  | 0 |  |  | 0 |  | 0 |  |  | 0 | [11 empty] | 18 |  | 0 |  |  | 0 |  | 0 |  |  | 0
[9 empty] | 0 |  | X | X | X | X | X
[9 empty] | 0 |  | X | X | X | X | X |  |  |  | Doors |  | linear feet, ft | [16 empty] | Doors |  | linear feet, ft
[9 empty] | 0 |  | X | X | X | X | X |  |  |  | Main Door includes lamp replacement | zone 2 | 3.24 | 600 | 0 | 0 | 20 | 64.8 | LED-Wall-97 LPW-2700 lm | 28 | 2.3143 | 1 | 60000 | 0 | 0 |  |  | 0 |  | Main Door includes lamp replacement | zone 2 | 3.24 | 400 | 0 | 0 | 14 | 45.36 | LED-Wall-101 LPW-2800 lm | 28 | 1.62 | 1 | 100000 | 0 | 0 |  | 0 |  | 0 |  |  | 0 | 0 | 0 |  |  | 0 |  | 14 |  | 0 |  |  | 0 |  | 0 |  |  | 0 |  | 0 |  |  | 0 | 0 | 0 |  |  | 0 |  | 35 |  | 0 |  |  | 0 |  | 0 |  |  | 0
[9 empty] | 0 |  | X | X | X | X | X |  |  |  | ballast replacement | [11 empty] | 60000 | [6 empty] | ballast replacement | [11 empty] | 100000 | [15 empty] | 14 |  | 0 |  |  | 0 |  | 0 |  |  | 0 | [11 empty] | 35 |  | 0 |  |  | 0 |  | 0 |  |  | 0
[9 empty] | 0 |  | X | X | X | X | X |  |  |  | Other Doors - includes lamp replacement | zone 2 | 7.3418 | 600 | 0 | 0 | 20 | 146.8368 | LED-Wall-97 LPW-2700 lm | 28 | 5.2442 | 1 | 60000 | 0 | 0 |  |  | 0 |  | Other Doors - includes lamp replacement | zone 2 | 7.3418 | 500 | 0 | 0 | 14 | 102.7858 | LED-Wall-101 LPW-2800 lm | 28 | 3.6709 | 1 | 100000 | 0 | 0 |  | 0 |  | 0 |  |  | 0 | 0 | 0 |  |  | 0 |  | 14 |  | 0 |  |  | 0 |  | 0 |  |  | 0 |  | 0 |  |  | 0 | 0 | 0 |  |  | 0 |  | 35 |  | 0 |  |  | 0 |  | 0 |  |  | 0
[9 empty] | 0 |  | X | X | X | X | X |  |  |  | ballast replacement | [11 empty] | 60000 | [6 empty] | ballast replacement | [11 empty] | 100000 | [15 empty] | 14 |  | 0 |  |  | 0 |  | 0 |  |  | 0 | [11 empty] | 35 |  | 0 |  |  | 0 |  | 0 |  |  | 0
[9 empty] | 0 |  | X | X | X | X | X |  |  |  | Rool-up Door includes lamp replacement | zone 2 | 0.1404 | 600 | 0 | 0 | 20 | 2.808 | LED-Wall-97 LPW-2700 lm | 28 | 0.10029 | 1 | 60000 | 0 | 0 |  |  | 0 |  | Rool-up Door includes lamp replacement | zone 2 | 0.1404 | 900 | 0 | 0 | 14 | 1.9656 | LED-Wall-101 LPW-2800 lm | 28 | 0.0702 | 1 | 100000 | 0 | 0 |  | 0 |  | 0 |  |  | 0 | 0 | 0 |  |  | 0 |  | 14 |  | 0 |  |  | 0 |  | 0 |  |  | 0 |  | 0 |  |  | 0 | 0 | 0 |  |  | 0 |  | 35 |  | 0 |  |  | 0 |  | 0 |  |  | 0
[9 empty] | 0 |  | X | X | X | X | X |  |  |  | ballast replacement | [11 empty] | 60000 | [6 empty] | ballast replacement | [11 empty] | 100000 | [15 empty] | 14 |  | 0 |  |  | 0 |  | 0 |  |  | 0 | [11 empty] | 35 |  | 0 |  |  | 0 |  | 0 |  |  | 0
[9 empty] | 0 |  | X | X | X | X | X | [10 empty] | 214.4448 | [18 empty] | 150.1114
[9 empty] | 0 |  | X | X | X | X | X |  |  |  | Main Door includes lamp replacement | Zone 3 | 3.24 | 750 | 0 | 0 | 30 | 97.2 | LED-Wall-97 LPW-2700 lm | 28 | 3.4714 | 1 | 60000 | 0 | 0 |  |  | 0 |  | Main Door includes lamp replacement | Zone 3 | 3.24 | 0 | 0 | 0 | 21 | 68.04 | LED-Wall-101 LPW-2800 lm | 28 | 2.43 | 1 | 100000 | 0 | 0 |  | 0 |  | 0 |  |  | 0 | 0 | 0 |  |  | 0 |  | 14 |  | 0 |  |  | 0 |  | 0 |  |  | 0 |  | 0 |  |  | 0 | 0 | 0 |  |  | 0 |  | 35 |  | 0 |  |  | 0 |  | 0 |  |  | 0
[9 empty] | 0 |  | X | X | X | X | X |  |  |  | ballast replacement | [11 empty] | 60000 | [6 empty] | ballast replacement | [11 empty] | 100000 | [15 empty] | 14 |  | 0 |  |  | 0 |  | 0 |  |  | 0 | [11 empty] | 35 |  | 0 |  |  | 0 |  | 0 |  |  | 0
[9 empty] | 0 |  | X | X | X | X | X |  |  |  | Other Doors - includes lamp replacement | Zone 3 | 7.3418 | 750 | 0 | 0 | 30 | 220.2552 | LED-Wall-97 LPW-2700 lm | 28 | 7.8663 | 1 | 60000 | 0 | 0 |  |  | 0 |  | Other Doors - includes lamp replacement | Zone 3 | 7.3418 | 400 | 0 | 0 | 21 | 154.1786 | LED-Wall-101 LPW-2800 lm | 28 | 5.5064 | 1 | 100000 | 0 | 0 |  | 0 |  | 0 |  |  | 0 | 0 | 0 |  |  | 0 |  | 14 |  | 0 |  |  | 0 |  | 0 |  |  | 0 |  | 0 |  |  | 0 | 0 | 0 |  |  | 0 |  | 35 |  | 0 |  |  | 0 |  | 0 |  |  | 0
[9 empty] | 0 |  | X | X | X | X | X |  |  |  | ballast replacement | [11 empty] | 60000 | [6 empty] | ballast replacement | [11 empty] | 100000 | [15 empty] | 14 |  | 0 |  |  | 0 |  | 0 |  |  | 0 | [11 empty] | 35 |  | 0 |  |  | 0 |  | 0 |  |  | 0
[9 empty] | 0 |  | X | X | X | X | X |  |  |  | Rool-up Door includes lamp replacement | Zone 3 | 0.1404 | 750 | 0 | 0 | 20 | 2.808 | LED-Wall-97 LPW-2700 lm | 28 | 0.10029 | 1 | 60000 | 0 | 0 |  |  | 0 |  | Rool-up Door includes lamp replacement | Zone 3 | 0.1404 | 500 | 0 | 0 | 21 | 2.9484 | LED-Wall-101 LPW-2800 lm | 28 | 0.1053 | 1 | 100000 | 0 | 0 |  | 0 |  | 0 |  |  | 0 | 0 | 0 |  |  | 0 |  | 14 |  | 0 |  |  | 0 |  | 0 |  |  | 0 |  | 0 |  |  | 0 | 0 | 0 |  |  | 0 |  | 35 |  | 0 |  |  | 0 |  | 0 |  |  | 0
[9 empty] | 0 |  | X | X | X | X | X |  |  |  | ballast replacement | [11 empty] | 60000 | [6 empty] | ballast replacement | [11 empty] | 100000 | [15 empty] | 14 |  | 0 |  |  | 0 |  | 0 |  |  | 0 | [11 empty] | 35 |  | 0 |  |  | 0 |  | 0 |  |  | 0
[9 empty] | 0 |  | X | X | X | X | X | [10 empty] | 320.2632 | [18 empty] | 225.167
[9 empty] | 0 |  | X | X | X | X | X |  |  |  | Main Door includes lamp replacement | Zone 4 | 3.24 | 1300 | 0 | 0 | 30 | 97.2 | LED-Wall-97 LPW-2700 lm | 28 | 3.4714 | 1 | 60000 | 0 | 0 |  |  | 1 |  | Main Door includes lamp replacement | Zone 4 | 3.24 | 900 | 0 | 0 | 21 | 68.04 | LED-Wall-101 LPW-2800 lm | 28 | 2.43 | 1 | 100000 | 0 | 0 |  | 1 |  | 1204.5857 |  |  | 233.8007 | 0 | 829.5819 | 1.7339 |  | 2267.9684 |  | 14 |  | 0 |  |  | 0 |  | 0 |  |  | 0 |  | 1642.68 |  |  | 163.6605 | 0 | 981.4759 |  |  | 2787.8164 |  | 35 |  | 0 |  |  | 0 |  | 0 |  |  | 0 | EXCLUDED
[9 empty] | 0 |  | X | X | X | X | X |  |  |  | ballast replacement | [11 empty] | 60000 | [6 empty] | ballast replacement | [11 empty] | 100000 | [15 empty] | 14 |  | 602.2929 |  |  | 385.7712 |  | 813.001 |  |  | 1801.0651 | [11 empty] | 35 |  | 821.34 |  |  | 270.0398 |  | 829.4969 |  |  | 1920.8767 |  | EXCLUDED
[9 empty] | 0 |  | X | X | X | X | X |  |  |  | Other Doors - includes lamp replacement | Zone 4 | 7.3418 | 1300 | 0 | 0 | 30 | 220.2552 | LED-Wall-97 LPW-2700 lm | 28 | 7.8663 | 1 | 60000 | 0 | 0 |  |  | 1 |  | Other Doors - includes lamp replacement | Zone 4 | 7.3418 | 0 | 0 | 0 | 21 | 154.1786 | LED-Wall-101 LPW-2800 lm | 28 | 5.5064 | 1 | 100000 | 0 | 0 |  | 1 |  | 2729.5912 |  |  | 529.7924 | 0 | 1879.8327 | 1.7339 |  | 5139.2163 |  | 14 |  | 0 |  |  | 0 |  | 0 |  |  | 0 |  | 3722.3129 |  |  | 370.8547 | 0 | 2224.0244 |  |  | 6317.192 |  | 35 |  | 0 |  |  | 0 |  | 0 |  |  | 0 | EXCLUDED
[9 empty] | 0 |  | X | X | X | X | X |  |  |  | ballast replacement | [11 empty] | 60000 | [6 empty] | ballast replacement | [11 empty] | 100000 | [15 empty] | 14 |  | 1364.7956 |  |  | 874.1575 |  | 1842.2603 |  |  | 4081.2134 | [11 empty] | 35 |  | 1861.1564 |  |  | 611.9102 |  | 1879.64 |  |  | 4352.7067 |  | EXCLUDED
[9 empty] | 0 |  | X | X | X | X | X |  |  |  | Rool-up Door includes lamp replacement | Zone 4 | 0.1404 | 1300 | 0 | 0 | 20 | 2.808 | LED-Wall-97 LPW-2700 lm | 28 | 0.10029 | 1 | 60000 | 0 | 0 |  |  | 1 |  | Rool-up Door includes lamp replacement | Zone 4 | 0.1404 | 400 | 0 | 0 | 21 | 2.9484 | LED-Wall-101 LPW-2800 lm | 28 | 0.1053 | 1 | 100000 | 0 | 0 |  | 1 |  | 34.7991 |  |  | 6.7542 | 0 | 23.9657 | 1.7339 |  | 65.5191 |  | 14 |  | 0 |  |  | 0 |  | 0 |  |  | 0 |  | 71.1828 |  |  | 7.092 | 0 | 42.5306 |  |  | 120.8054 |  | 35 |  | 0 |  |  | 0 |  | 0 |  |  | 0 | EXCLUDED
[9 empty] | 0 |  | X | X | X | X | X |  |  |  | ballast replacement | [11 empty] | 60000 | [6 empty] | ballast replacement | [11 empty] | 100000 | [15 empty] | 14 |  | 17.3996 |  |  | 11.1445 |  | 23.4867 |  |  | 52.0308 | [11 empty] | 35 |  | 35.5914 |  |  | 11.7017 |  | 35.9449 |  |  | 83.238 |  | EXCLUDED
[9 empty] | 0 |  | X | X | X | X | X | [10 empty] | 320.2632 | [18 empty] | 225.167
[9 empty] | 0 |  | X | X | X | X | X
[9 empty] | 0 |  | X | X | X | X | X |  |  |  | Façade |  | area, ft2 | [16 empty] | Façade |  | area, ft2
[9 empty] | 0 |  | X | X | X | X | X |  |  |  | includes lamp replacement | zone 2 | 1550 | 600 | 0 | 0 | 0.1 | 155 | LED-FLD-134 LPW-5600 lm | 39 | 3.9744 | 1 | 100000 | 0 | 0 |  |  | 0.5 |  | includes lamp replacement | zone 2 | 1550 | 400 | 0 | 0 | 0.1 | 155 | LED-FLD-134 LPW-5600 lm | 39 | 3.9744 | 1 | 100000 | 0 | 0 |  | 0.5 |  | 1023 |  |  | 267.6731 | 0 | 771.2577 | 1.6735 |  | 2061.9308 |  | 23 |  | 0 |  |  | 0 |  | 0 |  |  | 0 |  | 1023 |  |  | 133.8365 | 0 | 642.0401 |  |  | 1798.8766 |  | 35 |  | 0 |  |  | 0 |  | 0 |  |  | 0 | EXCLUDED
[9 empty] | 0 |  | X | X | X | X | X |  |  |  | ballast replacement | [11 empty] | 100000 | [6 empty] | ballast replacement | [11 empty] | 100000 | [15 empty] | 23 |  | 511.5 |  |  | 441.6606 |  | 814.7997 |  |  | 1767.9603 | [11 empty] | 35 |  | 511.5 |  |  | 441.6606 |  | 814.7997 |  |  | 1767.9603
[9 empty] | 0 |  | X | X | X | X | X |  |  |  |  | zone 3 | 1550 | 750 | 0 | 0 | 0.15 | 232.5 | LED-FLD-134 LPW-5600 lm | 39 | 5.9615 |  |  | 0 | 0 |  |  | 0.5 |  | " " | zone 3 | 1550 | 500 | 0 | 0 | 0.15 | 232.5 | LED-FLD-134 LPW-5600 lm | 39 | 5.9615 | 1 | 100000 | 0 | 0 |  | 0.5 |  | 1534.5 |  |  | 401.5096 | 0 | 1156.8865 | 1.6735 |  | 3092.8961 |  | 0 |  | 0 |  |  | 0 |  | 0 |  |  | 0 |  | 1534.5 |  |  | 200.7548 | 0 | 963.0602 |  |  | 2698.315 |  | 35 |  | 0 |  |  | 0 |  | 0 |  |  | 0 | EXCLUDED
[9 empty] | 0 |  | X | X | X | X | X | [22 empty] | " " | [11 empty] | 100000 | [15 empty] | 0 |  | 0 |  |  | 0 |  | 0 |  |  | 0 | [11 empty] | 35 |  | 767.25 |  |  | 662.4909 |  | 1222.1995 |  |  | 2651.9404 |  | EXCLUDED
[9 empty] | 0 |  | X | X | X | X | X |  |  |  |  | zone 4 | 1550 | 1300 | 0 | 0 | 0.2 | 310 | LED-FLD-134 LPW-5600 lm | 39 | 7.9487 |  |  | 0 | 0 |  |  | 0 |  | " " | zone 4 | 1550 | 900 | 0 | 0 | 0.2 | 310 | LED-FLD-134 LPW-5600 lm | 39 | 7.9487 | 1 | 100000 | 0 | 0 |  | 0 |  | 0 |  |  | 0 | 0 | 0 |  |  | 0 |  | 0 |  | 0 |  |  | 0 |  | 0 |  |  | 0 |  | 0 |  |  | 0 | 0 | 0 |  |  | 0 |  | 35 |  | 0 |  |  | 0 |  | 0 |  |  | 0
[9 empty] | 0 |  | X | X | X | X | X | [22 empty] | " " | [11 empty] | 100000 | [15 empty] | 0 |  | 0 |  |  | 0 |  | 0 |  |  | 0 | [11 empty] | 35 |  | 0 |  |  | 0 |  | 0 |  |  | 0
[9 empty] | 0 |  | X | X | X | X | X
[10 empty] | 0 | X | X | X | X | X |  |  |  | Mid-rise Apartment | [18 empty] | Mid-rise Apartment | [16 empty] | Mid-rise Apartment | [10 empty] | Mid-rise Apartment | [10 empty] | Mid-rise Apartment | [10 empty] | Mid-rise Apartment | [9 empty] | Mid-rise Apartment | 0 | 0
[10 empty] | 0 | X | X | X | X | X
[10 empty] | 0 | X | X | X | X | X | [6 empty] | 600 | 0 | 0 | [11 empty] | 1 |  |  |  |  | 400 | 0 | 0
[10 empty] | 0 | X | X | X | X | X | [6 empty] | 750 | 0 | 0 | [16 empty] | 500 | 0 | 0
[10 empty] | 0 | X | X | X | X | X | [6 empty] | 1300 | 0 | 0 | [16 empty] | 900 | 0 | 0
[10 empty] | 0 | X | X | X | X | X |  |  |  | Area required per space |  | 325 | [16 empty] | Area required per space |  | 325
[10 empty] | 0 | X | X | X | X | X |  |  |  | # of Parking Spaces |  | 87.9292 | [16 empty] | # of Parking Spaces |  | 87.9292
[10 empty] | 0 | X | X | X | X | X |  |  |  | # of spaces per fixture |  | 20 | [16 empty] | # of spaces per fixture |  | 20
[10 empty] | 0 | X | X | X | X | X |  |  |  | # of Fixtures | 0 | 4.3965 | [16 empty] | # of Fixtures | 0 | 4.3965
[10 empty] | 0 | X | X | X | X | X |  |  |  | Parking |  | area, ft2 | [16 empty] | Parking |  | area, ft2
[10 empty] | 0 | X | X | X | X | X |  |  |  | includes lamp replacement | zone 2 | 28577 | 600 | 0 | 0 | 0.06 | 1714.62 | LED-PK-92 LPW-13000 lm | 141 | 12.1604 | 1 | 100000 | 6 | 21 | 517.4274 |  | 0.5 |  | includes lamp replacement | zone 2 | 28577 | 400 | 0 | 0 | 0.04 | 1143.08 | LED-PK-109 LPW-14500 lm | 134 | 8.5304 | 1 | 100000 | 4 | 21 | 941.7954 | 0.5 |  | 9216.331 |  |  | 2515.1545 | 146.55 | 7090.6383 | 1.6752 |  | 18968.6738 |  | 23 |  | 0 |  |  | 0 |  | 0 |  |  | 0 |  | 7720.517 |  |  | 1121.6283 | 97.7 | 4981.2959 |  |  | 13921.1412 |  | 35 |  | 0 |  |  | 0 |  | 0 |  |  | 0 | EXCLUDED
[10 empty] | 0 | X | X | X | X | X |  |  |  | ballast replacement | [11 empty] | 50000 | [6 empty] | ballast replacement | [11 empty] | 50000 | [15 empty] | 11 |  | 945.4731 |  |  | 675.6788 |  | 1352.6785 |  |  | 2973.8304 | [11 empty] | 18 |  | 663.2423 |  |  | 473.9837 |  | 948.8939 |  |  | 2086.1198 |  | EXCLUDED
[10 empty] | 0 | X | X | X | X | X |  |  |  |  | zone 3 | 28577 | 750 | 0 | 0 | 0.1 | 2857.7 | LED-PK-92 LPW-13000 lm | 141 | 20.2674 | 1 | 100000 | 10 | 21 | 517.4274 |  | 0.5 |  | " " | zone 3 | 28577 | 500 | 0 | 0 | 0.06 | 1714.62 | LED-PK-109 LPW-14500 lm | 134 | 12.7957 | 1 | 100000 | 6 | 21 | 896.948 | 0.5 |  | 15193.2501 |  |  | 3883.1925 | 244.25 | 11435.7867 | 1.6895 |  | 30756.4794 |  | 23 |  | 0 |  |  | 0 |  | 0 |  |  | 0 |  | 11330.6392 |  |  | 1451.6465 | 146.55 | 7123.7215 |  |  | 20052.5572 |  | 35 |  | 0 |  |  | 0 |  | 0 |  |  | 0 | EXCLUDED
[10 empty] | 0 | X | X | X | X | X | [15 empty] | 50000 | [6 empty] | " " | [11 empty] | 50000 | [15 empty] | 11 |  | 1575.7885 |  |  | 1126.1314 |  | 2254.4641 |  |  | 4956.384 | [11 empty] | 18 |  | 994.8635 |  |  | 710.9755 |  | 1423.3408 |  |  | 3129.1798 |  | EXCLUDED
[10 empty] | 0 | X | X | X | X | X |  |  |  |  | zone 4 | 28577 | 1300 | 0 | 0 | 0.13 | 3715.01 | LED-PK-92 LPW-13000 lm | 141 | 26.3476 | 1 | 100000 | 13 | 21 | 517.4274 |  | 0 |  | " " | zone 4 | 28577 | 900 | 0 | 0 | 0.08 | 2286.16 | LED-PK-109 LPW-14500 lm | 134 | 17.0609 | 1 | 100000 | 9 | 21 | 0 | 0 |  | 0 |  |  | 0 | 0 | 0 |  |  | 0 |  | 23 |  | 0 |  |  | 0 |  | 0 |  |  | 0 |  | 0 |  |  | 0 | 0 | 0 |  |  | 0 |  | 35 |  | 0 |  |  | 0 |  | 0 |  |  | 0
[10 empty] | 0 | X | X | X | X | X | [15 empty] | 50000 | [6 empty] | " " | [11 empty] | 50000 | [15 empty] | 11 |  | 0 |  |  | 0 |  | 0 |  |  | 0 | [11 empty] | 18 |  | 0 |  |  | 0 |  | 0 |  |  | 0
[10 empty] | 0 | X | X | X | X | X
[10 empty] | 0 | X | X | X | X | X |  |  |  | Doors |  | linear feet, ft | [16 empty] | Doors |  | linear feet, ft
[10 empty] | 0 | X | X | X | X | X |  |  |  | Main Door includes lamp replacement | zone 2 | 0 | 600 | 0 | 0 | 20 | 0 | LED-Wall-97 LPW-2700 lm | 28 | 0 | 1 | 60000 | 0 | 0 |  |  | 0.5 |  | includes lamp replacement | zone 2 | 0 | 400 | 0 | 0 | 14 | 0 | LED-Wall-101 LPW-2800 lm | 28 | 0 | 1 | 100000 | 0 | 0 |  | 0.5 |  | 0 |  |  | 0 | 0 | 0 |  |  | 0 |  | 14 |  | 0 |  |  | 0 |  | 0 |  |  | 0 |  | 0 |  |  | 0 | 0 | 0 |  |  | 0 |  | 35 |  | 0 |  |  | 0 |  | 0 |  |  | 0
[10 empty] | 0 | X | X | X | X | X |  |  |  | ballast replacement | [11 empty] | 60000 | [6 empty] | ballast replacement | [11 empty] | 100000 | [15 empty] | 14 |  | 0 |  |  | 0 |  | 0 |  |  | 0 | [11 empty] | 35 |  | 0 |  |  | 0 |  | 0 |  |  | 0
[10 empty] | 0 | X | X | X | X | X |  |  |  | Other Doors - includes lamp replacement | zone 2 | 0 | 1300 | 0 | 0 | 20 | 0 | LED-Wall-97 LPW-2700 lm | 28 | 0 | 1 | 60000 | 0 | 0 |  |  | 0.5 |  | includes lamp replacement | zone 2 | 0 | 400 | 0 | 0 | 14 | 0 | LED-Wall-101 LPW-2800 lm | 28 | 0 | 1 | 100000 | 0 | 0 |  | 0.5 |  | 0 |  |  | 0 | 0 | 0 |  |  | 0 |  | 14 |  | 0 |  |  | 0 |  | 0 |  |  | 0 |  | 0 |  |  | 0 | 0 | 0 |  |  | 0 |  | 35 |  | 0 |  |  | 0 |  | 0 |  |  | 0
[10 empty] | 0 | X | X | X | X | X |  |  |  | ballast replacement | [11 empty] | 60000 | [6 empty] | ballast replacement | [11 empty] | 100000 | [15 empty] | 14 |  | 0 |  |  | 0 |  | 0 |  |  | 0 | [11 empty] | 35 |  | 0 |  |  | 0 |  | 0 |  |  | 0
[10 empty] | 0 | X | X | X | X | X |  |  |  | Rool-up Door includes lamp replacement | zone 2 | 0 | 0 | 0 | 0 | 20 | 0 | LED-Wall-97 LPW-2700 lm | 28 | 0 | 1 | 60000 | 0 | 0 |  |  | 0 |  | includes lamp replacement | zone 2 | 0 | 400 | 0 | 0 | 14 | 0 | LED-Wall-101 LPW-2800 lm | 28 | 0 | 1 | 100000 | 0 | 0 |  | 0 |  | 0 |  |  | 0 | 0 | 0 |  |  | 0 |  | 14 |  | 0 |  |  | 0 |  | 0 |  |  | 0 |  | 0 |  |  | 0 | 0 | 0 |  |  | 0 |  | 35 |  | 0 |  |  | 0 |  | 0 |  |  | 0
[10 empty] | 0 | X | X | X | X | X |  |  |  | ballast replacement | [11 empty] | 60000 | [6 empty] | ballast replacement | [11 empty] | 100000 | [15 empty] | 14 |  | 0 |  |  | 0 |  | 0 |  |  | 0 | [11 empty] | 35 |  | 0 |  |  | 0 |  | 0 |  |  | 0
[10 empty] | 0 | X | X | X | X | X | [10 empty] | 0
[10 empty] | 0 | X | X | X | X | X |  |  |  | Main Door includes lamp replacement | Zone 3 | 0 | 750 | 0 | 0 | 30 | 0 | LED-Wall-97 LPW-2700 lm | 28 | 0 | 1 | 60000 | 0 | 0 |  |  | 0.5 |  | " " | zone 3 | 0 | 500 | 0 | 0 | 21 | 0 | LED-Wall-101 LPW-2800 lm | 28 | 0 | 1 | 100000 | 0 | 0 |  | 0.5 |  | 0 |  |  | 0 | 0 | 0 |  |  | 0 |  | 14 |  | 0 |  |  | 0 |  | 0 |  |  | 0 |  | 0 |  |  | 0 | 0 | 0 |  |  | 0 |  | 35 |  | 0 |  |  | 0 |  | 0 |  |  | 0
[10 empty] | 0 | X | X | X | X | X |  |  |  | ballast replacement | [11 empty] | 60000 | [6 empty] | " " | [11 empty] | 100000 | [15 empty] | 14 |  | 0 |  |  | 0 |  | 0 |  |  | 0 | [11 empty] | 35 |  | 0 |  |  | 0 |  | 0 |  |  | 0
[10 empty] | 0 | X | X | X | X | X |  |  |  | Other Doors - includes lamp replacement | Zone 3 | 0 | 750 | 0 | 0 | 30 | 0 | LED-Wall-97 LPW-2700 lm | 28 | 0 | 1 | 60000 | 0 | 0 |  |  | 0 |  | " " | zone 3 | 0 | 500 | 0 | 0 | 21 | 0 | LED-Wall-101 LPW-2800 lm | 28 | 0 | 1 | 100000 | 0 | 0 |  | 0 |  | 0 |  |  | 0 | 0 | 0 |  |  | 0 |  | 14 |  | 0 |  |  | 0 |  | 0 |  |  | 0 |  | 0 |  |  | 0 | 0 | 0 |  |  | 0 |  | 35 |  | 0 |  |  | 0 |  | 0 |  |  | 0
[10 empty] | 0 | X | X | X | X | X |  |  |  | ballast replacement | [11 empty] | 60000 | [6 empty] | " " | [11 empty] | 100000 | [15 empty] | 14 |  | 0 |  |  | 0 |  | 0 |  |  | 0 | [11 empty] | 35 |  | 0 |  |  | 0 |  | 0 |  |  | 0
[10 empty] | 0 | X | X | X | X | X |  |  |  | Rool-up Door includes lamp replacement | Zone 3 | 0 | 750 | 0 | 0 | 30 | 0 | LED-Wall-97 LPW-2700 lm | 28 | 0 | 1 | 60000 | 0 | 0 |  |  | 0 |  | " " | zone 3 | 0 | 500 | 0 | 0 | 21 | 0 | LED-Wall-101 LPW-2800 lm | 28 | 0 | 1 | 100000 | 0 | 0 |  | 0 |  | 0 |  |  | 0 | 0 | 0 |  |  | 0 |  | 14 |  | 0 |  |  | 0 |  | 0 |  |  | 0 |  | 0 |  |  | 0 | 0 | 0 |  |  | 0 |  | 35 |  | 0 |  |  | 0 |  | 0 |  |  | 0
[10 empty] | 0 | X | X | X | X | X |  |  |  | ballast replacement | [11 empty] | 60000 | [6 empty] | " " | [11 empty] | 100000 | [15 empty] | 14 |  | 0 |  |  | 0 |  | 0 |  |  | 0 | [11 empty] | 35 |  | 0 |  |  | 0 |  | 0 |  |  | 0
[10 empty] | 0 | X | X | X | X | X | [10 empty] | 0
[10 empty] | 0 | X | X | X | X | X |  |  |  | Main Door includes lamp replacement | Zone 4 | 0 | 1300 | 0 | 0 | 30 | 0 | LED-Wall-97 LPW-2700 lm | 28 | 0 | 1 | 60000 | 0 | 0 |  |  | 0 |  | " " | zone 4 | 0 | 900 | 0 | 0 | 21 | 0 | LED-Wall-101 LPW-2800 lm | 28 | 0 | 1 | 100000 | 0 | 0 |  | 0 |  | 0 |  |  | 0 | 0 | 0 |  |  | 0 |  | 14 |  | 0 |  |  | 0 |  | 0 |  |  | 0 |  | 0 |  |  | 0 | 0 | 0 |  |  | 0 |  | 35 |  | 0 |  |  | 0 |  | 0 |  |  | 0
[10 empty] | 0 | X | X | X | X | X |  |  |  | ballast replacement | [11 empty] | 60000 | [6 empty] | " " | [11 empty] | 100000 | [15 empty] | 14 |  | 0 |  |  | 0 |  | 0 |  |  | 0 | [11 empty] | 35 |  | 0 |  |  | 0 |  | 0 |  |  | 0
[10 empty] | 0 | X | X | X | X | X |  |  |  | Other Doors - includes lamp replacement | Zone 4 | 0 | 1300 | 0 | 0 | 30 | 0 | LED-Wall-97 LPW-2700 lm | 28 | 0 | 1 | 60000 | 0 | 0 |  |  | 0 |  | " " | zone 4 | 0 | 900 | 0 | 0 | 21 | 0 | LED-Wall-101 LPW-2800 lm | 28 | 0 | 1 | 100000 | 0 | 0 |  | 0 |  | 0 |  |  | 0 | 0 | 0 |  |  | 0 |  | 14 |  | 0 |  |  | 0 |  | 0 |  |  | 0 |  | 0 |  |  | 0 | 0 | 0 |  |  | 0 |  | 35 |  | 0 |  |  | 0 |  | 0 |  |  | 0
[10 empty] | 0 | X | X | X | X | X |  |  |  | ballast replacement | [11 empty] | 60000 | [6 empty] | " " | [11 empty] | 100000 | [15 empty] | 14 |  | 0 |  |  | 0 |  | 0 |  |  | 0 | [11 empty] | 35 |  | 0 |  |  | 0 |  | 0 |  |  | 0
[10 empty] | 0 | X | X | X | X | X |  |  |  | Rool-up Door includes lamp replacement | Zone 4 | 0 | 1300 | 0 | 0 | 30 | 0 | LED-Wall-97 LPW-2700 lm | 28 | 0 | 1 | 60000 | 0 | 0 |  |  | 0.5 |  | " " | zone 4 | 0 | 900 | 0 | 0 | 21 | 0 | LED-Wall-101 LPW-2800 lm | 28 | 0 | 1 | 100000 | 0 | 0 |  | 0.5 |  | 0 |  |  | 0 | 0 | 0 |  |  | 0 |  | 14 |  | 0 |  |  | 0 |  | 0 |  |  | 0 |  | 0 |  |  | 0 | 0 | 0 |  |  | 0 |  | 35 |  | 0 |  |  | 0 |  | 0 |  |  | 0
[10 empty] | 0 | X | X | X | X | X |  |  |  | ballast replacement | [11 empty] | 60000 | [6 empty] | " " | [11 empty] | 100000 | [15 empty] | 14 |  | 0 |  |  | 0 |  | 0 |  |  | 0 | [11 empty] | 35 |  | 0 |  |  | 0 |  | 0 |  |  | 0
[10 empty] | 0 | X | X | X | X | X | [10 empty] | 0
[10 empty] | 0 | X | X | X | X | X
[10 empty] | 0 | X | X | X | X | X |  |  |  | Façade |  | area, ft2 | [16 empty] | Façade |  | area, ft2
[10 empty] | 0 | X | X | X | X | X |  |  |  | includes lamp replacement | zone 2 | 1777 | 600 | 0 | 0 | 0.1 | 177.7 | LED-FLD-134 LPW-5600 lm | 39 | 4.5564 | 1 | 100000 | 0 | 0 |  |  | 0.5 |  | includes lamp replacement | zone 2 | 1777 | 400 | 0 | 0 | 0.1 | 177.7 | LED-FLD-134 LPW-5600 lm | 39 | 4.5564 | 1 | 100000 | 0 | 0 |  | 0.5 |  | 1172.82 |  |  | 306.8742 | 0 | 884.2096 | 1.6735 |  | 2363.9038 |  | 23 |  | 0 |  |  | 0 |  | 0 |  |  | 0 |  | 1172.82 |  |  | 153.4371 | 0 | 736.0679 |  |  | 2062.325 |  | 35 |  | 0 |  |  | 0 |  | 0 |  |  | 0 | EXCLUDED
[10 empty] | 0 | X | X | X | X | X |  |  |  | ballast replacement | [11 empty] | 100000 | [6 empty] | ballast replacement | [11 empty] | 100000 | [15 empty] | 23 |  | 586.41 |  |  | 506.3425 |  | 934.1284 |  |  | 2026.8809 | [11 empty] | 35 |  | 586.41 |  |  | 506.3425 |  | 934.1284 |  |  | 2026.8809
[10 empty] | 0 | X | X | X | X | X |  |  |  |  | zone 3 | 1777 | 750 | 0 | 0 | 0.15 | 266.55 | LED-FLD-134 LPW-5600 lm | 39 | 6.8346 | 1 | 100000 | 0 | 0 |  |  | 0.5 |  | " " | zone 3 | 1777 | 500 | 0 | 0 | 0.15 | 266.55 | LED-FLD-134 LPW-5600 lm | 39 | 6.8346 | 1 | 100000 | 0 | 0 |  | 0.5 |  | 1759.23 |  |  | 460.3113 | 0 | 1326.3144 | 1.6735 |  | 3545.8558 |  | 23 |  | 0 |  |  | 0 |  | 0 |  |  | 0 |  | 1759.23 |  |  | 230.1557 | 0 | 1104.1019 |  |  | 3093.4875 |  | 35 |  | 0 |  |  | 0 |  | 0 |  |  | 0 | EXCLUDED
[10 empty] | 0 | X | X | X | X | X | [15 empty] | 100000 | [6 empty] | " " | [11 empty] | 100000 | [15 empty] | 23 |  | 879.615 |  |  | 759.5137 |  | 1401.1926 |  |  | 3040.3213 | [11 empty] | 35 |  | 879.615 |  |  | 759.5137 |  | 1401.1926 |  |  | 3040.3213
[10 empty] | 0 | X | X | X | X | X |  |  |  |  | zone 4 | 1777 | 1300 | 0 | 0 | 0.2 | 355.4 | LED-FLD-134 LPW-5600 lm | 39 | 9.1128 | 1 | 100000 | 0 | 0 |  |  | 0 |  | " " | zone 4 | 1777 | 900 | 0 | 0 | 0.2 | 355.4 | LED-FLD-134 LPW-5600 lm | 39 | 9.1128 | 1 | 100000 | 0 | 0 |  | 0 |  | 0 |  |  | 0 | 0 | 0 |  |  | 0 |  | 23 |  | 0 |  |  | 0 |  | 0 |  |  | 0 |  | 0 |  |  | 0 | 0 | 0 |  |  | 0 |  | 35 |  | 0 |  |  | 0 |  | 0 |  |  | 0
[10 empty] | 0 | X | X | X | X | X | [15 empty] | 100000 | [6 empty] | " " | [27 empty] | 23 |  | 0 |  |  | 0 |  | 0 |  |  | 0 | [11 empty] | 0 |  | 0 |  |  | 0 |  | 0 |  |  | 0
[10 empty] | 0 | X | X | X | X | X
Large Office
[48 empty] | 90.1-2007 |  |  |  | 90.1-2010
[48 empty] | New Construc- tion | Mainte- nance | Replace- ment Year | Replace- ment Cost | New Construc- tion | Mainte- nance | Replace- ment Cost
[49 empty] | 66537.658 |  |  | 17055.4055
Standalone_Retail_Interior Lighting
Standalone Retail
[48 empty] | 90.1-2007 |  |  |  | 90.1-2010
[48 empty] | New Construc- tion | Mainte- nance | Replace- ment Year | Replace- ment Cost | New Construc- tion | Mainte- nance | Replace- ment Cost
[49 empty] | #REF! |  |  | #REF!
Primary_School_Interior Lighting
Primary School
[48 empty] | 90.1-2007 |  |  |  | 90.1-2010
[48 empty] | New Construc- tion | Mainte- nance | Replace- ment Year | Replace- ment Cost | New Construc- tion | Mainte- nance | Replace- ment Cost
[49 empty] | #REF! |  |  | #REF!
Small_Hotel_Interior Lighting
Small Hotel
[48 empty] | 90.1-2007 |  |  |  | 90.1-2010
[48 empty] | New Construc- tion | Mainte- nance | Replace- ment Year | Replace- ment Cost | New Construc- tion | Mainte- nance | Replace- ment Cost
[49 empty] | #REF! |  |  | #REF!
Mid-rise Apartment_Interior Lighting
Mid-rise Apartment
[48 empty] | 90.1-2007 |  |  |  | 90.1-2010
[48 empty] | New Construc- tion | Mainte- nance | Replace- ment Year | Replace- ment Cost | New Construc- tion | Mainte- nance | Replace- ment Cost
[49 empty] | #REF! |  |  | #REF!

## Ext Lighting Comp (hidden)
90.1 Cost Effectiveness Analysis - Exterior Lighting - Equipment and Labor Cost Details
Exterior lighting equipment and installation costs are estimated for 1. fixtures lamps and ballasts, 2. light poles and parking, 3. conduit in slab and 4. occupancy sensors
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29
Costs Fixtures, Lamps and Ballasts | [28 empty] | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10
Fixture ID | Fixture and Lamp Description | [5 empty] | New Construction | [10 empty] | Replacement Costs | [10 empty] | 1: Light Pole with 2 Arm Bracket Costs
| Fixture Location | Type | Lamp Watts | Number of lamps | Fixture Input Watts | Lamp Life | Fixture cost (ballast included) | Fixture Source | Fixture Label in Source | Lamp Code | Lamp Cost |  | Lamp Label in Source | Fixture Cost Including Lamp(s) | Installation Labor Hours | Installation Labor Cost | Installation Labor RS Means Reference | Relamp Labor Hours | Relamp Labor Cost | Lamp Relamp Labor RS Means 2012 2661-23.10 section | Ballast Description | Ballast Life Hours | Replace-ment Ballast Cost | Ballast Cost Source | Ballast Label in Source | Replace Ballast Labor Hours | Replace Ballast Labor Cost | Ballast Replace Labor RS Means 2012 Reference Number (section 26 51 13.90 if not show) | 1: Material; 5: Labor; 8: Construction Equipment | Source
|  | 2013 | [26 empty] | Length, ft | Steel | Aluminum | Average | Steel | Aluminum | Average | Steel | Aluminum | Average
None | [28 empty] | 1: 0
MH-PU-50-D | Door | Wall Pack | 50 | 1 | 63 | 10000 | 216 |  | 4GWG8 | BD17 | 56 | as above | 1F398 | 272 | 1 | 67.35 | 2556-23.10-0200 | 0.26667 | 17.9602 | 1000 | Pulse Start 1 Lamp | 50000 | 129.3 | see above | 6XPW1 | 1 | 67.35 | 7610 | 14 | 1002 | 925 | 963.5 | 133 | 121 | 127 | 0 | 0 | 0 | All RS Means Electrical 2012 26 56 13.10
[29 empty] | 15 | 1022 | 1017.5 | 1019.75 | 137.5 | 129 | 133.25 | 0 | 0 | 0
[29 empty] | 16 | 1042 | 1110 | 1076 | 142 | 137 | 139.5 | 0 | 0 | 0
[29 empty] | 18 | 1087 | 1127.5 | 1107.25 | 266 | 243.5 | 254.75 | 45 | 50 | 47.5
[29 empty] | 20 | 1342 | 1145 | 1243.5 | 390 | 350 | 370 | 45.5 | 51 | 48.25
[29 empty] | 21 | 1352 | 1220 | 1286 | 395.5 | 354 | 374.75 | 46.05 | 51.65 | 48.85
LED-Flood-104 LPD-2600 lm | Façade | Floodlight - Wide Light Distribution | 25 | 1 | 25 | 100000 | 265 | grainger.com | 53VR85 |  | 0 |  |  | 265 | 1 | 67.35 | 2556-23.10-0200 | 0 | 0 |  |  | 100000 | 132.5 |  | Assumes 50% of fixture cost | 1 | 67.35 | 7610 | 30 | 1442 | 1895 | 1668.5 | 445 | 390 | 417.5 | 51 | 57.5 | 54.25
MH-PU-70-D | Door | Wall Pack | 70 | 1 | 85 | 12000 | 216 |  | 4GWG8 | BD17 | 46.75 | as above | 1E694 | 262.75 | 1 | 67.35 | 2556-23.10-0200 | 0.26667 | 17.9602 | 1000 | Pulse Start 1 Lamp | 50000 | 153.5 | see above | 1XUD6 | 1 | 67.35 | 7610 | 35 | 1632 | 2120 | 1876 | 465 | 445 | 455 | 57.5 | 60 | 58.75
MH-PU-70-RD | Rolling Door | Wall Pack | 70 | 1 | 85 | 12000 | 216 |  | 4GWG8 | BD17 | 46.75 | as above | 1E694 | 262.75 | 1 | 67.35 | 2556-23.10-0200 | 0.26667 | 17.9602 | 1000 | Pulse Start 1 Lamp | 50000 | 153.5 | see above | 1XUD6 | 1 | 67.35 | 7610 | 38 | 1762 | 2220 | 1991 | 519 | 471 | 495 | 65.7 | 62.4 | 64.05
MH-PU-70-F | Façade | Floodlight - Wide Light Distribution | 70 | 1 | 85 | 12000 | 250.25 |  | 3GB10 | BD17 | 49.15 | as above | 6V746 | 299.4 | 1 | 67.35 | 2556-23.10-0200 | 0.26667 | 17.9602 | 1000 | Pulse Start 1 Lamp | 50000 | 153.5 | see above | 1XUD6 | 1 | 67.35 | 7610 | 40 | 1957 | 2370 | 2163.5 | 600 | 510 | 555 | 78 | 66 | 72
LED-PK-85 LPW-6600 lm | Parking | Site Lighting Fixture | 73 | 1 | 73 | 100000 | 588 | grainger.com | 45HE15 |  |  |  |  | 588 | 2.963 | 199.5581 | 2556-36.20-1950 | 0 | 0 |  |  | 100000 | 294 |  | Assumes 50% of fixture cost | 2.963 | 199.5581 | 7610 | 1: 1 Interpolated values for 15, 18, and 38 feet; or 18 feet, steel pole values are from source not interpolated
LED-FLD-134 LPW-5600 lm | Façade | Floodlight - Wide Light Distribution | 39 | 1 | 39 | 100000 | 514.8 | goodmart.com | FFLED39N/PC |  | 0 |  |  | 514.8 | 2 | 134.7 | 2556-36.20-1180 | 0 | 0 |  |  | 100000 | 257.4 |  | Assumes 50% of fixture cost | 2 | 134.7 | 7610 | 1: 0
MH-PU-150-P | Parking | Flood | 150 | 1 | 186 | 15000 | 160 | Goodmart | EZHH150QT | BD17 | 53.85 | as above | 1G980 | 213.85 | 2.963 | 199.5581 | 2556-36.20-1950 | 0.26667 | 17.9602 | 1000 | Pulse Start 1 Lamp | 50000 | 151 | see above | 4CRJ2 | 1 | 67.35 | 7610
MH-PU-175-RD | Rolling Door | Wall Pack | 175 | 1 | 210 | 15000 | 313.25 |  | 2RGX4 | ED28 | 29.65 | as above | 4V550 | 342.9 | 2.963 | 199.5581 | 2556-36.20-1950 | 0.26667 | 17.9602 | 1000 | Pulse Start 1 Lamp | 50000 | 138.55 | see above | 1XUK1 | 1 | 67.35 | 7610
MH-PU-175-P | Parking | Floodlight | 175 | 1 | 210 | 15000 | 210 | Goodmart | FXH175SFQT | ED28 | 29.65 | as above | 4V550 | 239.65 | 2.963 | 199.5581 | 2556-36.20-1950 | 0.26667 | 17.9602 | 1000 | Pulse Start 1 Lamp | 50000 | 138.55 | see above | 1XUK1 | 1 | 67.35 | 7610
MH-PU-250-P | Parking | Security Lighting | 250 | 1 | 284 | 15000 | 637.5 |  | 3JXC5 | ED28 | 15.6 | as above | 2V712 | 653.1 | 2.963 | 199.5581 | 2556-36.20-1950 | 0.26667 | 17.9602 | 1100 | Pulse Start 1 Lamp | 50000 | 156.25 | see above | 4CRH6 | 1 | 67.35 | 7620
MH-PU-320-P | Parking | Floodlight | 320 | 1 | 363 | 20000 | 325 | Goodmart | FXLH320SFPSQ | ED28 | 86.4 | as above | 3APK2 | 411.4 | 3.636 | 244.8846 | 2556-36.20-2000 | 0.26667 | 17.9602 | 1200 | Pulse Start 1 Lamp | 50000 | 151.75 | see above | 4CRH7 | 1.143 | 76.981 | 7630
MH-PU-320-F | Parking | Floodlight | 320 | 1 | 363 | 20000 | 325 | Goodmart | FXLH320SFPSQ | ED28 | 86.4 | as above | 3APK2 | 411.4 | 3.636 | 244.8846 | 2556-36.20-2000 | 0.26667 | 17.9602 | 1200 | Pulse Start 1 Lamp | 50000 | 151.75 | see above | 4CRH7 | 1.143 | 76.981 | 7630
MH-PU-1000-P | Parking | Mounted Floodlight | 1000 | 1 | 1075 | 15000 | 679 | Goodmart | MPNK-S76-1000- 277V-F1-AP-LL | BT37 | 66.3 | as above | 2YGE1 | 745.3 | 4 | 269.4 | 2556-36.20-2200 | 0.4 | 26.94 | 1300 | Pulse Start 1 Lamp | 50000 | 249.75 | see above | 4VMY8 | 1.333 | 89.7776 | 7640
CFL-26-D | Door | Wall Pack | 26 | 2 | 58 | 12000 | 143 | 1000bulbs | WPTF42 1 or 2 lamp | Biax 4 Pin | 47.26 | as above | 4FFC2 | 237.52 | 1 | 67.35 | 2556-23.10-0200 | 0.08889 | 5.9867 | 0560 | Electronic CF Ballast Programmed/Rapid Start 2 Lamp | 40000 | 54.45 | see above | 2XKV9 |  | 0
|  | 2016 | [26 empty] | 1: Exterior Lighting Conduit in Slab
MH-PR-70-F | Façade | Floodlight - Wide Light Distribution | 70 | 1 | 98 | 6000 | 250.25 | Grainger #403 2012/2013 Ref | 3GB10 | BD17 | 46.75 | as above | 1E694 | 297 | 1 | 67.35 | 2556-23.10-0200 | 0.26667 | 17.9602 | 1000 | Probe Start | 50000 | 42.88 | http://www.kolmart.com | 70-Watt-Pulse-Start-Metal-Halide-Ballast-Kit-4T_p_20.html Moo70-71C-511-DK | 1 | 67.35 | 7610 | 1: Description; 2: Material $/linear ft.; 3: Labor $/linear ft.; 4: Source
MH-PR-70-D | Door | Wall Pack | 70 | 1 | 98 | 6000 | 216 | Grainger #403 2012/2013 Ref | 4GWG8 | BD17 | 46.75 | as above | 1E694 | 262.75 | 1 | 67.35 | 2556-23.10-0200 | 0.26667 | 17.9602 | 1000 | Probe Start | 50000 | 42.88 | http://www.kolmart.com | 70-Watt-Pulse-Start-Metal-Halide-Ballast-Kit-4T_p_20.html Moo70-71C-511-DK | 1 | 67.35 | 7610 | 1: 3/4 in. PVC; 2: 0.97; 3: 1.79; 4: RS Means 2012, 26 05 39.30 3250
MH-PR-70-RD | Rolling Door | Wall Pack | 70 | 1 | 98 | 6000 | 216 | Grainger #403 2012/2013 Ref | 4GWG8 | BD17 | 46.75 | as above | 1E694 | 262.75 | 1 | 67.35 | 2556-23.10-0200 | 0.26667 | 17.9602 | 1000 | Probe Start | 50000 | 42.88 | http://www.kolmart.com | 70-Watt-Pulse-Start-Metal-Halide-Ballast-Kit-4T_p_20.html Moo70-71C-511-DK | 1 | 67.35 | 7610
MH-PR-175-P | Parking | Flood | 175 | 1 | 210 | 10000 | 160 | Goodmart | EZHH150QT | BD17 | 53.85 | as above | 1G980 | 213.85 | 2.963 | 199.5581 | 2556-36.20-1950 | 0.26667 | 17.9602 | 1000 | Probe Start 1 Lamp | 50000 | 96.3 | see above | 1XUD9 | 1 | 67.35 | 7610
MH-PR-175-RD | Rolling Door | Flood | 175 | 1 | 210 | 10000 | 160 | Goodmart | EZHH150QT | BD17 | 53.85 | as above | 1G980 | 213.85 | 1 | 67.35 | 2556-23.10-0200 | 0.26667 | 17.9602 | 1000 | Probe Start 1 Lamp | 50000 | 96.3 | see above | 1XUD9 | 1 | 67.35 | 7610
LED-PK-85 LPW-6600 lm | Parking | Site Lighting Fixture | 73 | 1 | 73 | 100000 | 588 | grainger.com | 45HE15 |  | 0 |  |  | 588 | 2.963 | 199.5581 | 2556-36.20-1950 | 0 | 0 | 1000 |  | 50000 | 155.5 | see above | 1XUD7 | 1 | 67.35 | 7610 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
LED-PK-91 LPW-5600 lm | Parking | Site Lighting Fixture | 59 | 1 | 59 | 100000 | 588 | grainger.com | 53VR14 |  | 0 |  |  | 531 | 2.963 | 152.5945 | 2556-36.20-1950 | 0 | 0 | 1000 |  | 50000 | 155.5 | see above | 1XUD7 | 1 | 67.35 | 7610 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
LED-PK-92 LPW-13000 lm | Parking | Site Lighting Fixture | 141 | 1 | 141 | 100000 | 840 | grainger.com | 45HE17 |  | 0 |  |  | 840 | 2.963 | 152.5945 | 2556-36.20-1950 | 0 | 0 | 1000 |  | 50000 | 155.5 | see above | 1XUD7 | 1 | 67.35 | 7610 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
LED-PK-102 LPW-28700 lm | Parking | Site Lighting Fixture | 281 | 1 | 281 | 100000 | 1021 | grainger.com | 53CJ35 |  | 0 |  |  | 1021 | 2.963 | 152.5945 | 2556-36.20-1950 | 0 | 0 | 1000 |  | 50000 | 155.5 | see above | 1XUD7 | 1 | 67.35 | 7610 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
LED-PK-107 LPW-30200 lm | Parking | Site Lighting Fixture | 281 | 1 | 281 | 100000 | 1021 | grainger.com | 53CJ30 |  | 0 |  |  | 1021 | 2.963 | 152.5945 | 2556-36.20-1950 | 0 | 0 | 1000 |  | 50000 | 155.5 | see above | 1XUD7 | 1 | 67.35 | 7610
LED-PK-109 LPW-14500 lm | Parking | Site Lighting Fixture | 134 | 1 | 134 | 100000 | 1100 | grainger.com | 45HE19 |  | 0 |  |  | 1100 | 2.963 | 152.5945 | 2556-36.20-1950 | 0 | 0 | 1000 |  | 50000 | 155.5 | see above | 1XUD7 | 1 | 67.35 | 7610 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
LED-PK-116 LPW-16040 lm | Parking | Site Lighting Fixture | 138 | 1 | 134 | 100000 | 1408 | grainger.com | 22EL87 |  | 0 |  |  | 1408 | 2.963 | 152.5945 | 2556-36.20-1950 | 0 | 0 | 1000 |  | 50000 | 155.5 | see above | 1XUD7 | 1 | 67.35 | 7610 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
MH-PR-250-P | Parking | Floodlight | 250 | 1 | 295 | 10000 | 300 | Goodmart | MEGH250SFPSQ | ED28 | 15.6 | as above | 2V712 | 315.6 | 2.963 | 152.5945 | 2556-36.20-1950 | 0.26667 | 17.9602 | 1100 | Probe Start 1 Lamp | 50000 | 126.7 | see above | 1XUE1 | 1 | 67.35 | 7620
MH-PR-360-P | Parking | Security Lighting | 360 | 1 | 400 | 20000 | 562 | Grainger #403 2012/2013 Ref | 3JXC6 | ED37 | 65.2 | as above | 5XN61 | 627.2 | 3.636 | 244.8846 | 2556-36.20-2000 | 0.26667 | 17.9602 | 1200 | Probe Start 1 Lamp | 50000 | 156.5 | est. same as 400 | 1FYG3 | 1.143 | 76.981 | 7630
MH-PR-400-F | Parking | Security Lighting | 400 | 1 | 460 | 20000 | 562 | Grainger #403 2012/2013 Ref | 3JXC6 | ED37 | 86.6 | as above | 6XV25 | 0 | 3.636 | 244.8846 | 2556-36.20-2000 | 0.26667 | 17.9602 | 1200 | Probe Start 1 Lamp | 50000 | 156.5 | see above | 1FYG3 | 1.143 | 76.981 | 7630
MH-PR-400-P | Parking | Security Lighting | 400 | 1 | 460 | 20000 | 562 | Grainger #403 2012/2013 Ref | 3JXC6 | ED37 | 86.6 | as above | 6XV25 | 0 | 3.636 | 244.8846 | 2556-36.20-2000 | 0.26667 | 17.9602 | 1200 | Probe Start 1 Lamp | 50000 | 156.5 | see above | 1FYG3 | 1.143 | 76.981 | 7630
MH-PR-1000-P | Parking | Mounted Floodlight | 1000 | 1 | 1076 | 12000 | 679 | Goodmart | MPNK-S76-1000- 277V-F1-AP-LL | BT37 | 66.3 | as above | 2YGE1 | 745.3 | 4 | 269.4 | 2556-36.20-2200 | 0.4 | 26.94 | 1300 | Probe Start 1 Lamp | 50000 | 240.75 | see above | 1XUE5 | 1.333 | 89.7776 | 7640
CFL-32-D | Door | Wall Pack | 32 | 2 | 72 | 12000 | 143 | 1000bulbs | WPTF42 1 or 2 lamp | Three Tube 4 pin | 75.3 | as above | 1PHA4 | 293.6 | 1 | 67.35 | 2556-23.10-0200 | 0.08889 | 5.9867 | 0560 | Electronic CF Ballast Programmed Start 1 or 2 Lamps | 40000 | 40.7 | see above | 4KGJ8 |  | 0
Linear Fluorescent T-8 32 W Lamps
F-28-F | Façade | High Abuse Fixture | 32 | 1 | 28 | 30000 | 292.5 | Grainger #403 2012/2013 Ref | 3FB62 | T8 - Bi-Pin Base | 5.81 | as above | 4WW56 | 298.31 | 2 | 134.7 | 2556-36.20-1180 | 0.08889 | 5.9867 | 0180 | Electronic Instant Start 1 Lamp | 40000 | 46.6 | see above | 5PTN3 | 1 | 67.35 | 2651-13.50-7630
F-36-F | Façade | High Abuse Fixture | 32 | 1 | 36 | 30000 | 292.5 | Grainger #403 2012/2013 Ref | 3FB62 | T8 - Bi-Pin Base | 5.81 | as above | 4WW56 | 298.31 | 2 | 134.7 | 2556-36.20-1180 | 0.08889 | 5.9867 | 0180 | Electronic Instant Start 1 Lamp | 40000 | 28.65 | see above | 1PCV8 | 1 | 67.35 | 2651-13.50-7630
F-2L-48-F | Façade | High Abuse Fixture | 32 | 2 | 48 | 30000 | 315.75 | Grainger #403 2012/2013 Ref | 3FB60 | T8 - Bi-Pin Base | 5.81 | as above | 4WW56 | 327.37 | 2 | 103.5 | 2556-36.20-1180 | 0.13334 | 6.9001 | 0180 | Electronic Ballast Instant Start 2 Lamp | 40000 | 40.1 | see above | 4XLC9 | 1 | 51.75 | 2651-13.50-7630
None | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
LED-Wall-85 LPW-2300 lm | Door | Wall Pack | 26 | 1 | 26 | 100000 | 627 | grainger.com | 31A146 |  | 0 |  |  | 627 | 1 | 67.35 | 2556-23.10-0200 | 0 | 0 |  |  | 100000 | 313.5 |  | Assumes 50% of fixture cost | 1 | 67.35
LED-Wall-97 LPW-2700 lm | Door | Wall Pack | 28 | 1 | 28 | 60000 | 347 | grainger.com | 53VY41 |  | 0 |  |  | 347 | 1 | 67.35 | 2556-23.10-0200 | 0 | 0 |  |  | 60000 | 173.5 |  | Assumes 50% of fixture cost | 1 | 67.35
LED-Wall-101 LPW-2800 lm | Door | Wall Pack | 28 | 1 | 28 | 100000 | 676 | grainger.com | 53WA35 |  | 0 |  |  | 676 | 1 | 67.35 | 2556-23.10-0200 | 0 | 0 |  |  | 100000 | 338 |  | Assumes 50% of fixture cost | 1 | 67.35
LED-Wall-103 LPW-2900 lm | Door | Wall Pack | 28 | 1 | 28 | 100000 | 649 | grainger.com | 53WA53 |  | 0 |  |  | 649 | 1 | 67.35 | 2556-23.10-0200 | 0 |  |  |  | 100000 | 324.5 |  | Assumes 50% of fixture cost | 1 | 67.35
LED-Wall-86 LPW-7700 lm | Door | Wall Pack | 83 | 1 | 83 | 60000 | 523 | grainger.com | 53VZ13 |  | 0 |  |  | 523 | 1 | 67.35 | 2556-23.10-0200 | 0 | 0 |  |  | 60000 | 261.5 |  | Assumes 50% of fixture cost | 1 | 67.35
LED-Wall-101 LPW-8000 lm | Door | Wall Pack | 80 | 1 | 83 | 60000 | 485.5 | grainger.com | 53XX85 |  | 0 |  |  | 485.5 | 1 | 67.35 | 2556-23.10-0200 | 0 | 0 |  |  | 60000 | 242.75 |  | Assumes 50% of fixture cost | 1 | 67.35

## Env_Proto
[12 empty] | 90.1 Cost Effectiveness - Cost Estimate - Envelope, Power, Other | [14 empty] | 2007
Actual climate zones change with each state selected
[6 empty] | SO | LO | SR | PS | SH | MA | Item and Addenda / Affected Prototype and Item |  | Base Code Envelope | 2019 |  |  |  | Target Code Envelope | 2022 | [6 empty] | Base Code Costs | [19 empty] | Target Code
| Climate Zones Affected |  |  |  |  | Prototypes Affected | [17 empty] | Other Cost Parameters |  |  | New Construction Costs | [9 empty] | Maintenance Cost | Replacement Costs (none) | [8 empty] | New Construction Costs | [10 empty] | Maintenance Costs | Replacement Costs
Code Check = 1 to include | CZ_1 | CZ_2 | CZ_3 | CZ_4 | CZ_5 | Small Office | Large Office | Standalone Retail | Primary School | Small Hotel | Mid-rise Apartment |  | Climate Zone & Prototype | Description of cost items | Source | Not Used | Varies, see below | Varies, see below | Description of Cost Items | Source |  | Varies, see below | Varies, see below |  |  |  | Material $/UoM (if applicable) | Material Subtotal |  | Labor $/ft2 |  | Labor Subtotal | Construction Equipment $/UoM (if applicable) | Construction Equipment Subtotal | Cost Adjustments | Total | Annual Main- tenance (none) | Replacement Life years | Material Subtotal |  | Labor Cost/ hour | Labor Hours | Labor Subtotal with replacement hour adjustment | Construction Equipment Subtotal | Cost Adjustments | Total | Material $/UoM (if applicable) | Material Subtotal |  | Labor $/ft2 |  | Labor Subtotal | Construction Equipment Subtotal | Construction Equipment Subtotal | Cost Adjustments | Added Commis- sioning | Total Cost | Annual Main- tenance Cost | Replace- ment Life (years) | Material Subtotal | Labor Crew | Labor Cost/ hour | Labor Hours | Labor Subtotal with replacement hour adjustment | Construction Equipment Subtotal | Cost Adjustments | Added Commis- sioning | Total | New Construction Costs Target minus Base for verification
| 2A | 3A | 3B | 4A | 5A | [6 empty] | Building Envelope
[12 empty] | Building Insulation and Windows |  | Base code envelope cost. Values for material and labor cost per area of assembly including all cost adjustments except general contractor and contingency. Cost with adjustment adds the general contractor and contingency only. | Faithful and Gould Envelope Cost Database See "Envelope Comp" sheet in this workbook for additional descriptions |  | Area, ft2 or # doors | Slab Insulation Area (slab perimeter x insulation depth), ft2 | Target code envelope cost. Values for material and labor cost per area of assembly including all cost adjustments except general contractor and contingency. Cost with adjustment adds the general contractor and contingency only. |  |  | Area, ft2 or # doors | Slab Insulation Area (slab perimeter x insulation depth), ft2 |  |  | Slab-on-grade Slab only (Used for base code and target code), $/ft2 | Material $/ft2 |  |  | Slab-on-grade Slab only Labor (Used for base code and target code) $/ft2 | Labor $/ft2 (for slab-on-grade, this labor is for insulation only) |  | Construction Equipment $/ft2 or $/ft for slab edge |  | General Contractor Markup and Contingency Only other cost adjustments incorporated in envelope unit costs | [9 empty] | Additional Replacement Overhead and General Contractor Markup and Contingency P other cost adjustments incorporated in envelope unit costs |  | Material $/ft2 |  |  |  | Labor $/ft2 (for slab-on-grade, this labor is for insulation only) |  | Construction Equipment $/ft2 or $/ft for slab edge |  | General Contractor Markup and Contingency Only other cost adjustments incorporated in envelope unit costs
[15 empty] | Base Code Requirement - opaque u-factor, F-factor for slab on grade, or u-factor/SHGC for windows and skylights | [11 empty] | For slab-on-grade, this represents the cost of insulation in $/ft2 of insulation area. If no insulation is required, this cost is zero. | [19 empty] | For slab-on-grade, this represents the cost of insulation in $/ft2 of insulation area. If no insulation is required, this cost is zero.
[13 empty] | _SO | Small Office |  |  |  |  | Small Office | [49 empty] | 0 | SO
| 1 | 1 | 1 |  |  | 1 | [6 empty] | 2-3SO | 21sf_Door_0.7unins | Means/Lowes |  | 2 |  | 21sf_Door_0.37_insPU | Means/Lowes |  | 2 |  |  |  |  | 455 | 910 |  |  | 47.5 | 95 | 0 | 0 | 150.75 | 1155.75 |  | 40 | 910 |  |  |  | 156.75 | 0 | 160.0125 | 1226.7625 | 483.3689 | 966.7378 |  |  | 47.5 | 95 | 0 | 0 | 159.2607 |  | 1220.9985 |  | 40 | 966.7378 |  |  |  | 156.75 | 0 | 187.7063 |  | 1311.1941 | 65.2485 | SO
| 1 |  |  |  |  | 1 | [6 empty] | 2SO | Windows | 0.46, 0.25 |  | 642.4528 |  | Windows | #N/A |  | 642.4528 |  |  |  |  | 16.703 | 10730.8739 |  |  | 33.8448 | 21743.687 | 0 | 0 | 4871.1841 | 37345.745 |  | 40 | 10730.8739 |  |  |  | 35877.0835 | 0 | 6991.1936 | 53599.151 | #N/A | #N/A |  |  | #N/A | #N/A | #N/A | #N/A | #N/A |  | #N/A |  | 40 | #N/A |  |  |  | #N/A | #N/A | #N/A |  | #N/A | #N/A | SO
|  | 1 |  |  |  | 1 | [6 empty] | 3SO | Windows | 0.42, 0.25 |  | 642.4528 |  | Windows | #N/A |  | 642.4528 |  |  |  |  | 17.0794 | 10972.724 |  |  | 33.8448 | 21743.687 | 0 | 0 | 4907.4616 | 37623.8726 |  | 40 | 10972.724 |  |  |  | 35877.0835 | 0 | 7027.4711 | 53877.2786 | #N/A | #N/A |  |  | #N/A | #N/A | #N/A | #N/A | #N/A |  | #N/A |  | 40 | #N/A |  |  |  | #N/A | #N/A | #N/A |  | #N/A | #N/A | SO
|  |  | 1 |  |  | 1 | [6 empty] | 3SO | Windows | 0.42, 0.25 |  | 642.4528 |  | Windows | #N/A |  | 642.4528 |  |  |  |  | 17.0794 | 10972.724 |  |  | 33.8448 | 21743.687 | 0 | 0 | 4907.4616 | 37623.8726 |  | 40 | 10972.724 |  |  |  | 35877.0835 | 0 | 7027.4711 | 53877.2786 | #N/A | #N/A |  |  | #N/A | #N/A | #N/A | #N/A | #N/A |  | #N/A |  | 40 | #N/A |  |  |  | #N/A | #N/A | #N/A |  | #N/A | #N/A | SO
|  |  |  | 1 | 1 | 1 | [6 empty] | 4-5SO | 21sf_Door_0.5_insPS | Means/Lowes |  | 2 |  | 21sf_Door_0.37_insPU | Means/Lowes |  | 2 |  |  |  |  | 476.33 | 952.66 |  |  | 47.5 | 95 | 0 | 0 | 157.149 | 1204.809 |  | 40 | 952.66 |  |  |  | 156.75 | 0 | 166.4115 | 1275.8215 | 483.3689 | 966.7378 |  |  | 47.5 | 95 | 0 | 0 | 159.2607 |  | 1220.9985 |  | 40 | 966.7378 |  |  |  | 156.75 | 0 | 187.7063 |  | 1311.1941 | 16.1895 | SO
|  |  |  | 1 |  | 1 | [6 empty] | 4SO | Windows | 0.36, 0.36 |  | 642.4528 |  | Windows | #N/A |  | 642.4528 |  |  |  |  | 15.9381 | 10239.4849 |  |  | 33.8448 | 21743.687 | 0 | 0 | 4797.4758 | 36780.6476 |  | 40 | 10239.4849 |  |  |  | 35877.0835 | 0 | 6917.4853 | 53034.0536 | #N/A | #N/A |  |  | #N/A | #N/A | #N/A | #N/A | #N/A |  | #N/A |  | 40 | #N/A |  |  |  | #N/A | #N/A | #N/A |  | #N/A | #N/A | SO
[5 empty] | 1 | 1 | [6 empty] | 5SO | Windows | 0.36, 0.38 |  | 642.4528 |  | Windows | #N/A |  | 642.4528 |  |  |  |  | 15.628 | 10040.2731 |  |  | 33.8448 | 21743.687 | 0 | 0 | 4767.594 | 36551.5541 |  | 40 | 10040.2731 |  |  |  | 35877.0835 | 0 | 6887.6035 | 52804.9601 | #N/A | #N/A |  |  | #N/A | #N/A | #N/A | #N/A | #N/A |  | #N/A |  | 40 | #N/A |  |  |  | #N/A | #N/A | #N/A |  | #N/A | #N/A | SO
[14 empty] | Large Office |  |  |  |  | Large Office | [49 empty] | 0 | LO
| 1 | 1 | 1 |  |  |  | 1 | [5 empty] | 2-3LO | 21sf_Door_0.7unins | Means/Lowes |  | 12 |  | 21sf_Door_0.37_insPU | Means/Lowes |  | 12 |  |  |  |  | 455 | 5460 |  |  | 47.5 | 570 | 0 | 0 | 904.5 | 6934.5 |  | 40 | 5460 |  |  |  | 940.5 | 0 | 960.075 | 7360.575 | 483.3689 | 5800.4268 |  |  | 47.5 | 570 | 0 | 0 | 955.564 |  | 7325.9908 |  | 40 | 5800.4268 |  |  |  | 940.5 | 0 | 1126.238 |  | 7867.1648 | 391.4908 | LO
| 1 | [5 empty] | 1 | [5 empty] | 2LO | Windows | 0.46, 0.25 |  | 49904.2016 |  | Windows | #N/A |  | 49904.2016 |  |  |  |  | 16.703 | 833548.6811 |  |  | 33.8448 | 1688997.7212 | 0 | 0 | 378381.9603 | 2900928.3627 |  | 40 | 833548.6811 |  |  |  | 2786846.24 | 0 | 543059.2382 | 4163454.1593 | #N/A | #N/A |  |  | #N/A | #N/A | #N/A | #N/A | #N/A |  | #N/A |  | 40 | #N/A |  |  |  | #N/A | #N/A | #N/A |  | #N/A | #N/A | LO
|  | 1 |  |  |  |  | 1 | [5 empty] | 3LO | Windows | 0.42, 0.25 |  | 49904.2016 |  | Windows | #N/A |  | 49904.2016 |  |  |  |  | 17.0794 | 852335.018 |  |  | 33.8448 | 1688997.7212 | 0 | 0 | 381199.9109 | 2922532.6501 |  | 40 | 852335.018 |  |  |  | 2786846.24 | 0 | 545877.1887 | 4185058.4467 | #N/A | #N/A |  |  | #N/A | #N/A | #N/A | #N/A | #N/A |  | #N/A |  | 40 | #N/A |  |  |  | #N/A | #N/A | #N/A |  | #N/A | #N/A | LO
|  |  | 1 |  |  |  | 1 | [5 empty] | 3LO | Windows | 0.42, 0.25 |  | 49904.2016 |  | Windows | #N/A |  | 49904.2016 |  |  |  |  | 17.0794 | 852335.018 |  |  | 33.8448 | 1688997.7212 | 0 | 0 | 381199.9109 | 2922532.6501 |  | 40 | 852335.018 |  |  |  | 2786846.24 | 0 | 545877.1887 | 4185058.4467 | #N/A | #N/A |  |  | #N/A | #N/A | #N/A | #N/A | #N/A |  | #N/A |  | 40 | #N/A |  |  |  | #N/A | #N/A | #N/A |  | #N/A | #N/A | LO
|  |  |  | 1 | 1 |  | 1 | [5 empty] | 4-5LO | 21sf_Door_0.5_insPS | Means/Lowes |  | 12 |  | 21sf_Door_0.37_insPU | Means/Lowes |  | 12 |  |  |  |  | 476.33 | 5715.96 |  |  | 47.5 | 570 | 0 | 0 | 942.894 | 7228.854 |  | 40 | 5715.96 |  |  |  | 940.5 | 0 | 998.469 | 7654.929 | 483.3689 | 5800.4268 |  |  | 47.5 | 570 | 0 | 0 | 955.564 |  | 7325.9908 |  | 40 | 5800.4268 |  |  |  | 940.5 | 0 | 1126.238 |  | 7867.1648 | 97.1368 | LO
|  |  |  | 1 |  |  | 1 | [5 empty] | 4LO | Windows | 0.36, 0.36 |  | 49904.2016 |  | Windows | #N/A |  | 49904.2016 |  |  |  |  | 15.9381 | 795378.7539 |  |  | 33.8448 | 1688997.7212 | 0 | 0 | 372656.4713 | 2857032.9464 |  | 40 | 795378.7539 |  |  |  | 2786846.24 | 0 | 537333.7491 | 4119558.743 | #N/A | #N/A |  |  | #N/A | #N/A | #N/A | #N/A | #N/A |  | #N/A |  | 40 | #N/A |  |  |  | #N/A | #N/A | #N/A |  | #N/A | #N/A | LO
[5 empty] | 1 |  | 1 | [5 empty] | 5LO | Windows | 0.36, 0.38 |  | 49904.2016 |  | Windows | #N/A |  | 49904.2016 |  |  |  |  | 15.628 | 779904.459 |  |  | 33.8448 | 1688997.7212 | 0 | 0 | 370335.327 | 2839237.5073 |  | 40 | 779904.459 |  |  |  | 2786846.24 | 0 | 535012.6049 | 4101763.3039 | #N/A | #N/A |  |  | #N/A | #N/A | #N/A | #N/A | #N/A |  | #N/A |  | 40 | #N/A |  |  |  | #N/A | #N/A | #N/A |  | #N/A | #N/A | LO
[13 empty] | _SR | Standalone Retail |  |  |  |  | Standalone Retail | [49 empty] | 0 | SR
| 1 | 1 | 1 |  |  |  |  | 1 |  |  |  |  | 2-3SR | 21sf_Door_0.7unins | Means/Lowes |  | 8 |  | 21sf_Door_0.37_insPU | Means/Lowes |  | 8 |  |  |  |  | 455 | 3640 |  |  | 47.5 | 380 | 0 | 0 | 603 | 4623 |  | 40 | 3640 |  |  |  | 627 | 0 | 640.05 | 4907.05 | 483.3689 | 3866.9512 |  |  | 47.5 | 380 | 0 | 0 | 637.0427 |  | 4883.9939 |  | 40 | 3866.9512 |  |  |  | 627 | 0 | 750.8253 |  | 5244.7765 | 260.9939 | SR
| 1 | 1 | 1 | 1 | 1 |  |  | 1 |  |  |  |  | 2-5SR | 80sf_RU_Door_0.5_insPS | Means/Lowes |  | 5 |  | 80sf_RU_Door_0.31_insPU | Means/Lowes |  | 5 |  |  |  |  | 925 | 4625 |  |  | 585 | 2925 | 0 | 0 | 1132.5 | 8682.5 |  | 40 | 4625 |  |  |  | 4826.25 | 0 | 1417.6875 | 10868.9375 | 1006.27 | 5031.35 |  |  | 666.27 | 3331.35 | 0 | 0 | 1254.405 |  | 9617.105 |  | 40 | 5031.35 |  |  |  | 5496.7275 | 0 | 1747.1571 |  | 12275.2346 | 934.605 | SR
| 1 | [6 empty] | 1 |  |  |  |  | 2SR | Windows | 0.45, 0.25 |  | 903.6107 |  | Windows | #N/A |  | 903.6107 |  |  |  |  | 19.9158 | 17996.167 |  |  | 31.7976 | 28732.6529 | 0 | 0 | 7009.323 | 53738.1429 |  | 40 | 17996.167 |  |  |  | 47408.8774 | 0 | 9810.7566 | 75215.801 | #N/A | #N/A |  |  | #N/A | #N/A | #N/A | #N/A | #N/A |  | #N/A |  | 40 | #N/A |  |  |  | #N/A | #N/A | #N/A |  | #N/A | #N/A | SR
|  | 1 | [5 empty] | 1 |  |  |  |  | 3SR | Windows | 0.42, 0.25 |  | 903.6107 |  | Windows | #N/A |  | 903.6107 |  |  |  |  | 20.2009 | 18253.7466 |  |  | 31.7976 | 28732.6529 | 0 | 0 | 7047.9599 | 54034.3595 |  | 40 | 18253.7466 |  |  |  | 47408.8774 | 0 | 9849.3936 | 75512.0176 | #N/A | #N/A |  |  | #N/A | #N/A | #N/A | #N/A | #N/A |  | #N/A |  | 40 | #N/A |  |  |  | #N/A | #N/A | #N/A |  | #N/A | #N/A | SR
|  |  | 1 |  |  |  |  | 1 |  |  |  |  | 3SR | Windows | 0.42, 0.25 |  | 903.6107 |  | Windows | #N/A |  | 903.6107 |  |  |  |  | 20.2009 | 18253.7466 |  |  | 31.7976 | 28732.6529 | 0 | 0 | 7047.9599 | 54034.3595 |  | 40 | 18253.7466 |  |  |  | 47408.8774 | 0 | 9849.3936 | 75512.0176 | #N/A | #N/A |  |  | #N/A | #N/A | #N/A | #N/A | #N/A |  | #N/A |  | 40 | #N/A |  |  |  | #N/A | #N/A | #N/A |  | #N/A | #N/A | SR
|  |  |  | 1 | 1 |  |  | 1 |  |  |  |  | 4-5SR | 21sf_Door_0.5_insPS | Means/Lowes |  | 8 |  | 21sf_Door_0.37_insPU | Means/Lowes |  | 8 |  |  |  |  | 476.33 | 3810.64 |  |  | 47.5 | 380 | 0 | 0 | 628.596 | 4819.236 |  | 40 | 3810.64 |  |  |  | 627 | 0 | 665.646 | 5103.286 | 483.3689 | 3866.9512 |  |  | 47.5 | 380 | 0 | 0 | 637.0427 |  | 4883.9939 |  | 40 | 3866.9512 |  |  |  | 627 | 0 | 750.8253 |  | 5244.7765 | 64.7579 | SR
|  |  |  | 1 |  |  |  | 1 |  |  |  |  | 4SR | Windows | 0.36, 0.36 |  | 903.6107 |  | Windows | #N/A |  | 903.6107 |  |  |  |  | 19.1978 | 17347.3022 |  |  | 31.7976 | 28732.6529 | 0 | 0 | 6911.9933 | 52991.9484 |  | 40 | 17347.3022 |  |  |  | 47408.8774 | 0 | 9713.4269 | 74469.6064 | #N/A | #N/A |  |  | #N/A | #N/A | #N/A | #N/A | #N/A |  | #N/A |  | 40 | #N/A |  |  |  | #N/A | #N/A | #N/A |  | #N/A | #N/A | SR
[5 empty] | 1 |  |  | 1 |  |  |  |  | 5SR | Windows | 0.36, 0.38 |  | 903.6107 |  | Windows | #N/A |  | 903.6107 |  |  |  |  | 18.9116 | 17088.7394 |  |  | 31.7976 | 28732.6529 | 0 | 0 | 6873.2088 | 52694.6012 |  | 40 | 17088.7394 |  |  |  | 47408.8774 | 0 | 9674.6425 | 74172.2592 | #N/A | #N/A |  |  | #N/A | #N/A | #N/A | #N/A | #N/A |  | #N/A |  | 40 | #N/A |  |  |  | #N/A | #N/A | #N/A |  | #N/A | #N/A | SR
[13 empty] | _PS | Primary School |  |  |  |  | Primary School | [49 empty] | 0 | PS
| 1 | 1 | 1 | [5 empty] | 1 |  |  |  | 2-3PS | 21sf_Door_0.7unins | Means/Lowes |  | 25 |  | 21sf_Door_0.37_insPU | Means/Lowes |  | 25 |  |  |  |  | 455 | 11375 |  |  | 47.5 | 1187.5 | 0 | 0 | 1884.375 | 14446.875 |  | 40 | 11375 |  |  |  | 1959.375 | 0 | 2000.1562 | 15334.5312 | 483.3689 | 12084.2225 |  |  | 47.5 | 1187.5 | 0 | 0 | 1990.7584 |  | 15262.4809 |  | 40 | 12084.2225 |  |  |  | 1959.375 | 0 | 2346.3291 |  | 16389.9266 | 815.6059 | PS
| 1 | [7 empty] | 1 |  |  |  | 2PS | Windows | 0.47, 0.25 |  | 9464.5528 |  | Windows | #N/A |  | 9464.5528 |  |  |  |  | 23.8087 | 225338.7369 |  |  | 28.3704 | 268513.1497 | 0 | 0 | 74077.783 | 567929.6695 |  | 40 | 225338.7369 |  |  |  | 443046.6969 | 0 | 100257.8151 | 768643.2489 | #N/A | #N/A |  |  | #N/A | #N/A | #N/A | #N/A | #N/A |  | #N/A |  | 40 | #N/A |  |  |  | #N/A | #N/A | #N/A |  | #N/A | #N/A | PS
|  | 1 | [6 empty] | 1 |  |  |  | 3PS | Windows | 0.43, 0.25 |  | 9464.5528 |  | Windows | #N/A |  | 9464.5528 |  |  |  |  | 24.1547 | 228613.3207 |  |  | 28.3704 | 268513.1497 | 0 | 0 | 74568.9706 | 571695.4409 |  | 40 | 228613.3207 |  |  |  | 443046.6969 | 0 | 100749.0026 | 772409.0203 | #N/A | #N/A |  |  | #N/A | #N/A | #N/A | #N/A | #N/A |  | #N/A |  | 40 | #N/A |  |  |  | #N/A | #N/A | #N/A |  | #N/A | #N/A | PS
|  |  | 1 | [5 empty] | 1 |  |  |  | 3PS | Windows | 0.43, 0.25 |  | 9464.5528 |  | Windows | #N/A |  | 9464.5528 |  |  |  |  | 24.1547 | 228613.3207 |  |  | 28.3704 | 268513.1497 | 0 | 0 | 74568.9706 | 571695.4409 |  | 40 | 228613.3207 |  |  |  | 443046.6969 | 0 | 100749.0026 | 772409.0203 | #N/A | #N/A |  |  | #N/A | #N/A | #N/A | #N/A | #N/A |  | #N/A |  | 40 | #N/A |  |  |  | #N/A | #N/A | #N/A |  | #N/A | #N/A | PS
|  |  |  | 1 | 1 |  |  |  | 1 |  |  |  | 4-5PS | 21sf_Door_0.5_insPS | Means/Lowes |  | 25 |  | 21sf_Door_0.37_insPU | Means/Lowes |  | 25 |  |  |  |  | 476.33 | 11908.25 |  |  | 47.5 | 1187.5 | 0 | 0 | 1964.3625 | 15060.1125 |  | 40 | 11908.25 |  |  |  | 1959.375 | 0 | 2080.1438 | 15947.7687 | 483.3689 | 12084.2225 |  |  | 47.5 | 1187.5 | 0 | 0 | 1990.7584 |  | 15262.4809 |  | 40 | 12084.2225 |  |  |  | 1959.375 | 0 | 2346.3291 |  | 16389.9266 | 202.3684 | PS
|  |  |  | 1 |  |  |  |  | 1 |  |  |  | 4PS | Windows | 0.37, 0.36 |  | 9464.5528 |  | Windows | #N/A |  | 9464.5528 |  |  |  |  | 23.1287 | 218902.8409 |  |  | 28.3704 | 268513.1497 | 0 | 0 | 73112.3986 | 560528.3892 |  | 40 | 218902.8409 |  |  |  | 443046.6969 | 0 | 99292.4307 | 761241.9686 | #N/A | #N/A |  |  | #N/A | #N/A | #N/A | #N/A | #N/A |  | #N/A |  | 40 | #N/A |  |  |  | #N/A | #N/A | #N/A |  | #N/A | #N/A | PS
[5 empty] | 1 |  |  |  | 1 |  |  |  | 5PS | Windows | 0.37, 0.38 |  | 9464.5528 |  | Windows | #N/A |  | 9464.5528 |  |  |  |  | 22.8469 | 216235.8057 |  |  | 28.3704 | 268513.1497 | 0 | 0 | 72712.3433 | 557461.2986 |  | 40 | 216235.8057 |  |  |  | 443046.6969 | 0 | 98892.3754 | 758174.878 | #N/A | #N/A |  |  | #N/A | #N/A | #N/A | #N/A | #N/A |  | #N/A |  | 40 | #N/A |  |  |  | #N/A | #N/A | #N/A |  | #N/A | #N/A | PS
[13 empty] | _SH | Small Hotel - Residential |  |  |  |  | Small Hotel - Residential | [49 empty] | 0 | SH
[13 empty] | 2-5SH | Note: sliding exterior doors in rooms are modeled as fenestration. |  |  |  |  | Note: sliding exterior doors in rooms are modeled as fenestration. | [50 empty] | SH
| 1 | [8 empty] | 1 |  |  | 2SH | Windows | 0.46, 0.25 |  | 1420.33 |  | Windows | #N/A |  | 1420.33 |  |  |  |  | 20.3282 | 28872.7409 |  |  | 31.158 | 44254.6421 | 0 | 0 | 10969.1075 | 84096.4905 |  | 40 | 28872.7409 |  |  |  | 73020.1595 | 0 | 15283.9351 | 117176.8355 | #N/A | #N/A |  |  | #N/A | #N/A | #N/A | #N/A | #N/A |  | #N/A |  | 40 | #N/A |  |  |  | #N/A | #N/A | #N/A |  | #N/A | #N/A | SH
|  | 1 | [7 empty] | 1 |  |  | 3SH | Windows | 0.43, 0.25 |  | 1420.33 |  | Windows | #N/A |  | 1420.33 |  |  |  |  | 20.5556 | 29195.7126 |  |  | 31.158 | 44254.6421 | 0 | 0 | 11017.5532 | 84467.908 |  | 40 | 29195.7126 |  |  |  | 73020.1595 | 0 | 15332.3808 | 117548.253 | #N/A | #N/A |  |  | #N/A | #N/A | #N/A | #N/A | #N/A |  | #N/A |  | 40 | #N/A |  |  |  | #N/A | #N/A | #N/A |  | #N/A | #N/A | SH
|  |  | 1 | [6 empty] | 1 |  |  | 3SH | Windows | 0.43, 0.25 |  | 1420.33 |  | Windows | #N/A |  | 1420.33 |  |  |  |  | 20.5556 | 29195.7126 |  |  | 31.158 | 44254.6421 | 0 | 0 | 11017.5532 | 84467.908 |  | 40 | 29195.7126 |  |  |  | 73020.1595 | 0 | 15332.3808 | 117548.253 | #N/A | #N/A |  |  | #N/A | #N/A | #N/A | #N/A | #N/A |  | #N/A |  | 40 | #N/A |  |  |  | #N/A | #N/A | #N/A |  | #N/A | #N/A | SH
|  |  |  | 1 | [5 empty] | 1 |  |  | 4SH | Windows | 0.37, 0.36 |  | 1420.33 |  | Windows | #N/A |  | 1420.33 |  |  |  |  | 19.0672 | 27081.7162 |  |  | 31.158 | 44254.6421 | 0 | 0 | 10700.4537 | 82036.8121 |  | 40 | 27081.7162 |  |  |  | 73020.1595 | 0 | 15015.2814 | 115117.1571 | #N/A | #N/A |  |  | #N/A | #N/A | #N/A | #N/A | #N/A |  | #N/A |  | 40 | #N/A |  |  |  | #N/A | #N/A | #N/A |  | #N/A | #N/A | SH
[5 empty] | 1 |  |  |  |  | 1 |  |  | 5SH | Windows | 0.37, 0.38 |  | 1420.33 |  | Windows | #N/A |  | 1420.33 |  |  |  |  | 18.7136 | 26579.4875 |  |  | 31.158 | 44254.6421 | 0 | 0 | 10625.1194 | 81459.2491 |  | 40 | 26579.4875 |  |  |  | 73020.1595 | 0 | 14939.9471 | 114539.5941 | #N/A | #N/A |  |  | #N/A | #N/A | #N/A | #N/A | #N/A |  | #N/A |  | 40 | #N/A |  |  |  | #N/A | #N/A | #N/A |  | #N/A | #N/A | SH
[13 empty] | _SHNR | Small Hotel - Non-residential |  |  |  |  | Small Hotel - Non-residential | [49 empty] | 0 | SHNR
| 1 | 1 | 1 | [6 empty] | 1 |  |  | 2-3SHNR | 21sf_Door_0.7unins | Means/Lowes |  | 3 |  | 21sf_Door_0.37_insPU | Means/Lowes |  | 3 |  |  |  |  | 455 | 1365 |  |  | 47.5 | 142.5 | 0 | 0 | 226.125 | 1733.625 |  | 40 | 1365 |  |  |  | 235.125 | 0 | 240.0188 | 1840.1437 | 483.3689 | 1450.1067 |  |  | 47.5 | 142.5 | 0 | 0 | 238.891 |  | 1831.4977 |  | 40 | 1450.1067 |  |  |  | 235.125 | 0 | 281.5595 |  | 1966.7912 | 97.8727 | SHNR
| 1 | [8 empty] | 1 |  |  | 2SHNR | Windows | 0.46, 0.25 |  | 567.53 |  | Windows | #N/A |  | 567.53 |  |  |  |  | 20.3282 | 11536.8588 |  |  | 31.158 | 17683.0997 | 0 | 0 | 4382.9938 | 33602.9523 |  | 40 | 11536.8588 |  |  |  | 29177.1146 | 0 | 6107.096 | 46821.0694 | #N/A | #N/A |  |  | #N/A | #N/A | #N/A | #N/A | #N/A |  | #N/A |  | 40 | #N/A |  |  |  | #N/A | #N/A | #N/A |  | #N/A | #N/A | SHNR
|  | 1 | [7 empty] | 1 |  |  | 3SHNR | Windows | 0.43, 0.25 |  | 567.53 |  | Windows | #N/A |  | 567.53 |  |  |  |  | 20.5556 | 11665.9106 |  |  | 31.158 | 17683.0997 | 0 | 0 | 4402.3515 | 33751.3619 |  | 40 | 11665.9106 |  |  |  | 29177.1146 | 0 | 6126.4538 | 46969.4789 | #N/A | #N/A |  |  | #N/A | #N/A | #N/A | #N/A | #N/A |  | #N/A |  | 40 | #N/A |  |  |  | #N/A | #N/A | #N/A |  | #N/A | #N/A | SHNR
|  |  | 1 | [6 empty] | 1 |  |  | 3SHNR | Windows | 0.43, 0.25 |  | 567.53 |  | Windows | #N/A |  | 567.53 |  |  |  |  | 20.5556 | 11665.9106 |  |  | 31.158 | 17683.0997 | 0 | 0 | 4402.3515 | 33751.3619 |  | 40 | 11665.9106 |  |  |  | 29177.1146 | 0 | 6126.4538 | 46969.4789 | #N/A | #N/A |  |  | #N/A | #N/A | #N/A | #N/A | #N/A |  | #N/A |  | 40 | #N/A |  |  |  | #N/A | #N/A | #N/A |  | #N/A | #N/A | SHNR
|  |  |  | 1 | 1 |  |  |  |  | 1 |  |  | 4-5SHNR | 21sf_Door_0.5_insPS | Means/Lowes |  | 3 |  | 21sf_Door_0.37_insPU | Means/Lowes |  | 3 |  |  |  |  | 476.33 | 1428.99 |  |  | 47.5 | 142.5 | 0 | 0 | 235.7235 | 1807.2135 |  | 40 | 1428.99 |  |  |  | 235.125 | 0 | 249.6173 | 1913.7323 | 483.3689 | 1450.1067 |  |  | 47.5 | 142.5 | 0 | 0 | 238.891 |  | 1831.4977 |  | 40 | 1450.1067 |  |  |  | 235.125 | 0 | 281.5595 |  | 1966.7912 | 24.2842 | SHNR
|  |  |  | 1 | [5 empty] | 1 |  |  | 4SHNR | Windows | 0.37, 0.36 |  | 567.53 |  | Windows | #N/A |  | 567.53 |  |  |  |  | 19.0672 | 10821.208 |  |  | 31.158 | 17683.0997 | 0 | 0 | 4275.6462 | 32779.9539 |  | 40 | 10821.208 |  |  |  | 29177.1146 | 0 | 5999.7484 | 45998.071 | #N/A | #N/A |  |  | #N/A | #N/A | #N/A | #N/A | #N/A |  | #N/A |  | 40 | #N/A |  |  |  | #N/A | #N/A | #N/A |  | #N/A | #N/A | SHNR
[5 empty] | 1 |  |  |  |  | 1 |  |  | 5SHNR | Windows | 0.37, 0.38 |  | 567.53 |  | Windows | #N/A |  | 567.53 |  |  |  |  | 18.7136 | 10620.5294 |  |  | 31.158 | 17683.0997 | 0 | 0 | 4245.5444 | 32549.1735 |  | 40 | 10620.5294 |  |  |  | 29177.1146 | 0 | 5969.6466 | 45767.2906 | #N/A | #N/A |  |  | #N/A | #N/A | #N/A | #N/A | #N/A |  | #N/A |  | 40 | #N/A |  |  |  | #N/A | #N/A | #N/A |  | #N/A | #N/A | SHNR
[13 empty] | _MA | Mid-rise Apartment |  |  |  |  | Mid-rise Apartment | [50 empty] | MA
[13 empty] | 2-5MA | Note: Sliding doors in Apartment are modeled as fenestration |  |  |  |  | Note: Sliding doors in Apartment are modeled as fenestration | [50 empty] | MA
| 1 | [9 empty] | 1 |  | 2MA | Windows | 0.49, 0.25 |  | 3303.9815 |  | Windows | #N/A |  | 3303.9815 |  |  |  |  | 27.5025 | 90867.6329 |  |  | 25.5876 | 84540.9576 | 0 | 0 | 26311.2886 | 201719.8791 |  | 40 | 90867.6329 |  |  |  | 139492.5801 | 0 | 34554.0319 | 264914.2449 | #N/A | #N/A |  |  | #N/A | #N/A | #N/A | #N/A | #N/A |  | #N/A |  | 40 | #N/A |  |  |  | #N/A | #N/A | #N/A |  | #N/A | #N/A | MA
|  | 1 | [8 empty] | 1 |  | 3MA | Windows | 0.45, 0.25 |  | 3303.9815 |  | Windows | #N/A |  | 3303.9815 |  |  |  |  | 27.7614 | 91723.1791 |  |  | 25.5876 | 84540.9576 | 0 | 0 | 26439.6205 | 202703.7572 |  | 40 | 91723.1791 |  |  |  | 139492.5801 | 0 | 34682.3639 | 265898.123 | #N/A | #N/A |  |  | #N/A | #N/A | #N/A | #N/A | #N/A |  | #N/A |  | 40 | #N/A |  |  |  | #N/A | #N/A | #N/A |  | #N/A | #N/A | MA
|  |  | 1 | [7 empty] | 1 |  | 3MA | Windows | 0.45, 0.25 |  | 3303.9815 |  | Windows | #N/A |  | 3303.9815 |  |  |  |  | 27.7614 | 91723.1791 |  |  | 25.5876 | 84540.9576 | 0 | 0 | 26439.6205 | 202703.7572 |  | 40 | 91723.1791 |  |  |  | 139492.5801 | 0 | 34682.3639 | 265898.123 | #N/A | #N/A |  |  | #N/A | #N/A | #N/A | #N/A | #N/A |  | #N/A |  | 40 | #N/A |  |  |  | #N/A | #N/A | #N/A |  | #N/A | #N/A | MA
|  |  |  | 1 | [6 empty] | 1 |  | 4MA | Windows | 0.38, 0.35 |  | 3303.9815 |  | Windows | #N/A |  | 3303.9815 |  |  |  |  | 26.6419 | 88024.2 |  |  | 25.5876 | 84540.9576 | 0 | 0 | 25884.7736 | 198449.9312 |  | 40 | 88024.2 |  |  |  | 139492.5801 | 0 | 34127.517 | 261644.2971 | #N/A | #N/A |  |  | #N/A | #N/A | #N/A | #N/A | #N/A |  | #N/A |  | 40 | #N/A |  |  |  | #N/A | #N/A | #N/A |  | #N/A | #N/A | MA
[5 empty] | 1 | [5 empty] | 1 |  | 5MA | Windows | 0.38, 0.37 |  | 3303.9815 |  | Windows | #N/A |  | 3303.9815 |  |  |  |  | 26.3274 | 86985.3224 |  |  | 25.5876 | 84540.9576 | 0 | 0 | 25728.942 | 197255.2221 |  | 40 | 86985.3224 |  |  |  | 139492.5801 | 0 | 33971.6854 | 260449.5879 | #N/A | #N/A |  |  | #N/A | #N/A | #N/A | #N/A | #N/A |  | #N/A |  | 40 | #N/A |  |  |  | #N/A | #N/A | #N/A |  | #N/A | #N/A | MA
| 1 |  |  |  |  | 1 | [6 empty] | 2SO | Climate Zone 2A | [55 empty] | SO
| 1 |  |  |  |  | 1 | [6 empty] | 2SO | Roof - Attic and other | #N/A |  | 6445.6274 |  | Roof - Attic and other | #N/A |  | 6445.6274 |  |  |  |  | #N/A | #N/A |  |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A |  | 40 | #N/A |  |  |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A |  |  | #N/A | #N/A | #N/A | #N/A | #N/A |  | #N/A |  | 40 | #N/A |  |  |  | #N/A | #N/A | #N/A |  | #N/A | #N/A | SO
| 1 |  |  |  |  | 1 | [6 empty] | 2SO | Above Ground Wall - Wood-framed | #N/A |  | 2387.9911 |  | Above Ground Wall - Wood-framed | #N/A |  | 2387.9911 |  |  |  |  | #N/A | #N/A |  |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A |  | 40 | #N/A |  |  |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A |  |  | #N/A | #N/A | #N/A | #N/A | #N/A |  | #N/A |  | 40 | #N/A |  |  |  | #N/A | #N/A | #N/A |  | #N/A | #N/A | SO
| 1 |  |  |  |  | 1 | [6 empty] | 2SO | Slab-on-grade - Unheated | #N/A |  | 5493 | #N/A | Slab-on-grade - Unheated | #N/A |  | 5493 | #N/A |  |  | #N/A | #N/A | #N/A |  | #N/A | #N/A | #N/A | #N/A | 0 | #N/A | #N/A |  | 40 | #N/A |  |  |  | #N/A | 0 | #N/A | #N/A | #N/A | #N/A |  |  | #N/A | #N/A | #N/A | #N/A | #N/A |  | #N/A |  | 40 | #N/A |  |  |  | #N/A | #N/A | #N/A |  | #N/A | #N/A | SO
|  | 1 |  |  |  | 1 | [6 empty] | 3SO | Climate Zone 3A |  |  |  |  | Climate Zone 3A | [50 empty] | SO
|  | 1 |  |  |  | 1 | [6 empty] | 3SO | Roof - Attic and other | #N/A |  | 6445.6274 |  | Roof - Attic and other | #N/A |  | 6445.6274 |  |  |  |  | #N/A | #N/A |  |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A |  | 40 | #N/A |  |  |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A |  |  | #N/A | #N/A | #N/A | #N/A | #N/A |  | #N/A |  | 40 | #N/A |  |  |  | #N/A | #N/A | #N/A |  | #N/A | #N/A | SO
|  | 1 |  |  |  | 1 | [6 empty] | 3SO | Above Ground Wall - Wood-framed | #N/A |  | 2387.9911 |  | Above Ground Wall - Wood-framed | #N/A |  | 2387.9911 |  |  |  |  | #N/A | #N/A |  |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A |  | 40 | #N/A |  |  |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A |  |  | #N/A | #N/A | #N/A | #N/A | #N/A |  | #N/A |  | 40 | #N/A |  |  |  | #N/A | #N/A | #N/A |  | #N/A | #N/A | SO
|  | 1 |  |  |  | 1 | [6 empty] | 3SO | Slab-on-grade - Unheated | #N/A |  | 5493 | #N/A | Slab-on-grade - Unheated | #N/A |  | 5493 | #N/A |  |  | #N/A | #N/A | #N/A |  | #N/A | #N/A | #N/A | #N/A | 0 | #N/A | #N/A |  | 40 | #N/A |  |  |  | #N/A | 0 | #N/A | #N/A | #N/A | #N/A |  |  | #N/A | #N/A | #N/A | #N/A | #N/A |  | #N/A |  | 40 | #N/A |  |  |  | #N/A | #N/A | #N/A |  | #N/A | #N/A | SO
|  |  | 1 |  |  | 1 | [6 empty] | 3SO | Climate Zone 3B |  |  |  |  | Climate Zone 3B | [50 empty] | SO
|  |  | 1 |  |  | 1 | [6 empty] | 3SO | Roof - Attic and other | #N/A |  | 6445.6274 |  | Roof - Attic and other | #N/A |  | 6445.6274 |  |  |  |  | #N/A | #N/A |  |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A |  | 40 | #N/A |  |  |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A |  |  | #N/A | #N/A | #N/A | #N/A | #N/A |  | #N/A |  | 40 | #N/A |  |  |  | #N/A | #N/A | #N/A |  | #N/A | #N/A | SO
|  |  | 1 |  |  | 1 | [6 empty] | 3SO | Above Ground Wall - Wood-framed | #N/A |  | 2387.9911 |  | Above Ground Wall - Wood-framed | #N/A |  | 2387.9911 |  |  |  |  | #N/A | #N/A |  |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A |  | 40 | #N/A |  |  |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A |  |  | #N/A | #N/A | #N/A | #N/A | #N/A |  | #N/A |  | 40 | #N/A |  |  |  | #N/A | #N/A | #N/A |  | #N/A | #N/A | SO
|  |  | 1 |  |  | 1 | [6 empty] | 3SO | Slab-on-grade - Unheated | #N/A |  | 5493 | #N/A | Slab-on-grade - Unheated | #N/A |  | 5493 | #N/A |  |  | #N/A | #N/A | #N/A |  | #N/A | #N/A | #N/A | #N/A | 0 | #N/A | #N/A |  | 40 | #N/A |  |  |  | #N/A | 0 | #N/A | #N/A | #N/A | #N/A |  |  | #N/A | #N/A | #N/A | #N/A | #N/A |  | #N/A |  | 40 | #N/A |  |  |  | #N/A | #N/A | #N/A |  | #N/A | #N/A | SO
|  |  |  | 1 |  | 1 | [6 empty] | 4SO | Climate Zone 4A |  |  |  |  | Climate Zone 4A | [50 empty] | SO
|  |  |  | 1 |  | 1 | [6 empty] | 4SO | Roof - Attic and other | #N/A |  | 6445.6274 |  | Roof - Attic and other | #N/A |  | 6445.6274 |  |  |  |  | #N/A | #N/A |  |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A |  | 40 | #N/A |  |  |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A |  |  | #N/A | #N/A | #N/A | #N/A | #N/A |  | #N/A |  | 40 | #N/A |  |  |  | #N/A | #N/A | #N/A |  | #N/A | #N/A | SO
|  |  |  | 1 |  | 1 | [6 empty] | 4SO | Above Ground Wall - Wood-framed | #N/A |  | 2387.9911 |  | Above Ground Wall - Wood-framed | #N/A |  | 2387.9911 |  |  |  |  | #N/A | #N/A |  |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A |  | 40 | #N/A |  |  |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A |  |  | #N/A | #N/A | #N/A | #N/A | #N/A |  | #N/A |  | 40 | #N/A |  |  |  | #N/A | #N/A | #N/A |  | #N/A | #N/A | SO
|  |  |  | 1 |  | 1 | [6 empty] | 4SO | Slab-on-grade - Unheated | #N/A |  | 5493 | #N/A | Slab-on-grade - Unheated | #N/A |  | 5493 | #N/A |  |  | #N/A | #N/A | #N/A |  | #N/A | #N/A | #N/A | #N/A | 0 | #N/A | #N/A |  | 40 | #N/A |  |  |  | #N/A | 0 | #N/A | #N/A | #N/A | #N/A |  |  | #N/A | #N/A | #N/A | #N/A | #N/A |  | #N/A |  | 40 | #N/A |  |  |  | #N/A | #N/A | #N/A |  | #N/A | #N/A | SO
[5 empty] | 1 | 1 | [6 empty] | 5SO | Climate Zone 5A |  |  |  |  | Climate Zone 5A | [50 empty] | SO
[5 empty] | 1 | 1 | [6 empty] | 5SO | Roof - Attic and other | #N/A |  | 6445.6274 |  | Roof - Attic and other | #N/A |  | 6445.6274 |  |  |  |  | #N/A | #N/A |  |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A |  | 40 | #N/A |  |  |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A |  |  | #N/A | #N/A | #N/A | #N/A | #N/A |  | #N/A |  | 40 | #N/A |  |  |  | #N/A | #N/A | #N/A |  | #N/A | #N/A | SO
[5 empty] | 1 | 1 | [6 empty] | 5SO | Above Ground Wall - Wood-framed | #N/A |  | 2387.9911 |  | Above Ground Wall - Wood-framed | #N/A |  | 2387.9911 |  |  |  |  | #N/A | #N/A |  |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A |  | 40 | #N/A |  |  |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A |  |  | #N/A | #N/A | #N/A | #N/A | #N/A |  | #N/A |  | 40 | #N/A |  |  |  | #N/A | #N/A | #N/A |  | #N/A | #N/A | SO
[5 empty] | 1 | 1 | [6 empty] | 5SO | Slab-on-grade - Unheated | #N/A |  | 5493 | #N/A | Slab-on-grade - Unheated | #N/A |  | 5493 | #N/A |  |  | #N/A | #N/A | #N/A |  | #N/A | #N/A | #N/A | #N/A | 0 | #N/A | #N/A |  | 40 | #N/A |  |  |  | #N/A | 0 | #N/A | #N/A | #N/A | #N/A |  |  | #N/A | #N/A | #N/A | #N/A | #N/A |  | #N/A |  | 40 | #N/A |  |  |  | #N/A | #N/A | #N/A |  | #N/A | #N/A | SO
| 1 | [5 empty] | 1 | [5 empty] | 2LO | Climate Zone 2A |  |  |  |  | Climate Zone 2A | [50 empty] | LO
| 1 | [5 empty] | 1 | [5 empty] | 2LO | Roof - Insulation Entirely above Deck | #N/A |  | 38353.3472 |  | Roof - Insulation Entirely above Deck | #N/A |  | 38353.3472 |  |  |  |  | #N/A | #N/A |  |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A |  | 40 | #N/A |  |  |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A |  |  | #N/A | #N/A | #N/A | #N/A | #N/A |  | #N/A |  | 40 | #N/A |  |  |  | #N/A | #N/A | #N/A |  | #N/A | #N/A | LO
| 1 | [5 empty] | 1 | [5 empty] | 2LO | Above Ground Wall - Mass | #N/A |  | 74857.0885 |  | Above Ground Wall - Mass | #N/A |  | 74857.0885 |  |  |  |  | #N/A | #N/A |  |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A |  | 40 | #N/A |  |  |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A |  |  | #N/A | #N/A | #N/A | #N/A | #N/A |  | #N/A |  | 40 | #N/A |  |  |  | #N/A | #N/A | #N/A |  | #N/A | #N/A | LO
| 1 | [5 empty] | 1 | [5 empty] | 2LO | Below Grade wall | #N/A |  | 6396 |  | Below Grade wall | #N/A |  | 6396 |  |  |  |  | #N/A | #N/A |  |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A |  | 40 | #N/A |  |  |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A |  |  | #N/A | #N/A | #N/A | #N/A | #N/A |  | #N/A |  | 40 | #N/A |  |  |  | #N/A | #N/A | #N/A |  | #N/A | #N/A | LO
|  | 1 |  |  |  |  | 1 | [5 empty] | 3LO | Climate Zone 3A |  |  |  |  | Climate Zone 3A | [50 empty] | LO
|  | 1 |  |  |  |  | 1 | [5 empty] | 3LO | Roof - Insulation Entirely above Deck | #N/A |  | 38353.3472 |  | Roof - Insulation Entirely above Deck | #N/A |  | 38353.3472 |  |  |  |  | #N/A | #N/A |  |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A |  | 40 | #N/A |  |  |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A |  |  | #N/A | #N/A | #N/A | #N/A | #N/A |  | #N/A |  | 40 | #N/A |  |  |  | #N/A | #N/A | #N/A |  | #N/A | #N/A | LO
|  | 1 |  |  |  |  | 1 | [5 empty] | 3LO | Above Ground Wall - Mass | #N/A |  | 74857.0885 |  | Above Ground Wall - Mass | #N/A |  | 74857.0885 |  |  |  |  | #N/A | #N/A |  |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A |  | 40 | #N/A |  |  |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A |  |  | #N/A | #N/A | #N/A | #N/A | #N/A |  | #N/A |  | 40 | #N/A |  |  |  | #N/A | #N/A | #N/A |  | #N/A | #N/A | LO
|  | 1 |  |  |  |  | 1 | [5 empty] | 3LO | Below Grade wall | #N/A |  | 6396 |  | Below Grade wall | #N/A |  | 6396 |  |  |  |  | #N/A | #N/A |  |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A |  | 40 | #N/A |  |  |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A |  |  | #N/A | #N/A | #N/A | #N/A | #N/A |  | #N/A |  | 40 | #N/A |  |  |  | #N/A | #N/A | #N/A |  | #N/A | #N/A | LO
|  |  | 1 |  |  |  | 1 | [5 empty] | 3LO | Climate Zone 3B |  |  |  |  | Climate Zone 3B | [50 empty] | LO
|  |  | 1 |  |  |  | 1 | [5 empty] | 3LO | Roof - Insulation Entirely above Deck | #N/A |  | 38353.3472 |  | Roof - Insulation Entirely above Deck | #N/A |  | 38353.3472 |  |  |  |  | #N/A | #N/A |  |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A |  | 40 | #N/A |  |  |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A |  |  | #N/A | #N/A | #N/A | #N/A | #N/A |  | #N/A |  | 40 | #N/A |  |  |  | #N/A | #N/A | #N/A |  | #N/A | #N/A | LO
|  |  | 1 |  |  |  | 1 | [5 empty] | 3LO | Above Ground Wall - Mass | #N/A |  | 74857.0885 |  | Above Ground Wall - Mass | #N/A |  | 74857.0885 |  |  |  |  | #N/A | #N/A |  |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A |  | 40 | #N/A |  |  |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A |  |  | #N/A | #N/A | #N/A | #N/A | #N/A |  | #N/A |  | 40 | #N/A |  |  |  | #N/A | #N/A | #N/A |  | #N/A | #N/A | LO
|  |  | 1 |  |  |  | 1 | [5 empty] | 3LO | Below Grade wall | #N/A |  | 6396 |  | Below Grade wall | #N/A |  | 6396 |  |  |  |  | #N/A | #N/A |  |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A |  | 40 | #N/A |  |  |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A |  |  | #N/A | #N/A | #N/A | #N/A | #N/A |  | #N/A |  | 40 | #N/A |  |  |  | #N/A | #N/A | #N/A |  | #N/A | #N/A | LO
|  |  |  | 1 |  |  | 1 | [5 empty] | 4LO | Climate Zone 4A |  |  |  |  | Climate Zone 4A | [50 empty] | LO
|  |  |  | 1 |  |  | 1 | [5 empty] | 4LO | Roof - Insulation Entirely above Deck | #N/A |  | 38353.3472 |  | Roof - Insulation Entirely above Deck | #N/A |  | 38353.3472 |  |  |  |  | #N/A | #N/A |  |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A |  | 40 | #N/A |  |  |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A |  |  | #N/A | #N/A | #N/A | #N/A | #N/A |  | #N/A |  | 40 | #N/A |  |  |  | #N/A | #N/A | #N/A |  | #N/A | #N/A | LO
|  |  |  | 1 |  |  | 1 | [5 empty] | 4LO | Above Ground Wall - Mass | #N/A |  | 74857.0885 |  | Above Ground Wall - Mass | #N/A |  | 74857.0885 |  |  |  |  | #N/A | #N/A |  |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A |  | 40 | #N/A |  |  |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A |  |  | #N/A | #N/A | #N/A | #N/A | #N/A |  | #N/A |  | 40 | #N/A |  |  |  | #N/A | #N/A | #N/A |  | #N/A | #N/A | LO
|  |  |  | 1 |  |  | 1 | [5 empty] | 4LO | Below Grade wall | #N/A |  | 6396 |  | Below Grade wall | #N/A |  | 6396 |  |  |  |  | #N/A | #N/A |  |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A |  | 40 | #N/A |  |  |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A |  |  | #N/A | #N/A | #N/A | #N/A | #N/A |  | #N/A |  | 40 | #N/A |  |  |  | #N/A | #N/A | #N/A |  | #N/A | #N/A | LO
[5 empty] | 1 |  | 1 | [5 empty] | 5LO | Climate Zone 5A |  |  |  |  | Climate Zone 5A | [50 empty] | LO
[5 empty] | 1 |  | 1 | [5 empty] | 5LO | Roof - Insulation Entirely above Deck | #N/A |  | 38353.3472 |  | Roof - Insulation Entirely above Deck | #N/A |  | 38353.3472 |  |  |  |  | #N/A | #N/A |  |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A |  | 40 | #N/A |  |  |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A |  |  | #N/A | #N/A | #N/A | #N/A | #N/A |  | #N/A |  | 40 | #N/A |  |  |  | #N/A | #N/A | #N/A |  | #N/A | #N/A | LO
[5 empty] | 1 |  | 1 | [5 empty] | 5LO | Above Ground Wall - Mass | #N/A |  | 74857.0885 |  | Above Ground Wall - Mass | #N/A |  | 74857.0885 |  |  |  |  | #N/A | #N/A |  |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A |  | 40 | #N/A |  |  |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A |  |  | #N/A | #N/A | #N/A | #N/A | #N/A |  | #N/A |  | 40 | #N/A |  |  |  | #N/A | #N/A | #N/A |  | #N/A | #N/A | LO
[5 empty] | 1 |  | 1 | [5 empty] | 5LO | Below Grade wall | #N/A |  | 6396 |  | Below Grade wall | #N/A |  | 6396 |  |  |  |  | #N/A | #N/A |  |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A |  | 40 | #N/A |  |  |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A |  |  | #N/A | #N/A | #N/A | #N/A | #N/A |  | #N/A |  | 40 | #N/A |  |  |  | #N/A | #N/A | #N/A |  | #N/A | #N/A | LO
| 1 | [6 empty] | 1 |  |  |  |  | 2SR | Climate Zone 2A |  |  |  |  | Climate Zone 2A | [50 empty] | SR
| 1 | [6 empty] | 1 |  |  |  |  | 2SR | Roof - Insulation Entirely above Deck | #N/A |  | 24695 |  | Roof - Insulation Entirely above Deck | #N/A |  | 24695 |  |  |  |  | #N/A | #N/A |  |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A |  | 40 | #N/A |  |  |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A |  |  | #N/A | #N/A | #N/A | #N/A | #N/A |  | #N/A |  | 40 | #N/A |  |  |  | #N/A | #N/A | #N/A |  | #N/A | #N/A | SR
| 1 | [6 empty] | 1 |  |  |  |  | 2SR | Above Ground Wall - Mass | #N/A |  | 11766.9625 |  | Above Ground Wall - Mass | #N/A |  | 11766.9625 |  |  |  |  | #N/A | #N/A |  |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A |  | 40 | #N/A |  |  |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A |  |  | #N/A | #N/A | #N/A | #N/A | #N/A |  | #N/A |  | 40 | #N/A |  |  |  | #N/A | #N/A | #N/A |  | #N/A | #N/A | SR
| 1 | [6 empty] | 1 |  |  |  |  | 2SR | Slab-on-grade - Unheated | #N/A |  | 24695 | #N/A | Slab-on-grade - Unheated | #N/A |  | 24695 | #N/A |  |  | #N/A | #N/A | #N/A |  | #N/A | #N/A | #N/A | #N/A | 0 | #N/A | #N/A |  | 40 | #N/A |  |  |  | #N/A | 0 | #N/A | #N/A | #N/A | #N/A |  |  | #N/A | #N/A | #N/A | #N/A | #N/A |  | #N/A |  | 40 | #N/A |  |  |  | #N/A | #N/A | #N/A |  | #N/A | #N/A | SR
| 1 | [6 empty] | 1 |  |  |  |  | 2SR | Skylights | 0.65, 0.3 |  | 256 |  | Skylights | #N/A |  | 256 |  |  |  |  | 28.0626 | 7184.0376 |  |  | 69.3757 | 17760.1856 | 0 | 0 | 3741.6335 | 28685.8567 |  | 40 | 7184.0376 |  |  |  | 29304.3062 | 0 | 5473.2516 | 41961.5955 | #N/A | #N/A |  |  | #N/A | #N/A | #N/A | #N/A | #N/A |  | #N/A |  | 40 | #N/A |  |  |  | #N/A | #N/A | #N/A |  | #N/A | #N/A | SR
|  | 1 | [5 empty] | 1 |  |  |  |  | 3SR | Climate Zone 3A |  |  |  |  | Climate Zone 3A | [50 empty] | SR
|  | 1 | [5 empty] | 1 |  |  |  |  | 3SR | Roof - Insulation Entirely above Deck | #N/A |  | 24695 |  | Roof - Insulation Entirely above Deck | #N/A |  | 24695 |  |  |  |  | #N/A | #N/A |  |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A |  | 40 | #N/A |  |  |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A |  |  | #N/A | #N/A | #N/A | #N/A | #N/A |  | #N/A |  | 40 | #N/A |  |  |  | #N/A | #N/A | #N/A |  | #N/A | #N/A | SR
|  | 1 | [5 empty] | 1 |  |  |  |  | 3SR | Above Ground Wall - Mass | #N/A |  | 11766.9625 |  | Above Ground Wall - Mass | #N/A |  | 11766.9625 |  |  |  |  | #N/A | #N/A |  |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A |  | 40 | #N/A |  |  |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A |  |  | #N/A | #N/A | #N/A | #N/A | #N/A |  | #N/A |  | 40 | #N/A |  |  |  | #N/A | #N/A | #N/A |  | #N/A | #N/A | SR
|  | 1 | [5 empty] | 1 |  |  |  |  | 3SR | Slab-on-grade - Unheated | #N/A |  | 24695 | #N/A | Slab-on-grade - Unheated | #N/A |  | 24695 | #N/A |  |  | #N/A | #N/A | #N/A |  | #N/A | #N/A | #N/A | #N/A | 0 | #N/A | #N/A |  | 40 | #N/A |  |  |  | #N/A | 0 | #N/A | #N/A | #N/A | #N/A |  |  | #N/A | #N/A | #N/A | #N/A | #N/A |  | #N/A |  | 40 | #N/A |  |  |  | #N/A | #N/A | #N/A |  | #N/A | #N/A | SR
|  | 1 | [5 empty] | 1 |  |  |  |  | 3SR | Skylights | 0.55, 0.3 |  | 256 |  | Skylights | #N/A |  | 256 |  |  |  |  | 33.818 | 8657.4136 |  |  | 94.3715 | 24159.1142 | 0 | 0 | 4922.4792 | 37739.0071 |  | 40 | 8657.4136 |  |  |  | 39862.5385 | 0 | 7277.9928 | 55797.9449 | #N/A | #N/A |  |  | #N/A | #N/A | #N/A | #N/A | #N/A |  | #N/A |  | 40 | #N/A |  |  |  | #N/A | #N/A | #N/A |  | #N/A | #N/A | SR
|  |  | 1 |  |  |  |  | 1 |  |  |  |  | 3SR | Climate Zone 3B |  |  |  |  | Climate Zone 3B | [50 empty] | SR
|  |  | 1 |  |  |  |  | 1 |  |  |  |  | 3SR | Roof - Insulation Entirely above Deck | #N/A |  | 24695 |  | Roof - Insulation Entirely above Deck | #N/A |  | 24695 |  |  |  |  | #N/A | #N/A |  |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A |  | 40 | #N/A |  |  |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A |  |  | #N/A | #N/A | #N/A | #N/A | #N/A |  | #N/A |  | 40 | #N/A |  |  |  | #N/A | #N/A | #N/A |  | #N/A | #N/A | SR
|  |  | 1 |  |  |  |  | 1 |  |  |  |  | 3SR | Above Ground Wall - Mass | #N/A |  | 11766.9625 |  | Above Ground Wall - Mass | #N/A |  | 11766.9625 |  |  |  |  | #N/A | #N/A |  |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A |  | 40 | #N/A |  |  |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A |  |  | #N/A | #N/A | #N/A | #N/A | #N/A |  | #N/A |  | 40 | #N/A |  |  |  | #N/A | #N/A | #N/A |  | #N/A | #N/A | SR
|  |  | 1 |  |  |  |  | 1 |  |  |  |  | 3SR | Slab-on-grade - Unheated | #N/A |  | 24695 | #N/A | Slab-on-grade - Unheated | #N/A |  | 24695 | #N/A |  |  | #N/A | #N/A | #N/A |  | #N/A | #N/A | #N/A | #N/A | 0 | #N/A | #N/A |  | 40 | #N/A |  |  |  | #N/A | 0 | #N/A | #N/A | #N/A | #N/A |  |  | #N/A | #N/A | #N/A | #N/A | #N/A |  | #N/A |  | 40 | #N/A |  |  |  | #N/A | #N/A | #N/A |  | #N/A | #N/A | SR
|  |  | 1 |  |  |  |  | 1 |  |  |  |  | 3SR | Skylights | 0.55, 0.3 |  | 256 |  | Skylights | #N/A |  | 256 |  |  |  |  | 33.818 | 8657.4136 |  |  | 94.3715 | 24159.1142 | 0 | 0 | 4922.4792 | 37739.0071 |  | 40 | 8657.4136 |  |  |  | 39862.5385 | 0 | 7277.9928 | 55797.9449 | #N/A | #N/A |  |  | #N/A | #N/A | #N/A | #N/A | #N/A |  | #N/A |  | 40 | #N/A |  |  |  | #N/A | #N/A | #N/A |  | #N/A | #N/A | SR
|  |  |  | 1 |  |  |  | 1 |  |  |  |  | 4SR | Climate Zone 4A |  |  |  |  | Climate Zone 4A | [50 empty] | SR
|  |  |  | 1 |  |  |  | 1 |  |  |  |  | 4SR | Roof - Insulation Entirely above Deck | #N/A |  | 24695 |  | Roof - Insulation Entirely above Deck | #N/A |  | 24695 |  |  |  |  | #N/A | #N/A |  |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A |  | 40 | #N/A |  |  |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A |  |  | #N/A | #N/A | #N/A | #N/A | #N/A |  | #N/A |  | 40 | #N/A |  |  |  | #N/A | #N/A | #N/A |  | #N/A | #N/A | SR
|  |  |  | 1 |  |  |  | 1 |  |  |  |  | 4SR | Above Ground Wall - Mass | #N/A |  | 11766.9625 |  | Above Ground Wall - Mass | #N/A |  | 11766.9625 |  |  |  |  | #N/A | #N/A |  |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A |  | 40 | #N/A |  |  |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A |  |  | #N/A | #N/A | #N/A | #N/A | #N/A |  | #N/A |  | 40 | #N/A |  |  |  | #N/A | #N/A | #N/A |  | #N/A | #N/A | SR
|  |  |  | 1 |  |  |  | 1 |  |  |  |  | 4SR | Slab-on-grade - Unheated | #N/A |  | 24695 | #N/A | Slab-on-grade - Unheated | #N/A |  | 24695 | #N/A |  |  | #N/A | #N/A | #N/A |  | #N/A | #N/A | #N/A | #N/A | 0 | #N/A | #N/A |  | 40 | #N/A |  |  |  | #N/A | 0 | #N/A | #N/A | #N/A | #N/A |  |  | #N/A | #N/A | #N/A | #N/A | #N/A |  | #N/A |  | 40 | #N/A |  |  |  | #N/A | #N/A | #N/A |  | #N/A | #N/A | SR
|  |  |  | 1 |  |  |  | 1 |  |  |  |  | 4SR | Skylights | 0.5, 0.4 |  | 256 |  | Skylights | #N/A |  | 256 |  |  |  |  | 30.9409 | 7920.8694 |  |  | 95.3753 | 24416.087 | 0 | 0 | 4850.5435 | 37187.4999 |  | 40 | 7920.8694 |  |  |  | 40286.5436 | 0 | 7231.1119 | 55438.5249 | #N/A | #N/A |  |  | #N/A | #N/A | #N/A | #N/A | #N/A |  | #N/A |  | 40 | #N/A |  |  |  | #N/A | #N/A | #N/A |  | #N/A | #N/A | SR
[5 empty] | 1 |  |  | 1 |  |  |  |  | 5SR | Climate Zone 5A |  |  |  |  | Climate Zone 5A | [50 empty] | SR
[5 empty] | 1 |  |  | 1 |  |  |  |  | 5SR | Roof - Insulation Entirely above Deck | #N/A |  | 24695 |  | Roof - Insulation Entirely above Deck | #N/A |  | 24695 |  |  |  |  | #N/A | #N/A |  |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A |  | 40 | #N/A |  |  |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A |  |  | #N/A | #N/A | #N/A | #N/A | #N/A |  | #N/A |  | 40 | #N/A |  |  |  | #N/A | #N/A | #N/A |  | #N/A | #N/A | SR
[5 empty] | 1 |  |  | 1 |  |  |  |  | 5SR | Above Ground Wall - Mass | #N/A |  | 11766.9625 |  | Above Ground Wall - Mass | #N/A |  | 11766.9625 |  |  |  |  | #N/A | #N/A |  |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A |  | 40 | #N/A |  |  |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A |  |  | #N/A | #N/A | #N/A | #N/A | #N/A |  | #N/A |  | 40 | #N/A |  |  |  | #N/A | #N/A | #N/A |  | #N/A | #N/A | SR
[5 empty] | 1 |  |  | 1 |  |  |  |  | 5SR | Slab-on-grade - Unheated | #N/A |  | 24695 | #N/A | Slab-on-grade - Unheated | #N/A |  | 24695 | #N/A |  |  | #N/A | #N/A | #N/A |  | #N/A | #N/A | #N/A | #N/A | 0 | #N/A | #N/A |  | 40 | #N/A |  |  |  | #N/A | 0 | #N/A | #N/A | #N/A | #N/A |  |  | #N/A | #N/A | #N/A | #N/A | #N/A |  | #N/A |  | 40 | #N/A |  |  |  | #N/A | #N/A | #N/A |  | #N/A | #N/A | SR
[5 empty] | 1 |  |  | 1 |  |  |  |  | 5SR | Skylights | 0.5, 0.4 |  | 256 |  | Skylights | #N/A |  | 256 |  |  |  |  | 30.9409 | 7920.8694 |  |  | 95.3753 | 24416.087 | 0 | 0 | 4850.5435 | 37187.4999 |  | 40 | 7920.8694 |  |  |  | 40286.5436 | 0 | 7231.1119 | 55438.5249 | #N/A | #N/A |  |  | #N/A | #N/A | #N/A | #N/A | #N/A |  | #N/A |  | 40 | #N/A |  |  |  | #N/A | #N/A | #N/A |  | #N/A | #N/A | SR
| 1 | [7 empty] | 1 |  |  |  | 2PS | Climate Zone 2A |  |  |  |  | Climate Zone 2A | [50 empty] | PS
| 1 | [7 empty] | 1 |  |  |  | 2PS | Roof - Insulation Entirely above Deck | #N/A |  | 73960 |  | Roof - Insulation Entirely above Deck | #N/A |  | 73960 |  |  |  |  | #N/A | #N/A |  |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A |  | 40 | #N/A |  |  |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A |  |  | #N/A | #N/A | #N/A | #N/A | #N/A |  | #N/A |  | 40 | #N/A |  |  |  | #N/A | #N/A | #N/A |  | #N/A | #N/A | PS
| 1 | [7 empty] | 1 |  |  |  | 2PS | Above Ground Wall - Steel-framed | #N/A |  | 17577.0267 |  | Above Ground Wall - Steel-framed | #N/A |  | 17577.0267 |  |  |  |  | #N/A | #N/A |  |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A |  | 40 | #N/A |  |  |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A |  |  | #N/A | #N/A | #N/A | #N/A | #N/A |  | #N/A |  | 40 | #N/A |  |  |  | #N/A | #N/A | #N/A |  | #N/A | #N/A | PS
| 1 | [7 empty] | 1 |  |  |  | 2PS | Slab-on-grade - Unheated | #N/A |  | 73960 | #N/A | Slab-on-grade - Unheated | #N/A |  | 73960 | #N/A |  |  | #N/A | #N/A | #N/A |  | #N/A | #N/A | #N/A | #N/A | 0 | #N/A | #N/A |  | 40 | #N/A |  |  |  | #N/A | 0 | #N/A | #N/A | #N/A | #N/A |  |  | #N/A | #N/A | #N/A | #N/A | #N/A |  | #N/A |  | 40 | #N/A |  |  |  | #N/A | #N/A | #N/A |  | #N/A | #N/A | PS
| 1 | [7 empty] | 1 |  |  |  | 2PS | Skylights | 0.65, 0.3 |  | 144 |  | Skylights | #N/A |  | 144 |  |  |  |  | 29.0116 | 4177.6678 |  |  | 45.6215 | 6569.4982 | 0 | 0 | 1612.0749 | 12359.2409 |  | 40 | 4177.6678 |  |  |  | 10839.672 | 0 | 2252.601 | 17269.9407 | #N/A | #N/A |  |  | #N/A | #N/A | #N/A | #N/A | #N/A |  | #N/A |  | 40 | #N/A |  |  |  | #N/A | #N/A | #N/A |  | #N/A | #N/A | PS
|  | 1 | [6 empty] | 1 |  |  |  | 3PS | Climate Zone 3A |  |  |  |  | Climate Zone 3A | [50 empty] | PS
|  | 1 | [6 empty] | 1 |  |  |  | 3PS | Roof - Insulation Entirely above Deck | #N/A |  | 73960 |  | Roof - Insulation Entirely above Deck | #N/A |  | 73960 |  |  |  |  | #N/A | #N/A |  |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A |  | 40 | #N/A |  |  |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A |  |  | #N/A | #N/A | #N/A | #N/A | #N/A |  | #N/A |  | 40 | #N/A |  |  |  | #N/A | #N/A | #N/A |  | #N/A | #N/A | PS
|  | 1 | [6 empty] | 1 |  |  |  | 3PS | Above Ground Wall - Steel-framed | #N/A |  | 17577.0267 |  | Above Ground Wall - Steel-framed | #N/A |  | 17577.0267 |  |  |  |  | #N/A | #N/A |  |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A |  | 40 | #N/A |  |  |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A |  |  | #N/A | #N/A | #N/A | #N/A | #N/A |  | #N/A |  | 40 | #N/A |  |  |  | #N/A | #N/A | #N/A |  | #N/A | #N/A | PS
|  | 1 | [6 empty] | 1 |  |  |  | 3PS | Slab-on-grade - Unheated | #N/A |  | 73960 | #N/A | Slab-on-grade - Unheated | #N/A |  | 73960 | #N/A |  |  | #N/A | #N/A | #N/A |  | #N/A | #N/A | #N/A | #N/A | 0 | #N/A | #N/A |  | 40 | #N/A |  |  |  | #N/A | 0 | #N/A | #N/A | #N/A | #N/A |  |  | #N/A | #N/A | #N/A | #N/A | #N/A |  | #N/A |  | 40 | #N/A |  |  |  | #N/A | #N/A | #N/A |  | #N/A | #N/A | PS
|  | 1 | [6 empty] | 1 |  |  |  | 3PS | Skylights | 0.55, 0.3 |  | 144 |  | Skylights | #N/A |  | 144 |  |  |  |  | 29.7483 | 4283.7509 |  |  | 65.676 | 9457.3447 | 0 | 0 | 2061.1643 | 15802.2599 |  | 40 | 4283.7509 |  |  |  | 15604.6188 | 0 | 2983.2555 | 22871.6251 | #N/A | #N/A |  |  | #N/A | #N/A | #N/A | #N/A | #N/A |  | #N/A |  | 40 | #N/A |  |  |  | #N/A | #N/A | #N/A |  | #N/A | #N/A | PS
|  |  | 1 | [5 empty] | 1 |  |  |  | 3PS | Climate Zone 3B |  |  |  |  | Climate Zone 3B | [50 empty] | PS
|  |  | 1 | [5 empty] | 1 |  |  |  | 3PS | Roof - Insulation Entirely above Deck | #N/A |  | 73960 |  | Roof - Insulation Entirely above Deck | #N/A |  | 73960 |  |  |  |  | #N/A | #N/A |  |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A |  | 40 | #N/A |  |  |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A |  |  | #N/A | #N/A | #N/A | #N/A | #N/A |  | #N/A |  | 40 | #N/A |  |  |  | #N/A | #N/A | #N/A |  | #N/A | #N/A | PS
|  |  | 1 | [5 empty] | 1 |  |  |  | 3PS | Above Ground Wall - Steel-framed | #N/A |  | 17577.0267 |  | Above Ground Wall - Steel-framed | #N/A |  | 17577.0267 |  |  |  |  | #N/A | #N/A |  |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A |  | 40 | #N/A |  |  |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A |  |  | #N/A | #N/A | #N/A | #N/A | #N/A |  | #N/A |  | 40 | #N/A |  |  |  | #N/A | #N/A | #N/A |  | #N/A | #N/A | PS
|  |  | 1 | [5 empty] | 1 |  |  |  | 3PS | Slab-on-grade - Unheated | #N/A |  | 73960 | #N/A | Slab-on-grade - Unheated | #N/A |  | 73960 | #N/A |  |  | #N/A | #N/A | #N/A |  | #N/A | #N/A | #N/A | #N/A | 0 | #N/A | #N/A |  | 40 | #N/A |  |  |  | #N/A | 0 | #N/A | #N/A | #N/A | #N/A |  |  | #N/A | #N/A | #N/A | #N/A | #N/A |  | #N/A |  | 40 | #N/A |  |  |  | #N/A | #N/A | #N/A |  | #N/A | #N/A | PS
|  |  | 1 | [5 empty] | 1 |  |  |  | 3PS | Skylights | 0.55, 0.3 |  | 144 |  | Skylights | #N/A |  | 144 |  |  |  |  | 29.7483 | 4283.7509 |  |  | 65.676 | 9457.3447 | 0 | 0 | 2061.1643 | 15802.2599 |  | 40 | 4283.7509 |  |  |  | 15604.6188 | 0 | 2983.2555 | 22871.6251 | #N/A | #N/A |  |  | #N/A | #N/A | #N/A | #N/A | #N/A |  | #N/A |  | 40 | #N/A |  |  |  | #N/A | #N/A | #N/A |  | #N/A | #N/A | PS
|  |  |  | 1 |  |  |  |  | 1 |  |  |  | 4PS | Climate Zone 4A |  |  |  |  | Climate Zone 4A | [50 empty] | PS
|  |  |  | 1 |  |  |  |  | 1 |  |  |  | 4PS | Roof - Insulation Entirely above Deck | #N/A |  | 73960 |  | Roof - Insulation Entirely above Deck | #N/A |  | 73960 |  |  |  |  | #N/A | #N/A |  |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A |  | 40 | #N/A |  |  |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A |  |  | #N/A | #N/A | #N/A | #N/A | #N/A |  | #N/A |  | 40 | #N/A |  |  |  | #N/A | #N/A | #N/A |  | #N/A | #N/A | PS
|  |  |  | 1 |  |  |  |  | 1 |  |  |  | 4PS | Above Ground Wall - Steel-framed | #N/A |  | 17577.0267 |  | Above Ground Wall - Steel-framed | #N/A |  | 17577.0267 |  |  |  |  | #N/A | #N/A |  |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A |  | 40 | #N/A |  |  |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A |  |  | #N/A | #N/A | #N/A | #N/A | #N/A |  | #N/A |  | 40 | #N/A |  |  |  | #N/A | #N/A | #N/A |  | #N/A | #N/A | PS
|  |  |  | 1 |  |  |  |  | 1 |  |  |  | 4PS | Slab-on-grade - Unheated | #N/A |  | 73960 | #N/A | Slab-on-grade - Unheated | #N/A |  | 73960 | #N/A |  |  | #N/A | #N/A | #N/A |  | #N/A | #N/A | #N/A | #N/A | 0 | #N/A | #N/A |  | 40 | #N/A |  |  |  | #N/A | 0 | #N/A | #N/A | #N/A | #N/A |  |  | #N/A | #N/A | #N/A | #N/A | #N/A |  | #N/A |  | 40 | #N/A |  |  |  | #N/A | #N/A | #N/A |  | #N/A | #N/A | PS
|  |  |  | 1 |  |  |  |  | 1 |  |  |  | 4PS | Skylights | 0.5, 0.4 |  | 144 |  | Skylights | #N/A |  | 144 |  |  |  |  | 30.1155 | 4336.6307 |  |  | 65.676 | 9457.3447 | 0 | 0 | 2069.0963 | 15863.0717 |  | 40 | 4336.6307 |  |  |  | 15604.6188 | 0 | 2991.1874 | 22932.4369 | #N/A | #N/A |  |  | #N/A | #N/A | #N/A | #N/A | #N/A |  | #N/A |  | 40 | #N/A |  |  |  | #N/A | #N/A | #N/A |  | #N/A | #N/A | PS
[5 empty] | 1 |  |  |  | 1 |  |  |  | 5PS | Climate Zone 5A |  |  |  |  | Climate Zone 5A | [50 empty] | PS
[5 empty] | 1 |  |  |  | 1 |  |  |  | 5PS | Roof - Insulation Entirely above Deck | #N/A |  | 73960 |  | Roof - Insulation Entirely above Deck | #N/A |  | 73960 |  |  |  |  | #N/A | #N/A |  |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A |  | 40 | #N/A |  |  |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A |  |  | #N/A | #N/A | #N/A | #N/A | #N/A |  | #N/A |  | 40 | #N/A |  |  |  | #N/A | #N/A | #N/A |  | #N/A | #N/A | PS
[5 empty] | 1 |  |  |  | 1 |  |  |  | 5PS | Above Ground Wall - Steel-framed | #N/A |  | 17577.0267 |  | Above Ground Wall - Steel-framed | #N/A |  | 17577.0267 |  |  |  |  | #N/A | #N/A |  |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A |  | 40 | #N/A |  |  |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A |  |  | #N/A | #N/A | #N/A | #N/A | #N/A |  | #N/A |  | 40 | #N/A |  |  |  | #N/A | #N/A | #N/A |  | #N/A | #N/A | PS
[5 empty] | 1 |  |  |  | 1 |  |  |  | 5PS | Slab-on-grade - Unheated | #N/A |  | 73960 | #N/A | Slab-on-grade - Unheated | #N/A |  | 73960 | #N/A |  |  | #N/A | #N/A | #N/A |  | #N/A | #N/A | #N/A | #N/A | 0 | #N/A | #N/A |  | 40 | #N/A |  |  |  | #N/A | 0 | #N/A | #N/A | #N/A | #N/A |  |  | #N/A | #N/A | #N/A | #N/A | #N/A |  | #N/A |  | 40 | #N/A |  |  |  | #N/A | #N/A | #N/A |  | #N/A | #N/A | PS
[5 empty] | 1 |  |  |  | 1 |  |  |  | 5PS | Skylights | 0.5, 0.4 |  | 144 |  | Skylights | #N/A |  | 144 |  |  |  |  | 30.1155 | 4336.6307 |  |  | 65.676 | 9457.3447 | 0 | 0 | 2069.0963 | 15863.0717 |  | 40 | 4336.6307 |  |  |  | 15604.6188 | 0 | 2991.1874 | 22932.4369 | #N/A | #N/A |  |  | #N/A | #N/A | #N/A | #N/A | #N/A |  | #N/A |  | 40 | #N/A |  |  |  | #N/A | #N/A | #N/A |  | #N/A | #N/A | PS
| 1 | [8 empty] | 1 |  |  | 2SH | Climate Zone 2A |  |  |  |  | Climate Zone 2A | [50 empty] | SH
| 1 | [8 empty] | 1 |  |  | 2SH | Roof - Insulation Entirely above Deck | #N/A |  | 10801.5609 |  | Roof - Insulation Entirely above Deck | #N/A |  | 10801.5609 |  |  |  |  | #N/A | #N/A |  |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A |  | 40 | #N/A |  |  |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A |  |  | #N/A | #N/A | #N/A | #N/A | #N/A |  | #N/A |  | 40 | #N/A |  |  |  | #N/A | #N/A | #N/A |  | #N/A | #N/A | SH
| 1 | [8 empty] | 1 |  |  | 2SH | Above Ground Wall - Steel-framed | #N/A |  | 11542.19 |  | Above Ground Wall - Steel-framed | #N/A |  | 11542.19 |  |  |  |  | #N/A | #N/A |  |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A |  | 40 | #N/A |  |  |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A |  |  | #N/A | #N/A | #N/A | #N/A | #N/A |  | #N/A |  | 40 | #N/A |  |  |  | #N/A | #N/A | #N/A |  | #N/A | #N/A | SH
| 1 | [8 empty] | 1 |  |  | 2SH | Slab-on-grade - Unheated | #N/A |  | 0 |  | Slab-on-grade - Unheated | #N/A |  | 0 |  |  |  |  | #N/A | #N/A |  |  | #N/A | #N/A | #N/A | 0 | #N/A | #N/A |  | 40 | #N/A |  |  |  | #N/A | 0 | #N/A | #N/A | #N/A | #N/A |  |  | #N/A | #N/A | #N/A | #N/A | #N/A |  | #N/A |  | 40 | #N/A |  |  |  | #N/A | #N/A | #N/A |  | #N/A | #N/A | SH
|  | 1 | [7 empty] | 1 |  |  | 3SH | Climate Zone 3A |  |  |  |  | Climate Zone 3A | [50 empty] | SH
|  | 1 | [7 empty] | 1 |  |  | 3SH | Roof - Insulation Entirely above Deck | #N/A |  | 10801.5609 |  | Roof - Insulation Entirely above Deck | #N/A |  | 10801.5609 |  |  |  |  | #N/A | #N/A |  |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A |  | 40 | #N/A |  |  |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A |  |  | #N/A | #N/A | #N/A | #N/A | #N/A |  | #N/A |  | 40 | #N/A |  |  |  | #N/A | #N/A | #N/A |  | #N/A | #N/A | SH
|  | 1 | [7 empty] | 1 |  |  | 3SH | Above Ground Wall - Steel-framed | #N/A |  | 11542.19 |  | Above Ground Wall - Steel-framed | #N/A |  | 11542.19 |  |  |  |  | #N/A | #N/A |  |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A |  | 40 | #N/A |  |  |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A |  |  | #N/A | #N/A | #N/A | #N/A | #N/A |  | #N/A |  | 40 | #N/A |  |  |  | #N/A | #N/A | #N/A |  | #N/A | #N/A | SH
|  | 1 | [7 empty] | 1 |  |  | 3SH | Slab-on-grade - Unheated | #N/A |  | 0 |  | Slab-on-grade - Unheated | #N/A |  | 0 |  |  |  |  | #N/A | #N/A |  |  | #N/A | #N/A | #N/A | 0 | #N/A | #N/A |  | 40 | #N/A |  |  |  | #N/A | 0 | #N/A | #N/A | #N/A | #N/A |  |  | #N/A | #N/A | #N/A | #N/A | #N/A |  | #N/A |  | 40 | #N/A |  |  |  | #N/A | #N/A | #N/A |  | #N/A | #N/A | SH
|  |  | 1 | [6 empty] | 1 |  |  | 3SH | Climate Zone 3B |  |  |  |  | Climate Zone 3B | [50 empty] | SH
|  |  | 1 | [6 empty] | 1 |  |  | 3SH | Roof - Insulation Entirely above Deck | #N/A |  | 10801.5609 |  | Roof - Insulation Entirely above Deck | #N/A |  | 10801.5609 |  |  |  |  | #N/A | #N/A |  |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A |  | 40 | #N/A |  |  |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A |  |  | #N/A | #N/A | #N/A | #N/A | #N/A |  | #N/A |  | 40 | #N/A |  |  |  | #N/A | #N/A | #N/A |  | #N/A | #N/A | SH
|  |  | 1 | [6 empty] | 1 |  |  | 3SH | Above Ground Wall - Steel-framed | #N/A |  | 11542.19 |  | Above Ground Wall - Steel-framed | #N/A |  | 11542.19 |  |  |  |  | #N/A | #N/A |  |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A |  | 40 | #N/A |  |  |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A |  |  | #N/A | #N/A | #N/A | #N/A | #N/A |  | #N/A |  | 40 | #N/A |  |  |  | #N/A | #N/A | #N/A |  | #N/A | #N/A | SH
|  |  | 1 | [6 empty] | 1 |  |  | 3SH | Slab-on-grade - Unheated | #N/A |  | 0 |  | Slab-on-grade - Unheated | #N/A |  | 0 |  |  |  |  | #N/A | #N/A |  |  | #N/A | #N/A | #N/A | 0 | #N/A | #N/A |  | 40 | #N/A |  |  |  | #N/A | 0 | #N/A | #N/A | #N/A | #N/A |  |  | #N/A | #N/A | #N/A | #N/A | #N/A |  | #N/A |  | 40 | #N/A |  |  |  | #N/A | #N/A | #N/A |  | #N/A | #N/A | SH
|  |  |  | 1 | [5 empty] | 1 |  |  | 4SH | Climate Zone 4A |  |  |  |  | Climate Zone 4A | [50 empty] | SH
|  |  |  | 1 | [5 empty] | 1 |  |  | 4SH | Roof - Insulation Entirely above Deck | #N/A |  | 10801.5609 |  | Roof - Insulation Entirely above Deck | #N/A |  | 10801.5609 |  |  |  |  | #N/A | #N/A |  |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A |  | 40 | #N/A |  |  |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A |  |  | #N/A | #N/A | #N/A | #N/A | #N/A |  | #N/A |  | 40 | #N/A |  |  |  | #N/A | #N/A | #N/A |  | #N/A | #N/A | SH
|  |  |  | 1 | [5 empty] | 1 |  |  | 4SH | Above Ground Wall - Steel-framed | #N/A |  | 11542.19 |  | Above Ground Wall - Steel-framed | #N/A |  | 11542.19 |  |  |  |  | #N/A | #N/A |  |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A |  | 40 | #N/A |  |  |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A |  |  | #N/A | #N/A | #N/A | #N/A | #N/A |  | #N/A |  | 40 | #N/A |  |  |  | #N/A | #N/A | #N/A |  | #N/A | #N/A | SH
|  |  |  | 1 | [5 empty] | 1 |  |  | 4SH | Slab-on-grade - Unheated | #N/A |  | 0 |  | Slab-on-grade - Unheated | #N/A |  | 0 |  |  |  |  | #N/A | #N/A |  |  | #N/A | #N/A | #N/A | 0 | #N/A | #N/A |  | 40 | #N/A |  |  |  | #N/A | 0 | #N/A | #N/A | #N/A | #N/A |  |  | #N/A | #N/A | #N/A | #N/A | #N/A |  | #N/A |  | 40 | #N/A |  |  |  | #N/A | #N/A | #N/A |  | #N/A | #N/A | SH
[5 empty] | 1 |  |  |  |  | 1 |  |  | 5SH | Climate Zone 5A |  |  |  |  | Climate Zone 5A | [50 empty] | SH
[5 empty] | 1 |  |  |  |  | 1 |  |  | 5SH | Roof - Insulation Entirely above Deck | #N/A |  | 10801.5609 |  | Roof - Insulation Entirely above Deck | #N/A |  | 10801.5609 |  |  |  |  | #N/A | #N/A |  |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A |  | 40 | #N/A |  |  |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A |  |  | #N/A | #N/A | #N/A | #N/A | #N/A |  | #N/A |  | 40 | #N/A |  |  |  | #N/A | #N/A | #N/A |  | #N/A | #N/A | SH
[5 empty] | 1 |  |  |  |  | 1 |  |  | 5SH | Above Ground Wall - Steel-framed | #N/A |  | 11542.19 |  | Above Ground Wall - Steel-framed | #N/A |  | 11542.19 |  |  |  |  | #N/A | #N/A |  |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A |  | 40 | #N/A |  |  |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A |  |  | #N/A | #N/A | #N/A | #N/A | #N/A |  | #N/A |  | 40 | #N/A |  |  |  | #N/A | #N/A | #N/A |  | #N/A | #N/A | SH
[5 empty] | 1 |  |  |  |  | 1 |  |  | 5SH | Slab-on-grade - Unheated | #N/A |  | 0 |  | Slab-on-grade - Unheated | #N/A |  | 0 |  |  |  |  | #N/A | #N/A |  |  | #N/A | #N/A | #N/A | 0 | #N/A | #N/A |  | 40 | #N/A |  |  |  | #N/A | 0 | #N/A | #N/A | #N/A | #N/A |  |  | #N/A | #N/A | #N/A | #N/A | #N/A |  | #N/A |  | 40 | #N/A |  |  |  | #N/A | #N/A | #N/A |  | #N/A | #N/A | SH
| 1 | [8 empty] | 1 |  |  | 2SHNR | Climate Zone 2A |  |  |  |  | Climate Zone 2A | [50 empty] | SHNR
| 1 | [8 empty] | 1 |  |  | 2SHNR | Roof - Insulation Entirely above Deck | #N/A |  | 0 |  | Roof - Insulation Entirely above Deck | #N/A |  | 0 |  |  |  |  | #N/A | #N/A |  |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A |  | 40 | #N/A |  |  |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A |  |  | #N/A | #N/A | #N/A | #N/A | #N/A |  | #N/A |  | 40 | #N/A |  |  |  | #N/A | #N/A | #N/A |  | #N/A | #N/A | SHNR
| 1 | [8 empty] | 1 |  |  | 2SHNR | Above Ground Wall - Steel-framed | #N/A |  | 4713.55 |  | Above Ground Wall - Steel-framed | #N/A |  | 4713.55 |  |  |  |  | #N/A | #N/A |  |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A |  | 40 | #N/A |  |  |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A |  |  | #N/A | #N/A | #N/A | #N/A | #N/A |  | #N/A |  | 40 | #N/A |  |  |  | #N/A | #N/A | #N/A |  | #N/A | #N/A | SHNR
| 1 | [8 empty] | 1 |  |  | 2SHNR | Slab-on-grade - Unheated | #N/A |  | 10801.5609 | #N/A | Slab-on-grade - Unheated | #N/A |  | 10801.5609 | #N/A |  |  | #N/A | #N/A | #N/A |  | #N/A | #N/A | #N/A | #N/A | 0 | #N/A | #N/A |  | 40 | #N/A |  |  |  | #N/A | 0 | #N/A | #N/A | #N/A | #N/A |  |  | #N/A | #N/A | #N/A | #N/A | #N/A |  | #N/A |  | 40 | #N/A |  |  |  | #N/A | #N/A | #N/A |  | #N/A | #N/A | SHNR
|  | 1 | [7 empty] | 1 |  |  | 3SHNR | Climate Zone 3A |  |  |  |  | Climate Zone 3A | [50 empty] | SHNR
|  | 1 | [7 empty] | 1 |  |  | 3SHNR | Roof - Insulation Entirely above Deck | #N/A |  | 0 |  | Roof - Insulation Entirely above Deck | #N/A |  | 0 |  |  |  |  | #N/A | #N/A |  |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A |  | 40 | #N/A |  |  |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A |  |  | #N/A | #N/A | #N/A | #N/A | #N/A |  | #N/A |  | 40 | #N/A |  |  |  | #N/A | #N/A | #N/A |  | #N/A | #N/A | SHNR
|  | 1 | [7 empty] | 1 |  |  | 3SHNR | Above Ground Wall - Steel-framed | #N/A |  | 4713.55 |  | Above Ground Wall - Steel-framed | #N/A |  | 4713.55 |  |  |  |  | #N/A | #N/A |  |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A |  | 40 | #N/A |  |  |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A |  |  | #N/A | #N/A | #N/A | #N/A | #N/A |  | #N/A |  | 40 | #N/A |  |  |  | #N/A | #N/A | #N/A |  | #N/A | #N/A | SHNR
|  | 1 | [7 empty] | 1 |  |  | 3SHNR | Slab-on-grade - Unheated | #N/A |  | 10801.5609 | #N/A | Slab-on-grade - Unheated | #N/A |  | 10801.5609 | #N/A |  |  | #N/A | #N/A | #N/A |  | #N/A | #N/A | #N/A | #N/A | 0 | #N/A | #N/A |  | 40 | #N/A |  |  |  | #N/A | 0 | #N/A | #N/A | #N/A | #N/A |  |  | #N/A | #N/A | #N/A | #N/A | #N/A |  | #N/A |  | 40 | #N/A |  |  |  | #N/A | #N/A | #N/A |  | #N/A | #N/A | SHNR
|  |  | 1 | [6 empty] | 1 |  |  | 3SHNR | Climate Zone 3B |  |  |  |  | Climate Zone 3B | [50 empty] | SHNR
|  |  | 1 | [6 empty] | 1 |  |  | 3SHNR | Roof - Insulation Entirely above Deck | #N/A |  | 0 |  | Roof - Insulation Entirely above Deck | #N/A |  | 0 |  |  |  |  | #N/A | #N/A |  |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A |  | 40 | #N/A |  |  |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A |  |  | #N/A | #N/A | #N/A | #N/A | #N/A |  | #N/A |  | 40 | #N/A |  |  |  | #N/A | #N/A | #N/A |  | #N/A | #N/A | SHNR
|  |  | 1 | [6 empty] | 1 |  |  | 3SHNR | Above Ground Wall - Steel-framed | #N/A |  | 4713.55 |  | Above Ground Wall - Steel-framed | #N/A |  | 4713.55 |  |  |  |  | #N/A | #N/A |  |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A |  | 40 | #N/A |  |  |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A |  |  | #N/A | #N/A | #N/A | #N/A | #N/A |  | #N/A |  | 40 | #N/A |  |  |  | #N/A | #N/A | #N/A |  | #N/A | #N/A | SHNR
|  |  | 1 | [6 empty] | 1 |  |  | 3SHNR | Slab-on-grade - Unheated | #N/A |  | 10801.5609 | #N/A | Slab-on-grade - Unheated | #N/A |  | 10801.5609 | #N/A |  |  | #N/A | #N/A | #N/A |  | #N/A | #N/A | #N/A | #N/A | 0 | #N/A | #N/A |  | 40 | #N/A |  |  |  | #N/A | 0 | #N/A | #N/A | #N/A | #N/A |  |  | #N/A | #N/A | #N/A | #N/A | #N/A |  | #N/A |  | 40 | #N/A |  |  |  | #N/A | #N/A | #N/A |  | #N/A | #N/A | SHNR
|  |  |  | 1 | [5 empty] | 1 |  |  | 4SHNR | Climate Zone 4A |  |  |  |  | Climate Zone 4A | [50 empty] | SHNR
|  |  |  | 1 | [5 empty] | 1 |  |  | 4SHNR | Roof - Insulation Entirely above Deck | #N/A |  | 0 |  | Roof - Insulation Entirely above Deck | #N/A |  | 0 |  |  |  |  | #N/A | #N/A |  |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A |  | 40 | #N/A |  |  |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A |  |  | #N/A | #N/A | #N/A | #N/A | #N/A |  | #N/A |  | 40 | #N/A |  |  |  | #N/A | #N/A | #N/A |  | #N/A | #N/A | SHNR
|  |  |  | 1 | [5 empty] | 1 |  |  | 4SHNR | Above Ground Wall - Steel-framed | #N/A |  | 4713.55 |  | Above Ground Wall - Steel-framed | #N/A |  | 4713.55 |  |  |  |  | #N/A | #N/A |  |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A |  | 40 | #N/A |  |  |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A |  |  | #N/A | #N/A | #N/A | #N/A | #N/A |  | #N/A |  | 40 | #N/A |  |  |  | #N/A | #N/A | #N/A |  | #N/A | #N/A | SHNR
|  |  |  | 1 | [5 empty] | 1 |  |  | 4SHNR | Slab-on-grade - Unheated | #N/A |  | 10801.5609 | #N/A | Slab-on-grade - Unheated | #N/A |  | 10801.5609 | #N/A |  |  | #N/A | #N/A | #N/A |  | #N/A | #N/A | #N/A | #N/A | 0 | #N/A | #N/A |  | 40 | #N/A |  |  |  | #N/A | 0 | #N/A | #N/A | #N/A | #N/A |  |  | #N/A | #N/A | #N/A | #N/A | #N/A |  | #N/A |  | 40 | #N/A |  |  |  | #N/A | #N/A | #N/A |  | #N/A | #N/A | SHNR
[5 empty] | 1 |  |  |  |  | 1 |  |  | 5SHNR | Climate Zone 5A |  |  |  |  | Climate Zone 5A | [50 empty] | SHNR
[5 empty] | 1 |  |  |  |  | 1 |  |  | 5SHNR | Roof - Insulation Entirely above Deck | #N/A |  | 0 |  | Roof - Insulation Entirely above Deck | #N/A |  | 0 |  |  |  |  | #N/A | #N/A |  |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A |  | 40 | #N/A |  |  |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A |  |  | #N/A | #N/A | #N/A | #N/A | #N/A |  | #N/A |  | 40 | #N/A |  |  |  | #N/A | #N/A | #N/A |  | #N/A | #N/A | SHNR
[5 empty] | 1 |  |  |  |  | 1 |  |  | 5SHNR | Above Ground Wall - Steel-framed | #N/A |  | 4713.55 |  | Above Ground Wall - Steel-framed | #N/A |  | 4713.55 |  |  |  |  | #N/A | #N/A |  |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A |  | 40 | #N/A |  |  |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A |  |  | #N/A | #N/A | #N/A | #N/A | #N/A |  | #N/A |  | 40 | #N/A |  |  |  | #N/A | #N/A | #N/A |  | #N/A | #N/A | SHNR
[5 empty] | 1 |  |  |  |  | 1 |  |  | 5SHNR | Slab-on-grade - Unheated | #N/A |  | 10801.5609 | #N/A | Slab-on-grade - Unheated | #N/A |  | 10801.5609 | #N/A |  |  | #N/A | #N/A | #N/A |  | #N/A | #N/A | #N/A | #N/A | 0 | #N/A | #N/A |  | 40 | #N/A |  |  |  | #N/A | 0 | #N/A | #N/A | #N/A | #N/A |  |  | #N/A | #N/A | #N/A | #N/A | #N/A |  | #N/A |  | 40 | #N/A |  |  |  | #N/A | #N/A | #N/A |  | #N/A | #N/A | SHNR
| 1 | [9 empty] | 1 |  | 2MA | Climate Zone 2A |  |  |  |  | Climate Zone 2A | [50 empty] | MA
| 1 | [9 empty] | 1 |  | 2MA | Roof - Insulation Entirely above Deck | #N/A |  | 8435.9609 |  | Roof - Insulation Entirely above Deck | #N/A |  | 8435.9609 |  |  |  |  | #N/A | #N/A |  |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A |  | 40 | #N/A |  |  |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A |  |  | #N/A | #N/A | #N/A | #N/A | #N/A |  | #N/A |  | 40 | #N/A |  |  |  | #N/A | #N/A | #N/A |  | #N/A | #N/A | MA
| 1 | [9 empty] | 1 |  | 2MA | Above Ground Wall - Steel-framed | #N/A |  | 13296.0185 |  | Above Ground Wall - Steel-framed | #N/A |  | 13296.0185 |  |  |  |  | #N/A | #N/A |  |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A |  | 40 | #N/A |  |  |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A |  |  | #N/A | #N/A | #N/A | #N/A | #N/A |  | #N/A |  | 40 | #N/A |  |  |  | #N/A | #N/A | #N/A |  | #N/A | #N/A | MA
| 1 | [9 empty] | 1 |  | 2MA | Slab-on-grade - Unheated | #N/A |  | 8435.9609 | #N/A | Slab-on-grade - Unheated | #N/A |  | 8435.9609 | #N/A |  |  | #N/A | #N/A | #N/A |  | #N/A | #N/A | #N/A | #N/A | 0 | #N/A | #N/A |  | 40 | #N/A |  |  |  | #N/A | 0 | #N/A | #N/A | #N/A | #N/A |  |  | #N/A | #N/A | #N/A | #N/A | #N/A |  | #N/A |  | 40 | #N/A |  |  |  | #N/A | #N/A | #N/A |  | #N/A | #N/A | MA
|  | 1 | [8 empty] | 1 |  | 3MA | Climate Zone 3A |  |  |  |  | Climate Zone 3A | [50 empty] | MA
|  | 1 | [8 empty] | 1 |  | 3MA | Roof - Insulation Entirely above Deck | #N/A |  | 8435.9609 |  | Roof - Insulation Entirely above Deck | #N/A |  | 8435.9609 |  |  |  |  | #N/A | #N/A |  |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A |  | 40 | #N/A |  |  |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A |  |  | #N/A | #N/A | #N/A | #N/A | #N/A |  | #N/A |  | 40 | #N/A |  |  |  | #N/A | #N/A | #N/A |  | #N/A | #N/A | MA
|  | 1 | [8 empty] | 1 |  | 3MA | Above Ground Wall - Steel-framed | #N/A |  | 13296.0185 |  | Above Ground Wall - Steel-framed | #N/A |  | 13296.0185 |  |  |  |  | #N/A | #N/A |  |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A |  | 40 | #N/A |  |  |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A |  |  | #N/A | #N/A | #N/A | #N/A | #N/A |  | #N/A |  | 40 | #N/A |  |  |  | #N/A | #N/A | #N/A |  | #N/A | #N/A | MA
|  | 1 | [8 empty] | 1 |  | 3MA | Slab-on-grade - Unheated | #N/A |  | 8435.9609 | #N/A | Slab-on-grade - Unheated | #N/A |  | 8435.9609 | #N/A |  |  | #N/A | #N/A | #N/A |  | #N/A | #N/A | #N/A | #N/A | 0 | #N/A | #N/A |  | 40 | #N/A |  |  |  | #N/A | 0 | #N/A | #N/A | #N/A | #N/A |  |  | #N/A | #N/A | #N/A | #N/A | #N/A |  | #N/A |  | 40 | #N/A |  |  |  | #N/A | #N/A | #N/A |  | #N/A | #N/A | MA
|  |  | 1 | [7 empty] | 1 |  | 3MA | Climate Zone 3B |  |  |  |  | Climate Zone 3B | [50 empty] | MA
|  |  | 1 | [7 empty] | 1 |  | 3MA | Roof - Insulation Entirely above Deck | #N/A |  | 8435.9609 |  | Roof - Insulation Entirely above Deck | #N/A |  | 8435.9609 |  |  |  |  | #N/A | #N/A |  |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A |  | 40 | #N/A |  |  |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A |  |  | #N/A | #N/A | #N/A | #N/A | #N/A |  | #N/A |  | 40 | #N/A |  |  |  | #N/A | #N/A | #N/A |  | #N/A | #N/A | MA
|  |  | 1 | [7 empty] | 1 |  | 3MA | Above Ground Wall - Steel-framed | #N/A |  | 13296.0185 |  | Above Ground Wall - Steel-framed | #N/A |  | 13296.0185 |  |  |  |  | #N/A | #N/A |  |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A |  | 40 | #N/A |  |  |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A |  |  | #N/A | #N/A | #N/A | #N/A | #N/A |  | #N/A |  | 40 | #N/A |  |  |  | #N/A | #N/A | #N/A |  | #N/A | #N/A | MA
|  |  | 1 | [7 empty] | 1 |  | 3MA | Slab-on-grade - Unheated | #N/A |  | 8435.9609 | #N/A | Slab-on-grade - Unheated | #N/A |  | 8435.9609 | #N/A |  |  | #N/A | #N/A | #N/A |  | #N/A | #N/A | #N/A | #N/A | 0 | #N/A | #N/A |  | 40 | #N/A |  |  |  | #N/A | 0 | #N/A | #N/A | #N/A | #N/A |  |  | #N/A | #N/A | #N/A | #N/A | #N/A |  | #N/A |  | 40 | #N/A |  |  |  | #N/A | #N/A | #N/A |  | #N/A | #N/A | MA
|  |  |  | 1 | [6 empty] | 1 |  | 4MA | Climate Zone 4A |  |  |  |  | Climate Zone 4A | [50 empty] | MA
|  |  |  | 1 | [6 empty] | 1 |  | 4MA | Roof - Insulation Entirely above Deck | #N/A |  | 8435.9609 |  | Roof - Insulation Entirely above Deck | #N/A |  | 8435.9609 |  |  |  |  | #N/A | #N/A |  |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A |  | 40 | #N/A |  |  |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A |  |  | #N/A | #N/A | #N/A | #N/A | #N/A |  | #N/A |  | 40 | #N/A |  |  |  | #N/A | #N/A | #N/A |  | #N/A | #N/A | MA
|  |  |  | 1 | [6 empty] | 1 |  | 4MA | Above Ground Wall - Steel-framed | #N/A |  | 13296.0185 |  | Above Ground Wall - Steel-framed | #N/A |  | 13296.0185 |  |  |  |  | #N/A | #N/A |  |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A |  | 40 | #N/A |  |  |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A |  |  | #N/A | #N/A | #N/A | #N/A | #N/A |  | #N/A |  | 40 | #N/A |  |  |  | #N/A | #N/A | #N/A |  | #N/A | #N/A | MA
|  |  |  | 1 | [6 empty] | 1 |  | 4MA | Slab-on-grade - Unheated | #N/A |  | 8435.9609 | #N/A | Slab-on-grade - Unheated | #N/A |  | 8435.9609 | #N/A |  |  | #N/A | #N/A | #N/A |  | #N/A | #N/A | #N/A | #N/A | 0 | #N/A | #N/A |  | 40 | #N/A |  |  |  | #N/A | 0 | #N/A | #N/A | #N/A | #N/A |  |  | #N/A | #N/A | #N/A | #N/A | #N/A |  | #N/A |  | 40 | #N/A |  |  |  | #N/A | #N/A | #N/A |  | #N/A | #N/A | MA
[5 empty] | 1 | [5 empty] | 1 |  | 5MA | Climate Zone 5A |  |  |  |  | Climate Zone 5A | [50 empty] | MA
[5 empty] | 1 | [5 empty] | 1 |  | 5MA | Roof - Insulation Entirely above Deck | #N/A |  | 8435.9609 |  | Roof - Insulation Entirely above Deck | #N/A |  | 8435.9609 |  |  |  |  | #N/A | #N/A |  |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A |  | 40 | #N/A |  |  |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A |  |  | #N/A | #N/A | #N/A | #N/A | #N/A |  | #N/A |  | 40 | #N/A |  |  |  | #N/A | #N/A | #N/A |  | #N/A | #N/A | MA
[5 empty] | 1 | [5 empty] | 1 |  | 5MA | Above Ground Wall - Steel-framed | #N/A |  | 13296.0185 |  | Above Ground Wall - Steel-framed | #N/A |  | 13296.0185 |  |  |  |  | #N/A | #N/A |  |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A |  | 40 | #N/A |  |  |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A |  |  | #N/A | #N/A | #N/A | #N/A | #N/A |  | #N/A |  | 40 | #N/A |  |  |  | #N/A | #N/A | #N/A |  | #N/A | #N/A | MA
[5 empty] | 1 | [5 empty] | 1 |  | 5MA | Slab-on-grade - Unheated | #N/A |  | 8435.9609 | #N/A | Slab-on-grade - Unheated | #N/A |  | 8435.9609 | #N/A |  |  | #N/A | #N/A | #N/A |  | #N/A | #N/A | #N/A | #N/A | 0 | #N/A | #N/A |  | 40 | #N/A |  |  |  | #N/A | 0 | #N/A | #N/A | #N/A | #N/A |  |  | #N/A | #N/A | #N/A | #N/A | #N/A |  | #N/A |  | 40 | #N/A |  |  |  | #N/A | #N/A | #N/A |  | #N/A | #N/A | MA
1 | 1 | 1 | 1 | 1 | 1 | 1 | [5 empty] | Infiltration testing, 90.1-2019t |  | No leakage testing |  |  |  |  | Leakage testing | PNNL Tech Brief | [6 empty] | 0 | [8 empty] | 0 | [20 empty] | 385 | [11 empty] | 385
1 |  |  |  | 1 | 1 | 1 | [5 empty] | Thermal bridging, 90.1-2019av |  | thermal bridge, unmitigated |  |  |  |  | parapet, balcony/deck at opaque wall intersection, balcony/deck at vertical fenestration, Total Cladding Support linear thermal bridge, opaque wall - vertical fen. Intersection | 90.1 Envelope Subcommittee | [6 empty] | 0 | [8 empty] | 0 | [20 empty] | 1760 | [11 empty] | 1760
1 |  |  |  | 1 | 1 |  | 1 |  |  |  |  | Thermal bridging, 90.1-2019av |  | thermal bridge, unmitigated | [5 empty] | 90.1 Envelope Subcommittee | [6 empty] | 0 | [8 empty] | 0 | [20 empty] | 28258 | [11 empty] | 28258
1 |  |  |  | 1 | 1 |  |  | 1 |  |  |  | Thermal bridging, 90.1-2019av |  | thermal bridge, unmitigated | [5 empty] | 90.1 Envelope Subcommittee | [6 empty] | 0 | [8 empty] | 0 | [20 empty] | 3103 | [11 empty] | 3103
1 |  |  |  | 1 | 1 |  |  |  | 1 |  |  | Thermal bridging, 90.1-2019av |  | thermal bridge, unmitigated | [5 empty] | 90.1 Envelope Subcommittee | [6 empty] | 0 | [8 empty] | 0 | [20 empty] | 13680 | [11 empty] | 13680
1 |  |  |  | 1 | 1 |  |  |  |  | 1 |  | Thermal bridging, 90.1-2019av |  | thermal bridge, unmitigated | [5 empty] | 90.1 Envelope Subcommittee | [6 empty] | 0 | [8 empty] | 0 | [20 empty] | 4157 | [11 empty] | 4157
1 |  |  |  | 1 | 1 | [5 empty] | 1 | Thermal bridging, 90.1-2019av |  | thermal bridge, unmitigated | [5 empty] | 90.1 Envelope Subcommittee | [6 empty] | 0 | [8 empty] | 0 | [20 empty] | 5055 | [11 empty] | 5055
[12 empty] | Roof Reflectance Addendum 90.1-07f 90.1-2010 section 5.5.3.1.1 |  | 90.1-2007 section 5.5.3.1.1 requires roof exterior surface to have minimum propertiese: 0.7 solar reflectance (this is initial not aged value) a thermal emittance of at least 0.75, and a solar reflective index of 0.82, all according to test methods identified in this section. There are several exceptions - the exception for roofs over ventilated attics applies to the small office prototype. The rest of the selected prototypes are affected. No costs shown for 90.1-2007. Incremental costs only shown under 90.1-2010 costs. Same approach for IECC 2009 and 2012 | Faithful and Gould |  | not used | Roof area, ft2 | 90.1-2010 section 5.5.3.1.1 requires roof exterior surface to have minimum propertiese: 0.55 three-year aged solar reflectance (this is more stringent than 0.7 initial not aged value) a thermal emittance of at least 0.75, or a three-year aged solar reflective index of 64, or increased insulation, with the first subject to testing and accreditation identified in the Standard. There are several exceptions - the exception for roofs over ventilated attics applies to the small office prototype. The rest of the selected prototypes are affected. Average incremental material costs only were estimated for an average EPDM and TPO that does not meet the 90.1-2010 requirements compared to the same corresponding materials that do meet the requirements. Labor is assumed to be the same for both 90.1-2007 and 90.1-2010 cases. The TPO membrane with the higher requirements adds no cost. The EPDM requires a special finish to meet the requirements which adds $0.15/ft2. The source for these incremental costs is DOE Building Technologies Guidelines for Selecting Cool Roofs (DOE 2010). | DOE Building Technologies Guidelines for Selecting Cool Roofs DOE. 2010. “Guidelines for Selecting Cool Roofs”, V1.2. U.S. Department of Energy, Washington, D.C. Accessed October 25, 202. http://www1.eere.energy.gov/femp/pdfs/coolroofguide.pdf |  |  | Roof area, ft2
[19 empty] | Roof finish costs per ft2 on this line | [28 empty] | 0.95 | [6 empty] | 0.1425 | 0 | 1.0925 |  | 40 | 0.95 |  |  |  | 0 |  | 0.15911 | 0 | 1.1091 | 1.0925
| 1 | 1 | 1 | 0 | 0 | [6 empty] | Need in CZ 1-3 |  | Large Office |  |  |  | 38400 | Large Office |  |  |  | 38400 | [24 empty] | 5760 | [6 empty] | 864 | 0 | 6624 |  | 40 | 5760 |  |  |  | 0 |  | 964.7078 | 0 | 6724.7078 | 6624
| 1 | 1 | 1 | 0 | 0 | [6 empty] | Need in CZ 1-3 |  | Standalone Retail |  |  |  | 24742 | Standalone Retail |  |  |  | 24742 | [24 empty] | 3711.3 | [6 empty] | 556.695 | 0 | 4267.995 |  | 40 | 3711.3 |  |  |  | 0 |  | 621.5834 | 0 | 4332.8834 | 4267.995
| 1 | 1 | 1 | 0 | 0 | [6 empty] | Need in CZ 1-3 |  | Primary School |  |  |  | 73960 | Primary School |  |  |  | 73960 | [24 empty] | 11094 | [6 empty] | 1664.1 | 0 | 12758.1 |  | 40 | 11094 |  |  |  | 0 |  | 1858.0675 | 0 | 12952.0675 | 12758.1
| 1 | 1 | 1 | 0 | 0 | [6 empty] | Need in CZ 1-3 |  | Small Hotel |  |  |  | 43200 | Small Hotel |  |  |  | 43200 | [24 empty] | 6480 | [6 empty] | 972 | 0 | 7452 |  | 40 | 6480 |  |  |  | 0 |  | 1085.2963 | 0 | 7565.2963 | 7452
| 1 | 1 | 1 | 0 | 0 | [6 empty] | Need in CZ 1-3 |  | Mid-rise Apartment |  |  |  | 33700 | Mid-rise Apartment |  |  |  | 33700 | [24 empty] | 5055 | [6 empty] | 758.25 | 0 | 5813.25 |  | 40 | 5055 |  |  |  | 0 |  | 846.6316 | 0 | 5901.6316 | 5813.25
[12 empty] | Vestibule Addendum 90.1-07q 90.1-2010 section 5.4.3.4 Add to small office in CZ-4A, 4B, 4C |  | No vestibule. Glazed entry include two 3 ft. swinging doors 9 ft. height by 12 ft. wide meeting 90.1 glazing performance requirements. Lobby area on interior same width as entry with side walls wood framed witth gypsum board separating lobby from adjacent spaces. Separate out by climate, if glazing performance by climate zone results in different glazing costs. This is the same as the outer entry and lobby walls as for 90.1-2010. No baseline cost. | baseline entry estimated assumed by PNNL based on experience |  | not used | not used | Vestibule is 10 ft. hight by 12 ft. wide by by 7 ft. deep (7 ft. is the minimum depth in this requirement) into the building interior, glazed on interior entry wall, side walls wood framed witth gypsum board. Side walls same as 90.1-2007 baseline. Exterior entry is the same as in 90.1-2007 baseline. Interior entry wall is floor to ceiling storefront, fully glazed including entry door. Interior entry storefront and swinging door glazing are all storefront with 3/8" plate glass without low-e with total area of 120 ft2, 78 ft2 glazing with two storefront 3 ft. by 7 ft. doors Climate zone 4 is the only climate zone which has a vestibule added by this addendum under 90.1-2010. For IECC 2009 to 2012, there are no differences in the vestibule requirements, so no costs. For comparison between 90.1-2007 and IECC 2012, vestibule is added for climate zone 3 as well as 4. | Added vestibule entry estimated by PNNL to match the minimum required vestibule and based on experience. Costs for added interior entry wall from RS Means Construction Cost Data 2012 08 43 0500 |  | not used | Interior storefront entry, ft2
| 0 | 0 | 0 | 1 | 0 | [8 empty] | Small Office No vestibule |  |  |  |  | Small Office Added - climate zone 1 |  |  |  | 120 | [14 empty] | 40 | [9 empty] | 2460 | 2 Glaz | 46.2 | 12.84 | 593.208 |  |  | 457.9812 | 0 | 3511.1892 |  | 40 | 2460 | 2 Glaz | 46.2 | 21.186 | 978.7932 |  | 573.0711 | 0 | 4011.8643 | 3511.1892
[12 empty] | Air Leakage for Windows and Doors Addendum 90.07am 90.1-2010 section 5.4.3.2 |  | Air leakage requirements for doors and windows in 90.1-2007 require that leakage not exceed 1.0 cfm/ft2 for glazed swinging entrance doors and revolving doors, and 0.4 cfm/ft2 for all other products. Testing is done in accordance with NFRC 400. There is an exception for field fabricated fenestration and doors. No base cost is listed under 90.1-2007. An incremental cost is shown under 90.1-2010. Description of the window assembles under 90.1-2007 is included here for comparison. |  |  | Window area including doors, or skylight area. Areas include framing. ft2 |  | Air leakage requirements for doors and windows in 90.1-2010 vary by type of window. Listed here are the leakage values for types with cost estimates in this analysis. See 90.1-2010 5.4.3.2 for testing methods. * Curtainwall and storefront 0.06 cfm/ft2 * Skylights 0.3 cfm/ft2 or 0.5 cfm/ft2 depending on testing method. Assume the 0.3 cfm/ft2 reflects a reduction in leakage from the 0.4 cfm/ft2 required in 90.1-2007. *All other products 0.2 cfm/ft2 or 0.3 cfm/ft2 depending on testing method. 90.1 Envelope Subcommittee members indicate that the air leakage requirements in 2010 reflect common practice that has been in place for many years even since before 90.1-2007 for many producst. In reality, building projects in states adopting the newer Standard will not see an increase in project costs for this provision. However, the modeled energy savings reflects this change being codified and not identified previously in the 90.1 code development, so a cost estimate is developed. Determining the cost difference is difficult with no window products available applicable to the prototype models that do not meet the current air leakage requirements. A curtainwall manufacturer technical expert said that infiltration has been tightened over time for two reasons unrelated to specific air leakage standards, 1) reduced u-factors, u-factor testing is affected by leakage rates, 2) moisture infiltration and concerns about mold and associated liability. The changes have been achieved primarily in design, not manufacturing. The technical expert indicated that this engineering effort translates into an average of around $0.05/ft2 to $0.10/ft2 of window area. This cost is related to the volume of project sales, which is considerably higher for manufactured windows than for curtain wall systems. As a result, this cost is estimated as an incremental material cost of $0.05/ft2 of window area for all of the windows. | 90.1 Envelope Subcommittee members individual opinions. Interview with K. Best, Benson Industries, window curtainwall, storefront and custom manufactured windows |  | Window area including doors, or skylight area. Areas include framing. | Material cost per ft2
| 1 | 1 | 1 | 1 | 1 | [8 empty] | Small Office - Fixed metal frame windows, double glazed, average of with and without thermal break, leakage rate maximum 0.4 cfm/ft2. |  |  | 165 |  | Fixed metal frame windows, double glazed, average of with and without thermal break, leakage rate maximum 0.2 or 0.3 cfm/ft2 - see note above on testing methods. |  |  | 165 | 0.05 | [24 empty] | 8.25 |  |  |  | 0 | 0 | 0 | 1.2375 | 0 | 9.4875 |  | 40 | 8.25 | [5 empty] | 1.3817 | 0 | 9.6317 | 9.4875
| 1 | 1 | 1 | 1 | 1 | [8 empty] | Large Office Windows - Ribbon windows in prototype, assumed to be curtain wall average without thermal break/thermally improved/thermal break. Site-built, no leakage rate required |  |  | 40320 |  | Large Office Windows - Ribbon windows in prototype, assumed to be curtain wall average without thermal break/thermally improved/thermal break. Site-built, no leakage rate required |  |  | 40320 | 0.05 | [24 empty] | 2016 |  |  |  | 0 | 0 | 0 | 302.4 | 0 | 2318.4 |  | 40 | 2016 | [5 empty] | 337.6477 | 0 | 2353.6477 | 2318.4
| 1 | 1 | 1 | 1 | 1 | [8 empty] | Standalone Retail Windows - Fixed metal frame windows, double glazed, average of with and without thermal break, leakage rate maximum 0.4 cfm/ft2. |  |  | 581 |  | Standalone Retail Windows - Fixed metal frame windows, double glazed, average of with and without thermal break, leakage rate maximum 0.4 cfm/ft2. |  |  | 581 | 0.05 | [24 empty] | 29.05 |  |  |  | 0 | 0 | 0 | 4.3575 | 0 | 33.4075 |  | 40 | 29.05 | [5 empty] | 4.8654 | 0 | 33.9154 | 33.4075
| 1 | 1 | 1 | 1 | 1 | [8 empty] | Standalone Retail Skylights - Double glazed skylight, white, curbed, leakage rate 0.4 cfm/ft2 |  |  | 72 |  | Standalone Retail Skylights - Double glazed skylight, white, curbed, leakage rate 0.4 cfm/ft2 |  |  | 72 | 0.05 | [24 empty] | 3.6 |  |  |  | 0 | 0 | 0 | 0.54 | 0 | 4.14 |  | 40 | 3.6 | [5 empty] | 0.60294 | 0 | 4.2029 | 4.14
| 1 | 1 | 1 | 1 | 1 | [8 empty] | Primary School Windows - Fixed metal frame windows, double glazed, average of with and without thermal break, leakage rate maximum 0.4 cfm/ft2. |  |  | 9215 |  | Primary School Windows - Fixed metal frame windows, double glazed, average of with and without thermal break, leakage rate maximum 0.4 cfm/ft2. |  |  | 9215 | 0.05 | [24 empty] | 460.75 |  |  |  | 0 | 0 | 0 | 69.1125 | 0 | 529.8625 |  | 40 | 460.75 | [5 empty] | 77.1683 | 0 | 537.9183 | 529.8625
| 1 | 1 | 1 | 1 | 1 | [8 empty] | Primary School Skylights - Double glazed skylight, white, curbed, leakage rate 0.4 cfm/ft2 |  |  | 144 |  | Primary School Skylights - Double glazed skylight, white, curbed, leakage rate 0.4 cfm/ft2 |  |  | 144 | 0.05 | [24 empty] | 7.2 |  |  |  | 0 | 0 | 0 | 1.08 | 0 | 8.28 |  | 40 | 7.2 | [6 empty] | 0 | 7.2 | 8.28
| 1 | 1 | 1 | 1 | 1 | [8 empty] | Small Hotel Windows - Fixed metal frame windows, double glazed, average of with and without thermal break, leakage rate maximum 0.4 cfm/ft2. |  |  | 4649 |  | Small Hotel Windows - Fixed metal frame windows, double glazed, average of with and without thermal break, leakage rate maximum 0.4 cfm/ft2. |  |  | 4649 | 0.05 | [24 empty] | 232.45 |  |  |  | 0 | 0 | 0 | 34.8675 | 0 | 267.3175 |  | 40 | 232.45 | [5 empty] | 38.9317 | 0 | 271.3817 | 267.3175
| 1 | 1 | 1 | 1 | 1 | [8 empty] | Mid-rise Apartments WindowsResidential vertical slider metal frame windows, double glazed without thermal break, leakage rate maximum 0.4 cfm/ft2 |  |  | 1751 |  | Mid-rise Apartments WindowsResidential vertical slider metal frame windows, double glazed without thermal break, leakage rate maximum 0.4 cfm/ft2 |  |  | 1751 | 0.05 | [24 empty] | 87.55 |  |  |  | 0 | 0 | 0 | 13.1325 | 0 | 100.6825 |  | 40 | 87.55 | [5 empty] | 14.6632 | 0 | 102.2132 | 100.6825
[12 empty] | Building Envelope Air Sealing Addendum 90.07bf 90.1-2010 section 5.4.3.1 |  | 90.1-2007, section 5.4.3.1 Building Envelope Sealing requires sealing, caulking, gasketing, and weatherization to minimize air leakage of a list of seven building envelope components that include the entire building enclosures joints, seams, junctions, openings, between components such as wall and roof sections, and fenestration. There are no costs in this section. Costs are estimated under 90.1-2010 as incremental added costs. |  |  |  |  | 90.1-2010 Section 5.4.3.1 requires the building envelope to be designed and constructed with a continuous air barrier, but the definition of continuous air barrier is "the combination of interconnected materials, assemblies, and sealed joints and components of the building envelope that minimize air leakage into or out of the building envelope." No specific leakage rate or testing is required. This definition allows the requirement to be met as in 90.1-2007, with sealing of joints etc. at component boundaries. There are some additional air barrier design requirements, and a section of materials such as plywood etc. that are required to meet a pressure differential of 0.3 in. w.g. under test conditions. Members of the 90.1 Envelope Subcommittee supported the interpretation that a continuous membrane air sealing system is not required, and that the requirement primarily increase quality assurance and quality control (QA/QC) of the building air sealing. This cost is estimated by PNNL based on the cost of building envelope commissioning although commissioning is not required to meet 90.1. Blower door or other testing costs are not included. The incremental cost is assumed by PNNL to be 25% (in the absence of any more accurate value) of the cost of the portion of envelope/enclosure commissioning associated primarily with air sealing. The costs are shown as total cost under labor, not commissioning in the estimate, with no additional OH&P. Two commissioning firms shared views about the cost and scope of envelope commissioning which includes involvement throughout design such as development of owner requirements, and design reviews, and throughout construction including review of submittals, and frequent site inspections during the core air barrier installation period. One commissioning agent provided a total building envelope commissioning cost of $0.25 to $0.45/ft2 (without physical testing) for a range of building sizes with about 25% of that focused on air sealing, with the rest focused primarily on water and moisture control (Epsten Group). The other commissioning agent emphasized that the costs do not vary substantially with building size and provided an estimate on the order of $60,000 for mid-range size and complexity buildings and an estimate that about 50% of that is associated with air sealing (WJE). Both firms emphasized the air sealing and water and moisture control are integrated and any separation is rough. Costs per square foot are higher for smaller buildings as there are fixed costs to provide the basic level of service including reporting, meetings, and site visits. Costs are higher for more complex buildings such as laboratories and hospitals with tighter requirements for pressurization and air changes. The primary consumers of these services currently are government and institutional building projects, and the scope and costs may vary as the commercial market grows. A base cost of $10,000 plus $0.40/ft2 is assumed by PNNL as a starting point. 10% of this, or $1,000 plus $0.04/ft2 is assumed to be the cost of the additional envelope QA/QC for this addendum (37.5% for air sealing out of total envelope commissioning multiplied by 25% of for added QA/QC for 90.1-2010 relative to the air sealing envelope commissioning rounded up). Costs are treated as commissioning. | 90.1 Envelope Subcommittee members D. Draper and K. Dehganian, Epsten Group F. Aldous, WJE PNNL staff A source on building envelope/enclosure commissioning, NIBS Guideline 3-2012 Building Enclosure Commissioning Process BECx is available at http://www.wbdg.org/ccb/browse_doc.php?d=7167 |  |  | Total Floor Area, ft2
| 1 | 1 | 1 | 1 | 1 | [8 empty] | Small Office Air Sealing |  |  |  |  | Small Office |  |  |  | 5500 | [32 empty] | 1220 | 1220 |  | 40 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1220
| 1 | 1 | 1 | 1 | 1 | [8 empty] | Large Office Air Sealing |  |  |  |  | Large Office |  |  |  | 498640 | [32 empty] | 20945.6 | 20945.6 |  | 40 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 20945.6
| 1 | 1 | 1 | 1 | 1 | [8 empty] | Standalone Retail Air Sealing |  |  |  |  | Standalone Retail |  |  |  | 24690 | [32 empty] | 1987.6 | 1987.6 |  | 40 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1987.6
| 1 | 1 | 1 | 1 | 1 | [8 empty] | Primary School Air Sealing |  |  |  |  | Primary School |  |  |  | 73970 | [32 empty] | 3958.8 | 3958.8 |  | 40 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 3958.8
| 1 | 1 | 1 | 1 | 1 | [8 empty] | Small Hotel Air Sealing |  |  |  |  | Small Hotel |  |  |  | 43210 | [32 empty] | 2728.4 | 2728.4 |  | 40 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 2728.4
| 1 | 1 | 1 | 1 | 1 | [8 empty] | Mid-rise Apartment Air Sealing |  |  |  |  | Mid-rise Apartment |  |  |  | 33740 | [32 empty] | 2349.6 | 2349.6 |  | 40 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 2349.6
[12 empty] | Skylights Added for Daylighting Addendum 90.1-07ab and 90.1-07dd 90.1-2010 section 5.5.4.2.3 |  | There are no requirements to include skylights in 90.1-2007. Some of the selected prototypes for the cost effectiveness analysis include some skylights based on prevalence of these in real buildings: primary school mulitipurpose room, and standalone retail core retail space. The addenda add skylight area to the standalone retail only; primary school baseline meets the skylight area requirement already. There are no baseline costs shown, just the incremental costs under the 90.1-2010 costs |  |  |  |  | The addenda require enclosed area larger than 5,000 ft2 directly under a roof with 15' ceiling height or greater for selected space types to include skylights so the that toplit area is at least half of the floor area. Minimum skylight area is 3% of the daylit areas with a skylight visible transmittance of at least 40%, or sufficient to provide an effective aperature of a least 1%. Primary School and Standalone Retail are potentially affectd out of the selected prototypes, but primary school already includes sufficient skylights in the affected area, the multi-purpose room. Standalone retail does have some skylights in the core retail space subject to the requirement, but some additional skylights much be added. According to the analysis described in the Achieving the 30% Goal report, an additional 184 ft2 of skylight. Skylight costs/ft2 are from envelope costs above for corresponding climate and skylight type. | Faithful and Gould, commercial envelope cost data base. Labor crew and rate adjusted for RS Means Construction Cost Data 2012 | added skylight area, ft2 90.1-2010 | added skylight area, ft2 IECC-2012 Need to enter correct value below | Area for selected state | [23 empty] | Cost $/ft2 |  |  |  | Cost $/ft2
| 1 | 1 | 1 | 1 | 1 | [8 empty] | Standalone Retail - no baseline costs |  |  |  |  | Climate Zone 1 for state |  | 184 | 184 | 184 | [23 empty] | #N/A | #N/A |  |  | #N/A | #N/A |  |  | #N/A | 0 | #N/A |  | 40 | #N/A |  |  | #N/A | #N/A |  | #N/A | 0 | #N/A | #N/A
| 1 | 1 | 1 | 1 | 1 | [8 empty] | Standalone Retail - no baseline costs |  |  |  |  | Climate Zone 2 for state |  | 184 | 184 | 184 | [23 empty] | 0 | 0 |  |  | 0 | 0 |  |  | 0 | 0 | 0 |  | 40 | 0 |  |  | 0 | 0 |  | 0 | 0 | 0 | 0
| 1 | 1 | 1 | 1 | 1 | [8 empty] | Standalone Retail - no baseline costs |  |  |  |  | Climate Zone 3 for state |  | 184 | 184 | 184 | [23 empty] | #N/A | #N/A |  |  | #N/A | #N/A |  |  | #N/A | 0 | #N/A |  | 40 | #N/A |  |  | #N/A | #N/A |  | #N/A | 0 | #N/A | #N/A
| 1 | 1 | 1 | 1 | 1 | [8 empty] | Standalone Retail - no baseline costs |  |  |  |  | Climate Zone 4 for state |  | 184 | 184 | 184 | [23 empty] | 0 | 0 |  |  | 0 | 0 |  |  | 0 | 0 | 0 |  | 40 | 0 |  |  | 0 | 0 |  | 0 | 0 | 0 | 0
| 1 | 1 | 1 | 1 | 1 | [8 empty] | Standalone Retail - no baseline costs |  |  |  |  | Climate Zone 5 for state |  | 184 | 184 | 184 | [23 empty] | #N/A | #N/A |  |  | #N/A | #N/A |  |  | #N/A | 0 | #N/A |  | 40 | #N/A |  |  | #N/A | #N/A |  | #N/A | 0 | #N/A | #N/A
90.1 Section 8 Power
[12 empty] | Transformer Efficiency Addendum 90.13 bt 90.1-2016 section 8.4.4 |  | Addendum 90.1-13bt incorporates the Federal (EPACT 2005; DOE-2016) regulations for low-voltage dry-type distribution transformers. This requires increased efficiency compared with 90.1-2013. For the 90.1-07, costs for transformers is developed for the 3-phase tranformers, aluminum wound in the size ranges in Table 8.1 in 90.1-2010 section 8.1.2 up to 150 kVa. Costs are middle of the market cost estimates at today's prices for transformers with efficiencies that existed prior to implementation of EPACT 2005. The efficiency of older transformers are assumed consistent with the analysis presented in Achieving the 30% Goal (reference under Source). For reference, analysis for 75 kVA transformer used a base 96.6% versus 98.2% for 90.1-2010. Based on information from transformer manufacturers, the cost estimate is 5% less for material costs compared to the 90.1-2010 efficiency transformers. Only material costs are shown, labor is the same for both years of 90.1. This same percentage approach is applied for the transformers with an inflation factor applied based on Means differences. Note that in reality, projects will not see an increase in transformer costs due to implementing 90.1-2010 as the code for a government jurisdiction, as the price difference was absorbed years ago, and the lower efficiency units are not available. Costs are developed for the prototypes that are larger than 50,000 ft2, and transformer quantity and sizes are developed for total plug load power, and incandescent lighting, which are what are generally served by step-down transformers. Transformers are sized so that peak load is 75% of the transformer capacity. Baseline efficiencies are not computed for all sizes. A partload curve for 75 kVA was developed for savings analysis for this addendum as documented in the Achieving the 30% Goal... was based on a 75 kVa transformer. | Efficiency analysis - Achieving the 30% Goal: Energy and Cost Savings, Thornton et al. 2011, PNNL-20405 This 5% difference is based on two conversations with manufacturers by Faithful and Gould staff. 1) Square D Technical Support 1-888-778-2733, list transformer pricing remains unchanged from 2007 through 2012. 2) Tierney Transformer Company - the pricing for transformers not meeting EPACT 2005 and not regulated by 90.1 2007 were about 10% less than today's pricing in comparison at today's pricing. | look at rulemaking data |  | Transformer Efficiency | Addendum 90.1-2010 section 8.1.2 incorporates the Federal (EPACT 2005) regulations for low-voltage dry-type distribution transformers. Minimum efficiency values are in Table 8.1. The 90.1-2010 costs for transformers are developed for the current market 3-phase tranformers, aluminum wound in the size ranges and efficiencies in Table 8.1 in 90.1-2010 section 8.1.2 up to 150 kVa. Only material costs are shown, labor is the same for both years of 90.1. Note that in reality, projects will not see an increase in transformer costs due to implementing 90.1-2010 as the code for a government jurisdiction, as the price difference was absorbed years ago, and the lower efficiency units are not available. Costs are developed for the prototypes that are larger than 50,000 ft2, and transformer quantity and sizes are developed for total plug load power, and incandescent lighting, which are what are generally served by step-down transformers. Transformers are sized so that peak load is 75% of the transformer capacity. | Faithful and Gould staff. 1) Square D 2) Tierney Transformer Company |  | Transformer Size, kVa | Transformer Efficiency |  | Inflation factor from 2012 to 2018; included in cost adjustments
[14 empty] | Standard size transformers, 90.1-2013 |  |  |  |  | Standard size transformers kVa, 90.1-2016 | [25 empty] | 0
[14 empty] | 15 |  |  |  | 97 | 15 |  |  | 15 | 97.89 |  | 1.4 |  |  | 1050.6834 | [6 empty] | 640.9169 | 1691.6002 |  | 30 | [6 empty] | 0 |  |  | 1105.9825 | [6 empty] | 674.6493 |  | 1780.6318 |  | 30 | 1105.9825 | [5 empty] | 185.2344 |  | 1291.2169 | 89.0316
[14 empty] | 30 |  |  |  | 97.5 | 30 |  |  | 30 | 98.23 |  | 1.4 |  |  | 1110.1066 | [6 empty] | 677.165 | 1787.2716 |  | 30 | [6 empty] | 0 |  |  | 1168.5332 | [6 empty] | 712.8053 |  | 1881.3385 |  | 30 | 1168.5332 | [5 empty] | 195.7106 |  | 1364.2439 | 94.0669
[14 empty] | 45 |  |  |  | 97.7 | 45 |  |  | 45 | 98.4 |  | 1.4 |  |  | 1342.4122 | [6 empty] | 818.8715 | 2161.2837 |  | 30 | [6 empty] | 0 |  |  | 1413.0655 | [6 empty] | 861.97 |  | 2275.0355 |  | 30 | 1413.0655 | [5 empty] | 236.6659 |  | 1649.7314 | 113.7518
[14 empty] | 75 |  |  |  | 98 | 75 |  |  | 75 | 98.6 |  | 1.4 |  |  | 2000.9729 | [6 empty] | 1220.5935 | 3221.5663 |  | 30 | [6 empty] | 0 |  |  | 2106.2872 | [6 empty] | 1284.8352 |  | 3391.1225 |  | 30 | 2106.2872 | [5 empty] | 352.7694 |  | 2459.0567 | 169.5561
[14 empty] | 112.5 |  |  |  | 98.2 | 112.5 |  |  | 112.5 | 98.74 |  | 1.4 |  |  | 2620.6484 | [6 empty] | 1598.5955 | 4219.2439 |  | 30 | [6 empty] | 0 |  |  | 2758.5772 | [6 empty] | 1682.7321 |  | 4441.3094 |  | 30 | 2758.5772 | [5 empty] | 462.0176 |  | 3220.5948 | 222.0655
[14 empty] | 150 |  |  |  | 98.3 | 150 |  |  | 150 | 98.83 |  | 1.4 |  |  | 3811.7472 | [6 empty] | 2325.1658 | 6136.913 |  | 30 | [6 empty] | 0 |  |  | 4012.3655 | [6 empty] | 2447.543 |  | 6459.9085 |  | 30 | 4012.3655 | [5 empty] | 672.007 |  | 4684.3725 | 322.9954
| 1 | 1 | 1 | 1 | 1 |  | 1 | [6 empty] | Large Office (2) 112.5 kVA, (2) 150 kVA transformers at assumed baseline efficiency |  |  |  |  | Large Office (2) 112.5 kVA, (2) 150 kVA transformers at assumed baseline efficiency |  |  | (2) 112.5, (2) 150 | [5 empty] | 12864.7912 | [6 empty] | 1929.7187 | 14794.5099 |  | 30 | [6 empty] | 0 |  |  | 13541.8855 | [6 empty] | 2031.2828 |  | 15573.1683 |  | 30 | 13541.8855 | [5 empty] | 2268.0492 |  | 15809.9347 | 778.6584
| 1 | 1 | 1 | 1 | 1 |  |  |  | 1 |  |  |  |  | Primary School (2) 75 kVA transformers at assumed baseline efficiency |  |  |  |  | Primary School (2) 75 kVA transformers at assumed baseline efficiency |  |  | (2) 75 | [5 empty] | 4001.9458 | [6 empty] | 600.2919 | 4602.2376 |  | 30 | [6 empty] | 0 |  |  | 4212.5745 | [6 empty] | 631.8862 |  | 4844.4607 |  | 30 | 4212.5745 | [5 empty] | 705.5388 |  | 4918.1133 | 242.223
[12 empty] | Receptacle Occupancy Control Addendum 90.1-10bf 90.1-2013 section 8.4.2 |  | 90.1-2010 has requirements for receptacle load control; however those spaces are not included here. Only space types with new requirements are listed here, so the baseline costs are for outlets wired without control. Using means cost and labor, assume 3 x 25 (75) feet of wire per outlet. Basis: 16 outlets per occupancy sensor zone. Unit costs shown on this row to right are costs per control relay with 8 controlled outlets. | Plug Load Density, W/ft2 | Affected Area | Assumed number of watts/control relay | Number of control relays - nearest half | Addendum 90.1-10bf expands those requirements to additional areas by adding conference rooms, print/copy rooms, break rooms, and classrooms other than computer classrooms to the list of spaces requiring control and reducing the time to shut-off power when using an occupancy sensor to 20 minutes instead of 30 minutes. The cost estimate was based on occupancy sensor control. The cost estimate is based on occupancy sensor control using lighting occupancy sensors, plug load power relays, additional wiring, and additional labor for split receptacles. Using means cost and labor, assume 4 x 25 (100) feet of wire per outlet. Basis: 16 outlets (split) per occupancy sensor zone, and occupancy sensors installed for lighting with power pack required. Note that for larger areas, up to 32 outlets could be controlled, each with a split circuitry. The cost is based on 16 outlets per zone, 8 controlled and 8 uncontrolled. | Cost source: Watt stopper digital power pack cost from Kele controls. For smaller areas, simple bare contact added to existing lighting occupancy sensors acheives result at lower cost. Below - Plug Load Density, W/ft2 | Affected Area | Assumed number of watts/ control relay | Number of control relays |  |  |  |  | 150 | Unit cost per 16 uncontrolled outlets |  |  | 487.5 | Unit cost per 16 uncontrolled outlets | [5 empty] | one third cost requires replacement |  |  |  | one third cost requires replacement |  |  |  |  | 419.9 | Unit cost per control relay on 8 outlets, with 8 uncontrolled outlets |  |  | 765 | Unit cost per control relay on 8 outlets, with 8 uncontrolled outlets | [6 empty] | one third cost requires replacement |  |  |  | one third cost requires replacement
[48 empty] | 419.9 |  |  |  | 765
[14 empty] | RS Means 2014 Mech. Book 26 05 19.90 0030 Wire #12 copper type THW, solid, C.L.F | [11 empty] | 12 | 12.5 | 150 |  |  | 39 | 487.5 | [13 empty] | 16 | 12.5 | 200 |  | 39 |  | 624
[14 empty] | 26 27 26.10 3600 Relays, 120 V or 277 V standard Ea. | [31 empty] | 1 | 41 | 41 |  | 35.5 |  | 35.5
[14 empty] | 26 09 23.10 0200 Remote power pack | [31 empty] | 1 | 33 | 33 |  | 44.5 |  | 44.5
[14 empty] | Grainger 2014 6DXE6 Occupancy Sensor | [31 empty] | 1 | 145.9 | 145.9 |  | 61 |  | 61
| 1 | 1 | 1 | 1 | 1 | 1 | [7 empty] | Small Office - Break Room | 0.63 | 110 | 528 | 0.5 | Small Office - Break Room | 0.63 | 110 | 528 | 0.5 |  |  |  |  | 75 |  |  |  | 243.75 |  |  | 91.8 | 410.55 |  | 20 | 25 |  |  |  | 131.8688 |  | 54.2638 | 211.1325 |  | 209.95 |  |  |  | 382.5 |  |  | 170.6256 |  | 763.0756 |  | 20 | 69.9833 |  |  |  | 206.9325 |  | 105.1852 |  | 382.1011 | 352.5256
| 1 | 1 | 1 | 1 | 1 | 1 | [7 empty] | Small Office - Conference Room | 0.63 | 440 | 528 | 1 | Small Office - Conference Room | 0.63 | 440 | 528 | 1 |  |  |  |  | 150 |  |  |  | 487.5 |  |  | 183.6 | 821.1 |  | 20 | 50 |  |  |  | 263.7375 |  | 108.5275 | 422.265 |  | 419.9 |  |  |  | 765 |  |  | 341.2512 |  | 1526.1512 |  | 20 | 139.9667 |  |  |  | 413.865 |  | 210.3705 |  | 764.2022 | 705.0512
| 1 | 1 | 1 | 1 | 1 |  | 1 | [6 empty] | Large Office - Classroom | 0.75 | 1895 | 528 | 3 | Large Office - Classroom | 0.75 | 1895 | 528 | 3 |  |  |  |  | 450 |  |  |  | 1462.5 |  |  | 550.8 | 2463.3 |  | 20 | 150 |  |  |  | 791.2125 |  | 325.5825 | 1266.795 |  | 1259.7 |  |  |  | 2295 |  |  | 1023.7536 |  | 4578.4536 |  | 20 | 419.9 |  |  |  | 1241.595 |  | 631.1115 |  | 2292.6065 | 2115.1536
| 1 | 1 | 1 | 1 | 1 |  | 1 | [6 empty] | Large Office - Break Room | 0.75 | 1147 | 528 | 2 | Large Office - Break Room | 0.75 | 1147 | 528 | 2 |  |  |  |  | 300 |  |  |  | 975 |  |  | 367.2 | 1642.2 |  | 20 | 100 |  |  |  | 527.475 |  | 217.055 | 844.53 |  | 839.8 |  |  |  | 1530 |  |  | 682.5024 |  | 3052.3024 |  | 20 | 279.9333 |  |  |  | 827.73 |  | 420.741 |  | 1528.4043 | 1410.1024
| 1 | 1 | 1 | 1 | 1 |  | 1 | [6 empty] | Large Office - Conference Room | 0.75 | 7729 | 528 | 11 | Large Office - Conference Room | 0.75 | 7729 | 528 | 11 |  |  |  |  | 1650 |  |  |  | 5362.5 |  |  | 2019.6 | 9032.1 |  | 20 | 550 |  |  |  | 2901.1125 |  | 1193.8025 | 4644.915 |  | 4618.9 |  |  |  | 8415 |  |  | 3753.7632 |  | 16787.6632 |  | 20 | 1539.6333 |  |  |  | 4552.515 |  | 2314.0755 |  | 8406.2238 | 7755.5632
| 1 | 1 | 1 | 1 | 1 |  |  | 1 | [5 empty] | Standalone Retail - Classroom | 0.7 | 99 | 528 | 0.5 | Standalone Retail - Classroom | 0.7 | 99 | 528 | 0.5 |  |  |  |  | 75 |  |  |  | 243.75 |  |  | 91.8 | 410.55 |  | 20 | 25 |  |  |  | 131.8688 |  | 54.2638 | 211.1325 |  | 209.95 |  |  |  | 382.5 |  |  | 170.6256 |  | 763.0756 |  | 20 | 69.9833 |  |  |  | 206.9325 |  | 105.1852 |  | 382.1011 | 352.5256
| 1 | 1 | 1 | 1 | 1 |  |  | 1 | [5 empty] | Standalone Retail - Break Room | 0.7 | 272 | 528 | 0.5 | Standalone Retail - Break Room | 0.7 | 272 | 528 | 0.5 |  |  |  |  | 75 |  |  |  | 243.75 |  |  | 91.8 | 410.55 |  | 20 | 25 |  |  |  | 131.8688 |  | 54.2638 | 211.1325 |  | 209.95 |  |  |  | 382.5 |  |  | 170.6256 |  | 763.0756 |  | 20 | 69.9833 |  |  |  | 206.9325 |  | 105.1852 |  | 382.1011 | 352.5256
| 1 | 1 | 1 | 1 | 1 |  |  | 1 | [5 empty] | Standalone Retail - Conference Room | 0.7 | 25 | 528 | 0.5 | Standalone Retail - Conference Room | 0.7 | 25 | 528 | 0.5 |  |  |  |  | 75 |  |  |  | 243.75 |  |  | 91.8 | 410.55 |  | 20 | 25 |  |  |  | 131.8688 |  | 54.2638 | 211.1325 |  | 209.95 |  |  |  | 382.5 |  |  | 170.6256 |  | 763.0756 |  | 20 | 69.9833 |  |  |  | 206.9325 |  | 105.1852 |  | 382.1011 | 352.5256
| 1 | 1 | 1 | 1 | 1 |  |  |  | 1 |  |  |  |  | Primary School - Classroom | 1.39 | 35829 | 528 | 94.5 | Primary School - Classroom | 1.39 | 35829 | 528 | 94.5 |  |  |  |  | 14175 |  |  |  | 46068.75 |  |  | 17350.2 | 77593.95 |  | 20 | 4725 |  |  |  | 24923.1937 |  | 10255.8491 | 39904.0429 |  | 39680.55 |  |  |  | 72292.5 |  |  | 32248.2384 |  | 144221.2884 |  | 20 | 13226.85 |  |  |  | 39110.2425 |  | 19880.012 |  | 72217.1045 | 66627.3384
| 1 | 1 | 1 | 1 | 1 |  |  |  | 1 |  |  |  |  | Primary School - Break Room | 1 | 95 | 528 | 0.5 | Primary School - Break Room | 1 | 95 | 528 | 0.5 |  |  |  |  | 75 |  |  |  | 243.75 |  |  | 91.8 | 410.55 |  | 20 | 25 |  |  |  | 131.8688 |  | 54.2638 | 211.1325 |  | 209.95 |  |  |  | 382.5 |  |  | 170.6256 |  | 763.0756 |  | 20 | 69.9833 |  |  |  | 206.9325 |  | 105.1852 |  | 382.1011 | 352.5256
| 1 | 1 | 1 | 1 | 1 |  |  |  | 1 |  |  |  |  | Primary School - Conference Room | 1 | 380 | 528 | 1 | Primary School - Conference Room | 1 | 380 | 528 | 1 |  |  |  |  | 150 |  |  |  | 487.5 |  |  | 183.6 | 821.1 |  | 20 | 50 |  |  |  | 263.7375 |  | 108.5275 | 422.265 |  | 419.9 |  |  |  | 765 |  |  | 341.2512 |  | 1526.1512 |  | 20 | 139.9667 |  |  |  | 413.865 |  | 210.3705 |  | 764.2022 | 705.0512
| 1 | 1 | 1 | 1 | 1 |  |  |  |  | 1 |  |  |  | Small Hotel - Break Room | 2 | 351 | 528 | 1.5 | Small Hotel - Break Room | 2 | 351 | 528 | 1.5 |  |  |  |  | 225 |  |  |  | 731.25 |  |  | 275.4 | 1231.65 |  | 20 | 75 |  |  |  | 395.6062 |  | 162.7913 | 633.3975 |  | 629.85 |  |  |  | 1147.5 |  |  | 511.8768 |  | 2289.2268 |  | 20 | 209.95 |  |  |  | 620.7975 |  | 315.5557 |  | 1146.3032 | 1057.5768
| 1 | 1 | 1 | 1 | 1 |  |  |  |  | 1 |  |  |  | Small Hotel - Conference Room | 0.57 | 864 | 528 | 1 | Small Hotel - Conference Room | 0.57 | 864 | 528 | 1 |  |  |  |  | 150 |  |  |  | 487.5 |  |  | 183.6 | 821.1 |  | 20 | 50 |  |  |  | 263.7375 |  | 108.5275 | 422.265 |  | 419.9 |  |  |  | 765 |  |  | 341.2512 |  | 1526.1512 |  | 20 | 139.9667 |  |  |  | 413.865 |  | 210.3705 |  | 764.2022 | 705.0512
90.1 Section 10 Other
| 1 | [10 empty] | Motor Efficiency Addendum 90.07aj 90.1-2010 section 10.4.1 |  | These costs are covered under mechanical because motors are associated with mechanical equipment capacity. See "Mech Costs Comp" worksheet in this workbook. |  |  |  |  | These costs are covered under mechanical because motors are associated with mechanical equipment capacity. See "Mech Costs Comp" worksheet in this workbook.
1 | 1 | 1 | 1 | 1 | 1 |  | 1 |  |  |  |  | Renewables, 0.50 W/sf, 90.1-2019by,cc |  | No renewable energy |  |  |  |  | Onsite PV | [16 empty] | 0 | [20 empty] | 92908 | [11 empty] | 92908
1 | 1 | 1 | 1 | 1 | 1 |  |  | 1 |  |  |  | Renewables, 0.50 W/sf, 90.1-2019by,cc |  | No renewable energy |  |  |  |  | Onsite PV | [16 empty] | 0 | [20 empty] | 24390 | [11 empty] | 24390
1 | 1 | 1 | 1 | 1 | 1 |  |  |  | 1 |  |  | Renewables, 0.50 W/sf, 90.1-2019by,cc |  | No renewable energy |  |  |  |  | Onsite PV | [16 empty] | 0 | [20 empty] | 63280 | [11 empty] | 63280
1 | 1 | 1 | 1 | 1 | 1 |  |  |  |  | 1 |  | Renewables, 0.50 W/sf, 90.1-2019by,cc |  | No renewable energy |  |  |  |  | Onsite PV | [16 empty] | 0 | [20 empty] | 29610 | [11 empty] | 29610
1 | 1 | 1 | 1 | 1 | 1 | [5 empty] | 1 | Renewables, 0.50 W/sf, 90.1-2019by,cc |  | No renewable energy |  |  |  |  | Onsite PV | [16 empty] | 0 | [20 empty] | 22757 | [11 empty] | 22757
1 | 1 | 1 | 1 | 1 | 1 |  | 1 |  |  |  |  | Elevator performance, 90.1-2019cf |  | Base elevator efficiency |  |  |  |  | Improved efficiency | 10% of RSMeans base cost | [6 empty] | 0 | [8 empty] | 0 | [20 empty] | 143400 | [11 empty] | 143400
1 | 1 | 1 | 1 | 1 | 1 |  |  |  |  | 1 |  | Elevator performance, 90.1-2019cf |  | Base elevator efficiency |  |  |  |  | Improved efficiency | 10% of RSMeans base cost | [6 empty] | 0 | [8 empty] | 0 | [20 empty] | 23900 | [11 empty] | 23900
1 | 1 | 1 | 1 | 1 | 1 | [5 empty] | 1 | Elevator performance, 90.1-2019cf |  | Base elevator efficiency |  |  |  |  | Improved efficiency | 10% of RSMeans base cost | [6 empty] | 0 | [8 empty] | 0 | [20 empty] | 11950 | [11 empty] | 11950
1 | 1 | 1 | 1 | 1 | 1 | 1 | [5 empty] | Energy Credits, 90.1-2019ap |  | No energy credits |  |  |  |  | Energy credits | [16 empty] | 0 | [20 empty] | 4003 | [11 empty] | 4003
1 | 1 | 1 | 1 | 1 | 1 |  | 1 |  |  |  |  | Energy Credits, 90.1-2019ap |  | No energy credits |  |  |  |  | Energy credits | [16 empty] | 0 | [20 empty] | 364286 | [11 empty] | 364286
1 | 1 | 1 | 1 | 1 | 1 |  |  | 1 |  |  |  | Energy Credits, 90.1-2019ap |  | No energy credits |  |  |  |  | Energy credits | [16 empty] | 0 | [20 empty] | 11198 | [11 empty] | 11198
1 | 1 | 1 | 1 | [5 empty] | 1 |  |  | Energy Credits, 90.1-2019ap |  | No energy credits |  |  |  |  | Energy credits | [16 empty] | 0 | [20 empty] | 31216 | [11 empty] | 31216
1 |  |  |  | 1 | 1 |  |  |  | 1 |  |  | Energy Credits, 90.1-2019ap |  | No energy credits |  |  |  |  | Energy credits | [16 empty] | 0 | [20 empty] | 40329 | [11 empty] | 40329
1 | 1 | [8 empty] | 1 |  | Energy Credits, 90.1-2019ap |  | No energy credits |  |  |  |  | Energy credits | [16 empty] | 0 | [20 empty] | 16209 | [11 empty] | 16209
1 |  | 1 | 1 | 1 | 1 |  |  |  |  | 1 |  | Energy Credits, 90.1-2019ap |  | No energy credits |  |  |  |  | Energy credits | [16 empty] | 0 | [20 empty] | 13048 | [11 empty] | 13048
1 | 1 | 1 | 1 | 1 | 1 | [5 empty] | 1 | Energy Credits, 90.1-2019ap |  | No energy credits |  |  |  |  | Energy credits | [16 empty] | 0 | [20 empty] | 10698 | [11 empty] | 10698
| 1 | [10 empty] | Elevator Lighting and Exhaust Addendum 90.1-07df 90.1-2010 section 10.4.3 |  | No energy credits | PNNL lighting design for lighting selections. Products and costs from online source shown under description. Labor New, RS means Electrical 2012 26 51 13.50 3535 Downlight, recess mount, for both types. 1 fixture, 1 hour Replace, RS Means Electrical 2012 01 93 12.16 2530 | Lamp life | Lamp replacement life/full load equivalent operating hours, used for determining replacement life | Quantity of elevators | 90.1-2010 requires that elevator lighitng have a minimum efficacy of 35 lumens/watt. The 90.1 costs are based on the same LED design described undert the 90.1-2007 description. This lighting system is the sole lighting system priced for the 90.1-2010 case. 90.1-2010 sets a limit of 33W/cfm of exhaust air. The savings analysis did not include any savings for this item, as this threshold is easily met by the products in the market. No costs are identified for this item. The requirement includes a "standby mode" where lights and fans turn off if elevator is unoccupied with doors closed more than 15 minutes. Costs assumed to include an occupancy sensor, and $50 (incorporated with equipment costs) to integrate with control logic for doors and elevator activation. 90.1-2010 LED option- same as Baseline LED option Fixtures 7W R20 LED, 6 Fixtures, l lamp/fixture Price $20, Source www.goodmart.com/products/juno-tc1-4-in-miniature-universal-tc-non-insulated-incandescent-recessed-housing.htm Lamp 7W R20 LED, 310 lumens, system efficacy 44 lm/W, LPD 1.47 W/ft2, 50 FC, (90% fixture efficiency, coef. of utilization (CU) 0.85), lamp life 45,000 hours Price $23.47, Source www.homedepot.com/Electrical-Light-Bulbs-LED-Light-Bulbs/Philips/h_d1/N- 5yc1vZbm79Z1z0xeukZ15bZ1z132nbZ1z0ykp2/R-203285524/h_d2/ProductDisplay?catalogId=10053&langId=-1&storeId=10051 | PNNL lighting design for lighting selections. Products and costs from online source shown under description. Labor - Downlight RS Means Electrical 2012 26 51 13.50 3535, and 13.55 0100 Downlight, recess mount, for both types. | Lamp life | Lamp replacement life/full load equivalent operating hours, used for determining replacement life | Quantity of elevators
| 1 | [12 empty] | No energy credits |  | 2500 | 0.28539 | 1 |  |  |  |  | 1 |  |  |  |  | 94 | 1 Elec | 51.5 | 4 | 206 |  |  | 45 | 345 |  | 1 | 56 | 1 Elec | 51.5 | 3.5112 | 180.8268 |  | 35.524 | 272.3508
| 1 | [12 empty] | No energy credits |  | 45000 | 5 | 1 |  |  |  |  | 1 |  |  |  |  | 260.82 | 1 Elec | 51.5 | 6 | 309 |  |  | 85.473 | 655.293 |  | 5 | 140.82 | 1 Elec | 51.5 | 1.3167 | 67.8101 |  | 31.2945 | 239.9246
| 1 | [12 empty] | No energy credits |  |  |  | 1 | 90.1-2010 LED System (same as baseline LED System), replacement shown is lamps only, rounded to 21 years. |  | 45000 | 21 | 1 |  |  |  |  | 144.046 | 1 Elec | 51.5 | 4.6 | 236.9 |  |  | 57.1419 | 438.0879 |  | 1 | 39.2 | 1 Elec | 51.5 | 3.5112 | 126.5788 |  | 24.8668 | 190.6456 |  | 260.82 | 1 Elec | 51.5 | 6 | 309 |  |  | 85.473 | 0 | 655.293 |  | 21 | 140.82 | 1 Elec | 51.5 | 0.798 | 67.8101 |  | 34.7432 | 0 | 243.3733
| 1 | [12 empty] | No energy credits |  |  |  | 1 | Occupancy sensor and controls integration, 30 year life |  |  |  | 1 | [14 empty] | 5 | 42.246 | 1 Elec | 51.5 | 1.3167 | 20.343 |  | 9.3884 | 71.9774 |  | 221.5 | 1 Elec | 51.5 | 1.143 | 58.8645 |  |  | 42.0547 | 0 | 322.4192
| 1 | 1 | 1 | 1 | 1 | [8 empty] | No energy credits |  |  | 8760 | 12 | Large Office |  |  | 2154 | 12 |  |  |  |  | 1728.552 | 1 Elec | 51.5 | 55.2 | 2842.8 |  |  | 685.7028 | 5257.0548 |  | 1 | 470.4 | 1 Elec | 51.5 | 42.1344 | 1518.9451 |  | 298.4018 | 2287.7469 |  | 5787.84 | 1 Elec | 51.5 | 85.716 | 4414.374 |  |  | 1530.3321 | 0 | 11732.5461 |  | 21 | 1689.84 | 1 Elec | 51.5 | 9.576 | 813.7206 |  | 416.9189 | 0 | 2920.4795 | 6475.4913
| 1 | 1 | 1 | 1 | 1 | [8 empty] | No energy credits |  |  |  | 12 |  |  |  |  | 12 | [11 empty] | 0 |  |  | 5 | 506.952 | 1 Elec | 618 | 15.8004 | 244.1162 |  | 112.6602 | 863.7284
| 1 | 1 | 1 | 1 | 1 | [8 empty] | No energy credits |  |  | 8760 | 2 | Small Hotel |  |  | 2154 | 2 |  |  |  |  | 288.092 | 1 Elec | 51.5 | 9.2 | 473.8 |  |  | 114.2838 | 876.1758 |  | 1 | 78.4 | 1 Elec | 51.5 | 7.0224 | 253.1575 |  | 49.7336 | 381.2911 |  | 964.64 | 1 Elec | 51.5 | 14.286 | 735.729 |  |  | 255.0554 | 0 | 1955.4244 |  | 21 | 281.64 | 1 Elec | 51.5 | 1.596 | 135.6201 |  | 69.4865 | 0 | 486.7466 | 1079.2486
| 1 | 1 | 1 | 1 | 1 | [8 empty] | No energy credits |  |  |  | 2 |  |  |  |  | 2 | [14 empty] | 5 | 84.492 | 1 Elec | 103 | 2.6334 | 40.686 |  | 18.7767 | 143.9547
| 1 | 1 | 1 | 1 | 1 | [8 empty] | No energy credits |  |  | 8760 | 1 | Mid-rise Apartment |  |  | 2154 | 1 |  |  |  |  | 144.046 | 1 Elec | 51.5 | 4.6 | 236.9 |  |  | 57.1419 | 438.0879 |  | 1 | 39.2 | 1 Elec | 51.5 | 3.5112 | 126.5788 |  | 24.8668 | 190.6456 |  | 482.32 | 1 Elec | 51.5 | 7.143 | 367.8645 |  |  | 127.5277 | 0 | 977.7122 |  | 21 | 140.82 | 1 Elec | 51.5 | 0.798 | 67.8101 |  | 34.7432 | 0 | 243.3733 | 539.6243
| 1 | 1 | 1 | 1 | 1 | [8 empty] | No energy credits |  |  |  | 1 |  |  |  |  | 1 | [14 empty] | 5 | 42.246 | 1 Elec | 51.5 | 1.3167 | 20.343 |  | 9.3884 | 71.9774
[71 empty] | Base | Target | Difference | Difference

## ENV_Comp (hidden)
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22
| 1 | 3 |  | 2 | [5 empty] | Raw Cost |  |  |  | Multipliers |  |  |  | Final Cost |  |  |  |  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11
CZ/Prototype/Location/Description | Code | Prototype | CZ | Component | Assembly | U-factor | SHGC | U/SHGC | Assembly Description | Material | Labor | Equipment | Total | Material | Labor | Equipment | Total | Material | Labor | Equipment | Total | ProtoAbv | 1: Envelope Dimensions
1LOAbove Ground Wall - Mass2010 | 2010 | Large Office | 1 | Above Ground Wall | Mass | 0.58 |  | 0.58 |  | 4.4893 | 7.7042 | 0.63208 | 12.8256 | 1.047 | 1.046 | 0 | 1 | 4.7003 | 8.0586 | 0 | 12.8256 | LO |  |  | roof | wall-above grade | Below-grade wall | Floor area | Slab perimeter | window | skylight | 3x7_Door | 8x10_RUdoor
1LOAbove Ground Wall - Mass2010 | 2010 | Large Office | 1 | Above Ground Wall | Mass | 0.58 |  | 0.58 |  | 4.4893 | 7.7042 | 0.63208 | 12.8256 | 1.047 | 1.046 | 0 | 1 | 4.7003 | 8.0586 | 0 | 12.8256 | LO |  |  | ft2 | ft2 | ft2 | ft2 | ft | ft2 | ft2 | ea | ea
2LOAbove Ground Wall - Mass2010 | 2010 | Large Office | 2 | Above Ground Wall | Mass | 0.151 |  | 0.151 | Concrete Wall, 8" thick, poured in place (Means 2014) + Polyiso insulation | 5.8312 | 8.4749 | 0.63208 | 14.9382 | 1.047 | 1.046 | 0 | 1 | 6.1052 | 8.8648 | 0 | 14.9382 | LO | SO | Small Office | 6445.6274 | 2387.9911 | 0 | 5493 | 302.8333 | 642.4528 | 0 | 2 | 0 | SO
3LOAbove Ground Wall - Mass2010 | 2010 | Large Office | 3 | Above Ground Wall | Mass | 0.123 |  | 0.123 | Concrete Wall, 8" thick, poured in place (Means 2014) + Polyiso insulation | 6.0047 | 8.4749 | 0.63208 | 15.1117 | 1.047 | 1.046 | 0 | 1 | 6.2869 | 8.8648 | 0 | 15.1117 | LO | LO | Large Office | 38353.3472 | 74857.0885 | 6396 | 38353.3472 | 799.5 | 49904.2016 | 0 | 12 | 0 | LO
4LOAbove Ground Wall - Mass2010 | 2010 | Large Office | 4 | Above Ground Wall | Mass | 0.104 |  | 0.104 | Concrete Wall, 8" thick, poured in place (Means 2014) + Polyiso insulation | 6.1782 | 8.4749 | 0.63208 | 15.2853 | 1.047 | 1.046 | 0 | 1 | 6.4686 | 8.8648 | 0 | 15.2853 | LO | SR | Retail Standalone | 24695 | 11766.9625 | 0 | 24695 | 633.5 | 903.6107 | 256 | 8 | 5 | SR
5LOAbove Ground Wall - Mass2010 | 2010 | Large Office | 5 | Above Ground Wall | Mass | 0.090 |  | 0.090 | Concrete Wall, 8" thick, poured in place (Means 2014) + Polyiso insulation | 6.3518 | 8.4749 | 0.63208 | 15.4588 | 1.047 | 1.046 | 0 | 1 | 6.6503 | 8.8648 | 0 | 15.4588 | LO | PS | Primary School | 73960 | 17577.0267 | 0 | 73960 | 2064.3167 | 9464.5528 | 144 | 25 | 0 | PS
5LOAbove Ground Wall - Mass2010 | 2010 | Large Office | 5 | Above Ground Wall | Mass | 0.09 |  | 0.09 |  | 6.3518 | 8.4749 | 0.63208 | 15.4588 | 1.047 | 1.046 | 0 | 1 | 6.6503 | 8.8648 | 0 | 15.4588 | LO | SH | Small Hotel | 10801.5609 | 16259.1803 | 0 | 10801.5609 | 480 | 1982.9056 | 0 | 3 | 0 | SH
5LOAbove Ground Wall - Mass2010 | 2010 | Large Office | 5 | Above Ground Wall | Mass | 0.09 |  | 0.09 |  | 6.3518 | 8.4749 | 0.63208 | 15.4588 | 1.047 | 1.046 | 0 | 1 | 6.6503 | 8.8648 | 0 | 15.4588 | LO | NR | Small Hotel | 10801.5609 | 16259.1803 | 0 | 10801.5609 | 480 | 1982.9056 | 0 | 3 | 0 | NR
6LOAbove Ground Wall - Mass2010 | 2010 | Large Office | 6 | Above Ground Wall | Mass | 0.08 |  | 0.08 |  | 6.5253 | 8.4749 | 0.63208 | 15.6323 | 1.047 | 1.046 | 0 | 1 | 6.832 | 8.8648 | 0 | 15.6323 | LO | MA | Mid-rise Apartment | 8435.9609 | 13296.0185 | 0 | 8435.9609 | 799.5 | 3303.9815 | 0 | 0 | 0 | MA
6LOAbove Ground Wall - Mass2010 | 2010 | Large Office | 6 | Above Ground Wall | Mass | 0.08 |  | 0.08 |  | 6.5253 | 8.4749 | 0.63208 | 15.6323 | 1.047 | 1.046 | 0 | 1 | 6.832 | 8.8648 | 0 | 15.6323 | LO
7LOAbove Ground Wall - Mass2010 | 2010 | Large Office | 7 | Above Ground Wall | Mass | 0.071 |  | 0.071 |  | 6.7354 | 8.4749 | 0.63208 | 15.8424 | 1.047 | 1.046 | 0 | 1 | 7.0519 | 8.8648 | 0 | 15.8424 | LO
8LOAbove Ground Wall - Mass2010 | 2010 | Large Office | 8 | Above Ground Wall | Mass | 0.071 |  | 0.071 |  | 6.7354 | 8.4749 | 0.63208 | 15.8424 | 1.047 | 1.046 | 0 | 1 | 7.0519 | 8.8648 | 0 | 15.8424 | LO
1MAAbove Ground Wall - Steel-framed2010 | 2010 | Mid-rise Apartment | 1 | Above Ground Wall | Steel-framed | 0.124 |  | 0.124 |  | 5.1668 | 6.6189 | 0 | 11.7857 | 0.974 | 1.039 | 0 | 1 | 5.0324 | 6.8771 | 0 | 11.7857 | MA
1MAAbove Ground Wall - Steel-framed2010 | 2010 | Mid-rise Apartment | 1 | Above Ground Wall | Steel-framed | 0.124 |  | 0.124 |  | 5.1668 | 6.6189 | 0 | 11.7857 | 0.974 | 1.039 | 0 | 1 | 5.0324 | 6.8771 | 0 | 11.7857 | MA | 1: Insulation Depth
2MAAbove Ground Wall - Steel-framed2010 | 2010 | Mid-rise Apartment | 2 | Above Ground Wall | Steel-framed | 0.064 |  | 0.064 | 3.5 inch x 1-5/8 inch x 0.043 inch - Cold-Formed Steel Framing, Cavity Batt + Exterior Polyiso insulation | 6.0837 | 7.3024 | 0 | 13.3861 | 0.974 | 1.039 | 0 | 1 | 5.9256 | 7.5872 | 0 | 13.3861 | MA | 1: F-Factor; 2: Depth (ft)
3MAAbove Ground Wall - Steel-framed2010 | 2010 | Mid-rise Apartment | 3 | Above Ground Wall | Steel-framed | 0.064 |  | 0.064 | 3.5 inch x 1-5/8 inch x 0.043 inch - Cold-Formed Steel Framing, Cavity Batt + Exterior Polyiso insulation | 6.0837 | 7.3024 | 0 | 13.3861 | 0.974 | 1.039 | 0 | 1 | 5.9256 | 7.5872 | 0 | 13.3861 | MA | 1: 0.73; 2: 0
4MAAbove Ground Wall - Steel-framed2010 | 2010 | Mid-rise Apartment | 4 | Above Ground Wall | Steel-framed | 0.064 |  | 0.064 | 3.5 inch x 1-5/8 inch x 0.043 inch - Cold-Formed Steel Framing, Cavity Batt + Exterior Polyiso insulation | 6.0837 | 7.3024 | 0 | 13.3861 | 0.974 | 1.039 | 0 | 1 | 5.9256 | 7.5872 | 0 | 13.3861 | MA | 1: 0.54; 2: 2
5MAAbove Ground Wall - Steel-framed2010 | 2010 | Mid-rise Apartment | 5 | Above Ground Wall | Steel-framed | 0.064 |  | 0.064 | 3.5 inch x 1-5/8 inch x 0.043 inch - Cold-Formed Steel Framing, Cavity Batt + Exterior Polyiso insulation | 6.0837 | 7.3024 | 0 | 13.3861 | 0.974 | 1.039 | 0 | 1 | 5.9256 | 7.5872 | 0 | 13.3861 | MA | 1: 0.52; 2: 2
5MAAbove Ground Wall - Steel-framed2010 | 2010 | Mid-rise Apartment | 5 | Above Ground Wall | Steel-framed | 0.064 |  | 0.064 |  | 6.0837 | 7.3024 | 0 | 13.3861 | 0.974 | 1.039 | 0 | 1 | 5.9256 | 7.5872 | 0 | 13.3861 | MA | 1: 0.51; 2: 2